## gtgg1986to2001Fields
Gas Transmission and Gathering Systems Incident Reports for 1986 - 2001 (PHMSA Form 7100.2 Rev. 3-84) - Data Dictionary for Flagged Data file
Field Name | Data Type | Field Name Description | Form Location
DATAFILE_AS_OF | Date | Data as of date | Not on the form
SIGNIFICANT | Varchar2 | Identify if record meets the significant criteria or not: If there was fatality, injury, or total property damage is $50K or more in 1984 dollars, then SIGNIFICANT=’YES’, else SIGNIFICANT=’NO’. | Not on the form
SERIOUS | Varchar2 | Identify if record meets the SERIOUS criteria or not: If there was fatality or injury then SERIOUS = ‘YES’ else SERIOUS = ’NO’. | Not on the form
SYSTEM_TYPE | Varchar2 | System Type = 'GT (Gas Transmission)’ when PRTLK = TRANSMISSION SYSTEM or TRANSMISSION LINE OF DISTRIBUTION SYSTEM. System Type = 'GG (Gas Gathering)' when PRTLK = GATHERING SYSTEM. System Type is blank when PRTLK is NO DATA or blank. | Not on the form
RPTID | Number | PHMSA DOT assigned unique identifier for report | Top of first page
DOR | Varchar2 | Date when report was received at DOT | Top of first page
OPID | Number | Operator's OPS-issued Operator Identification number | Part 1 - General report information
NAME | Varchar2 | Operator Name | Part 1 - General report information
ACCITY | Varchar2 | Location of incident - City | Part 1 - General report information
ACCOUNTY | Varchar2 | Location of incident - County | Part 1 - General report information
ACSTATE | Varchar2 | Location of incident - State | Part 1 - General report information
ACZIP | Varchar2 | Location of incident - Zip Code | Part 1 - General report information
MPOST | Varchar2 | Mile Post/Valve Station | Part 1 - General report information
SURVY | Varchar2 | Survey station number | Part 1 - General report information
DTHH | Number | Time incident took place | Part 1 - General report information
IDATE | Date | Date incident occurred | Part 1 - General report information
CLASS | Number | Class location of the incident as described in 49 CFR Section 192.5 | Part 1 - General report information
SHORE | Varchar2 | Did the incident take place offshore? (Yes/No) | Part 1 - General report information
OFFAREA | Varchar2 | Offshore area location | Part 1 - General report information
BNUMB | Varchar2 | Offshore block number | Part 1 - General report information
OFFST | Varchar2 | Offshore state | Part 1 - General report information
OCS | Varchar2 | Did offshore incident take place on the Outer continental shelf? (Yes/No/Null) | Part 1 - General report information
IFED | Varchar2 | Did incident take place on Federal land other than Outer Continental Shelf? (Yes/No/Null) | Part 1 - General report information
ITYPE | Varchar2 | Incident type; Leak, Rupture, Other | Part 1 - General report information
RUPLN | Number | Rupture length | Part 1 - General report information
FAT | Number | Total number of fatalities | Part 1 - General report information
INJ | Number | Total number of injured requiring inpatient hospitalization | Part 1 - General report information
TOTAL_COST | Number | Total of Property Damage/Loss | Part 1 - General report information
TOTAL_COST_IN84 | Number | Converted Property Damage to 1984 dollars | Not on the form
TOTAL_COST_CURRENT | Number | Converted Property Damage to Current Year dollars | Not on the form
OPJUD | Varchar2 | Operator judgment | Part 1 - General report information
STHH | Number | Number of hours that elapsed till area was made safe | Part 1 - General report information
STMN | Number | Number of minutes that elapsed till area was made safe | Part 1 - General report information
TELRN | Varchar2 | Report number of matching NRC telephonic report | Part 1 - General report information
TELRT | Varchar2 | Date incident was reported to NRC (yyyymmdd) | Part 1 - General report information
INPRS | Number | Estimated pressure at point and time of incident. | Part 1 - General report information
MXPRS | Number | Maximum allowable operating pressure (MAOP in PSIG) | Part 1 - General report information
MPEST | Varchar2 | Max allowable operating pressure was established by test or by 49 CFR, section 192.619 | Part 1 - General report information
TEST | Number | The test pressure if the MAOP was established by test | Part 1 - General report information
CAUSE | Varchar2 | Apparent cause of the incident | Part 2 - Apparent cause of incident
MAP_CAUSE | Varchar2 | Cause by PHMSA for 20 year incident trending | Not on the form
MAP_SUBCAUSE | Varchar2 | SubCause by PHMSA for 20 year incident trending | Not on the form
PRTLK | Varchar2 | Incident occurred; Transmission System, Gathering System, Transmission Line of Distribution system | Part 4 - Origin of the incident
PRTFL | Varchar2 | Failure occurred; Body of pipe, Fitting, Mechanical Joint, Other, Valve, Weld | Part 4 - Origin of the incident
PRTFO | Varchar2 | Text describing Other for PRTLK field | Part 4 - Origin of the incident
MLKD | Varchar2 | Material involved; Steel, Other | Part 4 - Origin of the incident
MLKDO | Varchar2 | Text describing Other Plastic or Other for MLKD field | Part 4 - Origin of the incident
PRTSY | Varchar2 | Part of system involved in incident; Pipeline, Regulator/Metering System, Compressor Station, Other | Part 4 - Origin of the incident
PRTSO | Varchar2 | Text describing Other Plastic or Other for PRTSY field | Part 4 - Origin of the incident
PRTYR | Number | Year part was installed | Part 4 - Origin of the incident
NMDIA | Number | Nominal Pipe Size (NPS) (diameter) in inches | Part 5 - Material Specification
THK | Number | Wall thickness in inches | Part 5 - Material Specification
SPEC | Varchar2 | Material specification | Part 5 - Material Specification
SMYS | Number | System maximum yield strength | Part 5 - Material Specification
SEAM | Varchar2 | Seam type | Part 5 - Material Specification
VALVE | Varchar2 | Valve type | Part 5 - Material Specification
MANU | Varchar2 | Manufacturer | Part 5 - Material Specification
MANYR | Number | Year manufactured | Part 5 - Material Specification
LOCLK | Varchar2 | Area of Incident; Under Pavement, Above Ground, Under Ground or Under Water, Other | Part 6 - Environment
LOCLO | Varchar2 | Text describing Other for field LOCLK | Part 6 - Environment
PNAME | Varchar2 | Incident Report Prepared by | Part 7 - Preparer and Authorized Signature
PHONE | Varchar2 | Preparer's telephone number | Part 7 - Preparer and Authorized Signature
LOC | Varchar2 | Location where corrosion occurred; Internally, Externally | Part A - Corrosion
ADESC | Varchar2 | Visual description of corrosion; Localized Pitting, General Corrosion, Other | Part A - Corrosion
DESCO | Varchar2 | Text describing Other for field ADESC | Part A - Corrosion
CAUCR | Varchar2 | Cause of Corrosion; Galvanic, Other | Part A - Corrosion
CAUCO | Varchar2 | Text describing Other for field CAUCR | Part A - Corrosion
COAT | Varchar2 | Pipe Coating Information; Bare, Coated | Part A - Corrosion
PROT | Varchar2 | Was corroded pipeline cathodically protected? (Yes/No/Null) | Part A - Corrosion
CPYR | Number | Year Cathodic Protection Started | Part A - Corrosion
CAULK | Varchar2 | Primary cause of incident | Part B - Damage by Outside Forces
DMGO | Varchar2 | Text describing Other for field DMGO | Part B - Damage by Outside Forces
NOTIF | Varchar2 | Did operator get prior notification that equipment would be used in the area? (Yes/No/Null) | Part B - Damage by Outside Forces
NOTDT | Varchar2 | Date when notification received (yyyymmdd) | Part B - Damage by Outside Forces
MARK | Varchar2 | Was pipeline location marked either as a result of notification or by markers already in place? (Yes/No/Null) | Part B - Damage by Outside Forces
MRKTP | Varchar2 | Specify type of marking | Part B - Damage by Outside Forces
STAT | Varchar2 | Does a statute or ordinance require the outside party to determine whether underground facility(ies) exist? (Yes/No/Null) | Part B - Damage by Outside Forces
CAULC | Varchar2 | Cause of the construction defect; Construction, Material | Part C - Construction Defect
CAULO | Varchar2 | Description of components other than pipe | Part C - Construction Defect
CTEST | Varchar2 | Was part which leaked tested before incident occurred? (Yes/No/Null) | Part C - Construction Defect
TESTD | Varchar2 | Date of test (yyyymmdd) | Part C - Construction Defect
MED | Varchar2 | Test medium; Water, Gas, Other | Part C - Construction Defect
MEDO | Varchar2 | Text describing Other for field MED | Part C - Construction Defect
TMPS | Number | Time held at test pressure in hours | Part C - Construction Defect
LKPS | Number | Estimated test pressure at point of incident (psig) | Part C - Construction Defect
NARRATIVE | Varchar2 | Narrative description of factors contributing to the incident | Part 3 - Narrative description of factors contributing to the incident

## gtgg1986to2001
DATAFILE_AS_OF | SIGNIFICANT | SERIOUS | SYSTEM_TYPE | RPTID | DOR | OPID | NAME | ACCITY | ACCOUNTY | ACSTATE | ACZIP | MPOST | SURVY | DTHH | IDATE | CLASS | SHORE | OFFAREA | BNUMB | OFFST | OCS | IFED | ITYPE | RUPLN | FAT | INJ | TOTAL_COST | TOTAL_COST_IN84 | TOTAL_COST_CURRENT | OPJUD | STHH | STMN | TELRN | TELRT | INPRS | MXPRS | MPEST | TEST | CAUSE | MAP_CAUSE | MAP_SUBCAUSE | PRTLK | PRTFL | PRTFO | MLKD | MLKDO | PRTSY | PRTSO | PRTYR | NMDIA | THK | SPEC | SMYS | SEAM | VALVE | MANU | MANYR | LOCLK | LOCLO | PNAME | PHONE | LOC | ADESC | DESCO | CAUCR | CAUCO | COAT | PROT | CPYR | CAULK | DMGO | NOTIF | NOTDT | MARK | MRKTP | STAT | CAULC | CAULO | CTEST | TESTD | MED | MEDO | TMPS | LKPS | NARRATIVE
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19860033 |  | 15488 | PHILLIPS 66 NATURAL GAS CO |  | CAMPBELL | WY |  |  | 0+00 | 830 | 1986-01-27 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 6 | 0 |  | 19860127 | 850 | 1424 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: GATHERING SYSTEM; PRTFL: NO DATA; MLKD: NO DATA; PRTSY: PIPELINE; PRTSO: & SPHERE RECEIVER; PRTYR: 0; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: NO DATA; PNAME: R D GUNLIKSON - ASSOC PROCESS; PHONE: 3072373791; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | PIPELINE PRESSURE WAS BEING REDUCED BY VENTING TO THE ATMOSPHERE. SOME UNKNOWN SOURCE IGNITED THE GAS.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19860037 |  | 15105 | PANHANDLE EASTERN PIPELINE CO | WAVERLY | MORGAN | IL | 62692 | C-38 | 73+10 | 955 | 1986-01-17 | 1 | NO |  |  | IL | NO | NO | OTHER | 0 | 0 | 0 | 60000 | 56789.3697 | 123717.0048 | Null | 0 | 15 |  | 19860117 | 451 | 845 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: FILLET; MLKD: STEEL; PRTSY: OTHER; PRTSO: 2" BRANCH CONNECTION; PRTYR: 1963; NMDIA: 16; THK: 0.25; SPEC: X-52; SMYS: 0; MANU: UNK; MANYR: 0; LOCLK: UNDER GROUND; PNAME: HARRY BAGGERLY, AREA SUPT.; PHONE: 2174352261; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | THE OPERATION OF A BACKHOE IN THE VICINITY OF A 2" BRANCH CONNECTION INTRODUCEDSTRESSES IN THE PIPING WHICH CAUSED IT TO BREAK AT THE TAP CONNECTION TO A 16" PIPELINE
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19860039 |  | 2620 | COLUMBIA GULF TRANSMISSION CO | EUGENE ISLAND | OFFSHORE | LA |  | X-1881, 492.72 |  | 1230 | 1986-01-15 |  | YES | E.I. | 293 |  | YES | NO | LEAK | 0 | 0 | 0 | 120000 | 113578.7395 | 247434.0097 | Null | 0 | 0 |  | 19860117 | 1100 | 1440 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: POWER GAS PIPING; MLKD: STEEL; PRTSY: OTHER; PRTSO: POWER GAS PIPING; PRTYR: 1969; NMDIA: 0.5; THK: 0.15; SPEC: SCH. 80 316 S.S; SMYS: 0; MANYR: 0; LOCLK: UNDER WATER; PNAME: R. J. UPCHURCH; PHONE: 7136211200; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: YES; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19860042 |  | 5304 | FLORIDA GAS TRANSMISSION CO | MT. VERNON | BALDWIN | AL | 36560 | 195.1 | 229+87 | 900 | 1986-02-10 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 33 |  | 19860210 | 950 | 975 | BY TEST | 1220 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | GIRTH | STEEL |  | PIPELINE |  | 1965 | 30 | 0.34 | API 5L | 60000 | ERW |  | U.S.STEEL | 1965 | UNDER GROUND |  | JEFF WHIPPO, COMPLIANCE ENGR. | 7136546237 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | GIRTH WELD | YES | 19660109 | WATER |  | 24 | 1220 | CRACK ON TOP OF GIRTH WELD WAS LEAKING.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19860049 |  | 19610 | TRANSWESTERN PIPELINE CO | HOUSTON | HARRIS | TX | 77001 | MP. 21 LIPSCOMB | 1107 | 1650 | 1986-02-21 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 117000 | 110739.271 | 241248.1595 | Null | 0 | 45 |  | 19860224 | 400 | 550 | BY TEST | 825 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: FILLET; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1979; NMDIA: 4.5; THK: 0.24; SPEC: A53; SMYS: 35000; SEAM: SEAMLESS; MANU: BLUE WATER MAINT; MANYR: 1979; LOCLK: ABOVE GROUND; PNAME: JEFF WHIPPO, COMPLIANCE ENGR.; PHONE: 7136546237; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | A BROKEN BOLT IN THE COMPRESSOR CAUSED VIBRATION WHICH CAUSED A 4.5" NIPPLE FROM A SUCTION BOTTLE TO BREAK AROUND A CIRCUMFERENTIAL FILLET WELD.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19860056 |  | 19235 | TEXAS EASTERN GAS PIPELINE CO | LANCASTER | GARRARD | KY | 40422 | 434.65 | 22949 | 205 | 1986-02-21 | 1 | NO |  |  |  | Null | NO | RUPTURE | 487 | 0 | 3 | 1300000 | 1230436.344 | 2680535.105 | Null | 1 | 1 |  | 19860221 | 987 | 1000 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1957; NMDIA: 30; THK: 0.38; SPEC: 5LX-52; SMYS: 52000; SEAM: ELECTRIC WELD; MANU: REPUBLIC; MANYR: 1957; LOCLK: UNDER GROUND; PNAME: W. B. MCGEHEE, MANAGER; PHONE: 7137595353; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | THE PIPELINE RUPTURED NEAR THE SOUTH END OF A ROAD CROSSING AT KENTUCKY STATE HIGHWAY #52. THE CAUSE OF THE INCIDENT IS CURRENTLY UNDER INVESTIGATION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19860057 |  | 10030 | KN ENERGY INC (KANSAS NEBRASKA NATURAL GAS CO INC) | SHARON SPRINGS | WALLACE | KS | 67758 |  | 1402 | 1045 | 1986-02-14 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 0 |  | 19860214 | 425 | 700 | BY CFR 192.619(A)(3) | 1 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1965; NMDIA: 3.5; THK: 0.14; SMYS: 24000; SEAM: EW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: A. T. MCMASTER, DIRECTOR; PHONE: 4024622141; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19860124; MARK: YES; MRKTP: TEMP & PERM MARKERS; STAT: NO; CTEST: Null | LEAK REPORT COVERS A NATURAL GAS LEAK THAT OCCURED ON K N ENERGY, INC.'S (K N) 3-INCH TRANSMISSION PIPELINE IN WALLACE COUNTY, KANSAS ON FEBRUARY 14, 1986. IGNITION DID NOT OCCUR. HOWEVER, THE LEAK DID DISRUPT SERVICE TO CITY OF SHARON SPRINGS, KS, FOR APPROXIMATELY TEN HOURS. THE CITY HAS APPROXIMATELY 550 GAS METERS.THE LEAK WAS CAUSED BY AN OUTSIDE PARTY UTILIZING A BACKHOE TO INSTALL A PIPELINE FOR ANOTHER COMPANY UNDER K N'S 3-INCH PIPELINE. IN ADVANCE OF SUCH EXCAVATION, K N WAS NOTIFIED OF THE PLANNED EXCAVATION AND IT EXPOSED THE 3-INCH PIPELINE THAT WAS SUBSEQUENTLY DAMAGED. K N REQUESTED THAT ITS PERSONNEL BE PRESENT WHEN THE UNDERCROSSING WAS TO BE MADE. UNFORTUNATELY, K N RECEIVED NO CALL SO ITSPERSONNEL WAS NOT PRESENT WHEN THE PIPLINE WAS HIT. NO INJURIES OR SIGNIFICANT PROPERTY DAMAGE OCCURRED.THE DAMAGE PORTION OF PIPELINE IS IN A CLASS I LOCATION, MARKED WITHPERMANENT MARKERS. ONE IS A PIPELINE MARKER LOCATED 2,707 SOUTHOF THE INCIDENT WHICH IS CLEARLY VISIBLE FROM THE POINT OF IMPACT.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19860058 |  | 2714 | CONSOLIDATED GAS TRANSMISSION CORP | LIGHTBURN | LEWIS | WV |  |  |  | 100 | 1986-02-13 | 1 | NO |  |  |  | Null | NO | RUPTURE | 1 | 0 | 1 | 600 | 567.8937 | 1237.17 | Null | 0 | 1 |  | 19860213 | 835 | 100 | BY TEST | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: EMCO METER; MLKD: OTHER; MLKDO: CAST IRON; PRTSY: COMPRESSOR STATION; PRTYR: 1967; NMDIA: 0; THK: 0; SMYS: 0; MANU: ROCKWELL MFG.; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: JACK ADAMS; PHONE: 3046238410; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | STATION EMPLOYEE OPENED 1" BALL VALVE ON BYPASS WHICH ALLOWED GAS AT 835 PSIG TO ENTER EMCO METER (RATED AT 100 PSIG) RESULTING IN METER CASE RUPTURING.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19860059 |  | 18536 | SOUTHWEST GAS CORP | WADSWORTH |  | NV | 89701 | 2.54 | 118 | 1515 | 1986-02-19 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 11 |  | 19860220 | 520 | 700 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: UNKNOWN; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1963; NMDIA: 12; THK: 0.22; SPEC: API 5LX; SMYS: 52000; SEAM: ELEC RESISTANCE; MANYR: 0; LOCLK: UNDER WATER; PNAME: CLARK STONER, MANAGER; PHONE: 7028825775; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | FLOODING OF THE TRUCKEE RIVER NEAR WADSWORTH, NV CAUSED THE 12" STEEL HIGH PRESSURE CARSON LATERAL TO BE WASHED OUT WHERE IT CROSSES THE TRUCKE RIVER.SEE ATTACHED LETTER.INTENSE RAIN STORMS BEG. ON THE 13TH OF FEB. CAUSED FLOODINGOF THE TRUCKEE RIVER. THIS FLOODING SUBSEQUENTLY CAUSED THE WASHOUTOF SOUTHWEST'S 12-INCH HIGH-PRESSURE LINE SERVICING THE COMMUNITIES OFWADSWORTH, FERNLEY, FALLON, YERINGTON, CARSON CITY, MINDEN, GARDNERVILLE, SOUTHAND NORTH LAKE TAHOE, NEVEDA, AND SOUTH AND NORTH LAKE TAHOE CA. THE WASHOUTOCCURRED AT 1515 HOURS ON WED., FEB. 19, 1986. P-2 & P-3 CURTAILMENT WASINITIATED, BUT EVENTUALLY ALL SERV. TO THE NEV. COMMUNITIES WAS LOST,EXCEPT FOR LAKE TAHOE AND FALLON AREAS ON FEB. 19, 1986.RELIGHTS STARTED IN SOUTHWEST'S AREAS AS SOON AS POSSIBLE AFTER THEDISTRIBUTION SYSTEMS WERE PURGED. SNOW MADE RELIGHTS VERY DIFFICULT.RELIGHTS STARTED FEB 24 & COMPLETED MARCH 3RD.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19860060 |  | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | CALE | NEVADA | AR | 71828 |  | 5846+6 | 1930 | 1986-02-24 | 1 | NO |  |  |  | Null | NO | RUPTURE | 75 | 0 | 0 | 147354 | 139469.0131 | 303836.5922 | Null | 1 | 45 |  | 19860224 | 750 | 800 | BY TEST | 960 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1951 | 20 | 0.25 | STEEL GRADE + 46 | 1150 | ERW |  | YOUGSTOWN | 1949 | UNDER GROUND |  | RAYMOND D GERMANY - MGR | 3182262708 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL |  | YES | 19770517 | WATER |  | 24 | 960 | LINE "S", 20" O.D. PIPELINE BLEW OUT AT 75' SECTION IN THE BODY OF THE PIPE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19860064 |  | 15007 | PACIFIC GAS & ELECTRIC CO | COTTONWOOD | TEHAMA | CA |  | 7.23 | 381&74 | 2234 | 1986-02-23 | 1 | NO |  |  |  | Null | NO | RUPTURE | 0 | 0 | 0 | 1350000 | 1277760.8188 | 2783632.6091 | YES | 3 | 4 |  | 19860224 | 480 | 600 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: UNKNOWN; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1962; NMDIA: 12; THK: 0.5; SPEC: API 5L GR B; SMYS: 35000; SEAM: SEAMLESS; MANYR: 0; LOCLK: UNDER WATER; PNAME: BRUCE P SADLER - MGR; PHONE: 4159723161; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | TRANSMISSION MAIN RUPTURED DUE TO STRESS CAUSED BY EXCESSIVE WATER FLOW IN SACRAMENTO RIVER DURING FLOODING.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19860067 |  | 15007 | PACIFIC GAS & ELECTRIC CO | ROCKLIN | PLACER | CA | 95677 | 3.2 | 168+96 | 1605 | 1986-03-06 | 1 | NO |  |  | CA | Null | NO | LEAK | 0 | 0 | 0 | 50000 | 47324.4748 | 103097.504 | YES | 19 | 5 |  | 19860306 | 498 | 500 | BY TEST | 1180 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1962; NMDIA: 8; THK: 0.19; SPEC: AP15LX X42; SMYS: 42000; SEAM: ERW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: BRUCE P. SADLER, MANAGER; PHONE: 4159723161; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PIPELINE MARKERS; STAT: YES; CTEST: Null | PREVIOUS DAMAGE TO PIPELINE BY CONTRACTOR WAS DISCOVERED BY PG AND E PERSONNEL AND LEAKAGE REPAIRED. CONTRACTOR, WHILE GRADING PROPERTY, STRUCK STEEL PIPELINEWITH A CATERPILLAR TRACTOR ALLOWING GAS TO ESCAPE TO ATMOSPHERE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19860071 |  | 2731 | CHEVRON PIPELINE CO | TEXAS CITY | GALVESTON | TX | 77401 | MP 29.25 | 1544+4 | 624 | 1986-03-17 | 2 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 100000 | 94648.9495 | 206195.0081 | Null | 2 | 0 |  | 19860317 | 908 | 1440 | NO DATA | 2160 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: HOT WATER HEATER; MLKD: STEEL; PRTSY: OTHER; PRTSO: TUBE HEATER; PRTYR: 1973; NMDIA: 0; THK: 0; SMYS: 0; MANU: NATIONAL TANK CO.; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: J. T. NUCKOLS, ESF&H SPECIALIST; PHONE: 4098393131; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: NO DATA; CTEST: Null; MED: NO DATA; TMPS: 0; LKPS: 0 | EQUIPMENT FAILURE INSIDE A GAS FIRED - WATER FILLED ETHYLENE HEATER. THIS HEATER HAS ETHYLENE PASSING THRU A TUBE COIL ETHYLENE HEATER. ITS TEMPERATURE FOR BETTER MEASUREMENT. IT APPEARS THAT THERE WAS A TUBE FAILURE. UNTIL DOW PIPE LINE COMPLETES THE ANALYSIS OF THEIR EQUIPMENT NO DEFINITE CONCLUSION CAN BE MADE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19860077 | 1986-04-15 | 3260 | DELTA NATURAL GAS CO INC | BARBOURVILLE | KNOX | KY | 40906 |  |  | 2130 | 1986-03-26 | 2 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 45 |  | 19860326 | 180 | 300 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1966; NMDIA: 6; THK: 0.19; SPEC: API 5L GRADE B; SMYS: 24000; SEAM: SEAMLESS; MANYR: 0; LOCLK: UNDER GROUND; PNAME: GEORGE BILLINGS, MANAGER, GAS SUPPLY; PHONE: 6067446171; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: LINE MARKER POSTS; STAT: YES; CTEST: Null | AN EQUIPMENT OPERATOR MINING COAL AT 9:30P.M. GOUGED A HOLE IN THE 6" STEEL PIPELINE. THE AFFECTED SECTION OF THE LINE WAS TAKEN OUT OF SERVICE UNTIL THE NECESSARY REPAIRS WERE MADE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19860078 |  | 15007 | PACIFIC GAS & ELECTRIC CO | PRINCETON | COLUSA | CA | 95970 | 4.82 | 254+01 | 1405 | 1986-03-09 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 88000 | 83291.0756 | 181451.6071 | YES | 1 | 18 |  | 19860309 | 620 | 800 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: NOT KNOWN AT TIME OF RPRT; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1955; NMDIA: 10.75; THK: 0.37; SPEC: API 5L GRB; SMYS: 35000; SEAM: SEAMLESS; MANYR: 0; LOCLK: UNDER WATER; PNAME: BRUCE P SADLER - MGR; PHONE: 4159723162; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | IT IS SPECULATED THAT HEAVY WATER RUN-OFF CREATED UNDUE FFORCE ON THE 10" PIPELINE RESULTING IN THE LINE BREAK.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19860080 |  | 19160 | TENNESSEE GAS PIPELINE CO | HARRIS | WALLER | TX | 77423 |  |  | 1820 | 1986-03-02 | 1 | NO |  |  |  | Null | NO | RUPTURE | 47 | 0 | 0 | 244662 | 231570.0129 | 504480.8307 | Null | 1 | 0 |  |  | 695 | 750 | BY TEST | 1042 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1944; NMDIA: 24; THK: 0.25; SPEC: SPEC-DTD 10/10/43; SMYS: 50000; SEAM: EFW; MANU: A.O. SMITH; MANYR: 1944; LOCLK: UNDER GROUND; PNAME: R. L. DEAN, MANGER, CODES & STANDARDS; PHONE: 7137572858; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: Null; STAT: NO; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19860081 |  | 18732 | SUNOLIN CHEMICAL CO | DEEPWATER | SALEM | NJ | 08023 | 10/2389 | 10/238 | 1200 | 1986-04-03 | 3 | NO |  |  | NJ | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 0 |  | 19860403 | 212 | 1170 | BY TEST | 1640 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1961; NMDIA: 4.5; THK: 0.19; SPEC: API-5L-GRADE B; SMYS: 3500; SEAM: WELDED PIPE; VALVE: 600# PIPELINE; MANU: SWEPCO TUBE CORP.; MANYR: 1961; LOCLK: UNDER GROUND; PNAME: BURLEY R. MELTON, SAFETY, HEALTH & ENVIRONMENTAL MGR.; PHONE: 3027923130; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19860331; MARK: YES; MRKTP: WOODEN STAKE; STAT: YES; CTEST: Null | DUPONT ADVISED SUN OLIN THAT SOME ELECTRICAL WORK WAS GOING TO BE DONE AT THE UNION CARBIDE CONSTRUCTION SITE IN NEW JERSEY NEAR THE METERING STATION. SUN OLINNOTITIED SUN PIPELINE TO SUPPLY SOMEONE FOR THE JOB. SUN PIPELINE REPRESENTATIVE, JIMMY JACKSON CAME ON SITE TO ADVISE UNION CARBIDE'S ELECTRICAL CONTRACTOR.AT APPROXIMATELY 12 NOON ON THURSDAY, APRIL 3, THE AUGUR DIGGING THE HOLE PUNCTURED A PIPELINE. SUN OLIN WAS NOTIFIED AT 12:05 P.M. SHOWED GREATER THAN 500 PPM CARBON MONOXIDE IN THE AIR, THEREBY CONFIRMING THAT IT WAS THE CARBON MONOXIDEPIPELINE THAT WAS DAMAGED. DUPONT SHUT DOWN THEIR CARBON MONXIDE USER AT THE RIVER WAS CLOSED AT 12:30 P.M. DAVE SCHMIDT OF DUPONT ESTIMATED THE IMMEDIATE AREA WAS SAFE (LESS THAN 50 PPM CARBON MONOXIDE WITHIN A 20 FOOT RADIUS FROM THE LOCATION OF THE HOLE IN THE PIPELINE) AT 1:00 P.M. THE PIPELINE WAS CONSIDERED ESSENTIALLY DEPRESSURED AT 1:30 P.M. AT 3:00 P.M., DUPONT PUT NITROGEN FROM THENITROGEN PRODUCT LINE INTO THE CARBON MONOXIDE PIPELINE WITH 1/2 INCH TUBING. AT 4:12 P.M., SUN OLIN STARTED DEPRESSURING THE CARBON MONOXIDE PRODUCT PIPELINEFROM THE NEW JERSEY RIVER VALVE MANIFOLD TO THE SUN OLIN FLARE. AT 4:15 P.M., SUN OLIN STARTED DEPRESSURING THE CARBON MONOXIDE PRODUCT PIPELINE FROM THENEW JERSEY RIVER VALVE MANIFOLD TO THE SUN OLINE FLARE. AT 4:15 PM, ITWAS DECIDED TO HAND DIG OUT THE AUGUR EQUIPMENT. AT A DEPTH OF ABOUT 4 FEET,THEY COULD SEE THE AUGUR HAD PUNCTURED A TRIANGULAR HOLE WITH A BASE OF ABOUT1 INCH AND ABOUT 1/2 INCH HIGH IN THE SIDE OF THE CARBON MONOXIDE PIPELINE.THE PIPELINE WAS CLAMPED BETWEEN 6-7 PM. AND SHORTLY THEREAFTER, THE NEWJERSEY RIVER VALVE WAS OPENED, THE ENTIRE PIPELINE STARTED TO PURGE BACK TOSUN OLIN WHICH THEN DISPLACED THE REMAINING CARBON MONOXIDE IN THE LINE WITHNITROGEN. AT ABOUT 10:30 PM, IT WAS DECIDED TO PURGE THE PIPELINE THROUGHOUTTHURSDAY AND FRIDAY NIGHT, THEN MAKE ANOTHER GAS ANALYSIS EARLY SATURDAYMORNING. ON SATURDAY MORNING, APRIL 5, THE LINE WAS SAFE AND THE DAMAGEDSECTION OF THE PIPE WAS CUT OUT AND REPLACED WITH A NEW 21-1/2 INCH SECTION OFPIPE.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19860082 |  | 18064 | ST JOHN THE BAPTIST PARISH UTILITIES | GARYVILLE | ST JOHN THE BAPTIST | LA | 70051 |  |  | 13 | 1986-01-23 |  | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 1 | 15000 | 14197.3424 | 30929.2512 | Null | 6 | 0 |  | 19860123 | 60 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: OTHER; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1955; NMDIA: 2; THK: 0.15; SMYS: 0; MANYR: 0; LOCLK: UNDER GROUND; PNAME: PATRICK T. MCTOPY, DIRECTOR; PHONE: 5045352259; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | THE CONTRACTOR WAS IN THE PROCESS OF CONDEMNING AN EXISTING GAS LINE WHEN LEAKING GAS IGNITED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19860083 |  | 20230 | UNITED GAS PIPELINE CO | HOUMA | TERREBONNE | LA | 70063 | 3.13 | 165+10 | 330 | 1986-03-24 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 260000 | 246087.2688 | 536107.021 | YES | 3 | 15 |  | 19860324 | 794 | 1105 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1959; NMDIA: 12; THK: 0.31; SPEC: API 5L; SMYS: 35000; SEAM: SMLS; MANU: NATIONAL STEEL; MANYR: 0; LOCLK: UNDER WATER; PNAME: W. F. ST. GERMAIN, PIPELINE SAFETY ANALYST; PHONE: 7132295772; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; STAT: NO; CTEST: Null | A CARGO VESSEL (THE GREEN CANYON EXPRESS) TRAVELING IN DENSE FOG, COMPLETELY OUTOF THE CHANNEL, IN THE HOUMA NAVIGATION CANAL, STRUCK THE CANAL CROSSING RISER, SEVERING THE LINE AND IGNITING THE GAS. THE GAS SUPPLY WAS CUT OFF WITHIN MINUTES BY SUPERIOR OIL PERSONNEL NEARBY.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19860093 |  | 20230 | UNITED GAS PIPELINE CO | MARKSVILLE | AVOYELLES | LA | 71351 | 115 | 6155+6 | 1415 | 1986-04-01 | 1 | NO |  |  |  | Null | Null | LEAK | 0 | 0 | 0 | 92906 | 87934.5531 | 191567.5342 | Null | 0 | 20 |  | 19860403 | 865 | 1000 | BY TEST | 1500 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: COMPRESSOR BEARING; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1963; NMDIA: 0; THK: 0; SMYS: 0; MANU: COOPER; MANYR: 1963; LOCLK: UNDER WATER; LOCLO: & ABOVE GROUND; PNAME: W F ST GERMAIN - P/L SAFETY ANALYST; PHONE: 7132295772; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | OIL HOLES ON COMPRESSOR BEARING APPARENTLY WERE CLOGGED CAUSING THE BEARING ANDSHAFT TO OVERHEAT AND IGNITE THE OIL AND GAS.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19860099 |  | 2555 | COLLET VENTURES INC- COPELAND PLANT | AQUILA | WASHINGTON | AL | 36558 |  |  | 715 | 1986-02-18 | 2 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 4 | 50 |  | 19860218 | 1000 | 2552 | BY TEST | 2850 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1985 | 3 | 0.3 | API 5L GRADE B | 48280 | SEAMLESS PIPE |  | VALBUREC | 1984 | UNDER GROUND |  | LARRY G SMITH - SAFETY SUP | 2058463634 | INTERNALLY | LOCALIZED PITTING |  | NO DATA |  | COATED | YES | 1985 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | ORIGINAL TESTING SHOWED POSSIBLE MATERIAL DEFECT BUT AFTER EXTENXIVE TESTING ITWAS PROVEN TO BE SULFIDE STRESS DUE TO LACK OF CONSTANT FLOW THROUGH LINE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19860101 |  | 20040 | UNION CARBIDE CORP | VERDONVILLE | LOGAN | WV |  |  |  | 2210 | 1986-05-07 | 2 | NO |  |  |  | Null | NO | RUPTURE | 2 | 0 | 0 | 15800 | 14954.534 | 32578.8113 | YES | 1 | 30 |  | 19860508 | 195 | 225 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1948 | 10 | 0.25 | API 5L | 36000 | FURNAC BUTT WEL |  | A O SMITH | 1947 | UNDER GROUND |  | C L THOMPSON - P/L GROUP LEADER | 3047472419 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | BARE | YES | 1985 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | THE INCIDENT OCCURED IN A 10" NATURAL GAS PIPELINE APPROXIMATELY 40 FEET FROM THE FENCE LINE OF A COMPRESSOR STATION WHICH PUMPS NATURAL GAS. GENERAL EXTERNAL GALVANIC CORROSION ACCELERATED BY THE COMPRESSOR OUTLET TEMPERATURE (90 DEGREES F) IS BELIEVED TO BE THE PRIMARY CAUSE. OTHER POTENTIALLY CONTRIBUTING FACTORS ARE THE LOCAL SOIL CONDITIONS AND POSSIBLY VIBRATIONS FROM THE COMPRESSOR.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19860102 |  | 12690 | MONTANA POWER CO |  | POWELL | MT | 59722 |  | 220+00 | 405 | 1986-05-03 | 1 | NO |  |  |  | Null | NO | RUPTURE | 3 | 0 | 0 | 160000 | 151438.3193 | 329912.0129 | Null | 2 | 0 |  | 19860503 | 460 | 500 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1931 | 20 | 0.25 | SMITHWELD | 50000 | ELECTRIC WELD |  | A O SMITH | 1931 | UNDER GROUND |  | KENNETH J ERICKSON - ENG SECT HEAD GAS OPER | 4067235421 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1938 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | THE RUPTURE ORIGINATED IN A LOCALIZED CORROSION AREA APPROXIMATELY ONE (1) FOOTIN DIAMETER. RUPTURE PROPAGATED TO THE THREE (3) FOOT LENGTH MENTIONED ABOVE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19860103 |  | 12690 | MONTANA POWER CO |  | PARK | MT |  | MP-81.2 | 4288+2 | 415 | 1986-04-08 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 30300 | 28678.6317 | 62477.0874 | Null | 1 | 0 |  | 19860409 | 450 | 751 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1931; NMDIA: 10; THK: 0.25; SPEC: SMITH WELD ERW; SMYS: 35000; SEAM: SMITH WELD ERW; VALVE: ROCKWELL FIG 48; MANU: A O SMITH CORP; MANYR: 1931; LOCLK: UNDER GROUND; PNAME: KENNETH J ERICKSON - ENG SECT HEAD; PHONE: 4067235421; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PIPELINE MARKER POST; STAT: YES; CTEST: Null | A SELF POWERED SCRAPPER PUSHED BY A D-7 TRACTOR TORE A VERY LARGE HOLE IN THE PIPE RESULTING IN A RAPID LOSS OF GAS TO THE ATMOSPHERE.
2021-02-26 10:36 | YES | YES | GG (Gas Gathering) | 19860104 |  | 17620 | ROCKY MOUNTAIN NATURAL GAS CO INC | COLLBRAN | MESA | CO |  | 325 |  | 1545 | 1986-04-21 | 2 | NO |  |  |  | Null | NO | LEAK | 0 | 1 | 3 | 6000 | 5678.937 | 12371.7005 | YES | 2 | 30 |  | 19860421 | 250 | 720 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: GATHERING SYSTEM; PRTFL: FITTING; PRTFO: 4" ORIFACE METER RUN; MLKD: NO DATA; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 0; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: WILLARD CLAPPER - SAFETY DIR; PHONE: 3039458617; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | CHANGING ORIFACE IN A "DANIELS ORIFACE FITTIN" GAS ESCAPED AND SOME IGNITION, POSSIBLE SPARK FROM STATIC ELECTRICITY FROM STEEL TOOLS OR CLOTHING UNABLE TO DETERMINE EXACTLY. VERY LITTLE EXPLOSION - FLASH BURN UNDER PRESSURE PROBLEM.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19860105 |  | 13750 | NORTHERN NATURAL GAS CO |  | STAFFORD | KS |  | 14.065 | 115+00 | 550 | 1986-04-11 | 1 | NO |  |  |  | Null | NO | RUPTURE | 75 | 0 | 0 | 150000 | 141973.4243 | 309292.5121 | Null | 1 | 10 |  | 19860411 | 760 | 800 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | WELD | LONGITUDINAL SEAM | STEEL |  | PIPELINE |  | 1951 | 26 | 0.28 | API 5LX | 52000 | ELECTRIC FLASH |  | A O SMITH | 1951 | UNDER GROUND |  | T N VIK - TECH SERV | 4026334812 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1956 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19860106 |  | 10030 | KN ENERGY INC (KANSAS NEBRASKA NATURAL GAS CO INC) |  | PHILLIPS | KS | 67647 |  | 433+70 | 1500 | 1986-04-24 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 45 |  |  | 280 | 480 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1961; NMDIA: 2.38; THK: 0.15; SPEC: API 5L; SMYS: 25000; SEAM: CW; MANU: REPUBLIC PIPE; MANYR: 1961; LOCLK: UNDER GROUND; PNAME: A T MCMASTER - DIR - P/L; PHONE: 4024622141; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PERMANENT LINE MARKER; STAT: NO; CTEST: Null | 2 3/8" BURIED LINE WAS DAMAGED BY J B FIELD, HIRED MAN FOR NELSON FARMS, LONG ISLAND, KANSAS, WHILE CHISELING GROUND. NO PRIOR NOTIFICATION TO K N THAT WORK WAS GOING TO BE DONE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19860107 |  | 20230 | UNITED GAS PIPELINE CO | CHATHAM | JACKSON | LA | 71226 | 406.53 | 21465+ | 2350 | 1986-04-17 | 1 | NO |  |  |  | Null | NO | RUPTURE | 31 | 0 | 0 | 431224 | 408148.9862 | 889162.3616 | Null | 1 | 6 |  | 19860418 | 740 | 936 | BY TEST | 1207 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1952; NMDIA: 30; THK: 0.38; SPEC: API 5LX; SMYS: 52000; MANU: A O SMITH; MANYR: 1952; LOCLK: UNDER GROUND; PNAME: WAYNE STGERMAIN - PIPELINE SAFETY ANALYST; PHONE: 7132295772; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: MATERIAL; CTEST: YES; TESTD: 19800923; MED: WATER; TMPS: 8; LKPS: 1207 | WILL BE FILLED IN AFTER METALURGICAL INVESTIGATION IS COMPLETE; ON SUPPLEMENTAL
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19860108 |  | 22476 | WESTERN KENTUCKY GAS CO | CROFTON | CHRISTIAN | KY |  |  | 38+230 | 1635 | 1986-05-06 | 2 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 25 |  | 19860506 | 160 | 410 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1931; NMDIA: 10; THK: 0.22; SMYS: 0; MANYR: 1930; LOCLK: UNDER GROUND; PNAME: WILLIAM R WOOD - MGR TRANS STORAGE; PHONE: 5026858000; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: STANDARD MARKER POST; STAT: NO; CTEST: Null | DOZER OPERATOR HIT LINE WHILE MAKING A DRAINAGE WATERWAY ACROSS FARM LAND.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19860112 |  | 18484 | SOUTHERN CALIFORNIA GAS CO | WHITEWATER | RIVERSIDE | CA | 92282 | 126.4 |  | 1817 | 1986-04-23 | 1 | NO |  |  |  | Null | YES | OTHER | 0 | 0 | 0 | 132260 | 125182.7007 | 272713.5177 | Null | 2 | 22 |  | 19860423 | 530 | 826 | BY TEST | 1428 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: OTHER; PRTFO: RELIEF VALVES; MLKD: NO DATA; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 0; NMDIA: 0; THK: 0; SMYS: 0; VALVE: MODEL 472-AC; MANU: FISHER; MANYR: 0; LOCLK: UNDER PAVEMENT; PNAME: L J FAST - MGR OF TRANSMISSION; PHONE: 0000000000; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | TWO FISHER MODEL 472-AC 6" RELIEF VALVES AT WHITEWATER STATION "FAILED" IN THE OPEN POSITION WHEN COMPANY PERSONNEL MISTAKENLY CLOSED A 2" CONTROL VALVE DURINGA PIGGING OPERATION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19860114 |  | 13120 | NATURAL GAS PIPELINE CO OF AMERICA | SAYRE | BECKHAM | OK | 73662 |  | 37+15 | 120 | 1986-03-31 | 1 | NO |  |  |  | Null | NO | RUPTURE | 97 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 0 |  |  | 827 | 945 | BY TEST | 1450 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1973 | 16.75 | 0.25 | 5LX | 52000 |  |  | AMERICAN STEEL | 1973 | UNDER GROUND |  | F R FLEET - MGR CODES & STD | 3126913786 | INTERNALLY | LOCALIZED PITTING |  | OTHER | CO2 | COATED | YES | 1973 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | RUPTURE OCCURED DUE TO INTERNAL CORROSION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19860115 |  | 1472 | BLACK MARLIN PIPELINE CO | HOUSTON |  | TX | 77001 |  |  | 1030 | 1986-05-31 |  | YES |  | 171 |  | YES | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19860531 | 1150 | 1440 | BY TEST | 2175 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | FITTING | FLANGE | STEEL |  | PIPELINE |  | 1984 | 6 | 0.43 | API 5L | 52000 | SEAMLESS |  |  | 0 | UNDER WATER |  | TERRANCE W. DOYLE | 7139405526 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION | 6" ANSI #900 FLANGE | YES | 19841021 | WATER |  | 24 | 1150
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19860118 |  | 20230 | UNITED GAS PIPELINE CO | CARTHAGE | PANOLA | TX | 76533 |  | 14+90 | 245 | 1986-05-31 | 2 | NO |  |  | TX | Null | NO | RUPTURE | 22 | 0 | 0 | 250000 | 236622.3739 | 515487.5202 | Null | 1 | 0 |  | 19860531 | 750 | 864 | BY TEST | 1080 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | COMPRESSOR STATION |  | 1945 | 18 | 0.34 |  | 50000 | FLASH WELD |  | A. O. SMITH | 1945 | UNDER GROUND |  | WAYNE ST. GERMAIN | 7132295772 | INTERNALLY | LOCALIZED PITTING |  | OTHER | C02 & WATER | COATED | YES | 1954 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19860123 |  | 405 | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | EUGENE ISLAND |  | LA |  |  |  | 1200 | 1986-05-28 |  | YES | E.I. | 40 |  | YES | NO | LEAK | 0 | 0 | 0 | 100000 | 94648.9495 | 206195.0081 | Null | 0 | 0 |  | 19860529 | 750 | 1300 | BY TEST | 1800 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | LONGITUDINAL SEAM | STEEL |  | PIPELINE |  | 1965 | 20 | 0.41 | API 5LX | 52000 | DOUBLE SUBMERGE |  | US STEEL | 1965 | UNDER WATER |  | ROBERT J. LECZNAR, MANAGER | 3134962456 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL |  | YES | 19651203 | WATER |  | 24 | 1800 | LEAK LOCATED AT LONGITUDINAL SEAM. SEAM LOCATED NEAR TOP OF PIPE AT THE 10:30 POSITION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19860124 |  | 4280 | EL PASO NATURAL GAS CO | PHOENIX | MARICOPA | AZ | 85044 | 22+4619 | 1207+2 | 1520 | 1986-04-30 | 2 | NO |  |  | AZ | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 4 | 0 |  | 19860430 | 548 | 650 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1950; NMDIA: 16; THK: 0.25; SMYS: 35000; MANU: JONES & LAUGHLIN; MANYR: 1949; LOCLK: UNDER GROUND; PNAME: W. W. THOMPSON, PHOENIX AREA SUPT; PHONE: 6028394286; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19860319; MARK: YES; MRKTP: YELLOW PAINT; STAT: YES; CTEST: Null | BLUESTAKE REQUIRES UPDATE OF MARKINGS IF OVER 10 DAYS AND NO CONSTRUCTION ACTIVITY ON PAVED AREAS AND 5 DAYS ON DIRT SURFACES.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19860126 |  | 13845 | NORTHWEST PIPELINE CORP | RANGELY | GARFIELD | CO |  | 245.63 | 12969 | 754 | 1986-05-11 | 1 | NO |  |  | CO | Null | NO | LEAK | 0 | 0 | 0 | 47200 | 44674.3042 | 97324.0438 | YES | 0 | 30 |  | 19860511 | 600 | 809 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: GIRTH; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1955; NMDIA: 26; THK: 0.28; SPEC: API5LX X52; SMYS: 1731; SEAM: DSAW; MANU: CONSOLIDATED WEST; MANYR: 1955; LOCLK: UNDER GROUND; PNAME: M. B. ANDERSON, COMPLIANCE SPECIALIST; PHONE: 8015846908; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19860127 |  | 18608 | STANDARD PACIFIC GAS LINE INC | SAN PABLO | CONTRA COSTA | CA | 94806 | 197.72 | 10424 | 1330 | 1986-05-09 | 3 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 5 |  | 19860509 | 239 | 250 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1960; NMDIA: 22; THK: 0.31; SPEC: A. O. SMITH; SMYS: 33000; SEAM: SSAW; MANU: A. O. SMITH; MANYR: 1930; LOCLK: UNDER GROUND; PNAME: DAVE D. CRAIG, SR. GAS ENGR; PHONE: 4159437986; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PAINT, STAKES; STAT: YES; CTEST: Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19860128 |  | 13750 | NORTHERN NATURAL GAS CO | HARRISON | HARRISON | IA | 51546 | 25780 |  | 1015 | 1986-05-07 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 100000 | 94648.9495 | 206195.0081 | Null | 0 | 0 |  | 19860528 | 418 | 500 | NO DATA | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1961; NMDIA: 6; THK: 0.19; SPEC: API 5L; SMYS: 35000; SEAM: ELECTRIC WELD; MANU: VALMONT INDUSTRIES; MANYR: 1960; LOCLK: UNDER GROUND; PNAME: T. N. VIK. TECH. SERVICES; PHONE: 4026334812; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: CONSTRUCTION; CTEST: NO; MED: NO DATA; TMPS: 0; LKPS: 0
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19860130 |  | 20245 | UNITED TEXAS TRANSMISSION CO | GOODRICH | POLK | TX | 77335 | 5.18 | 273+65 | 711 | 1986-04-08 | 1 | NO |  |  |  | Null | NO | RUPTURE | 25 | 0 | 0 | 63687 | 60279.0765 | 131319.4148 | Null | 3 | 0 |  | 19860408 | 375 | 415 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: MECHANICAL JOINT; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1928; NMDIA: 18; THK: 0; SPEC: STYLE 38; SMYS: 0; MANU: DRESSER; MANYR: 1928; LOCLK: UNDER GROUND; PNAME: RONALD WELLS, COORDINATOR; PHONE: 7132295737; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19860136 |  | 19570 | TRANSCO GAS PIPELINE CORP | CONYERS | ROCKDALE | GA |  | 1058.88 | 3873 | 1730 | 1986-06-09 | 2 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 150000 | 141973.4243 | 309292.5121 | Null | 0 | 40 |  | 19860610 | 20 | 800 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: .25" STEEL CONTOL LINE; MLKD: STEEL; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1962; NMDIA: 0.25; THK: 0.04; SPEC: ASTM-A269; SMYS: 25000; SEAM: SEAMLESS; MANU: GREENVILLE TUBE CORP; MANYR: 1985; LOCLK: ABOVE GROUND; PNAME: B. R. LANDES, SR., COMPLIANCE ANALYST; PHONE: 7134392001; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19860139 |  | 2384 | NORTHWEST CENTRAL PIPELINE CORP | PLATTE CITY | PLATTE | MO | 64098 |  | 72+50 | 1120 | 1986-06-17 | 1 | NO |  |  | MO | NO | NO | OTHER | 0 | 0 | 0 | 30000 | 28394.6849 | 61858.5024 | YES | 1 | 45 |  | 19860617 | 410 | 465 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1931; NMDIA: 4.5; THK: 0.14; SMYS: 35000; MANYR: 0; LOCLK: UNDER GROUND; PNAME: WARREN A ETHERIDGE - COOR , REG COMP; PHONE: 9185884427; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19860326; MARK: YES; MRKTP: VENT MARKERS; STAT: Null; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19860143 |  | 10030 | KN ENERGY INC (KANSAS NEBRASKA NATURAL GAS CO INC) | DAWSON | DAWSON | NE | 68901 |  | 2025 | 1312 | 1986-06-03 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 50 |  | 19860603 | 720 | 500 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: LONGITUDINAL; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1947; NMDIA: 8.63; THK: 0.25; SMYS: 24000; SEAM: LAP WELD; MANYR: 0; LOCLK: UNDER GROUND; PNAME: A.T. MCMASTER, DIRECTOR/PIPELINE; PHONE: 4024622141; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19860144 |  | 10030 | KN ENERGY INC (KANSAS NEBRASKA NATURAL GAS CO INC) | MEADOW GROVE | MADISON | NE |  |  | 658+93 | 600 | 1986-07-04 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 30 |  | 19860707 | 775 | 800 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: GIRTH; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 0; NMDIA: 1.25; THK: 0.14; SPEC: A-25; SMYS: 25000; SEAM: WELDED; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: A. T. MCMASTER, DIRECTOR/PIPELINE OPERATIONS; PHONE: 4024622141; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PIPELINE MARKER 20'; STAT: NO; CTEST: Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19860150 |  | 18516 | SOUTHERN NATURAL GAS CO | PRATTVILLE | AUTAUGA | AL | 36067 | 213.610 |  | 242 | 1986-07-12 | 2 | NO |  |  |  | Null | NO | RUPTURE | 3 | 0 | 0 | 1300000 | 1230436.344 | 2680535.105 | Null | 8 | 23 |  | 19860712 | 920 | 1200 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1958; NMDIA: 8; THK: 0.5; SPEC: API 5L; SMYS: 35000; SEAM: SEAMLESS; VALVE: RELIANCE REG; MANU: NATIONAL; MANYR: 1958; LOCLK: ABOVE GROUND; PNAME: CHARLES S. FARRELL, SUP. PIPELINE CODE & SAFETY REGUL; PHONE: 2053257554; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19860151 |  | 3 | ACADIAN GAS PIPELINE SYSTEM |  | ASSUMPTION | LA |  |  |  | 825 | 1986-08-05 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 35 |  | 19860805 | 440 | 650 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1940; NMDIA: 7; THK: 0.19; SPEC: API 5LX; SMYS: 52000; SEAM: ERW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: J. P. SCHWARZ, ASST. MANAGER OF OPERATIONS; PHONE: 5044462791; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: WARNING SIGNS; STAT: YES; CTEST: Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19860153 |  | 12462 | MID - LOUISIANA GAS CO | NATCHEZ | ADAMS | MS | 39210 | #1 STATION | MP 94+ | 30 | 1986-07-18 | 3 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 130000 | 123043.6344 | 268053.5105 | Null | 2 | 45 |  | 19860718 | 160 | 350 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: MEASUREMENT STATION; MLKD: OTHER; MLKDO: MEASUREMENT STATION BLDG; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 0; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: THOMAS E. TUCKER, MANAGER, PIPELINES; PHONE: 3184458225; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PIPELINE SIGNS & BARRICAD; STAT: Null; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19860158 |  | 3 | ACADIAN GAS PIPELINE SYSTEM |  | ASSUMPTION | LA |  |  |  | 640 | 1986-07-09 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 25 |  | 19860709 | 490 | 650 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1940; NMDIA: 7; THK: 0.19; SPEC: API 5LX; SMYS: 52000; SEAM: ERW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: J P SCHARZ - ASST MGR OF OPER; PHONE: 5044462791; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: WARNING SIGNS; STAT: YES; CTEST: Null
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19860159 |  | 25165 | ENSERCH GAS TRANSMISSION CO | RAYWOOD | LIBERTY | TX |  | 0 | 0+50 | 1128 | 1986-06-24 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 1 | 0 | 311590 | 294916.6619 | 642483.0257 | Null | 2 | 30 |  | 19860624 | 711 | 1200 | BY TEST | 1646 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1981; NMDIA: 16; THK: 0; SPEC: API 5L X; SMYS: 56000; SEAM: ELEC WL SMLS; MANYR: 0; LOCLK: UNDER GROUND; PNAME: R G WALKER - SUPT I; PHONE: 7136722551; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PIPELINE WARNING SIGNS; STAT: NO; CTEST: Null | A VACUUM TRUCK HIT OUR LINE. TRHE IMPACT BROKE THE WELD SADDLE OFF OF THE 16' LINE CAUSING THE PIPE TO RUPTURE AND THE GAS WAS IGNITED BY THE TRUCK ENGINE. THERESULTING FIRE KILLED THE DRIVER AND COMPLETELY DESTROYED ALL EGT MEASUREMENT AND ODORIZATION FACILITIES AT THIS LOCATION.! **** LONE STAR GAS SUBMITTED REPORT FOR SAME INCIDENT. SEE 860152
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19860160 |  | 2384 | NORTHWEST CENTRAL PIPELINE CORP | OKLAHOMA CITY | CLEVELAND | OK |  | 50 | 1824+5 | 1935 | 1986-07-06 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 1 | 0 | 0 | 0 | 0 | Null | 4 | 0 |  | 19860707 | 385 | 656 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1956; NMDIA: 16; THK: 0.31; SPEC: GR B 35; SMYS: 35000; SEAM: SLMS; MANYR: 0; LOCLK: UNDER GROUND; PNAME: WARREN A ETHERIDGE; PHONE: 9185884427; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PIPELINE MARKERS; STAT: YES; CTEST: Null
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19860164 |  | 4280 | EL PASO NATURAL GAS CO | WILLIAMS | COCONINO | AZ |  | 276+ |  | 835 | 1986-08-12 | 2 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 3 | 0 | 0 | 0 | Null | 0 | 5 |  | 19860812 | 22 | 845 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: COMPRESSOR ENGINE; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1953; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: RICHARD FAVILA - STANDARDS ENG; PHONE: 9155412062; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: MATERIAL; CAULO: CRANKCASE; CTEST: NO; MED: NO DATA; TMPS: 0; LKPS: 0 | ON AUGUST 12, 1986, AT 8:35 AM, A CRANKCASE EXPLOSION OCCURED AT WILLIAMS COMPRESSOR STATION THAT RESULTED IN THE INJURY OF THREE (3) EPNG EMPLOYEES. SUBSEQUENT INVESTIGATION REVEALED A FRACTURE OF THE #2 BEARING CAP AND THE RESULTANT MELTING OF THE BEARING BABBITT INTO THE CRANKCASE OIL AS THE CAUSE OF THE EXPLOSION.THE INVESTIGATION COMMITTEE HAS CONCLUDED THAT THE CAUSE SHALL BE CLASSIFIED ASA MECHANICAL FAILURE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19860166 |  | 2616 | COLUMBIA GAS TRANSMISSION CORP | SENECA | PENDLETON | WV | 26884 |  | 6529+5 | 1555 | 1986-08-04 | 1 | NO |  |  |  | Null | NO | RUPTURE | 60 | 0 | 0 | 135000 | 127776.0819 | 278363.2609 | YES | 0 | 45 |  | 19860804 | 794 | 800 | BY TEST | 880 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1956 | 26 | 0.28 | API 5LX | 52000 | DSA |  | NATIONAL TUBE | 1956 | UNDER GROUND |  | A S BECKETT - SUPV ENG | 3043572797 | EXTERNALLY | LOCALIZED PITTING |  | OTHER | SEE COMMENTS | COATED | YES | 1957 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | PIPE SECTION HAS BEEN SUBMITTED FOR METALLURGICAL ANALYSIS TO ASCERTAIN CAUSE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19860170 |  | 13120 | NATURAL GAS PIPELINE CO OF AMERICA |  | SAN PATRICIO | TX |  | 75 | 3980+2 | 1624 | 1986-07-16 | 1 | NO |  |  |  | Null | NO | RUPTURE | 25.75 | 0 | 0 | 103226 | 97702.3247 | 212846.859 | Null | 1 | 30 |  | 19860716 | 705 | 900 | BY TEST | 1215 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1965; NMDIA: 30; THK: 3.13; SPEC: 5L; SMYS: 60000; MANU: A O SMITH; MANYR: 0; LOCLK: UNDER GROUND; PNAME: F R FLEET - MGR CODES & STD; PHONE: 3126913786; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: CONSTRUCTION; CTEST: YES; TESTD: 19831206; MED: WATER; TMPS: 8; LKPS: 1215 | 30" MAINLINE RUPTURED AT A 6" COLD TAP.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19860171 |  | 19235 | TEXAS EASTERN GAS PIPELINE CO | FOUKE | MILLER | AR | 71837 | 66.93 | 3533+9 | 740 | 1986-06-27 | 1 | NO |  |  |  | Null | NO | RUPTURE | 46 | 0 | 0 | 531000 | 502585.9221 | 1094895.4929 | Null | 1 | 28 |  | 19860627 | 0 | 830 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1943 | 24 | 0.38 | 5L | 37000 | SEAMLESS |  | NATIONAL | 1942 | UNDER GROUND |  | S R PUGH - SUPV | 7137593090 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | COATED | YES | 1950 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | THE PIPELINE WAS OUT OF NORMAL OPERATING SERVICE AT THE TIME OF THE FAILURE. THE MAINLINE VALVE DOWNSTREAM OF THE POINT OF RUPTURE WAS CLOSED FOR PIPE REPLACEMENT ACTIVITIES IN PROGRESS IN THE DOWNSTREAM VALVE SECTION. THE PIPELINE SEGMENTWHICH FAILED WAS CONNECTED TO THREE LATERALS CONNECTING FOUR WELLS TO THE MAINLINE TO ACCUMULATE ENOUGH GAS FOR A REVERSE FLOW PIGGING OPERATION. NO DIRECT PRESSURE MEASUREMENT EQUIPMENT WAS IN SERVICE ON THE MAINLINE AT THE TIME OF FAILURE, THEREFORE THE EXACT PRESSURE ON THE MAINLINE CANNOT BE DETERMINED. THE SETTING OF THE ONLY RELIEF VALVE ON THE MAIN LINE SEGMENT WAS VERIFIED AT 847 PSIG ON MAY 19, 1986 PRIOR TO THE INCIDENT AND WAS CERTIFIED AFTER THE INCIDENT AT 850 PSIG. THIS RELIEF VALVE DID NOT RELIEVE. TWO OF THE RELIEF VALVES ON THE LATERALSWERE SET AT 848 PSIG AND THE THIRD SET AT 840 PSIG. AFTER THE INCIDENT THE LATERAL RELIEF VALVE SETTINGS WERE CERTIFIED AT 830 PSIG, 848 PSIG, AND 875 PSIG. THE RELIEF VALVES CERTIFIED AT 830 PSIG DID NOT. THE PIPELINE HAD BEEN SHUT-IN FORAPPROXIMATLY 25 HOURS, SO THE PRESSURES IN THE SEGMENT OF PIPELINE WERE AT OR NEAR STEADY STATE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19860174 |  | 405 | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | HIGH ISLAND | EAST ADDITION | TX |  |  |  | 900 | 1986-08-20 |  | YES | H.I. | A-340 |  | YES | NO | LEAK | 0 | 0 | 0 | 50000 | 47324.4748 | 103097.504 | Null | 6 | 0 |  | 19860821 | 1000 | 1440 | BY TEST | 2852 | CORROSION | CORROSION | INTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: 90^ L.R. ELL; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1977; NMDIA: 12; THK: 0.5; SPEC: API 5LX Y42; SMYS: 42000; MANYR: 0; LOCLK: UNDER WATER; PNAME: ROBERT J LECZNER - MGR REGS & PROCEDURES; PHONE: 3134962452; LOC: INTERNALLY; ADESC: NO DATA; CAUCR: NO DATA; COAT: COATED; PROT: YES; CPYR: 1978; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19860175 |  | 13120 | NATURAL GAS PIPELINE CO OF AMERICA | LAKE CALCASIEU | CAMERON | LA |  | 132 | 6959+5 | 730 | 1986-08-05 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 50000 | 47324.4748 | 103097.504 | Null | 0 | 0 |  | 19860812 | 1060 | 1100 | BY TEST | 1451 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1967; NMDIA: 30; THK: 0.36; SPEC: 5LX65; SMYS: 65000; MANYR: 0; LOCLK: UNDER WATER; PNAME: F. ROY FLEET, MANAGER CODES & STANDARDS; PHONE: 3126913786; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: ROW MARKERS ON SHORE; STAT: YES; CTEST: Null | PIPELINE WAS GOUGED AND DENTED BY THIRD PARTY EQUIPMENT WHICH CAUSED A CRACK THAT LEAKED.ON AUGUST 6, 1986 AT 0730 HOURS, BUBBLING WAS REPORTED ON THE RIGHT OF WAY OF NATURAL GAS PIPELINE COMPANY OF AMERICA'S #1-30" LOUISIANA MAINLINE. THE INCIDENTSITE IS IN THE SALTWATER BARRIER CANAL ON THE EAST SIDE OF CALCASIEU LAKE, CAMERON PARISH, LA. THE LEAK RESULTED FROM A CRACK BY A GOUGE AND DENT BY AN UNKNOWNTHIRD PARTY. NO INJURIES OR FIRE RESULTED FROM THE LEAK. THE AFFECTED SECTION OF PIPE WAS REMOVED AND REPLACED, AND THE PIPELINE WAS RETURNED TO SERVICE. THE INCIDENT REPORT FORM IS ATTACHED.
2021-02-26 10:36 | YES | YES | GG (Gas Gathering) | 19860176 |  | 4280 | EL PASO NATURAL GAS CO | FARMINGTON | SAN JUAN | NM | 87401 | .42 | 22+41 | 2205 | 1986-08-28 | 1 | NO |  |  | NM | Null | YES | LEAK | 0 | 0 | 2 | 0 | 0 | 0 | Null | 13 | 5 |  | 19860828 | 220 | 584 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: GATHERING SYSTEM; PRTFL: NO DATA; MLKD: STEEL; PRTSY: OTHER; PRTSO: PIGGING LIQUID RESERVOIR; PRTYR: 1966; NMDIA: 34; THK: 0.41; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: RICHARD FAVILA, STANDARDS ENGR.; PHONE: 9155412062; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | ON AUGUST 28, 1986 AT 10:05 P.M. DURING NORMAL PIGGING OPERATIONS, AN EXPLOSIONAND FIRE OCCURRED AT THE PIGGING FACILITY ON THE CHACO-LINDRITH FIELD LINES WHICH RESULTED IN INJURY TO TWO(2) EPNG EMPLOYEES. SUBSEQUENT INVESTIGATION REVEALED THAT VAPORS WHICH HAD ACCUMULATED IN A LOW AREA FROM AN OPEN PIT RECEIVING THEPIGGING LIQUIDS OR POSSIBLY FROM A LEAK IN THE GAGE GLASS AREA WERE APPARENTLY IGNITED BY A VEHICLE WHICH WAS BEING DRIVEN BY ONE OF THE INJURED INDIVIDUALS. THE OTHER INJURED INDIVIDUAL WAS OBSERVING THE LIQUID LEVEL IN THE GAGE GLASS ANDWAS IN RADIO CONTACT WITH THE PERSON DRIVING THE VEHICLE WHEN THE EXPLOSION ANDFIRE OCCURRED.
2021-02-26 10:36 | YES | YES | GG (Gas Gathering) | 19860177 |  | 4280 | EL PASO NATURAL GAS CO | FARMINGTON | SAN JUAN | NM | 87401 | .42 | 22+41 | 1600 | 1986-09-01 | 1 | NO |  |  | NM | Null | YES | LEAK | 0 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 5 |  | 19860828 | 0 | 0 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: GATHERING SYSTEM; PRTFL: NO DATA; MLKD: STEEL; PRTSY: OTHER; PRTSO: PIGGING LIQUID RESERVOIR; PRTYR: 1966; NMDIA: 34; THK: 0.41; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: RICHARD FAVILA, STANDARDS ENGR.; PHONE: 9155412062; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | ON SEPTEMBER 1, 1986 AT 4:00 P.M. AN EXPLOSION OCCURRED AT THE PIGGING FACILITYON THE CHACO-LINDRITH FIELD LINE WHICH RESULTED IN INJURY TO THREE (3) EPNG EMPLOYEES; HOWEVER, ONLY ONE REQUIRED HOSPITALIZATION. THE INCIDENT OCCURRED WHILE A CREW WAS PREPARING TO REPLACE THE SECTION OF 34-INCH PIPE RESERVOIR WHICH HAD BEEN DAMAGED IN THE EXPLOSION AND FIRE WHICH HAD OCCURRED ON AUGUST 28, 1986. ASA WELDER STARTED TO TACK WELD THE PIPE, THE EXPLOSION OCURRED INJURING THE EMPLOYEES.
2021-02-26 10:36 | YES | YES | GG (Gas Gathering) | 19860181 |  | 15493 | PHILLIPS PETROLEUM CO |  | CONVERSE | WY |  |  |  | 830 | 1986-09-09 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 1 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19860909 | 680 | 1424 | BY TEST | 2166 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: GATHERING SYSTEM; PRTFL: OTHER; PRTFO: ENCLOSURE HUB; MLKD: STEEL; PRTSY: OTHER; PRTSO: SPHERE RECEIVER; PRTYR: 1972; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: R D GUNLIKSON - ASSO PROCESS ENGR; PHONE: 3072373791; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | AVAILABLE MEANS OF RELEASING PRESSURE FROM SPHERE RECEIVER NOT USED. RECEIVER UNDER PRESSURE WHEN EMPLOYEE TRIED TO REMOVE CAP.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19860187 |  | 2748 | CONSUMERS POWER CO |  | KALKASKA | MI | 49739 |  | 506+13 | 1150 | 1986-09-10 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 6 | 25 |  | 19860910 | 850 | 960 | BY TEST | 1588 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1971; NMDIA: 12; THK: 0.25; SPEC: API5LX; SMYS: 42000; SEAM: ELEC RESIST WEL; MANU: YOUNGSTOWN SHEET&TUBE; MANYR: 1971; LOCLK: UNDER GROUND; PNAME: W J DEVRIES - GAS OPER SUPVR; PHONE: 5177881201; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: LIGHTNING; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | LIGHTNING STRUCK A TREE 36 FEET AWAY FROM THE 12" PIPELINE AND TRAVELED TO THE PIPELINE VIA THE TREE'S ROOTS. THIS RESULTED IN A PINHOLE LEAK ON THE TOP OF THE
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19860198 |  | 2714 | CONSOLIDATED GAS TRANSMISSION CORP | ELK CITY | LEWIS | WV | 26452 |  | 102' | 1130 | 1986-10-01 | 1 | NO |  |  | WV | Null | NO | RUPTURE | 0 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 0 |  | 19861001 | 950 | 959 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: DRIP BARREL; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1954; NMDIA: 10; THK: 0.03; SPEC: UNKNOWN; SMYS: 0; SEAM: RESISTANCE WELD; MANU: UNKNOWN; MANYR: 1954; LOCLK: UNDER GROUND; PNAME: JACK L. ADAMS, AMDINISTRATOR ENGR. CONST.; PHONE: 3046238410; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | BOTTOM BARRELL OF STEP LADDER DRIP (12" SECTION) SEPARATED IN SEAM.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19860200 |  | 2128 | CASCADE NATURAL GAS CORP | SKAGIT |  | WA |  | V-2 | 732+48 | 1400 | 1986-10-28 | 1 | NO |  |  | WA | NO | NO | NO DATA | 0 | 0 | 0 | 0 | 0 | 0 | Null | 1 | 5 |  | 19861028 | 350 | 400 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1957; NMDIA: 8.62; THK: 0.19; SPEC: SPI5LX-42; SMYS: 42000; SEAM: ERW; MANU: UNKNOWN; MANYR: 1956; LOCLK: UNDER GROUND; PNAME: RALPH E. BOYD, CHIEF ENGINEER; PHONE: 2066243900; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; STAT: YES; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19860205 |  | 18484 | SOUTHERN CALIFORNIA GAS CO | NEWBERRY SPRINGS | SAN BERNARDINO | CA | 92365 | NEWBERRY COMPR. STA. |  | 1305 | 1986-10-06 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 50000 | 47324.4748 | 103097.504 | YES | 0 | 30 |  | 19861006 | 11 | 0 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: DOMESTIC APPLIANCES; MLKD: NO DATA; PRTSY: OTHER; PRTSO: DOMESTIC APPLIANCES; PRTYR: 1967; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: L.J. FAST, MANAGER OF TRANSMISSION; PHONE: 2136892345; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | REGULATOR MALFUNCTION
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19860206 |  | 22365 | WESTAR TRANSMISSION CO |  | GRAY | TX |  |  | 1774+2 | 600 | 1986-10-10 | 1 | NO |  |  |  | Null | NO | RUPTURE | 24 | 0 | 0 | 78000 | 73826.1806 | 160832.1063 | Null | 2 | 0 |  | 19861010 | 960 | 1235 | BY TEST | 1449 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1970 | 12.75 | 0.25 | AP5LX46 | 1800 | E.R.W. | STEEL ANSI 600 | U.S. STEEL | 1970 | UNDER GROUND |  | H.D. DYSON/SUPERINTENDENT | 0003710505 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL |  | YES | 19700805 | WATER |  | 24 | 1449 | CRACK IN SEAM OF PIPE OPENED CAUSING RUPTURE. THIS FAILURE WAS IN A DRAW APPROXIMATELY 12' DEEP AND 80' WIDE. BAD SEAM IN JOINT OF PIPE. NUMEROUS COROSION PITSUNRELATED TO PIPE FAILURE WERE NOTED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19860208 |  | 602 | ARKLA ENERGY RESOURCES | CURTIS | CLARK | AR | 71728 | 132 | 6982+7 | 1140 | 1986-11-02 | 1 | NO |  |  |  | Null | NO | RUPTURE | 260 | 0 | 0 | 185988 | 176035.6883 | 383497.9716 | Null | 0 | 45 |  |  | 650 | 800 | BY TEST | 1150 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; PRTFO: 45 DEGREES E11; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1953; NMDIA: 20; THK: 0.25; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: RAYMOND D. GERMANY, MANAGER ENVIRONMENTAL HLTH & SAFETY; PHONE: 3182262708; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: CONSTRUCTION; CAULO: 45 DEGREES E11 DAMAGED BY PIG; CTEST: YES; TESTD: 19860609; MED: WATER; TMPS: 8; LKPS: 1141 | A SECTION OF 20" PIPE ON AN OVERHEAD CROSSING BLEW OUT, PIPE HAD APPARENTLY BEEN DAMAGED BY PIG IN 45 DEGREE E11.
2021-02-26 10:36 | YES | YES |  | 19860210 |  | 18180 | SESCO PRODUCTION CO | HENDERSON | RUSK | TX |  | MOCKINGBIRD/DAVID ST |  | 800 | 1986-10-29 | 3 | NO |  |  | TX | Null | NO | RUPTURE | 0.5 | 0 | 4 | 500 | 473.2447 | 1030.975 | Null | 1 | 0 |  | 19861029 | 400 | 800 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: NO DATA; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1966; NMDIA: 4; THK: 0.13; SMYS: 0; VALVE: PLUG & GATE; MANYR: 0; LOCLK: UNDER GROUND; PNAME: GEORGE H. TEMPLE; PHONE: 2147572842; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; MARK: YES; STAT: YES; CTEST: Null | CONSTRUCTION CREW (CHAPARRAL GENERAL CONSTRUCTION CO., INC.) RUPTURED PIPELINE WITH FRONT-END LOADER WHILE ESCAVATING FOR STREET CONSTRUCTION.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19860211 |  | 13120 | NATURAL GAS PIPELINE CO OF AMERICA | PONTIAC | LIVINGSTON | IL | 60544 |  | 61049+ | 935 | 1986-10-30 | 1 | NO |  |  |  | Null | Null | LEAK | 0 | 0 | 0 | 62300 | 58966.2956 | 128459.49 | Null | 0 | 0 |  |  | 0 | 900 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | LONGITUDINAL | STEEL |  | PIPELINE |  | 1951 | 30 | 0.34 | 5LX | 52000 | ELECTRIC WELD |  | A.O. SMITH | 1951 | UNDER GROUND |  | F. ROY FLEET, MANAGER, CODES & STANDARDS | 3126913786 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION |  | YES | 19510403 | GAS |  | 0 | 948 | LEAK CAUSED BY INCOMPLETE FUSION OF THE LONGITUDINAL SEAM.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19860213 |  | 19235 | TEXAS EASTERN GAS PIPELINE CO | LAMBERTVILLE | HUNTERDON | NJ | 08530 | 260.63 | 13761+ | 1325 | 1986-10-31 | 1 | NO |  |  | NJ | Null | NO | OTHER | 0 | 0 | 0 | 50000 | 47324.4748 | 103097.504 | Null | 0 | 45 |  | 19861031 | 50 | 1050 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; MLKD: OTHER; PRTSY: PIPELINE; PRTYR: 1965; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: R.E. THOMURE, MANAGER, CODES & REGULATORY; PHONE: 7137595353; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | ON OCTOBER 31, 1986 AT 9:34 A.M. E.S.T. A SCHEDULED ROUTINE BLOW-DOWN OF TEXAS EASTERN'S 36" LINE NO. 27 WAS INITIATED JUST EAST OF THE DELAWARE RIVER HUNTERDON COUNTY, NEW JERSEY. THE PRESSURE ON LINE NO. 27 WAS 850 PSIG AT THE TIME THE BLOW-DOWN WAS STARTED THROUGH THE 10" X 8" BLOW-DOWN VALVE. AT 1:25P.M. E.S.T. AFTER THE PRESSURE HAD BEEN REDUCED TO APPROX. 50 PSIG, THE ESCAPING GAS IGNITED AND BURNED TWO HIGH VOLTAGE POWER LINES. THE CAUSE OF THE IGNITION HAS NOT BEEN DETERMINED AT THIS TIME. THE POWER LINES WERE LOCATED APPROX. 48' NORTH OF THE BLOW-DOWN STACK. THIS INCIDENT DID NOT RESULT IN ANY POWER OUTAGE.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19860214 |  | 15105 | PANHANDLE EASTERN PIPELINE CO | STINNETT | HUTCHINSON | TX | 79083 |  |  | 1337 | 1986-11-13 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 1 | 0 | 750000 | 709867.1216 | 1546462.5606 | Null | 4 | 53 |  | 19861113 | 0 | 0 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: NO DATA; MLKD: NO DATA; PRTSY: NO DATA; PRTSO: LIQUID SEPARATION FACILIT; PRTYR: 1982; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: A.R. GOOD, MANAGER; PHONE: 8169682922; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | A CONTRACTOR'S EMPLOYEE WAS STEAMING A FROZEN DRAIN LINE FROM A NATURAL GAS CONDENSATE STORAGE TANK, LIQUID WAS RELEASED THROUGH AN OPEN VALVE, AND VAPOR FROM THE LIQUID WAS IGNITED BY THE OPEN FLAME ON THE CONTRACTOR'S STEAMER TRUCK.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19860218 |  | 19160 | TENNESSEE GAS PIPELINE CO | RICHMOND | MADISON | KY | 40475 | 103-1+15.08 | 268+23 | 1700 | 1986-11-05 | 3 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19861105 | 487 | 0 | NO DATA | 1517 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1971; NMDIA: 0.24; THK: 0.38; SPEC: 5LX; SMYS: 52000; SEAM: DSA; MANU: REPUBLIC; MANYR: 1969; LOCLK: UNDER GROUND; PNAME: R. L. DEAN, MANAGER, CODES & STANDARDS; PHONE: 7137572858; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | A SMALL 11/16" TAPERED DRILLED HOLE WAS PARTIALLY DRILLED INTO MAIN BODY OF PIPE AT THE 7 O'CLOCK POSITION. LEAK DID NOT START UNTIL AFTER HYDROSTATICALLY TESTED ON 9/30/86.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870001 |  | 14210 | OKLAHOMA NATURAL GAS CO | MUSKOGEE | MUSKOGEE | OK | 74402 |  |  | 1930 | 1986-12-02 | 2 | NO |  |  | OK | Null | NO | RUPTURE | 5 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 30 |  | 19861202 | 550 | 720 | BY TEST | 1120 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1968; NMDIA: 12; THK: 0.2; SPEC: API-5LX X-42; SMYS: 42000; SEAM: ERW; MANU: LONE STAR STEEL; MANYR: 1968; LOCLK: UNDER PAVEMENT; PNAME: JAMES M. WOOD; PHONE: 9185887600; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | THE LINE THAT FAILED WAS INSTALLED IN JUNE 1986. THIS PROJECT WAS A RELOCATION REQUIRED DUE TO HIGHWAY CONSTRUCTION. THE PIPELINE WAS DESIGNED, INSTALLED, AND TESTED IN ACCORDANCE WITH THE ASME B31.8-1968 EDITION CODE FOR "GAS TRANSMISSIONAND DISTRIBUTION PIPING SYSTEMS." THE LINE PIPE MATERIAL WAS 12 3/4" O.D.,27.20#(0.203"),API-5LX., X-42 ERW MANUFACTURED BY LONE STAR STEEL. THE LINE WAS HYDROSTATICALLY TESTED TO 1100 PSIG FOR FOUR HOURS, WHICH ESTABLISHED AN MAOP OF 720 PSIG IN A CLASS 2 LOCATION. DUE TO THE SUPPLY TO THIS SYSTEM AND NO NEED FOR THE720 PSIG PRESSURE TO SERVE MARKET, THE PIPELINE HAS OPERATED AT 300 TO 350 PSIGSINCE INSTALLATION. THE NEED FOR 50O PSIG MAXIMUM OPERATING PRESSURE ON THIS PIPELINE IS NOW REQUIRED TO SERVE MARKET. SINCE THE LINE HAD NOT OPERATED HIGHER THAN 350 PSIG. IT WAS DECIDED TO GO THROUGH AN UPRATING PROCEDURE. A WRITTEN PLANWAS PREPARED AS PER SUBPART K OF THE D.O.T. RULES. THE PRESSURE IS TO BE INCREASED IN 100 PSIG INCREMENTS TO 750 (500 X 1.5) WITH A FLAME-IONIZATION LEAK SURVEY DURING THE 24-HOUR HOLD PERIOD. THE LINE RUPTURED AT 55O PSIG, WHICH WAS THE SECOND STEP OF THE PRESSURE INCREASES. THE 550 PSIG WAS ATTAINED AT ABOUT 1600 HOURS ON DECEMBER 2, 1986, AND THE LINE FAILED AT 1930 HOURS ON DECEMBER 2, 1986. NO FIRE, NO FATALITIES. AND NO INJURIES RESULTED FROM THE RUPTURE. SERVICE WAS IN
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19870003 |  | 20230 | UNITED GAS PIPELINE CO | FANNIN | RANKIN | MS | 39042 | M.P. 247.55 | 13071+ | 320 | 1986-12-06 | 1 | NO |  |  | MS | Null | NO | RUPTURE | 21 | 0 | 0 | 685000 | 648345.3044 | 1412435.8054 | Null | 0 | 40 |  | 19861206 | 780 | 920 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1962; NMDIA: 30; THK: 0.5; SPEC: API-5LX; SMYS: 52000; SEAM: ERW; MANU: A.O. SMITH; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: W.F. ST.GERMAIN; PHONE: 7132295772; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | THERE IS NO APPARENT CAUSE FOR THE RUPTURE, BUT A METALLURGICAL INVESTIGATION IS UNDERWAY ON SAMPLES OF THE RUPTURED PIPE TO DETERMINE THE CAUSE OF RUPTURE. UNITED HAS TWO 30" LINES CROSSING PELAHATCHIE BAY. A VALVE SITE IS LOCATED ON EACHSIDE OF THE BAY WHERE THE LOOP TERMINATES WITH A CROSSOVER AND VALVE TYING INTOTHE 30" MAIN LINE. THE LOOP LINE, AT HTE NORTH VALVE SITE RUPTURED IN THE BODY OF THE PIPE 2'-11 1/2" FROM THE LONGITUDINAL SEAM AT A POINT 8'-4' SOUTH OF THE CROSSOVER AND VALVE PIPING OUT OF THE TOP OF THE TEE AT THE 30" MAIN LINE TIE-INPOINT.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19870004 |  | 18152 | SEA ROBIN PIPELINE CO | EUGENE ISLAND |  | LA |  | 0 + 15 | X | 2330 | 1986-11-24 |  | YES | OFFSHORE LOUISIANA | 273 |  | YES | Null | OTHER | 0 | 0 | 0 | 90000 | 85184.0546 | 185575.5073 | Null | 7 | 45 |  | 19861125 | 1000 | 1647 | BY TEST | 2153 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: GATHERING SYSTEM; PRTFL: VALVE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1979; NMDIA: 12; THK: 0.5; SPEC: API-5LX; SMYS: 42000; SEAM: SEAMLESS; VALVE: CAMERON BALL V/; MANU: ARMCO; MANYR: 0; LOCLK: UNDER WATER; PNAME: W.F. ST. GERMAIN; PHONE: 7132295772; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | A SHRIMP BOAT HUNG A NET IN THE LINE, DAMAGING A 2 INCH TAP VALVE.
2021-02-26 10:36 | YES | YES | GG (Gas Gathering) | 19870005 |  | 4280 | EL PASO NATURAL GAS CO |  | BECKHAM | OK |  |  |  | 1310 | 1986-12-06 | 1 | NO |  |  | OK | Null | NO | RUPTURE | 3 | 1 | 0 | 0 | 0 | 0 | Null | 0 | 50 |  | 19861206 | 889 | 1267 | BY TEST | 1521 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1985; NMDIA: 6.63; THK: 0.19; SMYS: 42000; MANU: NEWPORT STEEL; MANYR: 0; LOCLK: UNDER GROUND; PNAME: RICHARD FAVILA; PHONE: 9155412062; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | ON DECEMBER 12, 1986, AT 1:10 P.M. AN EXPLOSION OCCURRED ON THE 6-5/8" O.D. NONJURISDICTIONAL LINE TO APACHE CORP. - PUCKETT WELL #1-16, THAT RESULTED IN THE DEATH OF A BULLDOZER OPERATOR EMPLOYED BY APACHE CORP. THE OPERATOR WAS KILLED WHEN. WHILE MOVING THE BULLDOZER FROM ONE LOCATION TO ANOTHER, THE BULLDOZER SANK IN THE WET SOIL AND STRUCK AND RUPTURED OUR LINE. THE LINE HAD APPROXIMATELY 4 FEET OF COVER. THE FORCE OF THE EXPLOSION THREW THE OPERATOR FROM THE BULLDOZER AND CAUSED HIS DEATH. UNDER THE REGULATIONS ISSUED BY THE DEPARTMENT OF TRANSPORTATION IN THE CODE OF FEDERAL REGULATIONS, TITLE 49, SUBTITLE B, CHAPTER 1, PART 191, EL PASO NATURAL GAS COMPANY SUBMITS THE REPORTS COVERING THE INCIDENT WHICHOCCURRED ON DECEMBER 6, 1986, ON EL PASO NATURAL GAS COMPANY'S LINE TO APACHE CORPORATION'S PUCKETT WELL #1-16 IN EL PASO'S SOUTH ZYBACH GATHERING SYSTEM. EVENTHOUGH THIS FACILITY IS NONJURISTICTIONAL, DUE TO THE DEATH OF A BULLDOZER OPERATOR EMPLOYED BY APACHE CORPORATION, WE TELEPHONICALLY REPORTED THIS INCIDENT TOTHE DEPARTMENT OF TRANSPORTATION.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19870008 |  | 18646 | STINGRAY PIPELINE CO |  |  | LA |  | 1004C-700 |  | 847 | 1986-11-26 |  | YES | WEST CAMERON, OCS | 587-A |  | YES | NO | LEAK | 0 | 0 | 0 | 200000 | 189297.8991 | 412390.0162 | YES | 0 | 0 |  | 19861201 | 1020 | 1250 | BY TEST | 2152 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | NO DATA |  | STEEL |  | PIPELINE |  | 0 | 24 | 0.5 | API-5LX-60 | 60000 | SAW |  | BETHLEHEM STEEL | 1974 | UNDER WATER |  | J. R. LEHMAN | 7136641254 | INTERNALLY | OTHER | X-RAY | OTHER |  | NO DATA | YES | 0 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | NONE KNOWN AT THIS TIME.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19870012 |  | 602 | ARKLA ENERGY RESOURCES | WINSLOW | CRAWFORD | AR | 72959 |  |  | 1245 | 1986-11-10 | 1 | NO |  |  | AR | Null | YES | RUPTURE | 0 | 0 | 0 | 75000 | 70986.7122 | 154646.2561 | Null | 3 | 0 |  | 19861110 | 900 | 100 | BY TEST | 1250 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1968; NMDIA: 20; THK: 0.25; SPEC: X.60; SMYS: 1350; SEAM: DOUBLE SUBMERGE; MANU: KAISER; MANYR: 1967; LOCLK: UNDER GROUND; PNAME: RAYMOND D. GERMANY; PHONE: 3182262708; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870014 |  | 19235 | TEXAS EASTERN GAS PIPELINE CO | LINDEN | MIDDLESEX | NJ | 07036 | 1474.19 |  | 1130 | 1986-12-12 | 2 | NO |  |  | NJ | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 30 |  | 19861213 | 620 | 795 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: 1" ON 26" THREADOLET; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1962; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 1962; LOCLK: OTHER; LOCLO: IN REGULATOR PIT; PNAME: R. E. THOMURE; PHONE: 7137593131; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | A BACKHOE WAS WORKING NEAR A REGULATOR PIT WHEN THE BACKHOE BUCKET STRUCK A BLEED OFF ASSEMBLY CAUSING A 1" THREADED PIPE NIPPLE TO BE STRIPPED FROM A THREAD-O-LET FITTING. ALL PERSONNEL WERE REMOVED FROM THE VICINITY OF THE LEAK AND THE AREA WAS SECURED BY TEXAS EASTERN AND AUTHORITIES. THE AREA WAS SECURED WITHIN 30MINUTES AFTER THE INCIDENT OCCURRED. THE SOURCE OF GAS CONTINUED AND SECURITY OF THE AREA WAS MAINTAINED UNTIL THE LEAK WAS STOPPED. THE PIPELINE WAS BLOWN DOWN AND A PIPE PLUG WAS INSTALLED TO STOP THE LEAK. THIS INCIDENT DID NOT CAUSE ANY PERSONAL INJURIES OR FIRE. VERY MINOR MATERIAL DAMAGE RESULTED FROM THE INCIDEN
2021-02-26 10:36 | YES | NO |  | 19870016 |  | 20230 | UNITED GAS PIPELINE CO | CALVIN | WINN | LA | 71410 | 381.8 | 20157+ | 2210 | 1986-11-12 |  | NO |  |  | LA | Null | NO | RUPTURE | 36.75 | 0 | 0 | 221665 | 209803.594 | 457062.1647 | Null | 0 | 20 |  | 19861113 | 834 | 936 | BY TEST | 1205 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: NO DATA; PRTFL: NO DATA; MLKD: NO DATA; PRTSY: NO DATA; PRTYR: 1952; NMDIA: 30; THK: 0.38; SPEC: API SLX; SMYS: 52000; SEAM: FLASHWELD; MANU: A. O. SMITH; MANYR: 1952; LOCLK: NO DATA; PNAME: W. F. ST. GERMAIN; PHONE: 7132295772; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | WILL BE FILLED IN AFTER METALLURGICAL INVESTIGATION IS COMPLETE, ON SUPPLEMENTAL REPORT.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19870017 |  | 7605 | HOUSTON PIPELINE CO | JIM HOGG |  | TX |  |  | 0+94 | 1700 | 1986-10-14 | 1 | NO |  |  |  | Null | NO | RUPTURE | 40 | 0 | 1 | 5000 | 4732.4475 | 10309.7504 | Null | 2 | 0 |  | 19861015 | 640 | 1365 | BY TEST | 1502 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1976 | 12 | 0.25 | 5LX | 52000 | ERW |  | AMERICAN | 1975 | UNDER GROUND |  | NASSER PEBDANI | 7139405326 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL |  | YES | 19860831 | WATER |  | 24 | 1502 | IN OUR LETTER OF SEPTEMBER 12, 1986, WE REPORTED THAT THIS INCIDENT WAS ORIGINALLY REPORTED IN ERROR AN AUGUST 27, 1986 AS IT HAD BEEN DETERMINED THAT THE ORIGIN WAS NOT A PART OF OUR DISTRIBUTION SYSTEM. AFTER FURTHER INVESTIGATION, IT HASBEEN DETERMINED THAT THE INCIDENT WAS REPORTABLE. INITIAL FIELD TEST REPORTS INDICATED REGULATOR ALLOWED EXCESSIVE PRESSURE ON CUSTOMER PIPING. FURTHER LABORATORY TESTS INDICATED REGULATOR FUNCTIONED PROPERLY. AFTER FURTHER REVIEW OF FIELDDOCUMENTATION OF EVENTS, IT WAS DISCOVERED THAT SEVERAL FIELD TESTS WERE ACTUALLY PERFORMED INDICATING MALFUNCTION OF SERVICE REGULATOR. SUBSEQUENTLY, WE ARE SUBMITTING AN INCIDENT REPORT. WE REGRET ANY INCONVENIENCE THIS MAY HAVE CAUSED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870024 |  | 21031 | VALERO TRANSMISSION CO | ARANSAS - ROCKPORT | ARANSAS | TX |  |  |  | 1500 | 1986-12-30 |  | YES |  |  | TX | Null | NO | LEAK | 0 | 0 | 0 | 50000 | 47324.4748 | 103097.504 | Null | 4 | 0 |  | 19861230 | 650 | 915 | BY TEST | 1500 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1969; NMDIA: 8.63; THK: 0.25; SPEC: API5LX42; SMYS: 2667; SEAM: DSA; MANYR: 0; LOCLK: UNDER WATER; PNAME: ROY DE LA HOUSSAYE; PHONE: 5128837982; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | PIPELINE WAS HIT BY MARINE VESSEL. WE DO NOT KNOW WHO WAS RESPONSIBLE FOR DAMAGE. APPEARS THAT A BARGE HIT PIPE CAUSING DAMAGE.
2021-02-26 10:36 | YES | YES | GG (Gas Gathering) | 19870026 |  | 22655 | WILLISTON BASIN INTERSTATE PIPELINE CO | GOATS PASS COMPRESSOR STA | BILLINGS | ND |  | S1/2SW1/4 SEC.27 |  | 1200 | 1986-12-15 | 1 | NO |  |  |  | Null | YES | LEAK | 0 | 0 | 1 | 350000 | 331271.3234 | 721682.5283 | Null | 2 | 30 |  | 19861215 | 0 | 0 | NO DATA | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: GATHERING SYSTEM; PRTFL: OTHER; MLKD: OTHER; MLKDO: FIBERGLASS OR PLASTIC; PRTSY: COMPRESSOR STATION; PRTYR: 1985; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: W. EYER; PHONE: 4063597200; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: NO DATA; CTEST: NO; MED: NO DATA; TMPS: 0; LKPS: 0 | LEAK OR CRACK OCCURRED IN A FIBERGLASS WASTE LIQUED TANK OR IN PLASTIC PIPE LEADING TO TANK. EXACT LOCATION UNKNOWN. FIRE DESTROYED FACILITIES.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19870030 |  | 13063 | NATIONAL FUEL GAS SUPPLY CORP | HORTON TOWNSHIP | ELK | PA |  |  |  | 1000 | 1986-07-11 | 4 | NO |  |  |  | Null | NO | RUPTURE | 1 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  |  | 1380 | 0 | NO DATA | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1986; NMDIA: 4; THK: 0.24; SPEC: GRADE B; SMYS: 0; SEAM: ERW; MANU: NAPSCO; MANYR: 1985; LOCLK: UNDER GROUND; PNAME: JOHN H. SAMONSKY, III; PHONE: 8146766531; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: MATERIAL; CTEST: NO; MED: WATER; TMPS: 0; LKPS: 1380 | TWO INCH & FOUR INCH PIPE WAS TO BE LAID IN THE GATHERING SYSTEM OF BELMOUTH STORAGE FIELD, A REMOTE AREA IN ELK COUNTY, PA. WHEN TESTED, A TOTAL OF FIVE FAILURES WERE FOUND, ALL BELOW 2000 PSIG, 4 IN 4", AND 1 IN 2". FURTHER INVESTIGATIONREVEALED THAT AT LEAST SOME OF THE PIPE WAS ACTUALLY STRUCTURAL TUBING SHIPPED AND BILLED AS PRIME ERW PIPE. ALL 4" PIPE HAS BEEN REPLACED.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19870041 |  | 3230 | DELHI GAS PIPELINE CORP | DALLAS | DALLAS | TX | 75201 |  |  | 1007 | 1986-12-10 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19861211 | 940 | 1345 | BY TEST | 1480 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1978 | 6 | 0.19 | APISL | 42000 | ERW |  | U.S.S. | 0 | UNDER GROUND |  | GARY E. REED OPER. ENGR. SUPR. | 2149542115 | INTERNALLY | LOCALIZED PITTING |  | OTHER | CHEMICAL | COATED | YES | 1978 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | INCIDENT OCCURRED DURING THE REPAIR OF A LEAK IN A 6" PIPELINE. THE LINE HAD BEEN BLOWDOWN & ISOLATED FOR THE REPAIR PROCEDURES. DURING THE REMOVAL OF THE LEAKING PIPELINE SEGMENT, A SUDDEN, SHORT DURATION GAS FLOW WAS EXPERIENCED. LINE WAS INTERNALLY INHIBITED.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19870044 |  | 18646 | STINGRAY PIPELINE CO |  |  | LA | 77001 | 1004C-700 | 135023 | 511 | 1987-02-13 |  | YES | W.C. | 587-A |  | YES | NO | RUPTURE | 1 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 5 |  | 19870213 | 1120 | 1250 | BY TEST | 2152 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1974 | 24 | 0.5 | API-5LX-60 | 60000 | SAW |  | BETHLEHEM STEEL | 1974 | NO DATA |  | A.E. FAWCETT III, SUPERVISING ENGINEER | 7136641254 | INTERNALLY | LOCALIZED PITTING |  | OTHER |  | COATED | YES | 1974 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | LINE WAS BLOWN DOWN TO INSTALL REPAIR CLAMP ON LEAK AND WAS BEING REPRESSURED FOR SERVICE WHEN RUPTURE OCCURRED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870047 |  | 405 | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  |  | LA |  |  | 73108 | 715 | 1987-02-02 |  | YES | E.I. | 266C |  | YES | NO | LEAK | 0 | 0 | 0 | 50000 | 46285.5638 | 100834.2115 | Null | 0 | 0 |  | 19870202 | 850 | 1300 | BY TEST | 2701 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | GIRTH | STEEL |  | PIPELINE |  | 1970 | 12 | 0.38 | API 5LX | 46000 | ELECTRIC RESIST |  | LONE STAR | 1970 | UNDER WATER |  | R.J. LECZNAR | 3134962456 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION |  | YES | 19700415 | WATER |  | 32 | 2685
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19870050 |  | 18646 | STINGRAY PIPELINE CO |  |  | LA |  | 1004C-700 | 178131 | 726 | 1987-02-01 |  | YES | WEST CAMERON | 587-A |  | YES | NO | LEAK | 0 | 0 | 0 | 200000 | 185142.255 | 403336.8458 | YES | 0 | 0 |  | 19870201 | 930 | 1250 | BY TEST | 2152 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1974 | 24 | 0.5 | API-5LX-60 | 60000 | SAW |  | BETHLEHEM STEEL | 1974 | UNDER WATER |  | A.E. FAWCETT, SUPERVISING ENGINEER | 7136641254 | INTERNALLY | OTHER |  | OTHER |  | COATED | YES | 0 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870052 |  | 22365 | WESTAR TRANSMISSION CO | LENORAH | MARTIN | TX |  |  | 2647.0 | 1730 | 1987-02-17 | 1 | NO |  |  | TX | Null | NO | OTHER | 0 | 0 | 0 | 10000 | 9257.1128 | 20166.8423 | Null | 20 | 0 |  | 19870218 | 275 | 428 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: TAP; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1930; NMDIA: 8; THK: 0.22; SMYS: 1320; SEAM: LW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: R.L TOMLINSON, SUPERINTENDENT; PHONE: 8067473037; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: 2 SIGNS 1200 FT. AWAY; STAT: NO; CTEST: Null | FARMER WAS DEEP PLOWING & HIT AN ABONDONED TAP THAT EXTENDED 9 INCHES ABOVE PIPELINE (PIPELINE HAD 21 INCHES OF COVER) FARMER ALSO FAILED TO NOTIFY ANYONE UNTIL THE NEXT DAY.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870059 |  | 18536 | SOUTHWEST GAS CORP | CARSON LATERAL |  | NV |  | 64.47 |  | 710 | 1987-02-11 | 3 | NO |  |  | NV | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 20 |  | 19870211 | 445 | 520 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: NO DATA; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1964; NMDIA: 8; THK: 0.19; SMYS: 24000; SEAM: ELECTRIC RESIST; MANYR: 0; LOCLK: UNDER GROUND; PNAME: C.E. STONER, MANAGER OF ENGINEERING; PHONE: 7028825776; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PIPELINE MARKERS; STAT: NO; CTEST: Null | WHILE ATTEMPTING TO LOCATE A CULVERT, CONTRACTOR DUG INTO 8" HIGH PRESSURE TRANSMISSION LINE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19870072 |  | 8040 | ILLINOIS POWER CO | CLARMIN | WASHINGTON | IL |  |  |  | 1400 | 1987-03-29 | 3 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 100000 | 92571.1275 | 201668.4229 | Null | 3 | 0 |  | 19870329 | 250 | 400 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: OTHER; PRTSO: STORAGE FIELD WELL; PRTYR: 1961; NMDIA: 5.5; THK: 0.24; SPEC: API 14# GRADE H-40 C; SMYS: 3110; SEAM: SEAMLESS; MANYR: 0; LOCLK: UNDER GROUND; PNAME: DENNIS ANDERSON; PHONE: 2174246515; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: NO DATA; CTEST: Null; MED: NO DATA; TMPS: 0; LKPS: 0 | SUBSIDENCE INA COAL MINE ABADONED IN 1948 CAUSED A LEAK IN THE I.,P.C. #2 GAS GAS STORAGE WELL IN ILLINOIS POWER'S TILDEN GAS STORAGE FIELD. AS ARESULT OF THISSUBSIDENCE, THE 5 1/2" O.D PRODUCTION CASING AND 8 5/8" O.D. MINE CASING WERE DAMAGEED AND GAS ESCAPED INTO THE ABANDONED COAL MINE.THREE ILLINOIS POWER OBSERVATION WELLS COMPLETED IN THE ABANDONED MINE WERE USEDTO VENT THE ESCAPING GAS TO ATMOSPHERE WITHIN THREE HOURS TO CONTROL THE PRESSURE IN THE ABANDONED MINE. NUMEROUS ATTEMPTS TO PUMP FLIUD DOWN THE WELL FAILED TO KILL THE WELL AND STOP THE FLOW OF GAS. A COILED TUBING UNIT WAS ALSO UTILIZED IN ATTEMPTS TO KILL THE WELL WITH FLUID WERE UNSUCCESSFUL. ARIG WAS THEN UTILIZED TO MILL OUT APPROXIMATELY 12.5 FEET OF DAMAGED CASING TO ALLOW FLUID TO BEPUMPED INTO THE WEL TO STOP THE FLOW OF GAS. THE DAMAGE I.P.C #2 WELL WAS THENPLUGGED WITH CEMENT
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19870078 |  | 13120 | NATURAL GAS PIPELINE CO OF AMERICA |  |  | TX |  |  | 113+00 | 1530 | 1987-01-13 |  | YES | HI | 342B |  | YES | NO | LEAK | 0 | 0 | 0 | 150000 | 138856.6913 | 302502.6344 | Null | 0 | 0 |  |  | 0 | 1440 | BY TEST | 2160 | CORROSION | CORROSION | INTERNAL | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1978; NMDIA: 12.75; THK: 0.38; SPEC: 5LX; SMYS: 52000; MANU: ARMCO STEEL; MANYR: 1977; LOCLK: UNDER WATER; PNAME: R LANDERS; PHONE: 3126913605; LOC: INTERNALLY; ADESC: NO DATA; CAUCR: NO DATA; COAT: COATED; PROT: YES; CPYR: 1977; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | THERE ARE 2 LEAKS ON THE 12" PIPELINE DUE TO INTERNAL CORROSION
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870079 |  | 456 | AMOCO GAS CO |  | JEFFERSON | TX |  |  | 430+37 | 1415 | 1987-04-06 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 3 | 0 |  | 19870407 | 350 | 1000 | BY TEST | 1500 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1966 | 8 | 0.32 | GRADE B | 35000 | ERW |  | BETHLEHEM STEEL | 1965 | OTHER | ABOVE WATER | JAMES H COLLINS - SENIOR INSP | 4099482501 | EXTERNALLY | LOCALIZED PITTING |  | OTHER | ENVIROMENT | COATED | YES | 1966 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | THE PIPE IS ON PILINGS PARRALLELING KEITH LAKE BRIDGE. CORROSION STARTED UNDERTHE COATING, CAUSING A SMALL PIT AND A RESULTING LEAK.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19870084 |  | 13120 | NATURAL GAS PIPELINE CO OF AMERICA | LINCOLN | LINCOLN | KS |  | 320 | 15984+ | 1540 | 1987-02-13 | 1 | NO |  |  |  | Null | Null | OTHER | 0 | 0 | 0 | 70545 | 65304.3019 | 142266.9889 | Null | 12 | 0 |  |  | 600 | 712 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1931; NMDIA: 18; THK: 0.38; SPEC: GRADE A; SMYS: 30000; MANU: A O SMITH; MANYR: 0; LOCLK: UNDER GROUND; PNAME: F ROY FLEET; PHONE: 3126913605; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19870107; MARK: YES; MRKTP: YELLOW PIPELINE MRKER FLG; STAT: YES; CTEST: Null | CONTRACTOR OPERATOR GOUGEED 18" PIPELINE WITH 235 CAT BACKHOE BUCKET WHILE CLEANING DRAINAGE DICTH. PIPELINES WERE FLAGGED, PRODDED AND DEPTH RECORDED ON FLAGS ON 1/7/87. COMPANY INSPECTORS WERE PRESENT AND WITNESSED THE DAMAGE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19870089 |  | 15493 | PHILLIPS PETROLEUM CO |  | MIDLAND | TX | 79762 |  | 132+67 | 0 | 1986-12-01 | 4 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 90000 | 85184.0546 | 185575.5073 | YES | 0 | 0 |  | 19870213 | 582 | 1310 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1960 | 6 | 0.16 |  | 35000 | ELECTRIC WELD | PLUG 600# | MERCO | 0 | UNDER WATER |  | V MARTIN | 9153671404 | EXTERNALLY | GENERAL CORROSION |  | NO DATA |  | COATED | YES | 1960 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | FOR APPROXIMATELY ONE YEAR, THE GENERAL AREA WHERE THE LEAK ACCURRED HAS BEEN UNDER WATER DUE TO EXCESSIVE AMOUNT OF RAINFALL AND IRRIGATION BY LANDOWNER. AREA REQUIRED DRAINAGE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19870091 |  | 20245 | UNITED TEXAS TRANSMISSION CO | BEAUMONT | JEFFERSON | TX | 77705 | 54.38 | 2871+3 | 650 | 1987-03-02 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 147232 | 136294.3224 | 296920.4524 | YES | 0 | 0 |  | 19870302 | 350 | 415 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1928 | 18 | 0.25 | APL 5L | 33000 | SMLS |  | A O SMITH | 0 | UNDER PAVEMENT |  | W F ST GERMIAN | 7132295772 | EXTERNALLY | OTHER | INFO NOT AVAILABLE | OTHER | INFO NOT AVAILABLE | COATED | YES | 1954 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | LINE WAS LEAKING UNDER PAVED COUNTY ROAD (GENTRY ROAD). COMPANY PERSONAL MONITORED THE LEAK CONTINUALLY FROM TIME OF VERIFATION UNTIL THE LINE WAS SHUT DOWN.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870092 |  | 21031 | VALERO TRANSMISSION CO | CRYSTAL CITY | ZAVALA | TX |  | .4 |  | 1000 | 1987-02-04 | 1 | NO |  |  | TX | Null | NO | OTHER | 0 | 0 | 0 | 1000 | 925.7113 | 2016.6842 | YES | 0 | 0 |  |  | 60 | 397 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1930; NMDIA: 4; THK: 0.25; SMYS: 2666; MANYR: 1930; LOCLK: UNDER GROUND; PNAME: P WARD; PHONE: 5122462395; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19870102; MARK: YES; MRKTP: STAKES & FLAGS; STAT: NO; CTEST: Null | 4" PIPELINE WAS HIT BY TENNESSEE PIPELINE CONSTRUCTION COMPANY WHILE EXCAVATING.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870093 |  | 21031 | VALERO TRANSMISSION CO |  | KLEBERG | TX |  | NORTH HWY #77 | 373+85 | 0 | 1987-03-06 | 1 | NO |  |  | TX | Null | NO | LEAK | 0 | 0 | 0 | 18000 | 16662.803 | 36300.3161 | YES | 0 | 0 |  | 19870306 | 700 | 1063 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1974 | 16 | 0.28 | API 5LX 42 | 1470 | ERW |  | BETHLEHEM | 0 | UNDER GROUND |  | TERRY EARLEY | 5128834724 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1974 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | THIS IS A RESULT OF A CORROSION LEAK IN A TRANSMISSION LINE. THE LEAK DEVELOPED IN A RURAL AREA AND PRESENTED NO HAZARD. IT IS BEING REPORTED BECAUSE IT EXCEEDS THE PROPERTY DAMAGE LIMIT
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19870094 |  | 4904 | EXXON CO USA | SEAL BEACH | ORANGE | CA | 90740 |  |  | 1340 | 1987-05-13 |  | YES | PRC | PRC196 | CA | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 10 |  | 19870513 | 125 | 200 | BY TEST | 300 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1955; NMDIA: 3; THK: 0.22; SPEC: API 5L; SMYS: 35000; SEAM: GRD B, SEAMLESS; MANYR: 1955; LOCLK: UNDER WATER; PNAME: E P RIEHL - STAFF ENGINEER; PHONE: 8054942290; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | AT 1:40 PM ON MAY 13, 1987, THE LONG BEACH FIRE DEPT REPORTED AN OIL SPILL 500 YARDS OFFSHORE SEAL BEACH, CALIF. 10 BARRELS OF CRUDE OIL LEAKED OUT OF AN EIGHTINCH EMULSION PIPELINE CONNECTING EXXON'S BELMONT ISLAND PRODUCTION FACILITY WITH CRUDE OIL PROCESSING FACILITES AT EXXON'S SEAL BEACH SEPARATION CENTER. PRODUCTION FROM BELMONT ISLAND WAS IMMEDIATELY SHUT-IN TO MINIMIZE THE EXTENT OF THE SPILL. CLEAN-UP OPERATIONS WERE PROMPTLY INITIATED WITH THE NOTIFICATION OF CLEAN COASTAL WATERS AND INTERNATIONAL TECHNOLOGY CORP. THE NATIONAL RESPONCE CENTERWAS NOTIFIED AT 2:04 PM (NRC REPORT #5573). APPROXIMATELY TWO BARRELS OF CRUDE OIL WASHED ASHORE ALONG A FOUR MILE STRETCH OF SEAL BEACH AND LONG BEACH. CLEAN-UP OPERATIONS WERE COMPLETED BY 7:30 PM ON MAY 15, 1987. AN UNDERWATER INSPECTION OF THE EIGHT INCH EMULSION PIPELINE REVEALED A 5/8" DIA. HOLE. THIS HOLE WAS CAUSED BY INTERNAL CORROSION IN THE 32 YEAR OLD PIPELINE. AN INSPECTION OF THE ADJACENT THREE INCH PURCHASE GAS PIPELINE REVEALED A 1/4" DIA HOLE. THIS HOLE WAS THE RESULT OF EXTERNAL EROSION AS THE CRUDE OIL EMULSION AND ENTRAINED SAND EXITED THE EIGHT INCH EMULSION PIPELINE. AN UNKNOWN, BUT RELATIVELY SMALL QUANTITY OF NATURAL GAS ESCAPED FROM THE TREE INCH GAS PIPELINE AND BUBBLED TO THE OCEAN SURFACE. ALL HOLES WERE SUBSEQUENTLY CLAMPED BY DIVERS.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19870095 |  | 12342 | MEMPHIS LIGHT GAS & WATER DIVISION | MEMPHIS | SHELBY | TN | 38134 |  |  | 1120 | 1987-07-10 |  | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 1 | 16500 | 15274.236 | 33275.2898 | Null | 0 | 40 |  | 19870710 | 96 | 100 | BY TEST | 150 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: BODY OF PIPE; MLKD: OTHER; MLKDO: PE; PRTSY: PIPELINE; PRTYR: 0; NMDIA: 2; THK: 0.22; SPEC: ASTM D-2513; SMYS: 1600; SEAM: EXTRUDED; MANU: PHILLIPS; MANYR: 1986; LOCLK: UNDER GROUND; PNAME: CURTIS DILLIHUNT; PHONE: 9013201452; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19870630; MARK: NO; STAT: YES; CTEST: Null | CONTRACTOR WAS TRENCHING ACROSS ROAD AND HIT GAS MAIN, CAUSING A FIRE THAT DAMAGED TRENCHER AND BURNED OPERATOR AN ARM AND NECK.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870100 |  | 2616 | COLUMBIA GAS TRANSMISSION CORP | FREDERICK | FREDERICK | MD |  |  | 2+05 | 2130 | 1987-06-30 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 45000 | 41657.0074 | 90750.7903 | YES | 3 | 0 |  | 19870630 | 580 | 937 | BY TEST | 1495 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: NO DATA; MLKD: STEEL; MLKDO: & ASBESTOS GASKETS; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1977; NMDIA: 6; THK: 0.28; SPEC: API-5L, GRADE B; SMYS: 2958; SEAM: SUBMERGED ARC; MANYR: 0; LOCLK: OTHER; LOCLO: IN BUILDING; PNAME: CRAIG A KOWALSKI; PHONE: 7034655152; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | LIGHTNING STRUCK AN INDIRECT WATER BATH HEATER OWNED AND OPERATED BY WASHINGTONGAS LIGHT (WGL) AT BRINK STATION. A FIRE ENSUED AND SPREAD TO THEIR BUILDING. THE BUILDING WAS DESTROYED, DROPPING THE ROOF ONTO COLUMBIA'S MEASURING STATION AND OTHER WGL FACILITIES AS LOCATED THEREIN. THIS DESTROYED COLUMBIA'S ROCKWELL T-18 TURBINE METER SETTING AND DAMAGED RELATED 6"PIPE (ALONG WITH OTHER WGL FACILITIES).
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19870101 |  | 5304 | FLORIDA GAS TRANSMISSION CO | SINTON | SAN PATRICIO | TX | 78387 | 127.93 | 1697 + 95 | 1500 | 1987-07-08 | 1 | NO |  |  |  | Null | NO | RUPTURE | 10 | 0 | 2 | 0 | 0 | 0 | Null | 1 | 45 |  | 19870708 | 940 | 1052 | BY TEST | 1220 | CORROSION | CORROSION | EXTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1958; NMDIA: 20; THK: 0.28; SMYS: 52000; MANYR: 0; LOCLK: UNDER GROUND; PNAME: JEFF WHIPPO, COMPLIANCE ENGINEER; PHONE: 7138537321; LOC: EXTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: NO DATA; COAT: COATED; PROT: YES; CPYR: 1958; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | CORROSION WAS EXTERNAL, ON THE BOTTOM OF THE PIPE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19870102 |  | 22182 | WASHINGTON GAS LIGHT CO | SPRINGFIELD | FAIRFAX | VA | 22151 | 16 MI. MARK ON I-270 |  | 2200 | 1987-06-30 | 3 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 500000 | 462855.6375 | 1008342.1145 | Null | 2 | 26 |  | 19870701 | 580 | 600 | BY TEST | 900 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: VALVE; MLKD: STEEL; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1978; NMDIA: 1; THK: 0; SPEC: SPEC ASTM A-126-42; SMYS: 0; VALVE: 400 LB CLASS; MANU: ROCKWELL; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: C.E. GOODSON III - SAFETY SUPERVISOR; PHONE: 7037504584; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | ON THE EVENING OF JUNE 30, 1987, LIGHTING STRUCK A GATE STATION WHICH DELIVERS NATURAL GAS FROM COLUMBIA TRANSMISSION COMPANY TO WASHINGTON GAS LIGHT COMPANY. A LINE HEATER VALVE WAS THE POINT OF STRIKE, WAS BURNED THROUGH AND IGNITION OCCURRED. THE FLAMES INTENSIFIED UNTIL THE ENTIRE STATION WAS FULLY INVOLVED. MUTUALEFFORTS OF COLUMBIA AND WASHINGTON GAS LED TO THE CLOSING OF THE STATION INLET AND OUTLET VALVES WHICH ALLOWED THE FIRE TO EXTINGUISH ITSELF.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19870104 |  | 11680 | LONE STAR GAS CO | DALLAS | DALLAS | TX | 75201 |  | 370+14 | 1300 | 1987-06-10 | 1 | NO |  |  | TX | Null | NO | RUPTURE | 4 | 0 | 0 | 5483 | 5075.6749 | 11057.4796 | Null | 2 | 30 |  | 19870610 | 295 | 500 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | GATHERING SYSTEM | OTHER | MAIN LINE DRIP | STEEL |  | OTHER | MAIN LINE DRIP | 0 | 8 | 0.25 | AP15L-GR. B | 35000 | EW |  |  | 0 | UNDER GROUND |  | R.D. HEATHERINGTON | 8174421379 | EXTERNALLY | NO DATA |  | NO DATA |  | NO DATA | YES | 1969 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | CORROSION IN A MAIN LINE DRIP ON LINE OS-8".
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19870105 |  | 3230 | DELHI GAS PIPELINE CORP | CORPUS CHRISTI | NUECES | TX | 78405 |  |  | 1400 | 1987-06-08 | 3 | NO |  |  |  | Null | Null | LEAK | 0 | 0 | 0 | 5441 | 5036.795 | 10972.7789 | Null | 0 | 0 |  |  | 320 | 564 | BY TEST | 620 | CORROSION | CORROSION | INTERNAL | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1942; NMDIA: 6.63; THK: 0.19; SMYS: 0; SEAM: ERW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: SAMUEL M. SIMPSON DISTRICT SAFETY; PHONE: 5128828402; LOC: INTERNALLY; ADESC: NO DATA; CAUCR: NO DATA; COAT: COATED; PROT: YES; CPYR: 1971; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | PIPELINE WAS PURCHASED FROM SUN OIL CO. IN 1971. PRIOR RECORDS INDICATE THAT SUN HAD CATHODIC PROTECTION ON PIPELINE PRIOR TO DELHI'S PURCHASE. THIS LINE IS SCHEDULED FOR REPLACEMENT ON 7/14/87
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870112 |  | 19570 | TRANSCO GAS PIPELINE CORP | MELVILLE | ST LANDRY | LA |  | 559.98 | 6562+6 | 500 | 1987-05-24 | 1 | NO |  |  |  | Null | NO | RUPTURE | 1.5 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 1 |  | 19870524 | 650 | 780 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: GIRTH; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1966; NMDIA: 18; THK: 0.5; SPEC: API 5LX; SMYS: 52000; SEAM: SEAMLESS; MANU: U.S. STEEL; MANYR: 1966; LOCLK: UNDER GROUND; PNAME: B. R. LANDES - SR. COMPLIANCE ANALYST; PHONE: 7134392001; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | PART B AS A RESULT OF THE GATES BEING CLOSED AT THE OLD RIVER DIVERSION STATION, THERE WAS A DROP IN THE LEVEL OF THE ATCHAFALAYA RIVER IN A SHORT PERIOD OF TIME . IT IS SURMISED THAT THIS CONDITION CONTRIBUTED TO THE SLOUGHING OF THE EAST BANK.PART 3 INCIDENT OCCURRED ON EAST BANK OF ATCHAFALAYA RIVER. THE PIPELINE PULLED APART AT A GIRTH WELD BECAUSE OF STRESSES CAUSED BY THE SLOUGHING OF THE EAST BANK. CURRENT PLANS ARE FOR THIS PIPELINE TO BE ABANDONED IN PLACE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870113 |  | 13845 | NORTHWEST PIPELINE CORP | 15 MI NW OF RANGLY | RIO BLANCO | CO |  | 293.75 | 15494+ | 1010 | 1987-05-26 | 1 | NO |  |  | CO | Null | YES | LEAK | 0 | 0 | 0 | 24000 | 22217.0706 | 48400.4215 | YES | 0 | 0 |  | 19870529 | 510 | 809 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | LONG | STEEL |  | PIPELINE |  | 1956 | 26 | 0.28 | API 5LX52 | 1124 | DSA |  | CONSOLIDATED WEST | 1955 | UNDER GROUND |  | MYRLE B. ANDERSON COMPLIANCE SPECIALIST | 8015846908 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL |  | YES | 19560522 | WATER |  | 1 | 867 | PART C #4 3/4 - INCH CRACK IN LONGSEAM
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870115 |  | 2616 | COLUMBIA GAS TRANSMISSION CORP | STRONGSVILLE | CUYAHOGA | OH | 44136 |  | 360+53 | 1957 | 1987-05-25 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 4 | 22 |  | 19870526 | 220 | 250 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: VALVE; MLKD: STEEL; PRTSY: OTHER; PRTSO: 1" LINE FROM UNDGRD. DIP; PRTYR: 1958; NMDIA: 1; THK: 0; SPEC: FIG.524, 500 WOG; SMYS: 0; VALVE: PLUG; MANU: NORDSTROM; MANYR: 1958; LOCLK: ABOVE GROUND; PNAME: A.S. BECKETT SUPERVISORY ENGINEER; PHONE: 3043572797; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; STAT: NO; CTEST: Null | PART B #3INCIDENT RESULTED FROM A MOTORCYCLE TRAFFIC ACCIDENT; SEE ATTACHED COPY OF OHIOTRAFFIC ACCIDENT REPORT NO. 87-4172 BY STRONGSVILLE POLICE DEPT. THE MOTORCYCLEBROKE VALVE LOOSE FROM 1" PIPE, CAUSING GAS TO ESCAPE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19870117 |  | 11680 | LONE STAR GAS CO | WAURIKA | JEFFERSON | OK |  |  | 6+94 | 600 | 1987-05-28 | 1 | NO |  |  | OK | Null | NO | OTHER | 0 | 0 | 0 | 350000 | 323998.9463 | 705839.4802 | Null | 9 | 0 |  | 19870529 | 265 | 375 | BY TEST | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1918; NMDIA: 12; THK: 0.25; SPEC: 24000; SMYS: 0; VALVE: 500; MANYR: 0; LOCLK: NO DATA; PNAME: P.R. TARRANT; PHONE: 2147413711; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870118 |  | 11680 | LONE STAR GAS CO |  | CRANE | TX |  |  | 18380+ | 1500 | 1987-04-22 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 47500 | 43971.2856 | 95792.5009 | Null | 48 | 0 |  | 19870422 | 700 | 960 | BY TEST | 1203 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 0; NMDIA: 36; THK: 0.37; SPEC: API-5LX; SMYS: 65000; SEAM: ERW; MANYR: 1972; LOCLK: UNDER GROUND; PNAME: PHILLIP MURDOCK; PHONE: 2147413711; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: SIGNS ON POSTS; STAT: NO; CTEST: Null | BULLDOZER OPERATOR WORKING ON A WELL FOR ANOTHER COMPANY HIT LONE STAR'S 36" LINE. THE OPERATOR WAS NOT AWARE OF THE LINE. PIPELINE DID NOT RUPTURE BUT WAS DAMAGED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870119 |  | 11680 | LONE STAR GAS CO | CORSICANA | NAVARRO | TX | 75110 |  | MEAS.S | 1100 | 1987-04-29 | 3 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 50000 | 46285.5638 | 100834.2115 | Null | 0 | 30 |  | 19870429 | 0 | 300 | BY TEST | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: INSTRUMENT BLDG.; MLKD: NO DATA; PRTSY: OTHER; PRTSO: INSTRUMENT BLDG. & EQUIP.; PRTYR: 1983; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: RICHARD EDMONDSON SUPT. I; PHONE: 8177520770; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | EMPLOYEES ATTEMPTED TO RE-LIGHT THE TITARTOR, EXPLOSION AND FIRE DESTROYED THE BUILDING AND ALL THE EQUIPMENT.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19870123 |  | 21031 | VALERO TRANSMISSION CO | FREER COMPRESSOR STATION | WEBB | TX | 78357 | 94.5 | 4991+6 | 1250 | 1987-05-12 | 1 | NO |  |  |  | Null | NO | RUPTURE | 5 | 0 | 0 | 200000 | 185142.255 | 403336.8458 | Null | 2 | 0 |  | 19870512 | 931 | 1010 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | INTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1961; NMDIA: 20; THK: 0.28; SPEC: API 5LX-52; SMYS: 1461; MANYR: 1960; LOCLK: UNDER GROUND; PNAME: ROYCE SLIVA AREA SUPERVISOR; PHONE: 5127243981; LOC: INTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: OTHER; CAUCO: IRON OXIDE; COAT: COATED; PROT: YES; CPYR: 1962; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | REASON FOR FAILURE IS UNKNOWN AT THIS TIME. METALLURGICAL INVESTIGATION IS BEINGCONDUCTED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870124 |  | 19325 | TEXAS UTILITIES FUEL CO |  | NAVARRO | TX |  | K-15 |  | 515 | 1987-05-27 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 45 |  | 19870527 | 605 | 1091 | BY TEST | 1201 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1971 | 6 | 0.16 | X42 | 1777 | ERW |  |  | 0 | UNDER GROUND |  | BILLY G. BROWN LEAD OPERATOR | 8177393031 | INTERNALLY | GENERAL CORROSION |  | OTHER | INTERNAL CORROSION | COATED | YES | 1971 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | SMALL LEAK ABOUT 200 YARDS WEST OF MILES MARKER K-15 OFF OF COUNTY RD. LT-2-87
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870128 |  | 8149 | INTER - CITY GAS MINNESOTA PIPELINES LTD | WARROAD | ROSEAU | MN |  |  |  | 1600 | 1987-08-13 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  |  | 520 | 802 | BY TEST | 1365 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1970 | 12 | 0.16 | API 5L X52 | 52000 | ERW |  | IPSCO (CANADA) | 1970 | UNDER GROUND |  | W. TIBELIUS, P. ENG. - ASST. CHIEF ENGINEER | 2049343944 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | COATED | YES | 1970 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | CORROSION LEAK WAS DISCOVERED DURING LEAK SURVEY. CORRODED SECTION WAS REPLACEDWITH PRETESTED PIPE (1392 PSIG) - COMPLETED AUGUST 24, 1987
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870130 |  | 2616 | COLUMBIA GAS TRANSMISSION CORP | 2 MI NORTH OF FOSTER | PENDLETON | KY | 41043 | 4300/736 DETAIL A | 159+88 | 1710 | 1987-08-06 | 1 | NO |  |  | KY | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 50 |  | 19870806 | 320 | 1123 | BY TEST | 1528 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1985; NMDIA: 24; THK: 0.29; SPEC: API 5 LX; SMYS: 65000; SEAM: DSAW; MANU: ARMCO; MANYR: 1981; LOCLK: UNDER GROUND; PNAME: HAROLD FLETCHER - AREA SUPT.; PHONE: 6067445832; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; MARK: YES; MRKTP: WHITE/ORANGE 4"D X 4'H; STAT: NO; CTEST: Null | PART 3:HOLLOWAY CONSTRUCTION WAS CROSSING PIPELINE WITH HEAVY EARTH MOVING EQUIPMENT (SCRAPER PANS AND DOZERS) WHEN A PAN STRUCK THE PIPELINE, AFTER REMOVING FIVE (5)FEET OF EARTH COVER. PART B # 3:THE PIPELINE HAD BEEN RELOCATED FOR CONSTRUCTION OF THE A-A HIGHWAY, AND A STATE INSPECTOR, WHO KNEW THE PIPELINE LOCATION, WAS ON THE JOB SITE AT THE TIME OF THE INCIDENT. ALSO, THE CONSTRUCTION SUPERINTENDENT WAS AWARE OF THE PIPELINE LOCATION AND HAD DISCUSSED THE HAZARDS WITH EQUIPMENT OPERATORS.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870135 |  | 12690 | MONTANA POWER CO |  | BEAVERHEAD | MT |  | MP 60.4 | 3170+1 | 1930 | 1987-07-17 | 3 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 11900 | 11015.9642 | 23998.5423 | Null | 2 | 0 |  | 19870718 | 370 | 590 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: GIRTH; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1964; NMDIA: 3; THK: 0.16; SPEC: API 5LX-42; SMYS: 42000; SEAM: ERW; MANU: LONG STAR; MANYR: 1964; LOCLK: UNDER GROUND; PNAME: ROGER L. RAWLS CHIEF GAS ENGINEER; PHONE: 4067235421; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: MARKERS IN PLACE; STAT: YES; CTEST: Null | PIPE CONTAINED MULTIPLE DENTS IN A SPACE OF 6 FEET. THERE WAS ALSO EVIDENCE OF BENDING UPWARD WHICH RESULTED IN A TENSION FAILURE IN A GIRTH WELD
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19870142 |  | 20245 | UNITED TEXAS TRANSMISSION CO | GALVESTON BAY | CHAMBERS | TX | 77514 | 20.97 | 1107+2 | 1415 | 1987-07-22 |  | YES |  | 288 | TX | Null | NO | LEAK | 0 | 0 | 0 | 100000 | 92571.1275 | 201668.4229 | Null | 0 | 0 |  | 19870722 | 850 | 955 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1959 | 10 | 0.25 | API-5LX | 42000 | SEAMLESS |  | NATIONAL | 1959 | UNDER WATER |  | RON WELLS - COORDINATOR | 7132295737 | INTERNALLY | LOCALIZED PITTING |  | OTHER | SEE NO 2, THIS PART | COATED | NO | 0 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | COMPANY PERSONNEL MONITORED LEAK CONTINUALLY FROM TIME OF INITIAL NOTIFICATION ON 7/21/87 UNTIL THE LINE WAS SHUT DOWN FOR REPAIR ON 7/23/87. TELEPHONIC NOTIFICATION TO THE RRC WAS MADE WHEN LEAK WAS CONFIRMED TO BE ON UTTCO FACILITIES ON 7/22/87
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19870145 |  | 21031 | VALERO TRANSMISSION CO | SAN ANTONIO |  | TX | 78250 | 13.375 | 706+20 | 900 | 1987-09-16 | 3 | NO |  |  | TX | Null | NO | RUPTURE | 11 | 0 | 1 | 20000 | 18514.2255 | 40333.6846 | Null | 0 | 30 |  | 19870916 | 500 | 731 | BY TEST | 1109 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1962; NMDIA: 24; THK: 0.28; SPEC: X-52; SMYS: 1281; SEAM: SEAMLESS; MANYR: 0; LOCLK: UNDER GROUND; PNAME: TERRY EARLEY; PHONE: 5122462395; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PIPELINE MARKERS; STAT: NO; CTEST: Null | LOCATION MARKED WITH PIPELINE MARKERS WITH COMPANY NAME AND 24-HOUR EMERGENCY NUMBER.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19870146 |  | 19160 | TENNESSEE GAS PIPELINE CO | ST. MARY PARISH |  | LA |  | 519A-101+12.57 | 663+51 | 330 | 1987-09-11 |  | YES | BAY ATCHAFALAYA |  |  | Null | NO | RUPTURE | 0 | 0 | 0 | 111000 | 102753.9515 | 223851.9494 | Null | 4 | 10 |  | 19870911 | 870 | 1015 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1959; NMDIA: 10; THK: 2.79; SPEC: X-52; SMYS: 52000; SEAM: DOUBLE-SUBMERGE; MANU: LONE STAR; MANYR: 1956; LOCLK: UNDER WATER; PNAME: RICHARD WINN; PHONE: 7137572581; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: YES; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870147 |  | 22365 | WESTAR TRANSMISSION CO | MONAHANS | WARD | TX |  | 1192+34 2294+32 | 1254+1 | 1630 | 1987-09-14 | 1 | NO |  |  | TX | Null | NO | RUPTURE | 0.06 | 0 | 0 | 50000 | 46285.5638 | 100834.2115 | Null | 1 | 15 |  | 19870914 | 830 | 953 | BY TEST | 1048 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1969; NMDIA: 20; THK: 0.25; SPEC: X56; SMYS: 1400; SEAM: ELECTRIC WELD; MANYR: 0; LOCLK: NO DATA; PNAME: R.L. TOMLINSON; PHONE: 8067473037; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19870914; MARK: YES; MRKTP: METAL POST WITH SIGN; STAT: YES; CTEST: Null | WESTAR SUPERVISOR REMAINED ON SITE UNTIL CONTRACTOR FINISHED EXPOSING & CROSSING PIPELINE. AFTER WESTAR SUPERVISOR LEFT CONTRACTOR BEGAN SHAVING TOP WALLS OF DITCH & HIT PIPELINE WITH BACKHOE BUCKET. CONTRACTOR FOR CHEVRON PUNCTURED WESTARLINE #4000 WITH BACKHOE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870148 |  | 2436 | CLAJON GAS CO | LAGRANGE | FAYETTE | TX | 78945 | .201 | 10+61 | 800 | 1987-09-24 | 1 | NO |  |  | TX | Null | NO | RUPTURE | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 30 |  | 19870924 | 420 | 1200 | BY TEST | 1850 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: VALVE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1982; NMDIA: 4; THK: 0.16; SPEC: X-42; SMYS: 0; VALVE: BALL VALVE; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: WILLIAM WEISER; PHONE: 4095425702; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: SIGNS; STAT: YES; CTEST: Null | THE GRADALL VEHICLE WAS WEST BOUND ON 2981 WHEN THE DRIVER MR. LUNA LOST CONTROLON A DOWN HILL SLOPE-RAN OFF THE ROAD TO THE LEFT, CROSSED THE DITCH, THE FENCEAND HIT THE PIPELINE TAP-PASSING OVER THE TAP AND CAME TO REST APPROX. 10' WESTOF THE TAP. MR. LUNA DROVE THE VEHICLE AWAY FROM THE FIRE AT THE TAP-BACK ACROSS FM 2981.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870150 |  | 4070 | EAST TENNESSEE NATURAL GAS CO | JOHNSON CITY | WASHINGTON | TN | 37601 | .775 | 40+93 | 1600 | 1987-07-27 | 2 | NO |  |  |  | Null | NO | RUPTURE | 2.5 | 0 | 0 | 18000 | 16662.803 | 36300.3161 | Null | 1 | 31 |  |  | 490 | 706 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1963; NMDIA: 6; THK: 0.19; SPEC: API-5LX; SMYS: 42000; SEAM: SEAMLESS; VALVE: N/A; MANU: U.S. STEEL; MANYR: 1963; LOCLK: UNDER GROUND; PNAME: A. CREECH NEWSOME, JR.; PHONE: 6156946344; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PIPELINE MARKERS; STAT: YES; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870152 |  | 13063 | NATIONAL FUEL GAS SUPPLY CORP | KANE FIELD | ELK | PA | 16735 | 1339 N. OF B&O RR |  | 20 | 1987-09-03 | 1 | NO |  |  | PA | Null | NO | RUPTURE | 4.5 | 0 | 0 | 0 | 0 | 0 | Null | 1 | 0 |  | 19870903 | 449 | 485 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1908; NMDIA: 12; THK: 0.33; SMYS: 24000; MANYR: 0; LOCLK: UNDER GROUND; PNAME: JOHN SAMONSKY,III; PHONE: 8146766531; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: MATERIAL; CTEST: Null; MED: NO DATA; TMPS: 0; LKPS: 0 | HORIZONTAL FAILURE. LINE C WAS LAID IN 1908. IN 1947 THE PIPE WAS PICKED UP, RECONDITIONED AND PUT BACK IN THE GROUND.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19870154 |  | 1998 | C B GAS GATHERING INC |  | JIM WELLS | TX |  | COMPRESSOR STATION |  | 445 | 1987-08-09 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 33000 | 30548.4721 | 66550.5796 | YES | 1 | 0 |  |  | 125 | 1050 | BY TEST | 2140 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: GATHERING SYSTEM; PRTFL: VALVE; MLKD: OTHER; MLKDO: FLEX HOSE; PRTSY: COMPRESSOR STATION; PRTYR: 1985; NMDIA: 0; THK: 0; SMYS: 0; VALVE: 1" BALL VALVE; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: B.J. BURTON; PHONE: 5128886851; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | SMALL LEAK IN STARTING GAS SYSTEM WHICH POSSIBLY IGNITED FROM ELECTRICAL SYSTEMAND BURNED 125# START GAS HOSE IN HALF TO FEED FIRE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870155 |  | 19323 | TEXAS SOUTHEASTERN GAS CO | WALLER | HARRIS | TX | 77484 |  |  | 1650 | 1987-09-09 | 1 | NO |  |  | TX | Null | NO | RUPTURE | 1 | 0 | 0 | 4000 | 3702.8451 | 8066.7369 | YES | 2 | 20 |  | 19870911 | 380 | 500 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1938; NMDIA: 6; THK: 0.19; SPEC: GRADE B; SMYS: 24000; MANYR: 1938; LOCLK: UNDER GROUND; PNAME: CHARLES WORST, JR.; PHONE: 4098653114; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: SIGN ON POST; STAT: NO; CTEST: Null | PEANUT FARMER HIT OUR PIPELINE WITH HIS HARVESTING MACHINE.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19870157 |  | 405 | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | WEST CAMERON |  | LA |  | X1=1303903.77,Y1=140 | X2=130 | 1100 | 1987-08-20 |  | YES | W.C. | 331 |  | YES | NO | LEAK | 0 | 0 | 0 | 82000 | 75908.3246 | 165368.1068 | Null | 2 | 0 |  | 19870820 | 1000 | 1440 | BY TEST | 2160 | CORROSION | CORROSION | INTERNAL | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1979; NMDIA: 12; THK: 0.38; SPEC: API5L X-52; SMYS: 52000; MANYR: 0; LOCLK: UNDER WATER; PNAME: ROBERT LECZNAR; PHONE: 3134962194; LOC: INTERNALLY; ADESC: NO DATA; CAUCR: NO DATA; COAT: COATED; PROT: YES; CPYR: 1979; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19870158 |  | 602 | ARKLA ENERGY RESOURCES | GURDON | CLARK | AR | 71743 |  | 4987+60 | 110 | 1987-08-13 | 1 | NO |  |  |  | Null | NO | RUPTURE | 0 | 0 | 0 | 70352 | 65125.6396 | 141877.7689 | Null | 1 | 15 |  | 19870813 | 270 | 350 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 0 | 20 | 0.31 | UNKNOWN | 0 | UNKNOWN | N/A | UNKNOWN | 0 | ABOVE GROUND |  | RAYMOND D. GERMANY, MANAGER | 3184292708 | EXTERNALLY | GENERAL CORROSION |  | NO DATA |  | BARE | YES | 0 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | A SECTION OF 20" PIPE IN CREEK CROSSING RUPTURED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870159 |  | 288 | ALGONQUIN GAS TRANSMISSION CO | WESTWOOD | NORFOLK | MA | 02090 | 4.5 TRACT I-1-29 | I-1-12 | 1150 | 1987-09-02 | 3 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 38175 | 35339.0279 | 76986.9204 | Null | 2 | 10 |  | 19870902 | 440 | 750 | BY TEST | 1125 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1952; NMDIA: 12; THK: 0.25; SPEC: API5LX42; SMYS: 42000; SEAM: E.W.; MANU: A.O. SMITH; MANYR: 0; LOCLK: UNDER GROUND; PNAME: J.E. BRUCE; PHONE: 6172544040; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19870902; MARK: YES; MRKTP: PAINT ON GRASS; STAT: YES; CTEST: Null | LINE WITH A FRONT END LOADER, STRUCK AND PUNCTURED THE PIPELINE. THE LOCATION OF THE PIPELINE HAD BEEN ERRONEOUSLY MARKED. LOCATION OF PIPELINE HAD BEEN ERRONEOUSLY MARKED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19870161 |  | 18548 | SOUTHWESTERN GAS PIPELINE INC | EASTLAND | EASTLAND | TX | 76448 | VALVE #2 & #3 |  | 1305 | 1987-08-25 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 251939 | 233222.7729 | 508081.408 | Null | 0 | 25 |  | 19870825 | 235 | 550 | BY TEST | 1200 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1966; NMDIA: 6; THK: 0.16; SPEC: API5LX42; SMYS: 42000; SEAM: ERW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: MICHAEL HOWETH; PHONE: 8173251321; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: METAL SIGNS; STAT: NO; CTEST: Null | WELL SITE BEING CONSTRUCTED BY A PRODUCING COMPANY. DID NOT CALL TO HAVE PIPELINES LOCATED. IGNORED POSTED LINE MARKERS IN THE VICINITY INDICATING PIPELINES ARE PRESENT.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870164 |  | 7605 | HOUSTON PIPELINE CO | ARANSAS |  | TX |  | ACC. #3041 | 385+53 | 1345 | 1987-08-21 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 10000 | 9257.1128 | 20166.8423 | Null | 1 | 45 |  | 19870821 | 20 | 1169 | BY TEST | 1596 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: BLOWDOWN RISER; MLKD: STEEL; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 0; NMDIA: 8; THK: 0.32; SPEC: GR.B; SMYS: 35000; SEAM: SEAMLESS; VALVE: F.X.W #1667; MANU: WALWORTH; MANYR: 1964; LOCLK: ABOVE GROUND; PNAME: FRANK DIEMONT; PHONE: 7138537322; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | DURING THE GAS PURGE OF THE LINE, LIQUID HYDROCARBON SPRAYED FROM THE BLOWDOWN RISER. THE PURGING OPERATION WAS SHUTDOWN IMMEDIATELY BUT ABOUT 10 MINUTES LATERTHE GAS/LIQUID PHASE CAUGHT FIRE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870170 |  | 3230 | DELHI GAS PIPELINE CORP | PECOS |  | TX | 79772 | 11,000' OF EAST HWY | 2052+8 | 1415 | 1987-10-08 | 1 | NO |  |  | TX | Null | NO | LEAK | 0 | 0 | 0 | 9000 | 8331.4015 | 18150.1581 | Null | 0 | 0 |  | 19871008 | 600 | 720 | BY TEST | 1050 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: VALVE; MLKD: STEEL; PRTSY: OTHER; PRTSO: PIPELINE TAP; PRTYR: 1967; NMDIA: 1; THK: 0.19; SMYS: 0; VALVE: 1" GATE VALVE; MANYR: 0; LOCLK: UNDER GROUND; PNAME: ROBERT W. WALKER; PHONE: 9154454971; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | DURING EXCAVATION OF DELHI'S FARM SYSTEM 12" A LEAK WAS DISCOVERED IN THE THREADS OF A 1" PIPELINE TAP. THE LEAK WAS DUE TO EXTERNAL FORCE OF MESQUITE TREE ROOTS WHICH HAD GROWN AROUND THE 1" FITTING AND VALVE. THE TAP WAS INACTIVE AND THEVALVE WAS PLUGGED.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19870171 |  | 2436 | CLAJON GAS CO | LAGRANGE | FAYETTE | TX | 78945 |  |  | 2030 | 1987-10-10 |  | NO |  |  |  | Null | NO | RUPTURE | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 45 |  | 19871010 | 150 | 0 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: GATHERING SYSTEM; PRTFL: OTHER; PRTFO: CARBURATOR; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 0; NMDIA: 0; THK: 0; SPEC: D.N.A.; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: WILLIAM E. WEISER; PHONE: 4095425702; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | PRELIMINARY INDICATIONS POINT TO THE CARBURATION IN THE FUEL SYSTEM.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870172 |  | 10170 | KENTUCKY - WEST VIRGINIA GAS CO | LANGLEY | FLOYD | KY |  |  |  | 930 | 1987-11-04 | 3 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  |  | 82 | 200 | BY TEST | 200 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 0; NMDIA: 16; THK: 0.25; SMYS: 0; MANYR: 0; LOCLK: UNDER GROUND; PNAME: CECIL E. LESTER; PHONE: 6068862312; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: CONSTRUCTION; CAULO: 45DEGREE MITER WELD; CTEST: Null; MED: NO DATA; TMPS: 0; LKPS: 82 | PIPE BROKE IN 45DEGREE MITER WELD.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870173 |  | 5304 | FLORIDA GAS TRANSMISSION CO | MUNSON | SANTA ROSA | FL | 32570 | 260.87 | 37+91 | 1814 | 1987-10-27 | 1 | NO |  |  |  | Null | NO | RUPTURE | 50 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 3 |  | 19871027 | 972 | 975 | BY TEST | 1095 | CORROSION | CORROSION | EXTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1959; NMDIA: 24; THK: 0.31; SMYS: 52000; SEAM: DSAW; MANU: REPUBLIC; MANYR: 0; LOCLK: UNDER GROUND; PNAME: JEFF WHIPPO; PHONE: 7138537322; LOC: EXTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: GALVANIC; COAT: COATED; PROT: YES; CPYR: 1959; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | EXTERNAL CORROSION OVER ABOUT A 15 INCH AREA WITH PITTING AS DEEP AS 0.170" IS THE APPARENT CAUSE OF THE FAILURE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870183 |  | 15007 | PACIFIC GAS & ELECTRIC CO | VALLEJO | SOLANO | CA |  | 28.90 |  | 1032 | 1987-08-28 | 1 | NO |  |  | CA | Null | NO | RUPTURE | 1 | 0 | 0 | 50000 | 46285.5638 | 100834.2115 | Null | 3 | 20 |  | 19870828 | 480 | 675 | BY TEST | 1200 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1961; NMDIA: 24; THK: 3.13; SPEC: APISLX 52; SMYS: 52000; SEAM: DSAW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: J.B. STOUTAMORE; PHONE: 4159733204; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19870827; MARK: YES; MRKTP: FLAGS ON STAKES; STAT: YES; CTEST: Null | CONTRACTOR EXCAVATING FOR NEW SUBDIVISION STRUCK LINE WITH A TRACTOR, ALLOWING GAS TO ESCAPE TO ATMOSPHERE. BUILDINGS WERE EVACUATED AND TRAFFIC REROUTED.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19870184 |  | 18646 | STINGRAY PIPELINE CO | VERMILION |  | LA |  | #1004A-200 | 168,70 | 630 | 1987-09-10 |  | YES | VER. | 247 |  | YES | NO | LEAK | 0 | 0 | 0 | 200000 | 185142.255 | 403336.8458 | Null | 0 | 0 |  | 19870910 | 975 | 1200 | BY TEST | 1861 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: GATHERING SYSTEM; PRTFL: FITTING; PRTFO: 2" PIPE NIPPLE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1974; NMDIA: 2.38; THK: 0.34; SPEC: GR.B ASTM Z-106-1968; SMYS: 35000; MANYR: 0; LOCLK: UNDER WATER; PNAME: J.E. SHEFFIELD; PHONE: 8169682922; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | SHRIMP BOAT WAS REPORTED IN AREA OF DAMAGE AT TIME OF LEAK.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19870186 |  | 19730 | TRUNKLINE GAS CO | THOMPSONVILLE | FRANKLIN | IL |  | 107 GATE+6.9 MILES | 363+19 | 330 | 1987-09-15 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 60000 | 55542.6765 | 121001.0537 | Null | 3 | 30 |  | 19870915 | 850 | 900 | BY TEST | 1250 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1967 | 36 | 0.38 | API -5LX | 60000 | EW |  | BETHLEHEM | 1967 | UNDER GROUND |  | L.R. VALENTINE, SR. | 3172931452 | EXTERNALLY | LOCALIZED PITTING |  | OTHER | LOCALIZED PITTING | COATED | YES | 1967 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | FAILURE OCCURRED IN INACTIVE CORROSIVE BLOTCH.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870190 |  | 17442 | RIO GRANDE VALLEY GAS CO |  | HIDALGO | TX |  | MONTE CHRISTO STAT | MP 72 | 1255 | 1987-08-05 | 1 | NO |  |  | TX | Null | NO | RUPTURE | 0 | 0 | 0 | 40000 | 37028.451 | 80667.3692 | Null | 2 | 0 |  | 19870805 | 503 | 453 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | INTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1927; NMDIA: 12; THK: 0.25; SMYS: 941; SEAM: LAP; MANYR: 0; LOCLK: UNDER GROUND; PNAME: MICHAEL MYERS; PHONE: 5125423531; LOC: INTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: GALVANIC; COAT: NO DATA; PROT: YES; CPYR: 1961; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | OUR INITIAL REPORT STATED THE FAILURE OCCURRED AT 530 PSIG. HOWEVER, ATTACHED IS A COPY OF A PRESSURE CHART TAKEN FROM THE METER STATION JUST UPSTREAM OF THE RELIEF VALVE WHICH IS CALIBRATED IN PSIA. THIS CHART SHOWS THE FAILURE OCCURRED AT518 PSIA. THE DIFFERENCE IN ABSOLUTE AND GAUGE PRESSURE IN HIDALGO COUNTY IS 14.65 WHICH MEANS THE FAILURE OCCURRED AT APPROXIMATELY 503 PSIG. CONSIDERING THE CHART ACCURACY AND THE FACT THAT THE RELIEF VALVE FUNCTIONED PROPERLY DURING THETEST THE MORNING OF THE INCIDENT, WE HAVE CONCLUDED THE FAILURE OCCURRED JUST PRIOR TO THE RELIEF VALVE GOING OPEN.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870196 |  | 13063 | NATIONAL FUEL GAS SUPPLY CORP | JENKS TWP. | FOREST | PA |  | 2700 N. OF VALVE |  | 2050 | 1987-08-24 | 1 | NO |  |  | PA | Null | NO | RUPTURE | 0 | 0 | 0 | 0 | 0 | 0 | Null | 1 | 40 |  | 19870825 | 443 | 485 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1908; NMDIA: 12; THK: 0.33; SMYS: 24000; MANYR: 0; LOCLK: UNDER GROUND; PNAME: JOHN H. SAMONSKY, III; PHONE: 8146766531; LOC: EXTERNALLY; ADESC: GENERAL CORROSION; CAUCR: GALVANIC; COAT: BARE; PROT: NO; CPYR: 0; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | GENERAL CORROSION REDUCED WALL THICKNESS OF PIPE.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19870197 |  | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | MAYFIELD |  | MI |  | 0 |  | 1015 | 1987-10-28 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 2 |  | 19871030 | 100 | 1050 | BY TEST | 2400 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: WILLIS BALL RECEIVER; MLKD: STEEL; PRTSY: OTHER; PRTSO: WILLIS BALL RECEIVER; PRTYR: 1975; NMDIA: 0; THK: 0; SMYS: 0; VALVE: 8"PIG BALL RECE; MANU: WILLIS OIL TOOL; MANYR: 1975; LOCLK: ABOVE GROUND; PNAME: BRUCE NIEMAN; PHONE: 3132566439; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | OPERATOR IN PREPARING TO REMOVE PIG BALL FROM LINE ASSUMED THAT HE COMPLETELY BLEW DOWN RECEIVER. PRESSURE REMAINED IN THE RECEIVER AND THE CAP WAS REMOVED WITH PRESSURE REMAINING IN THE RECIEVER BODY. THE CAP BLEW OFF RESULTING IN INJURY OF TWO COMPANY PERSONNEL. ONE EMPLOYEE WAS RELEASED ON THE DAT OF THE ACCIDENT, THE OTHER WAS HOSPITALIZED UNTIL 10/31/87.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870199 |  | 602 | ARKLA ENERGY RESOURCES | OZARK |  | AR | 72949 |  | 589+39 | 1630 | 1987-10-24 | 1 | NO |  |  |  | Null | NO | RUPTURE | 0 | 0 | 0 | 12150 | 11247.392 | 24502.7134 | Null | 2 | 30 |  | 19871024 | 445 | 550 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1929; NMDIA: 8; THK: 0.19; SMYS: 0; MANYR: 0; LOCLK: UNDER GROUND; PNAME: RAYMOND D. GERMANY,MGR.,ENVIRN.,MENTAL HEALTH & SAFETY; PHONE: 3184292708; LOC: EXTERNALLY; ADESC: GENERAL CORROSION; CAUCR: NO DATA; COAT: COATED; PROT: YES; CPYR: 1961; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | A SECTION OF "8" PIPE RUPTURED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19870200 |  | 4280 | EL PASO NATURAL GAS CO | BLOOMFIELD | SAN JUAN | NM | 87499 |  |  | 1938 | 1987-10-14 | 2 | NO |  |  | NM | Null | NO | OTHER | 0 | 0 | 0 | 500000 | 462855.6375 | 1008342.1145 | Null | 1 | 52 |  | 19871015 | 0 | 0 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: TURBINE CONTROL CAB; MLKD: OTHER; MLKDO: VARIOUS MATERIALS; PRTSY: COMPRESSOR STATION; PRTYR: 1971; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: RICHARD FAVILA,STANDARDS ENGINEER; PHONE: 9155412062; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | ON WEDNESDAY, OCTOBER 14, 1987, AT 7:30 P.M. THE BLANCO "C" #2 TURBINE CONTROL CAB EXPLODED, WRECKING THE CONTROL SYSTEM WIRING, THE UNIT MOTOR FROM VARIOUS SYSTEM COMPONENTS RESULTED IN AN UNCONTROLLED LEAKAGE OF GAS FROM THE COMPRESSOR CASE THROUGH THE SEAL OIL SYSTEM INTO THE LUBRICATION OIL RESERVOIR UNDERNEATH THE ACCESSORY CAB WHERE GAS MIGRATED INTO THE CONTROL CAB AND IGNITED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19870204 |  | 19570 | TRANSCO GAS PIPELINE CORP | BRAZOS | GULF OF MEXICO | TX |  | 6.77 | 357+46 | 1000 | 1987-10-22 |  | YES | BRAZOS | A-23 |  | YES | NO | RUPTURE | 0.33 | 0 | 0 | 66700 | 61744.942 | 134512.8381 | Null | 0 | 10 |  | 19871023 | 950 | 1440 | BY TEST | 1980 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: WELD-O-LET; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1983; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: UNDER WATER; PNAME: B.R.LANDES,SR.,COMPLIANCE ANALYST; PHONE: 7134392001; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | A LARGE TRAWLING NET AND CABLES WERE FOUND WRAPPED AROUND A 2" TAP VALVE. IT IS ASSUMED THAT THE NET WAS DRAGGED ACROSS THE PIPELINE AND DISLODGED THE 2" VALVE AND WELD-O-LET.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870209 |  | 2669 | COMMONWEALTH GAS PIPELINE CORP |  | SUFFOLK | VA | 23434 |  | 2709+0 | 835 | 1987-11-18 | 1 | NO |  |  |  | Null | NO | RUPTURE | 0 | 0 | 0 | 5000 | 4628.5564 | 10083.4211 | YES | 0 | 30 |  | 19871118 | 520 | 600 | BY TEST | 955 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1950; NMDIA: 12; THK: 0.25; SPEC: API-5LX GRADE X42; SMYS: 1647; SEAM: ERW; MANU: YOUNGSTOWN; MANYR: 1950; LOCLK: UNDER GROUND; PNAME: WAYNE C. HILDRETH,VP,OPERATIONS; PHONE: 8043235351; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: 9"X12"SIGNS; STAT: YES; CTEST: Null | FAILURE OCCURED WHILE D-6 DOZER WAS BEING OPERATED OVER THE PIPELINE. PIPE MAYHAVE BEEN HIT BY TRACK CLEAT.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19870212 |  | 2616 | COLUMBIA GAS TRANSMISSION CORP |  | FLOYD | KY |  |  | 197+92 | 1440 | 1987-10-27 | 1 | NO |  |  | KY | Null | NO | LEAK | 0 | 0 | 4 | 0 | 0 | 0 | Null | 0 | 20 |  | 19871027 | 286 | 374 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: MECHANICAL JOINT; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1931; NMDIA: 20; THK: 0.31; SMYS: 0; MANYR: 0; LOCLK: UNDER GROUND; PNAME: A.S.BECKETT,SUPERVISOR ENGINEER; PHONE: 3043572753; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | A CONTRACTOR'S CONSTRUCTION CREW WAS REMOVING COVER FROM THE LINE.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19870216 |  | 405 | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | GALVESTON |  | TX |  | X=3373465 | 43042 | 1200 | 1987-11-02 |  | YES | GALVESTON BLOCK | 245 |  | YES | NO | LEAK | 0 | 0 | 0 | 500000 | 462855.6375 | 1008342.1145 | Null | 0 | 0 |  | 19871102 | 1300 | 1440 | BY TEST | 2160 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1987; NMDIA: 10; THK: 0.44; SPEC: API-5LX; SMYS: 42000; MANYR: 0; LOCLK: UNDER WATER; PNAME: ROBERT J. LECZNAR,MGR.CODES STDS&PROC.; PHONE: 3134962456; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null
2021-02-26 10:36 | YES | YES |  | 19870217 |  | 13845 | NORTHWEST PIPELINE CORP | OPAL | LINCOLN | WY | 83124 |  |  | 933 | 1987-11-06 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 4 | 0 | 0 | 0 | Null | 0 | 10 |  | 19871106 | 0 | 792 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: NO DATA; PRTFL: NO DATA; MLKD: NO DATA; PRTSY: OTHER; PRTSO: GASOLINE PLANT; PRTYR: 1958; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: MYRLE B. ANDERSON,COMPLIANCE SPEC.,; PHONE: 8015846906; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | PROJECTS WERE NEARING COMPLETION TO REPLACE THE CONCRETE FOUNDATIONS AND INSTALLNEW PULSATION BOTTLES ON THE TWO REFRIGERATION COMPRESSORS, #1 CLARK AND #2 CLARK. A SCHEDULED, ONE DAY MAINTENANCE SHUT DOWN OF THE OIL PLANT BEGAN A 6:45AMON NOVEMBER 6,1987. NORTHWEST PIPELINE EMPLOYEES WERE PERFORMING MAINTENANCE ON THE #2 CLARK. TWO CONTRACTORS, ARROW INDUSTRIES, INC. AND ITS SUBCONTRACTOR TED MILLER CO., INC. WERE FINISHING WORK ON THE #1 CLARK. THEIR WORK INCLUDED POURING A GROUT CAP UNDER THE #1 CLARK AND REINSTALLING BLOCK VALVES IN THE BASEMENT OF THE #1 CLARK. AT 9:33AM, GAS RELEASED BY A SPARK FROM A VACCUM CLEANER NEAR THE BASEMENT. THE RESULTING FLASH FIRE INJURED SIX PERSONS, FOUR REQUIRING HOSPITALIZATION, AND MINOR DAMAGE TO THE BUILDING AND EQUIPMENT. ONE OF THE INJURED IS STILL HOSPITALIZED. THE MAIN FIRE WAS TWO INITIAL FLASHES THAT LASTED JUST SECONDS. ALL THE INJURIES OCCURRED DURING THESE FIRST FEW SECONDS. OTHER, SMALLER FIRES WERE EXTINGUISHED BY PLANT PERSONNEL WITHIN A FEW MINUTES. THE SOURCE OF THE GAS IS UNDER INVESTIGATION, BUT THOUGHT TO BE FROM LINES THAT WERE HABING BLINDS REPLACED BY VALVES FOLLOWING CONSTRUCTION WORK.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19870225 |  | 21031 | VALERO TRANSMISSION CO | CORPUS CHRISTI | NUECES | TX |  | M.P. 1 | 500+00 | 800 | 1987-11-03 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 10000 | 9257.1128 | 20166.8423 | Null | 0 | 0 |  | 19871104 | 600 | 712 | BY TEST | 1220 | CORROSION | CORROSION | EXTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1966; NMDIA: 16; THK: 0.22; SPEC: API 5LX52; SMYS: 1424; SEAM: ERW; MANYR: 0; LOCLK: UNDER PAVEMENT; PNAME: TERRY EARLEY/MANAGER OF CODES&RECORDS; PHONE: 5122462395; LOC: EXTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: GALVANIC; COAT: COATED; PROT: YES; CPYR: 0; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | AN EXTERNAL CORROSION PIT DEVELOPED IN THE CARRIER PIPE LOCATED INSIDE A CASING. LEAK WAS IN AN AREA OF DAMAGED COATING. THE PIPELINE WASA TAKEN OUT OF SERVIOCE AND A NEW SECTION OF PIPE WAS INSTALLED IN THE EXISTING CASING.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880001 |  | 10030 | KN ENERGY INC (KANSAS NEBRASKA NATURAL GAS CO INC) |  | SHERIDAN | NE | 69347 |  | 1191+4 | 850 | 1988-01-13 | 1 | NO |  |  |  | Null | NO | LEAK | 0.5 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 10 |  | 19880113 | 480 | 725 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1960; NMDIA: 4.5; THK: 0.16; SPEC: GRADE B; SMYS: 35000; SEAM: ERW; VALVE: N/A; MANU: REPUBLIC; MANYR: 1960; LOCLK: ABOVE GROUND; PNAME: A.T.MCMASTER,DIRECTOR-PIPELINE; PHONE: 4024622141; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: LINE MARKER; STAT: NO; CTEST: Null | THE ATTACHED INCIDENT REPORT COVERS A LEAK THAT OCCURRED ON K N ENERGY, INC.'S (K N'S) 4-INCH TOP-OF-GROUND TRANMISSION PIPELINE IN SHERIDAN COUNTY, NEBRASKA ON JANUARY 13, 1988. IGNITION DID NOT OCCUR AND THERE WERE NO INJURIES OR FATALITIES AS A RESULT OF THE LEAK. SERVICE WAS TEMPORARILY INTERRUPTED TO 109 DOMESTIC AND 13 COMMERCIAL CUSTOMERS IN THE COMMUNITY OF GORDON, NEBRASKA AND ON THE RURAL ROUTES.THE LEAK WAS CAUSED BY AN OUTSIDE PARTY OPERATING SNOW REMOVAL EQUIPMEWNT. THEDAMAGED PROTION OF THE PIPELINE IS IN A CLASS I LOCATION AND WAS MARKED WITH PERMANENT LINE MARKERS. THE DAMAGED PORTION WAS PART OF A PIPELINE PATROL CONDUCTED ON APRIL 15, 1987. A PERMANENT REPAIR WAS ACCOMPLISHED BY REPLACING 20 FEET OF THE DAMAGED PIPELINE WITH PRETESTED PIPE OF EQUAL OR GREATER SPECIFICATIONS.TELEPHONIC REPORT OF THE ABOVE LEAK WAS TRANSMITTED TO ENSIGN CHERRY OF THE DEPARTMENT OF TRANSPORTATION AND TO MARGARET HARDER WITH THE NEBRASKA STATE FIRE MARSHAL'S DISTRICT OFFICE AT NORTH PLATTE, NEBRASKA AT 11:50 A.M. CDT ON JANUARY 13, 1988. UPDATED TELEPHONIC REPORTS WERE TRANSMITTED TO THE NEBRASKA STATE FIREMARSHAL'S OFFICE AT 3:30 P.M. CDT ON JANUARY 14, 1988 AND TO DOT AT 3:15 P.M. ON THE SAME DATE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880002 |  | 4510 | EQUITABLE GAS CO | SKIN CREEK STORAGE POOL | LEWIS | WV | 26452 | N/A | 14+12 | 2130 | 1987-12-05 | 1 | NO |  |  | WV | Null | YES | RUPTURE | 0 | 0 | 0 | 128000 | 118491.0432 | 258135.5813 | Null | 36 | 0 |  | 19871208 | 925 | 1000 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: OXY-ACETYLENE-BUTTWELD; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1950; NMDIA: 8; THK: 0.32; SPEC: N/A; SMYS: 24000; SEAM: N/A; VALVE: N/A; MANU: N/A; MANYR: 1936; LOCLK: UNDER GROUND; PNAME: E.F.MOSES,JR.,MANAGER-TECH.SERV.DEPT.; PHONE: 4125335340; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | CONTRACTOR CUT GAS SERVICE LINE WHILE TRENCHING TO INSTALL ELECTRIC CABLE. GASIGNITYED AND DESTROYED THE TRENCHING MACHINE. ( NO SECOND COPY).GE FIELD POOL LOCATED IN THE STONEWALL JACKSON LAKE PROJECT, LEWIS COUNTY, WESTVIRGINIA. THIS PROJECT IS UNDER THE AUSPICES OF THE U.S. ARMY CORPS OFF ENGINEERS, OHIO RIVER DIVISION. NATURAL GAS BLEW FOR APPROXIMATELY THIRTY-SIX HOURS UNTIL IT WAS DISCOVERED AT 0930 HOURS ON DECEMBER 7, 1987, AT WHICH TIME THE STORAGE POOL WAS SHUT-IN.A PRESSURE TRANSMITTER RELAYED THE PRESSURED DROP AT THE COPLEY RUN COMPRESSOR STATION LOCATED APPROXIMATELY FOUR MILES FROM THE RUPTURE. THE TWO OPERATING UNITS AND DEPARTMENT DIRECTLY INVOLVED TRANSPORTATION OPERATIONS, TRANSMISSION DEPARTMENT AND THE GAS CONTROL DEPARTMENT.INTERDEPARTMENTAL INVESTIGATION AND DISCUSSIONS ENSUED IMMEDIATELY AFTER DISCOVERY OF THE PRESSURE DROP. IT WAS ERRONEOUSLY DECIDED, AT THAT TIME, THAT THE PRESSURE DROP WAS DUE TO A FAULTY PRESSURE TRANSMITTER. THIS TRANSMITTER HAS HAD A HISTORY OF OPERATION AND MAINTENANCE PROBLEMS AND WAS SCHEDULED TO BE REPLACED.OTHER FACTORS CONTRIBUTING TO THE EXTENDED RESPONSE TIME WERE:1. REMOTE LOCATION. SINCE THE RUPTURE IS LOCATED IN A U.S. GOVERNMENT CONTROLLED AREA, THERE WERE NO PUBLIC ROADS OPEN OR HOUSES IN THE GENERAL VICINITY - NO ONE COULD HEAR OR SEE THE ESCAPING NATURAL GAS.2. THE NATURAL GAS DIDNOT IGNITE.3. THE RUPTURE OCCURED IN THE EVENING DURING THE MIDDLE OF THE WEEDEND. THERE WERE NO EQUITABLE PERSONNEL NOR DAM CONSTRUCTION WORKERS IN THE AREA TO HEAR OR WITNESS THE ESCAPING NATURAL GAS. ALSO, SINCE DEER HUNTING SEASON CLOSED THE EVENING OF DECEMBER 5, 1987, THERE WERE NO HUNTERS IN THE AREA.4. THE CAUSE OF THE WELD FAILURE IS CURRENTLY UNDER INVESTIGATION. ALL OXY-ACETYLENE WELDED PIPE IN THE SKIN CREEK STORAGE POOL IS SCHEDULED TO BE REPLACED ASSOON AS POSSIBLE.CONSTRUCTION IS CURRENTLY UNDERWAY TO REPLACE ALL OXY-ACETYLENE PIPE IN THE POOL. FURTHER, AN INVESTIGATIVE TASK FORCE HAS ALREADY SUBMITTED APRELIMINARY REPORT ON THE INCIDENT AND ADDITIONAL, INTERNAL RECOMMENDATIONS WILL BE FORTHCOMING PROMPTLY.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19880005 |  | 14210 | OKLAHOMA NATURAL GAS CO | MCCURTAIN,HASKELL |  | OK | 74944 |  |  | 1145 | 1987-12-04 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 25549 | 23650.9974 | 51524.2654 | YES | 1 | 10 |  | 19871204 | 450 | 800 | BY TEST | 900 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1965; NMDIA: 6; THK: 0.16; SPEC: API 5L; SMYS: 35000; SEAM: EW; MANU: LONE STAR; MANYR: 1965; LOCLK: UNDER GROUND; PNAME: JAMES M. WOOD, CHIEF ENGINEER; PHONE: 9185887600; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: LINE MARKERS; STAT: YES; CTEST: Null | COUNTY CUTTING NEW ROAD PUNCTURED GAS LINE. GRADER BURNED. OPERATOR WAS TREATED AND RELEASED FROM LOCAL HOSPITAL.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880006 |  | 4070 | EAST TENNESSEE NATURAL GAS CO | SEYMOUR | SEVIER | TN | 37865 | 3301-1-12.278 | 650+42 | 1040 | 1987-12-14 | 3 | NO |  |  |  | Null | NO | RUPTURE | 1.08 | 0 | 0 | 25000 | 23142.7819 | 50417.1057 | Null | 1 | 45 |  |  | 500 | 640 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1953; NMDIA: 16; THK: 0.25; SPEC: API-5LX-X42; SMYS: 42000; SEAM: ERW; VALVE: N/A; MANU: YOUNGSTOWN PIPE; MANYR: 0; LOCLK: UNDER GROUND; PNAME: A. CREECH NEWSOME, JR., ASST. CHIEF ENGR.; PHONE: 6156946344; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PIPELINE MARKERS; STAT: YES; CTEST: Null | PROPERTY OWNER THOUGHT THE PIPELINE WAS DEEPER AND FAILED TO FOREWARN THE BULLDOZER OPERATOR OF THE EXISTENCE OFTHE PIPELINE. EXISTING STRUCTURE COUSING NATURAL GAS TO BLOW INTO CELLAR AREA AND EVENTURALLY WAS IGNITED AND EXPLODED. THE GAS COMPANY WAS NOTIFIED BY SOUTH HADLEY POLICE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880009 |  | 15931 | PUBLIC SERVICE CO OF COLORADO |  | ADAMS | CO | 80239 | N/A | SW1/4 | 245 | 1987-12-14 | 1 | NO |  |  | CO | Null | NO | RUPTURE | 0.25 | 0 | 0 | 102000 | 94422.5501 | 205701.7914 | Null | 2 | 15 |  | 19871214 | 265 | 1000 | BY TEST | 1500 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | FITTING | 1/2" NIPPLE-3"LONG | STEEL |  | REGULATOR/METERING SYSTEM |  | 1987 | 0.5 | 0.15 | ASTM A-120 | 25000 | FURNACE WELDED | N/A | UNKNOWN | 0 | ABOVE GROUND |  | MARK NOLAN - ENGINEER | 3035713750 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | 1/2" NIPPLE - 3" LONG | NO |  | NO DATA | 0 | 0 | 0 | 1/2" NIPPLE USED FOR PRESSURE TAP BROKE AT PIPE THREADS BELOW VALVE. ESCAPING GAS WAS IGNITED BY AN UNKNOWN SOURCE RESULTING IN A FIRE THAT DESTROYED THE REGULATOR/METER STATION. CAUSE OF RUPTURE AND FIRE IS UNDER INVESTIGATION.PART C- 1/2" NIPPLE CRACKED AND BROKE AT PIPE THREAD. THE CAUSED OF FAILURE ISUNDER INVESTIGATION. NIPPLE WAS INSTALLED IN PRE-TESTED, FABRICATED STATION PIPING AFTER FIELD INSTALLATION.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19880011 |  | 4904 | EXXON CO USA | PASADENA | HARRIS | TX |  |  |  | 1625 | 1987-12-11 | 3 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 35 |  | 19871214 | 800 | 910 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1952 | 0.12 | 0.25 | N/A | 0 | N/A |  | N/A | 0 | UNDER GROUND |  | JACK A. RICKNER, REGULATORY TECHNICIAN | 7750006132 | INTERNALLY | LOCALIZED PITTING |  | OTHER | BACTERIAL ACTION (SRB'S) | COATED | YES | 1969 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | INTERNAL CORROSION CAUSED BY SULFATE REDUCING BACTERIAL GROWTH.PART A- A CONTINUOUS CORROSION INHIBITOR INJECTION PROGRAM IS CURRENTLY IN PLACE. THIS PROGRAM WILL BE MIDIFIED TO INCLUDE BACTERIAL BATCH TREATMENT.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19880012 |  | 2436 | CLAJON GAS CO | WEST OF SOMERVILLE | BURLESON | TX |  |  |  | 1730 | 1988-01-09 | 1 | NO |  |  |  | Null | Null | RUPTURE | 0 | 0 | 0 | 500 | 448.3668 | 976.7778 | YES | 11 | 15 |  | 19880109 | 30 | 30 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: GATHERING SYSTEM; PRTFL: OTHER; PRTFO: TUBING; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1980; NMDIA: 0.38; THK: 0; SPEC: CADIUM PLATED STL.; SMYS: 0; SEAM: TUBING; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: WILLIAM E. WEISER D.O.T. SPECIALIST; PHONE: 4095425702; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | VIBRATION OF TUBING CAUSED METAL FATIGUE & BREAKAGE IN SUPPLY TUBING & WAS IGNIGHTED BY FIRE IN REBOILER
2021-02-26 10:36 | NO | NO |  | 19880013 |  | 2564 | COLORADO INTERSTATE GAS CO | EAST OF FORGAN | BEAVER | OK | 73982 | MOCANE COMPRESSOR ST |  | 620 | 1988-01-09 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 30 |  | 19880111 | 0 | 0 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: NO DATA; PRTFL: VALVE; MLKD: STEEL; PRTSY: OTHER; PRTYR: 0; NMDIA: 0; THK: 0; SMYS: 0; VALVE: FISHER 102; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: RICHARD H. FLINT II, STAFF ENG.; PHONE: 3035204350; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | ICE BUILD-UP ON THE OFFICE BUILDING WALL PLUGGED THE VENT ON THE REGULATOR SUPPPLYING GAS TO THE BUILDING (HEAT & HOT WATER). 26.7 PSIG GAS WENT TO THE FURNACE& HOT WATER HEATER, RESULTING IN AN EXPLOSION WHICH DESTROYED THE 33' X 58' SINGLE STORY BUILDING. THERE WERE NO PERSONNEL IN THE BUILDING AT THE TIME OF THE EXPLOSION.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19880024 |  | 15083 | PALO DURO PIPELINE CO | WHEELER | WHEELER | TX | 79096 | 4.06 | 214+55 | 1610 | 1987-12-30 | 1 | NO |  |  |  | Null | NO | RUPTURE | 16 | 0 | 0 | 36000 | 33325.6059 | 72600.6322 | YES | 0 | 10 |  | 19871230 | 100 | 1170 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1979; NMDIA: 16; THK: 0.25; SPEC: API-5LX-52; SMYS: 1625; SEAM: ERW; VALVE: N/A; MANU: U.S.STEEL; MANYR: 1979; LOCLK: UNDER GROUND; PNAME: RONALD WELLS/COORDINATOR; PHONE: 7132295737; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | PIPELINE RUPTURED AT 100 PSIG WHILE BEING PRESSURED UP AFTER TIE-IN SHUTDOWN ATWHEELER COMPRESSOR STATION II.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880033 |  | 13120 | NATURAL GAS PIPELINE CO OF AMERICA | HOFFMAN | CLINTON | IL | 62250 | 986 | 52066+ | 1730 | 1987-12-23 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 160000 | 148113.804 | 322669.4766 | Null | 6 | 35 |  | 19871223 | 805 | 858 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: BRANCH CONNECTION; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1966; NMDIA: 30; THK: 0.34; SPEC: 5LX; SMYS: 52000; SEAM: ELECTRIC FLASH; MANU: A.O.SMITH; MANYR: 1950; LOCLK: UNDER GROUND; PNAME: W.V.LEBAN, ENGINEER; PHONE: 3126913171; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | PENDING METALLURGICAL ANALYSIS OF FAILED SECTION. FRACTURE OCCURRED AT A WELD CONNECTING AN 8" X 30" SADDLE TO A REINFORCING SLEEVE OF A BRANCH CONNECTION ASSEMBLY
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19880043 |  | 5304 | FLORIDA GAS TRANSMISSION CO | EUNICE | ACADIA | LA | 70535 | M.P. 475.4 | N/A | 1400 | 1987-07-24 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 1 |  |  | 0 | 0 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: NO DATA; MLKD: NO DATA; PRTSY: COMPRESSOR STATION; PRTYR: 1960; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: JEFF WHIPPO, COMPLIANCE ENGINEER; PHONE: 7138537322; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | TWO CONTRACTOR EMPLOYEES WORKING WITH A TORCH WERE BURNED WHEN THEIR TORCH IGNITED GAS VENTING FROM A SCRUBBER WASTE STORAGE TANK'S VENT LINE AT FGT'S COMPRESSOR STATION..
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880059 |  | 2616 | COLUMBIA GAS TRANSMISSION CORP | BUSHKILL LEHMAN TOWNSHIP | PIKE | PA | 18324 | N/A | 6443+ | 410 | 1988-01-05 | 3 | NO |  |  | PA | Null | NO | RUPTURE | 20 | 0 | 0 | 150000 | 134510.0374 | 293033.3447 | Null | 2 | 30 |  | 19880105 | 1100 | 1203 | BY TEST | 1868 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1947 | 14 | 0.31 | API 5LK | 45000 | SEAMLESS | N/A | NATIONAL TUBE - USS | 1947 | UNDER GROUND |  | A.S.BECKETT, SUPERVISORY ENGINEER | 3043572767 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | BARE | YES | 1970 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880060 |  | 13063 | NATIONAL FUEL GAS SUPPLY CORP | MIX RUN GIBSON TOWNSHIP | CAMERON | PA |  |  | 113953 | 155 | 1988-01-27 | 1 | NO |  |  | PA | Null | NO | RUPTURE | 0 | 0 | 0 | 0 | 0 | 0 | Null | 3 | 35 |  |  | 490 | 660 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1953 | 12 | 0.31 | N/A | 24000 | SEAMLESS | N/A | NATIONAL TUBE | 1953 | UNDER GROUND |  | JOHN H. SAMONSKY, III, SUPERINTENDENT | 8146766531 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL |  | NO |  | NO DATA | 0 | 0 | 0 | NO REMARKS GIVEN.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880063 |  | 15329 | PEOPLES GAS LIGHT & COKE CO | CHICAGO | COOK | IL | 60617 |  |  | 1815 | 1988-01-09 | 3 | NO |  |  |  | Null | NO | RUPTURE | 40 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 2 |  | 19880109 | 270 | 287 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1961 | 16 | 0.38 | API 5L GRADE B | 35000 |  |  | UNKNOWN | 0 | ABOVE GROUND |  | G.F. ARMSTRONG, SUPT. CODES, STDS., & PLANT | 3124314713 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL |  | YES | 19610101 | WATER | 0 | 0 | 700 | FOR UNKNOWN REASONS, A SEGMENT OF H.P. STEEL PIPE EXPOSED ON A STRUCTURE OVER R.R. TRACKS, RUPTURED. THE PIPELINE SUPPLIES TWO LARGE CUSTOMERS. THE ONE SUPPLYTO THIS LINE CONTAINS AN AUTOMATIC VALVE WHICH COLSED AND SHUT OFF THE FOW OF GAS. THE GAS DID NOT IGNITE AND THERE WERE NO INJURIES. PRELIMINARY RESULTS FROM METALURGICAL EXAMINATIONS INDICATE THAT THE SECTION OF PIPE IN QUESTION HAS A HIGHER THAN SPECIFICATION CARBON CNTENT.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880067 |  | 20245 | UNITED TEXAS TRANSMISSION CO | LAKE JACKSON | BRAZORIA | TX | 77566 | 36.05 | 1903+ | 1600 | 1988-01-12 | 3 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 75000 | 67255.0187 | 146516.6723 | Null | 3 | 55 |  | 19880112 | 367 | 525 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1951; NMDIA: 20; THK: 0.25; SPEC: API-5LX-46; SMYS: 1150; SEAM: ERW; VALVE: N; MANU: YOUNGSTOWN; MANYR: 0; LOCLK: UNDER GROUND; PNAME: RON WELLS, COORDINATOR; PHONE: 7132295737; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19870917; MARK: YES; MRKTP: PIPELINE MARKER; STAT: NO; CTEST: Null | AFTER ISOLATING THE LINE, WE DUG UP THE PIPELINE LEAK AND OBSERVED A 3 FT. GOUGE AT APPROXIMATELY 11:00 ON THE DOW 20" LINE, APPARENTLY CAUSED BY A THIRD PARTYCONTRACTOR WORKING OVER OUR PIPELINE SYSTEM. A 4"X1/8" PORTION OF THE 3 FT. GOUGE ACTUALLY PENETRATED THE PIPELINE, CAUSING NTRUAL GAS TO ESCAPE. UNITED TEXAS IS PRESENTLY CONDUCTING AN INVESTIGATION INTO THE EVENTS SURROUNDING THIS LEAK.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880068 |  | 19160 | TENNESSEE GAS PIPELINE CO |  | CAMERON | LA |  | 507C-103+2.87 | 151+51 | 1400 | 1988-01-14 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 130000 | 116575.3658 | 253962.2321 | Null | 12 | 30 |  |  | 760 | 1140 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | LONGITUDINAL | STEEL |  | PIPELINE |  | 1956 | 20 | 0.38 | API 5LX | 52000 | DOUBLE SUB.ARC |  | CONSOLIDATED | 1955 | OTHER | MARSH | RICHARD A. WINN - ANALYST | 7137572581 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL |  | NO |  | NO DATA |  | 0 | 0
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19880069 |  | 456 | AMOCO GAS CO | WINNIE | CHAMBERS | TX |  |  | 2151+7 | 1100 | 1988-01-27 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 5850 | 5245.8915 | 11428.3004 | Null | 11 | 0 |  | 19880128 | 550 | 788 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | GATHERING SYSTEM | FITTING | FLANGE BOLTS | STEEL |  | OTHER | TAP VALVE | 1952 | 0 | 0 |  | 0 |  |  |  | 0 | OTHER | PASTURELAND | D.E.KOONS, SAFETY ENGINEER | 4099424920 | EXTERNALLY | GENERAL CORROSION |  | NO DATA |  | COATED | NO | 0 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | BOLTS CONNECTING A 2" TAP VALVE TO 16" TRANSMISSION LINE HAD DETERIORATED AND ALEAK HAD OCCURRED.MAIN LINE UNDER CATHODIC PROTECTION. TAP VALVE LINE WAS NOT ON IDLE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880077 |  | 5304 | FLORIDA GAS TRANSMISSION CO | LARGO, | PINELLAS | FL | 33542 | M.P. 100.7 | 5319+5 | 1445 | 1988-01-19 | 3 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 250000 | 224183.3957 | 488388.9078 | Null | 0 | 30 |  | 19880202 | 600 | 713 | BY TEST | 1061 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1959; NMDIA: 10; THK: 0.22; SPEC: API-5L; SMYS: 35000; MANYR: 0; LOCLK: UNDER GROUND; PNAME: JEFF WHIPPO, COMPLIANCE ENGINEER; PHONE: 7138537322; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: LINE MARKER & STAKE.; STAT: YES; CTEST: Null | THE ENCLOSED INCIDENT REPORT FOR FLORIDA GAS TRANSMISSION CO. DESCRIBES A DIG-IN BY AN OUTSIDE PARTY WHICH OCCURRED JANUARY 19, 1988. AT TRHE TIME OF OCCURRENCE THIS APPEARED NOT TO BE REPORTABLE NOTIFIED ONJANUARY 19, 1988 AS A COURTESY.AS COSTS OF MAKING A PERMANENT REPAIR ACCRUED AND THE ESTIMATED GAS LOSS WAS CALCULATED, IT BECAME APPARENT THAT THE $50,000 CRITERIA HAD BEEN EXCEEDED. TELEPHONIC NOTICE TO THE NATIONAL RESPONSE CENTER WAS MADE FOLOWING THIS DTERMINATION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880079 |  | 1734 | BRIDGELINE GAS DISTRIBUTION CO | TAFT | ST CHARLES | LA | 70066 | APPROX. STA.550+00 |  | 1400 | 1988-02-11 | 1 | NO |  |  | LA | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19880211 | 450 | 860 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: UNKNOWN; MLKD: STEEL; PRTSY: PIPELINE; PRTSO: RIVER CROSSING; PRTYR: 1962; NMDIA: 18; THK: 0.73; SPEC: API-5L-GR.B; SMYS: 35000; SEAM: N/A; VALVE: N/A; MANU: UNKNOWN; MANYR: 0; LOCLK: UNDER WATER; PNAME: A.M.SIMMERS-CODES& REG. COORD.; PHONE: 5045951605; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | THE SEGMENT THAT FAILED WAS IN A CROSSING OF THE MISSISSIPPI RIVER. THE SEGMENTWAS ISOLATED WITH APPROXIMATELY 450 PSIG PRESSURE WHEN FAILURE OCCURRED. NO INSPECTION OF THE LINE TO DETERMINE CAUSE OF FAILURE IS POSSIBLE UNTIL THE RIVER REACHES A LOWER STAGE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880080 |  | 13845 | NORTHWEST PIPELINE CORP | RANGELY | GARFIELD | CO |  | 246.67 MAINLINE | 13024+ | 800 | 1988-02-08 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 87000 | 78015.8217 | 169959.3399 | Null | 10 | 0 |  | 19880211 | 720 | 809 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: LONG;AT BUCKLE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1983; NMDIA: 26; THK: 0.34; SPEC: API 5LX X52; SMYS: 1396; SEAM: DSA; MANU: KAISER STEEL; MANYR: 1980; LOCLK: UNDER GROUND; PNAME: MYRLE B. ANDERSON, COMPLIANCE SPEC.; PHONE: 8015846908; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | THE DELAY IN TELEPHONIC REPORTING WAS DUE TO ORIGINAL COST ESTIMATE BEING LESS THAN $50,000.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880084 |  | 4060 | EAST OHIO GAS CO | RICHFIELD TWP., | SUMMIT | OH | 44286 |  | 39+70+ | 1440 | 1988-01-07 | 2 | NO |  |  | OH | Null | NO | RUPTURE | 52 | 0 | 0 | 90000 | 80706.0225 | 175820.0068 | Null | 0 | 25 |  | 19880107 | 450 | 650 | BY TEST | 826 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1958; NMDIA: 30; THK: 0.31; SPEC: API 5LX X52; SMYS: 1083; SEAM: SUBMERGED ARC; VALVE: N/A; MANU: REPUBLIC STEEL; MANYR: 1958; LOCLK: UNDER GROUND; PNAME: PAUL E. OLEKSA-ENVIR. & CODES ENGINEER; PHONE: 2164326858; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880085 |  | 19235 | TEXAS EASTERN GAS PIPELINE CO | LILLY | CAMBRIA | PA | 15939 | 54.84 | N/A | 2345 | 1988-01-23 | 1 | NO |  |  | PA | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 1 |  | 19880124 | 0 | 0 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: UN INVESTIGATION; MLKD: OTHER; MLKDO: UNDER INVESTIGATION; PRTSY: COMPRESSOR STATION; PRTYR: 0; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: R.E. THOMURE - COMPLIANCE & STDS; PHONE: 7137593131; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | THE INCIDENT CONSISTED OF A LUBRICATING OIL FIRE IN A TURINE UNIT AT THE COMPRESSOR STATION. THE CAUSE OF THE INCIDENT IS UNDER INVESTIGATION.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19880087 |  | 405 | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | TROY TOWNSHIP | WILL | IL |  | M.P. 816.77 |  | 2230 | 1988-02-21 | 1 | NO |  |  | IL | Null | NO | OTHER | 0 | 1 | 0 | 750000 | 672550.1871 | 1465166.7234 | Null | 1 | 30 |  | 19880222 | 832 | 850 | BY TEST | 1900 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: FLANGED JOINTS; MLKD: NO DATA; PRTSY: NO DATA; PRTYR: 0; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: ROBERT J. LECZNAR, MGR., C.S.&P.; PHONE: 3134962456; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | A RUNAWAY 18-WHEELED SEMI STRUCK AND DISLODGED TWO ABOVEDGROUND 12" FLANGED JOINTS AND IGNITED ESCAPING GAS. THE FIE CAUSED A SECONDARY PIPELINE FAILURE. A HOUSE LOCATED APPROXIMATELY 165' FROM TH FIE CENTER, CAUGHT FIRE AND WAS DESTROYED. THE DRIVER OF THE TRUCK DIED, BUT WE DO NOT KNOW WHETHER THIS OCCURRED BEFORE OR AT THE TIME OF THE ACCIDENT.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880095 |  | 15823 | POWER TEX JOINT VENTURE | LUBBOCK | LUBBOCK | TX | 79401 | 0+00 PLANT YARD |  | 440 | 1988-03-11 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 100000 | 89673.3583 | 195355.5631 | Null | 1 | 5 |  | 19880311 | 305 | 1000 | BY TEST | 1500 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: REGULATOR; MLKD: NO DATA; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1984; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: HAROLD PAULK, PIPELINE FOREMAN; PHONE: 8067990569; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | PRESSURE REGULATOR THAT IS PILOT OPERATED FAILED OPEN DUE TO THE FAILURE IN A DIAPHRAM IN THE CONTROL PILOT AND THUS CAUSE TEH DOWNSTREAM RELIEF VALVE TO GO OFF. A FIRE WAS STARTED BY STATIC ELECTRICITY OR SOME FOREIGN MATTER MOVING THROUGH THE RELIEF AND STRIKING METAL TO CAUSE A SPARK.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880097 |  | 2714 | CONSOLIDATED GAS TRANSMISSION CORP | CABIN CREEK, | KANAWHA | WV | 25130 |  | 268+28 | 1315 | 1988-03-11 | 1 | NO |  |  | WV | Null | NO | RUPTURE | 2.5 | 0 | 0 | 189600 | 170020.6873 | 370394.1477 | Null | 1 | 30 |  | 19880311 | 475 | 680 | BY TEST | 994 | CORROSION | CORROSION | EXTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1946; NMDIA: 12; THK: 0.31; SPEC: 5L-B; SMYS: 355000; SEAM: SEAMLESS; MANYR: 0; LOCLK: UNDER WATER; PNAME: JACK L. ADAMS, ADMINISTRATOR, ENG.; PHONE: 3046238410; LOC: EXTERNALLY; ADESC: GENERAL CORROSION; CAUCR: GALVANIC; COAT: BARE; PROT: YES; CPYR: 1975; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880106 |  | 22617 | WILLIAMS NATURAL GAS CO | WICHITA | SEDGWICK | KS | 67226 |  | 271+55 | 1730 | 1988-01-17 | 1 | NO |  |  | KS | Null | NO | RUPTURE | 3 | 0 | 0 | 4256 | 3816.4981 | 8314.3328 | YES | 3 | 30 |  | 19880118 | 160 | 190 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 0; NMDIA: 16; THK: 0.25; SMYS: 24000; SEAM: EW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: WARREN A. ETHERIDGE; PHONE: 9185884401; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PIPELINE MARKERS; STAT: YES; CTEST: Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880110 |  | 405 | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | EUGENE |  | LA |  | X= 1943671 | Y=2056 | 1530 | 1988-03-11 |  | YES | EUGENE ISLAND | 55 |  | YES | NO | LEAK | 0 | 0 | 0 | 200000 | 179346.7166 | 390711.1262 | Null | 0 | 0 |  | 19880312 | 825 | 1300 | BY TEST | 1768 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1965; NMDIA: 20; THK: 0.41; SPEC: API-5LX-52; SMYS: 52000; MANU: U.S. STEEL; MANYR: 1965; LOCLK: UNDER WATER; PNAME: ROBERT J. LECZNAR, MGR. C.S.&P.; PHONE: 3134962456; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880112 |  | 19160 | TENNESSEE GAS PIPELINE CO |  | JEFFERSON DAVIS | LA |  | 507C-101+ 15.18 | 802+10 | 1430 | 1988-02-15 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 67000 | 60081.1501 | 130888.2273 | Null | 0 | 0 |  |  | 725 | 1085 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | LONGITUDINAL | STEEL |  | PIPELINE |  | 1955 | 20 | 0.38 | API 5LX | 52000 | DOUBLE SUBMERGE |  | CONSOLIDATED | 1955 | UNDER GROUND |  | RICHARD A. WINN - ANALYST | 7137572581 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL |  | Null |  | NO DATA |  | 0 | 0 | PINHOLE LEAK IN LONGITUDINAL SEAM DUE TO MATERIAL DEFECT.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880113 |  | 13120 | NATURAL GAS PIPELINE CO OF AMERICA |  | LOGAN | CO |  | 74 | 3598+3 | 1330 | 1988-02-08 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 85000 | 76222.3545 | 166052.2286 | Null | 0 | 0 |  | 19880208 | 700 | 1000 | BY TEST | 1293 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: NO DATA; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1982; NMDIA: 36; THK: 0.36; SPEC: 5LX; SMYS: 70000; SEAM: SUBMERGED ARC; MANU: KAISER; MANYR: 1982; LOCLK: UNDER GROUND; PNAME: W.V. LEBAN, ENGINEER; PHONE: 3126913171; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: LINE MARKER 1333 FT.; STAT: NO; CTEST: Null | SEISMIC CREW USING A 5" AUGER GOUGED THE 36" PIPELINE. THERE WAS NO RELEASE OFGAS TO ATMOSPHERE. OPERATOR HAS REPLACED DAMAGED SECTION.TWO YEAR OLD "ONE CALL" SYSTEM EXISTS IS COLORADO. NATURAL HAS BEEN A MEMBER FOR ONE ONE-HALF YEARS.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880124 |  | 405 | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | HIGH ISLAND | GALVESTON | TX | 77623 | X=3,442,220.37 | Y=1254 | 1630 | 1988-03-21 |  | YES | HIGH ISLAND,SOUTH | A-533 |  | Null | NO | LEAK | 0 | 0 | 0 | 130000 | 116575.3658 | 253962.2321 | Null | 0 | 0 |  | 19880322 | 1066 | 1440 | BY TEST | 2160 | CORROSION | CORROSION | INTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1981; NMDIA: 16; THK: 0.44; SPEC: API 5LX; SMYS: 42000; MANYR: 0; LOCLK: UNDER WATER; PNAME: ROBERT J. LECZNAR, MGR., C.S. & P; PHONE: 3134962456; LOC: INTERNALLY; ADESC: OTHER; DESCO: PINHOLE LEAK; CAUCR: NO DATA; COAT: COATED; PROT: YES; CPYR: 1981; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880126 |  | 11680 | LONE STAR GAS CO | WINONA | SMITH | TX |  |  | 701+87 | 1140 | 1988-03-15 | 1 | NO |  |  | TX | Null | NO | OTHER | 0 | 0 | 0 | 16000 | 14347.7373 | 31256.8901 | YES | 2 | 35 |  | 19880315 | 640 | 1000 | BY TEST | 1240 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1954; NMDIA: 12; THK: 0.25; SPEC: API-5LX; SMYS: 42000; SEAM: EW; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: UNDER GROUND; PNAME: Q.L. BEDSOLE, JR. SUPT.; PHONE: 2144992811; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | CONTRACTOR EXCAVATING AND HAULING FILL DIRT FOR PROPERTY OWNER STRUCK LINE SEVERAL TIMES IN A 12 FT. SEGMENT ULTIMATELY CUTTING 1 1/4 & 3 3/4 HOLE IN PIPE WITHFRONT END LOADER.LINE MARKED AT HWY. 155 APPROX. 300' S.E. OF DAMAGE AREA. CONTRACTOR WORKING FOR PROPERTY OWNER WHO MUST HAVE BEEN AWARE OF LINE ON PROPERTY.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880127 |  | 1995 | CABOT GAS SUPPLY CORP | LUBBOCK | LUBBOCK | TX | 79417 | 0259-000 |  | 430 | 1988-03-11 | 3 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 40000 | 35869.3433 | 78142.2252 | Null | 1 | 30 |  | 19880311 | 361 | 571 | BY TEST | 1300 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: SUB. TO INTENSE HEAT; MLKD: STEEL; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1964; NMDIA: 12.75; THK: 0.38; SPEC: GRADE B; SMYS: 2059; SEAM: EW; VALVE: PLUG VALVES; MANU: NORDSTROM; MANYR: 1964; LOCLK: ABOVE GROUND; PNAME: R. L. TOMLINSON ASST. DIV. MANAGER; PHONE: 9159433102; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; STAT: YES; CTEST: Null | DAMAGE RESULTED FROMFIE OF THRID PARTY'S FACILITIES.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880128 |  | 21031 | VALERO TRANSMISSION CO |  | MATAGORDA | TX |  | 46.5 | 2458+5 | 715 | 1988-03-22 | 1 | NO |  |  | TX | Null | NO | RUPTURE | 60 | 0 | 0 | 120000 | 107608.0299 | 234426.6757 | Null | 1 | 0 |  | 19880322 | 945 | 1011 | BY TEST | 1200 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | LONGITUDINAL | STEEL |  | PIPELINE |  | 1963 | 20 | 0.28 | API 5 LX52 | 1461 | SUBMERGED ARC. | N/A | AMERICAN MANNEX CORP | 1962 | UNDER GROUND |  | JOHN SOMMER, MANAGER CODES AND RECORDS | 5122462395 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | NO DATA |  | YES |  | WATER |  | 0 | 1200 | CAUSE FO RUPTURE PENDING METALLURGICAL REPORT RESULTS.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880129 |  | 15105 | PANHANDLE EASTERN PIPELINE CO | HARRISONVILLE | CASS | MO |  | M.P.15 | 779+31 | 2142 | 1988-04-01 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 3 | 24 |  | 19880401 | 650 | 800 | BY TEST | 964 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: MECHANICAL JOINT; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1937; NMDIA: 24; THK: 0.28; SMYS: 48000; SEAM: SMLS; VALVE: N/A; MANU: NAT. TUBE, LORAIN; MANYR: 1937; LOCLK: UNDER GROUND; PNAME: ROBERT AL MOODY; PHONE: 8169681562; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: HEAVY RAINFALL FLOODING; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | MOVEMENT OF THE BANK OF A RAIN-SWOLLEN CREEK ALLOWED A JOINT OF PIPE TO PARTIALLY SLIP OUT A COUPLING.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19880131 |  | 3230 | DELHI GAS PIPELINE CORP | FT. COBB | CADDO | OK | 73038 | 0 | 0+00 | 2005 | 1988-05-16 | 1 | NO |  |  | OK | Null | NO | OTHER | 0 | 1 | 2 | 30000 | 26902.0075 | 58606.6689 | Null | 2 | 0 |  | 19880516 | 240 | 939 | BY TEST | 1105 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: NO FAILURE; MLKD: NO DATA; PRTSY: OTHER; PRTSO: FRAC TANK/SEP. FAC.; PRTYR: 1968; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: TIM MURPHY / DIST. SAFETY & ENV. COORD.; PHONE: 4058862274; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | PIPELINE WAS BEING DERPESSURED DURING PIGGING OPERATION IN A ONTROLLED AND MONITORED PROCEDURE. AN ACCUMULATION OF NATURAL GAS WAS IGNITED BY AN UNKNOWN SOURCE, RESULTING IN A FLASH FIRE AND SEBSEQUENT EXPLOSION THEREBY CAUSING BOCILY INJURY AND PROPETY DAMAGE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880143 |  | 405 | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | BYHALIA | DE SOTO | MS | 38611 | 352 | 7293+5 | 1450 | 1988-05-07 | 1 | NO |  |  | MS | Null | NO | LEAK | 0 | 0 | 0 | 57000 | 51113.8142 | 111352.671 | Null | 0 | 0 |  | 19880510 | 525 | 858 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1956; NMDIA: 30; THK: 0.34; SPEC: API 5LX52; SMYS: 52000; MANU: A.O. SMITH; MANYR: 1956; LOCLK: UNDER GROUND; PNAME: M. R. LASKOWSKI, REGS. ANALYST; PHONE: 3134962457; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: MATERIAL; CTEST: YES; TESTD: 19731102; MED: WATER; TMPS: 8; LKPS: 1200 | FIVE FOOT LONG LAMINATION AT THE 9:00 POSITION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880144 |  | 4280 | EL PASO NATURAL GAS CO | BLOOMFIELD | SAN JUAN | NM |  | N/A |  | 850 | 1988-04-27 | 2 | NO |  |  | NM | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 8 | 50 |  | 19880427 | 0 | 0 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: OIL SUMP TURBINE # 2; MLKD: OTHER; PRTSY: COMPRESSOR STATION; PRTYR: 1971; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: RICHARD FAVILA, STANDARDS ENGINEER; PHONE: 9155412062; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | ON APRIL 27, 1988, AT 8:50 A.M., AN EXPLOSION OCCURRED AT BLANCO "C" PLANT IN THE OIL SUMP OF THE #2 TURBINE. THIS TURBINE HAD NOT BEEN IN USE SINCE THE EXPLOSION AND FIRE THAT OCCURRED ON OCTOBER 17, 1987. SINCE THAT DATE, THE TURBINE HAD BEEN COMPLETELY OVERHAULED, THE COMPRESSOR SHAFT REPAIRED AND REBALANCED, ANDA NEW CONTROL SYSTEM INSTALLED. PRIOR TO RELEASING THE #2 TURBINE TO PLANT OPERATIONS, A 48-HOUR TEST RUN WAS TO BE COMPLETED. ATTEMPTS HAD BEEN MADE TO START THE TURBINE APRIL 26, 1988, BUT WERE NOT SUCCESSFUL. AFTER DEBUGGING OF CONTROLS, ETC., ANOTHER ATTEMPT WAS SCHEDULED FOR THE FOLLOWING MORNING. THE MORING OF APRIL 27, 9188, THE TURBINE HAD BEEN PLACED IN RATCHETING MODE. FOLLOWING APPROXIMATELY 25 MINUTES OF RATCHETING, THE EXPLOSION OCCURRED. THE FORCE OF THE EXPLOSION BLEW THE OIL SUMP HATCH DOOR OPEN AND OFF THE HINGES. A FLASH FIRE FOLLOWED THE EXPLOSION ESCAPING OUT OT THE SUMP THROUGH THE ACCESSORY CAB ON THE EAST AND WEST SIDES. EMPLOYEES OF EL PASO NATURAL GAS COMPANY AND FISH EMOLPYEES,ONE RECEIVED FIRST DRGREE BURNS TO HIS FACE AND THE OTHER A CONTUSED EARDRUM AND STRAINED MUSCLES IN THE NECK AND BACK. THESE INJURIES WEE OT LOST TIME INJURIES. THIS EXPLOSION IN CURRENTLY UNDER STUDY BY AN ACCIDENT INVESTIGATION TEAM.THE SOURCE OF IGNITION AD THE SOURCE OF FUEL HAVE NOT BEEN DETERMINED AT THIS TIME.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880151 |  | 13845 | NORTHWEST PIPELINE CORP | 20 MILES SE. PACATELLO | BANNOCK | ID |  | 596.6 MAINLINE | 9383+9 | 1600 | 1988-05-24 | 1 | NO |  |  |  | Null | NO | RUPTURE | 2 | 0 | 0 | 75000 | 67255.0187 | 146516.6723 | Null | 1 | 10 |  | 19880524 | 720 | 850 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1955; NMDIA: 22; THK: 0.25; SPEC: API 5LX X52; SMYS: 1182; SEAM: FLECTRIC WELD; MANU: CONSOL. WEST; MANYR: 1955; LOCLK: UNDER GROUND; PNAME: MYRLE ANDERSON, COMPLIANCE SPECIALIST; PHONE: 8015846908; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: COMPANY SIGN,PAINTED; STAT: NO; CTEST: Null | DIG IN BY FARMERS CONTRACTOR LANDLEVELING.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880156 |  | 10170 | KENTUCKY - WEST VIRGINIA GAS CO | WATER GAP | FLOYD | KY | 41653 | 1+00 | 48+84 | 1330 | 1988-06-07 | 1 | NO |  |  | KY | NO | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 0 |  | 19880607 | 125 | 255 | BY TEST | 280 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 0; NMDIA: 10; THK: 0.25; SMYS: 0; MANYR: 1941; LOCLK: UNDER GROUND; PNAME: CECIL E. LESTER, DES. ENGR; PHONE: 6068862312; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: YES; NOTDT: 19880602; MARK: YES; MRKTP: STAKES; STAT: NO; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880157 |  | 1552 | BLUE DOLPHIN PIPELINE CO |  |  | TX |  |  |  | 1030 | 1988-06-10 |  | YES | GA | 287 | TX | YES | Null | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19880610 | 400 | 1440 | BY TEST | 2175 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | WELD | GIRTH | STEEL |  | PIPELINE |  | 1966 | 20 | 0.5 | API 5 LX | 52000 | SEAMLESS | N/A | N/A | 1965 | UNDER WATER |  | JOHN C. MCDUFFIE, JR. - ENGINEER | 7136213993 | INTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1965 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | 250# ZINC BRACELETS ON 1/4 MILE SPACING USED DURING INITIAL CONSTRUCTION AND LINE WS BURIED FOUR FEET DEEP. RECTIFIER AND ANODE ADDED ON "A" PLATFORM IN 1969. RECTIFIER FUNCTION CHECKED OK 2-16-88. CABLES REPLACED 3/19/88.OFFSHORE OIL SHEEN REPORTED BY AMOCO TO MMS WAS REPORTED FOR INVESTIGATION TO IVORY PRODUCTION CO WHO OPERATES BLUE DOLPHIN PIPELINE FROM GA-288 TO FREEPORT, TX. INVESTIGATION REVEALED A CORROSION PIT WHICH WAS REPAIRED BY INSTALLING A SPLIT SLEEVE BOLT-ON, PLIDCO CLAMP, RATED 1000 PSI WP.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880159 |  | 19160 | TENNESSEE GAS PIPELINE CO | PLAQUEMINES PARISH |  | LA |  | 526A-2401+2.60 | 137+00 | 1200 | 1988-05-25 |  | YES | S.P. | 44 | LA | NO | NO | LEAK | 0 | 0 | 0 | 60000 | 53804.015 | 117213.3379 | Null | 0 | 0 |  | 19880527 | 0 | 1440 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: GIRTH; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1981; NMDIA: 12; THK: 0.5; SPEC: API 5LX; SMYS: 42000; SEAM: SEAMLESS; VALVE: N/A; MANU: U.S.S.; MANYR: 1981; LOCLK: UNDER WATER; PNAME: RICHARD A. WINN - ANALYST; PHONE: 7137572581; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: SUBSEA MUDSLIDE; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | PIPELINE IS LOCATED IN A KNOWN MUDSLIDE AREA. IT APPEARS THAT A MUDSLIDE CAUSED LEAK.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880161 |  | 19570 | TRANSCO GAS PIPELINE CORP | CARLSTADT | BERGEN | NJ | 07072 | M.P. 1825.73 |  | 1240 | 1988-01-20 | 1 | NO |  |  |  | NO | NO | LEAK | 0 | 0 | 0 | 85000 | 76222.3545 | 166052.2286 | Null | 0 | 10 |  | 19880120 | 5 | 230 | BY TEST | 345 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | TRANSMISSION SYSTEM | OTHER | HEAT EXCHANGER | OTHER | ALUMINUM | OTHER | LNG PLANT | 1965 | 0 | 0 | ASTM B209-3003 | 4500 | BRAZED | PLATE & FIN | STEWART WARNER | 1965 | OTHER | LNG COLD BOX | B.G. WOODWARD, MANAGER CODES | 7134392002 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | ON JANUARY 20, 1988 AN INCIDENT OCCURRED AT TRANSCONTINENTAL GAS PIPE LINE'S STATION 240 LNG PLANT THAT CAUSED DEFORMATION OF THE COLD BOX STRUCTURAL STEEL. AFTER THIS INCIDENT, AN INSPECTION OF THE PROCESS PIPING AND VESSELS INSIDE THE COLD BOX RESULTED IN THE DISCOVERY OF FOUR SMALL LEAKS IN AN ALUMINUM PLATE-FIN EXCHANGER(E-13). ADDITIONALLY, A CHEMICAL ANALYSIS F THE ATMOSPHERE INSIDE TH COLD BOX WAS MADE AFTER THE INCIDENT, BUT PRIOR TO THE INTERNAL INSPECTION. THIS ANALYSIS SHOWED THAT IN SOME PARTS OF THE COLD BOX THAT THERE WERE SUFFICIENT AMOUNTS OF OXYGEN (FROM AIR), ETHYLENE AND NATURAL GAS CONSTITUENTS PRESENT TO SUPPORT A LIMITED REGION OF COMBUSTION. IT IS BELIEVED THAT ADDITIONAL CONTRIBUTING FACTORS WERE NATURAL GAS INTERMITTENLY LEAKING FROM FLANGES ON EXCHANGERS E-8AND /OR E-9 IN THE COLD BOX AND AIR ENTERED THE COLD BOX DUE TO POOR PERFORMANCE OF THE NITROGEN PRUGE SYSTEM. ALTHOUGH THERE IS NO DIRECT EVIDENCE AS TO WHAT CAUSED THE DAMAGE TO THE COLD BOX,ANALYSIS SHOWS THAT A DEFLAGRATION OR MILD EXPLOSION PROBABLY OCCURRED IN A SMALL PORTION OF THE COLD BOX SPACE. HYPOTHETICALLY, THE SEQUENCE OF EVENTS WAS: 1) LOW LEAKAGE RATES OF EHTYLENE, 2) INTERMITTENT LEAKAGE OF NATURAL GAS, 3) PRESENCE OF OXYGEN (AIR), 4) A FLOW OF A GAS WHICH CREATED AN ELECTROSTATIC CHARGE, 5) A SPARK AND 6) COMBUSTION.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880163 |  | 21035 | VALERO INTERSTATE TRANSMISSION CO | FALFURRIAS | BROOKS | TX | 78355 | CAGE&MILLS BENNET | 3797+6 | 1800 | 1988-05-20 | 1 | NO |  |  | TX | NO | NO | RUPTURE | 820 | 0 | 0 | 230000 | 206248.7241 | 449317.7952 | YES | 1 | 40 |  | 19880520 | 930 | 936 | BY TEST | 1058 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1959; NMDIA: 20; THK: 0.25; SPEC: API 5LX 52; SMYS: 1300; SEAM: N/A; VALVE: N/A; MANU: N/A; MANYR: 1959; LOCLK: UNDER GROUND; PNAME: FERNANDO ARGUELLES, AREA FOREMEN; PHONE: 5127872427; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | STRUCTURE PIPE FAILURE DUE TO POSSIBLE STRESS CORROSION, NO TEST RESULT YET.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19880169 |  | 15493 | PHILLIPS PETROLEUM CO | PENWELL | ECTOR | TX |  |  | 51+32 | 700 | 1988-06-16 | 1 | NO |  |  | TX | Null | NO | RUPTURE | 10 | 0 | 0 | 11500 | 10312.4362 | 22465.8898 | YES | 0 | 45 |  | 19880616 | 90 | 140 | BY TEST | 175 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1971 | 18 | 0.19 | API 5L | 35000 | ERW | 150# METER VALV |  | 0 | UNDER GROUND |  | VIRGIE V. MARTIN, REGULATORY AIDE | 9153671404 | INTERNALLY | LOCALIZED PITTING |  | NO DATA |  | COATED | YES | 0 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | THIS LINE WAS PURCHASE FROM EL PASO NATURAL GAS IN JANUARY, 1987. AT THAT TIME,CATHODIC PROTECTION WAS ON THE LINE AN IS PROTECTED AT THIS TIME.LOCALIZED PITTING DUE TO INTERNAL CORROSION RESULTED IN RUPTURE. H2S EMISSION FORCED EVACUATION OF 11 OCCUPANTS AT TEXACO'S PENWELL FIELD OFFICE. NO INURIES OCCURRED OR HOSPITALIZATION REQUIRED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880170 |  | 21031 | VALERO TRANSMISSION CO | DILLY | FRIO | TX |  |  |  | 1045 | 1988-06-02 | 1 | NO |  |  | TX | Null | NO | OTHER | 0 | 0 | 0 | 1500 | 1345.1004 | 2930.3334 | Null | 0 | 45 |  |  | 80 | 220 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1930; NMDIA: 2; THK: 0.13; SPEC: N/A; SMYS: 2526; SEAM: N/A; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: UNDER GROUND; PNAME: T.E. DISBRO, AREA FOREMAN; PHONE: 5126212052; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PIPELINE SIGNS; STAT: NO; CTEST: Null | THIS INCIDENT WAS THE RESULT OF A ROAD GRADER HITTING THE PIPELINE AND SERVERING IT. THIS SECTION OF PIPE WAS REMOVED AND A NEW SECTION OF PIPE WAS INSTALLED.THE PIPELINE HAS BEEN RETURNED TO SERVICE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880187 |  | 12342 | MEMPHIS LIGHT GAS & WATER DIVISION | MEMPHIS | SHELBY | TN |  | 251-4303 |  | 830 | 1988-07-25 | 1 | NO |  |  | TN | NO | NO | OTHER | 0 | 0 | 0 | 50000 | 44836.6791 | 97677.7816 | Null | 1 | 40 |  | 19880725 | 515 | 725 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: FITTING; PRTFO: 6" 90 DEG. ELBOW; MLKD: STEEL; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1949; NMDIA: 6; THK: 0.25; SPEC: N/A; SMYS: 35000; SEAM: N/A; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: LEORNARD PHILLIPS, MANAGER, GAS OPERATIONS,; PHONE: 9013201401; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | CONTRACTOR DAMAGED SERVICE LINE WHILE BACKFILLING A DITCH THAT WAS CUT TO FACILITATE THE INSTALLATION OF A 66" WATER TRANSMISSION MAIN.HE BUILDING WAS OF DOUBLE BRICK WALL CONSTRUCTION WITH WOOD RAFTERS AND SHEETING, AND ASPHALT ROOF. THE BUILDING FIRE DAMAGED INSTRUMENT LINES AND FITTINGS ENTERING THE SOUTH GABLE, CAUSING GAS TO ESCAPE FROM THESE LINE AND FUELING THE FIRE. THE HEAT FROM THE BLAZE EXPANDED THE FLANGE BOLTS IN THE REGULATOR RUNS AND DESTROYED THE GASKET MATERIAL, ALLOWING MORE GAS TO ESCAPE AND FUEL THE FIRE FURTHER. ULTIMATELY, A 6" WELDED ELBOW ON AN INLET STUB RUPTURED, BLOWING OUT THE SOUTH WALL OF THE BUILDING AND GREATLY INTENSIFYING THE FIRE. FLAME AND HEAT FROM THE REGULATOR STATION FIRE WERE DIRECTED TOWARD METERING FACILITIES OWNED AND OPERATED BY TEXAS GAS TRANSMISSION CORP (TGT), CAUSING A 10" RISER TO FAIL AND RUPTURE. THE HEAT FROM THE METER STATION FIRE CAUSED AN 8" RUN-AROUND PIPE ON A TGTBLOCK VALVE TO FAIL AND ALLOW ADDITIONAL GAS TO ESCAPE. THE CONFLAGRATION COMPLETELY DESTROYED THE STATION'S METERING AND REGULATING FACILITIES AND ASSOCIATED INSTRUMENTATION EQUIPMENT. THERE WERE NO INJURIES OR FATALITIES.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880191 |  | 19270 | TEXAS GAS TRANSMISSION CORP | MEMPHIS | SHELBY | TN | 38181 | 251+4303/BV26 | 251+43 | 838 | 1988-07-25 | 1 | NO |  |  | TN | NO | NO | OTHER | 0 | 0 | 0 | 500000 | 448366.7914 | 976777.8156 | Null | 1 | 15 |  | 19880725 | 515 | 760 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: BODY OF PIPE; PRTFO: INSTRUMENT TUBING; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1963; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: JOHN W. FULLENWIDER, MGR. OF P/L SAFETY; PHONE: 5029268686; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | LIGHTNING STRUCK THE POWER SUPPLY AND/OR REGULATOR BUILDING OWNED BY MEMPHIS, LIGHT, GAS AND WATER (MGL&W). BUILDING WAS DOUBLE BRICK WALL WITH WOOD RAFTERS, WOOD SHEETING AND ASPHALT ROOFING. HEAT OR FALLING MATERIAL FROM ROOF STRUCTURECAUSED STEEL TUBING FITTINGS FOR CONTROL LINE TO EXPAND, LEAK, AND FUEL THE FIRE. THE ADDED HEAT EVENTUALLY RELAXED THE FLANGE BOLTS AND NUTS, AND CAUSED THE FLANGE GASKETS TO LEAK AND FUEL THE FIRE MORE. A 6" PIPE ELL INSIDE THE REGULATOR BUILDING RUPTURED. WHEN THE 6" ELL FAILED, THE BUILDING WAS DESTROYED BY ANEXPLOSION. HEAT FROM MLGW'S REGULATOR STATION WAS DIRECTED TOWARD A 10" RISER ON TEXAS GAS'S METER STATION AND CAUSED IT TO EXPAND AND FAIL. THE HEAT FROM THETXG METER STATION WAS DIRECTED TOWARD THE BLOCK VALVE AREA AND CAUSED THE 8" RUN-AROUND PIPE AND THE VALVE EXTENSION TO FAIL.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880197 |  | 21031 | VALERO TRANSMISSION CO | SAN ANTONIO | BEXAR | TX |  |  | 76+95 | 1320 | 1988-07-20 | 1 | NO |  | N/A | TX | NO | NO | OTHER | 0 | 0 | 0 | 11500 | 10312.4362 | 22465.8898 | Null | 0 | 30 |  | 19880720 | 195 | 481 | BY TEST | 722 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1981; NMDIA: 6; THK: 0.25; SPEC: API 5LX-52; SMYS: 3925; SEAM: ERW; VALVE: N/A; MANU: REPUBLIC; MANYR: 1981; LOCLK: UNDER GROUND; PNAME: T.E. DISBRO, AREA FOREMAN; PHONE: 0006212052; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PIPELINE SIGNS; STAT: NO; CTEST: Null | ALAMO CEMENT COMPANY CONSTRUCTING ROAD BESIDE RIGHT-OF-WAY. D-9 DOZER HIT 6" PIPELINE CAUSING 12" RIP IN PIPE; ALSO DAMAGING OVER 20 FEET OF PIPE WITH RIPPER.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880200 |  | 14435 | OZARK GAS PIPELINE CORP | WILBURTON | LATIMER | OK | 74578 | 239.7 | 12669+ | 1100 | 1988-08-03 | 1 | NO |  |  |  | NO | NO | LEAK | 0 | 0 | 0 | 45000 | 40353.0112 | 87910.0034 | Null | 7 | 0 |  | 19880803 | 760 | 1200 | BY TEST | 1686 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1982; NMDIA: 20; THK: 0.28; SPEC: API-STD-5LX; SMYS: 60000; SEAM: ERW; VALVE: N/A; MANU: AMERICAN STEEL; MANYR: 1981; LOCLK: UNDER GROUND; PNAME: LARRY N. LOUDENSLAGER, SAFETY COORD.; PHONE: 5016467400; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19880726; MARK: YES; MRKTP: FLAGS; STAT: YES; CTEST: Null | SOME OF THE PIPELINE MARKER FLAGS WERE PULLED UP OR DAMAGED BY LIVESTOCK IN THEAREA. INITIAL NOTIFICATION TO OZARK WAS DELAYED THREE HOURS DUE TO CONFUSION BY THE DRILLING CREW AND NOTIFICATION TO THE WRONG PIPELINE COMPANY.OZARK 20" TRANSMISSION LINE WAS PUNCTURED BY CGG SEISMIC DRILLING RIG. THE DRILL CREW MISTAKENLY DRILLED AT THE WRONG LOCATION BY MISREADING NUMBERS ON THEIR SURVEY FLAGS. THE CREW DID NOT SEE OZARK'S PIPELINE MARKER FLAGS WHICH WERE NEARBY. (SOME FLAGS HAS BEEN PULLED UP BY LIVESTOCK IN THE AREA).
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880201 |  | 3 | ACADIAN GAS PIPELINE SYSTEM | ASSUMPTION PARISH |  | LA |  |  |  | 725 | 1988-09-03 | 1 | NO |  |  |  | NO | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 30 |  | 19880903 | 420 | 650 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1940; NMDIA: 7; THK: 0.19; SPEC: API-5LX; SMYS: 52000; SEAM: ERW; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: UNDER GROUND; PNAME: W. DAVID POPE, III, P.E./OPERATIONS MGR.; PHONE: 5044462791; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: WARNING SIGNS; STAT: YES; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880203 |  | 21031 | VALERO TRANSMISSION CO | RIO GRANDE | STARR | TX |  | 20 WEST | 2350+3 | 2230 | 1988-07-25 | 1 | NO |  |  |  | NO | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 0 |  | 19880726 | 876 | 1006 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1961; NMDIA: 16; THK: 0.25; SPEC: N/A; SMYS: 0; MANYR: 0; LOCLK: UNDER GROUND; PNAME: FERNANDO ARGUELLES, AREA FOREMAN; PHONE: 5127872427; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: ROW MARKERS IN PLACE; STAT: NO; CTEST: Null | FARM TRACTOR PLOWING FIELD HIT LINE WITH PLOW. GAS LINE WAS VERY SHALLOW AND EXPOSED DUE TO EROSION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880206 |  | 19270 | TEXAS GAS TRANSMISSION CORP | T-12-S;R-3-W;SECTION 31; | CAMERON | LA |  | 6+3616 | 6+3616 | 530 | 1988-08-19 | 1 | NO |  |  | LA | NO | NO | RUPTURE | 2 | 0 | 0 | 50000 | 44836.6791 | 97677.7816 | Null | 2 | 6 |  | 19880819 | 785 | 1200 | BY TEST | 1500 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1952; NMDIA: 6; THK: 0.25; SPEC: API-5L; SMYS: 35000; SEAM: ERW; VALVE: N/A; MANU: YOUNGSTOWN; MANYR: 1952; LOCLK: UNDER WATER; PNAME: JOHN W. FULLENWIDER; PHONE: 5029268686; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: Null; MARK: YES; MRKTP: MARKERS ALREADY IN PLACE; STAT: Null; CTEST: Null | TEXAS GAS 6" LAKESSIDE-MALLARD BAY PIPELINE PARALLELS THE SOUTH SIDE OF THE INTRACOASTAL CANAL IN LOUISIANA AND CROSSES A CHANNEL FROM THE INTRACOASTAL CANAL TO GRAND LAKE. APPARENTLY THE PROP FROM A TUGBOAT PUSHING A HEAVY LOAD THROUGH THE CHANNEL HIT OUR PIPELINE, WHICH HAD APPROXIMATELY THREE FEET OF COVER. THE GOUGE WAS APPROXIMATELY 14" LONG AND .200" DEEP. THE PIPE FAILED LATER, AND THE RUPTURE WAS ABOUT 2 FEET LONG. LIGHTNING SET THE GAS ON FIRE, BUT NO ONE WAS NEAR, SO THERE WERE NO INJURIES OR OUTSIDE PROPERTY DAMAGE.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19880207 |  | 19235 | TEXAS EASTERN GAS PIPELINE CO | BERNVILLE | BERKS | PA | 19551 | M.P. 194.17 | N/A | 1445 | 1988-08-13 | 1 | NO |  |  |  | NO | NO | OTHER | 0 | 0 | 1 | 45000 | 40353.0112 | 87910.0034 | YES | 0 | 1 |  | 19880813 | 0 | 0 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: LUBE OIL SYSTEM; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1958; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: R.E. THOMURE-MGR. CODES, REGULATORY; PHONE: 7137593131; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | SEVERAL MODIFICATIONS WERE BEING MADE TO UPGRADE TURBINE UNIT NO. 1 AT BERNVILLE COMPRESSOR STATION WHEN THE INCIDENT OCCURED. THE STATION WAS OUT OF SERVICE AND ALL GAS HAD BEEN VENTED FROM THE COMPRESSOR UNIT PIPING. A GAUGE PANEL WAS BEING CUT AWAY FROM THE TURBINE SKID AT THE TIME OF THE INCIDENT. THE AREA AROUNDTHE GAUGE PANEL WAS CHECKED FOR THE PRESENCE OF NATURAL GAS PERIODICALLY PRIOR TO CUTTING AND NO GAS WAS INDICATED. A SMALL EXPLOSION OCCURRED, PROBABLY IN ORNEAR A NON-FLAMMABLE LUBE OIL RESERVOIR TO WHICH THE GAUGE PANEL WAS ATTACHED.UNDETECTED GAS IS SUSPECTED AS THE CAUSE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880208 |  | 18516 | SOUTHERN NATURAL GAS CO | OFFSHORE |  | LA |  | M.P.0.000-M.P. 0.473 |  | 0 | 1988-09-11 |  | YES | MAIN | 77 |  | YES | NO | OTHER | 0 | 0 | 0 | 3389000 | 3039030.1123 | 6620600.034 | Null | 0 | 1 |  | 19880920 | 1050 | 1440 | BY TEST | 2162 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: OTHER; PRTSO: PLATFORM RISER; PRTYR: 1984; NMDIA: 10; THK: 0.5; SPEC: API.5LX; SMYS: 42000; SEAM: SEAMLESS; MANU: USS; MANYR: 1984; LOCLK: UNDER WATER; PNAME: C. FARRELL, SUPV. PIPELINE CODE & SAFETY; PHONE: 2053257554; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | ON SEPTEMBER 8, 1988, THE MAIN PASS 77 STRUCTURE WAS SHUT- IN AND EVACUATED FORHURRICAN "FLORENCE". ON SEPTEMBER 11, 1988, THE PLATFORM WAS REMANNED. AN ATTEMPT TO BRING THE GAS LINE IN-SERVICE WAS ABORTED DUE TO LEAKAGE IN THE RISER. SUBSEQUENTLY, THE GULF WAS RE-EVACUATED FOR HURRICANE "GILBERT". AFTER THE HURRICANE " GILBERT" THREAT WAS OVER, SURVEYS AND DIVING INVESTIGATIONS WERE MADE WHICH INDICATE A MUDSLIDE ON THE OCEAN FLOOR OCCURRED NEAR THE MAIN PASS 77 STRUCTURE. THIS MUDSLIDE LATERALLY DISPLACED AOUT 2500'+ OF THE 10-INCH LINE AND PROVIDED THE NECESSARY FORCE TO BREAK THE RISER ATTACHED TO THE PLATFORM. THE PRESSURE ON THIS LINE,WHICH WAS NOT IN SERVICE AT THE TIME OF THE INCIDENT WAS 1050 PSI(+),FURTHER INVESTIGATIONS HAVE VERIFIED A CHECK VALVE INSTALLED IN THE LINE ATTHE BASE OF THE RISER CONTANED THE PRESURE ON THE PIPELINE AND THE ONLY DISCHARGE CAME FROM THE ISOLATED RISER PIPING.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880211 |  | 405 | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | OFFSHORE | WATERS | TX |  | X=3717735 | 155515 | 630 | 1988-09-10 |  | YES | HI | A325 |  | YES | NO | LEAK | 0 | 0 | 0 | 75000 | 67255.0187 | 146516.6723 | Null | 0 | 0 |  |  | 1100 | 1440 | BY TEST | 2694 | CORROSION | CORROSION | INTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1981; NMDIA: 10; THK: 0.37; SPEC: API 5LX 42; SMYS: 42000; MANU: KAWASKI; MANYR: 1980; LOCLK: UNDER WATER; PNAME: ROBET J. LECZNAR, MGR., C.S.&P; PHONE: 3134962456; LOC: INTERNALLY; ADESC: NO DATA; CAUCR: GALVANIC; COAT: COATED; PROT: YES; CPYR: 1981; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880214 |  | 19160 | TENNESSEE GAS PIPELINE CO | WEST CAMERON |  | LA |  | 507K-301+0.00 | 0+03 | 1130 | 1988-09-17 |  | YES |  | WC.176 |  | YES | NO | LEAK | 0 | 0 | 0 | 97000 | 86983.1575 | 189494.8962 | Null | 91 | 7 |  |  | 800 | 1201 | BY TEST | 1668 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: 1/2" PIPE NIPPLE; MLKD: STEEL; PRTSY: OTHER; PRTSO: SIDE VALVE COMPONENT; PRTYR: 1969; NMDIA: 0.5; THK: 0; SPEC: 3000 PSI; SMYS: 0; MANYR: 0; LOCLK: UNDER WATER; PNAME: RICHARD A. WINN, ANALYST; PHONE: 7137572581; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | THE VALVE GUARD WAS PULLED OFF OF THE SIDE VALVE ASSEMBLY, POSSIBLY BY A CABLE FROM A PASSING BOAT. THE VALVE GUARD HUNG ON THE OPERATOR ON THE 12" CHECK VALVE, SHEARING OFF THE OPERATOR AND BREAKING THE 1/2" NIPPLE.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19880218 |  | 13120 | NATURAL GAS PIPELINE CO OF AMERICA | BEATRICE | GAGE | NE | 68310 | MP 483 | 3 | 1400 | 1988-08-31 | 1 | NO |  | N/A |  | NO | NO | OTHER | 0 | 0 | 3 | 0 | 0 | 0 | Null | 0 | 0 |  | 19880901 | 0 | 712 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: ENGINE; MLKD: OTHER; MLKDO: N/A; PRTSY: COMPRESSOR STATION; PRTYR: 1931; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: W.V. LEBAN, ENGINEER; PHONE: 3126913171; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | TORCH IGNITED NATURAL GAS THAT HAD LEAKED INTO THE ENGINE CRANKCASE THROUGH THE COMPRESSOR PACKINGS. EMPLOYEES WERE USING A TORCH TO HEAT SPROCKET HUBS FOR REMOVAL FROM CRANKCASE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880219 |  | 19220 | TEXACO INC | MONTZ | ST CHARLES | LA | XX | APPROX. STA. 61+30 |  | 1150 | 1988-09-02 | 1 | NO |  |  | LA | NO | NO | LEAK | 0 | 0 | 0 | 12000 | 10760.803 | 23442.6676 | Null | 0 | 0 |  |  | 800 | 1440 | BY TEST | 2160 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1966 | 6 | 0.25 | GR. B, API 5L | 35000 | SEAMLESS |  | N/A | 0 | UNDER GROUND |  | AM. SIMMERS, ADMINISTRATOR-PIPELINE SAFETY | 5045951605 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1966 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | PINHOLE, ISOLATED LEAK DUE TO EXTERNAL CORROSION BELIEVED TO HAVE BEEN CAUSED BY STRAY CURRENT.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880222 |  | 5304 | FLORIDA GAS TRANSMISSION CO | REFUGIO | REFUGIO | TX | 78377 | MP 142.76 | 2489+9 | 940 | 1988-09-04 | 1 | NO |  | N/A |  | NO | NO | RUPTURE | 20 | 0 | 0 | 50000 | 44836.6791 | 97677.7816 | Null | 0 | 0 |  | 19880906 | 874 | 975 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1959 | 20 | 0.28 | N/A | 52000 | DSAW | N/A | KAISER | 0 | UNDER GROUND |  | JEFF WHIPPO - COMPLIANCE ENGINEER | 7138537322 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1959 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | THE ENCLOSED INCIDENT REPORT FOR FLORIDA GAS TRANSMISSION CO. DESCRIBES A RUPTURE WHICH OCCURRED ON SEPTEMBER 4TH, 1988. AFTER CALCULATIONS HAD BEEN MADE TO DETERMINE THE AMOUNT OF NATURAL GAS RELEASED TO THE ATMOSPHERE, IT WAS DETERMINED THAT THE $50,000 CRITERIA HAD BEEN EXCEEDED. TELEPHONIC NOTICE TO THE NATIONAL RESPONSE CENTER WAS MADE FOLLOWING THIS DETERMINATION.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880225 |  | 19160 | TENNESSEE GAS PIPELINE CO |  |  | TX |  | 821E-106-+3.37 | 177+87 | 800 | 1988-09-01 |  | YES | TX | 39 |  | YES | NO | LEAK | 0 | 0 | 0 | 200000 | 179346.7166 | 390711.1262 | Null | 0 | 0 |  |  | 1180 | 1440 | BY TEST | 2164 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | VALVE |  | STEEL |  | PIPELINE |  | 1981 | 24 | 0.5 | X-60 | 60000 | DSAW |  | U.S. STEEL | 1981 | UNDER WATER |  | RICHARD A. WINN - ANALYST | 7137572581 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | CRACKED IN SADDLE PAD AT 6" SIDE VALVE | YES | 19810710 | WATER |  | 8 | 2164 | 6" CRACK IN SADDLE PAD SIDE VALVE.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19880227 |  | 2616 | COLUMBIA GAS TRANSMISSION CORP | VANLUE | HANCOCK | OH | 45890 | N/A | 5476+8 | 1450 | 1988-08-17 | 1 | NO |  | N/A |  | NO | NO | LEAK | 0 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 15 |  | 19880818 | 123 | 185 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: MECHANICAL JOINT; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1909; NMDIA: 10; THK: 0.38; SPEC: N/A; SMYS: 0; SEAM: SMLS; VALVE: N/A; MANU: N/A; MANYR: 1909; LOCLK: UNDER GROUND; PNAME: A.S. BECKETT, SUPERVISORY ENGINEER; PHONE: 3043572797; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | PIPELINE PULLED-OUT OF UNDETECTED ORIGINAL COUPLING AFTER COMPLETING REPLACEMENT PIPELINE TIE-IN AND PRESSURIZING LINE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880228 |  | 6141 | GAS CO OF NEW MEXICO | LYBROOK | SAN JUAN | NM | 87013 | 5.2 | N/A | 550 | 1988-09-01 | 1 | NO |  | N/A |  | NO | YES | RUPTURE | 4 | 0 | 0 | 72367 | 64893.9192 | 141372.9604 | Null | 1 | 0 |  | 19880901 | 425 | 550 | BY TEST | 900 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1966; NMDIA: 12; THK: 0.22; SPEC: GRADE B; SMYS: 35000; SEAM: ERW; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: UNDER GROUND; PNAME: JON JONES - MANAGER, PIPELINE OPERATIONS; PHONE: 5056323311; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: METAL T-POST & SIGNS; STAT: YES; CTEST: Null | FAILURE OF THE DEPARTMENT OF ENERGY (D.O.E.) MAINLINE, PRIMARILY A BARE LINE, WAS CAUSED BY EXTENSIVE CORRISIVE IN A SECTION OF WRAPPED PIPE. SEVERAL SCRATCHES WERE FOUND ON THIS SECTION WHICH HAD RESULTED IN EXTENSIVE COATING DAMAGE AND ACCELERATED CORROSION REDUCING THE PIPE WALL TO PAPER THICKNESS. THE DEEPEST GROOVE CONTAINED A ONE INCH (1") PORTION THAT HAD CORRODED COMPLETELY THROUGH THE PIPE WALL CAUSING THE RUPTURE. IT IS APPARENT THAT THESE GROOVES AND SCRATCHES WERE ACTUALLY CLAW MARKS CAUSED BY A BACKHOE, THIRD PARTY DAMAGE THAT WENT UNREPAIRED.FURTHER INVESTIGATION REVEALED THAT THE D.O.E., OWNER OF THE MAINLINE, HAD HAD A CLOSE INTERVAL CATHODIC PROTECTION SURVEY DONE WITH A SUBSEQUENT INSTALLATIN OF ANODES AND/OR TEST STATIONS ON THIS LINE IN 1984. IT IS ASSUMED THAT THE DAMAGE TO THE MAINLINE OCCURRED THEN.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880229 |  | 456 | AMOCO GAS CO | PASADENA | HARRIS | TX |  | N/A | 1692+8 | 900 | 1988-08-16 | 3 | NO |  | N/A |  | NO | NO | LEAK | 0 | 0 | 0 | 1760 | 1578.2511 | 3438.2579 | Null | 4 | 0 |  | 19880816 | 500 | 700 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1961 | 12 | 0.22 | API 5L | 52000 | ERW | N/A | STUPP | 1960 | UNDER GROUND | CASING | D.E. KOONS, SAFETY ENGINEER | 4099424920 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1961 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | LEAK WAS CAUSED BY ATMOSPHERIC CORROSION AT A COATING HOLIDAY ON CARRIER PIPE IN THE CASING.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880237 |  | 20245 | UNITED TEXAS TRANSMISSION CO | HOUSTON | HARRIS | TX |  | M.P. 26.6 | 1408+1 | 1215 | 1988-08-24 | 3 | NO |  | N/A |  | NO | NO | LEAK | 0 | 0 | 0 | 5000 | 4483.6679 | 9767.7782 | Null | 0 | 30 |  | 19880825 | 240 | 403 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | MECHANICAL JOINT |  | OTHER | DRESSER COUPLE RUBBER | PIPELINE |  | 0 | 12 | 0.22 | API-5L | 0 | DRESSER COUPLE | N/A |  | 0 | UNDER GROUND |  | LAURI L. LATIERI - SUPERVISOR | 7139633236 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | DRESSER COUPLE | NO |  | NO DATA |  | 0 | 0 | DISCOVERED LEAK HAD OCCURRED IN RUBBER OF DRESSER COUPLE ON 8-24-88, INITIALLY THOUGHT COULD BE REPAIRED WITH A BAND CLAMP. ON EVENING OF 8/24, DECIDED LINE NEEDED TO BE SHUT IN FOR REPAIR.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19880238 |  | 11680 | LONE STAR GAS CO | SEYMOUR | FOARD | TX |  | AERIAL MARKER #22 | 1086+4 | 1015 | 1988-09-12 | 1 | NO |  | N/A |  | NO | NO | OTHER | 0 | 0 | 1 | 8260 | 7407.0194 | 16136.3695 | Null | 3 | 0 |  | 19880912 | 240 | 325 | BY TEST | 500 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1935; NMDIA: 4.5; THK: 0.17; SPEC: 7.64#/FT.; SMYS: 0; MANYR: 0; LOCLK: UNDER GROUND; PNAME: M. SAPP; PHONE: 2146702310; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: NO; MARK: YES; STAT: NO; CTEST: Null | SERVICE METER 200 FEET WEST OF WHERE LINE WAS DAMAGED PERMANENT LSG MARKER 2000FEET OF WHERE LINE WAS DAMAGED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880246 |  | 5304 | FLORIDA GAS TRANSMISSION CO | FRANKLINTON | WASHINGTON | LA | 70438 | M.P. 58.4 | 3084+4 | 1600 | 1988-09-29 | 1 | NO |  |  |  | NO | NO | LEAK | 0 | 0 | 0 | 51500 | 46181.7795 | 100608.115 | Null | 0 | 30 |  | 19880930 | 750 | 975 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: OTHER; MLKDO: STAINLESS STEEL; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1981; NMDIA: 0.38; THK: 0.04; SPEC: N/A; SMYS: 0; SEAM: SEAMLESS; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: JEFF WHIPPO, COMPLIANCE ENGINEER; PHONE: 7138537322; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | LIGHTNING STRIKE BROKE STAINLESS STEEL TUBING GAUGE LINE AND IGNITED GAS. PIPELINE FACILITIES DAMAGED BY FIRE; ELECTRONIC FACILITIES DAMAGED BY ELECTRICAL DISCHARGE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880252 |  | 20245 | UNITED TEXAS TRANSMISSION CO | PLEAK | FORT BEND | TX | 77471 | 0.37 | 19+54 | 1045 | 1988-08-06 | 2 | NO |  | N/A |  | NO | NO | RUPTURE | 0.5 | 0 | 0 | 7500 | 6725.5019 | 14651.6672 | Null | 1 | 25 |  | 19880806 | 345 | 445 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1938; NMDIA: 8; THK: 0.19; SPEC: N/A; SMYS: 1046; SEAM: LW; VALVE: N/A; MANU: N/A; MANYR: 1938; LOCLK: UNDER GROUND; PNAME: JANICE L. MARAK - TECHNICAL ASSISTANT; PHONE: 7139633238; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PIPELINE MARKER; STAT: NO; CTEST: Null | LANDOWNER WAS PLOWING FIELD AND STRUCK OUR PIPELINE CAUSING GOUGE IN PIPE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880254 |  | 11680 | LONE STAR GAS CO | PILOT POINT | DENTON | TX |  | 9 | 486+11 | 1240 | 1988-10-16 | 1 | NO |  | N/A |  | NO | NO | OTHER | 0 | 0 | 0 | 9500 | 8518.969 | 18558.7785 | YES | 0 | 35 |  | 19881016 | 185 | 500 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1928; NMDIA: 4; THK: 0.24; SPEC: N/A; SMYS: 24000; SEAM: N/A; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: UNDER GROUND; PNAME: J.A. RICHEY-LEAD OPERATOR; PHONE: 8176651777; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: FENCE POST PAINTED; STAT: NO; CTEST: Null | LAND OWNER WAS CLEARING BRUSH ON PROPERTY WITH A TRACK LOADER AND PUNCTURED PIPELINE. INFLICTED 4" DIAMETER HOLE IN PIPELINE. REPAIR MADE BY TAKING LINE OUT OF SERVICE AND REPLACING DAMAGED PIPE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880255 |  | 11680 | LONE STAR GAS CO | VAN ZANDT | CANTON | TX |  | N/A | 246+51 | 945 | 1988-10-06 | 1 | NO |  | N/A |  | NO | NO | OTHER | 0 | 0 | 0 | 15000 | 13451.0037 | 29303.3345 | YES | 1 | 30 |  | 19881006 | 180 | 250 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1950; NMDIA: 3; THK: 0.22; SPEC: API 5L; SMYS: 30000; SEAM: LAP WELD; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: UNDER GROUND; PNAME: F.M. MCCREARY-SUPERINTENDENT I; PHONE: 2144992811; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | 3- INCH PIPELINE HIT BY TP&L POWER DIGGER DIGGING PIER HOLES TO INSTALL H-FRAM POWER LINES CUTTING 2"X6" HOLE IN TOP QUARTER OF PIPE.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19880258 |  | 21031 | VALERO TRANSMISSION CO | RURAL, LAREDO | WEBB | TX | 78040 | N/A | 38+83 | 1730 | 1988-08-28 | 1 | NO |  | N/A | TX | NO | NO | RUPTURE | 0.5 | 0 | 0 | 0 | 0 | 0 | YES | 10 | 30 |  | 19880828 | 1000 | 1440 | BY TEST | 2160 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1977 | 6.63 | 0.16 | API 5LX42 | 1977 | ERW | N/A | N/A | 0 | UNDER GROUND |  | ROYCE SLIVA, AREA FOREMAN | 5127243981 | INTERNALLY | GENERAL CORROSION |  | NO DATA |  | COATED | YES | 1977 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | THIS INCIDENT WAS THE RESULT OF INTERNAL CORROSION ON OUR RURAL GATHERING PIPELINE. THE LINE WAS TAKEN OUT OF SERVICE AND THIRTY (30) FEET OF PIPE WAS REPLACED. THE LINE WAS RETURNED TO SERVICE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880263 |  | 19160 | TENNESSEE GAS PIPELINE CO | LOBELVILLE | PERRY | TN | 37097 | 79-2+3.95 | 208+60 | 805 | 1988-10-30 | 1 | NO |  | N/A |  | NO | NO | RUPTURE | 35 | 0 | 0 | 150000 | 134510.0374 | 293033.3447 | Null | 1 | 15 |  | 19881030 | 740 | 810 | BY TEST | 971 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1948 | 26 | 0.28 | X-52 | 52000 | FLASH | N/A | A.O. SMITH | 1948 | UNDER GROUND |  | RICHARD A. WINN, SR. REGULATORY ASSISTANT | 7137572581 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | COATED | YES | 1948 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | EXTERNAL GENERAL CORROSION APPROXIMATELY 24" LONG X .180" - .230" DEEP. APPROXIMATELY AT THE 5:00 POSITION.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880264 |  | 19160 | TENNESSEE GAS PIPELINE CO | CLEVELAND | SAN JACINTO | TX | 77327 | 26-1+3.23 | 170+50 | 330 | 1988-10-22 | 1 | NO |  | N/A |  | NO | NO | RUPTURE | 38 | 0 | 0 | 120000 | 107608.0299 | 234426.6757 | Null | 1 | 30 |  | 19881022 | 705 | 750 | BY TEST | 1038 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1944 | 24 | 0.25 | X-50 | 50000 | FLASH WELD |  | A.O. SMITH | 1944 | UNDER GROUND |  | RICHARD A. WINN, SR. REGULATORY ASST. | 7137572581 | INTERNALLY | OTHER | SCC | OTHER | SCC | COATED | YES | 1947 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | THE INCIDENT WAS CONCLUDED TO BE CAUSED PRIMARILY BY STRESS CORROSION CRACKING (SCC). A SMALL CLUSTER OF CRACKS WHICH APPEARS TO BE SCC WAS FOUND ON A BURNED PIECE OF RUPTURED PIPE.
2021-02-26 10:36 | YES | YES | GG (Gas Gathering) | 19880267 |  | 15493 | PHILLIPS PETROLEUM CO |  | ECTOR | TX |  | 17 |  | 1145 | 1988-11-21 |  | NO |  |  |  | NO | NO | RUPTURE | 0 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 10 |  | 19881121 | 70 | 140 | BY TEST | 175 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: GATHERING SYSTEM; PRTFL: OTHER; PRTFO: DRAIN LINE TO FRAC; MLKD: STEEL; PRTSY: OTHER; PRTSO: TEMP. CONNECTION; PRTYR: 1971; NMDIA: 18; THK: 0.38; SPEC: N/A; SMYS: 35000; SEAM: N/A; VALVE: 150 SERIES; MANU: N/A; MANYR: 0; LOCLK: NO DATA; PNAME: VIRGIE MARTIN, RREGULATORY CLERK; PHONE: 9153671404; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | 18" U GAS PIPELINE WAS BEING CLEANED BY PIGGING OPERATION. TWO RIVERS CONSTRUCTION CO., THE CONTRACTOR THE PROJECT, ALLOWED 6-INCH DRAIN LINE TO THE FRAC TANKTO COME LOOSE. SIDRO MORENO WAS HOSPITALIZED W/BROKEN FOREARM AND CUT ON FOREHEAD. ALBERT GARZA WAS GIVEN A BREATHING TREATMENT AND RELEASED. ISREAL LUNA WAS GIVEN BREATHING TREATMENT AND HOSPITALIZED OVERNIGHT FOR OBSERVATION. THE LOCATION OF THE INCIDENT IS NOT JURISDICTIONAL; HOWEVER, A PORTION OF THE LINE IS JURISDICTIONAL.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880268 |  | 405 | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | WEST JOLIET | WILL | IL |  | M.P. 816.77 |  | 2015 | 1988-11-08 |  | NO |  |  | IL | NO | NO | OTHER | 0 | 0 | 0 | 125000 | 112091.6979 | 244194.4539 | Null | 0 | 30 |  | 19881109 | 756 | 850 | BY TEST | 1309 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: NO DATA; MLKD: NO DATA; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1988; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: MICHAEL R. LASKOWSKI, LEAD ENGINEER; PHONE: 3134962457; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | LOW PRESSURE INSTRUMENT GAS VENTING FROM TRANSDUCERS IN CONTROL PANEL INSIDE THE METER BUILDING FOUND ITS WAY THROUGH ELECTRICAL CONDUIT INTO THE COMPUTER ROOM, IGNITED AND CAUSED A SMALL FIRE.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19880269 |  | 2327 | CHEVRON USA INC | WEST DELTA BLOCK 79 | PLATFORM | LA |  |  |  | 1800 | 1988-08-20 |  | YES |  |  |  | NO | NO | LEAK | 0 | 0 | 0 | 70000 | 62771.3508 | 136748.8942 | Null | 48 | 0 |  | 19880820 | 1000 | 1440 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | OTHER | RISER | 1970 | 20 | 0.63 | API 5LX | 52000 | SEAMLESS | N/A | U.S. STEEL | 1969 | OTHER | SPLASH ZONE | H. TODD HONES, CONSTRUCTION ENGINEER | 5043642007 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | NO | 0 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | THE 20" RISER WAS PROTECTED IN THE SPLASH ZONE VIA 26" CASING WITH TEH ANNULUS FILLED WITH COCRETE. THE 26" CASING TERMINATED ROUGHLY 10' ABOVE THE WATERLINE.THE CONCRETE WAS NOT ISOLATED FROM THE ENVIRONMENT AT THE 26" TERMINATION POINT. CONTINUAL WETTING OF THE CONCRETE RESULTED IN TEH CONCRETE BECOMING CHANNELED, THUS TRAPPING WATER NEXT TO THE 20" RISER. THE RISER SUFFERED SEVERE PITTING ALONG THE CHANNEL, AND SUBSEQUENT SANDBLASTIG CREATED A HOLE AT THIS AREA.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880270 |  | 13845 | NORTHWEST PIPELINE CORP | MOSES LAKE | GRANT | WA |  | 35.7 | 1888+8 | 940 | 1988-10-26 | 1 | NO |  | N/A |  | NO | NO | OTHER | 0 | 0 | 0 | 24000 | 21521.606 | 46885.3351 | YES | 1 | 45 |  | 19881026 | 690 | 811 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1957; NMDIA: 8.63; THK: 0.19; SPEC: 5LX42; SMYS: 1831; SEAM: ERW; MANU: KAISER; MANYR: 1957; LOCLK: UNDER GROUND; PNAME: MYRLE ANDERSON/ COMPLIANCE SPEC.; PHONE: 8015846908; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PERMANENT MARKERS; STAT: YES; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880271 |  | 13710 | NORTHERN ILLINOIS GAS CO | DESPLAINES | COOK | IL |  | 24.8 | 3 | 630 | 1988-11-09 | 3 | NO |  | N |  | NO | NO | OTHER | 0 | 0 | 0 | 50000 | 44836.6791 | 97677.7816 | Null | 1 | 45 |  | 19881109 | 160 | 562 | BY TEST | 1092 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: FITTING; PRTFO: BLOWDOWN; MLKD: NO DATA; PRTSY: NO DATA; PRTYR: 1965; NMDIA: 30; THK: 0.28; SPEC: API; SMYS: 60000; SEAM: S.A.; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: JOSEPH WAGNER - AREA MANAGER; PHONE: 3129838888; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | WHILE PURGING GAS FROM A PIPELINE PRIOR TO A TIE - IN, THE GAS WAS IGNITED BY AN UNKNOWN SOURCE ( SUSPECTED STATIC ELECTRICITY). THE HEAT MELTED OVERHEAD ELECTRIC LINES CAUSING THEY TO FAIL AND FALL TO THE GROUND.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880272 |  | 21035 | VALERO INTERSTATE TRANSMISSION CO | FALFARRIAS | JIM WELLS | TX | 78355 |  | 79+07 | 0 | 1988-09-23 | 1 | NO |  | N/A | TX | NO | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  |  | 780 | 1050 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1960; NMDIA: 12; THK: 0.22; SPEC: API 5LX-42; SMYS: 1442; SEAM: FRW; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: UNDER GROUND; PNAME: FERNANDO ARGUELLES, AREA FOREMAN; PHONE: 5127872427; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19880826; MARK: YES; MRKTP: SURVEY STAKES; STAT: NO; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880273 |  | 13660 | NORTH SHORE GAS CO | VERNON HILLS | LAKE | IL | 60061 |  |  | 1445 | 1988-10-20 | 3 | NO |  | N/A |  | NO | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 0 |  | 19881020 | 240 | 250 | BY TEST | 375 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1973; NMDIA: 24; THK: 0.25; SPEC: API5L; SMYS: 35000; SEAM: N/A; VALVE: N/A; MANU: N/A; MANYR: 1973; LOCLK: UNDER GROUND; PNAME: R.W. STEGMAN, MANAGER OF OPERATIONS; PHONE: 3123367400; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | CONTRACTOR GRADING SITE FOR ANEW PARKING AREA PIERCED 24" STEEL MAIN WITH TOOTHOF BULLDOZER.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880274 |  | 2616 | COLUMBIA GAS TRANSMISSION CORP | GLADY | RANDOLPH | WV | 26268 | N/A |  | 1730 | 1988-10-22 | 1 | NO |  | N/A |  | NO | NO | OTHER | 0 | 0 | 0 | 250000 | 224183.3957 | 488388.9078 | Null | 1 | 40 |  | 19881022 | 30 | 40 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: FUEL GAS FILTER; MLKD: OTHER; MLKDO: ALUMINUM; PRTSY: OTHER; PRTSO: DEHYDRATION PLANT; PRTYR: 1965; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: A.S. BECKETT, SUPERVISORY ENGINEER; PHONE: 3043572797; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | THE DEHYDRATION PLANT EXPLOSION AND RESULTING FIRE WHICH DESTROYED TWO GLYCOL HEATER; A GAS/GLYCOL SEPARATOR; A GLYCOL ACCUMULATOR TANK; FOUR GLYCOL PUMPS; ALLASSOCIATED PIPING, VALVES, REGULATORS AND FITTINGS; AND THE EQUIPMENT ENCLOSUREMADE DETERMINING THE ACTUAL CAUSE IMPOSSIBLE. THE PRESUMED CAUSE IS THAT DIRT OR FOREIGN MATTER CAUSED AN AUTOMATIC FLOAT DRAIN ASSEMBLY ON A BALSTON A-60 FILTER TO MALFUNCTION IN THE OPEN POSITION. THE FILTER WAS USED TO REMOVE GLYCOL, NOT REMOVED BY THE FUEL SCRUBBER, FROM GAS SCAVANGED VIA OF THE OF TEH GAS/GLYCOL SEPARATOR FOR THE GLYCOL HEATER FUEL GAS. (SEE FIGURE 1) THIS ALLOWED ALL THEGLYCOL TO BLOW FROM THE FILTER DRAIN, AND THEN 30 PSIG GAS TO ESCAPE. THE ESCAPING GAS THEN ACCUULATED IN THE EQUIPMENT ENCLOSURE UNTIL IT WAS IGNITED BY THE HEATER PILOTS. THE RESULTING HEAT FROM THE EXPLOSION AND FIRE MELTED THE NITRILE SEAT ND DEAPHRAM IN A FISHER 630 NREGULATOR ALLOWING 760 PSIG GAS TO FEED THE FIRE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880275 |  | 19160 | TENNESSEE GAS PIPELINE CO | PLAQUEMINES PARISH | STATE WATERS | LA |  | 526A-301+5.1 | 296+28 | 440 | 1988-11-12 |  | YES |  | W. BAY |  | NO | NO | RUPTURE | 37 | 0 | 0 | 80000 | 71738.6866 | 156284.4505 | Null | 1 | 53 |  | 19881112 | 860 | 1058 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1957; NMDIA: 12.75; THK: 0.31; SPEC: API-5LX; SMYS: 42000; SEAM: SEAMLESS; VALVE: N/A; MANU: NATIONAL TUBE; MANYR: 1956; LOCLK: UNDER WATER; PNAME: RICHARD A. WINN, SR. REGULATORY ASST.; PHONE: 7137572581; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | CONDITION OF PIPE INCIDATES A DREDGE OR DRILLING RIG HIT PIPELINE AND DAMAGED OVER 50 FEET, 37 FEET OF WHICH WAS CAUSED WHEN PIPE RUPTURED. THE RESPONSIBLE PARTY HAS NOT BEEN LOCATED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880297 |  | 21031 | VALERO TRANSMISSION CO | CRYSTAL CITY | DIMMIT | TX | 78834 |  |  | 300 | 1988-10-24 | 1 | NO |  | N/A | TX | NO | NO | OTHER | 0 | 0 | 0 | 1200 | 1076.0803 | 2344.2668 | Null | 0 | 30 |  |  | 10 | 40 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 0; NMDIA: 2; THK: 0; SPEC: N/A; SMYS: 0; SEAM: N/A; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: UNDER GROUND; PNAME: P. WARD, AREA CLERK; PHONE: 5122463386; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PD METER, CO SIGNS; STAT: NO; CTEST: Null | DOZER OPERTOR DID NOT NOTIFY US BEFORE DIGGING, BUT STATED HE WAS AWARE PIPE WAS THERE BECAUSE OF SIGNS. HE ASSUMED LINE WAS BURIED DEEPER.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19880298 |  | 15493 | PHILLIPS PETROLEUM CO | FRIENDSWOOD | GALVESTON | TX |  | MP45-46+58 |  | 1355 | 1988-11-28 |  | NO |  |  |  | NO | NO | OTHER | 0 | 0 | 1 | 70000 | 62771.3508 | 136748.8942 | Null | 9 | 5 |  | 19881128 | 1043 | 1090 | BY TEST | 1950 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1953; NMDIA: 0.11; THK: 0.28; SPEC: 5 LX-X42; SMYS: 0; MANYR: 1953; LOCLK: OTHER; LOCLO: CANAL CROSSING; PNAME: A.C. BIEBER, PPL GCA SUPT.; PHONE: 7133315271; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: RD PIPELINE WARNING SIGNS; STAT: NO; CTEST: Null | DOZER WITH HYDRAULIC EXTENDED MOWER STRUCK NEARBY PROPANE LINE WHICH INGITED. HEAT FROM ORIGINAL RUPTURE CAUSED 10" ETHYLENE LINE TO EXPLODE AND BURN.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880299 |  | 602 | ARKLA ENERGY RESOURCES | WATERLOO | OUACHITA | AR | 71863 | 26 | 1356+1 | 1720 | 1988-11-25 | 1 | NO |  | N/A |  | NO | NO | RUPTURE | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 55 |  | 19881125 | 380 | 415 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1929 | 0.12 | 0.31 | N/A | 1300 | ERW | N/A | YOUNGSTOWN | 1928 | ABOVE GROUND |  | R.G. TABOR, MANAGER OF SAFETY & DOT COMPLIANCE | 3184293710 | EXTERNALLY | GENERAL CORROSION |  | OTHER |  | BARE | YES | 1962 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | TRANSMISSION LINE RUPUTURED AT CREEK CROSSING.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880303 |  | 1217 | BEAR CREEK STORAGE CO | BIENVILLE | BIENVILLE | LA | 71008 | 2.5 MILES OF BIENVIL |  | 935 | 1988-11-29 | 1 | NO |  | N/A | LA | NO | NO | RUPTURE | 4 | 0 | 0 | 54900 | 49230.6737 | 107250.2042 | Null | 0 | 10 |  | 19881129 | 2400 | 3526 | BY TEST | 4411 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: METER TUBE; MLKD: STEEL; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1981; NMDIA: 0.6; THK: 0.43; SPEC: API 5LX; SMYS: 52000; SEAM: SEAM PIPE MAN.N; VALVE: N/A; MANU: DANIEL INDUS.; MANYR: 1980; LOCLK: ABOVE GROUND; PNAME: C.S. FARRELL, SUPERVISOR PIPELINE CODE; PHONE: 2053257554; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880309 |  | 10030 | KN ENERGY INC (KANSAS NEBRASKA NATURAL GAS CO INC) |  | THAYER | NE |  |  | 15+76 | 1445 | 1988-12-09 | 1 | NO |  | N/A | NE | NO | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 45 |  | 19881209 | 470 | 545 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1967; NMDIA: 2.38; THK: 0.13; SPEC: A-120; SMYS: 30000; SEAM: ERW; VALVE: N/A; MANU: SOUTHWEST PIPE; MANYR: 1967; LOCLK: NO DATA; PNAME: JAMES R. PHILLIPS-CONTRUCTION; PHONE: 4024622141; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: LINEMARKER; STAT: NO; CTEST: Null | THE PIPELINE WS HIT BY AN OUTSIDE PARTY OPERATING A BULLDOZER. THE DAMAGED PORTION OF THE PIPELIN IS IN A CLASS I LOCATION AND WAS MARKED WITH PERMANENT LINE MARKER. A PERMANENT REPAIR WAS COMPLETED BY REPLACING FIVE (5) FEET OF THE DAMAGED PIPELINE WITH PRETESTED PIPE OF EQUAL OR GREATER SPECIFICATION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19880311 |  | 405 | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | HIGH ISLAND BL. 471 |  | TX |  | X=3,597,634 | Y=1988 | 705 | 1988-11-17 |  | YES | HIGH ISLAND | 471 | TX | NO | NO | LEAK | 0 | 0 | 0 | 1785 | 1600.6694 | 3487.0968 | Null | 0 | 0 |  | 19881117 | 940 | 1440 | BY TEST | 3350 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1981; NMDIA: 12; THK: 0.69; SPEC: ASTMA-106 GRB; SMYS: 35000; SEAM: N/A; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: UNDER WATER; PNAME: MICHAEL R. LASKOWSKI, LEAD ENGINEER; PHONE: 3134962457; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19880312 |  | 18484 | SOUTHERN CALIFORNIA GAS CO | LOS ANGELES | LOS ANGELES | CA | 90403 | 121-113.59-0 | 84+23 | 1400 | 1988-11-10 | 3 | NO |  | N/A |  | NO | NO | LEAK | 0 | 0 | 0 | 72000 | 64564.818 | 140656.0054 | Null | 4 | 31 |  | 19881110 | 168 | 228 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | FITTING | 20" LOOSE RING FLANGE | STEEL |  | PIPELINE |  | 1944 | 20 | 0.31 | N/A | 1125 | N/A | N/A | N/A | 1944 | OTHER | VAULT | R.L. RUDZIK, MANAGER OF TRANSMISSION | 2136892345 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | 20" LOOSE RING FLANGE | NO |  | NO DATA |  | 0 | 0
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890021 |  | 19270 | TEXAS GAS TRANSMISSION CORP |  | OWEN | IN |  | 27+1500 | 27+150 | 847 | 1988-12-06 | 3 | NO |  |  | IN | NO | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 3 | 5 |  | 19881206 | 350 | 600 | BY TEST | 900 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 0; NMDIA: 6; THK: 0.2; SPEC: N/A; SMYS: 0; SEAM: N/A; MANU: N/A; MANYR: 1929; LOCLK: ABOVE GROUND; PNAME: JOHN W. FULLENWIDER; PHONE: 5029268686; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19881205; MARK: YES; MRKTP: MARKERS IN PLACE; STAT: NO; CTEST: Null | ON DECEMBER 6, 1988, AT 8:47AM., A CONTRACTOR WAS GRINDING UP TREE BRANCHES ON TEXAS GAS RIGHT-OF-WAY WITH HYDRO-AX EQUIPMENT AND HIT OUR ABOVEGROUND PIPE. THE BLADE ON THE HYDRO-AX PUT A 4 1/2" BY 1 1/2" HOLE IN THE PIPELINE. NO ONE WASHOSPITALIZED, AND ONLY 36 CUSTOMERS WERE WITHOUT GAS UNTIL 7:00 PM. OF DECEMBER6, 1988.
2021-02-26 10:36 | NO | NO |  | 19890022 |  | 13120 | NATURAL GAS PIPELINE CO OF AMERICA | OFFSHORE |  | LA |  |  |  | 910 | 1988-12-07 |  | YES | W. CAMERON | 551 |  | YES | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 0 |  | 19881207 | 1014 | 1200 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | UNSPECIFIED CORROSION | PRTLK: NO DATA; PRTFL: NO DATA; MLKD: NO DATA; PRTSY: NO DATA; PRTYR: 0; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: NO DATA; PHONE: 0000000000; LOC: NO DATA; ADESC: NO DATA; CAUCR: NO DATA; COAT: NO DATA; PROT: Null; CPYR: 0; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | A WORK CREW FLYING BACK FROM A PLATFORM HAD OBSERVED BUBBLING, I.E. A RELEASE OF GAS. THE LINE HAS BEEN SHUT-IN, BUT INCLEMENT WEATHER IS DELAYING REPAIRES. THEREFORE, WE ARE ISSUING THIS REPORT BASED ON PRELIMENARY INFORMATION. ADDITIONAL INFORMATION WILL BE PROVIDED TO YOU AS SOON AS POSSIBLE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19890023 |  | 21031 | VALERO TRANSMISSION CO | FRIENDSWOOD | GALVESTON | TX |  | 108.7 | 5832+5 | 1500 | 1988-11-28 | 1 | NO |  |  | TX | NO | NO | RUPTURE | 5 | 0 | 0 | 110000 | 98640.6941 | 214891.1194 | Null | 12 | 0 |  |  | 280 | 731 | BY TEST | 1098 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1962; NMDIA: 20; THK: 0.28; SPEC: API 5LX52; SMYS: 1461; SEAM: SUBMERGED ARC; MANU: AMER. MANNEX CORP.; MANYR: 1962; LOCLK: OTHER; LOCLO: OVERHD CANAL CROSSING; PNAME: JOE C. MOORE; PHONE: 4096572703; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: CANAL CROSSING; STAT: NO; CTEST: Null | AT APPROXIMATELY 2:00 PM. A TRACTOR MOWER STRUCK A PHILLIPS PETROLEUM PIPELINE WHICH CAUSED EXPLOSION WHICH IN TURN CAUSED OTHER PIPELINES TO RUPTURE AND EXPLODE. THIS CAUSED OUR PIPELINE TO RUPTURE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890025 |  | 22474 | WESTERN TRANSMISSION CORP |  |  | WY | 82321 | N/A | N/A | 1500 | 1988-08-26 |  | NO |  |  |  | NO | YES | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 30 |  |  | 610 | 1105 | BY TEST | 1105 | CORROSION | CORROSION | EXTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1965; NMDIA: 12; THK: 0.2; SMYS: 0; MANYR: 0; LOCLK: UNDER GROUND; PNAME: DEVEN K. DELAP , DIVISION AREA FOREMAN; PHONE: 3073832800; LOC: EXTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: GALVANIC; COAT: COATED; PROT: YES; CPYR: 1980; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | WHEN THE PIPE WAS INITIALLY INSTALLED INTO THE DITCH, WHAT APPEARS TO HAVE OCCURRED WAS THAT THE APING MACHINE MALFUNCTIONED IN THIS AREA AND DID NOT OVERLAP THE TAPE WHICH LEFT BARE PIPE OF APPROXIMATELY 1/4/ INCH WIDE THE ENTIRE CIRCUMFERENCE OF THE PIPE--APPROXIMATELY 50 FEET LONG. AT THE EXACT POINT OF THE CORROSION LEAK, THE PIPE CRADLE APPEARED TO HAVE DAMAGED THE COATING WHILE NEGOTIATINGA BEND. BOTH PROBLEMS ATTRIBUTED TO THE LEAK.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890026 |  | 3830 | GARLAND, CITY OF | WYLIE | COLLIN | TX | 75018 |  |  | 1017 | 1988-12-15 | 3 | NO |  | N/A | TX | NO | NO | OTHER | 0 | 0 | 0 | 1600 | 1434.7737 | 3125.689 | YES | 0 | 0 |  |  | 75 | 439 | BY TEST | 658 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1988; NMDIA: 16; THK: 0.25; SPEC: X42; SMYS: 0; SEAM: WELDED; VALVE: BALL; MANU: CAMERON; MANYR: 1988; LOCLK: ABOVE GROUND; PNAME: W.E. CARIKER; PHONE: 2142053032; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | BLOW DOWN NEW PIPELINE PRIOR TO FLOWING GAS.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890028 |  | 11808 | LOUISIANA INTRASTATE GAS CORP | RANGE 10E,T15S | ST MARY | LA |  | N/A | 9040+3 | 1215 | 1988-04-18 |  | NO |  |  |  | NO | NO | OTHER | 0 | 0 | 0 | 15000 | 13451.0037 | 29303.3345 | YES | 1 | 45 |  | 19880418 | 720 | 800 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1942 | 8 | 0.22 | X-42 | 0 | N/A |  | N/A | 1942 | UNDER GROUND |  | THOMAS E. TUCKER - DIV. ENGINEERING SUPV. | 3180445825 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 0 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | PIPELINE WAS SHORTED TO ANOTHER LINE IN THE SAME RIGHT OF WAY AND WAS RECIEVINGINADEQUATE CATHODIC PROTECTION AT THAT LOCATION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890029 |  | 11808 | LOUISIANA INTRASTATE GAS CORP | TULLOS | LA SALLE | LA | 71202 | 0.2 | 9+15 | 1040 | 1988-12-23 | 1 | NO |  | N/A |  | NO | NO | LEAK | 0 | 0 | 0 | 5000 | 4483.6679 | 9767.7782 | YES | 1 | 35 |  | 19881223 | 160 | 20 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 0; NMDIA: 4; THK: 0.13; SPEC: N/A; SMYS: 24000; SEAM: N/A; MANU: N/A; MANYR: 0; LOCLK: UNDER GROUND; PNAME: THOMAS E. TUCKER, DIV. ENGINEERING SUPV.; PHONE: 3184458225; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PIPELINE MARKER; STAT: NO; CTEST: Null | TIMBER CUTTING CREW WAS USING A DOZER TO PREPARE ROAD IN THE IMMEDIATE VICINITYOF THE PIPELINE. DOZER OPERATOR ALLOWED BLADE TO GOUGE PIPELINE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19890031 |  | 18516 | SOUTHERN NATURAL GAS CO | EAST OF BROOKSVILLE | NOXUBEE | MS |  | M.P. 211.1 | N/A | 215 | 1988-12-31 | 1 | NO |  | N/A |  | NO | NO | OTHER | 0 | 0 | 0 | 220000 | 197281.3882 | 429782.2389 | Null | 2 | 7 |  | 19881231 | 410 | 500 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: PIPE SEP. FR. COUPLING; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1930; NMDIA: 0.22; THK: 0.31; SPEC: API 5.; SMYS: 35000; SEAM: ELEC.FUSION WLD; VALVE: STYLE 38; MANU: DRESSER; MANYR: 1929; LOCLK: UNDER GROUND; PNAME: CHARLES S. FARRELL, JR. SUPVF. P/L CODE; PHONE: 2053257554; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | CONTINUED RAIN CAUSED THE GROUND SURROUNDING THE PIPELINE TO BECOME SATURATED AND ALLOWED THE PIPE TO SHIFT, RESULTING IN THE PIPE PULLING OUT OF THE MECHANICAL COUPLING.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890035 |  | 18548 | SOUTHWESTERN GAS PIPELINE INC | RURAL | PALO PINTO | TX | 76067 |  | 268+75 | 1625 | 1989-01-11 | 1 | NO |  | N/A |  | NO | NO | LEAK | 0 | 0 | 0 | 3919 | 3377.5423 | 7358.0571 | Null | 1 | 35 |  | 19890111 | 425 | 500 | BY TEST | 1080 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1978; NMDIA: 8; THK: 0.13; SPEC: X-42; SMYS: 42000; SEAM: ELEC.RESIST WLD; VALVE: N/A; MANU: N/A; MANYR: 1978; LOCLK: UNDER GROUND; PNAME: MICHAEL HOWETH SUPV. CODE COMPLIANCE; PHONE: 8173251321; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PAINT CRSS FEN. POSTS; STAT: NO; CTEST: Null | CONTRACTOR PLOWING IN TELEPHONE CABLE FOR SUTHWESTERN BELL TELEPHONE CO. FAILEDTO OBSERVE PIPELINE MARKING OF PAINTED CROSS FENCE AND DID NOT CALL OPERATOR FOR LINE LOCATION AND DEPTH. THREE FENCE POSTS PAINTED WITH THE COMPANIES COLORS WERE 10 FEET 6 INCHES FROM WHERE PIPELINE WAS HIT. PIPELINE WAS IN CONSOLIDATEDROCK IN A CLASS 1 LOCATION 23 INCHES DEEP.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890039 |  | 19160 | TENNESSEE GAS PIPELINE CO | WEST CAMERON |  | LA |  | 507K-200 | 468+40 | 730 | 1989-01-20 |  | YES | W. CAMERON | 173C |  | YES | NO | LEAK | 0 | 0 | 0 | 50000 | 43091.8901 | 93876.7168 | Null | 0 | 0 |  | 19890120 | 835 | 1273 | BY TEST | 1400 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1969 | 20 | 0.5 | X-60 | 60000 | SMLS | N/A | U.S. STEEL | 1968 | OTHER |  | RICHARD A. WINN, SR. REGULATORY ASST. | 7137572581 | EXTERNALLY | OTHER | GREVICE-TYPE | GALVANIC |  | COATED | NO | 0 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | LEAK WAS DISCOVERED ON 20" RISER AT +6' MEAN LOW GULF (MLG) UNDER A RISER CLAMP. RISER IS ATTACHED TO PLATFORM SUPPORT SYSTEM VIA CLAMPS. CORRODED PART OF PIPELINE WAS EXPOSED TO ATMOSHPERE AND, THEREFORE, RELIED ON COATINGS, NOT CATHODIC PROTECTION, FOR CORROSION CONTROL.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890040 |  | 6660 | GREAT LAKES GAS TRANSMISSION CO | CHANDLER TOWNSHIP | CHARLEVOIX | MI | 49713 | MP 722.81,MLV #11-0 |  | 113 | 1989-02-01 | 1 | NO |  | N/A |  | NO | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 37 |  | 19890203 | 910 | 974 | BY TEST | 2000 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: LINE SEPARATED; MLKD: OTHER; MLKDO: WIRE REINFORCED HOSE; PRTSY: COMPRESSOR STATION; PRTYR: 1981; NMDIA: 0.75; THK: 0; SPEC: N/A; SMYS: 0; SEAM: N/A; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: OTHER; LOCLO: INSIDE COMPRESSOR BUILDIN; PNAME: DONALD N. RHOADS - DIRECTOR, EASTERN OPERATIONS; PHONE: 6163478736; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | ON FEBRUARY 1, 1989, A FIRE CAUSED EXTENSIVE DAMAGE IN THE INSIDE OF A COMPRESSOR BUILDING AT GREAT LAKES GAS TRANSMISSION COMPANY'S BOYNE FALLS, MICHIGAN COMPRESSOR STATION. THE EXTERNAL APPURTENANCES OF THE COMPRESSOR PACKAGE WAS DAMAGED AS WELL AS THE BUILDING STRUCTURE. THE STATION WAS UNMANNED AT THE TIME OF IGNITION THEREFORE NO INJURIES WERE SUSTAINED. THE FIRST EMPLOYEE AT THE SCENE EXTINGUISHED THE MAJORITY OF THE FIRE. THE PROBABLE CAUSE OF THE FIRE WAS A STEEL REINFORCED FLEX LINE/FITTING FAILURE THAT SPRAYED NATRUAL GAS AND SEAL OIL ONTO THE HOT POWER TURBINE SECTION OF THE COMPRESSOR. THIS VIEW IS SUPPORTED BY THE PATTERN OF DESTRUCTION. THE MOST SEVERE DAMAGE OCCURRED ON THE WEST SIDE OF THE EXHAUST STACK BETWEEN THE POWER TURBINE & GAS COMPRESSOR. THE ESAST HALF OF THE SEAL OIL TANK WAS SEVERLY CHARRED. AT THAT TANK, THE REFERENCE GAS LINE TO THE SEAL OIL LEVEL SWITCH WAS FOUND SEPERATED.IT WAS AS IF THE FLEX LINE SEGMENT PULLED OUT OF ITS OWN CONNECTOR. IF SO, THE UPPER OPENING RELEASED HIGH PRESSURE GAS AND THE LOWER OPENING RELEASED THE SEAL OIL. BOTH MEDIA WOULD HAVE SPILLED DIRECTLY ON THE STILL HOT,POWER TURBINE CASING. IT SHOULD BE NOTED, THAT EVEN THOUGH THE UNIT WAS SHUT DOWN AT THE TIME OF IGNITION OF THE FIRE, THE SEALOIL WAS STILL BEING PUMPED AND GAS WAS STILL IN THE UNIT PIPING, AND THE POWERTURBINE EXTERNAL SHIELD MAY HAVE BEEN AS HOT AS 1500F. THE ESD SYSTEM EVACUATED THE GAS WITHIN THE COMPRESSOR STATION YARD AND BUILDINGS. ALL OTHER CRITICAL EMERGENCY DEVICES AND PROCEDURES FUNCIONED AS DESIGNED.MATERIAL SPECIFICATIONS UNDER INVESTIGATION.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19890041 |  | 2327 | CHEVRON USA INC | WEST DELTA |  | LA |  |  | 90+92. | 2140 | 1989-01-11 |  | YES | WD 27 | 23 |  | YES | NO | RUPTURE | 12 | 0 | 0 | 250000 | 215459.4506 | 469383.584 | Null | 1 | 15 |  | 19890113 | 1100 | 1461 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | OTHER | RISER | 1965 | 20 | 0.56 | API 5L | 52000 | SEAMLESS | N/A | N/A | 0 | UNDER WATER |  | ROBIN SCHWEHM/DESIGN & CONSTRUCTION ENGINEER | 5043642411 | EXTERNALLY | LOCALIZED PITTING |  | OTHER | SEAWATER | COATED | NO | 0 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | COATING FAILURE IN THE RISER SECTION ALLOWED SALTWATER TO COME IN CONTACT WITH THE PIPE AND CAUSED LOCALIZED PITTING.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890042 |  | 22655 | WILLISTON BASIN INTERSTATE PIPELINE CO | WORLAND | WASHAKIE | WY | 82401 | N/A | N/A | 915 | 1989-01-27 | 1 | NO |  | N/A |  | NO | NO | OTHER | 0 | 0 | 0 | 20000 | 17236.756 | 37550.6867 | YES | 0 | 5 |  | 19890127 | 0 | 0 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: COMPRESSOR; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1950; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: W. EYER, MANAGER; PHONE: 4063597200; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19890044 |  | 13750 | NORTHERN NATURAL GAS CO | LAKEVILLE | DAKOTA | MN | 55044 | MINNESOTA 1P TBS |  | 1220 | 1989-01-15 | 3 | NO |  | N/A |  | NO | NO | LEAK | 0 | 1 | 0 | 0 | 0 | 0 | Null | 0 | 45 |  | 19890115 | 514 | 1076 | BY TEST | 1702 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1980; NMDIA: 0.25; THK: 0.11; SPEC: N/A; SMYS: 0; SEAM: SEAMLESS; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: JOHN CASKEY, CODES COMPL. ENGR.; PHONE: 7138537326; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | DECEASED WAS ASPHYXIATED BY NATURAL GAS WHILE ATTEMPTING TO CLOSE VALVES IN A REGULATOR BUILDING TO ISOLATE A LEAK CAUSED BY THE FAILURE OF A REGULATOR CONTROLLINE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890045 |  | 10037 | KANSAS POWER & LIGHT CO | STAFFORD |  | KS | 67576 | LINE 0423 MPO+1328' | 196+44 | 1530 | 1989-01-13 | 1 | NO |  | N/A |  | NO | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 10 |  | 19890113 | 320 | 535 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: MECHANICAL JOINT; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1930; NMDIA: 4; THK: 0.24; SPEC: N/A; SMYS: 24000; SEAM: LAPWELD; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: UNDER GROUND; PNAME: JAMES W. INGRAM, VP GAS OPS; PHONE: 9132961959; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: MARKERS IN PLACE.; STAT: NO; CTEST: Null | LANDOWNER WAS FARMING AT 16" TO 18" DEPTH & HIT 4" PIPELINE, PULLING ONE JOINT OF PIPE OUT OF MECHANICAL COUPLING. AVERAGE DEPTH IS 24", DEPTH WAS 17" AT LOCATION OF INCIDENT.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19890059 |  | 18484 | SOUTHERN CALIFORNIA GAS CO | VALENCIA | LOS ANGELES | CA | 91355 |  |  | 1158 | 1988-11-02 | 1 | NO |  | N/A |  | NO | NO | RUPTURE | 7 | 0 | 0 | 160000 | 143477.3733 | 312568.901 | Null | 3 | 12 |  | 19881102 | 680 | 985 | BY TEST | 1500 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1975 | 20 | 0.47 | API-5LX | 52000 | SEAMLESS | N/A | N/A | 0 | UNDER GROUND |  | R. L. RUDZIK, MANAGER OF TRANSMISSION | 2136892345 | INTERNALLY | LOCALIZED PITTING |  | OTHER | CHEMICAL | COATED | YES | 1977 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | THE REGULATOR AND METER PERSONNEL MADE AN IMMEDIATE CHECK OF THE 26,000 FEET OF 4" AND 6" STEEL HIGH PRESSURE TAPLINE AND UPSTREAM REGULATOR STATION. ALL EQUIPMENT WAS FOUND TO BE FUNCTIONING PROPERLY AND NO LINE BREAKS WERE EVIDENT. PRESSURES TAKEN ALONG THE HIGH PRESSURE PIPELINE INDICATED NORMAL PRESSURES. IT WAS DETERMINED THAT THE PRESSURE LOSS RESULTED FROM AN EQUIPMENT PROBLEM AT THE SANTAQUIN #1 DISTRICT REGULATOR STATION. THE HIGH PRESSURE BLOCK VALVE AT THE STATION INLET HAD NORMAL PRESSURE INDICATED. THE COMPLETE LOSS OF PRESSURE IN THEDISTRIBUTION PIPING NECESSITATED AT TOTAL SHUTDOWN OF 659 COMMERCIAL AND RESIDENTIAL REGULATOR AND METER SETS. NATURAL GAS WAS TURNED BACK INTO THE DISTRIBUTION PIPING SYSTEM AT 2:16 AM. FEBRUARY 9, SIX HOURS AND 16 MINUTES AFTER THE INITIAL DISCOVERY OF SERVICE INTERRUPTION. THE PRESSURE IN THE SYSTEM WAS CONTROLLED BY MONITORING THE BYPASS VALVE AT THE STATION VALVE ASSEMBLY. A SUBSEQUENT CHECK OF THE STATION EQUIPMENT FOUND AN INLINE 2" - 300 ANSI STRAINER-FILTER TO BECOMPLETELY PLUGGED WITH VALVE GREASE WHICH MOVED INTO THE STRAINER AS A RESULT OF THE VERY HIGH STATION GAS FLOWS DUE TO EXTREMELY LOW TEMPERATURES. THE INLINE FILTER WAS REMOVED AND NORMAL REGULATING CAPABILITIES WERE RESUMED AT 10:00 AM. FEBRUARY 9, 1989.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19890060 |  | 22175 | WARREN PETROLEUM CO (NEW MEXICO GAS PIPELINE) |  | CRANE | TX | 79731 | N/A | SEC.25 | 2130 | 1989-02-13 | 1 | YES |  | B-26 |  | NO | NO | OTHER | 0 | 0 | 0 | 200000 | 172367.5605 | 375506.8672 | Null | 6 | 0 |  | 19890213 | 200 | 250 | BY TEST | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: COMPRESSOR COMPONENT; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1947; NMDIA: 0; THK: 0; SPEC: N/A; SMYS: 0; SEAM: N/A; VALVE: N/A; MANU: CLARK BROS.; MANYR: 1947; LOCLK: ABOVE GROUND; PNAME: M. D. TURNER PLANT ENGINEER; PHONE: 9153322191; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | AFTER BEING FRACTRUED, THE CROSSHEAD WAS FORCED INTO THE COMPRESSOR CYLINDER HOUSING BY THE CONNECTING ROD WHICH HAD ENOUGH FORCE TO BREAK THE CYLINDER ANCHOR BOLTS AND DISCHARGE PIPING ALLOWING GAS TO ESCAPE. THE IGNITION SOURCE WAS A SPARK CAUSED BY THE METAL TO METAL COLLISION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890061 |  | 1552 | BLUE DOLPHIN PIPELINE CO |  |  | TX |  | 32950' |  | 1420 | 1989-02-24 |  | YES | GA | 286 |  | YES | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 9 | 40 |  | 19890225 | 350 | 1000 | BY TEST | 2175 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | WELD | GIRTH | STEEL |  | PIPELINE |  | 1965 | 20 | 0.5 | API-5LX | 0 | SEAMLESSS | N/A | N/A | 1965 | UNDER WATER |  | JOHN C. MCDUFFIE- ENGINEER | 7136213993 | INTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1965 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | COAST GUARD NOTIFIED US OF SPILL REPORTED IN GA 286 ABOUT 1420 HRS ON 02-24-89 BOUY DROPPED HELICOPTER 1630 HRS; LINE SHUT IN 1725 HRS; ZERO LINE PRESSURE 2400HRS; INSTALLED 1500 WP 20" BOLT-ON, SPLIT SLEEVE PLIDCO CLAMP 1432 HRS ON 02-27-89; TESTED 450 PSI, 0215 HRS 02-28-89.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19890062 |  | 19570 | TRANSCO GAS PIPELINE CORP | CARLSTADT | BERGEN | NJ | 07072 | MP. 1825.73 |  | 435 | 1989-02-06 | 1 | NO |  | N/A |  | NO | NO | OTHER | 0 | 0 | 0 | 300000 | 258551.3407 | 563260.3009 | Null | 0 | 3 |  | 19890206 | 395 | 400 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; MLKD: OTHER; MLKDO: STAINLESS STEEL; PRTSY: OTHER; PRTSO: VAPORIZER; PRTYR: 1979; NMDIA: 4; THK: 0.12; SPEC: SS SA312; SMYS: 304; SEAM: N/A; VALVE: N/A; MANU: BS&B; MANYR: 1979; LOCLK: ABOVE GROUND; PNAME: B. R. LANDES, SR. COMPLIANCE ANALYST; PHONE: 7134392001; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | A SMALL CRACK WAS FOUND IN A TUBE IN THE COIL OF THE H-4B VAPORIZER AT THE LNG FACILITY. METALLURGISTS NOW HAVE THE TUBE SECTION CONTAINING THE CRACK AND ARE IN THE PROCESS OF INVESTIGATING REPORT, A SUPPLEMENTAL REPORT WILL BE SENT TO DOT ALONG WITH A COPY OF THE REPORT.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890063 |  | 19160 | TENNESSEE GAS PIPELINE CO | HOLLY SPRINGS | MARSHALL | MS | 38635 | 67-4+10.90 | 572+72 | 400 | 1989-01-27 | 1 | NO |  | N/A |  | NO | NO | LEAK | 0 | 0 | 0 | 50000 | 43091.8901 | 93876.7168 | Null | 1 | 15 |  |  | 550 | 780 | BY TEST | 1059 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | LONGITUDINAL | STEEL |  | PIPELINE |  | 1951 | 30 | 0.31 | API-5LX | 52000 | SAW | N/A | CONSOL.WESTERN | 1950 | UNDER GROUND |  | RICHARD A. WINN, SR. REGULATORY ASST. | 7137572581 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL |  | NO |  | NO DATA |  | 0 | 0 | THE CAUSE OF THE LEAK WAS DETERMINED TO BE DUE TO A MANUFACTUING DEFECT IN THE LONGITUDINAL WELD.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19890064 |  | 19160 | TENNESSEE GAS PIPELINE CO | LYNNFIELD | ESSEX | MA |  | 270C-301+2.05 | 108+47 | 155 | 1989-02-02 | 3 | NO |  | N/A |  | NO | NO | RUPTURE | 16 | 0 | 1 | 50000 | 43091.8901 | 93876.7168 | Null | 2 | 10 |  | 19890202 | 605 | 610 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: LONGITUDINAL SEAM; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1951; NMDIA: 12.75; THK: 0.28; SPEC: API-5LX; SMYS: 42000; SEAM: ERW; VALVE: N/A; MANU: YOUNGSTOWN; MANYR: 1950; LOCLK: UNDER GROUND; PNAME: RICHARD A. WINN, SR. REGULATORY ASST.; PHONE: 7137572581; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | A SUPPLEMENTAL REPORT WILL FOLLOW ONCE THE INDEPENDENT LAB REPORT DETERMINES THE CAUSE OF THE PIPE FAILURE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890065 |  | 18456 | SOUTHEAST ALABAMA GAS DISTRICT | COTTONTON | RUSSELL | AL | 36851 | SECT. NO. 100+00 |  | 1010 | 1989-02-16 | 1 | NO |  | N/A |  | NO | NO | RUPTURE | 6 | 0 | 0 | 7894 | 6803.3476 | 14821.256 | Null | 0 | 30 |  | 19890216 | 500 | 800 | BY TEST | 1200 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1966; NMDIA: 8.63; THK: 0.19; SPEC: API-5LX 42; SMYS: 42000; SEAM: WELDED; VALVE: N/A; MANU: L. B. FOSTER; MANYR: 1966; LOCLK: UNDER GROUND; PNAME: ARNIE C. COBB, JR.; PHONE: 2052224177; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: YELLOW FLAGS; STAT: YES; CTEST: Null | CONTRACTOR HAD FOUND UNACCEPTED SOIL ON STATE OF ALABAMA HIGHWAY PROJECT NO. 1246-6 AND FAILED TO NOTIFY GAS COMPANY THAT HE HAD RUN INTO THIS CONDITION. COROSS SECTION OF THIS AREA DID NOT SHOW ANY CUTTING OF EXISTING GRADE NECESSARY AT STATION 100 + 00. WHILE REMOVEING THIS UNACCEPTABLE SOIL, OPERATORS EQUIPMENT (PAN TYPE EARTH MOVER) STRUCK AND DAMAGED 8" TRANSMISSION GAS MAIN.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890066 |  | 18536 | SOUTHWEST GAS CORP | WADSWORTH | STOREY | NV |  | MP 2.54 | 118+11 | 1720 | 1989-02-03 | 1 | NO |  | N/A | NV | NO | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 5 | 55 |  | 19890203 | 620 | 830 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | FITTING | STOPPLE | STEEL |  | PIPELINE |  | 1989 | 16 | 0.38 | API 5LX | 52000 | WELDED | N/A | N/A | 0 | UNDER GROUND |  | C. E. STONER, MGR. OF GAS OPERATIONS | 7028825776 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION | T. D. WILLIAMSON STOPPLE FITTING | NO |  | NO DATA |  | 0 | 0 | A TRANSMISSON CREW WAS DISPATCHED FROM CARSON CITY. THE PRESSURE WAS LOWERED IN THE LINE. AFTER THE LINE WAS UNCOVERED, IT WAS DETERMINED THAT A 16" T.D. WILLIAMSON STOPPLE FITTING HAD A 9"-10"-LONG CRACK ON A FILET WELD. THE WELD WAS REPARIED AND THE LINE WAS PUT BACK IN SERVICE AT APPROXIMATELY 4:45 AM. ON FEBRUARY 4, 1989.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890074 |  | 20245 | UNITED TEXAS TRANSMISSION CO | PORT NECHES | JEFFERSON | TX |  | .18 | 9+36 | 1430 | 1989-02-20 | 3 | NO |  | N/A |  | NO | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 5 |  | 19890220 | 240 | 292 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1943 | 12 | 0.25 | UNKNOWN | 24000 | SEAMLESS | N/A | N/A | 1943 | ABOVE GROUND |  | LAURI ALTIERI/ SUPV. ENG. RECORDS | 7139633236 | EXTERNALLY | LOCALIZED PITTING |  | OTHER | ATMOSPHERIC | BARE | YES | 1949 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890075 |  | 1995 | CABOT GAS SUPPLY CORP | AMHERST | LAMB | TX |  | CABOT/MAPLES | 2232+9 | 815 | 1989-03-08 | 1 | NO |  | N/A |  | NO | NO | OTHER | 0 | 0 | 0 | 45000 | 38782.7011 | 84489.0451 | Null | 2 | 30 |  | 19890309 | 460 | 553 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: PIGGING OPERATION; MLKD: OTHER; MLKDO: LIQUIDS; PRTSY: PIPELINE; PRTYR: 1949; NMDIA: 8.63; THK: 0.32; SPEC: LW; SMYS: 1792; SEAM: N/A; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: UNDER PAVEMENT; PNAME: BOB TOMLINSON, AREA MANAGER; PHONE: 9155865838; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | AT APPROXIMATELY 11:45PM ON TUESDAY, MARCH 7, 1989 LIQUID FLOWED FROM THE MAPLE PLANT X PIPELINE INTO THE CABOT GAS SUPPLY, LUBBOCK TO FARWELL 8" +MAINLINE AT THE CABOT/MAPLE INTERCONNECT, LOCATED THREE MILES WEST OF AMHERST. APPROXIMATELY TWO WEEKS AGO, (EXACT DATE NOT KNOWN) MAPLE PUT A PIG IN THEIR PLANT-X PIPELINE. THE PIG DIDN'T COME IN AND GAS CONTINUED TO FLOW. ON MARCH 7TH,ACCORDING TO CABOT INSTRUMENTS AT THE INTERCONNECT, LIUID BEGAN FLOWING INTOTHE CABOT SYSTEM. THE DUMP LINES ON MAPLE'S SCRUBBER (AT THE INTERCONNECT), HAD BEEN DISCONNECTED AT A PREVIOUS TIME, LEAVING THE MAINLY CONDENSATE MIXTURE NO WHERE TO DISCHARGE OUTSIDE THE SYSTEM. ON WEDNESDAY MORNING, MARCH 8, 1989 CABOT AND ENERGAS EMPLOYEES WERE DISPATCHED TO VARIOUS LOCATIONS ALONG THE CABOT MAINLINE TO START DRAINING LIQUID AND VENTING GAS. AN INVESTIGATION IS STILL UNDER WAY TO DETERMINE THE AMOUNT OF LOSS. AN UNDETERMINED AMOUNT OF POSITIVE METERS WERE DAMAGED AND AN INDETERMINED NUMBER OF CUSTOMERS WERE SHUT IN. WE NOTIFIED THE TRRC ON MARCH 9, 1989.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890076 |  | 18516 | SOUTHERN NATURAL GAS CO |  |  | LA |  | M.P. 12.2 |  | 1705 | 1989-02-28 |  | YES | MAIN PASS | 151 |  | YES | NO | OTHER | 0 | 0 | 0 | 50000 | 43091.8901 | 93876.7168 | Null | 12 | 0 |  | 19890303 | 1000 | 1148 | BY TEST | 1435 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: BRANCH CONNECTION; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1983; NMDIA: 2.38; THK: 0.22; SPEC: API 51; SMYS: 35000; SEAM: N/A; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: UNDER WATER; PNAME: C.S. FARREL, SUPV. P/L CODE & SAFETY REGULATIONS; PHONE: 2053257554; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; MARK: YES; MRKTP: SATTELITE; STAT: YES; CTEST: Null | ANCHOR CABLE FROM A CONSTRUCTION BARGE BECAME TANGLED IN AN UNDERWATER BYPASS VALVE ASSEMBLY. VALVE ASSEMBLY WAS BROKEN OFF OF PIPELINE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890077 |  | 19235 | TEXAS EASTERN GAS PIPELINE CO |  | TERREBONNE | LA |  | 15.37 |  | 906 | 1989-03-05 | 1 | NO |  | N/A |  | NO | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19890305 | 0 | 0 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: ELECTRICAL EQUIP.; MLKD: OTHER; PRTSY: OTHER; PRTYR: 1971; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: ROBET E. THOMURE; PHONE: 7137595454; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | PREPARATIONS WERE BEING MADE FOR THE INSTALLATION OD A VARIABLE SPEED MOTOR CONTROLLER FOR AN ELECTRIC MOTOR DRIVEN GAS COMPRESSOR AT THE POINTE AU CHEINFACILITY. THE LOAD BREAKER SUPPLYING ELECTRICAL POWER TO THE ELECTRIC MOTOR DRIVEN GAS COMPRESSOR HAD BEEN REMOVED. THE EMPLOYEES PERFORMING THE WORK INSTALLED A GROUNDING CONDUCTOR ONTO A TERMINAL OF THE SURGE CAPACITOR, WHICH ISCONNECTED TO THE ENERGIZED SIDE OF THE 4160 VOLT BUS. DURING THIS WORK AN ELECTRIC ARC OCCURED BETWEEN THE MAIN BUS AND THE GROUNDING CONDUCTOR. ONE EMPLOYEE RECEIVED SCOND AND THIRD DEGREE BURNS ON FIFTY TO SIXTY PERCENT OF HIS BIODY. TWO EMPLOYEES EACH RECEIVED FIRST AND SECOND DEGREE BURNS TO THE FACE AND CHEST. THESE THREE EMPLOYEES WERE ADMITTED AS IN-PATIENTS TO HOSPITALS IN NEW ORLEANS AND HOUMA, LA., RESPECTIVELY. AN ADDITIONAL EMPLOYEE RECEIVED FIRST AND SECOND DEGREE BURNS ON HIS LEFT HAND AND WAS TREATED AND RELEASED ON MARCH 6. NO NATURAL GAS WAS INVLOVED IN THIS INCIDENT; HOWEVER IT IS BEING REPORTED UNDER THE CRITERIA FOR AN INCIDENT IN 49 CFR PART 191.3 AS AN EVENT THAT IS SIGNIFICANT IN THE JUDGEMENT OF THE OPERATOR.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19890102 |  | 14225 | RINGWOOD GATHERING CO | SECTION 34, T22N, R10W, | MAJOR | OK | 73768 |  | 1365+8 | 822 | 1989-04-20 | 1 | NO |  | N/A |  | NO | NO | OTHER | 0 | 0 | 2 | 40000 | 34473.5121 | 75101.3734 | Null | 0 | 5 |  | 19890420 | 628 | 775 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: NO DATA; MLKD: STEEL; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1953; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: CAROL CAUL , CONSULTANT; PHONE: 7136682250; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | A DIFFERENTIAL PRESSURE CONTROLLER ESCAPED THE LOCATED CLOSED POSITION AND PERMITTED A PNEUMATIC VALVE OPERATOR OPEN WHILE THE INJURED MEN WERE OPENING THE ORIFICE METER FLANGES PREPARATORY TO MAKING A ROUTINE INSPECTION OF THE ORIFICE PLATE. THE RESULTING ESCAPE OF GAS WAS IGNITED BY AN APPARENT SPARK.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19890103 |  | 8040 | ILLINOIS POWER CO | CHAMPAIGN | CHAMPAIGN | IL | 61820 | N/A | N/A | 1400 | 1989-03-31 | 3 | NO |  | N/A | IL | NO | NO | OTHER | 0 | 1 | 0 | 0 | 0 | 0 | Null | 0 | 1 |  | 19890331 | 300 | 415 | BY TEST | 625 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | MECHANICAL JOINT |  | STEEL |  | PIPELINE |  | 1966 | 12 | 0.25 | API5LGRB | 35000 | EW. OR SEAMLESS | N/A | N/A | 0 | OTHER | IN EXCAVATION | G.E. CARTER | 2174246853 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | ONE-PLIDCO SPLIT & SLEEVE FITTING. | NO |  | NO DATA |  | 0 | 0 | ON 3/31/89 AT APPROXIMATELY 2:00 P.M., A 12" TRANSMISSION MAIN UNDER 300 PSI OFPRESSURE SEPARATED WHERE A PLIDCO SPLIT AND SLEEVE FITING HAD BEEN INSTALLED. THE FITTING JOINTED THE ENDS OF A REPLACED SECTION OF THE MAIN AND THE EXISTING PORTION OF THE PIPELINE. THE OPERATING PRESSURE OF 700 PSI WAS BEING RESTORED IN100 INCREMENTS PRIOR TO THE ACCIDENT. BECAUSE OF THIS INCIDENT, AN ILLINOIS POWER EMPLOYEE, WHO WAS ADJACENT TO THE ABOVE DESCRIBED FITTING IN THE EXCAVATION, WAS FATALLY INJURED. THE CAUSE OF THIS OCCURRENCE IS UNDER INVESTIGATION BY ILLINOIS POWER.SUPPLEMENT : THE INVESTIGATION OF THIS INCIDENT BY ILLINOIS POWER CO IS NOT YETCOMPLETE. ARNOLD BLOCKMAN, ATTORNEY FOR ILLINOIS POWER CO WILL BE DISCUSSING THIS MATTER WITH HIS CONSULTANT AS TO THE CAUSE OF THIS INCIDENT. AFTER THAT INPUT, ILLINOIS POWER CO WILL BE BETTER ABLE TO DETERMINE ANY NEEDED FURTHER COURSE OF INVESTIGATION TO DETERMINE CAUSE. WE SHALL KEEP YOU ADVISED.FINAL UPDATE: THE INVESTIGATION OF THE INCIDENT BY ILLINOIS POWER CO IS COMPLETE. THE INCIDENT WAS CAUSED BY VAGUE, AMBIGUOUS AND MISLEADING INFORMATION SUPPLIED BY THE MANUFACTURER OF THE MECHANICAL CONNECTOR.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19890104 |  | 18516 | SOUTHERN NATURAL GAS CO | SOUTH PASS "B" |  | LA |  | M.P. 0.00 | 0+00 | 1940 | 1989-03-19 |  | YES | SOUTH | 60 |  | NO | NO | OTHER | 0 | 7 | 10 | 0 | 0 | 0 | Null | 0 | 0 |  | 19890320 | 0 | 1148 | BY TEST | 1435 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: NO DATA; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1974; NMDIA: 18; THK: 0.5; SPEC: API5LX; SMYS: 52000; MANYR: 0; LOCLK: OTHER; LOCLO: OFFSHORE PLATFORM; PNAME: CHARLES S. FARRELL-SUPV. P/L CODE & SAFETY REG.; PHONE: 2053257554; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | ON THE MORNING OF SUNDAY, MARCH 19, 1989, PIPELINES UNLIMITED SERVICES (PLUS),SOUTHERN'S INDEPENDENT CONTRACTOR, ARRIVED AT ARCO'S SOUTH PASS BLOCK 60 "B"PLATFORM. AT APPROXIMATELY 7:00 PM, A SUBCONTRACTOR SELECTED BY PLUS INITIATEDCOLD CUTTING OF THE 18" PIPELINE AT APPROXIMATELY THE +15 FOOT LEVEL BELOW ACLOSED VALVE AT APPROXIMATELY THE +20 FOOT LEVEL. THE COLD CUTTING DEVICE WASBEING OPERATED BY AN AIR COMPRESSOR ON A BOAT MOORED ADJACENT TO THE PLATFORMAND DIRECTLY UNDER THE RISER. WHEN TOTAL PENETRATION WAS FIRST MADE INTO THELINE, GAS AND LIQUID OOZED FROM THE CUT UNDER PRESSURE. THE SUBCONTRACTOR THENRE-RIGGED THE CUTTING DEVICE TO ALLOW THE COLD CUTTER TO BE OPERATED FROM THEWORK BOAT. CUTTING WAS RESUMED WITHOUT THE PREMISSION OF ANY REPRESENTATIVE OFSOUTHERN. SHORTLY THEREAFTER, THE LINE WAS COMPLETELY SEVERED AND GAS ANDLIQUIDS WERE EXHAUSTED FROM THE PIPELINE. THE GAS WAS IGNITED, CREATING A FIRE;SEVERAL OTHER PIPELINESTHEREAFTER EXPLODED, ENGULFING THE PLATFORM IN FLAMES.EXACT CAUSE OF THIS INCIDENT AND THE FACTORS THAT CONTRIBUTED TO IT ARE UNDERINVESTIGATION. ALTHOUGH THE INVESTIGATION HAS NOT BEEN COMPLETED, IT IS APPARENTTHAT ARCO, THE PLATFORM OPERATOR, HAD NOT PROPERLY BLED THE LINE DOWN IN ORDERPROPERLY TO RELIEVE IT OF PRESSURE. SUPPLEMENTAL REPORT 12/15/94 INDICATESTHAT LINE WAS OUT OF SERVICE... PLATFORM OPERATOR WAS TO HAVE RELIEVED LINE OFPRESSURE. CAUSE CHANGED FROM OTHER, TO DAMAGE BY OUTSIDE FORCES.. SUBMITTED BYERIC THOMAS (205) 325-7632.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890106 |  | 11680 | LONE STAR GAS CO | LINE 71-5-2-1 | COTTLE | TX |  | AERIAL MARKER #15 | 677+92 | 145 | 1989-02-03 | 1 | NO |  | N/A |  | NO | NO | OTHER | 0 | 0 | 0 | 20654 | 17800.398 | 38778.5942 | Null | 2 | 45 |  | 19890203 | 285 | 350 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 0 | 4.5 | 0.2 | GRADE A | 30000 | LAP WELD | N/A | N/A | 0 | UNDER GROUND |  | CHRIS FRANKLIN | 8175225642 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | NO DATA |  | NO |  | NO DATA |  | 0 | 0 | THERE IS NO RECORDED TEST PRESSURE ON THIS SEGMENT OF PIPE. LINE 71-5-2-1 WAS PURCHASED FROM UNITED GAS COMPANY IN 1967 AN MAXIMUM ALLOWABLE OPERATING PRESSURE WAS EXTABLISHED IN ACCORDANCE WITH 49 CFR 192.619(A)(3).
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19890107 |  | 3230 | DELHI GAS PIPELINE CORP | VICTORIA | VICTORIA | TX | 77901 | BV-26-BV-24 | 1326+5 | 900 | 1989-03-02 | 3 | NO |  | N/A | TX | NO | NO | LEAK | 0 | 0 | 0 | 24000 | 20684.1073 | 45060.8241 | Null | 1 | 0 |  | 19890302 | 240 | 824 | BY TEST | 2360 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1984 | 12.75 | 0.25 | API 5L X-42 | 49900 | ERW | N/A | NIPPON | 1984 | UNDER PAVEMENT |  | CLAY Y. SMITH, SAFETY & ENVIRONMENTAL AFFAIRS COORDINATOR | 5128828402 | INTERNALLY | LOCALIZED PITTING |  | OTHER | H2SK | COATED | YES | 1984 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890108 |  | 19325 | TEXAS UTILITIES FUEL CO | RIESEL | MCLENNAN | TX |  | 1 MILE SOUTH OF BUF6 |  | 1134 | 1989-03-08 | 2 | NO |  | N/A |  | NO | NO | LEAK | 0 | 0 | 0 | 3000 | 2585.5134 | 5632.603 | Null | 3 | 0 |  | 19890308 | 410 | 988 | BY TEST | 1250 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1958 | 12 | 0.25 | X-42 | 1647 | ERW | N/A | N/A | 0 | UNDER GROUND |  | B.G. STONE , GAS OPERATIONS SUPERVISOR | 8177392575 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 0 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | SHORTED CASING, LOCALIZED EXTERNAL PITTING. SMALL LEAK.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19890109 |  | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | NEW HAVEN TOWNSHIP | GRATIOT | MI |  | 40.5 | 2114+6 | 1755 | 1989-02-23 | 1 | NO |  | N/A |  | NO | NO | RUPTURE | 41.5 | 0 | 0 | 300000 | 258551.3407 | 563260.3009 | Null | 1 | 50 |  | 19890223 | 753 | 970 | BY CFR 192.619(A)(3) | 970 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1952; NMDIA: 24; THK: 0.31; SPEC: API 5LX-52; SMYS: 52000; SEAM: ERW; VALVE: N/A; MANU: A.O. SMITH; MANYR: 1951; LOCLK: UNDER GROUND; PNAME: BRUCE J. NIEMAN, MANAGER CODES & STANDARDS; PHONE: 3132566615; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19880714; MARK: YES; MRKTP: STAKES; STAT: YES; CTEST: Null | CONTRACTOR PLOWING INFIELD TILE ON JULY 15, 1988,STRICK AND DAMAGED LINE, DID NOT REPORT DAMAGE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890110 |  | 19160 | TENNESSEE GAS PIPELINE CO | TORRINGTON | LITCHFIELD | CT | 06790 | 259A-102+4.87 | 257+13 | 815 | 1989-04-11 | 2 | NO |  | N/A |  | NO | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 58 |  | 19890411 | 489 | 760 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1952; NMDIA: 4.5; THK: 0.24; SPEC: API STD. 5L; SMYS: 30000; SEAM: LAPWELD; MANU: JONES&LAUGHLIN; MANYR: 1951; LOCLK: UNDER GROUND; PNAME: RICHARD A. WINN, REGULATORY ANALYST; PHONE: 7135752581; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19890327; MARK: YES; MRKTP: TEMPORARY STAKES; STAT: YES; CTEST: Null | OUTSIDE PARTY/THIRD PARTY CONTRACOTR'S BACKHOE SEVERED LINE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890111 |  | 6914 | GULF STATES PIPELINE CORP | SHREVEPORT | CADDO | LA | 71107 | 31.05 | 1639 6 | 325 | 1989-04-02 | 3 | NO |  | N/A |  | NO | NO | LEAK | 0 | 0 | 0 | 50000 | 43091.8901 | 93876.7168 | YES | 8 | 15 |  | 19890403 | 300 | 988 | BY TEST | 1990 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: NO DATA; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1974; NMDIA: 12; THK: 0.38; SPEC: API5LX42; SMYS: 42000; SEAM: ERW; VALVE: N/A; MANU: LONE STAR STEEL; MANYR: 1973; LOCLK: UNDER WATER; PNAME: A.E. SCHLEMMER, P.E.; PHONE: 3182220026; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | THE CAUSE IS UNKNOWN AS IT OCCURRED UNDER HIGH WATERS AND IS STILL INACCESSIBLE. ACCORDING TO THE RECORD, 1988 AND 1989 HAVE SEEN THE HIGHEST BAYOU FLOOD LEVELS SINCE THE LINE WAS COMPLETED, MAY 9, 1974.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19890113 |  | 4280 | EL PASO NATURAL GAS CO | IGNACIO | LA PLATA | CO |  | N/A | 57+31 | 300 | 1989-03-02 | 1 | NO |  | N/A |  | NO | NO | RUPTURE | 12.3 | 0 | 0 | 334149 | 287982.2399 | 627376.2209 | Null | 3 | 45 |  | 19890306 | 461 | 500 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | OTHER | L TO DRIP ASSEMBLY | STEEL |  | OTHER | DRIP ASSEMBLY | 1957 | 12.75 | 0.26 | N/A | 0 | N/A | N/A | N/A | 0 | ABOVE GROUND |  | RICHARD FAVILA, SR. ENGINEER | 9155412062 | INTERNALLY | LOCALIZED PITTING |  | OTHER | ACCUMULATION OF WATER | COATED | YES | 1958 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | A RUPTURE OCCURRED ON THE INTERCONNECTING LINE TO A DRIP ASSEMBLY ON LATERAL 4A-41. THE 90 DEGREE "L" OF THE DRIP SHOWED SEVERE INTERNAL CORROSION DUE TO ACCUMULATION OF WATER IN THE DRIP ASSSEMBLY. THE SOURCE OF IGNITION HAS NOT BEEN DETERMINED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19890114 |  | 405 | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | HIGH ISLAND BLOCK A-494 |  | TX |  | X=3,629,983 | Y=179, | 920 | 1989-03-08 |  | YES | H.I. | A-494 |  | YES | NO | LEAK | 0 | 0 | 0 | 130000 | 112038.9143 | 244079.4637 | Null | 0 | 2 |  | 19890308 | 990 | 1440 | BY TEST | 2885 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | MECHANICAL JOINT |  | STEEL |  | PIPELINE |  | 1984 | 6 | 0 | 900#ANSI SPOOL | 0 | REPAIR UNIT | N/A | HYDROTECH | 1986 | UNDER WATER |  | MICHAEL R. LASKOWSKI, LEAD ENGR. | 3134962457 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION | 6" 900# ANSI, SPOOL PIECE REPAIR UNIT | YES | 19860924 | WATER |  | 1 | 1550
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19890115 |  | 13750 | NORTHERN NATURAL GAS CO | SALEM | MCCOOK | SD | 57058 | SALEM TOWN BORDER |  | 1400 | 1989-03-21 | 1 | NO |  | N/A |  | NO | NO | OTHER | 0 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 0 |  | 19890322 | 700 | 800 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: PORTABLE TEST APPARATUS; MLKD: NO DATA; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1956; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: JOHN W. CASKEY, CODE COMP. ENGR.; PHONE: 7138537326; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | MEASUREMENT TECHNICIAN CONNECTED A 125 PSIG RATED DIFFERENTIAL PRESSURE TEST APPARATUS TO PIPING OPERATING AT 700 PSIG. THE TEST APPARATUS FAILED AND A RELEASE OF GAS OCCURRED FOR A FEW SECONDS.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890116 |  | 1088 | BALTIMORE GAS & ELECTRIC CO | OWINGS MILLS | BALTIMORE | MD | 21117 | N/A | N/A | 1450 | 1989-06-02 | 3 | NO |  | N/A | MD | NO | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 5 |  | 19890602 | 310 | 340 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: MECHANICAL JOINT; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1931; NMDIA: 20; THK: 0.31; SPEC: N/A; SMYS: 35000; SEAM: N/A; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: UNDER GROUND; PNAME: MICHAEL A. POMETTO, PRINCIPAL ENG.; PHONE: 3012914549; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | AT APPROXIMATELY 1450 HOURS ON JUNE 2, 1989, THE PRINCIPAL GAS SYSTEM OPERATOR AT THE SPRING GARDENS GAS CONTROL CENTER NOTED AN INSTANTANEOUS INCREASE IN GAS FLOW AT THE OWINGS MILLS GATE STATION ON TYHE INSTRUMENTATION ON THE CONTROL PANEL. A CORRESPONDING PRESSURE DROP FROM 310 PSI TO 235 PSI WAS ALSO NOTED. AT 1510 HOURS, GAS CONTROL RECIEVED A REPORT OF A GAS LEAK AT 10426 REISTERSTOWN ROAD, OWINGS MILLS, MD. COMPANY CREWS WERE DISPATCHED TO THE SITE AND FIRE AND POLICE DEPARTMENTS WERE NOTIFIED. COMPANY REPRESENTATIVES DISCOVERED A SEVERE LEAKIN A 20 INCH GAS TRANSMISSION PIPELINE. THE UPSTREAM VALVE AT THE OWINGS MILLSGATE STATION WAS OPERATED AT 1520 HOURS. THE DOWNSTREAM MAIN LINE VALVE WAS OPERATED 1555 HOURS. THE LEAKING NATURAL GAS DID NOT EXPLODE OR IGNITE. THERE WERE NO INJURIES NOR FATALITIES. NO BUILDINGS OR STRUCTURES WERE DAMAGED OTHER THAN THE GAS PIPING. THE INCIDENT RESULTED FROM THE PIPE PULLOUT OF A 20 INCH COMPRESSION COUPLING. RELOCATION OF THE PIPELINE HAD RECENTLY BEEN PERFORMED 52 FEET DOWNSTREAM OF THE LEAK. THE COUPLING WAS NOT UNCOVERED FOR THE WORK. IT IS DEDUCED THAT THE CONSTRUCTION WORK UNKNOWINGLY DISTURBED THE PIPELINE ANCHORING SUFFICIENTLY TO ALLOW THE COUPLING TO PULL OUT.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19890118 |  | 8326 | ITAWAMBA INDUSTRIAL GAS CO | FULTON | ITAWAMBA | MS | 38843 | N/A | N/A | 2110 | 1989-05-03 | 1 | NO |  | N/A |  | NO | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 21 | 10 |  | 19890503 | 35 | 120 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1977 | 4 | 0.13 | API 5L | 42000 | SEAMLESS | PLUG | ROCKWELL | 1977 | UNDER GROUND |  | W.L. HEERING, ENGINEERING MANAGER | 6018622182 | EXTERNALLY | NO DATA |  | OTHER | STRAY CURRENT | COATED | YES | 1975 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | THE LEAK WAS A VERY SMALL PIN HOLE ON THE BOTTOM OF THE PIPE AND APPEARED TO BESOMETHING THAT WOULD RESULT FROM ELECTROYSIS CAUSED BY DAMAGE TO A SMALL AREA OF THE COATING. THE REPAIR WAS ACCOMPLISHED USING A SPLIT SADDLE MADE FROM A PIECE OF FOUR INCH .250 WALL STEEL PIPE ABOUT TWELVE INCHES LONG. THIS SPLIT SLEEVE WAS THEN WELDED LONGITUDINAL AND CIRCUMFERENTIAL ON THE PIPE TO COVER THE PIN HOLE OPENING IN THE PIPE. ALL WELDS WERE FILLET TYPE WITH WORK PERFORMED BY A QUALIFIED WELDER WITH CURRENT QUALIFICATION DOCUMENTS.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890119 |  | 19325 | TEXAS UTILITIES FUEL CO | MART | MCLENNAN | TX |  | 5 MILES W OF MART | UNKNOWN | 1245 | 1989-03-20 | 1 | NO |  | N/A |  | NO | NO | LEAK | 0 | 0 | 0 | 20000 | 17236.756 | 37550.6867 | Null | 1 | 50 |  | 19890320 | 420 | 988 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1959; NMDIA: 12; THK: 0.25; SPEC: X42; SMYS: 1647; SEAM: ERW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: DENNIS EVANS , SR. FUEL FAC. OPER; PHONE: 8177392575; LOC: EXTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: NO DATA; COAT: COATED; PROT: Null; CPYR: 0; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | LOCALIZED EXTERNAL PITTING. SMALL LEAK.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890120 |  | 7605 | HOUSTON PIPELINE CO | VICTORIA | VICTORIA | TX | 77901 | N/A | 100+43 | 1230 | 1989-03-17 | 3 | NO |  | N/A |  | NO | NO | LEAK | 0 | 0 | 0 | 25000 | 21545.9451 | 46938.3584 | Null | 0 | 0 |  | 19890317 | 426 | 500 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | FILLET | STEEL |  | PIPELINE |  | 1964 | 18 | 0.31 | API 5LX | 42000 | DSAW | N/A | KAISER | 0 | UNDER PAVEMENT |  | JEFF WHIPPO, COMPLIANCE ENGINEER | 7138537322 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION |  | YES | 19640719 | WATER |  | 24 | 1350 | DURING ORIGINAL CONSTRUCTION A 4" TAP WAS MADE ON THE 18" MAINLINE USING A WELD-O-LET. A THROUGH-WALL CRACK DEVELOPED IN THE 18" LINE UNDER THE TOE OF THE FILLET WELD.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890121 |  | 17169 | RED RIVER PIPELINE CORP |  | DAWSON | TX | 79331 | N/A | N/A | 2015 | 1989-04-28 | 1 | NO |  | N/A | TX | NO | NO | LEAK | 0 | 0 | 0 | 13000 | 11203.8914 | 24407.9464 | Null | 0 | 20 |  | 19890428 | 1190 | 1200 | BY TEST | 1850 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1982; NMDIA: 10; THK: 0.5; SPEC: API 5L GR B; SMYS: 35000; SEAM: N/A; VALVE: N/A; MANU: U.S. STEEL; MANYR: 1981; LOCLK: ABOVE GROUND; PNAME: ROBERT W. WALKER, SAFETY & ENVIRON.; PHONE: 9154454971; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | THE LEAK WAS A 9" x 1.25" CRESCENT SHAPE CRACK ON THE 10" DISCHARGE PIPING OF COMPRESSOR UNIT #30006 ALONG AND NEAR THE AREA OF A 3" WELD-O-LET SERVING AS THE INLET TO A RELIEF VALVE. THE CRACK WAS CAUSED BY EXTERNAL FORCE ON THE 10" PIPING WHEN THE 3" x 6" RELIEF VALVE OPENED AT APPROXIMATELY 1190 PSIG. THE MAJOR CONTRIBUTING FACTOR WAS THE FAILURE OF THE THREADS OF A FLANGE BOLT ON THE RELIEF VALVE OUTLET FLANGE WHICH CONNECTED THE RELIEF VALVE OUTLET SUPPORT. WITHOUT SUPPORT THE FORCE OF GAS FLOW THROUGH THE RELIEF VALVE AND ITS DISCHARGE BLOWDOWN PIPE ACTED ON THE 10" DISCHARGE PIPE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890122 |  | 22617 | WILLIAMS NATURAL GAS CO | TOPEKA | SHAWNEE | KS |  | N/A | 258+42 | 510 | 1989-04-29 | 2 | NO |  | N/A |  | NO | NO | RUPTURE | 4.3 | 0 | 0 | 10000 | 8618.378 | 18775.3434 | YES | 2 | 18 |  | 19890429 | 195 | 200 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1953; NMDIA: 8; THK: 0.2; SPEC: N/A; SMYS: 24000; SEAM: N/A; VALVE: N/A; MANU: N/A; MANYR: 1928; LOCLK: UNDER GROUND; PNAME: WARREN A. ETHERIDGE, COORDINATOR; PHONE: 9185884427; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890123 |  | 9010 | J - W OPERATING CO |  | CADDO | LA |  | 1.27 FALCO | 67+08 | 1700 | 1989-06-05 | 1 | NO |  | N/A | LA | NO | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 30 |  |  | 470 | 1000 | BY TEST | 1490 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1971 | 6.63 | 0.16 | X-42 | 42000 | ERW | N/A | N/A | 0 | NO DATA |  | C.F. KYLE, DISTRICT MANAGER | 3186881080 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1971 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890136 |  | 11680 | LONE STAR GAS CO | LELIA LAKE | DONLEY | TX |  | AERIAL MARKER 35 | 190+77 | 1800 | 1989-03-21 | 1 | NO |  | N/A |  | NO | NO | LEAK | 0 | 0 | 0 | 35000 | 30164.3231 | 65713.7018 | Null | 21 | 30 |  | 19890322 | 275 | 350 | BY TEST | 500 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1952; NMDIA: 4; THK: 0.2; SPEC: GR. A; SMYS: 30000; SEAM: LAP WELD; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: UNDER GROUND; PNAME: CHRIS FRANKLIN; PHONE: 8175525642; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: AERIAL MARKER #35; STAT: NO; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890154 |  | 7605 | HOUSTON PIPELINE CO | MCMULLEN |  | TX |  |  | L-3 734+7 | 1610 | 1989-04-21 | 1 | NO |  | N/A | XX | NO | NO | LEAK | 0 | 0 | 0 | 43000 | 37059.0255 | 80733.9765 | Null | 1 | 30 |  | 19890421 | 830 | 1035 | BY TEST | 1300 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1968 | 16 | 0.25 | 5LX | 52000 | ERW |  | REPUBLIC | 0 | UNDER GROUND |  | NASSER PEBDANI, CODE COMPLIANCE ENGR. | 7138537320 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | COATED | YES | 1969 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890155 |  | 25160 | MOBIL VANDERBILT-BEAUMONT PIPELINE CO | BEASLEY | FORT BEND | TX |  | MP 65.6 | 3456 +23 | 1640 | 1989-04-16 | 1 | NO |  | N/A | TX | NO | NO | LEAK | 0 | 0 | 0 | 42000 | 36197.1877 | 78856.4421 | Null | 0 | 30 |  | 19890416 | 590 | 824 | BY TEST | 1240 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1941 | 14 | 0.28 | API 5L | 35000 | SEAMLESS | N/A | NATIONAL TUBE | 1941 | UNDER GROUND |  | J.A. TEN EYCK | 2146582381 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1950 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19890156 |  | 3230 | DELHI GAS PIPELINE CORP | CORPUS CHRISTI | NUECES | TX |  | CLARKWOOD RD. | A-970 | 1600 | 1989-04-14 | 1 | NO |  | N/A | TX | NO | NO | LEAK | 0 | 0 | 0 | 9909 | 8539.9508 | 18604.4877 | Null | 2 | 0 |  | 19890414 | 350 | 829 | BY TEST | 1160 | CORROSION | CORROSION | EXTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 0 | 6.63 | 0.25 | UNKNOWN | 0 | N/A | N/A | N/A | 0 | UNDER GROUND |  | CLAY SMITH - SFETY AND ENVIRONMENTAL | 5128828401 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | COATED | YES | 1971 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | EXTERNAL CORROSION.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19890164 |  | 25160 | MOBIL VANDERBILT-BEAUMONT PIPELINE CO | BEASLEY | FORT BEND | TX |  | MP 68 | 3588+14 | 1815 | 1989-04-30 | 1 | NO |  | N/A | TX | NO | NO | LEAK | 0 | 0 | 0 | 75000 | 64637.8352 | 140815.0752 | Null | 1 | 35 |  | 19890430 | 625 | 824 | BY TEST | 1240 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1941 | 14 | 0.28 | API 5L GRADE B | 35000 | SEAMLESS | N/A | NATIONAL TUBE | 1941 | UNDER GROUND |  | J.A. TEN EYCK | 2146582381 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1950 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | ON APRIL 30, 1989, A LEAK WAS REPORTED AT MP 68 ON THE VANDERBILT TO BEAUMONT NATURAL GAS PIPELINE. THE PIPELINE WAS SHUT DOWN FROM THR ORIGIN STATION AT VANDERBILT TO MP 71 AND THE PRESSURE REDUCED. A FLAME IONIZATION INSPECTION WAS CONDUCTED OVER THIS SEGMENT OF THE PIPELINE. ADDITIONAL LEAKS WERE FOUND AT MP 65.8, ON MAY 2, 1989, AND AT MP 58.1 ON MAY 3, 1989. ONLY MINIMALS WERE REPAIRED BY INSTALLING THREE SECTIONS OF NEW LINE PIPE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19890165 |  | 19570 | TRANSCO GAS PIPELINE CORP | PINE GROVE | ST HELENA | LA |  | 19.49 | 1029.+18 | 1200 | 1989-07-29 | 1 | NO |  | N/A | XX | NO | NO | LEAK | 0 | 0 | 0 | 60000 | 51710.2681 | 112652.0602 | Null | 5 | 0 |  | 19890729 | 740 | 960 | BY TEST | 1265 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1958 | 24 | 0.31 | API5LX | 52000 | FLASH WELD |  | A.O. SMITH | 1958 | UNDER GROUND |  | B.R. LANDES, SR. CODES & COMP. | 7134392001 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1958 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19890166 |  | 2616 | COLUMBIA GAS TRANSMISSION CORP | FINDLAY | HANCOCK | OH | 45840 |  | 5949+45 | 1045 | 1989-06-09 | 1 | NO |  | N/A | XX | NO | NO | OTHER | 0 | 0 | 0 | 100000 | 86183.7802 | 187753.4336 | Null | 5 | 0 |  | 19890609 | 150 | 720 | BY TEST | 1200 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1968; NMDIA: 10; THK: 0.19; SPEC: API 5LX; SMYS: 42000; SEAM: ERW; VALVE: N/A; MANU: JONE & LAUGHLIN; MANYR: 1968; LOCLK: UNDER GROUND; PNAME: A.S. BECKETT, SUPERVISORY ENGINEER; PHONE: 3043572797; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: STEEL & PLASTIC MARKERS; STAT: YES; CTEST: Null | CONTRACTOR OPERATING FIELD TILING/TRENCHING MACHINE PUNCTURED LINE RESULTINGIN AN APPROXIMATE 2" DIA. HOLE.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19890168 |  | 10030 | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | NORTH PLATTE | LINCOLN | NE | 69101 |  |  | 850 | 1989-06-22 | 3 | NO |  | N/A | XX | NO | NO | OTHER | 0 | 0 | 2 | 300000 | 258551.3407 | 563260.3009 | Null | 0 | 2 |  | 19890622 | 739 | 1000 | BY TEST | 2000 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: VALVE OPENED; MLKD: OTHER; MLKDO: UNKNOWN; PRTSY: COMPRESSOR STATION; PRTYR: 1954; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: DON ALMOND - DIRECTOR - COMPR. STATIONS; PHONE: 4024622141; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: NO; MARK: NO; MRKTP: 0; STAT: NO; CTEST: Null | OPERATOR ACCIDENTALLY OPENED DISCHARGE ESD VALVE, ALLOWING GAS TO ESCAPE FROM OPEN DISCHARGE HEADER.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890173 |  | 11808 | LOUISIANA INTRASTATE GAS CORP | NATCHITOCHES | NATCHITOCHES | LA | 71457 | 58 |  | 930 | 1989-06-18 | 1 | NO |  | N/A | N | NO | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 30 |  | 19890618 | 266 | 325 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 0 | 5 | 0 | UNKNOWN | 24000 | N/A | N/A | N/A | 0 | UNDER GROUND |  | S.D. OSBORN, SUPERINTENDENT | 3183578050 | EXTERNALLY | GENERAL CORROSION |  | OTHER | UNKNOWN | BARE | YES | 1976 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890177 |  | 21031 | VALERO TRANSMISSION CO | LOSOYA | BEXAR | TX |  | N/A | 97+39 | 900 | 1989-05-16 | 1 | NO |  | N/A | TX | NO | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 0 |  |  | 660 | 731 | BY TEST | 1109 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1962 | 24 | 0.31 | API5LX-52 | 1352 | N/A | N/A | N/A | 0 | UNDER WATER |  | T. DISBRO, AREA FOREMAN | 5126212052 | INTERNALLY | LOCALIZED PITTING |  | OTHER | UNKNOWN | COATED | YES | 1962 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | TWO SMALL LEAKS IN SADF WEST, MEDINA RIVER SECONDARY CROSSING. BOTH LEAKS UNDERWATER REPAIRED BY CUTTING AND CAPPING SECONDARY CROSSING.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890181 |  | 1552 | BLUE DOLPHIN PIPELINE CO |  |  | TX |  |  |  | 1330 | 1989-07-26 |  | YES | GA | 286 | XX | YES | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 11 | 30 |  | 19890726 | 350 | 1000 | BY TEST | 2175 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1965 | 20 | 0.5 | API 5 LX | 52000 | N/A | N/A | N/A | 1965 | UNDER GROUND |  | JOHN C. MCDUFFIE, JR., ENGINEER | 7136213993 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1965 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | MMS NOTIFIED US OF OIL SLICK 0930 HOURS ON 7-26. WE DROPPED BUOY 1330 HOURS AND STARTED SHUTDOWN. LIFT BOAT ON LOCATION 2030 HOURS 7-27. DIVER FOUND LEAK 1830 HOURS 7-28. SET CLAMP 2045 HOURS 7-29. TEST 450 PSIG OK. RESUMED GAS SALES 0700 HOURS 7-30.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19890183 |  | 13120 | NATURAL GAS PIPELINE CO OF AMERICA | LUFKIN | ANGELINA | TX | 75901 | MP355/356 |  | 15 | 1989-06-25 | 1 | NO |  | N/A | XX | NO | NO | OTHER | 0 | 0 | 0 | 4000000 | 3447351.2099 | 7510137.3447 | YES | 3 | 30 |  | 19890625 | 739 | 858 | BY TEST | 1287 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: SEE PART 3; MLKD: OTHER; MLKDO: SEE PART 3; PRTSY: COMPRESSOR STATION; PRTYR: 1965; NMDIA: 0; THK: 0; SPEC: N/A; SMYS: 0; SEAM: N/A; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: OTHER; LOCLO: IN COMPRESSOR BUILDING; PNAME: F. ROY FLEET, SR. ENGINEER; PHONE: 3126913786; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | A FIRE WAS APPARENTLY CAUSED BY LUBE OIL ESCAPING FROM THE CHIP DETECTOR PIPING OF THE #10 UNIT. THE OIL WAS IGNITED BY AN UNKNOWN SOURCE. HYDRAULIC OIL AND AMBITROL SUBSEQUENTLY FUELED THE FIRE AS VALVES IN THOSE SYSTEMS MELTED. NATURAL GAS WAS NOT A FACTOR IN THE INCIDENT.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19890186 |  | 13120 | NATURAL GAS PIPELINE CO OF AMERICA | MUSCATINE | MUSCATINE | IA | 52760 | 827 |  | 615 | 1989-07-04 | 1 | NO |  | N/A | XX | NO | NO | OTHER | 0 | 0 | 0 | 100000 | 86183.7802 | 187753.4336 | Null | 1 | 30 |  | 19890705 | 650 | 712 | BY TEST | 1068 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: SEE PART 3; MLKD: STEEL; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1988; NMDIA: 0; THK: 0; SPEC: N/A; SMYS: 0; SEAM: N/A; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: F. ROY FLEET, SR. ENGINEER; PHONE: 3126913786; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | A SALES METER WAS DAMAGED BY A FIRE FUELED BY NATURAL GAS. THE CAUSE OF THEINCIDENT IS UNDER INVESTIGATION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890188 |  | 2731 | CHEVRON PIPELINE CO | TEXAS CITY | GALVESTON | TX |  | M.P. 28.72 | 1516.41 | 1100 | 1989-06-29 | 3 | NO |  | N/A | XX | NO | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19890628 | 350 | 1152 | BY TEST | 2160 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1978; NMDIA: 4.5; THK: 0.24; SPEC: N/A; SMYS: 35000; SEAM: SMLS; VALVE: N/A; MANU: U.S.S.; MANYR: 0; LOCLK: UNDER GROUND; PNAME: J.T. NUCKOLS, ESF/H SPECIALIST; PHONE: 4098393130; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | RELEASE WAS FROM A CRACK WHICH RESULTED FROM A DENT IN THE PIPELINE FROM AN UNKNOWN SOURCE AT AN UNDETERMINED TIME. LEAK WAS FOUND BY A SMALL AMOUNT OF PRODUCT BUBBLING UP THROUGH STANDING WATER. LINE WAS SHUT DOWN, PRUGED AND REPAIRES MADE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890195 |  | 25160 | MOBIL VANDERBILT-BEAUMONT PIPELINE CO | HOUSTON | HARRIS | TX | 77060 | 110 | 5827+04 | 1615 | 1989-07-09 | 3 | NO |  | N/A | TX | NO | NO | RUPTURE | 4 | 0 | 0 | 6200 | 5343.3944 | 11640.7129 | Null | 0 | 35 |  | 19890709 | 560 | 750 | BY TEST | 1125 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | FITTING | 6" FLANGE | STEEL |  | OTHER | TIE-IN TO METER SETTING | 1988 | 6 | 0.28 | ANSI600# WN RF FLANG | 35000 | N/A | N/A | NATIONAL | 1988 | UNDER GROUND |  | J.A. TEN EYCK | 2146582381 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | 6" ANSI 600# WN RF FLANGE | YES | 19881219 | WATER |  | 8 | 2199 | FRACTURE FAILURE OF WELD NECK FLANGE DUE TO A MANUFACTURING DEFECT. HYSTOSTATIC TEST PRESSURE COULD HAVE FURTHER INDUCED WEAKENING IN THE AREA OF THE DEFECT PRIOR TO THE FAILURE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19890197 |  | 19570 | TRANSCO GAS PIPELINE CORP | MISSISSIPPI CANYON |  | LA |  | 21.262 | 1122+63 | 700 | 1989-07-27 |  | YES | M.C. | 20-A | XX | YES | NO | LEAK | 0 | 0 | 0 | 375000 | 323189.1759 | 704075.3761 | Null | 0 | 0 |  |  | 850 | 1200 | BY TEST | 2180 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | FITTING | 12" FLANGE | STEEL |  | PIPELINE |  | 1985 | 12 | 0.88 | FLNG., 12", 600# | 0 | N/A | N/A | B.T.M.S. | 1985 | UNDER WATER |  | B.R.LANDES, SR. COMPLIANCE ANALYST | 7134392522 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | 12" FLANGE ON A SLIP JOIN | YES | 19850530 | WATER |  | 8 | 2180 | DURING A ROUTINE UNDERWATER INSPECTION USING A REMOTE OPERATED VEHICLE, BUBBLES WERE OBSERVED NEAR THE BOTTOM OF THE RISER ON THE A-4 LEG OF BLOCK 20-A PLATFORM. A VIDEO TAPE OF THE FACILITIES IN THIS AREA INDICATED THAT A LEAK WAS LOCATED APPROXIMATELY 10 FEET PAST THE TUBE TURN ON THE UPSTREAM 12" FLANGE ON THE B.I.M.S. SLIP JOINT CONNECTION. LEAK IS COMING FROM THE 12" RING JOINT GASKET. DEPTH OF WATER AT THIS LOCATION IS APPROXIMATELY 500 FEET.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890198 |  | 10030 | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | NE/4 SECTION 35, T11N,R7W | HAMILTON | NE |  |  | 246+03 | 840 | 1989-08-02 | 1 | NO |  | N/A | XX | NO | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 0 |  | 19890802 | 490 | 545 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1956; NMDIA: 3.5; THK: 0.16; SPEC: API-5L; SMYS: 25000; SEAM: CW; VALVE: N/A; MANU: REPUBLIC; MANYR: 1956; LOCLK: ABOVE GROUND; PNAME: JAMES R. PHILLIPS-CONST'R & STD. COMPL.; PHONE: 4024622141; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: LINE MARKER 278 FT. AWAY; STAT: NO; CTEST: Null | THE PIPELINE WAS HIT BY AN OUTSIDE PARTY OPERATING A WEED CUTTER. THE DAMAGED PORTION OF THE PIPELINE IS IN A CLASS I LOCATION AND WAS MARKED WITH PERMANENT LINE MARKERS. A PERMANENT REPAIR WAS COMPLETED BY REPLACING TWELVE (12) FEET OF THE DAMAGED PIPELINE WITH PRETESTED PIPE OF EQUAL OR GREATER SPECIFICAT
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19890203 |  | 405 | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  |  | TX |  | X=3,494,689 | Y=129,403 | 1700 | 1989-07-28 |  | YES | HI | A-511 | XX | YES | NO | LEAK | 0 | 0 | 0 | 65000 | 56019.4572 | 122039.7319 | Null | 0 | 0 |  | 19890804 | 1100 | 1440 | BY TEST | 0 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1979 | 20 | 0.5 | 5LX60 | 60000 | SUBMERGED ARC | N/A | KAISER STEEL | 0 | UNDER WATER |  | DONALD E. CROSS SC&P | 3134962460 | INTERNALLY | LOCALIZED PITTING |  | OTHER | UNKNOWN | COATED | YES | 1979 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890207 |  | 11680 | LONE STAR GAS CO | GLENROSE | SOMERVELL | TX |  |  | 126+71 | 2158 | 1989-05-16 | 1 | NO |  | N/A | XX | NO | Null | OTHER | 0 | 0 | 0 | 26595 | 22920.5764 | 49933.0257 | Null | 2 | 28 |  | 19890516 | 465 | 800 | BY TEST | 1200 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1973; NMDIA: 4; THK: 0.16; SPEC: B; SMYS: 35000; SEAM: EW; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: UNDER GROUND; PNAME: G.M. FOWLER - SUPERINTENDENT; PHONE: 8176453271; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: NO; MARK: NO; MRKTP: 0N; STAT: Null; CTEST: Null | WATER WASHED DAM OUT. PIPELINE CROSS CREEK IN DAM.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890208 |  | 11680 | LONE STAR GAS CO | ALVORD | WISE | TX |  | 186+43 | 83+29 | 1310 | 1989-08-02 | 1 | NO |  | N/A | XX | NO | NO | OTHER | 0 | 0 | 0 | 5000 | 4309.189 | 9387.6717 | Null | 0 | 55 |  | 19890802 | 475 | 800 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1950; NMDIA: 10; THK: 0.25; SPEC: GRADE A; SMYS: 30000; SEAM: N/A; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: UNDER GROUND; PHONE: 2146702310; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PAINTED FENCE POST; STAT: NO; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890213 |  | 17444 | RIO PIPELINE LP | LOS FRESNOS | CAMERON | TX |  | 3.5 |  | 1100 | 1989-07-26 | 3 | NO |  | N/A | TX | NO | NO | RUPTURE | 1 | 0 | 0 | 5000 | 4309.189 | 9387.6717 | YES | 1 | 0 |  | 19890727 | 70 | 100 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1947; NMDIA: 5; THK: 0; SPEC: N/A; SMYS: 0; SEAM: N/A; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: UNDER PAVEMENT; PNAME: MICHAEL L. MYERS, DIST. ENGINEER; PHONE: 5125423531; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19890721; MARK: YES; MRKTP: PIPELINE MARKER; STAT: NO; CTEST: Null | FOREMOST PAVING HIT OUR LINE AT FM 803 AND SH 100 AT APPROXIMATELY 11:15 AM.WE BLEW THE LINE DOWN TO ATMOSPHERE AT 12:15 PM. THE LINE WAS REPAIRED AND PUT BACK IN SERVICE BY 4:30 PM.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19890217 |  | 2616 | COLUMBIA GAS TRANSMISSION CORP |  | HARDY | WV | 26836 | M&R STATION 5420 | N/A | 1550 | 1989-08-14 | 2 | NO |  | N/A | XX | NO | NO | OTHER | 0 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 30 |  | 19890814 | 100 | 800 | BY TEST | 1200 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: M&R STATION 5420; MLKD: STEEL; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1967; NMDIA: 2; THK: 0.15; SPEC: API 5L; SMYS: 4539; SEAM: SEAMLESS; VALVE: PLUG; MANU: SETTING BY OPERATOR; MANYR: 1967; LOCLK: ABOVE GROUND; PNAME: R.R. ROUSH, QA ENGINEER; PHONE: 3043572977; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: ESTABLISHED BUILDING; STAT: NO; CTEST: Null | BACKHOE OPERATOR LOST CONTROL OF BACKHOE WHICH RAN INTO AND DESTROYED A MEASUREMENT & REGULATION STATION.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19890218 |  | 2327 | CHEVRON USA INC | MAIN PASS 299 FIELD |  | LA |  |  |  | 1200 | 1989-09-04 |  | YES |  | MP299 | XX | YES | NO | OTHER | 0 | 0 | 0 | 500000 | 430918.9012 | 938767.1681 | Null | 0 | 0 |  | 19890905 | 0 | 1440 | BY TEST | 1800 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1968; NMDIA: 6.63; THK: 0.31; SPEC: API 5L GRADE X46; SMYS: 46000; SEAM: ERW; VALVE: N/A; MANU: LONE STAR STEEL; MANYR: 1968; LOCLK: UNDER WATER; PNAME: L.J. MOORE SR. DESIGN & CONSTRUCTION; PHONE: 5043642276; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: Null; CTEST: Null | BREAK APPARENTLY CAUSED BY ANCHOR RECOVERY OPERATIONS FROM A YET UNKNOWN COMPANY. THE PIPE WAS COMPLETELY SEPARATED WITH SIGNIFICANT MARKINGS CAUSED BY ANCHOR SCRAPINGS.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890219 |  | 13580 | NORTH CAROLINA NATURAL GAS CORP | GOLDSBORO | WAYNE | NC | 27530 | M.P. 49 | 2574+72 | 1110 | 1989-07-25 | 3 | NO |  | N/A | XX | NO | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 25 |  | 19890725 | 523 | 771 | BY TEST | 1169 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1959; NMDIA: 10.75; THK: 0.19; SPEC: GRADE B; SMYS: 1259; SEAM: ERW; VALVE: N/A; MANU: N/A; MANYR: 1959; LOCLK: UNDER GROUND; PNAME: EDWARD KOSAREK,ASST. DIV. SUPERINTENDENT; PHONE: 9197343254; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: YELLOW MARKINGS SIGNS; STAT: YES; CTEST: Null | A LOCATION REQUEST TICKET WAS RECIEVED FROM U.L.O.C.O. ON 7/18/89. THE LOCATION ON THE TICKET WAS GIVEN AS THE INTERSECTION OF S.R. 1107 & MUSGRAVE ROAD. THE ACTUAL LOCATION WAS S.R. 1007 & MUSGRAVE RD. N.C.N.C. DOES NOT HAVE ANY FACILITIES ON OR NEAR S.R. 1107 IN WAYNE COUNTY, N.C.HERRING & RIVENBARK (CONTRACTOR) WAS TRENCHING TO INSTALL WATER LINES. TRENCHERSTRUCK 10" GAS LINE CAUSING A HOLE IN THE PIPELINE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890220 |  | 7605 | HOUSTON PIPELINE CO | EDNA | JACKSON | TX | 77957 | N/A | 214+63 | 2 | 1989-08-10 | 1 | NO |  | N/A | XX | NO | NO | RUPTURE | 15 | 0 | 0 | 50000 | 43091.8901 | 93876.7168 | Null | 2 | 20 |  | 19890810 | 736 | 780 | BY TEST | 860 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1953 | 24 | 0.31 | N/A | 42000 | SEAMLESS | N/A | NATIONAL TUBE | 0 | OTHER | CROSSING OVER WATER | JEFF WHIPPO - COMPLIANCE ENGR. | 7138537321 | INTERNALLY | LOCALIZED PITTING |  | OTHER | CHEMICAL | COATED | YES | 1953 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | THE BREAK OCCURRED IN A SUBMERGED CROSSING OF A WATER FILLED DITCH.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890221 |  | 18516 | SOUTHERN NATURAL GAS CO |  | BIENVILLE/QUACHITA PARISH | LA | 71008 | N/A | N/A | 1100 | 1989-08-28 | 1 | NO |  | N/A | XX | NO | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19890828 | 630 | 1145 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: UNKNOWN; MLKD: STEEL; PRTSY: PIPELINE; PRTSO: UNKNOWN; PRTYR: 0; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: OTHER; LOCLO: UNKNOWN; PNAME: C.S. FARRELL SUPV. PIPELINE CODE; PHONE: 2053257554; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | ON AUGUST 28, 1989, EXPLOSIVE DEVICES WERE DETECTED AT THREE LOCATIONS ON SOUTHERN'S HIGH PRESSURE INTERSTATE NATURAL GAS TRANSMISSION PIPELINE SYSTEM INBIENVILLE AND QUACHITA PARISHES, LOUISIANA. TWO DEVICES COMPOSED OF TWO FOUR-POUND STICKS OF FUSED DYNAMITE (EACH CHARGE) WERE VISUALLY DETECTED AND REMOVED. ONE DEVICE A LOCATION #2 HAD DETONATED PRIOR TO DISCOVERY BY COMPANY PERSONNEL. ALTHOUGH UNDER FEDERAL INVESTIGATION, NO ARREST HAVE BEEN MADE TO DATE.SUPPLEMENTAL REPORT INDICATES THAT INCIDENT RESULTED FROM VANDALISM. AFURTHER DESCRIPTION OF THE THREE LOCATIONS FOLLOWS: LOC #1 SOUTHERN'S SUGARBOWL #1 METER STATION LOGANSPORT LINE - MP 54.7 BIENVILLE PARISH, LA 71008DEVICE DETECTED AT 11 AM 8/28/89 DEVICE WAS ATTACHED TO 12" PIPE RISER DEVICEREMOVED BY AUTHORITIES. LOCATION #2 - SOUTHERN'S HWY 101 BLOCK GATE VALVELOGANSPORT LOOP LINE MP 53.103 1 1/2 MI. EAST OF LOC #1 BIENVILLE PARISH, LA71008 DEVICE EXPLODED PRIOR TO DETECTION. DISCOVERY BY COMPANY PERSONNEL1:00PM. DAMAGE WAS TO 20" VALVE EXTENSION. ESTIMATED DAMAGE TO EXTENSION$5000.00. NO GAS ESCAPED THE PIPELINE. LOC. #3- SOUTHERN'S QUACHITA RIVERCROSSING LOGANSPORT LINE. MP 8.322 (45 MI. EAST OF LOC #1). QUACHITA PARISH,LA. 71280. DEVICE DETECTED AT 5:40PM. DEVICE WAS ATTACHED TO 4" BLOWOFF RISER.DEVICE REMOVED BY AUTHORITIES. INVESTIGATION OF THE INCIDENT CONTINUES, ANDSOUTHERN HAS OFFERED A $10,000 REWARD.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890225 |  | 11808 | LOUISIANA INTRASTATE GAS CORP | RURAL | WINN | LA |  | 16.2 | 851+29 | 930 | 1989-09-15 | 1 | NO |  | N/A | XX | NO | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 10 |  | 19890915 | 140 | 185 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: VALVE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1930; NMDIA: 6; THK: 0.25; SPEC: API 5L GRADE B; SMYS: 35000; SEAM: SMLS; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: UNDER GROUND; PNAME: T.F. TUCKER, MANAGER - OPERATIONS; PHONE: 3184458225; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: NO; MARK: NO; MRKTP: 0N; STAT: Null; CTEST: Null | COMPANY MAINTENANCE CREW DAMAGED SIDE TAP VALVE WHILE PERFORMING ROUTINE MAINTENANCE ON PIPELINE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890230 |  | 18516 | SOUTHERN NATURAL GAS CO | ALA HACHE | PLAQUEMINES | LA |  | 11.833 |  | 610 | 1989-09-09 | 1 | NO |  | N/A | XX | NO | NO | RUPTURE | 3 | 0 | 0 | 50000 | 43091.8901 | 93876.7168 | Null | 1 | 30 |  | 19890909 | 970 | 1100 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1963; NMDIA: 12.75; THK: 0.5; SPEC: API-5L; SMYS: 35000; SEAM: SEAMLESS; VALVE: N/A; MANU: NATIONAL; MANYR: 1963; LOCLK: UNDER WATER; PNAME: CHARLES FARRELL , SUPV. PIPELINE CODE; PHONE: 2053257554; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19890903; MARK: NO; STAT: Null; CTEST: Null | THIRD PARTY WAS USING BARGE AND DRAGLINE TO DIG OUT ALONG RIVER BANK FOR FUTURE BARGE ACCESS. THE BUCKET HIT THE UNDERWATER RIVER LINE. SUBSEQUENT DIVER INSPECTION INDICATED VERY MINOR DAMAGE TO THE PIPE. APPROXIMATELY SIX DAYSLATER THE PIPELINE RUPTURED.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19890234 |  | 21021 | VAL GAS CO | ALAMO | HIDALGO | TX |  | 3243'SO OF TOWER RD | N/A | 1030 | 1989-08-21 | 1 | NO |  | N/A | TX | NO | NO | RUPTURE | 5 | 0 | 0 | 14000 | 12065.7292 | 26285.4807 | YES | 1 | 0 |  |  | 690 | 750 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1966 | 8.63 | 0.19 | GR.X-46 | 2005 | N/A | N/A | N/A | 0 | UNDER GROUND |  | FERNANDO ARGUELLES, AREA FOREMAN | 5126864353 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | COATED | YES | 1966 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | THIS FAILURE WAS LOCATED IN A WET AREA NEAR A SEWER POND DRAINAGE. EXTERNALCORROSION OCCURRED DUE TO COATING DISBONDMENT. VOLUME LOST BASED ON VALLEY COMPLEX SYSTEM LINE PACK LOST, PRODUCTION FLOWING FOR ONE HOUR AND 3.2 MILES OF 8" PIPE BLOWN TO "0" ON BLOWOUT SECTION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890235 |  | 19325 | TEXAS UTILITIES FUEL CO | FAIRFIELD | FREESTONE | TX |  | MILE POST 78 |  | 825 | 1989-08-29 | 1 | NO |  | NA | TX | NO | NO | LEAK | 0.17 | 0 | 0 | 20500 | 17667.675 | 38489.4539 | Null | 1 | 10 |  | 19890829 | 450 | 823 | BY TEST | 823 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | GIRTH | STEEL |  | PIPELINE |  | 1958 | 12 | 0.25 | X42 | 1647 | ERW | N/A | N/A | 1958 | UNDER GROUND |  | LONNIE ELLIOTT | 8177302575 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL |  | YES | 19860117 | WATER |  | 8 | 2050 | LEAK OCCURRED AT HEAT AFFECTED ZONE ADJACENT TO A GIRTH WELD.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19890236 |  | 19570 | TRANSCO GAS PIPELINE CORP | WASHINGTON | ST LANDRY | LA |  | WSF WELL #44 | N/A | 1810 | 1989-09-13 | 1 | NO |  | N/A | XX | NO | NO | OTHER | 0 | 0 | 3 | 568920 | 490316.7626 | 1068166.8345 | Null | 2 | 1 |  | 19890913 | 0 | 0 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: SWAGE TO UNION HUB; MLKD: OTHER; MLKDO: UNKNOWN; PRTSY: OTHER; PRTSO: UNKNOWN; PRTYR: 1976; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: OTHER; LOCLO: UNKNOWN; PNAME: B.R. LANDES, SR. COMPLIANCE ANALYST; PHONE: 7134392001; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | A CONTRACTOR WAS WORKING FOR TRANSCO ON WELL#44 AT PAD 18 REMOVING SAND FROMTHE PERFORATED ZONE OF THE WELL AND HAD INSTALLED A COIL TUBING UNIT AND ANINJECTOR ASSEMBLY ON THE WELL. DURING THE DESANDING OPERATION, THE CONTRACTOR'S TUBING UNIT (#2148) DEVELOPED A PROBLEM IN THE UNIT'S HYDRAULIC SYSTEM.A SECOND TUBING UNIT (#2140) WAS BROUGHT IN NEXT TO UNIT #2148. CONTRACTOR INTERCONNECTED THE TWO UNIT'S HYDRAULIC SYSTEMS AND CONTINUED THE OPERATION.BOTH UNITS WERE APPROXIMATELY 3-5 FEET FROM THE WELLHEAD WITH TWO CONTRACTORCREWMAN IN THE CONTROL HOUSE OF EACH UNIT. THE CONTRACTOR COMPLETED THE DESANDING AND WAS WITHDRAWING TUBING FROM WELL. TUBING WAS APPROACHING THE TOP OF THE WELL WHEN THE INJECTOR ASSEMBLY BROKE LOOSE AT THE 4 1/2" X 3" SWAGE, CAUSING GAS TO BLOW FROM THE WELL. WITHIN SECONDS THE GAS IGNITED, SENDING FLAMES 40 TO 50 FEET IN THE AIR. BOTH TUBING UNITS ALSO CAUGHT ON FIRE. TRANSCO EMPLOYEES, CALLED TO THE SITE,ISOLATED AND BLEW DOWN CONNECTING PIPELINES, AND WITH ANSUL 39 LB. DRY CHEMICAL EXTINGUISHERS, EXTINGUISHED THE TWO TUBING UNIT TRUCKS AND THE WELLHEAD FIRES AND SHUT THE VALVE. A TOTAL OF FOUR CONTRACTOR EMPLOYEES WERE INJURED. ALL FOUR WERE TRANSPORTED TO THE HOSPITAL. ONE EMPLOYEE WAS TREATED AND RELEASED; THE OTHER THREE WERE TRANSFERRED TO BURNCENTERS. THE 4 1/2" X 3" SWAGE IS A CONNECTION ASSEMBLED IN THE CONTRACTOR'S MECHANCIAL SHOP. THE ENTIRE ASSEMBLY, INCLUDING ALL VALVES, CONNECTIONS AND COIL TUBING WAS TESTED TO 4500 PSI AFTER ASSEMBLY ON THE WELLHEAD. THE TEST WAS PERFORMED BY THE CONTRACTOR PERSONNEL AND WITNESSED BY TRANSCO PERSONNEL
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19890242 |  | 2616 | COLUMBIA GAS TRANSMISSION CORP | UPPERVILLE | LOUDOUN | VA | 22176 | 5,961' E OF VALVE | 2910+13 | 1800 | 1989-09-28 | 1 | NO |  | N/A | XX | NO | NO | LEAK | 0 | 0 | 0 | 112000 | 96525.8339 | 210283.8457 | Null | 1 | 0 |  |  | 640 | 800 | BY TEST | 1114 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1954; NMDIA: 26; THK: 0.28; SPEC: API 5LX; SMYS: 520000; SEAM: ERW; VALVE: N/A; MANU: A.O. SMITH; MANYR: 1954; LOCLK: UNDER GROUND; PNAME: ROB R. ROUSH, QA ENGINEER; PHONE: 3043572977; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: LINE MARKER 75 FT.; STAT: YES; CTEST: Null | DURING LAND CLEARING OPERATION, A BACKHOE DIGGING HOLES TO BURY STUMPS PUNCTRUED PIPELINE, PRODUCING A 2-INCH BY 3-INCH HOLE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19890243 |  | 405 | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | HIGH ISLAND BL A-511, S. |  | TX |  | X=3,492,160 | Y=131,918 | 1455 | 1989-10-05 |  | YES | H.I. | A-511 | XX | YES | NO | LEAK | 0 | 0 | 0 | 152000 | 130999.346 | 285385.2191 | Null | 0 | 0 |  | 19891006 | 1100 | 1440 | NO DATA | 0 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1979 | 20 | 0.5 | 5LX60 | 60000 | SUBMERGED ARC | N/A | KAISER STEEL | 0 | UNDER WATER |  | DONALD E. CROSS, C.S.&P. | 3134962460 | INTERNALLY | LOCALIZED PITTING |  | NO DATA |  | COATED | YES | 1979 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19890247 |  | 11616 | LLANO INC | 10 MILES WEST OF HOBBS | LEA | NM | 88240 | SW 1/4, NE 1/4 | SEC.36 | 200 | 1989-10-02 | 3 | NO |  | N/A | NM | NO | NO | OTHER | 0 | 0 | 0 | 600000 | 517102.6815 | 1126520.6017 | Null | 3 | 10 |  | 19891002 | 1000 | 1100 | BY TEST | 1800 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: GATHERING SYSTEM; PRTFL: OTHER; PRTFO: COMPRESSOR VALVE; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1978; NMDIA: 0; THK: 0; SPEC: N/A; SMYS: 0; SEAM: N/A; VALVE: RECIPROCATING; MANU: INGERSOL-RAND; MANYR: 1978; LOCLK: ABOVE GROUND; PNAME: CLIFTON R. REED, AS'T GNRL. MANAGER; PHONE: 5053932153; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | INSPECTION OF THE CRYOGENIC PLANT COMPRESSION FACILITIES INVOLVED IN THE INCIDENT REVEALED THE ABSENCE OF A 1 5/8" "JACK BOLT" FROM AN INBOARD, DISCHARGEVALVE CAP ON A COMPRESSOR CYLINDER. DURING DISMANTLING OF THAT COMPRESSION CYLINDER, PARTICULARLY THAT VALVE ASSEMBLY, THE CENTER THROUGH BOLT WHICH HOLDS THE VALVE COMPONENTS TOGETHER WAS FOUND TO BE BROKEN. THE "VALVE CHAIR" WA S FOUND TO HAVE IMPACT DAMAGE FROM STRIKING THE JACK BOLT, OFF CENTER. THESEFINDINGS SUGGEST THE VALVE THROUGH BOLT FAILURE LED TO A "COCKING" OF THE VALVE CHAIR WHICH IN TURN STRUCK THE JACK BOLT. THE JACK BOLT, THROUGH JARRING CAUSED BY THE IMPACTING OF THE CHAIR, "BACKED OUT" OF ITS THREAD PROFILE. GAS LEAKAGE, AT 1000 PSIG, AROUND THE JACK BOLT BEGAN DURING THIS PROCESS. FAILURE OF THE JACK BOLT STARTING THREAD, APPROXIMATELY 270*, AND THE FIRST THREAD IN THE VALVE CAP SUGGEST A FORCEFUL REJECTION OF THE JACK BOLT FROM ITS PROFILE. GAS HAVING ACCUMULATED UNDER THE COMPRESSOR FACILITIES COVER, A 20'X40'X20' OPEN SKIRTED BUILDING, WAS SUBSEQUENTLY IGNITED. SOURCE OF IGNITIONCOULD HAVE BEEN SPARKS CREATED BY EXITING OF THE CARBON STEEL JACK BOLT OR FROM NUMEROUS, NORMAL HOT SPOTS ON THE INTERNAL COMBUSTION ENGINE WHICH WAS DRIVING THE COMPRSSOR. THE ENSUING NATURAL GAS FIRE WAS RESPONSIBLE FOR CAUSING A FIRE OF COMPRESSOR LUBRICATION OIL.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19890250 |  | 405 | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | HIGH ISLAND BLOCK 325 |  | TX |  | X=3,717,883.07 | 155,411.7 | 1130 | 1989-09-24 |  | YES | HIGH ISLAND | 325 | XX | YES | NO | LEAK | 0 | 0 | 0 | 400000 | 344735.121 | 751013.7345 | Null | 0 | 0 |  | 19890926 | 920 | 1440 | BY TEST | 2694 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 0 | 10 | 0.37 | 5LX42 | 42000 | ERW | N/A | REPUBLIC STEEL | 1980 | UNDER WATER |  | DONALD E. CROSS C S & P | 3134962460 | INTERNALLY | GENERAL CORROSION |  | OTHER | UNKNOWN | COATED | YES | 1981 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890251 |  | 11680 | LONE STAR GAS CO | TUCKER | ANDERSON | TX |  | N/A | 5892+80 | 830 | 1989-09-18 | 1 | NO |  | N/A | XX | NO | NO | OTHER | 0 | 0 | 0 | 10142 | 8740.759 | 19041.9532 | YES | 2 | 30 |  | 19890918 | 315 | 500 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1941; NMDIA: 12; THK: 0.38; SPEC: A; SMYS: 30000; SEAM: LAP WELD; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: UNDER GROUND; PNAME: L.M. MCKINNEY, SUPERINTENDENT; PHONE: 2145382171; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | ROAD GRADER GRADING LOGGING ROAD STRUCK PIPELINE CAUSING 3 1/4" TRIANGULAR HOL
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890252 |  | 1995 | CABOT GAS SUPPLY CORP | MONAHANS | WARD | TX | 79756 | LINE 4000-000 | 1070+20 | 745 | 1989-10-05 | 1 | NO |  | N/A | XX | NO | NO | RUPTURE | 0.25 | 0 | 0 | 42000 | 36197.1877 | 78856.4421 | Null | 3 | 15 |  | 19891005 | 825 | 953 | BY TEST | 1048 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1969; NMDIA: 20; THK: 0.25; SPEC: X-56; SMYS: 1400; SEAM: N/A; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: UNDER GROUND; PNAME: R.L. TOMLINSON-SUPT. SOUTHERN AREA; PHONE: 9155862939; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: LINE MARKER 1671' TO WEST; STAT: NO; CTEST: Null | INDEPENDENT CONTRACTOR HIT PIPELINE WITH A BACK HOE WHILE DITCHING TO LAY A WATER LINE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890253 |  | 21031 | VALERO TRANSMISSION CO | CRYSTAL CITY | ZAVALA | TX | 78834 | WCC BLOCK VALVE |  | 830 | 1989-09-22 | 1 | NO |  | N/A | TX | NO | NO | LEAK | 0 | 0 | 0 | 3500 | 3016.4323 | 6571.3702 | YES | 0 | 45 |  | 19890922 | 300 | 397 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1930 | 4.5 | 0.16 | UNKNOWN | 1664 | UNKNOWN | UNKNOWN | UNKNOWN | 1930 | UNDER GROUND |  | A.J. STRELCZYK, AREA FOREMAN | 5128765784 | EXTERNALLY | OTHER | UNKNWON | OTHER | UNKNOWN | COATED | YES | 1965 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | THIS INCIDENT WAS CAUSED BY AN EXTERNAL CORROSION LEAK ABOUT FOUR (4) MILES NORTH OF CRYSTAL CITY. THREE (3) CUSTOMERS AND ONE (1) PRODUCER WERE WITHOUTSERVICE FOR THREE (3) HOURS WHILE THE LINE WAS BLOCKED IN FOR REPAIR.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890256 |  | 22467 | WESTERN GAS SUPPLY CO | PAGOSA SPRINGS | ARCHULETA | CO | 81147 | 136+13.3 | 136+13.3 | 1055 | 1989-10-24 | 3 | NO |  | N/A | XX | NO | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 30 |  |  | 40 | 854 | BY TEST | 1281 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: PIPING AND VALVES; MLKD: STEEL; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1973; NMDIA: 3; THK: 0.16; SPEC: GRADE B; SMYS: 35000; SEAM: ERW; VALVE: PLUG; MANU: WALWORTH; MANYR: 1973; LOCLK: ABOVE GROUND; LOCLO: UNKNOWN; PNAME: SUZANNE ROBBINS, SPECIAL PROJECTS; PHONE: 3035724157; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | THE MICRO LOCK BRAKES FAILED ON A TOW TRUCK PARKED ON THE ROAD BEHIND THE METER STATION. THE TRUCK ROLLED DOWN THE HILL THROUGH THE STATION FENCE, STRIKING THE ABOVE GROUND PIPING. A 3" ANSI 150 PLUG VALVE RUPTURED. THE STATION PIPING ABOVE AND BELOW GROUND WAS TWISTED BY THE FORCE OF THE IMPACT.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890257 |  | 18779 | SUN REFINING & MARKETING CO | BRIDGEPORT | GLOUCESTER | NJ |  | N/A | N/A | 903 | 1989-10-23 | 4 | NO |  | N/A | NJ | NO | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 3 | 7 |  | 19891023 | 420 | 1136 | BY TEST | 1590 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1961 | 6 | 0.19 | API SPEC 5L GR. B | 2960 | ERW | N/A | N/A | 0 | UNDER WATER |  | MICHAEL J. WAGNER, OPERATIONS SUPT. | 2154475840 | INTERNALLY | LOCALIZED PITTING |  | OTHER | LOW POINT CORROSION | COATED | YES | 1963 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | THE SIX INCH LINE UNDER RACCOON CREEK AT BRIDGEPORT, NEW JERSEY, DEVELOPED ALEAK FROM INTERNAL LOW POINT ACQUIOUS CORROSION.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19890262 |  | 13120 | NATURAL GAS PIPELINE CO OF AMERICA |  |  | TX |  |  |  | 1800 | 1989-10-03 |  | YES | HIGH ISLAND | 7 | XX | NO | NO | RUPTURE | 1 | 11 | 3 | 750000 | 646378.3519 | 1408150.7521 | Null | 16 | 0 |  | 19891003 | 834 | 1200 | BY TEST | 1800 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1973; NMDIA: 16; THK: 0.31; SPEC: 5LX52; SMYS: 52000; SEAM: SEAMLESS; VALVE: N/A; MANU: US STEEL; MANYR: 1971; LOCLK: UNDER WATER; PNAME: R. ROY FLEET, SENIOR ENGINEER; PHONE: 3126913786; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: NAVIGATONAL CHARTS; STAT: NO; CTEST: Null | FISHING BOAT STRUCK PIPELINE APPROXIMATELY 1/2 MILE OFFSHORE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890263 |  | 4280 | EL PASO NATURAL GAS CO | PHOENIX | MARICOPA | AZ |  | 29+5180 (29.981) | 1267+91.2 | 1845 | 1989-10-18 | 3 | NO |  | N/A | XX | NO | NO | RUPTURE | 0.5 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 23 |  | 19891018 | 615 | 650 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: OTHER; MLKDO: UNKNOWN; PRTSY: PIPELINE; PRTYR: 1950; NMDIA: 16; THK: 0.25; SPEC: SMLS; SMYS: 35000; SEAM: N/A; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: UNDER GROUND; PNAME: RICHARD FAVILA, SENIOR ENGR.; PHONE: 9155412062; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: MP MARKER PLUS; STAT: YES; CTEST: Null | LAND OWNER HAD BEEN TOLD NOT TO MAKE CUTS OR REMOVE COVER FROM OUR PIPELINE.A CONTRACTOR HIRED BY LAND OWNER WAS GRADING WITH A BULLDOZER AND HIT AND RUPTURED OUR 16" LINE #2039.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19890269 |  | 2616 | COLUMBIA GAS TRANSMISSION CORP | TAD | KANAWHA | WV | 25201 | NONE | 380+42 | 930 | 1989-10-21 | 1 | NO |  | N/A | XX | NO | NO | LEAK | 0 | 0 | 0 | 100000 | 86183.7802 | 187753.4336 | Null | 1 | 30 |  | 19891021 | 700 | 963 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1956; NMDIA: 12; THK: 0.25; SPEC: API 5LX; SMYS: 52000; SEAM: SEAMLESS; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: UNDER GROUND; PNAME: R.R. ROUSH, QA ENGINEER; PHONE: 3043572977; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | A DOZER CONSTRUCTING AN ACCESS ROAD HIT AND SEPARATED THE PIPELINE RESULTING IN AN EXPLOSION AND FIRE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19890270 |  | 13120 | NATURAL GAS PIPELINE CO OF AMERICA |  |  | LA |  | N/A | N/A | 1300 | 1989-11-01 |  | YES | WEST CAMERON | 551 | XX | YES | NO | LEAK | 0 | 0 | 0 | 100000 | 86183.7802 | 187753.4336 | Null | 2 | 0 |  | 19891101 | 1000 | 1200 | BY TEST | 2160 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1980 | 8 | 0.25 | 5LX52 | 52000 | SEAMLESS | UNKNOWN | UNKNOWN | 0 | UNDER WATER |  | F.ROY FLEET, SENIOR ENGINEER | 7086913786 | INTERNALLY | LOCALIZED PITTING |  | OTHER | UNKNOWN | COATED | YES | 1980 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | LEAK WAS CAUSED BY INTERNAL CORROSION.REPAIRED BY INSTALLING A PLIDCO LEAK CLAMP.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19890271 |  | 19160 | TENNESSEE GAS PIPELINE CO | MOREHEAD | ROWAN | KY | 40351 | COMPRESSOR STA. 110 | N/A | 1205 | 1989-11-30 | 1 | NO |  | N/A | XX | NO | NO | OTHER | 0 | 0 | 0 | 3000000 | 2585513.4075 | 5632603.0085 | YES | 0 | 45 |  | 19891130 | 0 | 0 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: TURBINE; MLKD: OTHER; MLKDO: TURBINE; PRTSY: COMPRESSOR STATION; PRTYR: 1955; NMDIA: 0; THK: 0; SPEC: N/A; SMYS: 0; SEAM: N/A; VALVE: N/A; MANU: GENERAL ELECTRIC; MANYR: 1955; LOCLK: OTHER; LOCLO: COMPRESSOR STATION; PNAME: RICHARD A. WINN, REGULATORY ANALYST; PHONE: 7137572581; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | UNIT HAS BEEN DOWN SINCE 1983. RECENT OVERHAUL AND NEW CONTROLS WERE BEING VERIFIED AND ACCEPTED. POWER TURBINE FAILED. CAUSED OIL LEAK WHICH RESULTEDIN FIRE. THE FIRE DESTROYED THE UNIT WALL, ASSOCIATED WALLS, FLOOR, AND CEILING.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19890272 |  | 19136 | TEJAS GAS CO | CARTHAGE | PANOLA | TX | 75633 | 1/4 MI. EAST MLV #2. |  | 1645 | 1989-11-14 | 1 | NO |  | N/A | XX | NO | NO | OTHER | 0 | 0 | 1 | 5000 | 4309.189 | 9387.6717 | Null | 0 | 55 |  | 19891114 | 820 | 1271 | BY TEST | 1760 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1978; NMDIA: 10; THK: 0.22; SPEC: API 5L X-52; SMYS: 2119; SEAM: ERW; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: UNDER GROUND; PNAME: ELVIN C. LOYD DISTRICT SUPT.; PHONE: 2147530799; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: MARKER IN PLACE; STAT: NO; CTEST: Null | CONTRACTOR USING A D-7 DOZER STRUCK PIPELINE WHILE CONSTRUCING A RESERVE PITFOR A NEW PENZOIL WELL LOCATION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890273 |  | 2616 | COLUMBIA GAS TRANSMISSION CORP | ROCKBRIDGE | HOCKING | OH | 43149 | N/A | 711+00 | 200 | 1989-11-13 | 1 | NO |  | N/A | XX | NO | NO | RUPTURE | 24 | 0 | 0 | 50000 | 43091.8901 | 93876.7168 | Null | 1 | 0 |  | 19891113 | 793 | 800 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1951 | 20 | 0.28 | API 5LX | 42000 | SEAMLESS | N/A | N/A | 1951 | UNDER GROUND |  | R.R. ROUSH, QA ENGINEER | 3043572977 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | BARE | YES | 1974 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | NO KNOWN OUTSIDE FACTORS.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19890274 |  | 13120 | NATURAL GAS PIPELINE CO OF AMERICA |  | CAMERON | LA | 70631 | 99 | 5208+18 | 1230 | 1989-11-10 | 1 | NO |  | N/A | XX | NO | NO | LEAK | 0 | 0 | 0 | 130000 | 112038.9143 | 244079.4637 | Null | 6 | 30 |  | 19891110 | 860 | 1100 | BY TEST | 1555 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1978 | 30 | 0.36 | 5LX65 | 65000 | SUBMERGED ARC | N/A | US. STEEL | 1977 | UNDER GROUND |  | F. ROY FLEET | 7086913605 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL |  | YES | 19780518 | WATER |  | 8 | 1555 | LEAK DUE TO LAMINATION IN PIPE WALL.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19890282 |  | 9010 | J - W OPERATING CO |  | CADDO | LA |  | 4.98 FALCO | 263+20 | 945 | 1989-12-16 |  | NO |  |  | LA | NO | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 7 | 0 |  |  | 480 | 1000 | BY TEST | 1490 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1971; NMDIA: 6.63; THK: 0.16; SPEC: X-42; SMYS: 42000; SEAM: ERW; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: UNDER GROUND; PNAME: C.F. KYLE, DISTRICT MANAGER; PHONE: 3186881080; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19891105; MARK: YES; MRKTP: VERT. FIBERGLASS MARKERS; STAT: YES; CTEST: Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19890283 |  | 2620 | COLUMBIA GULF TRANSMISSION CO | UNKNOWN |  | LA |  |  | 28*-15'-09"N | 0 | 1989-12-02 |  | YES | S.P. | 77 | XX | YES | NO | LEAK | 0 | 0 | 0 | 4702000 | 4052361.3473 | 8828166.4487 | Null | 0 | 0 |  | 19891202 | 950 | 1440 | BY TEST | 2160 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1982; NMDIA: 12; THK: 0.5; SPEC: API-5L; SMYS: 2745; SEAM: SEAMLESS; VALVE: N/A; MANU: U.S. STEEL; MANYR: 1981; LOCLK: UNDER WATER; PNAME: THOMAS J. LEWIS, PROJECT ENGINEER; PHONE: 7139681416; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | THE EXISTING 12" PIPELINE FROM PENNZOIL PLATFORM "A" IN SOUTH PASS BLK. 57 TO A CONNECTION IN TENNESSEE GAS' 26" PIPELINE IN SOUTH PASS BLK. 77, A DISTANCE OF APPROXIMATELY 3.85 MILES, WAS PULLED OUT OF ITS ORIGINAL POSITION APPROXIMATELY 1800 TO 2400 FEET. THE PIPELINE SUSTAINED CONSIDERABLE DAMAGE, WITHA LEAK DEVELOPED IN SOUTH PASS BLK. 77. PLANS FOR THE REPAIR AND/OR REPLACEMENT OF THE DAMAGED PIPELINE ARE BEING FORMULATED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19890284 |  | 13750 | NORTHERN NATURAL GAS CO | FARMINGTON | DAKOTA | MN | 55024 | FARMINGTON DISTRICT |  | 410 | 1989-11-29 | 1 | NO |  | N/A | XX | NO | NO | OTHER | 0 | 0 | 0 | 91700 | 79030.5265 | 172169.8986 | Null | 0 | 0 |  | 19891205 | 765 | 950 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: ESD SYSTEM; MLKD: OTHER; MLKDO: UNKNOWN; PRTSY: COMPRESSOR STATION; PRTYR: 1965; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: JOHN W. CASKEY , CODE COMP. ENGR.; PHONE: 7138537325; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | A 1/2" NPS NIPPLE ON THE #4 COMPRESSOR RELIEF VALVE SENSING LINE FAILED RESULTING IN THE COMPRESSOR PLANT (FIVE COMPRESSORS) EMERGENCY SHUT DOWN SYSTEM ACTIVATING.SUPPLEMENTAL : AN UNNECCESSARY, UNPLANNED ACTIVATION OF THE COMPRESSOR PLANT (5UNITS) EMERGENCY SHUTDOWN SYSTEM OCCURRED. ONE INLET VALVE DID NOT CLOSE, RESULTING IN HIGH GAS LOSS.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19890285 |  | 405 | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | PLEASANT GROVE |  | MS | 38657 | M.P. 313.8 |  | 1634 | 1989-11-25 | 3 | NO |  | N/A | XX | NO | NO | OTHER | 0 | 0 | 0 | 1000000 | 861837.8025 | 1877534.3362 | Null | 2 | 0 |  | 19891125 | 800 | 858 | BY TEST | 1870 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: UNKNOWN; MLKD: OTHER; MLKDO: UNKNOWN; PRTSY: COMPRESSOR STATION; PRTYR: 1970; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: DONALD E. CROSS, C S & P; PHONE: 3134962460; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | PRELIMINARY CONCLUSION: ELECTRICAL MALFUNCTION OF TURBINE CONTROL SYSTEMS COUPLED WITH LUBE OIL AND GAS LEAK APEAR TO HAVE CAUSED THE FIRE. INVESTIGATION IS STILL IN PROGRESS.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900005 |  | 1552 | BLUE DOLPHIN PIPELINE CO | OFFSHORE |  | TX |  | N/A | 28 54' 35"N 94 48' 13"W | 800 | 1989-12-27 |  | YES | GA | 286 | XX | YES | NO | LEAK | 6 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19891227 | 140 | 1000 | BY TEST | 2175 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1965 | 20 | 0.5 | API 5LX | 52000 | SEAMLESS | N/A |  | 1965 | UNDER WATER |  | JOHN C. MCDUFFIE, JR. - ENGINEER | 7136213993 | INTERNALLY | LOCALIZED PITTING |  | OTHER | UNKNOWN | COATED | YES | 1965 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | HELICOPTER LINE SURVEY FOLLOWING CLAMP #5 AND GAS TEST PRESSURE APPLIED TO PIPELINE LOCATED BUBBLES IN BLOCK GA 286; SO DIVER BOAT WAS MOVED THERE AND CLAMP WAS SET BY 1502 HOURS ON 12/29/89 AND 400 PSI GAS PRESSURE TEST WAS SUCCESSFUL.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900006 |  | 1552 | BLUE DOLPHIN PIPELINE CO | Y |  | TX |  | N/A | 28 57' 00"N 95 07' 09"W | 1415 | 1989-12-21 |  | YES | GA | 276 | XX | YES | NO | LEAK | 5 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 0 | 22870 | 19891221 | 340 | 1000 | BY TEST | 2175 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1965 | 20 | 0.5 | API GLX | 52000 | SEAMLESS | N/A |  | 1965 | UNDER WATER |  | JOHN C. MCDUFFIE, JR-ENGINEER | 7136213993 | INTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1965 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | SLICK OBSERVED BY ARMS PERSONNEL IN HELICOPTER WAS REPORTED BY RADIO/TELEPHONE; SO A MARKER BOUY WAS DROPPED. PRODUCERS SHUT DOWN GAS DELIVERY WITHIN TWO HURS BUT REPAIR WAS WAS DELAYED BY HIGH SEAS AND RECORD COLD. SET PLIDCO, SPLIT SLEEVE, BOLT-ON, 1500 WP CLAMP BY 1000 HOURS 12/27/89; THEN 140 PSI TEST PRESSURE CREATED GAS BUBBLE EVIDENCE OF LEAK NO. 6 WHICH IS REPORTED SEPARATELY.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19900014 |  | 21031 | VALERO TRANSMISSION CO | FORT STOCKTON | PECOS | TX |  | WAHA COMPRESSOR STATION | N/A | 1245 | 1989-11-21 | 1 | NO |  | N/A | TX | NO | NO | OTHER | 0 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 5 | 20856 | 19891121 | 0 | 0 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: UNKNOWN; MLKD: OTHER; MLKDO: UNKNONW; PRTSY: COMPRESSOR STATION; PRTYR: 1968; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: UNDER GROUND; PNAME: JOHN SOMMER, MANAGER CODES AND RECORDS; PHONE: 5122462395; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | WHILE PERFORMING SCHEDULED MAINTENANCE WORK, TWO WORKERS WERE BURNED WHEN AFLASH FIRE ERUPTED. THE WORKERS WERE ATTEMPTING TO WELD A 24" END CAP TO A 24" PIPE IN THE WAHA COMPRESSOR YARD PIPING.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900015 |  | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | PRAGUE | GRANT | AR | 72150 | 1491+27 | 1491+27 | 1400 | 1989-12-23 | 1 | NO |  | N/A | XX | NO | NO | LEAK | 0 | 0 | 0 | 176000 | 151683.4532 | 330446.0432 | Null | 2 | 0 | 23457 | 19891228 | 310 | 470 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1920 | 12 | 0.25 | N/A | 0 | N/A | N/A |  | 0 | UNDER GROUND |  | RAUL G. ESPINOSA | 3184293924 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL |  | NO |  | OTHER | UNKNOWN | 0 | 0 | A CRACK DEVELOPED IN A WRINKLE BEND. CRACK FOLLOWED WRINKLE AND PIPE SPLIT, 22" LONG, WIDEST OPENING 1/4".
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900016 |  | 2616 | COLUMBIA GAS TRANSMISSION CORP | CLAYSVILLE | WASHINGTON | PA | 15376 | 0 | 10+28 | 508 | 1989-12-19 | 3 | NO |  | N/A | XX | NO | NO | RUPTURE | 13 | 0 | 0 | 101000 | 87045.6181 | 189630.968 | Null | 0 | 45 | 22645 | 19891219 | 520 | 600 | BY TEST | 983 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1949 | 20 | 0.31 | N/A | 35000 | ERW | N/A | N/A | 1949 | UNDER GROUND |  | R.R. ROUSH, QA ENGINEER | 3043572977 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | BARE | YES | 1971 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | NO OUTSIDE CONTRIBUTING FACTORS.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19900018 |  | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | NEW YORK | BRONX | NY | 10454 | HELLGATE STATION |  | 1310 | 1989-12-29 | 4 | NO |  | N/A | XX | NO | NO | RUPTURE | 11 | 2 | 1 | 50000 | 43091.8901 | 93876.7168 | Null | 1 | 20 | 23537 | 19891229 | 290 | 350 | BY TEST | 425 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 0; NMDIA: 30; THK: 0.5; SPEC: ASTM-134-42; SMYS: 35000; SEAM: SPIRALWELD; VALVE: N/A; MANYR: 0; LOCLK: UNDER GROUND; PNAME: RICHARD GAULIN, PLANNING ENGINEER; PHONE: 2124602838; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | FIRE AT RUPTURED 30" HIGH PRESSURE STEEL GAS MAIN. INVESTIGATION IS CONTINUING; SUPPLEMENTAL REPORT TO FOLLOW.SUPPLEMENT - AN EXPLOSION OCCURED IN TWO ELECTRIC MANHOLES, CAUSED BY THE IGNITION OF A GAS OF UNDETERMINED ORIGIN. THE EXPLSION IN THE MANHOLES SENT APRESSURE WAVE THROUGH THE SOIL WHICH RUPTURED AN ADJOINING MAIN.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900025 |  | 20230 | UNITED GAS PIPELINE CO | OFFSHORE |  | LA |  | 64.32 | 3395+90 | 1218 | 1989-12-28 |  | YES | LAKE PONTCHARTRAIN | 21 | LA | NO | NO | RUPTURE | 1 | 0 | 0 | 120000 | 103420.5363 | 225304.1203 | Null | 1 | 15 | 23434 | 19891228 | 360 | 755 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1941; NMDIA: 14; THK: 0.5; SPEC: A; SMYS: 30000; SEAM: SEAMLESS; VALVE: N/A; MANU: NATIONAL STEEL; MANYR: 0; LOCLK: UNDER WATER; PNAME: W.F. ST. GERMAIN, SR. PIPELINE/SAFETY; PHONE: 7132295772; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: NAVIGATION LIGHTS; STAT: YES; CTEST: Null | CAUSE OF DAMAGE IS NOT CONFIRMED, BUT PRELIMINARY EVIDENCE INDICATES THAT THE DAMAGE WAS CAUSED BY A SHELL DREDGE.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19900030 |  | 12792 | MORGAS CO | WILLIS RURAL | MONTGOMERY | TX | 77378 | 30.2 |  | 900 | 1989-12-22 | 3 | NO |  | N/A | TX | NO | NO | OTHER | 0 | 0 | 1 | 7500 | 6463.7835 | 14081.5075 | Null | 0 | 5 |  | 19891222 | 200 | 100 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: POSITIVE METER; MLKD: OTHER; MLKDO: ALUMINUM; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1987; NMDIA: 0; THK: 0; SMYS: 0; MANU: ROCKWELL; MANYR: 1980; LOCLK: OTHER; LOCLO: UNKNOWN; PNAME: CHARLES E. MOORE, VICE-PRES.; PHONE: 4097564431; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | EMPLOYEES WERE ATTEMPTING TO OPEN CITY GATE BY-PASS. EXCESSIVE PRESSURE REACHED POSITIVE DISPLACEMENT. METER EXPLODED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900035 |  | 1552 | BLUE DOLPHIN PIPELINE CO | OFFSHORE | BRAZORIA | TX |  | Y=428,178.88 | X=3,254,727.67 | 830 | 1990-01-21 |  | YES | GA | 275 | X | YES | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 | 01465 | 19900121 | 350 | 1000 | BY TEST | 2160 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1965 | 20 | 0.5 | API 5LX | 52000 | SEAMLESS | N/A | N/A | 1965 | UNDER WATER |  | JOHN C. MCDUFFIE, JR. ENGINEER | 7136213993 | INTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1965 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | HELICOPTER INVESTIGATION OF REPORTED OIL SLICK VERIFIED 100' WIDE x 5 MILES LONG COMING FROM BUBBLES IN GA-275; DROPPED BOUY 1000 HR ON 1/21; COMMENCED TELEPHONE REPORTS, FIELD SHUT IN, MOBILIZATION OF DIVERS, FABRICATION OF CLAMP BY TEAM IN ALVIN; DELIVERED 1600 HR ON 1/23; ACQUIRED HYDRO-TORC; CLAMP TIGHT 1500 HR 1/24 ; TESTED LINE 400 PSI GAS PRESSURE OK.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900036 |  | 12931 | MUSTANG FUEL CORP OF MISSISSIPPI | YAZOO | YAZOO | MS |  | 56 | 2956+80 | 1500 | 1990-01-20 | 1 | NO |  | N/A | XX | NO | NO | RUPTURE | 2 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  |  | 580 | 1100 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1971; NMDIA: 12; THK: 0.25; SPEC: N/A; SMYS: 0; SEAM: WELDED; MANYR: 0; LOCLK: UNDER GROUND; PNAME: T.C. RADER; PHONE: 6013523340; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: SHIFTING; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | GROUND SHIFTING
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900042 |  | 6141 | GAS CO OF NEW MEXICO | SEC. 24, T18S,R31E, | EDDY | NM | 88261 |  |  | 1700 | 1990-01-03 | 1 | NO |  |  | NM | Null | YES | OTHER | 0 | 0 | 0 | 150000 | 124708.2019 | 271679.8107 | Null | 2 | 30 | 00227 | 19900103 | 550 | 600 | BY TEST | 660 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1976; NMDIA: 8.63; THK: 0.19; SPEC: 5LX42; SMYS: 42000; SEAM: ERW; VALVE: N/A; MANU: N/A; MANYR: 1976; LOCLK: UNDER GROUND; PNAME: STEVEN EMRICK - DIRECTOR, ENGINEERING; PHONE: 5058888360; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19900103; MARK: YES; MRKTP: EXISTING CARSONITE MARKER; STAT: YES; CTEST: Null | A JETCO 7332 TRENCHER OWNED BY B & H CONSTRUCTION, P.O. BOX 977, EUNICE, NM 88231 AND OPERATED BY B.J. PILKENTON HIT AND SEVERED AN 8" GAS TRANSMISSION LINE. CONTRACTOR REQUESTED LINE LOCATE AND THEN BEGAN EXCAVATION BEFORE LINE WAS LOCATED BY OPERATOR.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900043 |  | 19160 | TENNESSEE GAS PIPELINE CO | LEAPWOOD | MCNAIRY | TN | 38052 | 74-1+7.42 | 392+30 | 1245 | 1990-01-11 | 1 | NO |  | N/A | XX | NO | NO | RUPTURE | 2 | 0 | 0 | 50000 | 41569.4006 | 90559.9369 | Null | 1 | 17 | 00774 | 19900111 | 680 | 750 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1944 | 24 | 0.25 | API 5LX | 50000 | N/A | N/A | A.O. SMITH | 1944 | OTHER | UNKNOWN | RICHARD A. WINN | 7137572581 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION |  | NO |  | NO DATA |  | 0 | 0 | RUPTURE OCCURRED IN WRINKLE (SAG) BEND. THERE WAS NO FIRE AND THE ONLY DAMAGE WAS TO THE PIPE INCLUDING GAS LOST.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900044 |  | 11680 | LONE STAR GAS CO | JOHNSON | AZLE | TX |  |  | 90+02 | 400 | 1989-12-23 | 1 | NO |  |  |  | Null | NO | RUPTURE | 0 | 0 | 0 | 32200 | 27751.1772 | 60456.6056 | YES | 10 | 0 |  | 19891223 | 210 | 500 | BY TEST | 550 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1953; NMDIA: 12; THK: 0.25; SPEC: API 5L; SMYS: 30000; SEAM: LAP WELD; MANYR: 0; LOCLK: UNDER GROUND; PNAME: G.M. FOWLER - SUPERINTENDENT; PHONE: 8176453271; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900045 |  | 20245 | UNITED TEXAS TRANSMISSION CO | PORT ARTHUR | JEFFERSON | TX |  | 73.30 | 3870+24 | 745 | 1989-11-12 | 3 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 26761 | 23063.6414 | 50244.6964 | YES | 5 | 15 |  | 19891112 | 700 | 780 | BY TEST | 1186 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: 2" DUMP LINE; MLKD: STEEL; PRTSY: OTHER; PRTSO: 2" DUMP LINE; PRTYR: 1952; NMDIA: 2; THK: 0.15; SPEC: UNKNOWN; SMYS: 35000; SEAM: SEAMLESS; MANYR: 0; LOCLK: UNDER GROUND; PNAME: PAUL HAAS/REG. COMPL. SPEC.; PHONE: 7139633243; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19891112; MARK: YES; MRKTP: P/L JUNCTION YARD; STAT: NO; CTEST: Null | BACK HOE HIT 2" DUMP LINE ON TRANSMISSION MAIN WHILE EXCAVATING FOR A VALVE REPLACEMENT.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900046 |  | 10030 | K N ENERGY INC(KANSAS NEBRASKA GAS CO) |  | NUCKOLLS | NE | 68961 |  | 763+10 | 500 | 1990-01-19 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 | 01475 | 19900121 | 350 | 400 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1952; NMDIA: 5.04; THK: 0.21; SPEC: N/A; SMYS: 0; SEAM: N/A; MANU: NORTHERN ORDINANCE CO; MANYR: 1946; LOCLK: UNDER GROUND; PNAME: JAMES R. PHILLIPS, CONSTR. & STANDARDS; PHONE: 4024622141; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: MATERIAL; CTEST: NO; MED: NO DATA; TMPS: 0; LKPS: 0 | TOWN METERING CHART (1.5 MILES AWAY FROM LEAK ARE) INDICATED A DROP IN SUPPLY PRESSURE OCCURRED ABOUT 5 A.M. ON 1/19/90. LEAKAGE INCREASED OVER THE NEXTFEW DAYS UNTIL A FEW CUSTOMER SERVICES WERE LOST IN TOWN. LEAKAGE INVESTIGATION CREW LOCATED DEFECTIVE PIPE SHORTLY AFTERWARDS AND MADE REPAIR. EXTENT AND LOCATION OF LEAK CAUSED GAS SERVICE TO NELSON, NE CUSTOMERS TO BE INTERRUPTED UNTIL REPAIRS WERE COMPLETED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900049 |  | 14211 | ONG TRANSMISSION CO | INGALLS | PAYNE | OK | 74074 |  |  | 900 | 1990-01-12 | 1 | NO |  |  | OK | Null | NO | OTHER | 0 | 0 | 0 | 52200 | 43398.4543 | 94544.5741 | Null | 2 | 15 |  | 19900112 | 100 | 200 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1954; NMDIA: 6; THK: 0.22; SPEC: API 5L; SMYS: 42000; SEAM: ERW; VALVE: N/A; MANYR: 0; LOCLK: UNDER GROUND; PNAME: JAMES M. WOOD, CHIEF ENGINEER; PHONE: 9185887600; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: LINE MARKERS; STAT: YES; CTEST: Null | CONTRACTOR CONSTRUCTING WELL LOCATION PUNCTURED PIPELINE WITH DOZER. LOST TOWNS OF PAWNEE AND INGALLS, OKLAHOMA; APPROXIMATELY 1350 CUSTOMERS.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19900056 |  | 2527 | COASTAL STATES GAS TRANSMISSION CO | BRAZOS BLOCK 368 |  | TX |  |  |  | 1500 | 1989-12-01 |  | YES | BRAZOS | 368 | TX | Null | NO | LEAK | 0 | 0 | 0 | 10000 | 8618.378 | 18775.3434 | Null | 0 | 0 |  | 19891204 | 585 | 1440 | BY TEST | 2400 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1975 | 8.62 | 0.32 | API 5LX-42 | 2698 | ERW |  |  | 0 | UNDER WATER |  | RICHARD SASSON | 7138776198 | INTERNALLY | OTHER | UNKNOWN | OTHER | INTERNAL LIQUIDS | COATED | YES | 1975 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900057 |  | 19325 | TEXAS UTILITIES FUEL CO |  | LEON | TX |  | BVA65 & BVA68 |  | 1323 | 1990-01-13 | 1 | NO |  |  | TX | Null | NO | LEAK | 0 | 0 | 0 | 28000 | 23278.8644 | 50713.5647 | Null | 48 | 0 |  | 19900115 | 235 | 468 | BY CFR 192.619(A)(3) | 193 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1957 | 8 | 0.32 | GRADE B | 2613 | ERW |  | N/A | 0 | UNDER GROUND |  | DANIEL RAY ALCORN | 2148126870 | INTERNALLY | GENERAL CORROSION |  | OTHER | UNKNOWN | COATED | YES | 0 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | PINHOLE LEAK IN 8 INCH PIPELINE BETWEEN MILE MARKER BVA65 AND BVA68 IN LEON CO.ON THE GRAPELAND - OLETHA PIPELINE. PINHOLE LEAK DUE TO CORROSION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900059 |  | 11680 | LONE STAR GAS CO | VICTORIA |  | TX |  | 195+76 |  | 1300 | 1989-01-18 | 1 | NO |  |  |  | Null | NO | RUPTURE | 0 | 0 | 0 | 15000 | 12927.567 | 28163.015 | YES | 0 | 45 |  | 19890118 | 511 | 617 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1942; NMDIA: 14; THK: 0.25; SPEC: GRADE A; SMYS: 30000; SEAM: LAP WELD; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: UNDER GROUND; PNAME: D.E. TROCHTA-SUPERINTENDENT; PHONE: 5125264612; PROT: Null; CAULK: EARTH MOVEMENT: SUBSIDENCE; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: NO; CTEST: Null | RUPTURED PIPE TO BE TESTED BY A METALLURGIST AT A LATER DATE FOR FURTHER INFORMATION ON CAUSE OF RUPTURE. PIPE TO SOIL READINGS AT THE SIGHT WERE NO. END:.87 SO. END:.91 WITH A SOIL POTENTIAL OF NEUTRAL.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900063 |  | 19235 | TEXAS EASTERN GAS PIPELINE CO | ATHENS | ATHENS | OH | 45701 | STATION 213 | MILE POST 620 | 154 | 1990-02-05 | 3 | NO |  |  | OH | Null | NO | OTHER | 0 | 0 | 0 | 50000 | 41569.4006 | 90559.9369 | Null | 1 | 6 | 06941 | 19900205 | 835 | 1100 | BY TEST | 2200 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: IMPELLER WHEEL; MLKD: OTHER; MLKDO: CAST STEEL; PRTSY: OTHER; PRTSO: UNKNOWN; PRTYR: 1956; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: W.M. DAVIS, MGR. TECH. OPERATIONS; PHONE: 7136275680; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: MATERIAL; CTEST: Null; MED: NO DATA; TMPS: 0; LKPS: 0 | IMPELLER WHEEL IS A PART OF THE AERO ASSEMBLY WHICH IS THE INTERNAL MAKE-UP OF THE CENTRIFUGAL COMPRESSOR.PART 3 - THE FAILURE OF THE COMPRESSOR UNIT WAS CAUSED BY THE DISINTEGRATION OFTHE RIVETED IMPELLER IN THE CLARK COMPRESSOR, RESULTING IN A VIBRATION WHICH BENT THE COMPRESSOR SHAFT, BROKE UP THE BEARING HOUSING IN THE COMPRESSOR PEDESTALAND BREACHED THE COMPRESSOR GAS SEAL.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900068 |  | 1552 | BLUE DOLPHIN PIPELINE CO |  | BRAZORIA | TX |  | Y=430,253.12 | X=3,240,345.81 | 745 | 1990-02-22 |  | YES | GA | 276 |  | YES | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 64 | 15 | 09305 | 19900222 | 335 | 1000 | BY TEST | 2160 | CORROSION | CORROSION | INTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1965; NMDIA: 20; THK: 0.5; SPEC: API 5 LX; SMYS: 52000; MANYR: 1965; LOCLK: UNDER WATER; PNAME: JOHN C. MCDUFFIE, JR. ENGINEER; PHONE: 7136213993; LOC: INTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: NO DATA; COAT: COATED; PROT: YES; CPYR: 1965; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | 0745 HRS SHEEN REPORTED BY COASTAL HELICOPTED MARKED BY OUR BUOY 1150 HRS. DIVE BOAT ARRIVED 2/24/90, 0600 HRS; LEAK LOCATED 1716 HRS; CLAMP SET 2131 HRS; TESTED OK 400 PSI GAS, 2/25/90 0001 HRS; CHECKED BLACK LIGHT = OK, 0702 HRS 2/25/90, STARED GAS SALES.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900070 |  | 11680 | LONE STAR GAS CO | D9-2-1-2 COLLIN |  | TX |  |  | 74+55 | 1035 | 1990-02-07 | 3 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 9700 | 8064.4637 | 17568.6278 | Null | 0 | 30 |  | 19900207 | 260 | 500 | BY TEST | 750 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1976; NMDIA: 6; THK: 0.25; SPEC: X42; SMYS: 42000; SEAM: SMLS; MANYR: 0; LOCLK: UNDER GROUND; PNAME: J.D. COKER, SUPT, I; PHONE: 8176651777; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19890525; MARK: YES; MRKTP: METAL SIGN & POST; STAT: NO; CTEST: Null | WHILE DIGGING OUT CONCRETE DRAIN PIPE, TRACK MOUNTED LOADER OPERATOR STRUCK AND PUNCTURED 6" STEEL PIPELINE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900071 |  | 22365 | WESTAR TRANSMISSION CO | HART | CASTRO | TX |  |  | 1296+00 | 1500 | 1990-02-26 | 1 | NO |  |  |  | Null | Null | OTHER | 0 | 0 | 0 | 5500 | 4572.6341 | 9961.5931 | Null | 1 | 55 |  | 19900226 | 450 | 500 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1954; NMDIA: 4; THK: 0.24; SPEC: API 5L GB; SMYS: 35000; SEAM: E.W.; MANYR: 0; LOCLK: UNDER GROUND; LOCLO: UNKNOWN; PNAME: H.D. DYSON , DISTRICT SUP'T.; PHONE: 8063713192; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: SIGNS; STAT: NO; CTEST: Null | FARMER HIT WHILE DEEP PLOWING. THIS PORTION OF LINE RUNS DOWNHILL INTO AN OLD LAKE BED. SOIL EROSION TOOK COVER FROM PIPELINE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900075 |  | 20230 | UNITED GAS PIPELINE CO |  |  | LA |  | 1.9 | 99 + 26 | 1100 | 1990-02-23 |  | YES | E.C. | 185 |  | YES | NO | LEAK | 0 | 0 | 0 | 98249 | 81683.0409 | 177948.4648 | Null | 0 | 0 | 09556 | 19900223 | 1080 | 1440 | NO DATA | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | VALVE |  | OTHER | VITON "A" O-RING | PIPELINE |  | 1988 | 0 | 0 |  | 0 |  | 8" | WHEATLEY | 1983 | UNDER WATER |  | WAYNE F. ST. GERMAIN | 7132295772 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | 8" ANSI 900 WHEATLEY WEXWE CHECK VALVE. | YES | 19880617 | WATER |  | 24 | 2217 | LEAK OCCURRED DUE TO THE FAILURE OF AN 0-RING SURROUNDING A DUST COVER ON THE EXTENDED ARM ( SEE ATTACHED SKETCH). THE 0-RING IS MADE OUT OF VITON "A" MATERIAL.SUPPLEMENT: AT 1610 HOURS ON 4/20/90 A PLIDCO CLAMP WAS INSTALLED TO FINALIZETHE REPAIRS.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900082 |  | 20230 | UNITED GAS PIPELINE CO | VENICE | PLAQUEMINES | LA | 70091 | 1.88 | 99+26 | 1325 | 1990-02-10 | 2 | NO |  |  |  | Null | NO | RUPTURE | 0 | 0 | 0 | 500000 | 415694.0063 | 905599.3691 | Null | 4 | 0 | 07978 | 19900212 | 535 | 845 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1951; NMDIA: 10; THK: 0.5; SPEC: API5L, GR. B; SMYS: 35000; SEAM: SEAMLEASS; VALVE: N/A; MANU: YOUNGSTOWN; MANYR: 1950; LOCLK: UNDER WATER; PNAME: D.J. SHEA, SR. ENGINEER; PHONE: 7132295856; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: 12' X 12' SIGNS; STAT: YES; CTEST: Null | LARGE SHIP, ATTEMPTING TO ANCHOR IN THE MISSISSIPPI RIVER, CAUGHT ANCHOR ON PIPELINE. IN ATTEMPTING TO FREE HIMSELF, PIPELINE WAS RUPTURED. PIPELINE CROSSING ALSO LISTED ON NOAA NAVIGATIONAL CHARTS OF MISSISSIPPI RIVER DELTA NO.11361.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900085 |  | 19160 | TENNESSEE GAS PIPELINE CO | EUGENE ISLAND |  | LA |  | 524X-202+0.00 | 0+02 | 1150 | 1990-02-14 |  | YES | EUGENE ISLAND | 338 |  | YES | NO | LEAK | 0 | 0 | 0 | 200000 | 166277.6025 | 362239.7476 | Null | 2 | 0 | 08379 | 19900214 | 1150 | 1964 | BY TEST | 2166 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1976; NMDIA: 2.38; THK: 0.22; SPEC: A-106; SMYS: 35000; SEAM: SMLS; MANYR: 1975; LOCLK: UNDER WATER; PNAME: RICHARD A. WINN, REGULATORY ANALYST; PHONE: 7137572581; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; MRKTP: 0N; STAT: Null; CTEST: Null | LOCATION OF INVOLVED FACILITIES LIMITS MARKING OF PIPELINE; HOWEVER, DETAILED CONSTRUCTION DRAWINGS EXIST FOR EXACT FACILITY COORDINATES.CONSTRUCTION BARGE WORKING IN THE EUGENE ISLAND BLOCK 338 AREA DRUG AN ACHOR ACROSS EXISTING VALVE ASSEMBLY SHEARING A 2" BLOWOFF VALVE FROM THE FABRICATED ASSEMBLY AT A DEPTH OF 250 FT.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900086 |  | 19160 | TENNESSEE GAS PIPELINE CO | BARKHAMSTED | LITCHFIELD | CT | 01001 | 2591-101+12.69 | 670+14.7 | 1840 | 1990-02-16 | 1 | NO |  |  |  | Null | NO | RUPTURE | 0 | 0 | 0 | 5000 | 4156.9401 | 9055.9937 | YES | 4 | 0 | 08722 | 19900216 | 645 | 760 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1952 | 4.5 | 0.24 | GRADE A | 30000 | LAP WELD |  | JONES & LAUGHLIN | 1952 | UNDER GROUND |  | RICHARD A. WINN, REGULATORY ANALYST | 7137578476 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION | N/A | NO |  | NO DATA |  | 0 | 0 | TGP'S 4" TORRINGTON LATERAL RUPTURED NEAR YAKMOSHUK ROAD IN BARKHAMSTED, CONNECTICUT. THERE WAS NO LOSS OF SERVICE TO CUSTOMERS. ORIGINATED AT A DENT AND 5" GOUGE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900087 |  | 602 | ARKLA ENERGY RESOURCES | MALVERN | HOT SPRING | AR | 72104 |  | 4517+76 | 5 | 1990-03-11 | 1 | NO |  |  |  | Null | NO | RUPTURE | 43 | 0 | 0 | 51000 | 42400.7886 | 92371.1356 | Null | 1 | 15 | 11793 | 19900311 | 415 | 530 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | LONGITUDINAL | STEEL |  | PIPELINE |  | 1947 | 18 | 0.28 | GRADE "B" | 0 | ERW | N/A | N/A | 1941 | UNDER GROUND |  | RAUL G. ESPINOSA, MGR. OF CONST., P/L SAFETY & DOT COMPLIANC | 3184293924 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL |  | YES | 19521119 | NO DATA |  | 24 | 0 | SEAM FAILURE, PIPE TO BE ANALYZED BY BATTELLE. MOP REDUCED TO 332 PSIG UNTIL BATTELLE RECOMMENDATINS ARE RECEIVED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900088 |  | 405 | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | EUGENE ISLAND | FEDERAL WATERS | LA |  | X=1,881,731.56 | Y= -66,264.35 | 1635 | 1990-03-12 |  | YES | EUGENE ISLAND | 266 |  | YES | NO | LEAK | 0 | 0 | 0 | 63000 | 52377.4448 | 114105.5205 | Null | 0 | 0 | 13228 | 19900313 | 880 | 1250 | BY TEST | 2683 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1970 | 12 | 0.38 | API-5LX | 46000 | ERW | N/A | AMERICAN STEEL | 1970 | OTHER | UNKNOWN | DONALD E. CROSS, C.S.&P. | 3134962460 | INTERNALLY | LOCALIZED PITTING |  | OTHER | UNKNOWN | COATED | YES | 1970 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900089 |  | 22617 | WILLIAMS NATURAL GAS CO | UNKNOWN | LABETTE | KS |  | 1-1/8 MI. E. M.P. # 10 | 903+17 | 815 | 1990-03-01 | 1 | NO |  |  | KS | Null | NO | RUPTURE | 48 | 0 | 0 | 50000 | 41569.4006 | 90559.9369 | YES | 0 | 0 | 10340 | 19900305 | 680 | 720 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: LONGITUDINAL; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1948; NMDIA: 20; THK: 0.25; SPEC: API 5L X 42; SMYS: 42000; SEAM: EW; VALVE: N/A; MANU: YOUNGSTOWN; MANYR: 1947; LOCLK: UNDER GROUND; PNAME: WARREN ETHERIDGE, COORD. REG. COMP.; PHONE: 9185884427; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900090 |  | 1552 | BLUE DOLPHIN PIPELINE CO |  | BRAZORIA | TX |  | Y=426,802.59 | X=3,264,212.86 | 755 | 1990-03-12 |  | YES | GA | 275 |  | YES | NO | LEAK | 9 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 | 11908 | 19900312 | 341 | 1000 | BY TEST | 2160 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1965 | 20 | 0.5 | API 5 LX | 52000 | SEAMLESS |  | N/A | 0 | UNDER WATER |  | JOHN C. MCDUFFIE, JR., ENGINEER | 7136213993 | INTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1965 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | OIL SLICK OBSERVED BY COASTAL HELICOPTER REPORTED TO US. WE DROPPED BUOY MARKER AND ORDERED OUT LOCAL DIVERS ON BOAT FROM LOUISIANA WHICH ARRIVED 1400 HRS. 13 MAR., BUT WAS FORCED OFF LOCATION BY WEATHER 14 MAR. AND RETURNED 15 MAR. TO INSTALL A CLAMP, TIGHTENED 1950 HRS, 15 MARCH. THEN TESTED OK W/BLACKLIGHT AND 400 PSI GAS PRESSURE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900091 |  | 19570 | TRANSCO GAS PIPELINE CORP | PINE GROVE | ST HELENA | LA |  | 22.52 | 1189+11 | 1430 | 1990-02-25 | 1 | NO |  |  |  | Null | NO | RUPTURE | 27 | 0 | 0 | 150000 | 124708.2019 | 271679.8107 | Null | 1 | 0 | 09747 | 19900225 | 833 | 975 | BY TEST | 1265 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1958 | 24 | 0.31 | API 5LX | 52000 | FLASH WELD |  | A.O. SMITH | 1958 | UNDER GROUND |  | B.R. LANDES, SR. COMPLIANCE ANALYST | 7134392522 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1958 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | THE RUPTURE BLEW OUT APPROXIMATELY 27 FEET OF THE PIPELINE. MEASUREMENTS MADE ALONG TEH SEAM WELD OF THE RECOVERED PIECES SHOWED THAT ALL THE MISSING PIPE FROM THE LINE HAD BEEN FOUND. THE RESULTS OF THE FIELD AND LABORATORY EXAMINATIONS SHOWED THAT THE FAILURE WAS THE RESULT OF WALL THINNING CAUSED BY EXTERNAL CORROSION OF THE PIPE BODY. THE TENSILE PROPERTIES AND THE CHEMICAL COMPOSITION OF THE FAILED PIPE MET THE REQUIREMENTS OF API SPECIFICATION 5L FOR GRADE X52. THE CAUSE OF THE CORROSION WAS NOT DETERMINED. SEE ATTACHED ADDITIONAL COMMENTS.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900100 | 1990-04-16 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA | UNKNOWN |  | LA |  |  |  | 1500 | 1990-03-14 |  | YES | EAST CAMERON | 34 |  | YES | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 72 | 0 |  | 19900315 | 460 | 1440 | BY TEST | 2350 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1978 | 12 | 0.34 | 5LX52 | 52000 | SEAMLESS |  | U.S. STEEL | 1978 | UNDER WATER |  | F. ROY FLEET | 7086913786 | INTERNALLY | OTHER | UNKNOWN | OTHER | UNKNOWN | COATED | YES | 1978 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | THE PIPELINE HAD BEEN SHUT-IN FOR TWO YEARS PRIOR TO LEAK. THE PIPELINE HASNOW BEEN FILLED WITH WATER IN PREPARATION FOR ABANDONMENT.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900101 | 1990-04-16 | 11680 | LONE STAR GAS CO | LOUISE | JACKSON | TX |  | 75.6 | 4092+59 | 430 | 1990-03-22 | 1 | NO |  |  |  | Null | Null | OTHER | 0 | 0 | 0 | 17485 | 14536.8194 | 31668.8099 | YES | 0 | 0 |  | 19900322 | 455 | 606 | BY TEST | 909 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1942; NMDIA: 16; THK: 0.38; SPEC: GRADE A; SMYS: 30000; SEAM: LAP WELL; VALVE: N/A; MANU: UNKNOWN; MANYR: 0; LOCLK: UNDER GROUND; PNAME: LOIS ROSS - CLERK; PHONE: 2146701566; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: LINE MARKER; STAT: NO; CTEST: Null | ONE MARKER 110 FEET AND THE OTHER MARKER IS 1957' FROM DAMAGE AREA.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900102 | 1990-04-19 | 20230 | UNITED GAS PIPELINE CO | CANTONMENT | ESCAMBIA | FL |  | 1.85 | 97+50 | 1015 | 1990-03-20 | 2 | NO |  |  |  | Null | NO | RUPTURE | 0.5 | 0 | 0 | 10700 | 8895.8517 | 19379.8265 | YES | 0 | 58 | 10402 | 19900320 | 330 | 465 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1941; NMDIA: 6; THK: 0.19; SPEC: 24; SMYS: 24000; SEAM: FURNACE LAP; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: UNDER GROUND; PNAME: W.F. ST. GERMAIN, SR. ANALYST; PHONE: 7132295772; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: ROAD MARKERS; STAT: YES; CTEST: Null | ESCAMBIA COUNTY MAINTENANCE DEPARTMENT ROAD GRADER HIT LINE WHILE GRADING ROAD DITCH.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900103 | 1990-04-20 | 19160 | TENNESSEE GAS PIPELINE CO | MOREHEAD | ROWAN | KY | 40351 | COMPRESSOR STA. 110 |  | 1745 | 1990-03-19 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 50000 | 41569.4006 | 90559.9369 | Null | 0 | 40 | 13346 | 19900319 | 0 | 0 | NO DATA | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: FLEX. FUEL GAS LINE; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1959; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: OTHER; LOCLO: COMPRESSION STATION; PNAME: RICHARD A. WINN, REGUALTORY ANALYST; PHONE: 7137572581; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: MATERIAL; CAULO: FLEXIBLE STEEL BRAIDED FUEL GAS LINE.; CTEST: Null; MED: NO DATA; TMPS: 0; LKPS: 0 | A FLEXIBLE (STEEL BRAIDED) FUEL GAS LINE TO THE #3 ENGINE BROKE AND IGNITED. THE FIRE BURNED THROUGH A RUBBER OIL DRAIN BOOT CAUSING OIL TO IGNITE AND SPREAD THE FIRE ON ONE SIDE OF THE #3 UNIT AND IMMEDIATELY UNDER THE UNIT AT BASEMENT LEVEL.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900104 | 1990-04-25 | 2252 | CHANNEL INDUSTRIES GAS CO | ORANGE |  | TX |  | 819-1+8.5 | 449+51 | 1530 | 1990-03-23 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 8 | 30 | 14107 | 19900323 | 500 | 0 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: TAP CONNECTION; MLKD: STEEL; PRTSY: OTHER; PRTSO: TAP CONNECTION; PRTYR: 1969; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: UNDER GROUND; PNAME: RICHARD A. WINN, REGULATORY ANALYST; PHONE: 7137572581; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | COMPANY'S CONTRACTOR WAS WORKING IN WET SOIL CONDITIONS WHICH CAUSED BACKHOETO PUSH SOIL AGAINST NIPPLE AND SIDE VALVE, CAUSING NIPPLE TO BREAK.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900108 | 1990-05-01 | 19160 | TENNESSEE GAS PIPELINE CO | NATCHITOCHES |  | LA | 71457 | 40-3X4.90 |  | 600 | 1990-04-02 | 1 | NO |  |  |  | Null | NO | RUPTURE | 0 | 0 | 0 | 1000000 | 831388.0126 | 1811198.7382 | Null | 2 | 0 | 15342 | 19900402 | 650 | 750 | BY TEST | 750 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1950; NMDIA: 26; THK: 0.5; SPEC: X-40; SMYS: 40000; SEAM: FLASH WELD; MANU: A.O. SMITH; MANYR: 1950; LOCLK: UNDER WATER; PNAME: RICHARD A. WINN, REGULATORY ANALYST; PHONE: 7137572581; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | RUPTURE OCCURRED IN APPROXIMATELY THE MIDDLE OF THE RED RIVER CROSSING. EXISTING HEAVY FLOODING CONDITIONS AND RESULTING STRONG CURRENTS AND RIVERBED WASHING WAS THE CAUSE OF THE INCIDENT.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900109 | 1990-05-03 | 19160 | TENNESSEE GAS PIPELINE CO | PILOTTOWN | PLAQUEMINES | LA |  | 526A-601+3.00 |  | 820 | 1990-04-03 | 1 | NO |  |  |  | Null | Null | LEAK | 0 | 0 | 0 | 800000 | 665110.4101 | 1448958.9905 | Null | 1 | 45 | 15590 | 19900403 | 800 | 1133 | BY TEST | 2014 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1956; NMDIA: 10.75; THK: 0.37; SPEC: X-42; SMYS: 42000; SEAM: SMLS; MANU: NATIONAL TUBE; MANYR: 1956; LOCLK: UNDER WATER; PNAME: RICHARD A. WINN, REGULATORY ANALYST; PHONE: 7137572581; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | MISSISSIPPI RIVERBED WASHIING FROM FLOODING AND STRONG CURRENTS PROBABLY CAUSED PIPELINE FAILURE. ACCESSIBILITY IS LIMITED UNTIL CURRENT FLOODING CONDITIONS SUBSIDE. THE LINE HAS BEEN TAKEN OUT OF SERVICE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900110 | 1990-05-04 | 405 | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | VIOLA | MERCER | IL | 61486 | 688.9 | 1224 + 24 | 1930 | 1990-04-06 | 1 | NO |  |  | IL | Null | NO | LEAK | 0 | 0 | 0 | 50000 | 41569.4006 | 90559.9369 | Null | 0 | 45 | 16217 | 19900406 | 750 | 975 | BY TEST | 1392 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | OTHER | WRINKLE BEND | STEEL |  | PIPELINE |  | 1949 | 24 | 0.31 | API-5LX | 52000 | DBL SUBMERGED | N/A | REPUBLIC STEEL | 1949 | UNDER GROUND |  | R.E. MAKOWSKI, DIRECTOR, C.S. & P. | 3134962156 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | N/A | YES | 19760913 | WATER |  | 24 | 1392 | THIS INCIDENT OCCURRED WHILE THE PIPELINE SEGMENT WAS BEING INSPECTED WITH ALINALOG DEVICE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900113 | 1990-05-24 | 13750 | NORTHERN NATURAL GAS CO (ENRON) | SEMINOLE | GAINES | TX |  |  |  | 215 | 1990-04-25 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 210000 | 174591.4826 | 380351.735 | Null | 0 | 0 | 18944 | 19900425 | 0 | 0 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: VALVE OPERATOR; MLKD: OTHER; MLKDO: UNKNOWN; PRTSY: COMPRESSOR STATION; PRTYR: 1967; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: TILFORD N. VIK, MANAGER, CODES & STDS; PHONE: 7138537329; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: LIGHTNING; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | LOSS OF AC POWER DUE TO LIGHTNING ACTIVATED STATION EMERGENCY SHUTDOWN SYSTEM. SUCTION SIDE VALVE FAILED TO OPERATE WHICH ALLOWED GAS TO VENT THROUGH STATION BLOWDOWNS UNTIL MANUALLY CLOSED (75 MIN.).
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19900114 | 1990-05-22 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA | REDWATER | BOWIE | TX |  | MIKE ROGERS METER STATION |  | 500 | 1990-04-22 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 1 | 0 | 0 | 0 | Null | 6 | 30 | 18365 | 19900422 | 730 | 1200 | BY TEST | 1800 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | VALVE |  | STEEL |  | REGULATOR/METERING SYSTEM |  | 1989 | 0 | 0 |  | 0 |  | 2" CLASS 600 CH | JUDD | 1983 | ABOVE GROUND |  | F. ROY FLEET, SENIOR ENGINEER | 7086913786 | EXTERNALLY | OTHER | UNKNOWN | OTHER | UNKNOWN | BARE | NO | 0 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | THE COVER BOLTS ON A 2" CHECK VALVE IN SOUR GAS SERVICE FAILED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900115 | 1990-05-14 | 12576 | MISSISSIPPI RIVER TRANSMISSION CORP | CARLISLE | LONOKE | AR | 72024 | 156 | 907+39 | 1320 | 1990-04-13 | 1 | NO |  |  |  | Null | NO | RUPTURE | 29.5 | 0 | 0 | 100000 | 83138.8013 | 181119.8738 | Null | 1 | 20 | 17128 | 19900413 | 680 | 720 | BY TEST | 888 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1968; NMDIA: 26; THK: 0.25; SPEC: API 5L; SMYS: 52000; SEAM: SUBMERGED ARC; MANU: U.S. STEEL; MANYR: 1968; LOCLK: UNDER GROUND; PNAME: PHILLIP J. HANKS, CODES & STANDS. ENGR.; PHONE: 3149919900; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900117 | 1990-06-01 | 13845 | NORTHWEST PIPELINE CORP | OLENE | KLAMATH | OR |  | MP 11.I, KLAMATH FALLS | 624+06 | 900 | 1990-05-09 | 2 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 0 | 21397 | 19900509 | 900 | 911 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | LONG | STEEL |  | PIPELINE |  | 1962 | 4.5 | 0.13 | API 5L | 1944 | ERW |  | REPUBLIC | 0 | OTHER | UNKNOWN | MURLE ANDERSON, PIPELINE SAFETY SPEC. | 8015846906 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL |  | YES | 19620325 | GAS |  | 0 | 0 | THERE WERE SEVERAL PINHOLE LEAKS IN THE LONG SEAM. THE LEAK WAS DISCOVERED DURING THE ANNUAL LEAK SURVEY.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900119 | 1990-06-06 | 12576 | MISSISSIPPI RIVER TRANSMISSION CORP |  | LAWRENCE | AR | 72476 | 252 | 1716+60 | 603 | 1990-05-06 | 1 | NO |  |  | AR | Null | NO | RUPTURE | 28 | 0 | 0 | 100000 | 83138.8013 | 181119.8738 | Null | 1 | 27 | 20690 | 19900506 | 680 | 720 | BY TEST | 902 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1957 | 26 | 0.25 | API 5L | 52000 | SMITHWELD |  | A.O. SMITH | 1957 | UNDER GROUND |  | PHILLIP J. HANKS, CODES & STDS. ENGR. | 3149917308 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION | NONE | YES | 19840802 | WATER |  | 9 | 902 | THE INITIAL REPORT FROM AN INDEPENDENT LABORATORY SUGGESTS THAT A GOUGE IN THE PIPE WAS THE ORIGIN OF FAILURE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900123 | 1990-06-27 | 405 | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  |  | TX |  | X=3,492,201 | Y= 131,857 | 1500 | 1990-06-01 |  | YES | HIA | A-511 |  | YES | NO | LEAK | 0 | 0 | 0 | 170000 | 141335.9621 | 307903.7855 | Null | 0 | 0 | 25140 | 19900604 | 1100 | 1440 | NO DATA | 0 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1979 | 20 | 0.5 | 5LX-60 | 60000 | SUBMERGED ARC |  | KAISER STEEL | 0 | UNDER WATER |  | ROBERT J. LECZNAR, MANAGER | 3134962456 | INTERNALLY | LOCALIZED PITTING |  | OTHER | UNKNOWN | COATED | YES | 1979 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900125 | 1990-07-06 | 19270 | TEXAS GAS TRANSMISSION CORP | T17N; R13W; SEC. 36 | CADDO | LA |  | 57+3200 |  | 800 | 1990-06-06 | 1 | NO |  |  | LA | NO | NO | LEAK | 0 | 0 | 0 | 1586450 | 1318955.5126 | 2873376.2382 | Null | 0 | 22 | 25510 | 19900606 | 585 | 770 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: NO DATA; PRTFO: UNKNOWN; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 0; NMDIA: 16; THK: 0.5; SPEC: X-46; SMYS: 2875; MANU: A.O SMITH; MANYR: 1950; LOCLK: UNDER WATER; PNAME: JAMES E. BEEZH; PHONE: 5029268686; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | NO REMARKS SHOWNED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900126 | 1990-07-09 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA | MAXEY | LAMAR | TX | 75421 | 286 | 15129+73 | 2030 | 1990-06-10 | 1 | NO |  |  |  | NO | NO | RUPTURE | 34 | 0 | 0 | 600000 | 498832.8076 | 1086719.2429 | Null | 4 | 30 | 26163 | 19900610 | 850 | 973 | BY TEST | 1352 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1975; NMDIA: 30; THK: 0.31; SPEC: 5LX; SMYS: 65000; SEAM: DSA; MANU: KAISER; MANYR: 1974; LOCLK: UNDER GROUND; PNAME: F. ROY FLEET, SENIOR ENGINEER; PHONE: 3126913786; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19900430; MARK: YES; MRKTP: PROBED AND STAKED; STAT: YES; CTEST: Null | THE RUPTURE INITIATED AT A 12" LONG GOUGE THAT WAS POSITIONED BETWEEN 3 O'CLOCK AND 6 O'CLOCK. PIPE WAS GOUGED A PERIOD OF TIME BEFORE THE INCIDENT OCCURRED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900133 | 1990-07-25 | 13750 | NORTHERN NATURAL GAS CO (ENRON) | WILLMAR | KANDIYOHI | MN | 56201 | M.P. 89.66 | N/A | 1040 | 1990-06-25 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 61000 | 50714.6688 | 110483.123 | Null | 0 | 55 | 28313 | 19900625 | 650 | 950 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1960; NMDIA: 8; THK: 0.25; SPEC: API 5L; SMYS: 35000; SEAM: ERW; VALVE: N/A; MANU: KAISER STEEL CORP; MANYR: 1960; LOCLK: UNDER GROUND; PNAME: JOHN W. CASKEY, CODE COMPLAINCE ENGINEER; PHONE: 7138537325; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19890915; MARK: YES; MRKTP: PERMANENT PIPELINE SIGNS; STAT: YES; CTEST: Null | MINNESOTA BRANCHLINE MNB 75601 WAS SEVERED BY A SCRAPER DOING EXCAVATION WORK FOR RECONSTRUCTION OF A COUNTY ROAD.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19900134 | 1990-07-26 | 18152 | SEA ROBIN PIPELINE CO |  |  | LA |  | 30" INDEX 701 | 36" PIG RECEIVER | 820 | 1990-06-25 |  | YES | VERMILION | 149 |  | YES | NO | OTHER | 0 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 5 | 28274 | 19900625 | 948 | 1200 | BY TEST | 1737 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: PIG RECEIVER; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1970; NMDIA: 0; THK: 0; SPEC: SERIES 600-H; SMYS: 1440; MANYR: 0; LOCLK: OTHER; LOCLO: OFFSHORE PLATFORM; PNAME: W. ST. GERMAIN, SR. P.L. ANALYST; PHONE: 7132295772; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | A CREW OF THREE (3) MEN WERE ATTEMPTING TO REMOVE A SPHERE FROM A PIG RECEIVER. AFTER BELIEVING THE PIGTRAP WAS "BLOWNDOWN" THEY ATTEMPTED TO OPEN THE PITTRAP DOOR. TRAPPED PRESSURE EJECTED BOTH THE PIG AND CLOSURE. THREE (3) MEN WERE INJURED, WITH TWO (2) REQUIRING INPATIENT HOSPITALIZATION. (NOTE: THEBLOWDOWN SYSTEM WAS A CLOSED SYSTEM TO A COMMON VENT ACROSS A BRIDGE ON A TRIPOD PLATFORM. NORMALLY, ALL VALVES BETWEEN THE BLOWDOWN VENT AND THE PIG RECEIVER WOULD BE OPENED TO ACHIEVE BLOWDOWN TO ATMOSPHERE. PRELIMINARY INVESTIGATIONS INDICATE THAT AT LEAST ONE OF THESE VALVES WAS NOT OPENED TO ALLOW THE PIG RECEIVER TO VENT PROPERLY.)
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900135 | 1990-08-02 | 19235 | TEXAS EASTERN GAS PIPELINE CO | GAYSPORT | MUSKINGUM | OH |  | MP 909.596 | 48026+28 | 1035 | 1990-07-03 | 1 | NO |  |  | OH | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | Null | 1 | 25 | 29366 | 19900703 | 560 | 630 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1943; NMDIA: 24; THK: 0.38; SPEC: N/A; SMYS: 37000; SEAM: SMLS; VALVE: N/A; MANU: USS; MANYR: 1943; LOCLK: OTHER; LOCLO: UNKNOWN; PNAME: STEVEN DIDIER - PIPELINER ENGINEER; PHONE: 3178473022; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | MOVEMENT OF A LANDSLIDE CAUSED TEXAS EASTERN TRANSMISSION'S 24" PIPELINE TO FAIL. THIS PIPELINE IS LOCATED IN A MAJOR LANDSLIDE AREA THAT ENCOMPASSES MOST OF THE PIPELINE RIGHT-OF-WAY. THIS LANDSLIDE IS TYPICAL OF MANY IN THIS REGION OF OHIO, BEING CHARACTERIZED AS OLD AND VERY SPASMODIC, INTERMITTENT, AND UNPREDICTABLE. THEY CAN BE TRIGGERED BY RAINFALL, CHANGES TO THE TERRAIN, OR BY NATURAL CAUSES. TEXAS EASTERN IS CURRENTLY BUILDING A 36" PIPELINE THROUGH THE SAME SLIDE REGION, PARALLEL TO OUR EXISTING RIGHT-OF-WAY. TO VOID THIS TYPE OF FAILURE ON THE NEW LINE, ITS BEING BURIED TO A GREATER DEPTH, PLACING IT WELL BELOW THE BASE OF SLIDE MOVEMENT.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900140 | 1990-08-02 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA |  |  | LA |  |  |  | 800 | 1990-06-27 |  | YES | WEST CAMERON | 552 |  | YES | NO | LEAK | 0 | 0 | 0 | 90000 | 74824.9211 | 163007.8864 | Null | 77 | 0 | 29641 | 19900705 | 1060 | 1200 | BY TEST | 2160 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1980 | 8 | 0.25 | 5LX52 | 52000 | SEAMLESS | N/A | N/A | 0 | OTHER | UNKNOWN | F. ROY FLEET SENIOR ENGINEER | 7086913786 | INTERNALLY | LOCALIZED PITTING |  | OTHER | UNKNOWN | COATED | YES | 1980 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | THE ATTACHED REPORT CONCERNS AND INCIDENT THAT OCCURRED OFFSHORE OF LOUISIANA. ON JUNE 30,1990, A LEAK WAS CONFIRMED ON THE WC-551 LATERAL IN WEST CAMERON BLOCK 552. THE LEAK WAS REPAIRED THE SAME DAY BY INSTALLING A CLAMP ON THE PIPE. NATURAL GAS PIPELINE COMPANY OF AMERICA OWNS AN INTEREST IN AND OPERATES THE JOINT INTEREST LATERAL.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19900142 | 1990-08-01 | 7055 | HANOVER ENERGY INC | ELDORADO | SCHLEICHER | TX | 76936 | MAINLINE |  | 1915 | 1990-07-03 | 1 | NO |  |  | TX | NO | NO | RUPTURE | 1.5 | 0 | 0 | 350000 | 290985.8044 | 633919.5584 | Null | 1 | 0 |  | 19900704 | 900 | 1050 | BY TEST | 1500 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 0 | 4 | 0.13 | N/A | 0 | N/A | N/A | N/A | 0 | UNDER GROUND |  | RONALD J. ERWIN | 0 0 0 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | THE PIPE | YES | 19890101 | GAS |  | 0 | 900 | SYSTEM PURCHASED FROM BP AMERICAN OCTOBER 1, 1988. OUR KNOWLEDGE IS LIMITEDDUE TO THE INFORMATION RECEIVED BY BP AMERICA. DURING CONSTRUCTION A JOINT OF .125 WALL X-42 WAS USED INADVERTENTLY.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900143 | 1990-08-17 | 2714 | CNG TRANSMISSION CORP | JOHNSONBURG | WYOMING | NY |  |  | 755+69 | 1045 | 1990-07-18 | 1 | NO |  |  |  | Null | NO | RUPTURE | 0.4 | 0 | 0 | 217000 | 180411.1987 | 393030.1262 | Null | 2 | 5 | 31555 |  | 520 | 650 | BY TEST | 994 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1959; NMDIA: 20; THK: 0.31; SPEC: API 5L; SMYS: 35000; SEAM: UNKNOWN; VALVE: N/A; MANU: N/A; MANYR: 1931; LOCLK: UNDER WATER; PNAME: JACK L. ADAMS, ADMINISTRATOR, CODES & STANDARDS; PHONE: 3046238410; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | LANDSLIDE PARALLEL TO PIPELINE CAUSED PIPE TO BUCKLE AND EVENTUALLY CRACK LONGITUDINALLY ALONG THE BUCKLE. FAILURE OCURRED UNDER TONAWANDA CREEK.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900147 | 1990-08-16 | 19160 | TENNESSEE GAS PIPELINE CO | SHIP SHOAL |  | LA |  | 523M-901+2.44 |  | 1500 | 1990-07-10 |  | YES | SHIP SHOAL | 158 |  | YES | NO | RUPTURE | 3 | 0 | 0 | 221000 | 183736.7508 | 400274.9211 | Null | 26 | 10 | 30303 | 19900710 | 990 | 1373 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1981 | 12.75 | 0.38 | X-42 | 42000 | SMLS | N/A | US STEEL | 1981 | UNDER WATER |  | RICHARD A. WINN, REGULATORY ANALYST | 7137572581 | INTERNALLY | LOCALIZED PITTING |  | OTHER | UNKNOWN | COATED | YES | 1981 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900149 | 1990-08-28 | 8040 | ILLINOIS POWER CO | LA SALLE | LA SALLE | IL | 61301 |  |  | 745 | 1990-08-17 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 70000 | 58197.1609 | 126783.9117 | Null | 1 | 30 | 35901 | 19900817 | 500 | 500 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: RELIEF VALVE; MLKD: OTHER; MLKDO: RUBBER BOOT; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 0; NMDIA: 6; THK: 0; SMYS: 0; VALVE: FLEX FLO II; MANU: GROVE; MANYR: 1982; LOCLK: ABOVE GROUND; PNAME: G E CARTER; PHONE: 2174246853; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | ON AUGUST 17, 1990, AT APPROXIMATELY 7:50AM, A FIRE WAS REPORTED AT THE LASALLE #2 DELIVERY STATION WHICH RECEIVES NATURAL GAS FROM NGPL. THE FIRE WAS REPORTED BY A NEIHBOR WHO NOTED A LIGHTENING STRIKE IN THE IMMEDIATE VICINITY & NOTED TWO DISTINCT FIRES. THE FIRST FIRE WAS NOTED AS A GLOW INSIDE A CONTROL VALVE BUILDING, FOLLOWED BY A BALL OF FIRE IN THE STATION. (NO EXPLOSION OCCURED, BUT FIRE/HEAT WAS THE SOURCE OF ALL DAMAGE). THE INITIAL INVESTIGATION THERORIZES THAT LIGHTEDING WAS THE SOURCE OF IGNITION TO A RELIEF VALVE BLOWING. FURTHER INVESTIGATION IS BEING PERFORMED AS TO THE CAUSE OF THIS OCCURRENCE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900150 | 1990-08-30 | 15329 | PEOPLES GAS LIGHT & COKE CO | FISHER | CHAMPAIGN | IL | 61843 |  |  | 430 | 1990-08-12 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 50000 | 41569.4006 | 90559.9369 | Null | 0 | 1 | 35069 | 19900812 | 1760 | 2000 | BY TEST | 3000 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: COMPRESSOR ROD; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1972; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: T KOLLER - SUPT; PHONE: 3124314741; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | A FRACTURE OCCURED IN A COMPRESSOR ROD AT THE POINT WHERE THE ROD ATTACHES TO THE COMPRESSOR PISTON. THIS FAILURE IN TURN CAUSED THE CYLINDER HEAD TO FAILAND THE COMPRESSOR FLANGE, HEAD AND PISTON WERE BLOWN OFF AND OUT OF THE COMPRESSOR. AUTOMATIC EQUIPMENT PERFORMED AN EMERGENCY SHUTDOWN OF THE UNIT ANDSHUT-IN THE GAS SUCTION AND DISCHARGE PIPING WITHOOUT FURTHER INCIDENT.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19900153 | 1990-08-29 | 2616 | COLUMBIA GAS TRANSMISSION CORP | BEVERLY | RANDOLPH | WV | 26253 |  | 5142+85 | 1001 | 1990-07-30 | 1 | NO |  |  |  | Null | NO | RUPTURE | 4 | 0 | 1 | 150000 | 124708.2019 | 271679.8107 | Null | 0 | 4 | 33262 | 19900730 | 800 | 800 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | FITTING | FAB BRANCH CONNECTION | STEEL |  | PIPELINE |  | 1951 | 26 | 0.41 | GRADE X-52 | 52000 | FLASH WELD |  | AO SMITH | 0 | UNDER GROUND |  | EDWARD B CLARK - SUPV ENG - QA | 3043572151 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | 26X24", SADDLE REINFORCED BRACH CONNECTION | NO |  | NO DATA |  | 0 | 0 | A PRELIMINARY INVESTIGATION INDICATED THAT THE RUPTURE INITIATED IN A 26 X 24 INCH OD, SADDLE REINFORCED BRANCH CONNECTION INSTALLED IN '51. THE PIPE MATERIALS USED HAVE BEEN DESCRIBED IN THE REPORT FORM. AT THE TIME OF THE RUPTURE THERE WAS CONTRUCTIONIN THIS AREA REQUIRED TO CONNECT A CROSSOVER TO ANOTHER PIPELINE. THE BACKFILL OVER THIS BRANCH CONNECTION HAD BEEN REMOVED. THE LOCATION OF THIS FAILURE RELATIVE TO THE FILES CREEK COMNPRESSOR STATION IN SHOWN IN FIGURE 1. VISUAL EXAMINATION OF THE FRACTURE SURFACES SHOWED EVIDENCE OF A LONG, PRE-EXISTING CRACK AT THE EDGE OF THE FILLET WELD TOE ON THE OUTSIDE SURFACE. THIS FRACTURE APPEARED TO BE PRIMARILY BRITTLE. IT IS POSSIBLE THAT THIS CRACK WAS FORMED FROM SMALL WELD FLAWS THAT WERE A RESULT FO THE ORIGINAL FABRICATION WELDING. PRESSURE FLUCTUATIONS OVER THE SERVICE LIFE CREATED A CYCLIC STRESS LOADING THAT CAUSED GROWTH AND LINKAGE TO FORM NEAR CRITICAL CRACK DIMENSIONS. THIS PARTICULAR LOCATION NEAR THE ASSUMED ORIGIN IS ONE OF THE HIGHEST STRESS IN SUCH A BRANCH CONNECTION. A DRAWING OF THIS RUPTURE IS ATTACHED AS FIGURE 2. ANY STRESS IMPOSED THAT WAS INCIDENTAL OF A NEW FORGED TEE IN THE 26" OD PIPELINE AND ASSOCIATED CROSSOVER PIPING MAY HAVE CONTRIBUTED TO ADDITIONAL CRACK GROWTH. THE RELATIVE LOCATION OF THE NEW TEE TO THE SUPTURE LOCATION IS SHOWN IN FIGURE 3. THE O TO 800 PSI PRESSURE INCREASE MAY HAVE ALSO CAUSED SOME GROWTH. A FOUR FOOT LONG SECTION OF THE BACK SIDE OF THE BRANCHCONNECTION WAS EJECTED FROM THE DITCH. THE LOCATION OF THIS SECTION HAS BEEN INDICATED IN FIGURE 3.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900154 | 1990-08-29 | 7605 | HOUSTON PIPELINE CO | MANVEL | BRAZORIA | TX | 77578 | MANVEL COMPRESSOR STATION |  | 1954 | 1990-07-24 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 300000 | 249416.4038 | 543359.6215 | Null | 1 | 21 | 32465 | 19900724 | 680 | 1100 | BY TEST | 1650 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1988; NMDIA: 0.25; THK: 0.12; SPEC: 316 SS, SCH.80; SMYS: 25000; SEAM: WELDED; MANYR: 0; LOCLK: OTHER; LOCLO: IN BUILDING (COMPRESSOR); PNAME: RODNEY ROGERS - SENIOR ENGINEER; PHONE: 7138537469; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | PIPE ON COMPRESSOR DISCHARGE HEADER FAILED, RESULTING IN A FIRE.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19900155 | 1990-08-28 | 5405 | FORT COBB FUEL IRRIGATION AUTH | EAKLY | CADDO | OK | 73033 | NE/4, S4, T9N, R13W |  | 1545 | 1990-07-19 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 30 | 31718 | 19900719 | 20 | 60 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: OTHER; PRTFO: NO FAILURE; MLKD: OTHER; MLKDO: PVC PIPE 2"; PRTSY: PIPELINE; PRTYR: 1970; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: OTHER; LOCLO: EXCAVATED LINE SECTION; PNAME: WILLIAM I CHURCHILL - CONTROLLER; PHONE: 4058433458; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | THE INCIDENT WAS A FIRE SUPPORTED BY ESCAPING NATURAL GAS DURING ROUTINE LINE MAINTENANCE. THE SPECIFIC TASK BEING PERFORMED WAS THE REPLACEMENT OF AN APPROXIMATE 390 FOOT SEGMENT OF 2" PVC DISTRIBUTION LINE TO PERMIT LOWERING OF THIS SEGMENT. THE SEGMENT HAD BEEN EXPOSED AT ABOVE GROUND LEVEL BY FLASH FLOODING DURING EARLIER HEAVY RAINFALLS. SEE ACCOMPANYING PHOTO #1 SHOWING EXPOSED LINE SEGMENT AND REPLACEMENT. PER STATEMENTS FROM ONE OF THE INJURED INDIVIDUALS, MR. WILLIS McGARRAH, FLOWING GAS FROM THE UPSTREAM (EAST) END OF THE SEGMENT OF LINECARRIED SOME FOREIGN PARTICLES. THESE WERE GREY/WHITE DUST OF DIRT IN APPERANCE FROM THE OPEN END OF THE LINE. THIS APPEARED TO HAVE CONTRIBUTED TO OR CAUSEWD THE INCIDENT BY STATIC ELECTRICITY SPARK IGNITION OF THE VENTING GAS STREAM.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900156 | 1990-09-06 | 4280 | EL PASO NATURAL GAS CO | THOREAU | MCKINLEY | NM |  | 361+3606 | 1800+60 | 1555 | 1990-08-09 | 1 | NO | N/A |  | NM | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 15 | 34851 | 19900810 | 545 | 697 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | TRANSMISSION SYSTEM | FITTING | 1" NIPPLE | STEEL |  | OTHER | MAINLINE DRIP | 1953 | 30 | 0.34 | API 5LX | 52000 | ELEC FUSION WEL | N/A | A.O. SMITH | 1953 | OTHER | CONCRETE BOX OPEN TOP | RICHARD FAVILA, SENIOR ENGINEER | 9155412062 | [6 empty] | Null |  | OPERATOR ACTION |  | NO |  | Null | 0 | Null |  |  | Null | [5 empty] | A CONTRACTOR, WHILE REMOVING A CONCRETE VAULT FROM AROUND A DRIP THAT WAS BEING REMOVED FROM AROUND A DRIP THAT WAS BEING REMOVED FROM OUR 30-INCH PERMIAN - SAN JUAN LINE NO. 1300, ACCIDENTLY KNOCKED OFF A 1-INCH NIPPLE DIRECTLY CONNECTED TO THE LINE, CAUSING GAS TO ESCAPE. THE LINE BLEW FOR APPROXIMATELYTHREE HOURS WHILE A 2-INCH BYPASS WAS INSTALLED TO PREVENT CURTAILMENT OF SERVICE TO THE TOWN OF THOREAU, NEW MEXICO. STATE HIGHWAY 57/412 WAS TEMPORARILY CLOSED DUE TO THE 2-INCH BYPASS BEING LAID ACROSS THE HIGHWAY WHILE REPAIRS WERE BEING MADE. THE LINE WAS REPAIRED AND BACK IN SERVICE BY 10:00 PM. MDT THE SAME DAY (08/09/90).
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19900158 | 1990-09-13 | 11616 | LLANO INC | SEC. 34, T21S, R34E | LEA COUNTY | NM |  | GRMSU #2 |  | 1715 | 1990-08-28 | 3 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 0 |  |  | 500 | 0 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: COMPRESSOR; MLKD: OTHER; MLKDO: CAST IRON; PRTSY: COMPRESSOR STATION; PRTYR: 1974; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: A.V.P & GEN. MGR; PHONE: 5053932153; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | LLANO EMPLOYEES HAD INSTALLEDNEW PRESURE PACKING ON A FIRST STAGE COMPRESSORCYLINDER. THE DISTANCE PIECE INSPECTION DOOR HAD BEEN REPLACED AND RE-PRESSURING OF THE COMPRESSOR CYLINDER INITIATED. GAS LEAKING BY THE NEW PRESSURE PACKING EXCEEDED THE CAPACITY OF THE DISTANCE PIECE VENT AND CAUSED AN PRESSURE BUILD-UP IN THE DISTANCE PIECE. THE PRESSURE BUILD-UP CAUSED THE DISTANCEPIECE INSPECTION DOOR TO FRAGMENT. THE CAST IRON FRAGMENTS FROM THE INSPECTION DOOR STRUCK AN EMPLOYEE IN THE FACE CAUSING SEVERE FACIAL INJURIES.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19900165 | 1990-09-25 | 2084 | CAPROCK PIPELINE CO | OKLAHOMA | BECKHAM | OK |  | HW 1778-000 | 230+53 | 930 | 1990-08-03 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 1 | 8500 | 7066.7981 | 15395.1893 | Null | 0 | 55 | 33968 | 19900803 | 0 | 0 | NO DATA | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: N/A; MLKD: OTHER; MLKDO: N/A; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 0; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: STEVE BUSTOS, COMPLIANCE COORDINATOR; PHONE: 8063736042; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: CONSTRUCTION; CAULO: CONDUIT; CTEST: Null; MED: NO DATA; TMPS: 0; LKPS: 0 | A VENT ON A POSITIONER VALVE WAS CLOGGED. NATURAL GAS SEEPAGE THROUGH THE CONDUIT, ENTERED THE INSTRUMENTATION BUILDING. THE GAS IGNITED AND A FLASH FIRE ENSUED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900171 | 1990-09-27 | 18516 | SOUTHERN NATURAL GAS CO | Y |  | LA |  | 4.942 | 260+91 | 830 | 1990-08-31 |  | YES | MAIN PASS | 292 | LA | YES | NO | LEAK | 0 | 0 | 0 | 200000 | 166277.6025 | 362239.7476 | Null | 0 | 0 | 37802 | 19900831 | 1025 | 1200 | BY TEST | 2175 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | VALVE |  | OTHER | RUBBER O-RING GASKET | OTHER | N/A | 1970 | 12 | 0 |  | 0 |  | CHECK FRANKFLO | FRANK WEATLEY | 1969 | UNDER WATER |  | CYRUS W. HARPER II, SENIOR ENGINEER | 2053257326 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | 12" ANSI 900# CHECK VALVE HORIZ SWING BOLTED | YES | 19690628 | WATER |  | 2 | 2175 | THE BOLTED BONNET COVER UTLITZES A RUBBER O-RING TYPE GASKET SEAL. APPARENTLY THE RUBBER GASKET HAS CRACKED OR DETERIORATED IN SEVERAL PLACES.PART 3 - DIVERS WERE INSPECTING A 12" RUTURE TAP AND DISCOVERED SLOW RELEASE OFBUBBLES FROM EXISTING CRACKS IN CONCRETE COATING. THE COATING WAS REMOVED AND IT WAS DETERMINED THAT THE LEAK WAS FROM TH BONNET ON THE CHECK VALVE. THE CHECK VALVE IS IN 234' OF WATER.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900172 | 1990-09-27 | 15350 | PEOPLES NATURAL GAS CO | BRIDGEVILLE | ALLEGHENY | PA |  | 50 | 33 +50 | 800 | 1990-08-30 | 3 | NO |  |  |  | Null | Null | RUPTURE | 0 | 0 | 0 | 50000 | 41569.4006 | 90559.9369 | Null | 2 | 30 | 37573 | 19900830 | 244 | 389 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1963; NMDIA: 20; THK: 0.31; SPEC: X42; SMYS: 42000; SEAM: ERW; VALVE: N/A; MANU: YOUNGSTOWN SHEET & TUBE COMPANY; MANYR: 1959; LOCLK: UNDER GROUND; PNAME: J.C. DAILEY, SR. ASSOC. ATTY; PHONE: 4124975668; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19900515; MARK: YES; MRKTP: FLAGS; STAT: YES; CTEST: Null | CONTRACTOR HIT TP-7575 WITH BULLDOZER. LINE HAD BEEN LOCATED AND MARKED BY THE PEOPLES NATURAL GAS COMPANY.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900173 | 1990-09-07 | 18484 | SOUTHERN CALIFORNIA GAS CO | SEPULVEDA | LOS ANGELES | CA | 90049 | 110.08 | 5812 + 22.4 | 1345 | 1990-08-04 | 3 | NO |  |  | CA | Null | NO | OTHER | 0 | 0 | 0 | 68000 | 56534.3849 | 123161.5142 | Null | 4 | 45 | 37272 | 19900804 | 180 | 228 | BY TEST | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: A.O. SMITH BEND; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1930; NMDIA: 26; THK: 0.28; SPEC: GRADE B; SMYS: 35000; SEAM: N/A; VALVE: N/A; MANU: N/A; MANYR: 1930; LOCLK: UNDER PAVEMENT; PNAME: R.L. RUDZIK, MANAGER OF TRANSMISSION & UNDERGROUND STOR STAF; PHONE: 2136892345; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19900730; MARK: YES; MRKTP: PAINTED ON STREET SURFACE; STAT: YES; CTEST: Null | USA TICKET INDICATED WORK TO BE DONE ON 8/3/90. SURVEILLANCE PERSON WENT TOJOB SITE, MARKED PIPELINE IN INTERSECTION, NO ONE WAS AT JOB SITE.ADDITIONAL - ON AUGUST 4, 1990, AT APPROXIMATELY 1:55PM THE LOS ANGELES FIRE DEPT. NOTIFIED OUR COMPANY OF BLOWING GAS AT SEPULVEDA AND CHURCH LANE/OVADA PLACE. THE DAMAGE TO THE LINE WAS CAUSED BY A STREET CONSTRUCTION MACHINE OPERATED BY THE CITY OF LOS ANGELES, DEPT. OF PUBLIC WORKS, BUREAU OF STREET MAINTENANCE. REPAIRS WERE MADE BY INSTALLING TWO 26" WELD CAPS. FOUR CUSTOMERS WERE AFFECTED BUT NO EVACUATIONS WERE NECESSARY. THERE WERE NO FIRES OR INJURIES ASSOCIATED WITH THIS INCIDENT. ESTIMATED COSTS ASSOCIATED WITH THIS INCIDENT WERE $68,000, WHICH INCLUDES GAS LOSSES ESTIMATED TO BE 4,781 MCF.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900178 | 1990-10-15 | 22617 | WILLIAMS NATURAL GAS CO | OVERLAND PARK | JOHNSON | KS | 66202 | REGULATOR STATION 9448 | 150 + 12 | 1720 | 1990-09-08 | 3 | NO |  |  | KS | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 0 |  | 19900909 | 125 | 160 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | VALVE |  | OTHER | UNKNOWN | REGULATOR/METERING SYSTEM |  | 0 | 0 | 0 |  | 0 |  | #1589 ANS 300 | MERCO -ROCKWELL | 0 | ABOVE GROUND |  | WARREN A. ETHERIDGE, COORDINATOR COMPLIANCE | 9185884427 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | 10" MERCO PLUG VALVE | NO |  | NO DATA |  | 0 | 0 | VALVE SEPARATION - MAIN BODY SEPARATED FROM FLANGE ALLOWING GAS ESCAPE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900180 | 1990-10-05 | 19570 | TRANSCO GAS PIPELINE CORP | CROWLEY | ACADIA | LA |  | 30.628 | 1617 + 18 | 130 | 1989-12-16 | 1 | NO |  |  |  | Null | NO | RUPTURE | 8.5 | 0 | 0 | 140000 | 120657.2923 | 262854.8071 | Null | 3 | 15 | 22489 | 19891216 | 840 | 910 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1950; NMDIA: 18; THK: 0.25; SPEC: API 5 LX; SMYS: 52000; SEAM: FLASH WELD; MANU: A.O. SMITH; MANYR: 1950; LOCLK: UNDER GROUND; PNAME: B. R. LANDES, SR. COMPLIANCE ANALYST; PHONE: 7134392001; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | ON DECEMBER 16, 1989 AT 1:30 A.M. TRANSCO FIELD PERSONNEL NOTICED A LOSS OF PRESSURE IN LINE A OF THE CENTRAL LOUISIANA LATERAL WHICH HAD BEEN OPERATING AT A PRESSURE OF 840 PSI. AS TRANSCO BEGAN SHUTTING IN THE AFFECTED PIPELINE SECTION, AT 1:40 A.M., HOUSTON DISPATCH RECEIVED A TELEPHONE CALL FROM THE ACADIA PARISH SHERIFF'S DEPARTMENT RELAYING A FARMER'S REPORT THAT HE HAD HEARDA LOUD NOISE IN A FIELD CLOSE TO HIS HOUSE. THE LOCATION OF THE LEAK WAS THEN NARROWED DOWN TO A SECTION OF LINE A BETWEEN THE VALVE SITES AT MILE POSTS23.61 AND 36.94. THE AFFECTED SECTION OF PIPELINE WAS ISOLATED BY MANUALLY CLOSING THESE VALVES. THREE HOURS AND FIFTEEN MINUTES AFTER THE LOSS OF PRESSURE WAS DETECTED THE AREA WAS MADE SAFE. THERE WAS NO FIRE AND DAMAGE WAS LIMITED TO A SECTION OF TRANSCO PIPELINE APPROXIMATELY 165 FEET LONG LOCATED IN A FARMERS FIELD. THE FIELD WAS NOT CULTIVATED AT THE TIME OF THE INCIDENT.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900183 | 1990-10-05 | 18484 | SOUTHERN CALIFORNIA GAS CO | EL MIRAGE | SAN BERNARDINO | CA | 92301 | 189.5 |  | 1325 | 1990-08-23 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 21200 | 17625.4259 | 38397.4132 | Null | 4 | 10 |  |  | 600 | 1258 | BY TEST | 1573 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: 2" NIPPLE; MLKD: STEEL; PRTSY: OTHER; PRTSO: BYPASS LINE; PRTYR: 1990; NMDIA: 2; THK: 0.22; SPEC: GRADE B; SMYS: 35000; SEAM: SEAMLESS; MANYR: 1989; LOCLK: UNDER GROUND; PNAME: R. L. RUDZIK, MANAGER OF TRANSMISSION; PHONE: 2136892345; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900185 | 1990-10-19 | 22617 | WILLIAMS NATURAL GAS CO | OVERLAND PARK | JOHNSON | KS | 66202 | GLAVIN METERING STATION | 0 + 05 | 1415 | 1990-09-20 | 3 | NO |  |  | KS | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 0 | 40171 | 19900920 | 203 | 260 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: UNKNOWN; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1946; NMDIA: 16; THK: 0.25; SMYS: 24000; SEAM: UNKNOWN; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: WARREN A. ETHERIDGE, COORDINATOR; PHONE: 9185884427; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: Null; MARK: YES; MRKTP: HEADER PIPING; STAT: Null; CTEST: Null | ACCIDENTLY STRUCK 1" TAP WHILE PERFORMING MAINTENANCE ACTIVITY
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19900188 | 1990-10-22 | 7605 | HOUSTON PIPELINE CO | KOUNTZE | HARDIN | TX | 77625 | INTERSECTION 16"&12"P.L. | 0 + 00 | 120 | 1990-10-03 | 1 | NO |  |  | TX | Null | NO | OTHER | 0 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 40 | 42086 | 19901003 | 0 | 0 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: UNKNOWN; MLKD: OTHER; MLKDO: UNKNOWN; PRTSY: PIPELINE; PRTYR: 1974; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: OTHER; LOCLO: UNKNOWN; PNAME: TILFORD N. VIK, ENGINEERING SPECIALIST; PHONE: 7138537329; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | LIQUIDS WERE BEING REMOVED FROM A PIPELINE (16", ACCT. 1136) BY PIGGING. REMOVED LIQUIDS AND VENTING GAS WERE BEING DISCHARGED INTO A 500 BBL. TANK OPENTO THE ATMOSPHERE. IT IS SURMISED THAT HEAVY HYDROCARBON VAPORS VENTING FROM THE TANK, COLLECTED NEAR GRADE LEVEL IN THE AREA AND WERE IGNITED BY A SOURCE WHICH HAS NOT YET BEEN CONFIRMED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900189 | 1990-10-23 | 14211 | ONG TRANSMISSION CO | ARDMORE | CARTER | OK | 73401 | I-35 #33 |  | 1140 | 1990-09-21 | 2 | NO |  |  | OK | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 50 | 40355 | 19900921 | 455 | 800 | BY TEST | 850 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | GIRTH | STEEL |  | PIPELINE |  | 1966 | 12 | 0.25 | API 5LX X-52 | 2040 | ERW |  | UNDETERMINED | 0 | UNDER GROUND |  | JAMES M. WOOD | 9185887600 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION | GIRTH WELD | YES | 19750930 | GAS |  | 3 | 850
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900190 | 1990-10-23 | 405 | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | HIGH ISLAND | SOUTH ADDITION | TX |  | X=3442611 Y=125147 |  | 0 | 1990-09-23 |  | YES | HIGH ISLAND | 533 |  | YES | NO | LEAK | 0 | 0 | 0 | 202500 | 168356.0726 | 366767.7445 | Null | 0 | 0 | 40645 | 19900924 | 1050 | 1440 | BY TEST | 2160 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | OTHER | UNKNOWN | STEEL |  | PIPELINE |  | 1981 | 16 | 0.44 | API 5X | 42000 |  |  |  | 0 | UNDER WATER |  | BARBARA J. HANNA, COMP. ANALYST | 3134965672 | INTERNALLY | OTHER | PINHOLE LEAK | OTHER | UNKNOWN | COATED | YES | 1981 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900191 | 1990-10-19 | 2714 | CNG TRANSMISSION CORP | SABINSVILLE | TIOGA | PA | 16943 |  |  | 415 | 1990-09-19 | 1 | NO |  |  | PA | Null | NO | OTHER | 0 | 0 | 0 | 143000 | 118888.4858 | 259001.4196 | Null | 0 | 15 | 40056 | 19900920 | 1880 | 2500 | BY TEST | 1630 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: 1" REGULATOR; MLKD: OTHER; MLKDO: UNKNOWN; PRTSY: COMPRESSOR STATION; PRTYR: 1951; NMDIA: 1; THK: 0; SMYS: 0; VALVE: 1"B.J.630-103; MANU: FISHER; MANYR: 1951; LOCLK: ABOVE GROUND; PNAME: JACK L. ADAMS, ADMINISTRATOR CODES AND STANDARDS; PHONE: 3046238410; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | A 1" REGULATOR ON THE PILOT LINE TO THE 6" STATION BLOWOFFS FAILED CAUSING THE PILOT LINE TO DRAIN AND OPENING THREE BLOWOFF VALVES AT SABINSVILLE COMPRESSOR STATION
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900192 | 1990-10-16 | 4280 | EL PASO NATURAL GAS CO | HURLEY | GRANT | NM | 88043 | MP4+3538' |  | 1830 | 1990-09-20 | 1 | NO |  |  | NM | Null | NO | RUPTURE | 1.5 | 0 | 0 | 50000 | 41569.4006 | 90559.9369 | Null | 4 | 0 | 40271 | 19900921 | 689 | 850 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1936; NMDIA: 6.63; THK: 0.18; SMYS: 35000; SEAM: SEAMLESS; MANU: NATIONAL TUBE; MANYR: 1936; LOCLK: UNDER GROUND; PNAME: RICHARD FAILA, SENIOR ENGINEER; PHONE: 9155412062; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: MARKER ON BOTH SIDES; STAT: NO; CTEST: Null | EPNG'S 6 5/8" LINE NO. 2010 WAS HIT BY A GRADER OWNED BY PHELPS DODGE, CAUSING AN 18 INCH TEAR.NEW MEXICO ONE-CALL SYSTEM IS PRESENTLY BEING IMPLEMENTED
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19900193 | 1990-10-30 | 4280 | EL PASO NATURAL GAS CO |  | SAN JUAN | NM |  | MP 5 + 3465' |  | 1243 | 1990-10-02 | 1 | NO |  |  |  | Null | NO | RUPTURE | 80 | 0 | 1 | 209210 | 173934.6861 | 378920.888 | Null | 1 | 12 | 42044 | 19901002 | 787 | 845 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1950; NMDIA: 24; THK: 0.27; SPEC: API 5LX; SMYS: 52000; MANU: KAISER; MANYR: 1950; LOCLK: UNDER GROUND; PNAME: RICHARD FAVILA, SENIOR ENGINEER; PHONE: 9155412062; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PIPELINE MARKERS; STAT: YES; CTEST: Null | A MAINTAINER BEING OPERATED BY BROKEN HILLS PROPRIETARY COMPANY WAS GRADING ADITCH PARALLELING OUR 24-INCH PIPELINE WHEN IT HIT AND RUPTURED THE PIPELINE. THERE WAS NO FIRE OR EXPLOSION BUT THE FORCE
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900194 | 1990-10-30 | 4280 | EL PASO NATURAL GAS CO |  | BLANCO | NM |  |  |  | 1459 | 1990-09-30 |  | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 0 | 41728 | 19900930 | 0 | 0 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: UNKNOWN; MLKD: OTHER; MLKDO: UNKNOWN; PRTSY: OTHER; PRTSO: UNKNOWN; PRTYR: 0; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: RICHARD FAVILA, SENIOR ENGINEER; PHONE: 9155412062; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | A FIRE INVOLVING TWO MERIDIAN OIL COMPANY TRUCKS WHICH WERE UNLOADING LIQUIDDRIP, OCCURRED AT THE BLANCO STORAGE TANKS LOCATED BETWEEN THE BLANCO AND CONOCO PLANTS. THE FIRE STARTED WHEN VAPORS FROM THE DOME HATCH OF THE TRUCK MIGRATED TO THE AIR INTAKE OF THE ENGINE ON THE OTHER TRUCK, CAUSING THE ENGINE TO START DIESELING (RUN AWAY) AND IT BACKFIRED. THIS BACKFIRE STARTED A FIRE WHICH DESTROYED TWO TRACTORS, A TWO HUNDRED BARREL TANK TRAILER, AN EQUIPMENT SHACK, AND INSTRUMENTATION ON A DRIP SYSTEM.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900198 | 1990-10-30 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA | STINNETT | MOORE | TX | 79083 | CP-170 |  | 930 | 1990-09-25 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 | 41090 | 19900925 | 0 | 800 | BY TEST | 1200 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: ABSORBER TOWER; MLKD: STEEL; PRTSY: OTHER; PRTSO: GAS TREATING UNIT; PRTYR: 1963; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: F. ROY FLEET, SENIOR ENGINEER; PHONE: 7086913786; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | WHILE PERFORMING MAINTENANCE INSIDE AN ABSORBER TOWER, 4 EMPLOYEES WERE BURNED BY A FLASH FIRE. TWO EMPLOYEES WERE HOSPITALIZED, AND 2 WERE TREATED AND RELEASED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900199 | 1990-10-30 | 2564 | COLORADO INTERSTATE GAS CO | AURORA | ARAPAHOE | CO | 80011 |  |  | 700 | 1990-10-02 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 | 42022 | 19901002 | 0 | 0 | NO DATA | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | OTHER | UNKNOWN | OTHER | UNKNOWN | REGULATOR/METERING SYSTEM |  | 1978 | 0 | 0 |  | 0 |  |  |  | 0 | OTHER | UNKNOWN | RICHARD H. FLINT II, SUPERVISOR | 7195204350 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | PROBE ON THERMTITRATOR | NO |  | NO DATA | 0 | 0 | 0 | FACTORS CONTRIBUTING TO THIS INCIDENT INCLUDE THE EXTREMELY LOW GAS FLOWS ANDA LOSS OF SENSITIVITY IN THE CONTROL SYSTEM, RESULTING IN INACCURATE READINGSBEING SUPPLIED TO PERSONNEL CONTROLLING THE GAS/AIR BLENDING SYSTEM. THE VOLUME DEMAND THROUGH THE GAS/AIR MIXER WAS REDUCED TO A LEVEL BELOW WHICH CONTROLS FOR THE MIXING EQUIPMENT FUNCTION AUTOMATICALLY, WHICH THEN REQUIRED SWITCHING THE CONTROLS TO A MANUAL BLENDING OPERATION. THE OPERATOR CONTROLS THE BLENDING BY THE READINGS ON TWO THERM-TITRATORS. IT IS PROBABLE THAT THE THERM-TITRATOR WAS NOT READING A REPRESENTATIVE SAMPLE OF THE GAS DUE TO A BROKEN THERM-TITRATOR PROBE. THE INSERTION PROBE ON THE THERMTITRATOR WAS BROKENOFF. THIS RESULTED IN THE MEASUREMENT OF A NON_REPRESENTATIVE SAMPLE OF GAS.TNE CAUSE OF THE BROKEN PROBE IS UNKNOWN
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19900204 | 1990-11-07 | 2436 | CLAJON GAS CO |  | BURLESON | TX |  |  | 91+50 | 1730 | 1990-09-13 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 1 |  |  | 0 | 1200 | BY TEST | 1900 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1979; NMDIA: 12; THK: 0.19; SPEC: X-60; SMYS: 0; SEAM: WELDED SEAM; MANYR: 1979; LOCLK: UNDER GROUND; PNAME: WILLIAM E. WEISER, R.P.L.S.; PHONE: 4095425702; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | D THE BELLHOLE. WHEN WELDERS STARTED WELDING, THE VAPORS IGNITED IN FLASH FI
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900210 | 1990-11-19 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA |  | UNKNOWN | LA |  |  |  | 1815 | 1990-10-16 |  | YES | WEST CAMERON | 212 |  | YES | NO | LEAK | 0 | 0 | 0 | 50000 | 41569.4006 | 90559.9369 | Null | 15 | 2 | 44006 | 19901017 | 1030 | 1200 | BY TEST | 1800 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1984 | 12 | 0.38 | 5LX52 | 52000 | SEAMLESS | N/A | ARMCO | 1984 | UNDER WATER |  | R. ROY FLEET, SENIOR ENGINEER | 7086913786 | INTERNALLY | LOCALIZED PITTING |  | OTHER | UNDER INVESTIGATION | COATED | YES | 1984 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | AT 6:15 PM ON OCTOBER 16, 1990, BUBBLING WATER WAS OBSERVED ABOUT 0.5 MILES FORM THE ARCO 212C PLATFORM. THE LEAK WAS CONFIRMED AT 9:17 AM ON OCTOBER 17AND REPAIRED WITH A LEAK CLAMP ON OCTOBER 20. NATURAL GAS PIPELINE COMPANY OF AMERICA OPERATES AND SHARES OWNERSHIP OF THE PIPLEINE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900212 | 1990-11-20 | 18484 | SOUTHERN CALIFORNIA GAS CO |  | KERN | CA | 93249 |  |  | 830 | 1990-10-22 | 1 | NO |  |  | CA | Null | NO | OTHER | 0 | 0 | 0 | 55000 | 45726.3407 | 99615.9306 | Null | 13 | 0 | 45792 | 19901031 | 373 | 400 | BY TEST | 750 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1961; NMDIA: 6; THK: 0.22; SPEC: GRADE B; SMYS: 2313; SEAM: SEAMLESS; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: UNDER GROUND; PNAME: R.L. RUDZIK, MGR OF TRANSMISSION & UNDERGROUND STORAGE STAFF; PHONE: 2136892345; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19901002; MARK: YES; MRKTP: STAKED; STAT: YES; CTEST: Null | THE PIPELINE WAS HIT BY A RIPPER THAT WAS SUBSOILING TO REPLANT A FIELD.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900214 | 1990-11-19 | 19235 | TEXAS EASTERN GAS PIPELINE CO | ELM GROVE | BOSSIER | LA | 71051 | 13.56 | 714 + 38 | 1400 | 1990-10-17 | 1 | NO |  |  |  | NO | NO | RUPTURE | 30 | 0 | 0 | 90000 | 74824.9211 | 163007.8864 | Null | 3 | 13 | 44095 | 19901018 | 840 | 935 | BY TEST | 1807 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1962; NMDIA: 14; THK: 0.25; SPEC: API 5L-46; SMYS: 46000; SEAM: SEAMLESS; VALVE: N/A; MANU: NATIONAL TUBE; MANYR: 1961; LOCLK: ABOVE GROUND; PNAME: LARRY SHED - SUPERVISING ENGINEER PLANT; PHONE: 7136276085; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: ORANGE PAINT, & RIBBON; STAT: NO; CTEST: Null | TRACTOR WAS DISKING THE FIELD WHEN PRODUCERS PIPING WAS HIT BY A DISK. THE 2" WELDOLET WAS TORN FROM THE PIPELINE AND APPROXIMATELY 30 FEET OF PIPE SPLIT OPEN.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19900216 | 1990-11-16 | 20230 | UNITED GAS PIPELINE CO | RINGGOLD | BIENVILLE | LA | 71068 |  |  | 1345 | 1990-10-16 | 1 | NO |  |  |  | NO | NO | OTHER | 0 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 2 | 43825 | 19901016 | 0 | 0 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: UNKNOWN; MLKD: OTHER; MLKDO: NO MATERIAL FAILURE; PRTSY: OTHER; PRTSO: PIT; PRTYR: 1977; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: OTHER; LOCLO: IN PIT; PNAME: WAYNE ST. GERMAIN - SR. PIPELINE SAFETY ANALY; PHONE: 7132295772; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | AN EXPLOSIVE ATMOSPHERE DEVELOPED OVER AN OPEN OIL AND WATER PIT AT BISHTINEAU COMPRESSOR SATION. THE EXPLOSIVE ATMOSPHERE IGNITED DUE TO CONSTRUCTION AT THE PIT. THE RESULTING "FLASH" CAUSED 2 MEN TO SUSTAIN BURN INJURIES REQUIRING HOSPITALIZATION.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900218 | 1990-12-03 | 18484 | SOUTHERN CALIFORNIA GAS CO | CORONA | RIVERSIDE | CA |  | 182.88 |  | 410 | 1990-11-07 | 3 | NO |  |  |  | NO | NO | OTHER | 0 | 0 | 0 | 210000 | 174591.4826 | 380351.735 | YES | 0 | 0 |  | 19901107 | 380 | 584 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: NONE; MLKD: STEEL; PRTSY: OTHER; PRTSO: N/A; PRTYR: 1947; NMDIA: 30; THK: 0.34; SPEC: 5LX; SMYS: 52000; SEAM: SUBMERGED; MANU: CONSOLIDATED STEEL; MANYR: 1946; LOCLK: UNDER GROUND; PNAME: R. L. RUDZIK/ MANAGER OF TRANSMISSION; PHONE: 2136893586; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19901107; MARK: YES; MRKTP: IN PLACE & LINE ISOLATED; STAT: YES; CTEST: Null | THE SOCALGAS OPERATES AND MAINTAINS AN UNDERGROUND 30-INCH NATURAL GASTRANSMISSION PIPELINE (LINE 2000) PARALLEL TO THE AT&SF TRACK IN THE GENERALAREA OF THE COLLISION SITE. THE DISTANCE FROM OUR PIPELINE TO THE RAILROADTRACKS VARIES FROM 60 TO 70 FEET, WITH THE CLOSEST DEBRIS FROM THE COLLISIONTO OUR PIPELINE BEING APPROXIMATELY 30 FEET. THE PIPELINE WAS INSPECTED INACCORDANCE WITH PRUDENT OPERATING PROCEDURES AND IT WAS DETERMINED THAT THEINTEGRITY OF THE PIPELINE WAS NOT COMPROMISED AT ANY POINT AS A RESULT OF THEFREIGHT TRAIN INCIDENT. ON NOVEMBER 7, 1990, AT APPROXIMATELY 10:30 P.M., WEWERE INFORMED BY AT&SF THAT HEAVY CRANE EQUIPMENT WOULD BE USED OVER OURPIPELINE FOR REPAIR AND CLEANUP PURPOSES. DUE TO THE UNCERTAINTY OF THEPLACEMENT OF THE EMERGENCY RAILROAD EQUIPMENT, THE LINE WAS TAKEN OUT OFSERVICE AND BLOWN DOWN. THIS BLOWDOWN OPERATION TOOK APPROXIMATELY TWO HOURSTO COMPLETE. IN ORDER TO ALLEVIATE AGENCY CONCERNS REGARDING THE INTEGRITY OFOUR LINE 2000 IN THE AREA OF THIS INCIDENT, THE SECTION IN QUESTION WASPOTHOLED AND HYDROSTATICALLY TESTED TO 90 PERCENT OF SMYS WHICH REVERIFIED THEINTEGRITY OF THE PIPELINE. SUPPLEMENTAL REPORT 10/03/94 INDICATED THAT THEINCIDENT HAS BEEN RECLASSIFIED AS "DAMAGE BY OUTSIDE FORCE." THE INCIDENT WASA RESULT OF A TRAIN COLLISION/DERAILMENT. THE OUTSIDE/THIRD PARTY WAS THEATCHISON, TOPEKA AND SANTA FE RAILROAD (AT&SF).
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900221 | 1990-11-27 | 19160 | TENNESSEE GAS PIPELINE CO | FRANKLIN | ST MARY | LA | 70538 | 507G-1010+4.64 | 245+00 | 255 | 1990-11-01 | 1 | NO |  |  |  | NO | NO | RUPTURE | 0 | 0 | 0 | 500000 | 415694.0063 | 905599.3691 | Null | 3 | 5 | 45968 | 19901101 | 980 | 1071 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1951; NMDIA: 12; THK: 0.38; SPEC: API 5L GRADE B; SMYS: 35000; SEAM: SEAMLESS; VALVE: N/A; MANU: YOUNGSTOWN; MANYR: 1950; LOCLK: UNDER WATER; PNAME: ALBERT T. RICHARDSON, MGR. CODES & STANDARDS; PHONE: 7137574292; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: WATERWAY CROSSING SIGNS; STAT: Null; CTEST: Null | SUSPECT MARIN VESSEL CAUSED DAMAGE AND SUBSEQUENT RUPTURE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900224 | 1990-12-13 | 4280 | EL PASO NATURAL GAS CO |  | LA PAZ | AZ |  | 727 + 2845 (727.539) |  | 345 | 1990-11-10 | 1 | NO | N/A | N/A |  | NO | NO | RUPTURE | 68 | 0 | 0 | 300000 | 249416.4038 | 543359.6215 | YES | 2 | 0 | 47160 | 19901110 | 740 | 809 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1947 | 26 | 0.28 | X52 | 52000 | FLASH WLEDED |  | A.O SMITH | 1947 | UNDER GROUND |  | RICHARD FAVILA, SENIOR ENGINEER | 9155412062 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | COATED | YES | 1947 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | GENERAL PIPE CORROSION IN THE IMMEDIATE AREA CAUSED THE PIPELINE TO RUPTURE AND THE FRICTION OF THE PIPELINE RIPPING IGNITED THE GAS.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900229 | 1990-12-19 | 5304 | FLORIDA GAS TRANSMISSION CO | TIVOLI | REFUGIO | TX | 77990 | M.P. 158.3 | 3310+29 | 1623 | 1990-11-24 | 1 | NO | N/A | N/A |  | NO | NO | RUPTURE | 74 | 0 | 0 | 150000 | 124708.2019 | 271679.8107 | Null | 0 | 0 | 48743 | 19901124 | 905 | 975 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | WELD | LONGITUDINAL | STEEL |  | PIPELINE |  | 1959 | 20 | 0.28 | API 5LX | 52000 | FLASH WELD |  | A.O. SMITH | 1959 | UNDER GROUND |  | ANTHONY ROCK, COMPLIANCE ENGINEER | 7138537300 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1959 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19900233 | 1990-12-26 | 3260 | DELTA NATURAL GAS CO INC | WILMORE | JESSAMINE | KY | 40390 |  |  | 855 | 1990-11-27 | 3 | NO | N/A | N/A |  | NO | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 30 | 49091 | 19901127 | 250 | 665 | BY TEST | 1000 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1985; NMDIA: 6; THK: 0.19; SPEC: API-5L-X42-A53-B; SMYS: 42000; SEAM: ELEC RESISTANCE; MANU: LTV PIPE; MANYR: 1985; LOCLK: UNDER GROUND; PNAME: MIKE ROBINSON - DIVISION MANAGER; PHONE: 6067446171; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PERM LINE MARKERS; STAT: NO; CTEST: Null | AT APPROXIMATELY 8:55 A.M. NOVEMBER 27, 1990, DELTA'S NICHOLASVILLE OFFICE RECEIVED A TELEPHONE CALL REPORTING A LINE BREAK ON THE NICHOLASVILLE BY-PASS NEAR KIMBERLY HEIGHTS SUBDIVISION. BILL GARDNER, DELTA'S NICHOLASVILLE/WILMORE DISTRIBUTION SUPERVISOR, AND JOE PEEL AND LAWRENCE RILEY, BOTH CUSTOMER SERVICE REPRESENTATIVES IN THE NICHOLASVILLE SYSTEM, ARRIVED AT THE SCENE IN APPROXIMATELY TEN MINUTES. THEY FOUND THAT DRIFTWOOD INC., A CONTRACTOR FOR GTE, HAD AUGERED THROUGH THE SIX-INCH STEEL TRANSMISSION LINE FEEDING WILMORE. THE PIPELINE HAD A TWO-INCH OPENING THAT WAS BLOWING GAS. BILL GARDNER SHUT IN THE VALVE AT THE NICHOLASVILLE TOWN BORDER STATION DISRUPTING NATURAL GAS SERVICE TO APPROXIMATELY 900 CUSTOMERS IN THE WILMORE SYSTEM. TWENTY-FOUR CUSTOMER SERVICE REPRESENTATIVES FROM DELTA'S NORTHERN & SOUTHERN DIVISIONS WERE DISPATCHED TO WILMORE IN ORDER TO EXPEDITE RESTORATION OF NATURAL GAS SERVICE TO THE AFFECTED CUSTOMERS. THE CUSTOMER SERVICE REPRESENTATIVES TURNED THE GAS OFF AT EACH METER. DELTA'S NORTHERN CONSTRUCTION CREW REPAIRED THE PIPELINE BY REPLACING A TWO FOOT SECTION OF SIX-INCH STEEL PIPE. REPAIRS WERE COMPLETE BY 2:30 P.M. THE PIPELINE WAS THEN PURGED AND ENERGIZED. NATURAL GAS SERVICE HAD BEEN RESTORED TO APROXIMATELY 800 CUSTOMERS BY 11:00 P.M. THAT EVENING. THE REMAINING 100 CUSTOMERS WERE RELIT THE NEXT DAY BEGINNING AT 7:00 A.M. GTE WAS INSTALLING AN ANCHOR FOR A TELEPHONE POLE WHEN THEY HIT WHATTHEY THOUGHT WAS ROCK. THEY CONTACTED DRIFTWOOD INC. FOR ASSISTANCE. DRIFTWOOD DRILLED THROUGH OUR PIPELINE WITH A CARBIDE TIP AUGER. GTE DID NOT CALLDELTA'S OFFICE FOR LINE LOCATION. DELTA HAD LINE MARKER POSTS ON EACH SIDE OF THE HIGHWAY MARKING THE ROAD CROSSING UNDER THE BY-PASS. THE FIRST LINE MARKER POST WAS LOCATED APPROXIMATELY 100 FEET FROM WHERE GTE WAS WORKING.SEVERAL OF DELTA'S YELLOW FLAGS WERE PRESENT WHERE THE LINE HAD BEEN PREVIOUSLY LOCATED IN KIMBERLY HEIGHTS SUBDIVISION. THERE WERE NO INJURIES OR FATALITIES ATTRIBUTABLE TO THIS INCIDENT.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900234 | 1990-12-28 | 18516 | SOUTHERN NATURAL GAS CO |  |  | LA |  | 21.403 | 1130+10 | 830 | 1990-11-20 |  | YES | MAIN PASS | 142 |  | YES | NO | LEAK | 0 | 0 | 0 | 160000 | 133022.082 | 289791.7981 | Null | 0 | 0 | 51113 | 19901214 | 975 | 1200 | BY TEST | 1802 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | VALVE |  | OTHER | ROBBER O-RING GASKET | PIPELINE |  | 1970 | 12 | 0 |  | 0 |  | CHECK | WHEATLEY | 1969 | UNDER WATER |  | CYRUS W. HARPER II, SR. ENGR. | 5048934951 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL |  | YES | 19691016 | WATER |  | 24 | 1802 | THE BOLTED BONNETT COVER UTILIZES A RUBBER O-RING GASKET SEAL. APPARENTLY THE RUBBER GASKET HAS CRACKED OR DETERIORATED IN SEVERAL PLACES.PART 3 - DIVERS WERE INSPECTING AN UNUSED UNDERWATER 12" TAP AND DISCOVERED A SLOW RELEASE OF BUBBLES FROM EXISTING CRACKS IN CONCRETE COATING. THE CONCRETE COATING WAS REMOVED AND THE BONNETT GASKET ON THE 12" CHECK VALVE WAS FOUND LEAKING. THE CHECK VALVE IS LOCATED IN 195' OF WATER.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19900236 | 1990-12-21 | 21031 | VALERO TRANSMISSION CO | S OF VALERO'S FREER CO ST | WEBB | TX | 78357 |  | 4819+23 TO 4820+09 | 1605 | 1990-11-26 | 1 | NO | N/A | N/A | TX | NO | NO | RUPTURE | 0 | 0 | 0 | 105630 | 87819.5158 | 191316.9227 | Null | 1 | 0 | 48938 | 19901126 | 845 | 1010 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1961; NMDIA: 20; THK: 0.28; SPEC: API 5LX-52; SMYS: 1461; SEAM: N/A; VALVE: N/A; MANU: UNKNOWN; MANYR: 1960; LOCLK: UNDER GROUND; PNAME: JIM MCDONALD, DISTRICT ENGINEER; PHONE: 5126877195; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | REASON FOR FAILURE IS UNKNOWN AT THIS TIME. METALLUGICAL INVESTIGATION IS BEING CONDUCTED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910001 | 1991-01-03 | 19235 | TEXAS EASTERN GAS PIPELINE CO | STATEN ISLAND | RICHMOND | NY |  | M.P. 2.16 | 119+40 | 250 | 1990-11-24 | 1 | NO | N/A | N/A |  | NO | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 | 48693 | 19901124 | 600 | 823 | BY TEST | 2165 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1950; NMDIA: 16; THK: 0.5; SPEC: GRADE B; SMYS: 35000; SEAM: AOSW; MANU: AOS; MANYR: 1950; LOCLK: OTHER; LOCLO: UNKNOWN; PNAME: JOSEPH G. DELLAQUILA - SUPV. ENGR.; PHONE: 7175408335; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: WARNING SIGNS; STAT: NO; CTEST: Null | BARGE OR TUG BOAT APPARENTLY HIT THE PIPELINE UNDER THE AUTHUR KILL RIVER, CAUSING A PUNCTURE THAT ALLOWED GAS TO BLOW TO ATMOSPHERE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19910002 | 1991-01-04 | 4280 | EL PASO NATURAL GAS CO |  | TORRANCE | NM |  | 232+1328' (232.252) |  | 15 | 1990-12-07 | 1 | NO | N/A | N/A |  | NO | NO | RUPTURE | 85 | 0 | 0 | 370299 | 307862.1497 | 670685.0815 | Null | 0 | 45 | 50251 | 19901207 | 660 | 836 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1960; NMDIA: 30; THK: 0.34; SMYS: 52000; SEAM: DSAW; MANU: KAISER; MANYR: 1960; LOCLK: UNDER GROUND; PNAME: RICHARD FAVILA, SENIOR ENGINEER; PHONE: 9155412062; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: MATERIAL; CTEST: NO; MED: NO DATA; TMPS: 0; LKPS: 0 | BELEN COMPRESSOR STATION EXPERIENCED A LOW SUCTION PRESSURE ALARM AT 9:10 PMON DECEMBER6, AND AN ESD AT 9:15 PM. lINCLON COMPRESSOR STATION REPORTED LOWREADINGS AND AT 9:30 PM PERSONNEL WERE DISPATCHED TO PATROL THE PIPELINE TO DETERMINE IF THERE HAD BEEN A PIPELINE FAILURE. THE RUPTURE WAS CONFIRMED AT 12:15 AM WHEN IT WAS DISCOVERED THAT APPROXIMATELY 85 FEET OF PIPELINE HAD BLOWN OUT. THE PIPELINE WAS ISOLATED AT ABOUT 12:45 AM. THERE WAS NO FIRE. NO LAW ENFORCEMENT OR FIRE DEPARTMENTS WERE INVOLVED. THE PIPELINE WAS BLOWN DOWNFROM VALVE 21 TO VALVE 23 (APPRO. 20 MILES).PART C - THE FRACTURE WAS NOT ASSOCIATED WITH A LONGITUDINAL SEAM OR A GIRTHWELD. THE FRACTURE FACE EXHIBITED BRITTLE FEATURES (FLAT FRACTURE WITH CHEVRON MARKINGS) THAT POINTED BACK TO AN AREA APPROXIMATELY 5 INCHES LONG, APPROXIMATELY 9 FEET FROM THE UP STREAM FRACTURED END. THIS AREA MAY HAVE BEEN THE INITIATION SITE, SINCE THE PIECE WAS CLEARLY BENT WITH A RUPTURED AND TORN HOLE ON THE OUTSIDE OF THE BEND. THE PIECE CONTAINED A WRINKLE BEND ON ITS UPSTREAM SIDE THAT EITHER WAS IN THE ORIGINAL PIPELINE OR WAS CAUSED BY TH RUPTURE. THE WRINKLE EXHIBITED A BRITTLE FRACTURE SURFACE WITH MANY CRACKS IN AND AROUND THE BEND. ULTRASONIC, MAGNETIC PARTICLE AND HARDNESS TESTS WERE PERFORMED ON THE POSSIBLE INITIATION SITE. THESE TESTS CONFIRMED A WALL THICKNESSOF .345 TO .350 INCHES. THERE WAS NO EVIDENCE OF INTERNAL OR EXTERNAL CORROSION. HARDNESS TESTING VERIFIED THAT THE AREA AROUND THE POSSIBLE RUPTURE INITIATION SITE WAS 38 HRC INDICATING THAT HYDROGEN STRESS CRACKING OF THE "HARDSPOT" WAS THE CAUSE OF THE FAILURE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19910003 | 1991-01-07 | 2714 | CNG TRANSMISSION CORP | TWILIGHT | BOONE | WV | 25204 |  | 1221+37 | 1220 | 1990-12-04 | 2 | NO | N/A | N/A |  | NO | NO | RUPTURE | 4 | 0 | 0 | 150000 | 124708.2019 | 271679.8107 | Null | 1 | 15 | 49913 | 19901204 | 525 | 560 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1946 | 12.75 | 0.31 | 5L-B | 35000 | SEAMLESS |  | N/A | 0 | UNDER WATER |  | JACK L. ADAMS, ADMINISTRATOR CODES & STD | 3046238410 | EXTERNALLY | LOCALIZED PITTING |  | OTHER | ATMOSPHERIC | BARE | YES | 1974 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | RUPTURE OCCURRED IN STREAM CROSSING. ESCAPING GAS IGNITED RESULTING IIN DAMAGE TO DWELLINGS NEAR PIPELINE.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19910004 | 1991-01-08 | 19160 | TENNESSEE GAS PIPELINE CO | BATESVILLE | PANOLA | MS | 38606 | COMPRESSOR STATION 63 |  | 850 | 1990-12-16 | 1 | NO | N/A | N/A |  | NO | NO | OTHER | 0 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 5 | 51355 | 19901217 | 741 | 750 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: COMPRESSOR PACKING; MLKD: OTHER; MLKDO: COMPRESSOR PACKING; PRTSY: COMPRESSOR STATION; PRTYR: 1948; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: ALBERT T. RICHARDSON, MANAGER, CODES & STANDARDS; PHONE: 7137574292; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | COMPRESSOR OPERATOR SUFFERED BURNS WHEN GAS LEAKING FROM COMPRESSOR PACKINGIGNITED FROM UNKNOWN SOURCE.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19910005 | 1991-01-08 | 18516 | SOUTHERN NATURAL GAS CO | WHITE CASTLE | IBERVILLE | LA | 70788 |  |  | 1100 | 1990-12-10 | 1 | NO | N/A | N/A |  | NO | NO | OTHER | 0 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 5 | 50607 | 19901210 | 625 | 1200 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | OTHER | SCRUBBER | STEEL |  | COMPRESSOR STATION |  | 1967 | 0 | 0 | MODEL D-66 | 0 |  |  | KING TOOL | 0 | ABOVE GROUND |  | KURT REGULSKI, SENIOR ENGINEER | 5048934951 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | GAS SCRUBBER - SHAFT & BEARING | Null |  | NO DATA |  | 0 | 0 | EMPLOYEES WERE REMOVING MOTOR AND GEARBOX ASSEMBLY FROM COMPRESSOR STATION #3 SCRUBBER. AS THE GEARBOX ASSEMBLY WAS REMOVED, THE SHAFT WAS BLOWN OUT OF THE SCRUBBER INJURING ONE EMPLOYEE. THE APPARENT CAUSE WAS AN INTERNAL BEARING FAILURE WHICH RESULTED IN SHAFT WEAR WHICH BROKE DUE TO ROTATION AGAINST THE BEARING SUPPORTS. THE INJURED EMPLOYEE IS EXPECTED TO RECOVER FULLY.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910009 | 1991-01-09 | 19730 | TRUNKLINE GAS CO | UNKNOWN | UNKNOWN | LA |  | LINE 319A-100 | 1766 + 80 EST. | 800 | 1990-12-06 |  | YES | SHIP SHOAL | 253 |  | YES | NO | RUPTURE | 0.5 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 15 | 50147 | 19901206 | 1065 | 1200 | BY TEST | 1559 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1969; NMDIA: 20; THK: 0.47; SPEC: API-5LX; SMYS: 52000; SEAM: SEAMLESS; VALVE: N/A; MANU: U.S. STEEL; MANYR: 1968; LOCLK: UNDER WATER; PNAME: M.E. ANDERSON TECHNICAL OPERATION SUPT.; PHONE: 7136276004; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: YES; CTEST: Null | UNION RIG KEYS #303 DRUG LEGS ACROSS PIPELINE WHILE PREPARING TO SET UP ON UNOCAL SS 253 PLATFORM.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910010 | 1991-01-10 | 19570 | TRANSCO GAS PIPELINE CORP | SEMINARY | COVINGTON | MS |  | 1.59 |  | 1054 | 1990-12-10 | 1 | NO |  |  |  | NO | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 26 | 50558 | 19901210 | 600 | 3500 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | OTHER | COMPRESSOR | STEEL |  | COMPRESSOR STATION |  | 1972 | 0 | 0 |  | 0 |  |  |  | 0 | OTHER | COMPRESSOR BLDG. | B.R. LANDES, STAFF COMPLIANCE ANALYST | 7134392001 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | COMPRESSOR ROD PACKING | NO |  | OTHER | VISUAL INSPECTION DAILY | 0 | 0 | MECHANICAL WEAR IN BRONZE COMPRESSOR ROD PACKING CAUSED GAS TO ESCAPE AND PASS BY IGNITION TRANSFORMERS.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910011 | 1991-01-10 | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | NEW YORK | NEW YORK | NY | 10021 |  |  | 1300 | 1990-11-17 | 4 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 | 48051 | 19901117 | 348 | 350 | BY TEST | 350 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: OTHER; PRTFO: NONE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1958; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: OTHER; LOCLO: UNKNOWN; PNAME: RICHARD C. GAULIN; PHONE: 2124602838; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | PRESSURE REGULATORS AT A TRANSMISSION METER STATION LOST CONTROL, ALLOWING DELIVERY PRESSURE TO INCREASE. FURTHER INVESTIGATION DISCLOSED THAT OVERRIDE SYSTEM OPERATED PROPERLY AND MAOP WAS NOT EXCEEDED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910012 | 1991-01-11 | 10030 | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | EDISON | FURNAS | NE | 68936 |  | 243+73. SEC.29-T4N-R22W | 130 | 1990-12-29 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 6000 | 4988.3281 | 10867.1924 | YES | 3 | 0 | 52880 | 19901229 | 300 | 300 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1947; NMDIA: 2.38; THK: 0.15; SPEC: UNKNOWN; SMYS: 0; SEAM: UNKNOWN; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: STEVE HAWES, CONS. & STANDARDS SPECIALIST; PHONE: 4024622141; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: LINEMARKER 300' EAST; STAT: NO; CTEST: Null | OVERHEAD CREEK CROSSING WAS HIT BY VEHICLE WHICH RAN OFF A GRAVEL ROAD.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19910014 | 1991-01-18 | 4280 | EL PASO NATURAL GAS CO | UNKNOWN | SAN JUAN | NM |  |  |  | 1110 | 1990-12-18 |  | NO | N/A | N/A |  | NO | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 0 | 51617 | 19901219 | 0 | 0 | NO DATA | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | GATHERING SYSTEM | OTHER | FUEL LINE | OTHER | REINFORCE RUBBER | OTHER | GLYCOL LINE & DEHYDRATOR | 1976 | 0.5 | 0 |  | 0 |  |  |  | 0 | ABOVE GROUND |  | RICHARD FAVILA, SENIOR ENGINEER | 9155412062 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | 1/2" GLYCOL LINE (FUEL LINE) TO DEHYDRATOR | Null |  | NO DATA |  | 0 | 0 | A 1/2" DIAMETER GLYCOL HOSE (FUEL LINE) TO THE DEHYDRATOR ON THE STANOLIND GAS COM. #1A GAS WELL BROKE AND IGNITED, SETTING FIRE TO THE DEHYDRATOR. THEGAS WELL WAS SHUT-IN AND THE FIRE WAS DYING OUT WHEN THE NAVAJO DAM VOLUNTEER FIRE DEPARTMENT ARRIVED AT THE SCENE. AS A PRECAUTIONARY MEASURE, THEY SPRAYED WATER ON AN ADJACENT HYDROCARBON LIQUID STORAGE TANK TO COOL IT OFF. THIS IS A NON-REPORTABLE INCIDENT, BUT WAS REPORTED AS A COURTESY TO THE DOT DUETO THE RESPONSE OF THE VOLUNTEER FIRE DEPARTMENT.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19910028 | 1991-02-01 | 19270 | TEXAS GAS TRANSMISSION CORP | GREENVILLE | CHICOT | AR |  | MLS 103+1419 (103.27) | T16S, R1E, SECTION 30 | 555 | 1991-01-04 | 1 | NO |  |  | AR | Null | NO | RUPTURE | 0 | 0 | 0 | 235000 | 188651.3859 | 410981.5717 | Null | 1 | 9 | 53566 | 19910109 | 638 | 840 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1950; NMDIA: 20; THK: 0.5; SPEC: AOS SPEC 1109-D; SMYS: 33000; SEAM: SUBMERGED ARC; VALVE: N/A; MANU: PLATE-INLAND STEEL; MANYR: 1950; LOCLK: UNDER WATER; PNAME: JAMES E BEECH - MANAGER PIPELINE SAFETY; PHONE: 5029268686; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | SINCE 1950, TEXAS GAS HAS OPERATED TWO 20" UNDERGROUND, NATURAL GAS PIPELINES CROSSING THE MISSISSIPPI RIVER AT THE LOCATION DESCRIBED ON THE ATTACHED FORM RSPA F7100.2. THESE LINES HAVE THE TEXAS GAS DESIGNATED NUMBERS OF 20" LINES 5 AND 6. ON JANUARY 4, 1991, AT APPROXIMATELY 5:55 AM., CST, AN UNDERWATER LEAK WAS DISCOVERED ON 20" LINE NO. 6. THE LINE WAS SHUT IN WITHIN 70 MINUTES OF DISCOVERY, AND A TELEPHONIC REPORT WAS MADE BEFORE 11:00 AM. BY TEXASGAS'S SENIOR ATTORNEY, NICK HETMAN. THE 20" NO. 5 LINE WHICH IS LOCATED APPROXIMATELY 150' NORTH OF THE FAILED LINE WAS SHUT IN WITHIN 24 HOURS AS A PRECAUTIONARY MEASURE. EXTREME FLOOD CONDITIONS AND SWIFT CURRENTS HAVE PROHIBITED DIVERS FROM INSPECTING THESE LINES; HOWEVER, SURVEY PARTIES (USING FATHOMETERS) HAVE DETERMINED SOME EXPOSURE OF THE NO. 5 LINE. NO APPARENT LEAKS HAVE BEEN DETECTED ON THE NO.5 LINE AT THIS TIME. REPLACEMENT PLANS FOR 20" LINE NOS. 5 AND 6 ARE UNDETERMINED AT THIS TIME.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910030 | 1991-02-04 | 19570 | TRANSCO GAS PIPELINE CORP | ST FRANCISVILLE | WEST FELICIANA | LA |  | 583.17 |  | 1700 | 1991-01-18 | 1 | NO |  |  |  | Null | NO | RUPTURE | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 5 | 53884 | 19910119 | 588 | 780 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: UNKNOWN; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1951; NMDIA: 18; THK: 0.5; SPEC: API 5L; SMYS: 35000; SEAM: SEAMLESS; VALVE: N/A; MANU: NATIONAL TUBE; MANYR: 1951; LOCLK: UNDER WATER; PNAME: B.R. LANDES, STAFF COMPLIANCE ANALYST; PHONE: 7134392001; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | INCIDENT HAS BEEN VERIFIED TO BE THE 18" UNDERWATER PIPELINE CROSSING THE MISSISSIPPI RIVER. THE AFFECTED RIVER CROSSING WAS ISOLATED BY AUTOMATIC VALVEOPERATORS AT THE TIME OF THE INCIDENT. THE RIVER CROSSING IS ISOLATED & AUTOMATIC VALVE OPERATORS DEACTIVIATED. DUE TO THE RESENT LEVEL AND FLOW CONDITIONS OF THE RIVER, AN INVESTIGATION AT THIS TIME IS IMPOSSIBLE. AS SOON AS RIVER CONDITIONS PERMIT, AN INVESTIGATION OF THE CAUSE AND EVALUATION OF DAMAGE WILL BE CONDUCTED AND A SUPPLEMENTAL REPORT WILL BE FILED TO THE DEPARTMENT OF TRANSPORTATION.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19910035 | 1991-02-11 | 405 | ANR PIPELINE CO | EUGENE |  | LA |  |  |  | 900 | 1991-01-06 |  | YES | E.I. | 217 |  | YES | NO | LEAK | 0 | 0 | 0 | 125000 | 100346.4819 | 218607.219 | Null | 0 | 0 | 54208 | 19910109 | 880 | 1250 | BY TEST | 2015 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1990; NMDIA: 6; THK: 0.28; SPEC: GRADE B; SMYS: 35000; SEAM: SEAMLESS; MANU: U.S. STEEL; MANYR: 1989; LOCLK: UNDER WATER; PNAME: BARBARA J. HANNA, COMP. ANALYST; PHONE: 3134965672; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; MRKTP: 0N; STAT: Null; CTEST: Null | 2" X 6" CONNECTION LOCATED IN 120' OF WATER IN GULF OF MEXICO.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19910041 | 1991-02-21 | 3 | ACADIAN GAS PIPELINE SYSTEM | UNKNOWN | ASSUMPTION | LA |  |  |  | 2325 | 1991-01-26 | 1 | NO | N/A | N/A |  | NO | NO | LEAK | 0 | 0 | 0 | 105000 | 84291.0448 | 183630.064 | Null | 2 | 25 | 56932 | 19910128 | 550 | 650 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1940; NMDIA: 7; THK: 0.19; SPEC: API 5LX; SMYS: 52000; SEAM: ERW; VALVE: N/A; MANU: N/A; MANYR: 0; LOCLK: UNDER GROUND; PNAME: JAMES P. SCHWARZ - OPERATIONS MANAGER; PHONE: 5044462791; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: WARNING SIGNS; STAT: YES; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910048 | 1991-02-21 | 4070 | EAST TENNESSEE NATURAL GAS CO | CHURCH HILL | HAWKINS | TN | 37642 | 3307-100+10.50 | 554+55 | 1605 | 1991-01-17 | 2 | NO | N/A | N/A | TN | NO | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 5 | 35 | 55473 | 19910117 | 500 | 706 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1962; NMDIA: 8; THK: 0.19; SPEC: API-5L GR. X-42; SMYS: 42000; SEAM: ERW; VALVE: N/A; MANU: REPUBLIC STEEL; MANYR: 1961; LOCLK: UNDER GROUND; PNAME: J.E. HERBERT, JR., PIPELINE TECHNICIAN; PHONE: 6156933501; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | PIPELINE STRUCK BY OUTSIDE PARTY EXCAVATING SOIL FROM PIPELINE RIGHT-OF-WAY. NO PRIOR NOTIFICATION OF EXCAVATION WAS GIVEN BY OUTSIDE PARTY. PIPELINE IS MARKED WITH PERMANENT PIPELINE MARKERS IN AREA OF EXCAVATION.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19910049 | 1991-02-21 | 20230 | UNITED GAS PIPELINE CO | SECTION 37,T-17-S,R-18-E | TERREBONNE | LA |  | 18.87 | 995+34 | 1410 | 1991-01-18 | 1 | NO | N/A | N/A |  | NO | NO | RUPTURE | 6 | 0 | 0 | 500000 | 401385.9275 | 874428.876 | Null | 2 | 10 | 55609 | 19910118 | 776 | 1029 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1943; NMDIA: 12; THK: 0.38; SPEC: N/A; SMYS: 35000; SEAM: ELECT. WELD; VALVE: N/A; MANU: NATIONAL; MANYR: 0; LOCLK: OTHER; LOCLO: UNKNOWN; PNAME: WAYNE ST. GERMAIN - PIPELINE SAT. ANALYST; PHONE: 7132295772; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: 4'X6' WARNING SIGNS; STAT: NO; CTEST: Null | TUG KAREN ELIZABETH, WITH FOUR EMPTY ARGES IN TOW, SRUCK AND RUPTURED 12" LINE CROSSING INTRACOASTAL CANAL IN TERREBONNE PARISH.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19910052 | 1991-03-03 | 13131 | CONOCO INC | YUKON | CANADIAN | OK |  | H |  | 100 | 1991-02-25 | 1 | NO | N/A | N/A | OK | NO | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 0 |  |  | 60 | 824 | BY TEST | 120 | CORROSION | CORROSION | EXTERNAL | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1979; NMDIA: 6.58; THK: 1.16; SMYS: 35000; SEAM: ERW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: DAVID COURTNEY - MEASUREMENT SUPERVISOR; PHONE: 4057874212; LOC: EXTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: GALVANIC; COAT: COATED; PROT: YES; CPYR: 1979; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910056 | 1991-03-08 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA |  |  | LA |  |  |  | 1200 | 1991-02-10 |  | YES | WEST CAMERON | 537 |  | YES | NO | LEAK | 0 | 0 | 0 | 50000 | 40138.5928 | 87442.8876 | Null | 72 | 0 | 59011 | 19910211 | 970 | 1200 | BY TEST | 2160 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1980 | 8 | 0.25 | 5LX52 | 52000 | ERW |  | REPUBLIC | 1980 | UNDER WATER |  | F. ROY FLEET - SENIOR ENGINEER | 7086913786 | INTERNALLY | LOCALIZED PITTING |  | OTHER | UNKNOWN | COATED | YES | 1980 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910057 | 1991-02-26 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA | KNOXVILLE | MARION | IA | 50138 |  |  | 2247 | 1991-02-05 | 1 | NO |  |  |  | NO | NO | OTHER | 0 | 0 | 0 | 53800 | 43189.1258 | 94088.5471 | Null | 1 | 33 | 59089 | 19910212 | 650 | 712 | BY TEST | 1070 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | VALVE |  | OTHER | INNER VALVE | COMPRESSOR STATION |  | 1974 | 0 | 0 |  | 0 |  | CONTROL VALVE | DAHL/SHAFER | 1974 | OTHER | UNKNOWN | F. ROY FLEET - SENIOR ENGINEER | 7086913786 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | DAHL CONTROL VALVE ON EMER BLOWDOWN SYS. | YES | 19900426 | GAS | 0 | 1 | 500
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19910058 | 1991-03-13 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA | MALVERN | HOT SPRING | AR | 72104 | 595 | 31398 & 65 | 1000 | 1991-01-22 | 1 | NO | N/A | N/A |  | NO | NO | LEAK | 0 | 0 | 0 | 71700 | 57558.742 | 125393.1008 | Null | 4 | 35 |  |  | 650 | 858 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: LONGITUDINAL; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1950; NMDIA: 30; THK: 0.34; SMYS: 52000; SEAM: 5LX52 FLASH; MANU: A.O. SMITH; MANYR: 1950; LOCLK: UNDER WATER; PNAME: F. ROY FLEET SENIOR ENGINEER; PHONE: 7086913786; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: MATERIAL; CTEST: YES; MED: WATER; TMPS: 8; LKPS: 1080
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19910060 | 1991-03-13 | 21035 | VALERO INTERSTATE TRANSMISSION CO | RACHAL | BROOKS | TX |  | BET HELSEY & JONES MLBW | 2753+29 TO 2769+26 | 1905 | 1991-02-15 | 1 | NO | N/A | N/A | TX | NO | NO | RUPTURE | 1597 | 0 | 0 | 143000 | 114796.3753 | 250086.6585 | Null | 1 | 30 | 59815 | 19910215 | 840 | 936 | BY TEST | 1150 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1959; NMDIA: 20; THK: 0.25; SPEC: API5LX-52; SMYS: 1300; SEAM: DSAW; VALVE: N/A; MANU: GERMAN PIPE; MANYR: 0; LOCLK: UNDER GROUND; PNAME: DANNY SANDVIG - AREA FOREMAN; PHONE: 5128423369; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910062 | 1991-03-14 | 18484 | SOUTHERN CALIFORNIA GAS CO | MONTEBELLO | LOS ANGELES | CA | 90640 |  |  | 110 | 1991-02-17 | 3 | NO | N/A | N/A | CA | NO | NO | LEAK | 0 | 0 | 0 | 60000 | 48166.3113 | 104931.4651 | Null | 0 | 15 | 60472 | 19910220 | 250 | 1000 | BY TEST | 5242 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | WELD | GIRTH | STEEL |  | PIPELINE |  | 1956 | 4 | 0.34 | GRADE B | 5242 | SEAMLESS |  | UNKNOWN | 0 | UNDER PAVEMENT |  | R. L. RUDZIK, MGR. OF TRANS AND UNDERGROUND STORAGE STAFF | 2136892345 | INTERNALLY | LOCALIZED PITTING |  | OTHER | UNDETERMINED AT THIS TIME | COATED | YES | 1956 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | ON FEBRUARY 17, 1991, AT APPROXIMTELY 1:10 AM., WE DISCOVERED LEAK WHICH WASLATER DETERMINED TO BE CAUSED BY INTERNAL CORROSION. THE PIPELINE WAS SHUT-IN AT 1:25 AM. REPAIRS WERE MADE BY INSTALLING A 4" LEAK CLAMP. THE PIPELINE HAS NOT BEEN RETURNED TO SERVICE. NO CUSTOMERS WERE AFFECTED BY THE SHUT DOWN, NOR WERE THERE ANY FIRES OR INJURIES ASSOCIATED WITH THIS INCIDENT. ESTIMATED COSTS ASSOCIATED WITH THIS INCIDENT WERE $60,000. DOT NOTIFICATION 02/20/91, REFERENCE REPORT #60472.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19910064 | 1991-03-19 | 19570 | TRANSCO GAS PIPELINE CORP | SALLADASBURG | LYCOMING | PA |  | 157.73 | 6760+99 | 2050 | 1991-02-15 | 1 | NO | N/A | N/A |  | NO | NO | OTHER | 0 | 0 | 0 | 6000000 | 4816631.1301 | 10493146.5123 | Null | 3 | 50 | 59812 | 19910215 | 1025 | 1200 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | OTHER | UNKNOWN | OTHER | UNKNOWN | COMPRESSOR STATION |  | 1990 | 0 | 0 |  | 0 |  |  |  | 0 | OTHER | COMPRESSOR | B.R. LANDES, STAFF COMPLIANCE ANALYST | 7134392001 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | SEE ATTACHED | NO |  | NO DATA | 0 | 0 | 0 | AT APPROXIMATELY 8:50 PM. EST ON FEBRUARY 15, 1991, TRANSCONTINENTAL GAS PIPELINE CORPORATIONS'S 12,600 HP SOLAR MARS TRUBINE EXPERIENCED A SLIGHT EXPLOSION, CAUGHT FIRE, AND BURNED. THE APPARENT CAUSE OF THE INCIDENT IS UNKNOWNAT THIS TIME. A TASK GROUP, CONSISTING OF PERSONNEL FROM TRANSCO, SOLAR, ANDA NEUTRAL OR OUTSIDE PARTY, HAS BEEN ESTABLISHED AND IS INVESTIGATING THE INCIDENT. UPON COMPLETION OF THE INVESTIGATION, A SUPPLEMENTAL REPORT WILL BEFILED WITH THE DEPARTMENT OF TRANSPORTATION. THE CAUSE OF THE INCIDENT WASTHE FAILURE OF A PORTION OF THE INLET GAS SCRUBBER INTERNALS WHICH RESULTED ONAPPROXIMATELY SIX POUNDS OF STEEL BEING CARRIED DOWN THE SUCTION LINE UNTILTHESE PIECES IMPACTED THE CENTRIFUGAL COMPRESSOR. THE TREMENDOUS FORCERESULTING FROM THE IMPACT LED TO TOTAL FAILURE OF THE COMPRESSOR BEARINGS ANDGAS SEALING SYSTEM AND THE RELEASE OF HIGH PRESSURE GAS (APPROXIMATELY 1,000PSIG) INTO THE COMPRESSOR BUILDING WHICH INITIATED THE FIRE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910071 | 1991-04-02 | 11680 | LONE STAR GAS CO | CHAPEL HILL | SMITH | TX |  | 60 | 3222+64 | 1900 | 1991-03-31 | 1 | NO | N/A | N/A |  | NO | NO | RUPTURE | 6 | 0 | 0 | 50000 | 40138.5928 | 87442.8876 | YES | 2 | 30 | 65987 | 19910331 | 800 | 1000 | BY TEST | 1250 | CORROSION | CORROSION | INTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1946; NMDIA: 14; THK: 0.26; SPEC: NON STANDARD; SMYS: 45000; SEAM: BRW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: LOIS ROSS - CLERK; PHONE: 2146701566; LOC: INTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: OTHER; COAT: COATED; PROT: YES; CPYR: 1957; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | LINE BLEW OUT CREEK BOTTOM.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910072 | 1991-04-24 | 13750 | NORTHERN NATURAL GAS CO (ENRON) | CLARION | WRIGHT | IA |  | 58.25 |  | 1205 | 1991-03-23 | 1 | NO | N/A | N/A |  | NO | NO | LEAK | 0 | 0 | 0 | 50000 | 40138.5928 | 87442.8876 | Null | 5 | 0 | 64885 | 19910323 | 500 | 500 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | TEMPERATURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: MECHANICAL JOINT; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1931; NMDIA: 20; THK: 0.28; SPEC: API 5L; SMYS: 30000; SEAM: ERW; VALVE: N/A; MANU: AO SMITH; MANYR: 1931; LOCLK: OTHER; LOCLO: PEAK BOG; PNAME: JOHN W. CASKEY, COMPLIANCE ENGINEER; PHONE: 7138537325; PROT: Null; CAULK: EARTH MOVEMENT: FROST; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | FROST HEAVE AND/OR FLOTATION CAUSED PIPE TO RAISE UP, RESULTING IN A LEAK ATA DRESSER COUPLED JOINT.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19910074 | 1991-04-18 | 13845 | NORTHWEST PIPELINE CORP | LA GRANDE | UNION | OR |  | 977.6 ON 22" MAINLINE | 30923+54 | 1135 | 1991-04-01 | 1 | NO | N/A | N/A |  | NO | NO | OTHER | 0 | 0 | 0 | 87600 | 70322.8145 | 153199.9391 | Null | 0 | 50 | 66101 | 19910401 | 750 | 850 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1956; NMDIA: 22; THK: 0.25; SPEC: API 5LX; SMYS: 52000; SEAM: DSA; VALVE: N/A; MANU: KAISER; MANYR: 1956; LOCLK: UNDER WATER; PNAME: MYRLE ANDERSON - PIPELINE SAFETY SPEC.; PHONE: 8015846908; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PERMANENT MARKERS; STAT: YES; CTEST: Null | A CABLE PLOWING TRACTOR, LAYING TELEPHONE CABLE STRUCK THE PIPELINE; 3" X 4"PUNCTURE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910079 | 1991-04-15 | 22617 | WILLIAMS NATURAL GAS CO | UNKNOWN | BUCHANAN | MO |  | 42 | 7+19 | 1430 | 1991-03-12 | 1 | NO | N/A | N/A | MO | NO | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 15 | 63260 | 19910312 | 424 | 465 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: VALVE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 0; NMDIA: 0; THK: 0; SMYS: 0; VALVE: ANSI 300 STEEL; MANU: CHAPMAN; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: WARREN ETHERIDGE; PHONE: 9185884427; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: FIRE; NOTIF: NO; MARK: YES; MRKTP: AERIAL MARKER #42; STAT: NO; CTEST: Null | FARMER BURNING BRUSH AND GRASS NEAR VALVE CAUSED PACKING TO FAIL.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19910083 | 1991-05-09 | 2616 | COLUMBIA GAS TRANSMISSION CORP | INEZ | MARTIN | KY | 41224 | N/A | 108+63 | 100 | 1991-04-13 | 2 | NO | N/A | N/A |  | NO | NO | LEAK | 0 | 0 | 1 | 18400 | 14771.0021 | 32178.9826 | Null | 2 | 30 | 68226 | 19910416 | 280 | 360 | BY TEST | 500 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | TRANSMISSION SYSTEM | OTHER | 1/2" STANDPIPE BROKE | STEEL |  | OTHER | 1/2" DRIP STANDPIPE | 1965 | 0.5 | 0.13 | UNKNOWN | 0 | UNKNOWN | N/A | UNKNOWN | 0 | ABOVE GROUND | VEH HIT ABOVE STANDPIPE | S.J. CHOBY, SR. CODES & STDS. ENGR. | 3043572349 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | PERMANENT BARRICADE | NO |  |  | Null | [5 empty] | PASSENGER VEHICLE BROKE THROUGH BARRICADE AND HIT DRIP LINE RESULTING IN BELOW GROUND BREAK AT SHUT-OFF VALVE. 1/2" DRIP LINE BROKEN OFF BY PASSENGER VEHICLE ACCIDENT RESULTING IN IGNITION AND DESTRUCTION OF TWO MOTOR VEHICLES AND HOSPITALIZATION OF DRIVER.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19910086 | 1991-05-16 | 22617 | WILLIAMS NATURAL GAS CO | WAKITA | GRANT | OK | 73771 | COMPRESSOR STATION |  | 704 | 1991-04-16 | 1 | NO | N/A | N/A |  | NO | NO | LEAK | 0 | 0 | 0 | 400000 | 321108.742 | 699543.1008 | Null | 1 | 30 | 68204 | 19910416 | 0 | 0 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: COMPRESSOR STATION; MLKD: OTHER; MLKDO: COMPRESSOR STATION; PRTSY: OTHER; PRTSO: UNKNOWN; PRTYR: 1965; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: WARREN ETHERIDGE; COORD., REG. COMP.; PHONE: 9185884427; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | A NATURAL GAS LEAK OCCURRED INSIDE A COMPRESSOR STATION BUILDING. THE GAS WAS IGNITED APPARENTLY BY AN ELECTRICAL SOURCE IN AN ADJACENT PART OF THE STRUCTURE. A COMPRESSOR VALVE CAP IS BELIEVED TO BE THE ORIGIN OF THE LEAK.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910089 | 1991-06-12 | 1552 | BLUE DOLPHIN PIPELINE CO | UNKNOWN | UNKNOWN | TX |  |  |  | 600 | 1991-05-01 |  | YES | GA | 287 |  | YES | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  |  | 500 | 1000 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 0 | 20 | 0.5 | API 5LX | 52000 | SEAMLESS |  |  | 0 | UNDER WATER | 4' BURIAL COVER | VERNON R. LUNING, OPERATIONS MANAGER | 7136213993 | INTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1965 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | WAS IN THE PROCESS OF PRESSURE TESTING THE PIPELINE WITH NATURAL GAS TO ESTABLISH AN NEW MAOP. LEAK OCCURRED AT APPROXIMATELY 500 PSI. PRESSURE WAS BLED TO 300 PSI AT WHICH TIME DIVERS INSTALLED A 1500 PSI WP BOLTED CLAMP. THE PIPELINE AND CLAMP WERE THEN PRESSURE TESTED TO 750 PSI WITH NATURAL GAS. NOOTHER LEAKS OCCURRED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910090 | 1991-06-12 | 10030 | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | UNKNOWN | SCOTTS BLUFF | NE |  |  | 9034+45 | 1645 | 1991-05-14 | 1 | NO | N/A | N/A | NE | Null | NO | OTHER | 0 | 0 | 0 | 25000 | 20069.2964 | 43721.4438 | YES | 1 | 0 | 71985 | 19910514 | 575 | 673 | BY TEST | 1420 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1968; NMDIA: 16; THK: 0.22; SPEC: X-52; SMYS: 1424; SEAM: ERW; VALVE: NONE; MANU: STUPP; MANYR: 1968; LOCLK: UNDER GROUND; PNAME: JAMES R. PHILLIPS, MANAGER-CONSTR. & STDS. COMPLIANCE; PHONE: 4024622141; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: STEEL POSTS W/ SIGNS.; STAT: NO; CTEST: Null | THIS REPORT COVERS A LINE HIT THAT OCCURRED ON KN ENERGY, INC.'S (K N'S) 16-INCH STEEL, BURIED TRANSMISSION PIPELINE IN SCOTTS BLUFF COUNTY, NEBRASKA ON MAY 14, 1991. IGNITION DID NOT OCCUR AND THERE WERE NO INJURIES FATALITIES AS A RESULT OF THE LINE BEING HIT. SERVICE WAS TEMPORARILY INTERRUPTED TO APPROXIMATELY 100 CUSTOMERS IN THE COMMUNITY OF MINATARE, NEBRASKA. THE PIPELINE WAS HIT BY AN OUTSIDE PARTY OPERATING A "V" PLOW PULLED BY A LARGE TRACTOR.THE DAMAGED PORTION OF THE PIPELINE WAS IN A CLASS 1 LOCATION AND WAS MARKEDWITH PERMANENT LINE MARKERS. A PERMANENT REPAIR WAS COMPLETED BY USE OF A WELD SLEEVE. TELEPHONIC REPORT OF THE ABOVE INCIDENT WAS TRANSMITTED ON REPORT #71985 TO THE DEPARTMENT OF TRANSPORTATION AND TO THE NEBRASKA STATE FIRE MARSHAL'S OFFICE IN LINCOLN, NEBRASKA ON MAY 14, 1991.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19910094 | 1991-06-17 | 2748 | CONSUMERS POWER CO | BIRMINGHAM | OAKLAND | MI |  | LAHSER CITY GATE STATION | N/A | 930 | 1991-05-07 | 3 | NO | N/A | N/A |  | NO | NO | OTHER | 0 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 10 | 71137 | 19910507 | 531 | 800 | BY TEST | 1120 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: NO FAILURE; MLKD: OTHER; MLKDO: BLOWDOWN; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1959; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: WILLIAM R. LOLL, SUPERINTENDENT; PHONE: 4177880566; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | EXPLOSION RESULTED WHEN GAS WAS VENTED FROM PIPING LOCATED AT THE CITY GATESTATION.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19910095 | 1991-06-17 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA | TEXARKANA | MILLER | AR | 75502 | MI-528 | 27910+22 | 1215 | 1991-05-14 | 1 | NO | N/A | N/A | AR | NO | NO | LEAK | 0 | 0 | 0 | 97000 | 77868.8699 | 169639.2019 | Null | 0 | 0 | 72084 | 19910514 | 750 | 858 | BY TEST | 1187 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | WELD | UNKNOWN | STEEL |  | OTHER | CLASS C PIPELINE DRIP | 1951 | 24 | 0.38 | 5LX42 | 42000 | FLASH WELD |  | AO SMITH | 0 | UNDER GROUND |  | PAUL S. BRWON, DESIGN ENGINEER SPEC. | 7086913791 | INTERNALLY | GENERAL CORROSION |  | OTHER | MICROBIOLOGICAL | COATED | YES | 1979 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | INTERNAL CORROSION SUSPECTED
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19910101 | 1991-06-25 | 21031 | VALERO TRANSMISSION CO | UNKNOWN | CRANE | TX | 79756 | 51.1 |  | 500 | 1991-06-09 | 1 | NO | N/A | N/A | TX | NO | NO | RUPTURE | 275 | 0 | 0 | 325000 | 260900.8529 | 568378.7694 | Null | 3 | 0 | 74921 | 19910609 | 1020 | 1051 | BY TEST | 1337 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1971 | 36 | 0.44 | API5LX-65 | 1582 | DSAW | N/A | VALUREE | 1970 | UNDER GROUND |  | JOHN SOMMER, MANAGER ENVIRONMENTAL & REG. COMPLIANCE | 5122462395 | EXTERNALLY | LOCALIZED PITTING |  | OTHER | UNKNOWN | COATED | YES | 1970 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | THE PIPELINE RUPTURED AT APPROXIMATELY 5 AM. ON JUNE 9, 1991. PROBABLE CAUSE IS EXTERNAL CORROSION PENDING VERIFICATION BY METALLURGICAL ANALYSIS. NO FIRE AND NO INJURIES. PIPELINE REPAIRED BY REPLACING WITH NEW PIPE. LINE BACKIN SERVICE ON JUNE 12,1991.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19910105 | 1991-07-01 | 19235 | TEXAS EASTERN GAS PIPELINE CO | LITTLE ROCK | PULASKI | AR | 72115 | M.P. 213.18 | 11255+90 | 1115 | 1991-06-01 | 3 | NO | N/A | N/A |  | NO | NO | OTHER | 0 | 0 | 0 | 90000 | 72249.467 | 157397.1977 | Null | 4 | 5 | 74081 | 19910601 | 560 | 830 | BY TEST | 1760 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1979; NMDIA: 24; THK: 0.33; SPEC: API 5LX; SMYS: 60000; SEAM: DSAW; MANU: U.S. STEEL; MANYR: 1979; LOCLK: UNDER GROUND; PNAME: DWAYNE E. TESCHENDORF; PHONE: 7136275573; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: MARKER POSTS; STAT: YES; CTEST: Null | BULLDOZER MOVING FILL DIRT ON LEVEE, GOUGED A 5.5" X 1.5" X 5.75" PUNCTUREOF THE PIPELINE. NO FIRE OR FATALITIES OCCURRED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910109 | 1991-07-08 | 15350 | PEOPLES NATURAL GAS CO | CARROLL | WASHINGTON | PA | 15033 | XS-288 |  | 1155 | 1991-06-11 | 3 | NO | N/A | N/A |  | NO | NO | OTHER | 0 | 0 | 0 | 51000 | 40941.3646 | 89191.7454 | Null | 1 | 30 | 75238 | 19910611 | 115 | 135 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: OTHER; PRTSO: UNKNOWN; PRTYR: 1981; NMDIA: 8; THK: 0.19; SPEC: GRADE B PIPE; SMYS: 0; MANYR: 0; LOCLK: OTHER; LOCLO: UNKNOWN; PNAME: JOYCE DAILEY - ATTORNEY; PHONE: 4124975668; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PERMANENT LINE MARKER; STAT: YES; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910110 | 1991-07-08 | 10030 | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | RURAL ROAD CROSSING | GRAHAM | KS |  |  | 237+50 | 1015 | 1991-06-19 | 1 | NO | N/A | N/A |  | NO | NO | RUPTURE | 0.25 | 0 | 0 | 3300 | 2649.1471 | 5771.2306 | YES | 1 | 0 | 76204 | 19910619 | 230 | 820 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1946; NMDIA: 3; THK: 0.22; SMYS: 0; MANU: YOUNGSTOWN; MANYR: 0; LOCLK: UNDER GROUND; PNAME: RICHARD BRUNOW - DIVISION SUPERINTENDENT; PHONE: 9135432135; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: ABOVEGROUND LINEMARKERS; STAT: NO; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910121 | 1991-08-19 | 2714 | CNG TRANSMISSION CORP | LIMESTONE | CLARION | PA | 16214 |  | 167+50 (INCIDENT SITE) | 945 | 1991-07-17 | 1 | NO | N/A | N/A |  | NO | NO | RUPTURE | 7 | 0 | 0 | 60250 | 48367.0043 | 105368.6796 | Null | 1 | 3 | 79769 | 19910717 | 755 | 822 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1947 | 14 | 0.38 | GRADE B | 42000 | SEAMLESS | N/A | J&L STEEL CORP. | 1947 | UNDER GROUND |  | JACK L. ADAMS, ADMINISTRATOR CODES & STANDARDS | 3046238410 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19910129 | 1991-09-03 | 15460 | KANSAS NATURAL INC | WICHITA | SEDGWICK | KS |  | MP 268 | 23 + 00 | 515 | 1991-04-10 | 3 | NO | N/A | N/A |  | NO | NO | OTHER | 0 | 0 | 1 | 0 | 0 | 0 | Null | 3 | 30 | 67563 | 19910410 | 0 | 0 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: AREA AROUND FRAC TANKS; MLKD: OTHER; MLKDO: UNKNOWN; PRTSY: OTHER; PRTSO: FRAC TANKS; PRTYR: 0; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: E. KEITH MITCHELL - MANAGER TECHNICAL; PHONE: 9134513330; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | ELY 4:45 AM., THE LIQUIDS IN FRONT OF THE TPIG BEGAN TO ARRIVE AT THE FACILITY. THE LIQUIDS WERE SEPARATED FROM THE GAS IN A SEPARATOR AND THEN LEVEL CONTROLLED INTO TWO FRAC TANKS. DUE TO THE VOLATILITY OF THE LIQUIDS, HYDROCARBON VAPOR WAS GENERATED OUT OF THE FRAC TANKS. BECAUSE OF COOL AND CALM WEATHER CONDITIONS, THE VAPORS ACCUMULATED ALONG THE GROUND AROUND THE TANKS. ATAPPROXIMATELY 5:15 AM., THE VAPORS IGNITED AND A FLASH FIRE RESULTED. ONE OF THE INDIVIDUALS PRESENT WAS SEVERELY BURNED. THE APPARENT SOURCE OF IGNITION WAS THE ENGINE OF AN EMPLOYEE'S PICK-UP OPERATING NEAR THE TANKS.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19910131 | 1991-09-06 | 20230 | UNITED GAS PIPELINE CO | EAST POINT | RED RIVER | LA |  | MP 52.09 | 2750+23 | 145 | 1991-08-06 | 1 | NO | N/A | N/A |  | NO | NO | RUPTURE | 30 | 0 | 0 | 344174 | 276293.2004 | 601911.368 | Null | 4 | 40 | 82454 | 19910806 | 781 | 897 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | OTHER | DRIP | STEEL |  | PIPELINE |  | 1945 | 24 | 0.34 | UNKNOWN | 50000 | FLASHWELD | N/A | A.O. SMITH | 1945 | UNDER GROUND |  | ST. GERMAIN - SR. P.L. SAFETY ANALYST | 7132295772 | INTERNALLY | LOCALIZED PITTING |  | OTHER | POSSIBLE CO2 | COATED | YES | 1950 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | INVESTIGATION INDICATES INNER DIAMETER FAILURE OF A LONGITUDINAL WELD SEAM ATTRIBUTED TO INTERNAL CORROSION.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19910133 | 1991-09-04 | 405 | ANR PIPELINE CO | U.S. FEDERAL WATERS |  | LA |  |  |  | 1145 | 1991-08-03 |  | YES | E.I. | 266E |  | YES | NO | LEAK | 0 | 0 | 0 | 101800 | 81722.1748 | 178033.7192 | Null | 0 | 0 | 82163 | 19910803 | 830 | 1250 | BY TEST | 2690 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1970 | 12.75 | 0.38 | API-5LX | 46000 | UNKNOWN |  | AMERICAN STEEL | 1970 | UNDER WATER |  | BARBARA J. HANNA | 3134965672 | INTERNALLY | OTHER | UNKNOWN | OTHER | UNKNOWN | COATED | YES | 1970 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | SUSPECTED INTERNAL CORROSION; NOT VERIFIED SINCE GRIPPER CLAMP WAS INSTALLED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910136 | 1991-09-03 | 19590 | TRANSOK INC | TULSA | TULSA | OK | 74119 | MILE POST 12 LINE 4 | 576+98 | 1448 | 1991-08-19 | 3 | NO | N/A | N/A |  | Null | NO | OTHER | 0 | 0 | 0 | 16700 | 13406.29 | 29205.9245 | Null | 4 | 12 | 84605 | 19910820 | 268 | 600 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: UNKNOWN; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1960; NMDIA: 24; THK: 0.28; SPEC: X-52; SMYS: 52000; SEAM: ARC WELD; VALVE: N/A; MANU: KAISER; MANYR: 1960; LOCLK: UNDER GROUND; PNAME: DAVID MATHIS: SAFETY & TRAINING SPECIALIST; PHONE: 9185619326; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19910814; MARK: YES; MRKTP: FLAGS; STAT: YES; CTEST: Null | A BULLDOZER OPERATED BY BENNY CRAIG, SHERWWOD CONT\STRUCTION 4716 N. 193 E. AVE. TULSA, OKALHOMA 918-266-6861, WAS BUILDING A TEMPORARY BYPASS ROAD ALONGMINGO ROAD FOR THE OKLAHOMA DEPARTMENT OF TRANSPORTATION. THE BULLDOZER HITTHE PIPELINE RESULTING IN THE TEAR.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19910137 | 1991-08-28 | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO |  | PORTER | IN |  | TASSINONG STATION |  | 1233 | 1991-08-02 | 1 | NO | N/A | N/A |  | NO | NO | LEAK | 0 | 0 | 1 | 400000 | 321108.742 | 699543.1008 | Null | 3 | 30 | 82101 | 19910802 | 275 | 320 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1954; NMDIA: 16; THK: 0.25; SPEC: AP15LX42; SMYS: 1325; MANU: N/A; MANYR: 1954; LOCLK: UNDER GROUND; PNAME: D.M. CAMPOS, MANAGER GAS CONTROL & STORAGE; PHONE: 2198535603; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19910422; MARK: YES; MRKTP: FLAGS; STAT: Null; CTEST: Null | CONTRACTOR WAS CLEARING THE AREA OF TREES AND BRUSH, USING A BULLDOZER, WHENHE PUNCTURED THE LINE THAT WAS CLEARLY MARKED. THE LEAKING GAS SOMEHOW IGNITED, CAUSING BURNES TO UPPER HALF OF THE BODY OF THE OPERATOR AND DESTROYING THE EQUIPMENT.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19910139 | 1991-08-23 | 19160 | TENNESSEE GAS PIPELINE CO | COLUMBUS | LOWNDES | MS |  | 546+0 |  | 1430 | 1991-07-23 | 4 | NO | N/A | N/A |  | NO | NO | LEAK | 0 | 0 | 4 | 0 | 0 | 0 | Null | 0 | 5 | 80666 | 19910723 | 0 | 936 | BY TEST | 936 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: COMPRESSOR UNLOADER; MLKD: OTHER; MLKDO: COMPRESSOR VALVE CAP GASK; PRTSY: COMPRESSOR STATION; PRTYR: 1959; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 1955; LOCLK: ABOVE GROUND; PNAME: L.A. SALINAS, STAFF CIVIL ENGINEER; PHONE: 7137572781; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: HURRICANE ANDREW; NOTIF: NO; MARK: YES; MRKTP: SIGNAGE ON PLATFORM; STAT: NO; CTEST: Null | GAS ESCAPING FROM TWO IMPROPERLY SEATED VALVE CAP GASKETS IGNITED CAUSING BURNES TO FOUR WORKMEN IN THE VICINITY.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910140 | 1991-08-23 | 19160 | TENNESSEE GAS PIPELINE CO | DANVILLE |  | KY |  | 100-4+2.48 |  | 1400 | 1991-07-23 | 1 | NO | N/A | N/A |  | NO | NO | RUPTURE | 0 | 0 | 0 | 50000 | 40138.5928 | 87442.8876 | Null | 5 | 55 | 80683 | 19910723 | 500 | 780 | BY TEST | 780 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1953; NMDIA: 30; THK: 0.41; SPEC: API - 5L; SMYS: 52000; SEAM: N/A; VALVE: N/A; MANU: REPUBLIC PIPE; MANYR: 1953; LOCLK: OTHER; LOCLO: UNKNOWN; PNAME: L.A. SALINAS, STAFF CIVIL ENGINEER; PHONE: 7137572781; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: P/L ROW MARKERS; STAT: Null; CTEST: Null | AN EQUIPMENT OPERATOR DIGGING NEAR OUR LINE, GOUGED THE PIPELINE, CAUSING A LEAK AND SUBSEQUENT RUPTURE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910142 | 1991-09-11 | 19235 | TEXAS EASTERN GAS PIPELINE CO | PLYMOUTH TOWNSHIP | MONTGOMERY | PA |  | M.P. 0.66 (LINE I-B-1) | 34+66 | 1845 | 1991-08-03 | 3 | NO | N/A | N/A |  | NO | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 30 |  | 19910803 | 150 | 718 | BY TEST | 815 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: INSTRUMENT CONTROL LINE; MLKD: STEEL; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1959; NMDIA: 0.25; THK: 0.02; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: DWAYNE E. TESCHENDORF; PHONE: 7136275573; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: UNKNOWN; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | WIND FROM STORM BLEW PART OF ROOF FROM A NEARBY WAREHOUSE INTO THE CONTROL LINE FOR A PRESSURE REGULATOR AT MEASURING STATION 517. THE PRESSURE REGULATOROPENED FULLY AND THE RELIEF VALVE WAS ACTIVATED AT 220 PSI AS DESIGNED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19910149 | 1991-10-07 | 12690 | MONTANA POWER CO | KALISPELL | FLATHEAD | MT | 59901 | 113.8 | 5978+73 | 1725 | 1991-05-10 | 2 | NO | N/A | N/A |  | NO | NO | OTHER | 0 | 0 | 0 | 145757 | 117009.6173 | 254908.2594 | Null | 2 | 5 |  | 19910510 | 400 | 662 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1962; NMDIA: 10; THK: 0.22; SPEC: API 5L; SMYS: 42000; SEAM: ERW; VALVE: ROCKWELL FIG.49; MANU: LONE STAR; MANYR: 1962; LOCLK: UNDER GROUND; PNAME: ROGER RAWLS- DIRECTOR OF ENGINEERING; PHONE: 4067235421; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PERMANENT PIPELINE MARKER; STAT: YES; CTEST: Null | A LARGE LOG LOADER WAS PICKING UP LOGS STACKED IN THE AREA TRAVERSEE BY THE PIPELINE. IN AN EFFORT TO GET UNDER THE BOTTOM OF THE STACK, A LARGE BOTTOM TINE ON THE LOADER WAS DRIVEN BELOW THE SURFACE OF THE GROUND COVERING THE PIPELINE, PENATRATING THE PIPELINE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19910153 | 1991-09-30 | 2616 | COLUMBIA GAS TRANSMISSION CORP |  | RICHLAND | OH | 44864 | LINE SL-2151 | 269+70 | 1009 | 1991-08-29 | 1 | NO | N/A | N/A |  | NO | NO | RUPTURE | 10 | 0 | 0 | 280000 | 224776.1194 | 489680.1706 | Null | 0 | 31 |  | 19910829 | 1090 | 1200 | BY TEST | 1800 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | OTHER | PIPELINE DRIP | STEEL |  | PIPELINE |  | 1951 | 20 | 0.5 | API5LX | 42000 | FLASH WELD | N/A | A.O. SMITH | 1951 | OTHER | UNKNOWN | J.O. LOKER, MANAGER TECHNICAL STANDARDS | 3043572767 | INTERNALLY | LOCALIZED PITTING |  | OTHER | PROBABLE BACTERIAL CORROS | COATED | YES | 1967 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | RUPTURE OF UNDERSLUNG PIPELINE DRIP LIFTED APPROXIMATELY 165' OF 20" PIPELINE OUT OF GROUND. INTERNAL CORROSION RESULTED IN A BRITTLE FRACTURE TYPE FAILURE.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19910158 | 1991-10-09 | 13580 | NORTH CAROLINA NATURAL GAS CORP | WILSON | WILSON | NC | 27893 | 6.14 | 728+58 | 1730 | 1991-09-21 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 80000 | 64221.7484 | 139908.6202 | Null | 1 | 0 |  |  | 423 | 763 | BY CFR 192.619(A)(3) | 890 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1959; NMDIA: 8.63; THK: 0.19; SPEC: GRADE B; SMYS: 35000; SEAM: ERW; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: EDWARD P. KOSAREK ASST DIV SUPT; PHONE: 9197343254; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19910812; MARK: YES; MRKTP: YELLOW FIBERGLASS SIGNS; STAT: YES; CTEST: Null | CONTRACTOR LAYING PARALLEL PIPELINE HIT EXISTING LINE TRACK HOE BUCKET.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19910159 | 1991-10-15 | 18484 | SOUTHERN CALIFORNIA GAS CO | CITY OF INDUSTRY | LOS ANGELES | CA | 91746 | PUENTE STATION | 4356 + 61.5 | 1830 | 1991-09-24 | 3 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 100000 | 80277.1855 | 174885.7752 | YES | 2 | 5 |  | 19910925 | 356 | 584 | BY CFR 192.619(A)(3) | 958 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: VALVE; PRTFO: INSTRUMENTATION; MLKD: OTHER; MLKDO: UNKNOWN; PRTSY: COMPRESSOR STATION; PRTYR: 1950; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: UNDER GROUND; LOCLO: INSIDE BUILDING; PNAME: R L RUDZIK MANAGER OF TRANSMISSION AND UNDERGROUND STORAGE S; PHONE: 2136892345; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: FIRE; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | FIRE. ON SEPTEMBER 24, 1991, AT APPROXIMATELY 6:30 PM, A FIRE OF UNKKNOWNORIGIN DESTROYED THE CONTENTS OF THE INSTRUMENTATION BUILDING AT THISFACILITY. GAS WAS CONTROLLED BY CLOSING THE VALVES ON PIPING LEADING INTO THEBUILDING. INVESTIGATION INTO THE CAUSE OF THE FIRE IS ON-GOING. NOCUSTOMERS WERE AFFECTED BY THE SHUTDOWN, NOR WERE THERE INJURIES ASSOCIATEDWITH THIS INCIDENT. ESTIMATED COSTS ASSOCIATED WITH THIS INCIDENT WERE$100,000. SUPPLEMENTAL REPORT 10/03/94 INDICATES THAT THE MOST LIKELY CAUSE OFTHE INCIDENT WAS AN ELECTRICAL SURGE RESULTING IN AN ARC THAT IGNITED GAS INTHE EQUIPMENT. ADDITIONAL INFORMATION INDICATED THAT THERE IS NOT CONCLUSIVEEVIDENCE AS TO THE CAUSE OF THE INCIDENT. MOST PROBABLE - ELECTRICAL SURGECAUSING FAILURE IN THE SYSTEM AND RESULTING IN AN ARC IGNITING GAS INSIDE THEEQUIPMENT.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19910160 | 1991-10-11 | 2327 | CHEVRON USA INC | MAIN PASS BLOCK 299 FIELD | GULF OF MEXICO | LA |  |  |  | 1400 | 1991-09-17 |  | YES | MP | 299 |  | YES | NO | OTHER | 0 | 0 | 0 | 300000 | 240831.5565 | 524657.3256 | Null | 0 | 0 |  | 19911007 | 0 | 1216 | NO DATA | 1800 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1968; NMDIA: 6.63; THK: 0.03; SPEC: API5L GRADE X46; SMYS: 46000; SEAM: FRW; MANU: LONE STAR STEEL; MANYR: 1968; LOCLK: UNDER WATER; PNAME: P LEVENDOSKI, FACILITIES ENGINEER; PHONE: 5043642334; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: NOT SPECIFIED; NOTIF: YES; NOTDT: 19810815; MARK: YES; MRKTP: STARFIX NAVIGATION SYSTEM; STAT: YES; CAULO: 2327CHEVRON USA INC; CTEST: Null | THE EXACT TIME OF INCIDENT IS UNKNOWN BECAUSE THE PIPELINE WAS NOT PRESSUREDUP DUE TO CONSTRUCTION ACTIVITIES AT MP 299 "B".
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19910161 | 1991-09-30 | 12696 | MONTEREY PIPELINE CO | WHITE CASTLE | ASCENSION | LA | 70788 | 7.5 | 359 + 22 ON BRS #9 | 1250 | 1991-09-28 | 1 | NO |  |  | LA | Null | NO | LEAK | 0 | 0 | 0 | 75000 | 60207.8891 | 131164.3314 | Null | 0 | 0 |  | 19910928 | 665 | 840 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1958; NMDIA: 10; THK: 0.25; SPEC: 28.04 X -42; SMYS: 42000; SEAM: ELECTRIC - WELD; MANU: REPUBLIC STEEL; MANYR: 1957; LOCLK: UNDER WATER; PNAME: RONALD P HENDERSON OPER ENG; PHONE: 7136567845; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: 8.5" X 11" SIGN ON EACH S; STAT: YES; CAULC: CONSTRUCTION; CAULO: 2696MONTEREY PIPELINE CO; CTEST: Null | LINE WAS HIT BY A BACKHOE DIGGING IN THE AREA.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910162 | 1991-10-30 | 21031 | VALERO TRANSMISSION CO | BASTROP | BASTROP | TX | 78215 | 1672+34 |  | 700 | 1991-04-05 | 1 | NO |  |  | TX | Null | NO | OTHER | 0 | 0 | 0 | 7500 | 6020.7889 | 13116.4331 | YES | 8 | 0 |  | 19910405 | 300 | 372 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: VALVE; MLKD: STEEL; PRTSY: OTHER; PRTSO: TAL VALVE; PRTYR: 1947; NMDIA: 6; THK: 0.19; SMYS: 0; VALVE: WESCOTT GATE500; MANU: WESTCOTT; MANYR: 1947; LOCLK: UNDER GROUND; PNAME: LONNIE GRADY AREA FOREMAN; PHONE: 5122475341; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: MATERIAL; CAULO: 1031VALERO TRANSMISSION CO; CTEST: Null | VALVE (6") CASTING CRACKED FOR UNKNOWN REASON. THIS 6" VALVE WAS REMOVED AND THE 6" LINE WAS TIED INTO THE 12" LINE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910163 | 1991-10-30 | 11680 | LONE STAR GAS CO | BLOOMING GROVE | NAVARRO | TX |  |  | 634+92 | 530 | 1991-03-27 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 20000 | 16055.4371 | 34977.155 | Null | 3 | 30 |  | 19910327 | 240 | 325 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1928; NMDIA: 3.5; THK: 156; SMYS: 2139; SEAM: LAP WELD; MANYR: 0; LOCLK: UNDER GROUND; PNAME: LOIS ROSS CLERK; PHONE: 2146701566; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: FENCE POST PAINTED 557" E; STAT: YES; CAULC: CONSTRUCTION; CAULO: 1680LONE STAR GAS CO; CTEST: Null | LINE WAS CUT INTO BY LAND OWNER USING BULL DOZER
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910164 | 1991-10-30 | 20245 | UNITED TEXAS TRANSMISSION CO | ORCHARD | FORT BEND | TX |  |  | 0 + 00 | 1155 | 1991-02-26 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 5 | 25 |  | 19910226 | 335 | 445 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | OTHER | VALVE FLANGE | OTHER | SEMI-STEEL | OTHER | SEPARATOR INLET VALVE | 1938 | 0 | 0 |  | 0 |  | 8" 500 WP GATE | WESTCOTT | 0 | OTHER |  | PAUL HAAS/SUPER. REG. COMP | 7139633243 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | FLANGE ON A 8" 500 W P WESTCOTT GATE VALVE | NO |  | NO DATA |  | 0 | 0 | UNITED TEXAS PERSONNEL FOUND DURING LEAK ANNUAL VALVE INSPECTION AND DISCOVERED A CRACK IN THE VALVE FLANGE. FOUND CRACK ON BOTTOM OF 8" FLANGE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910165 | 1991-10-30 | 11680 | LONE STAR GAS CO | RAVENNA | FANNIN | TX |  |  | 3192+44 | 1015 | 1991-02-09 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 5000 | 4013.8593 | 8744.2888 | Null | 0 | 45 |  | 19910209 | 250 | 320 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1926; NMDIA: 9; THK: 281; SMYS: 24000; MANYR: 0; LOCLK: UNDER GROUND; PNAME: LOIS ROSS CLERK; PHONE: 2146701566; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; MARK: YES; MRKTP: PAINTED POSTS SIGNS; STAT: NO; CAULC: CONSTRUCTION; CAULO: 1680LONE STAR GAS CO; CTEST: Null | LINE WAS STRUCK AND PUNCTURED BY A DOZER BEING USED TO FILL IN AN OLD POND.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910167 | 1991-10-30 | 15007 | PACIFIC GAS & ELECTRIC CO | SUNNYVALE | SANTA CLARA | CA | 94089 | MP 6.37, L-109 |  | 1255 | 1991-10-08 | 3 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 60000 | 48166.3113 | 104931.4651 | Null | 1 | 25 |  | 19911008 | 310 | 375 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1936; NMDIA: 22; THK: 0.31; SMYS: 33000; SEAM: SSAW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: W R MAZOTTI V P GAS & ELEC TECH SVS; PHONE: 4159736999; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; MRKTP: 0N; STAT: Null; CAULC: CONSTRUCTION; CAULO: 5007PACIFIC GAS & ELECTRIC CO; CTEST: Null | CONTRACTOR STRUCK TRANSMISSION LINE WITH BULLDOZER CASUING SEVERAL DENTS ANDGOUGES; PRESSURE REDUED IN LINE TO SAFE PRESSURE. SECTION REPLACED
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19910168 | 1991-10-29 | 21031 | VALERO TRANSMISSION CO | MATAGORDA |  | TX |  |  |  | 1500 | 1991-09-22 |  | YES |  | 487 | TX | Null | NO | RUPTURE | 12.5 | 0 | 0 | 50000 | 40138.5928 | 87442.8876 | Null | 1 | 30 |  | 19910922 | 680 | 1240 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1968; NMDIA: 12; THK: 0.31; SPEC: X-52; SMYS: 1832; MANYR: 0; LOCLK: UNDER WATER; PNAME: JOHN SUMMER MANAGER ENVIRONMENTAL & REGULATORY COMPLIANCE; PHONE: 5122462395; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: MATERIAL; CAULO: 1031VALERO TRANSMISSION CO; CTEST: Null | THE PILELINE RUPTURED SEPTEMBER 22, 1991 FROM UNDETERMINED CAUSES AND WAS TAKEN OUT OF SERVICE IMMEDIATELY. THE RUPTURED SECTION WAS REPLACED AND PIPELINE WAS PLACED IN SERVICE ON OCTOBER 17, 1991. A METALLURGICAL ANALYSIS OF THE FAILED PIPE IS BEING CONDUCTED TO DETERMINE THE CAUSE OF THE FAILURE. EXPECTED COMPLETION DATE IS DECEMBER 15, 1991.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19910169 | 1991-10-29 | 405 | ANR PIPELINE CO | VERMILION PARISH |  | LA |  | 0.00 |  | 850 | 1991-09-27 | 1 | NO |  |  | LA | Null | NO | RUPTURE | 35 | 0 | 0 | 323000 | 259295.3092 | 564881.0539 | Null | 1 | 0 |  | 19910927 | 980 | 1100 | NO DATA | 2006 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | WELD | LONGITUDINAL | STEEL |  | PIPELINE |  | 1967 | 24 | 0.5 | API-5LX | 60000 | FLASH WELDED |  | A O SMITH | 1966 | UNDER GROUND |  | BARBARA J HANNA COMPLIANCE ANALYST | 3134965672 | INTERNALLY | LOCALIZED PITTING |  | OTHER | LIQUIDS | COATED | Null | 1967 | NO DATA |  | Null |  | Null |  | Null | NO DATA | 0405ANR PIPELINE CO | Null | [5 empty] | LOCALIZED INTERNAL CORROSION,
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19910170 | 1991-11-19 | 18516 | SOUTHERN NATURAL GAS CO |  |  | LA |  |  |  | 1045 | 1991-10-18 |  | YES | E I | 333 |  | NO | NO | LEAK | 0 | 0 | 0 | 120000 | 96332.6226 | 209862.9302 | Null | 0 | 0 |  | 19911018 | 1140 | 1440 | BY TEST | 2160 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1977 | 12 | 0.38 | AP15LX | 52000 | SEAMLESS |  |  | 0 | UNDER WATER |  | C FARRELL SUP PIPELINE CODE & SAFETY | 2053257554 | EXTERNALLY | LOCALIZED PITTING |  | OTHER | CRACK IN CONCRETE COATING | COATED | YES | 1977 | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION | 8516SOUTHERN NATURAL GAS CO | Null
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19910171 | 1991-11-05 | 19325 | TEXAS UTILITIES FUEL CO | EUSTACE | HENDERSON | TX |  | 29.34 |  | 1100 | 1991-05-14 | 1 | NO |  |  | TX | Null | NO | RUPTURE | 30 | 0 | 1 | 55000 | 44152.452 | 96187.1764 | Null | 1 | 0 |  | 19910514 | 605 | 675 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1988; NMDIA: 16; THK: 0.25; SPEC: X42; SMYS: 42000; SEAM: ERW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: DANIEL R. ALCORN/PRINCIPAL ENG. ANALYST; PHONE: 2148126870; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: MARKERS ON FENCE; STAT: Null; CTEST: Null | TUFCO'S 16" PIPELINE WAS STRUCK AND PUNCTURED BY EQUIPMENT USED BY A THIRD PARTY CONTRACTOR INSTALLING A FIBER-OPTIC TELEPHONE CABLE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910172 | 1991-11-05 | 19325 | TEXAS UTILITIES FUEL CO | COMO | HOPKINS | TX |  | COMO STATION |  | 2100 | 1991-06-07 | 1 | NO |  |  | TX | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 30 |  |  | 0 | 0 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: STORAGE TANK; MLKD: STEEL; MLKDO: FIBERGLASS; PRTSY: OTHER; PRTSO: STORAGE TANK; PRTYR: 1988; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: DANIEL R, ALCORN/PRINCIPLE ANG ANALYST; PHONE: 2148126870; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: LIGHTNING STRIKE; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | LIGHTNING STRIKE TO STEEL DUMP LINE ATTACHMENT TO 210 BBL. FIBERGLASS NATURAL GAS CONDENSATE STORAGE TANK.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910173 | 1991-11-05 | 20245 | UNITED TEXAS TRANSMISSION CO | BEAUMONT | JEFFERSON | TX |  | 7.25 | 8820+83 | 1545 | 1991-06-12 | 3 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 40 |  | 19910613 | 210 | 292 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | VALVE | NOT SPECIFIED | STEEL |  | PIPELINE |  | 1945 | 12 | 0.25 |  | 24000 |  |  |  | 0 | UNDER GROUND |  | PAUL HASS/SUPER REG COMP | 7139633243 | EXTERNALLY | OTHER | NO VISUAL LEAK WAS INSIDE | OTHER | NO CAUSE ENTERED | COATED | YES | 1955 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | DUPONT EMPLOYEE DISCOVERED BUBBLES AROUND PIPELINE CASING VENT. UTTCO CREW EXCAVATED AND DISCOVERED LEAK COMING FROM INSIDE FILLED CASING.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910174 | 1991-11-05 | 11680 | LONE STAR GAS CO | VERNON | BAYLOR | TX |  | 21 | 1040+35 | 510 | 1991-07-09 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 7000 | 5619.403 | 12242.0043 | Null | 2 | 10 |  | 19910709 | 250 | 325 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1928; NMDIA: 45; THK: 0.17; SMYS: 0; MANYR: 0; LOCLK: UNDER GROUND; PNAME: LOIS ROSS CLERK; PHONE: 2146701566; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: AERIAL MARKER #21; STAT: NO; CTEST: Null | Pipe was hit by plow, knocking a small hole 1/2" deep.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910175 | 1991-11-05 | 11680 | LONE STAR GAS CO | RHINELAND | KNOX | TX |  | A M 53/2738+02 | #2740+49 | 1030 | 1991-08-19 | 1 | NO |  |  | TX | Null | NO | LEAK | 0 | 0 | 0 | 6800 | 5458.8486 | 11892.2327 | Null | 0 | 30 |  | 19910819 | 235 | 500 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1930; NMDIA: 8; THK: 0.22; SPEC: GRADE A; SMYS: 30000; SEAM: LAPWELD; VALVE: N/A; MANU: UNKNOWN; MANYR: 0; LOCLK: OTHER; LOCLO: NOT GIVEN IN REPORT; PNAME: PHILLIP MURDOCK - MANAGER; PHONE: 2146702229; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: SIGNS AT COUNTY ROAD; STAT: NO; CTEST: Null | MR. BROWN'S EMPLOYEE WAS DEEP PLOWING WITH A MOLD BOARD BREAKING PLOW WHEN THE PLOW STRUCK THE LINE CAUSING A HOLE AND LOSS OF GAS.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19910176 | 1991-11-05 | 11680 | LONE STAR GAS CO | CLARENDON | DONLEY | TX |  |  | 2235+23 | 1630 | 1991-08-20 | 1 | NO |  |  | TX | Null | NO | OTHER | 0 | 0 | 0 | 7600 | 6101.0661 | 13291.3189 | Null | 2 | 30 |  | 19910820 | 270 | 350 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1952; NMDIA: 4; THK: 0.2; SPEC: GRADE A; SMYS: 30000; SEAM: LAP WELD; MANU: UNKNOWN; MANYR: 0; LOCLK: UNDER GROUND; PNAME: PHILLIP MURDOCK - MANAGER; PHONE: 2146702229; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: LONE STAR GAS SIGN; STAT: NO; CTEST: Null | LINE WAS HIT BY PLOW.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910177 | 1991-11-05 | 19325 | TEXAS UTILITIES FUEL CO | BUFFALO | LEON | TX |  | SOUTH OF BV AA2 |  | 1545 | 1991-08-22 | 1 | NO |  |  | TX | Null | NO | LEAK | 0 | 0 | 0 | 5296 | 4251.4797 | 9261.9507 | YES | 0 | 30 |  | 19910822 | 325 | 1020 | BY CFR 192.619(A)(3) | 1200 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: 2" RISER CNNCT TO 8" PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1957; NMDIA: 8; THK: 0.19; SPEC: X42; SMYS: 42000; SEAM: ERW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: DANIEL R. ALCORN, PRINCIPAL ENGINEERING; PHONE: 2148126870; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19910822; MARK: YES; MRKTP: FENCES,ROAD CROSSINGS,ETC; STAT: NO; CTEST: Null | THIRD PARTY RIGHT-OF-WAY CLEARING CREW WERE WORKING ON TUFCO R.O.W. CONTRACTOR'S EQUIPMENT SHEARED A 2 INCH VALVE FROM A TWO INCH RISER THAT WAS CONNECTED TO THE 8" PIPELINE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910178 | 1991-11-05 | 11680 | LONE STAR GAS CO | BRAZOS | PALO PINTO | TX |  | 47 | 2629+78 | 530 | 1991-09-16 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 22634 | 18169.9382 | 39583.6464 | Null | 0 | 50 |  | 19910916 | 710 | 800 | BY TEST | 1200 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1960; NMDIA: 18; THK: 0.25; SPEC: API 5 LX 42; SMYS: 42000; SEAM: EW SMLS; MANU: UNKNOWN; MANYR: 0; LOCLK: UNDER GROUND; PNAME: PHILLIP MURDOCK - MANAGER; PHONE: 2146702229; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: ROAD, PAINTED POST,SIGNS; STAT: NO; CTEST: Null | dozer was digging a drilling site and hit the line causing hole in the pipe. pipeline road markings were 2998' from the incident.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910180 | 1991-11-05 | 11680 | LONE STAR GAS CO | ELMORE CITY | GARVIN | OK |  |  | 24+51 | 1245 | 1991-04-05 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 6827 | 5480.5235 | 11939.4519 | Null | 0 | 30 |  | 19910405 | 325 | 800 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1957; NMDIA: 8.58; THK: 188; SPEC: X-42; SMYS: 42000; SEAM: ELECTRIC WELD; VALVE: 800; MANU: NORDSTROM; MANYR: 0; LOCLK: UNDER GROUND; PNAME: LOIS ROSS, CLERK; PHONE: 2146701566; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: MARKING IN PLACE; STAT: YES; CTEST: Null | LINE WAS HIT BY FRONT END LOADER.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910181 | 1991-11-26 | 19590 | TRANSOK INC | LAWTON | COMANCHE | OK | 73501 | MP STERLING VALVE |  | 1610 | 1991-10-30 | 1 | NO |  |  | OK | Null | NO | OTHER | 0 | 0 | 0 | 12500 | 10034.6482 | 21860.7219 | Null | 2 | 20 |  | 19911030 | 308 | 720 | BY TEST | 1282 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; PRTFO: FAILURE NOT SPECIFIED; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1973; NMDIA: 16; THK: 0.22; SPEC: API STD 5L; SMYS: 52000; SEAM: ERW; VALVE: N/A; MANU: STUPP; MANYR: 1973; LOCLK: UNDER GROUND; PNAME: DAVID MATHIS - SAFETY TRAINING SPECIALIST; PHONE: 9185619326; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; MRKTP: 0Y; STAT: Null; CTEST: Null | BULLDOZER OPERATOR RICKY NUNN CALLED IN TEAR AT 16:10 DURING CONVERSTATION HE STATED NO NOTIFICATION HAD BEEN GIVEN TO ANYU ONE-CALL SYSTEM. A BULLDOZEROPERATED BY RICKY NUNN'S DOZER SERVICE WAS BURYING TRASH FOR LAND OWNER (DALE COOBY). WHILE DIGGING TRASH PIT TRANSOK INC. PIPELINE WAS STRUCK RESULTINGIN 1/4" ROUND TEAR.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910182 | 1991-11-27 | 20230 | UNITED GAS PIPELINE CO | SECTION 91, T-11-S, R-7-E | ST JOHN THE BAPTIST | LA |  | 58.32 | 3072+51 | 1240 | 1991-10-24 | 3 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 50000 | 40138.5928 | 87442.8876 | Null | 1 | 0 |  | 19911024 | 275 | 376 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: MECHANICAL JOINT; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1927; NMDIA: 18; THK: 0.31; SMYS: 24000; MANU: YOUNGSTOWN; MANYR: 0; LOCLK: UNDER GROUND; PNAME: W.F ST.GERMAIN, P.L. SAF. ANAL.; PHONE: 7132295772; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | CONTRACTOR INSTALLING A NEW LINE, TO REPLACE INCIDENT INVOLVED FACILITY, CAUSED EARTH MOVEMENT WHICH RESULTED IN SEPARATION AT A COUPLING.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910183 | 1991-12-02 | 22617 | WILLIAMS NATURAL GAS CO | OSBORNE | OSBORNE | KS |  | 1233+79 |  | 1405 | 1991-10-25 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 5000 | 4013.8593 | 8744.2888 | Null | 0 | 35 |  | 19911025 | 340 | 350 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 0; NMDIA: 4; THK: 0.11; SMYS: 24000; SEAM: UNK; MANYR: 0; LOCLK: UNDER GROUND; PNAME: WARREN A ETHERIDGE; PHONE: 9185884427; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: LINE MARKER (TYPICAL); STAT: NO; CTEST: Null | FARMER TORE HOLE IN PIPELINE WITH DEEP GROUND RIPPER.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19910184 | 1991-12-02 | 562 | ARCO OIL & GAS CO - DIV OF ATLANTIC RICHFIELD | BAKERSFIELD | KERN | CA | 93302 | LINE 201, VALVE STA 7 |  | 1015 | 1991-11-01 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 30 |  | 19911101 | 175 | 1172 | BY TEST | 1350 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: GATHERING SYSTEM; PRTFL: FITTING; PRTFO: 2" THREADED FITTING; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1950; NMDIA: 10; THK: 0.25; SPEC: GRADE B, A106; SMYS: 35000; SEAM: N/A; VALVE: N/A; MANYR: 0; LOCLK: OTHER; LOCLO: EXPOSED ON EXCAVATION; PNAME: KEVIN L. SMITH - OPERATION SUPT.; PHONE: 8057633235; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: SIGNS; STAT: NO; CTEST: Null | ON 11/1/91 AT APPROXIMATELY 10:15 A.M. A 1986 TOYOTA COROLLA WAS TRAVELLING EASTBOUND ON HIGHWAY 119 APPROXIMATELY 1.3 MILES EAST OF THE INTERSEDTION OF UTUPMAN ROAD AND HIGHWAY 119. THE VEHICLE VEERED OFF THE SOUTH SIDE OF THE HUGHWAY TRAVELLING APPROXIMATELY 525 FEET ACROSS UNDISTURBED LAND. THE VEHICLE CROSSED A PRIVATE ROAD EMBANKMENT AND CAME TO REST IN AN EXCAVATION. THE EXCAVATION WHICH WAS BARRICADED HAD BEEN DUG BY ARCO OIL AND GAS COMPANY TO MAKE REPAIRS TO A VALVE BOX. THE VEHICLE STRUCK AND DAMAGED A 2"X4" CONNECTIONON THE 1`0 INCH LINE CAUSING A RELEASE OF NATURAL GAS. NO PERSONAL INJURIESOCCURED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910185 | 1991-11-29 | 2616 | COLUMBIA GAS TRANSMISSION CORP | FLATROCK PLAINS | RANDOLPH | WV | 26263 |  | 359+79 | 800 | 1991-11-05 | 1 | NO |  |  |  | Null | YES | RUPTURE | 12 | 0 | 0 | 34000 | 27294.2431 | 59461.1636 | YES | 0 | 5 |  | 19911105 | 798 | 974 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1960 | 20 | 0.31 | API 5LX | 52000 | SEAMLESS | N/A | NATIONAL TUBE USS | 1960 | UNDER GROUND |  | J.O. LOKER, MANAGER TECHNICAL STANDARDS | 3043572767 | EXTERNALLY | OTHER | 8" X 9" CORRODED AREA | OTHER | ISOLATED CORROSION CELL | COATED | YES | 1961 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | RELATED CORROSION ACROSS ADJACENT FULL ENCIRCLEMENT FITTING AND OTHER PIPE TOTALED APPROXIMATELY 32" IN LENGTH X MAXIMUM 9" WIDTH. REMAINING PIPE IN EXCELLENT CONDITION.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19910211 | 1991-11-08 | 11818 | LOUISIANA - NEVADA TRANSIT | CANFIELD | LAFAYETTE | AR |  | MP 27 | MP 27 | 1500 | 1991-10-17 | 1 | NO |  |  | AR | Null | NO | OTHER | 0 | 0 | 0 | 66400 | 53304.0512 | 116124.1547 | Null | 2 | 6 |  |  | 300 | 450 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1939; NMDIA: 8; THK: 0.2; SPEC: API 5L; SMYS: 24000; SEAM: EW; VALVE: NONE; MANU: REPUBLIC; MANYR: 1939; LOCLK: UNDER GROUND; PNAME: JERI JONES, VICE PRESIDENT; PHONE: 5017774571; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: LINE MARKER SIGNS; STAT: YES; CTEST: Null | ARKANSAS ACT 762 OF 1991 SPECIFIES THAT ANYONE DIGGING IN THE VICINITY OF GAS OR HAZARDOUS CHEMICALS IS REQUIRED TO GIVE NOTICE TO THE ARKANSAS ONE-CALL CENTER. NO NOTICE RECEIVED. I ATTEMPTED TO NOTIFY D.O.T. BEGINNING AT 4:45 P.M. ON THAT DATE AT 1-800-424-8802 BUT REACHED A RECORDING. I TRIED AGAIN ON THE FOLLOWING DAT AND WAS STILL UNSUCCESSFUL. TELEPHONIC NOTICE WAS GIVEN TO THE ARKANSAS PUBLIC SERVICE COMMISSION, PIPELINE SAFETY DEPARTMENT, ON OCTOBER 17, 1991. DOZER OPERATED BY TIMBER COMPANY LOGGING IN THE VICINITY OF LNT MAINLINE DUG INTO LINE CAUSING A TEAR APPTOXIMATELY 3" X 10". ELECTRIC LINES IN THE AREA MAY HAVE BEEN A FACTOR IN THE IGNITION WHICH BURNED THE DOZER. OPERATOR ESCAPED INJURY.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910253 | 1991-12-10 | 2564 | COLORADO INTERSTATE GAS CO | LAKIN | KEARNY | KS | 68760 |  |  | 845 | 1991-11-12 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 10 |  | 19911112 | 250 | 285 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: VALVE; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1949; NMDIA: 0; THK: 0; SMYS: 0; VALVE: CAM-OPERATED CH; MANYR: 1949; LOCLK: ABOVE GROUND; LOCLO: INSIDE BUILDINGS; PNAME: RICHARD M FLINT; PHONE: 7195204350; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: NO DATA; CAULO: 2564COLORADO INTERSTATE GAS CO; CTEST: Null | COMBUSTION GASES FROM THE CYLINDER OF A GAS COMPRESSOR ENGINE ESCAPED THRU THE STARTING AIR INTAKE VALVE INTO THE STARTING AIR SYSTEM. AN EXPLOSION OCCURRED IN THE AIR PIPING IN THE COMPRESSOR & AUXILIARY BUILDINGS WHEN ACCUMULATED OIL FROM THE AIR IN THE COMPRESSOR & AUXILIARY BUILDINGS WHEN ACCUMULATED BLUBRICATING OIL FROM THE AIR COMPRESSORS IGNITED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19910254 | 1991-12-09 | 19160 | TENNESSEE GAS PIPELINE CO | CREOLE | CAMERON | LA |  | MP507A-103+5.68 |  | 1158 | 1991-11-05 | 1 | NO |  |  |  | Null | NO | RUPTURE | 1 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 53 |  | 19911106 | 886 | 1055 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1991 | 12.75 | 0.28 | API-5LX | 42000 | ERW |  | REPUBLIC | 1950 | UNDER GROUND |  | L A SALINAS | 7137572721 | INTERNALLY | GENERAL CORROSION | GENERAL INTERNAL CORROSIO | OTHER | INTERNAL CORROSION | COATED | YES | 1951 | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION | 9160TENNESSEE GAS PIPELINE CO | Null | [5 empty] | PIPELINE RUPTURED, CAUSING A FIRE AT CANAL CROSSING IN A RICE FIELD.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19910265 | 1991-12-24 | 12101 | MAPLE GAS CORP | LEA | LEA | NM |  |  | AIRSTRIP TIE-IN | 115 | 1991-11-25 | 1 | NO |  |  |  | NO | Null | OTHER | 0 | 0 | 0 | 300000 | 240831.5565 | 524657.3256 | Null | 1 | 0 |  | 19911219 | 475 | 792 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1976; NMDIA: 12; THK: 0.19; SPEC: GRADE B; SMYS: 0; SEAM: EWR; MANYR: 1975; LOCLK: UNDER GROUND; PNAME: JANICE SMITH - MGR REGULATORY COMP; PHONE: 8068573863; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: CONSTRUCTION; CAULO: 2101MAPLE GAS CORP; CTEST: Null | PIPELINE WAS ACQUIRED FROM TUCO, INC IN 1979 AND NO TEST RECORDS WERE TRANSFERRED AT THE TIME OF ACQUISITION.THIS IS THE PIPELINE WE BELIEVE SHOULD BE CLASSIFIED AS A GATHERING LINE. UNTIL A FINAL DETERMINATION IS MADE ON THE PROPER CLASSIFICATION OF THIS LINE,WE ARE CONTINUING INSPECTION, MAINTENANCE AND RECORDKEEPING FUNCTIONS AS THOUGH THE LINE WERE A TRANSMISSION LINE. THEREFORE WE ARE FILING THIS REPORT.AS I MENTIONED TO YOU, THE LEAK WAS DISCOVERED ON NOVEMBER 25, 1991 AND REPAIRED THE SAME DAY. AT THE TIME THE LEAK WAS DISCOVERED, IT WAS BELIEVED THE GAS LOSS WAS MINIMAL AND NOT OF A REPORTABLE QUANTITY. HOWEVER, WHEN MONTHLY VOLUMES WERE BALANCED, IT APPEARED THAT THE GAS LOSS WAS LARGER THAN ORIGINALLY THOUGHT AND WAS OF A REPORTABLE QUANTITY.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19920018 | 1992-01-22 | 2616 | COLUMBIA GAS TRANSMISSION CORP | WEST FINLEY | GREENE | PA | 15377 |  | 199+90 | 2050 | 1992-01-03 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 105000 | 82236.9985 | 179155.2749 | Null | 0 | 30 |  | 19920104 | 15 | 25 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: PIPE THREAD @ COLLAR; MLKD: OTHER; MLKDO: WROUGHT IRON; PRTSY: PIPELINE; PRTYR: 1898; NMDIA: 8; THK: 0.25; SPEC: UNKNOWN; SMYS: 0; SEAM: UNKNOWN; VALVE: N/A; MANU: UNKNOWN; MANYR: 1898; LOCLK: UNDER GROUND; PNAME: S.J. CHOBY - SR. CODES & STANDARDS ENGINEER; PHONE: 3043572767; PROT: Null; CAULK: EARTH MOVEMENT: SUBSIDENCE; NOTIF: YES; MARK: YES; MRKTP: PLASTIC LINE MARKERS; STAT: YES; CTEST: Null | SUBSTRATE COAL SEAM UNDER EFFECTED AREA WAS NOT MINED. SUBSIDENCE WAS NOT EXPECTED. ACTIVE MINING 1000 FEET AWAY. PIPELINE BROKE IN SCREW COUPLING DUETO LONGWALL MINING SUBSIDENCE. GAS MIGRATED 26 FEET TO HOUSE. EXPLOSION OCCURRED; HOUSE AND VEHICLE DESTROYED. IGNITION SOURCE UNKNOWN.
2021-02-26 10:36 | YES | YES | GG (Gas Gathering) | 19920019 | 1992-01-22 | 14215 | ONEOK EXPLORATION CO | BLANCHARD | MCCLAIN | OK |  |  |  | 915 | 1991-12-14 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 1 | 42200 | 33876.9723 | 73801.7971 | Null | 0 | 50 |  | 19911215 | 725 | 800 | BY CFR 192.619(A)(3) | 1200 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: OTHER; MLKDO: NOT REPORTED; PRTSY: PIPELINE; PRTYR: 1982; NMDIA: 8.63; THK: 0.19; SPEC: X-42; SMYS: 14200; SEAM: EW SMLS.; VALVE: 800 WOG; MANU: NORDSTROM; MANYR: 0; LOCLK: UNDER GROUND; PNAME: GERRY B. LYNN, CHEIF ENGINEER; PHONE: 9185887600; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19911209; MARK: YES; MRKTP: FLAGGED AT CROSSING; STAT: YES; CTEST: Null | LINE LOCATED AND GLAGGED IN 5 AREAS WHERE THE LINE WAS TO BE CROSSED. A PERMANENT CROSSING MARKER WAS WITHIN 60' OF THE POINT WHERE THE LINE WAS HIT. DOZER OPERATOR DEVIATED FROM PREDETERMINED ROUTE, WHICH WAS AGREED UPON BY CONTRACTOR AND ONEOK SERVICES, BY MAKING A LONG RADIUS TURN CHANGING DIRECTION FROM NORTH TO WEST. THE DOZER OPERATOR WAS PLOWING IN TELEPHONE CABLE AND HITTHE GAS LINE WHILE IN A TURN TO CHANGE DIRECTIONS BY 90 DEGREES. DOZER OPERATOR WAS TO TRAVEL PERPENDICULAR TO THE GAS LINE, MOVING NORTH TOWARD THE LINE AND TURNING 90 DEGREES TO TRAVEL WEST PARALLEL TO THE GAS LINE WITHOUT NEEDING TO CROSS OR BE "NEAR" THE GAS LINE.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19920020 | 1992-01-22 | 2616 | COLUMBIA GAS TRANSMISSION CORP | LEESBURG | LOUDOUN | VA | 22075 |  |  | 845 | 1991-12-31 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 1 |  | 19911231 | 855 | 1000 | BY TEST | 1500 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: VALVE; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1971; NMDIA: 6; THK: 0.28; SPEC: API 5L; SMYS: 35000; SEAM: SEAMLESS; VALVE: PILOT LOADED; MANU: U.S. INDUSTRIES, INC; MANYR: 1971; LOCLK: OTHER; LOCLO: VENT PIPE ON ROOF; PNAME: S.J. CHOBY - SR. CODES $ STANDARDS ENGINEER; PHONE: 3043572767; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | CONTRACTOR EMPLOYEE WAS HAMMERING HARD ON ROOF GAS VENT PIPE AND CAUSED A RELIEF DEVICE TO ACTIVATE. THE THRUST, FROM THE UNINTENDED RELEASE OF GAS, THREW THE EMPLOYEE OFF THE ROOF CAUSING INJURY.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19920022 | 1992-02-20 | 11680 | LONE STAR GAS CO | EMORY | RAINS | TX |  |  |  | 1040 | 1992-01-19 |  | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 50 |  | 19920119 | 0 | 0 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: GATHERING SYSTEM; PRTFL: OTHER; PRTFO: NON SPECIFIED; MLKD: OTHER; MLKDO: N/A; PRTSY: PIPELINE; PRTSO: TOWN PLT SYSTEM; PRTYR: 0; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: OTHER; LOCLO: N/A; PNAME: PHILLIP MURDOCH - MANAGER; PHONE: 2146702229; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | GAS CONTAINING HYDROGEN SULFIDE WAS ALLOWED TO ENTER TRANSMISSION SYSTEM.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19920025 | 1992-01-18 | 5304 | FLORIDA GAS TRANSMISSION CO | BROOKER | BRADFORD | FL | 32622 | 548 |  | 236 | 1992-01-20 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 400000 | 313283.8039 | 682496.2853 | Null | 0 | 10 |  | 19920120 | 920 | 975 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | FITTING | FLANGE | OTHER | FLANGE GASKET | COMPRESSOR STATION |  | 1959 | 0 | 0 |  | 0 |  |  |  | 0 | ABOVE GROUND |  | MERLIN H MOSEMAN - COMPLAINCE ENGR | 7138537301 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION | FIBER COMPOSITION FLANGE GASKET | NO |  | NO DATA | 0 | 0 | 0 | THE FLANGE GASKET WHICH DEVELOPED THE LEAK WAS INSTALLED USING A FIBER GASKET AND A SEALER. THE SEALANT MATERIAL DAMAGED THE FIBER GASKET INSTALLATION RESULTING IN A LEAK.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19920026 | 1992-02-20 | 2175 | CENTANA ENERGY CORP | LIBERAL | SEWARD | KS | 67901 |  |  | 1530 | 1991-12-07 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 230000 | 184637.5267 | 402237.283 | Null | 1 | 10 |  | 19911207 | 315 | 400 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1970; NMDIA: 6.63; THK: 0.16; SPEC: API 5L GRADE B; SMYS: 1187; SEAM: ELECTRIC-RESIST; MANYR: 0; LOCLK: UNDER GROUND; PNAME: F O GARRISON - PIPELINE SUPERVISOR; PHONE: 3166261567; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19911202; MARK: YES; MRKTP: MARKER POSTS; STAT: NO; CTEST: Null | ON DECEMBER 02/1991 JIM WHISENNAND, THE OWNER OF J&J OILFIELD SERVICE, PLACEDA ONE-CALL OPERATOR INFORMED MR. WHISENNAND THAT CENTANA ENERGY HAD FACILITIES IN THE AREA WHERE THE LINE RUPTURE OCCURRED ALONG WITH PANHANDLE EASTERN PIPELINE COMPANY (PEPL) AND SOUTHWESTERN BELL. ON DECEMBER 07, 1991 J&J OILFIELD SERVICE STARTED CONSTRUCTION IN THE AREA WHERE THE LINE RUPTURE OCCURRED. NO ONE AT CENTANA IS AWARE OF ANY ATTEMPT BY J&J OILFIELD SERVICE TO CONTACT CENTANA ENERGY CONCERNING FACILITIES IN THIS AREA. THEN AT 3:30 P.M. CENTANA'S 6" LINE WAS HIT AND RUPTURED CAUSING A LEAK AND SHORTLY THEREAFTER A FIR
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19920031 | 1992-01-27 | 13333 | NERCO OIL & GAS INC | GULF OF MEXICO | VERMILION | LA |  |  |  | 1200 | 1992-01-09 |  | YES | VERM | 103 |  | YES | NO | OTHER | 0 | 0 | 0 | 65000 | 50908.6181 | 110905.6464 | Null | 0 | 5 |  | 19920109 | 1200 | 1440 | BY TEST | 2160 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1971; NMDIA: 3.5; THK: 0.25; SPEC: SCH 40; SMYS: 24000; SEAM: SEAMLESS; VALVE: ANSI 600 # VALV; MANYR: 0; LOCLK: UNDER WATER; PNAME: RICHARD L KEELAN - SENIOR SAFETY ENG; PHONE: 7132605656; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: YES; MARK: YES; MRKTP: NOTIFICATION. MARINE SURV; STAT: YES; CTEST: Null | TUG WAS PULLING ANCHORS TO DERRICK BARGE WHEN ANCHOR CABLE RUBBED HOLE IN PIPELINE. DRY GAS ESCAPED. NO POLLUTION. PLATFORM SUPPLYING GAS TO PIPELINE SHUTIN ON PSL. PIPELINE BLEW DOWN IN APPROXIMATELY 45 MINUTES. LINE INSTALLED IN 1971. NOT BURIED. REPAIRED WITH SLEEVE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19920032 | 1992-02-05 | 1734 | BRIDGELINE GAS DISTRIBUTION CO | PARADIS | ST CHARLES | LA | 70080 | O/TEXACO PARADIS PLANT | 0+00 | 1700 | 1992-01-18 | 1 | NO |  |  | LA | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 6 | 0 |  | 19920118 | 416 | 1000 | BY TEST | 1600 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; MLKD: STEEL; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1986; NMDIA: 1; THK: 0.18; SPEC: ASME A105; SMYS: 35000; SEAM: SEAMLESS; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: GARY A GIORDANO - PIPELINE SAFETY COORDINATOR; PHONE: 5045956575; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: Null; MRKTP: 0Y; STAT: Null; CTEST: Null | A TEXACO 4" GAS PIPELINE RUPTURED IN A PIPE RACK AREA OF TEXACO'S PARADIS PLANT AROUND 5:00 O'CLOCK P.M. ON 1/18/92. BRIDGELINE'S LULING SYSTEM SUPPLY REGULATOR STATION IN LOCATED ADJACENT TO WHERE THIS TEXACO 4" PIPELINE RUPTURED. UPON RUPTURING, THE TEXACO 4" PIPELINE WHIPPED INTO A 1" FLANGED CONNECTION ON BRIDGELINE'S LULING SYSTEM PIPING UPSTREAM OF A REGULATOR STATION. THEIMPACT OF THE 4" PIPELINE ON BRIDGELINE'S 1" FLANGED CONNECTION CAUSED A 1" WELDNECK FLANGE TO SPLIT OPEN AND LEAK GAS. BECAUSE THE LOCATION OF THE LEAKON BRIDGELINE'S PIPING WAS UPSTREAM OF THE REGULATOR STATION, SEVERAL PLANT VALVES HAD TO BE CLOSED IN ORDER TO STOP THE GAS FROM LEAKING. BRIDGELINE DECIDED TO REPORT THE LEAKING 1" FLANGED CONNECTION AS AN INCIDENT WHEN IT WAS LEARNED THAT IT WOULD TAKE TIME TO CLOSE ALL OF THE TEXACO PLANT VALVES SUPPLYING GAS TO BRIDGELINE'S LEAKING PIPING. BRIDELINE FELT THAT THIS LEAK WAS SIGNIFICANT AT THE TIME OF THE INITIAL INVESTIGATION BECAUSE IT WAS UNKNOWN WHETHER THE RUPTURED TEXACO 4" LINE HAD CAUSED ANY OTHE DAMAGE TO BRIDGELINE PIPEING.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19920039 | 1992-03-02 | 6243 | GASCO INC | WAIPAHU | HONOLULU | HI | 96797 | STA - 442 + 50 |  | 1530 | 1992-02-10 | 4 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 100000 | 78320.951 | 170624.0713 | Null | 7 | 0 |  | 19920211 | 420 | 500 | BY TEST | 900 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1975; NMDIA: 16; THK: 0.22; SPEC: 5L X-52; SMYS: 52000; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: JON M ARAKAKI - OPERATIONS & MAINTENANCE SUPERVISOR; PHONE: 8085473556; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; MARK: NO; MRKTP: CONTRACTOR WAS TOLD GASCO; STAT: YES; CTEST: Null | CONRACTOR EXCAVATING FOR NEARBY OIL LINE, PUNCTURED GAS LINE WITH TOOTH OF BACKHOE FRONT BUCKET. CONTRACTOR WAS TOLD GASCO WOULD COME OUT THE NEXT DAY.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19920044 | 1992-03-20 | 20245 | UNITED TEXAS TRANSMISSION CO | SEALY | AUSTIN | TX |  | 12.00 | 63+60 | 835 | 1992-02-07 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 30700 | 24044.5319 | 52381.5899 | YES | 1 | 10 |  | 19920207 | 100 | 515 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: NON SPECIFIED; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1950; NMDIA: 4.5; THK: 0.24; SMYS: 24000; SEAM: FURNACE LAP WEL; MANU: BETHLEHEM; MANYR: 0; LOCLK: UNDER WATER; PNAME: PAUL HAAS - REG. COMPLAINCE COOR; PHONE: 7139633243; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | ON FEBRUARY 4, 1992, ENTEX REPORTED A SERVICE INTERRUPTION ON UNITED TEXAS' SEALY 4" (INDEX 90-17). UNITED TEXAS PERSONNEL PATROLLED THE LINE BY AERIAL PATROL AND DETECTED A GAS LEAK IN THE BRAZOS RIVER. EXTENSIVE FLOODING OF THEBRAZOS RIVER WAS THE APPARENT CAUSE OF THE LEAK. ACTUAL DAMAGE TO THE PIPELINE COULD NOT BE DETERMINED. THE PIPELINE CROSSING WAS ABANDONED IN PLACE AND GAS WAS REROUTED THROUGH OTHER SOURCES TO RESTORE SERVICE TO ENTEX.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19920053 | 1992-03-23 | 11680 | LONE STAR GAS CO | RIESEL | MCLENNAN | TX |  | 3 | 233+54 | 2200 | 1992-01-22 | 3 | NO |  |  |  | Null | NO | RUPTURE | 1 | 0 | 0 | 68117 | 53349.8822 | 116223.9987 | Null | 2 | 34 |  | 19920122 | 500 | 0 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1952; NMDIA: 12; THK: 0.25; SPEC: GRADE B; SMYS: 35000; SEAM: EW SMLS; MANYR: 0; LOCLK: UNDER GROUND; PNAME: PHILLIP MURDOCK - MANAGER; PHONE: 2146702229; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: COOL WEATHER/EXCESSIV RAI; NOTIF: NO; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | IT IS BELIEVED THAT COOL WEATHER AND EXCESSIVE RAIN CAUSED PIPE TO BREAK.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19920061 | 1992-04-13 | 19160 | TENNESSEE GAS PIPELINE CO | WHITE BLUFF | DICKSON | TN |  | M.P. 82-2+11.93 |  | 900 | 1992-03-15 | 2 | NO |  |  |  | Null | NO | RUPTURE | 0 | 0 | 2 | 4000000 | 3132838.0386 | 6824962.8529 | Null | 2 | 30 |  | 19920315 | 720 | 750 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: UNDETERMINED; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1948; NMDIA: 26; THK: 0.38; SPEC: API-5L; SMYS: 45000; SEAM: FLASH BUTT; MANU: A.O. SMITH; MANYR: 1947; LOCLK: UNDER GROUND; PNAME: G R ABEL; PHONE: 7137572408; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | PIPELINE RUPTURED AT CROSSOVER PIPING, CAUSING A FIRE NEAR ROAD CROSSING ANDRUPTURING UPSTREAM AND DOWNSTREAM BLOW OFFS AND CROSSOVERS.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19920062 | 1992-04-13 | 20230 | UNITED GAS PIPELINE CO | DELTA | MADISON | LA |  | 72.2 | 3811+88 | 910 | 1992-03-10 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 1 | 2 | 100000 | 78320.951 | 170624.0713 | Null | 1 | 15 |  | 19920310 | 350 | 475 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: MECHANICAL JOINT; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1939; NMDIA: 18; THK: 0.25; SMYS: 35000; SEAM: SEAMLESS; MANU: NATIONAL; MANYR: 0; LOCLK: OTHER; LOCLO: OPEN DITCH; PNAME: W F ST GERMAIN - SR P.L. SAF. ANALYST; PHONE: 7132295772; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | PIPELINE CREW INSTALLING WELDOVER SLEEVE OVER MECHANICAL COUPLING AT THE TIME OF THE INCIDENT. CONTRIBUTING FACTORS UNKNOWN AT THIS TIME.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19920068 | 1992-05-08 | 20040 | UNION CARBIDE CORP | TEXAS CITY | GALVESTON | TX | 77592 | GRANT ROAD & 5TH AVE |  | 1630 | 1992-04-05 | 2 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 5 | 20 |  | 19920407 | 450 | 720 | BY TEST | 1080 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: GASKET, GUAGE; MLKD: OTHER; MLKDO: NON SPECIFIED; PRTSY: PIPELINE; PRTSO: VALVE; PRTYR: 1979; NMDIA: 4; THK: 0.18; SPEC: AP1-5L; SMYS: 35000; SEAM: ERW; VALVE: GATE 300#; MANU: CRANE; MANYR: 1979; LOCLK: ABOVE GROUND; PNAME: ROBERT A POWNALL - ASSO PROJECT MANAGER; PHONE: 7168797055; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | INCIDENT AND FIRE AT ADJACENT METER DAMAGED GASKETS AND GAUGE AT ABOVE GROUND VALVE RESULTING IN PRODUCT LEAKAGE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19920070 | 1992-04-30 | 8200 | INTRATEX GAS CO | FRELSBURG | COLORADO | TX | 78950 | 81.5 | 4305+98 | 2100 | 1992-04-10 | 1 | NO |  |  |  | Null | YES | LEAK | 0 | 0 | 0 | 140500 | 110040.9361 | 239726.8202 | Null | 0 | 0 |  | 19920410 | 850 | 1050 | BY TEST | 1345 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: VALVE; MLKD: OTHER; MLKDO: VITON; PRTSY: PIPELINE; PRTYR: 1970; NMDIA: 8; THK: 0; SPEC: API 6-D; SMYS: 0; VALVE: WXF GATE VALVE; MANU: M&J VALVE CO; MANYR: 1970; LOCLK: ABOVE GROUND; PNAME: TILFORD N VIK - CODE COMPLIANCE ENG; PHONE: 7138537329; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | MINOR GAS LEAKAGE AT TWO LOCATIONS ON 8" BLOWDOWN VALVES - STEM SEAL AND FLANGE SURFACE BETWEEN BONNET AND MAIN VALVE BODY.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19920073 | 1992-04-27 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA | OTOE | OTOE | NE |  | 533 | 23780 + 35 | 1300 | 1992-03-18 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 50000 | 39160.4755 | 85312.0357 | Null | 0 | 30 |  | 19920318 | 550 | 712 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1942 | 26 | 0.25 | 5LX | 52000 | FLASH WELD |  | A O SMITH | 1942 | OTHER | CASED RR CROSSING | F ROY FLEET - SENOIR ENGINEER | 7086913786 | EXTERNALLY | LOCALIZED PITTING |  | OTHER | ATMOSPHERE | COATED | YES | 1942 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | THE LEAKING SEGMENT OF PIPE WAS REMOVED AND REPLACED WIHT PRETESTED PIPE ANDRETURNED TO SERVICE ON APRIL 15.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19920079 | 1992-05-21 | 2899 | CROSSTEX PIPELINE CO | MARSHALL | HARRISON | TX | 75670 |  |  | 1800 | 1992-04-20 | 2 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 100000 | 78320.951 | 170624.0713 | Null | 0 | 50 |  | 19920511 | 700 | 1000 | BY TEST | 1250 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: GATHERING SYSTEM; PRTFL: OTHER; PRTFO: ENGINE; MLKD: OTHER; MLKDO: ALUMINIUM ALLOYS; PRTSY: COMPRESSOR STATION; PRTYR: 1991; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: PHILIP C PONGETTI - FACILITIES SUPT.; PHONE: 9035347466; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | AN ENGINE ON ONE OF THE BOOSTER COMPRESSORS CAUGHT FIRE. THE HEAT OF THE FIRE MELTED THE FUEL GAS REGULATORS CAUSING FUEL GAS TO FURTHER FUEL THE FIRE. DAMAGE WAS TOO EXTENSIVE TO DRAW ACCURATE CONCLUSIONS.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19920081 | 1992-05-18 | 7605 | HOUSTON PIPELINE CO | TEXAS CITY | GALVESTON | TX | 77590 |  |  | 1830 | 1992-04-05 | 3 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 102000 | 79887.37 | 174036.5527 | Null | 3 | 40 |  | 19920405 | 400 | 545 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: GASKETS; MLKD: OTHER; MLKDO: COMPRESSED ASBESTOS; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1986; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: TILFORD N VIK - CODE COMPLAINCE ENGR; PHONE: 7138537329; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | THE COMBUSTION OF A LIQUID MATERIAL LOCATED IN A ROAD DITCH ADJACENT TO THE M
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19920082 | 1992-05-19 | 18646 | STINGRAY PIPELINE CO |  |  | LA |  |  |  | 1700 | 1992-04-16 |  | YES | EAST CAMERON | 322 |  | Null | NO | LEAK | 0 | 0 | 0 | 53100 | 41588.425 | 90601.3819 | Null | 0 | 0 |  | 19920416 | 850 | 1200 | BY TEST | 1800 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1983 | 6 | 0.344 | 5LX | 52000 |  |  | REPUBLIC | 1983 | UNDER WATER |  | F ROY FLEET - SR ENGINEER | 7086913786 | INTERNALLY | LOCALIZED PITTING |  | OTHER | UNKNOWN | COATED | YES | 1983 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19920083 | 1992-05-05 | 10030 | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | STERLING | LOGAN | CO | 80751 |  | 3421+65 | 1430 | 1992-04-23 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 0 |  | 19920423 | 540 | 800 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: MEAS. STA. & VALVE SET; MLKD: STEEL; PRTSY: OTHER; PRTSO: MEAS. STA. & VALVE SET; PRTYR: 1978; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: STEVE HAWES - CONSTR & STDS COMPL SPEC; PHONE: 4024622141; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: MEASURING; STAT: Null; CTEST: Null | PRODUCER DISCONNECTED WELL LINE FROM METER RUN SO IT COULD RUN PIG AND ALCOHOL THROUGH LINE TO LOWER DEWPOINTS. PRODUCSER'S LINE WAS OPEN TO ATMOSPHERE AND POINTING TOWARD K N METER RUN. WHEN PIG EXITED LINE, IT SOME HOW IGNITEDGAS. THE RESULTING FIRE BURNED THROUGH GASKETS AND ALLOWED MAINLINE GAS TO CATCH ON FIRE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19920084 | 1992-05-13 | 1472 | BLACK MARLIN PIPELINE CO | TEXAS CITY | GALVESTON | TX | 77590 |  |  | 1830 | 1992-04-05 | 3 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 216000 | 169173.2541 | 368547.9941 | Null | 3 | 40 |  | 19920405 | 700 | 947 | BY TEST | 1420 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: GASKET; MLKD: OTHER; MLKDO: COMPRESSED ASBESTOS; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1986; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: TILFORD N VIK - CODE COMPLAINCE ENGR; PHONE: 7138537329; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | THE COMBUSTION OF A LIQUID MATERIAL LOCATED ON A ROAD DITCH ADJACENT TO THE METER STATION APPEARS TO HAVE ALLOWED NATURAL GAS LEAKAGE AT THE FLANGED JOINTS DUE TO EXCESSIVE HEATING.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19920086 | 1992-05-11 | 2616 | COLUMBIA GAS TRANSMISSION CORP | PERKINS | GILMER | WV |  |  | 655+25 | 1410 | 1992-04-14 | 1 | NO |  |  |  | Null | NO | RUPTURE | 62 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 45 |  | 19920414 | 860 | 943 | BY TEST | 1190 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | WELD | LONGITUDINAL | STEEL |  | PIPELINE |  | 1947 | 20 | 0.31 | API5LX | 42000 | ELECTRIC RESIST |  | YOUNGSTOWN SHEET & TUBE | 1947 | UNDER GROUND |  | S J CHOBY SR - CODES & STANDARDS ENGR | 3043572349 | EXTERNALLY | OTHER | SELECTIVE SEAM CORROSION | GALVANIC |  | BARE | YES | 1960 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | INVESTIGATION REVEALED THAT A 62' SEGMENT OF OPERATOR'S LINE TM-7 WAS DAMAGED RESULTING FROM 1 43' RUPTURE ATTRIBUTED TO SELECTIVE SEAM CORROSION.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19920088 | 1992-05-22 | 19160 | TENNESSEE GAS PIPELINE CO | GULF OF MEXICO |  | LA |  | 509A-401+0.01 |  | 1500 | 1992-04-21 |  | YES | VER | 281 |  | YES | NO | LEAK | 0 | 0 | 0 | 125000 | 97901.1887 | 213280.0892 | YES | 0 | 0 |  | 19920421 | 1100 | 1440 | BY TEST | 2312 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | FITTING | 16" TEE | STEEL |  | PIPELINE |  | 1973 | 16 | 0.5 | MSS-SP-75 | 52000 |  |  |  | 0 | UNDER WATER |  | L A SALINAS | 7137572781 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | WELD TEE | Null | 19730605 | WATER |  | 4 | 2165 | LEAK OCCURRED IN TEE FITTING
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19920089 | 1992-05-22 | 19160 | TENNESSEE GAS PIPELINE CO | SARDIS | PANOLA | MS |  | 64-2+6.71 | 354+07 | 1945 | 1992-04-21 | 1 | NO |  |  |  | Null | NO | RUPTURE | 0 | 0 | 0 | 98000 | 76754.5319 | 167211.5899 | Null | 3 | 45 |  | 19920421 | 718 | 750 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: UNDETERMINED; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1948; NMDIA: 26; THK: 0.28; SPEC: API-5L; SMYS: 52000; SEAM: FLASH BUTT; MANU: A O SMITH; MANYR: 1948; LOCLK: UNDER GROUND; PNAME: L A SALINAS; PHONE: 7137572781; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | CAUSE UNKNOWN UNDER INVESTIGATION. RUPTURE WITH NO FIRE ON 100-2 LINE IN WRINKLE BEND UPSTREAM OF HWY. 315 CASED CROSSING.
2021-02-26 10:36 | YES | YES | GG (Gas Gathering) | 19920093 | 1992-06-30 | 22476 | WESTERN KENTUCKY GAS CO | HAWESVILLE | HANCOCK | KY | 42348 |  |  | 1419 | 1992-06-01 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 1 | 2000 | 1566.419 | 3412.4814 | YES | 1 | 0 |  | 19920601 | 240 | 320 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: GATHERING SYSTEM; PRTFL: OTHER; PRTFO: NIPPLE; MLKD: STEEL; PRTSY: OTHER; PRTSO: WELLHEAD; PRTYR: 1963; NMDIA: 0.75; THK: 0.11; SPEC: API 5L GRADE B; SMYS: 36000; SEAM: SEAMLESS; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: KEVIN AKERS - ENGINEER; PHONE: 5026858026; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: ABOVE GROUND EQUIPMENT; STAT: NO; CTEST: Null | UNDERGROUND GAS STORAGE WELLHEAD 3/4" LINE STRUCK BY A TRACTOR CAUSING A NIPPLE TO BREAK AND RELEASE GAS. THE GAS IGNITED CAUSING DRIVER TO SUSTAIN BURNS
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19920103 | 1992-07-23 | 3183 | DECATUR UTILITIES - DECATUR GAS DEPARTMENT | HILLSBORO | LAWRENCE | AL |  | 60.2 (US HWY 20) |  | 1755 | 1992-06-24 | 2 | NO |  |  | AL | Null | NO | RUPTURE | 0.5 | 0 | 1 | 200000 | 156641.9019 | 341248.1426 | Null | 0 | 37 |  | 19920624 | 65 | 667 | BY TEST | 1000 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1979; NMDIA: 10; THK: 0.19; SPEC: API-5LX; SMYS: 42000; SEAM: ELECTRIC RESIST; MANU: REPUBLIC STEEL; MANYR: 1979; LOCLK: UNDER WATER; PNAME: KEM CARR - CHIEF ENGINEERING/OPERATING MGR; PHONE: 2055521451; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; MARK: YES; MRKTP: FLAGGING AND PAINT; STAT: Null; CTEST: Null | CONSTOCK COMMUNICATIONS, INC. A CONTRACTOR INSTALLING FIBER OPTICS CABLE FOR SOUTHCENTRAL BELL, HIT AND RUPTURED DECATUR UTILITIES' 10 INCH GAS MAIN AT APPROXIMATELY 17:55 JUNE 24, 1992. THE RUPTURE OCCURRED AT A STREAM CROSSING(FOXES CREEK ALONG U.S. HIGHWAY 20 IN THE HILLSBORO AREA. THE RUPTURE WAS DUE TO THE CROSSING, SINKING AND LOADING OF THE CONTRACTOR'S LARGE DOZIER (KOMATSU D85) ONTO THE 1- INCH STEEL GAS MAIN. THE DOZIER AND TWO BACKHOES (CATERPILLAR 416 AND CASE 580 E) WERE BURNED AFTER THE GAS IGNITED. THE OPERATOR OF THE DOZIER WAS ALSO BURNED. THE BACKHOES WERE APPARENTLY TRYING TO FREE THE DOZIER THAT WAS STUCK. BARLIER IN THE DAY (6.24.92, 10:00 A.M. -12:30 P.M.), KEM CARR MET WITH COMSTOCK PESONNEL (JERRY EDWARDS, MIKE EAVES, CONSTRUCTION CREW), SOUTH CENTRAL BELL (RONNY HICKOK, ANOTHER REPRESENTATIVE), HIGHWAYDEPARTMENT (MR. WHITE, ANOTHER MAINTENANCE MAN) CONCERNING THEIR INSTALLATION OF FIBER OPTICS CABLE AND CONFLICTS WITH OUR GAS MAIN. COMSTOCK HAD HIT OUR 10" GAS MAIN THE DAY BEFORE (6/23/92, 4:00 P.M.) CAUSING A RUPTURE AND GAS RELEASE. THEIR DOZIER HAD SUNK AND RUPTURED OUR GAS MAIN IN MUCH THE SAME MANNER AS ON THE 24TH. MR. CARR DESCRIBED THE DANGER IN THE CONSTRUCTION METHODS, THEIR LACK OF COOPERATION AND COMMUNICATION AND THEIR APPARENT LACK OF REGARD FOR OUR GAS FACILITIES. IT WAS AGREED BY THOSE IN THE MEETING INCLUDINGCOMSTOCK PERSONNEL THAT COMSTOCK WOULD STAY A MINIMUM OF 3 FEET AWAY FROM OUR GAS FACILITIES. IT WAS AGREED BY THOSE IN THE MEETING INCLUDING COSNTOCK PERSONNEL THAT COMSTOCK WOULD STAY A MINIMUM OF 3 FEET AWAY FROM OUR GAS MAIN THEY WERE TO NOTIFY DU IMMEDIATELY AND NOT PROCEED UNTIL WE HAD AGREED ON AN ACCEPTABLE INSTALLATION METHOD. IF CONDITIONS PREVENTED THEM FROM PLOWING THE CABLE IN AND MAINTAINING THE REQUIRED SEPARATIONS FROM OUR GAS MAIN, THEY WERE TO USE TRENCHING, BACKHOES OR OTHER METHODS TO KEEP THE DOZIER OFF THE GAS MAIN.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19920109 | 1992-07-20 | 19160 | TENNESSEE GAS PIPELINE CO | PLAQUEMINES PARISH |  | LA |  | M.P. 525-2+10.87 |  | 2330 | 1992-06-16 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 250000 | 195802.3774 | 426560.1783 | Null | 0 | 0 |  | 19920617 | 870 | 1000 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: UNDETERMINED; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1966; NMDIA: 36; THK: 0.63; SPEC: API-5LX; SMYS: 60000; SEAM: SAW; MANU: U.S. STELL; MANYR: 1966; LOCLK: UNDER WATER; PNAME: L A SALINAS; PHONE: 7137572781; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | LEAK AT INTERSECTION OF SIDE VALVE ASSEMBLY 525C-101.2. LEAK WAS NOT CONDSIDERED A HAZARD
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19920111 | 1992-07-13 | 18484 | SOUTHERN CALIFORNIA GAS CO | SOUTH GATE | LOS ANGELES | CA | 90280 | 195.17 | 103+21 | 630 | 1992-06-17 | 3 | NO |  |  | CA | Null | NO | OTHER | 0 | 0 | 1 | 300 | 234.9629 | 511.8722 | Null | 0 | 3 |  | 19920618 | 346 | 425 | BY TEST | 1400 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: HOSE; MLKD: OTHER; MLKDO: RUBBER; PRTSY: OTHER; PRTSO: FIRE CONTROL STACK; PRTYR: 0; NMDIA: 2; THK: 0; SMYS: 0; MANU: BOSTON OTTER; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: GARY J LAMBERT - MANAGER, SAFETY; PHONE: 2132441200; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | CREW MEMBERS OVERPRESSURED A TWO-INCH RUBBER HOSE ASSEMBLY, CAUSING IT TO SEPARATE AND STRIKE THREE PEOPLE. HOSE RATING AND MAOP UNKNOWN. ONN JUNE 17,1992 AT APPROXIMATELY 6:30 A.M., GAS COMPANY EMPOYEES BEGAN BLOWING DOWN A SIX-FOOT SECTION OF LINE 765 THROUGH A TWO-INCH RUBBER HOSE ASSEMBLY TO A FREESTANDING FIRE CONTROL STACK LOCATED OUTSIDE THE EXCAVATION. THE HOSE ASSEMBLYSEPARATED AT THE FIRE CONTROL STACK END AFTER BEING OVERPRESSURRED. THE HOSE STRUCK THREE PEOPLE BEFORE BREAKING OFF AT THE INLET AND IT WAS APPROXIAMTELY FORTY SECONDS BEFORE IT WAS BROUGHT UNDER CONTROL BY CLOSURE OF THE INLET VALVE. TWO GAS COMPANY EMPLOYEES AND ONE CONTRACT INSPECTOR WEREINJURED. THE CONTRACT INSPECTOR'S INJURIES NECESSITATED INPATIENT HOSPITALIZATION. NO CUSTOMERS WERE AFFECTED NOR WERE THERE ANY FIRES ASSOCIATED WITH THIS INCIDENT. ESIMATED COSTS ASSOCIATED WITH INCIDENT WERE $300.00. DOT NOTIFICATION 06/18/92, REFERENCE REPORT #122500.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19920112 | 1992-07-13 | 4280 | EL PASO NATURAL GAS CO | CIBOLA |  | NM |  | 296.3 |  | 1938 | 1992-06-15 | 1 | NO |  |  |  | Null | NO | RUPTURE | 63 | 0 | 0 | 135708 | 106287.7961 | 231550.5147 | Null | 0 | 52 |  | 19920615 | 808 | 836 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | WELD | LONGITUDINAL | STEEL |  | PIPELINE |  | 1953 | 30 | 0.34 | API 5 L X | 52000 | EFW |  | A O SMITH | 1953 | UNDER GROUND |  | RICHARD FAVILA - SENIOR ENGINEER | 9155412862 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1953 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | WELD SEAM CORROSION AND THE DEVELOPMENT OF A NARROW OR CRACK-LIKE CORROSION PENETRATION IN THE EFW SEAM CAUSED THE PIPELINE TO RUPTURE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19920114 | 1992-08-07 | 405 | ANR PIPELINE CO | U S FEDERAL WATERS | (OFFSHORE) | LA |  | X= 1,861,757.91 | Y= -66,342.50 | 2115 | 1992-07-09 |  | YES | E.I | 266E |  | YES | NO | LEAK | 0 | 0 | 0 | 921400 | 721649.2422 | 1572130.1932 | Null | 0 | 0 |  | 19920709 | 830 | 1250 | BY TEST | 2690 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1970 | 12.75 | 0.38 | API-5LX | 46000 | ERW |  | AMERICAN STEEL | 1970 | UNDER WATER |  | DONALD E CROSS | 3134962460 | INTERNALLY | LOCALIZED PITTING |  | OTHER | NON SPECIFIED | COATED | YES | 1970 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19920118 | 1992-08-10 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA | TRURO | WARREN | IA | 50257 |  |  | 38 | 1992-07-05 | 1 | NO |  |  |  | Null | Null | OTHER | 0 | 0 | 0 | 90000 | 70488.8559 | 153561.6642 | Null | 1 | 0 |  | 19920705 | 550 | 712 | BY TEST | 1068 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: PROCEDURE; MLKD: OTHER; MLKDO: NON SPECIFIED; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1985; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: E ROY FLEET SENIOR ENGINEEE; PHONE: 7086913786; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | FOLLOWING A PROCEDURE TO RESTORE SERVICE AT HIS BLOWNDOWN STATION, AN OPERATOR ACTIVATED THE VALVE CONTROL PANEL WHILE THE BLOWDOWN VALVES WERE BEING RESET. GAS VENTED THROUGH 4 OF THE 6 BLOWDOWN VALVES.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19920120 | 1992-07-31 | 19570 | TRANSCO GAS PIPELINE CORP | OFFSHORE VERMILION |  | LA |  | 0.549 | 28 + 97 | 915 | 1992-07-02 |  | YES | VERM | 67 |  | YES | NO | LEAK | 0 | 0 | 0 | 53500 | 41901.7088 | 91283.8782 | Null | 4 | 20 |  | 19920702 | 740 | 1168 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | GIRTH | STEEL |  | PIPELINE |  | 1958 | 16 | 0.31 | API-5LX | 52000 | FLASH WELD |  | A.O. SMITH | 1958 | UNDER WATER |  | R R LANDES - STAFF COMPLAINCE ANALYST | 7134392001 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION | GIRTH WELD | YES |  | NO DATA |  | 0 | 0 | BUBBLES WERE OBSERVED BY TRANSCO PERSONNEL IN THE VICINITY OF TRANSCONTINENTAL GAS PIPE LINE CORPORATION'S PIPELINE WHILE FLYING OFFSHORE. DIVERS WERE DISPATCHED AND CONFIRMED THAT THE LEAK WAS A PINHOLE (3/16") IN THE 6 O'CLOCK POSITION IN A GIRTH WELD ON T.G.P.L.'S 16" PIPELINE IN VERMILION 67. THE PIPELINE WAS BLOWN DOWN AND THE REPAIR CLAMP WAS INSTALLED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19920121 | 1992-07-29 | 13750 | NORTHERN NATURAL GAS CO (ENRON) | BURDETT | PAWNEE | KS | 67523 | 6.9(M.P) | 365+70 | 1030 | 1992-07-13 | 1 | NO |  |  |  | Null | NO | RUPTURE | 30 | 0 | 0 | 107000 | 83803.4175 | 182567.7563 | Null | 1 | 50 |  | 19920713 | 837 | 870 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1950 | 20 | 0.28 | API 5LX | 49000 | SEAMLESS |  | NATIONAL TUBE | 1950 | UNDER GROUND |  | ANTHONY R ROCK - COMPLIANCE ENGR | 7136467346 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | COATED | YES | 1950 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19920122 | 1992-08-10 | 12270 | M I G C INC | GILLETTE | CAMPBELL | WY | 82717 |  |  | 1330 | 1992-08-03 | 1 | NO |  |  |  | Null | NO | RUPTURE | 0 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 30 |  | 19920803 | 540 | 700 | BY TEST | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1969; NMDIA: 8.63; THK: 1.25; SPEC: X 42; SMYS: 0; SEAM: ERW; MANU: NIPPON; MANYR: 1969; LOCLK: UNDER GROUND; PNAME: R F BECK - TRANSMISSION SUPT.; PHONE: 3076829710; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | STRESS ON LINE AT END OF CASING CAUSED RUPTURE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19920125 | 1992-08-24 | 12582 | MISSISSIPPI VALLEY GAS | AMORY | MONROE | MS | 38821 |  | 1039+00 | 545 | 1990-12-23 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 536693 | 446200.1267 | 972057.6844 | Null | 1 | 30 |  |  | 325 | 385 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: GIRTH; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1930; NMDIA: 8; THK: 0.25; SMYS: 0; SEAM: ERW; MANYR: 0; LOCLK: UNDER WATER; PNAME: JOE J POWELL JR. - VP TECHNICAL SERVICES; PHONE: 6019616853; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | ONE LINE IN A DUAL 8" RIVER CROSSING BROKE IN A WELD AFTER BEING UNDERMINED BY FLOOD WATERS AND SUBJECTED TO FORCE OF RUSHING WATER, COLLECTED DEBRIS ANDWEIGHT OF PIPE IN THE RESULTING UNSUPPORTED SPAN. GAS SERVICES WAS LOST TO ABOUT 12,000 CUSTOMERS DOWNSTREAM. THE BROKEN CROSSING WAS TAKEN OUT OF SERVICE AND THE INTACT CROSSING INSPECTED. IT WAS ALSO UNDERMINED TO THE EXTENT THAT REPLACEMENT OF BOTH LINES RATHER THAN REPAIR OF INTACT LINE WAS DEEMED APPROPRIATE. TEMPORARY BY-PASSES WERE CONSTRUCTED TO ALLOW RESTORATION OF SERVICE AND A SINGLE 12" CROSSINGG WAS ULTIMATELY INSTALLED. THE LEAKING GAS CAUSED NO DAMAGE. THE COST OF THE LOST GAS AND THE GAS USED TO KEEP PRESSURE ON THE INTACT CROSSING UNTIL VALES ON BOTH HEADERS COULD BE CLOSED WAS $25,682. THE COST OF TEMPORARY BYPASSES AND RESTORATION OF SERVICE TO 12,000 CUSTOMERS WAS $284,710. THE COST OF THE NEW CROSSING AND OTHER IMPROVEMENTS WAS $226,301. ORDER 21002 STATES THAT ALL OF THE ABOVE COSTS ARE PROPERTY DAMAGE AND THAT THIS INCIDENT REPORT MUST BE MADE FOR THAT REASON EVEN THOUGH THE ESCAPING GAS WAS NOT THE CAUSE OF THE DAMAGE BUT WAS A RESULT OF THE CROSSING BYTHE WASHOUT ALSO NECESSITATED THE TEMPORARY BYPASSES, RESTORATION OF SERVICE TO CUSTOMERS AND REPLACEMENT OF CROSSING. IN USING THIS INCIDENT REPORT FOR STATISTICAL REPORTING, IT WOULD BE INCORRECT TO ATTRIBUTE ANY OF ANY OF THESE COSTS TO DAMAGE BY A GAS LEAK.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19920132 | 1992-08-31 | 25103 | FERGUSON-BURLESON COUNTY GAS GATHERING SYSTEM | COLLEGE STATION | BRAZOS | TX | 77845 | STEEPHOLLOW 5 COMP STATIO | AUGUSTUS WILLIAMS A-58 | 930 | 1992-08-02 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 500000 | 391604.7548 | 853120.3566 | YES | 1 | 0 |  | 19920802 | 800 | 1000 | BY TEST | 1500 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | GATHERING SYSTEM | WELD | NON SPECIFIED | OTHER | NON SPECIFIED | COMPRESSOR STATION |  | 1992 | 0 | 0 |  | 0 |  |  |  | 0 | OTHER | NON SPECIFIED | MICHEAL HOWETH | 8173251321 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | SECOND STAGE VALVE HEAD BOLTS | Null |  | NO DATA |  | 0 | 0 | JGM ARIEL THREE (3) STAGE NATURAL GAS COMPRESSOR PART OF A RURAL NATURAL GASGATHERING SYSTEM HAD A FAILURE RELEASING NATURAL GAS TO THE ATMOSPHERE AND INGNITED CAUSING THE COMPRESSOR TO BURN. THIS UNIT WAS STARTED ON 4-16-92. THE RESULTS OF THE METALURGICAL ANALYSIS MAY REVEAL MORE FACTS THAT WILL HELP DETERMINE THE CAUSE OF THE INCIDENT, REPORT NUMBER 130311.ON AUGUST 2, 1992 FERGUSON-BURLESON COUNTY GAS GATHERING SYSTEM, A SUBSIDIARY OF SOUTHWESTERN GAS PIPELINE, INC., EXPERIENCE A FIRE AT AN UNATTENDED FIELD GAS GATHERING COMPRESSOR SITE KNOWN AS THE STEEPHOLLOW #5, LOCATED ON BIRD POND RD APPROXIMATELY 3 MILES WEST OF HWY 30 AND 3.5 MILES SOUTH SOUTHEAST OFCOLLEGE STATION, TEXAS IN BRAZOS COUNTY. THE INCIDENT WAS DISCOVERED AT 9:30AM AND WAS REPORTED TO THE 24 HOUR EMERGENCY NUMBER AT 10:40 AM. THIS NOTIFICATION WAS MADE DUE TO THE AREA WHERE THE INCIDENT OCCURRED AND THE ESTIMATED DOLLAR AMOUNT OF DAMAGE. THE STEEPHPLLOW #5 COMPRESSOR SITE IS LOCATED IN A RURAL, CLASS 1 LOCATION APPROXIMATELY 2 MILES FROM A DWELLING INTENDED FOR HUMAN OCCUPANCY. THERE WERE NO PERSONNEL INJURED OR KILLED. THE FIRE WAS CONTAINED BY 10:30 AM AND THE REMAINING COMPRESSORS WERE BACK IN OPERATION BY 2:30 PM. THERE WAS NO LOSS OF GAS SERVICE SINCE THE SUBJECT GATHERING LINE SERVES ANOTHER PART OF THE OPERATORS GAS PROCESSING FACILITIES DOWNSTREAM OF THIS LOCATION. THE ESTIMATED PROPERTY DAMAGE IS $500,000.00. THIS IS A REPLACEMENT COST OF THE COMPRESSOR AND A $1,000.00 VALUE OF THE GAS LOST. THE COSTESTIMATE WAS DETERMINED THE DAY AFTER THE INCIDENT, THEREFORE, THIS INCIDENTWAS REPORTED TO THE NTSB EMERGENCY RESPONSE CENTER ON TUESDAY, AUHUST 4, 1992. MR. CHUCK KOVALL ASSIGNED THE RSPA INCIDENT REPORT NUMBER, 130311, AT THAT TIME. SHORTLY AFTER REPORTING THE INCIDENT TO THE NTSB IN WASHINGTON, MR. R.G. (BOB) HOLTER WITH THE RSPA IN HOUSTON CALLED AND I REPORTED THE CHAIN OF EVENTS AND SPECIFIC DETAILS TO HIM. MR. HOLTER INDICATED TO ME THAT SINCENO ONE WAS INJURED OR KILLED, THE GENERAL PUBLIC WAS NOT AFFECTED, THE FACILITIES ARE INTRASTATE AND ARE RURAL GATHERING, HE DID NOT BELIEVE HIS SUPERVISORS WOULD HAVE HIM INVESTIGATE. I INFORMED MR. HOLTER THAT THE INCIDENT HADBEEN REPORTED TO THE RAILROAD COMMISSION AT THE TIME OF THE INCIDENT AND MR.DANNY NICHOLS, ENGINEERING TECHNICIAN, FROM THE RRC'S HOUSTON OFFICE INVESTIGATED THE INCIDENT ON SITE. AFTER A THOROUGH INVESTIGATION OF THE EQUIPMENT,IT APPEARS THAT A VALVE COVER HAD BLOWN OFF, SHEARING THE BOLTS THAT HELD ITON THE SECOND STAGE CYLINDER RELEASING GAS TO THE ATMOSPHERE. THIS COULD HAVE BEEN THE SOURCE OF IGNITION, HOWEVER, THE ACTUAL SOURCE HAS NOT ACTUALLY BEEN DETERMINED. FERGUSON-BURLESON'S INSURANCE CARRIER REQUESTED THAT THE COMPRESSOR PACKAGE ASSEMBLER TAKE THE UNIT TO THEIR SHOP AND DISASSEMBLE IT TO TDETERMINE WHAT IF ANYTHING IS SALVAGEABLE, WHICH WILL HAVE A DIRECT AFFECT ON THE ACTUAL COST OF REPLACEMENT. THE SHEARED BOLTS HAVE BEEN SENT TO A METALURHIST'S FOR ANALYSIS, THE RESULTS OF WHICH HAVE NOT YET BEEN RECIEVED. SHOULD THE RESULTS OF THESE EXAMINATIONS CHANGE THE COST ESTIMATE SIGNIFICANTLY AND THE METALURGIST'S REPORT REVEAL SOMETHING NEW, A SUPPLEMENTAL REPORT WILL BE COMPLETED AND FORWARDED PROMPTLY. THE DAMAGED COMPRESSR UNIT IS BEING PREPARED FOR SHIPMENT TO THE PACKAGER FOR INSPECTION ON AUGUST 19, 1992, TO BESHIPPED AS SOON AS POSSIBLE.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19920133 | 1992-08-31 | 15083 | PALO DURO PIPELINE CO | WHEELER | WHEELER | TX | 79079 | 0.00 | 0 + 00 | 705 | 1992-07-21 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 5 |  |  | 760 | 1440 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: VALVE ASSEMBLY; MLKD: STEEL; PRTSY: OTHER; PRTSO: SEPARATOR; PRTYR: 1979; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: CONRANH; PHONE: 7139633230; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | THE INCIDENT OCCURRED ON JULY 21 DURING SCHEDULED ROUTINE MAINTENANCE. A TWO(2) INCH VALVE ASSEMBLY USED TO BLOWDOWN A VERTICAL SEPARATOR BECAME DISCONNEDTED FROM THE THREADED NOZZLE OM THE SEPARATOR. THE FORCE OF THE BLOWDOEN GAS ROTATED THE VALVE ASSEMBLY COUNTER-CLOCKWISE, THEREBY LOOSENING THE THREADED CONNECTION. THE FORCE OF THE RELEASED GAS KNOCKED BOTH EMPLOYEES ON THE AREA TO THE GROUND. ONE EMPLOYEE REQUIRED INPATIENT HOSPITALIZATION. THE OTHER EMPLOYEE WAS TREATED FOR MINOR INJURIES AND RELEASED. SUPPL. REPORT4/7/1995 INDICATES THAT THE INCIDENT IS STILL UNDER INVESTIGATION AND ISCURRENTLY THE SUBJECT OF LITIGATION. (REQUESTED TO RECLASSIFY CAUSE OFINCIDENT). IF NATURAL'S COMPLETED INVESTIGATION INDICATES THATRECLASSIFICATION IS APPROPRIATE, NATURAL WILL FILE A SUPPL. REPORT (F.ROYFLEET 708-691-3786)
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19920134 | 1992-08-31 | 11683 | LONE STAR GAS CO OF TEXAS, INC | BRYAN | BRAZOS | TX |  |  | 15 + 06 | 330 | 1992-07-28 | 1 | NO |  |  |  | Null | NO | RUPTURE | 0 | 0 | 1 | 5000 | 3916.0475 | 8531.2036 | Null | 0 | 5 |  | 19920728 | 90 | 100 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: METER; MLKD: OTHER; MLKDO: CAST IRON METER; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1975; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: PHILLIPS MUNDOCK BY POD; PHONE: 2146702229; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19920136 | 1992-09-10 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA |  |  | LA |  |  |  | 1214 | 1992-08-03 |  | YES | WEST CAMERON | 165 | LA | YES | NO | LEAK | 0 | 0 | 0 | 50000 | 39160.4755 | 85312.0357 | Null | 1 | 45 |  | 19920803 | 1100 | 1200 | BY TEST | 1950 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1968 | 16 | 0.38 | 5LX | 52000 | SEAMLESS |  |  | 1967 | UNDER WATER |  | F ROY - FLEET SENOIR ENGINEER | 7086913786 | INTERNALLY | OTHER | N/A | OTHER | UNKNOWN | COATED | YES | 1968 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | INTERNAL CORROSION CAUSED LEAKS FROM TWO ISOLATED PITS 26 INCHES APART. THEPIPELINE HAD BEEN SHUT-IN.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19920137 | 1992-09-15 | 19235 | TEXAS EASTERN GAS PIPELINE CO | LANCASTER | FAIRFIELD | OH | 43130 | 94.68 | 4999+56 | 1700 | 1992-08-19 | 1 | NO |  |  | OH | Null | NO | RUPTURE | 14.5 | 2 | 0 | 154000 | 120614.2645 | 262761.0698 | Null | 2 | 35 |  | 19920819 | 674 | 809 | BY TEST | 1037 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1951; NMDIA: 26; THK: 0.28; SMYS: 52000; SEAM: ERW; MANU: A.O. SMITH; MANYR: 0; LOCLK: OTHER; PNAME: DWAYNE TESCHENDORF - SENOIR ENGINEER; PHONE: 7136275101; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; MARK: YES; MRKTP: MARKERS AT RD CROSSING &; STAT: YES; CTEST: Null | A FIBER OPTIC CABLE CONTRACTOR STRUCK TEXAS EASTERN'S 26" LINE 3. A FIRE BEGAN AND TWO CONTRACT CABLE EMPLOYEES DIED. THE FIRE LASTED 2 HOURS 35 MIUNTES.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19920139 | 1992-09-21 | 19160 | TENNESSEE GAS PIPELINE CO | GULF OF MEXICO |  | LA |  | 524C-401+0.00 |  | 0 | 1992-08-27 |  | YES | S. TIMB. | 24 |  | YES | NO | OTHER | 0 | 0 | 0 | 1600000 | 1253135.2155 | 2729985.1412 | Null | 0 | 0 |  | 19920827 | 0 | 1069 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: PLATFORM STRUCTURE; MLKD: OTHER; MLKDO: PLATFORM SUPPORT STRUCTUR; PRTSY: OTHER; PRTSO: 4-PILE STEEL JACKET PLATF; PRTYR: 0; NMDIA: 16; THK: 0.5; SPEC: API-5L; SMYS: 42000; MANU: NATIONAL TUBE; MANYR: 1961; LOCLK: UNDER WATER; PNAME: L A SALINAS; PHONE: 7137572781; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | PLATFORM DESTROYED BY HURRICANE ANDREW
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19920140 | 1992-09-21 | 18516 | SOUTHERN NATURAL GAS CO | EUGENE ISLAND |  | LA |  | 15.3 |  | 1200 | 1992-08-24 |  | YES | EI | 273 |  | YES | NO | LEAK | 0 | 0 | 0 | 120000 | 93985.1412 | 204748.8856 | Null | 0 | 0 |  | 19920825 | 1035 | 1440 | BY TEST | 2160 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | FITTING | PLIDCO FITTING | OTHER | 0-RING SEAL | PIPELINE |  | 1978 | 12 | 0 | FLANGE REPAIR + | 1900 | SPLIT SLEEVE |  | PLIDCO | 1984 | UNDER WATER |  | L D MATHEWS - EXECUTIVE VICE PRESIDENT | 2053257326 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | SEE PART 5 | YES |  | WATER | 0 | 0 | 0 | SEVERAL YEARS PRIOR TO THE INCIDENT UNDER CONSIDERATION, THE 12" EUGENEISLAND 261 SEA ROBIN PIPELINE WHICH TIES INTO THE 24" EUGENE ISLAND 330-206PIPELINE HAD A LEAK IN S SET OF FLANGES AT THE EUGENE ISLAND BLOCK 273 TIE-INLOCATION. SEA ROBIN INSTALLED A 12" 900# PLIDCO FLANGE REPAIR + SPLIT SLEEVETO REPAIR THE LEAKING FLANGES. THE PLIDCO FITTING RECENTLY DEVELOPED ANO-RING SEAL LEAK THAT WAS NOT DETECTABLE AT THE WATER SURFACE. THE WATERDEPTH IN THIS AREA IS APPROXIMATELY 180'. THE LEAK WAS DISCOVERED WHILEINSPECTING THE CONSTRUCTION OF OTHER FACILITIES IN THE IMMEDIATE VICINITY.THE LEAK WAS REPAIRED BY PUMPING THE SEAL AREA WITH A SEALING COMPOUND.SUPPLEMENTAL REPORT 12/15/94 INDICATES ITEM THAT LEAKED WAS A REPAIR COMPONENTTHE RATING OF WHICH WAS ESTABLISHED BY A PROTOTYPE TEST. REFERENCE 49 CFR192.143. LEAKING O-RING SEAL WAS THE CONSTRUCTION/MATERIAL DEFECT. SEE PART C
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19920141 | 1992-09-21 | 11680 | LONE STAR GAS CO | CAYUGA | ANDERSON | TX |  | MILE MARKER 68 | 4274 + 18 | 800 | 1992-08-30 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 5000 | 3916.0475 | 8531.2036 | Null | 2 | 0 |  | 19920830 | 334 | 425 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | CRACK IN GIRTH WELD | STEEL |  | PIPELINE |  | 1935 | 20 | 0.28 | GR. B | 35000 | EW-SMLS |  |  | 0 | UNDER GROUND |  | PHILLIP MURDOCK - MANAGER | 2146702229 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION | GIRTH WELD CRACKED WHERE A 30 DEG. MITER CUT WAS M | NO |  | NO DATA |  | 0 | 0 | GIRTH WELD CRACKED WHERE A 30 DEGREE MITER CUT WAS MADE ON PIPE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19920147 | 1992-09-30 | 18516 | SOUTHERN NATURAL GAS CO | SOUTH PASS BLOCK 60 | OFFSHORE | LA |  | .11 | 6 +-00 | 0 | 1992-08-26 |  | YES | SOUTH PASS BLOCK 60 | 60 |  | YES | NO | OTHER | 0 | 0 | 0 | 1500000 | 1174814.2645 | 2559361.0698 | Null | 0 | 0 |  | 19920827 | 600 | 1148 | BY TEST | 1148 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: MECHANICAL JOINT; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1973; NMDIA: 18; THK: 0.5; SMYS: 0; MANU: BIMS; MANYR: 1985; LOCLK: UNDER WATER; PNAME: A G THOMAS; PHONE: 2053257632; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; DMGO: UNDERWATER MUDSLIDE; NOTIF: NO; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | SHEAR JOINT (INSTALLED ON PIPELINE IN 1985) SEPARATION CAUSED BY A MUDSLIDE DURING HURRICANE ANDREW.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19920148 | 1992-09-28 | 19730 | TRUNKLINE GAS CO | SOUTH TIMBALIER | OFFSHORE | LA |  | PLATFORM T21 |  | 0 | 1992-08-25 |  | YES | ST | 72 |  | YES | Null | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 0 |  | 19920827 | 900 | 1200 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: UNKNOWN; MLKD: STEEL; PRTSY: PIPELINE; PRTSO: PLATFORM; PRTYR: 1969; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: UNDER WATER; PNAME: LARRY SHED; PHONE: 7137265695; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: HURRICANE; NOTIF: NO; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | DURING HURRICANE PLATFORM WAS SUBMERGED. UNKNOWN CONDITION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19920149 | 1992-09-28 | 12462 | MID - LOUISIANA GAS CO | NATCHEZ | ADAMS | MS |  | 108 | 866 LOOP LINE | 850 | 1992-08-27 | 1 | NO |  |  | MS | Null | NO | LEAK | 0 | 0 | 0 | 31000 | 24279.4948 | 52893.4621 | Null | 0 | 55 |  | 19920827 | 166 | 250 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: 45 DEGREE WELD ELBOW; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1988; NMDIA: 10; THK: 0.37; SPEC: SCHED.40 ASTM A234; SMYS: 35000; MANYR: 0; LOCLK: UNDER GROUND; PNAME: R E HARRIS - MANAGER TRANSMISSION; PHONE: 3186654426; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: NO; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | HEAVY RAINFALL FROM HURRICANE ANDREW CAUSED RIVER TO RISE TO WITHIN 3' OF TOP BANK, EROSION OF BANK IN RIVERBEND ALLOWED TREES FLOATING DOWN RIVER TO STRIKE LINE, BREAKING 45 DEGREE ELBOW.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19920150 | 1992-09-29 | 19325 | TEXAS UTILITIES FUEL CO | FARMERSVILLE | COLLIN | TX |  | P0.5 |  | 1700 | 1992-09-01 | 1 | NO |  |  | TX | NO | Null | RUPTURE | 6 | 0 | 0 | 50000 | 39160.4755 | 85312.0357 | YES | 1 | 0 |  | 19920901 | 500 | 873 | BY TEST | 1092 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1962; NMDIA: 10; THK: 0.22; SPEC: X42; SMYS: 42000; SEAM: ERW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: DANIEL R ALCORN/PRINCIPAL ENG. ANALYST; PHONE: 2148126870; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: RIGHT-OF-WAY MARKERS IN F; STAT: YES; CTEST: Null | THIRD PARTY CONTRACTOR WAS TRENCHING FOR A NEW PIPELINE. CONTRACTOR WAS AWARE OF TUFCO'S PIPELINE AND HAD CEASED TRENCHING TO MOVE TO OPPOSITE SIDE OF TUFCO'S RIGHT-OF-WAY. IN ERROR, CONTRACTOR RESUMED DIGGING AT TURCO'S PIPELINE
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19920151 | 1992-09-25 | 19570 | TRANSCO GAS PIPELINE CORP | OFFSHORE SHIP SHOAL |  | LA |  | 1.42 | 74+ 98 | 935 | 1992-08-27 |  | YES | SS | 118 |  | YES | NO | OTHER | 0 | 0 | 0 | 750000 | 587407.1322 | 1279680.5349 | Null | 0 | 0 |  | 19920827 | 1000 | 1250 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: PLATFORM RISER; MLKD: STEEL; PRTSY: OTHER; PRTSO: PLATFORM; PRTYR: 1975; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: OTHER; LOCLO: ON PLATFORM; PNAME: B R LANDES - STAFF COMPLIANCE ANALYST; PHONE: 7134392001; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: HURRICANE ANDREW; NOTIF: NO; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | AT APPROXIMATELY 9:35 A.M. ON AUGUST 27, 1992, HURRICANE ANDREW DESTROYED THE BLOCK 118E SHIP SHOAL PLATFORM OWNED BY ODECO. THE PLATFORM AND RISER WERECOMPLETELY OVERTURNED AND DESTROYED. TRANSCO HAD ONE 10" RISER ON THE PLATFORM. NO GAS WAS ONSERVED ON THE WATER SURFACE AT THIS LOACTION. THE PRODUCERWILL HAVE TO RECONSTRUCT THE PLATFORM AND THE TRANSCO PIPING AND FACILITIES WILL HAVE TO BE REPLACED AT THIS LOCATION, IN ADDITION TO OTHER UNDERWATER WORK THAT MUST OCCUR BEFORE THIS LOCATION WILL BE ABLE TO FLOW.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19920152 | 1992-09-25 | 19570 | TRANSCO GAS PIPELINE CORP | OFFSHORE SHIP SHOAL |  | LA |  | 16.17 | 854+83 | 935 | 1992-08-27 |  | YES | S.S | 72 |  | YES | NO | OTHER | 0 | 0 | 0 | 4000000 | 3132838.0386 | 6824962.8529 | Null | 0 | 0 |  | 19920827 | 970 | 0 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: PLATFORM RISERS; MLKD: STEEL; PRTSY: OTHER; PRTSO: PLATFORM; PRTYR: 1960; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: OTHER; LOCLO: ON PLATFORM; PNAME: B.R. LANDES STAFF COMPLIANCE ANALYST; PHONE: 7134392001; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: HURRICANE ANDREW; NOTIF: NO; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | ON AUGUST 27, 1992 THE EFM EQUIPMENT DATA INDICATED THE BLOCK 72A SHIP SHOALPLATFORM OWNED BY MOBIL GAVE WAY DUE TO HURRICANE ANDREW AT 9:35 A.M. TRANSCO HAD TWO 12" RISERS (ONE BELONGING TO NORTHERN NATURAL AND OPERATED BY TRANSCO), ONE 6" RISER, THREE 8" RISERS AND ONE 14" RISER. THE PLATFORM WAS NOTVISIBLE ON THE SURFACE OF THE WATER. ALL OF THE RISERS WERE DAMAGED AND PARTED FROM THE STRUCTURE. THE GAS ESCAPING FROM THE RISERS IGNITED AND WAS ON FIRE UNTIL 6:00 P.M. ON SEPTEMBER 1, 1992. COMPLETE RECONSTRUCTION OF PIPINGWILL HAVE TO BE ACCOMPLISHED BEFORE CERTAIN PRODUCERS CAN FLOW GAS. MAOP INFORMATION: 12" TO MOSQUITO BAY - 1168 PSIG; 12" TO MOBIL 72-J - 1168 PSIG; 8" LINES TO CHEVRON 108B, MOBIL 11-F AND MOBIL 87-B - 1250 PSIG; 6" TO ODECO 118-E - 1250 PSIG; ALL SHIP SHOAL PLATFORMS.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19920156 | 1992-10-06 | 18667 | STOCKER RESOURCES INC | LOS ANGELES | LOS ANGELES | CA | 90019 |  |  | 1230 | 1992-09-05 | 4 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 0 |  | 19920908 | 90 | 1000 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1968 | 8.63 | 0.32 |  | 35000 | SEAMLESS |  |  | 0 | OTHER | NON SPECIFIED | TROY E VALENZUELA - COMPLIANCE | 2132982266 | INTERNALLY | LOCALIZED PITTING |  | OTHER | ACCUMULATION OF LIQUIDS & | COATED | YES | 1980 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | STOCKER RESOURCES, INC. (STOCKER) WAS INFORMED IN SATURDAY, SEPTEMBER 5, 1992, BY CHEVRON PIPELINE CO. THAT A POSSIBLE LEAK EXISTED IN THE GRASSY MEDIAN DSTRIP OF SAN VICENTE BLVD. AT FOREST DRIVE. IT IS UNCLEAR WHETHER CHEVRON DISCOVERED THE LEAK DURING A LEAK SURVEY OR RECEIVED A COMPLAINT. STOCKER EMPLOYEE, JEFF WINKLER, WAS DISPATCHER TO THE SITE AND DISCOVERED DISCOLORED GRASS. BECAUSE THE AREA HISTORICALLY HAS SWAMP GAS, MR. WINKLER CONFIRMED THAT A PIPELINE LEAK EXISTED BY HAVING THE PIPELINE PRESSURED UP AND WITNESSED ADDISTIONAL EVIDENCE OF LEAK. PRODUCT WAS IMMEDIATELY SWITCHED INTO AN ADJACNETSTANDBY LINE. THE LEAK WAS ISOLATED AND DISCONTINUED WITHIN ON HOUR OF DISCOVERY. UPON EXCAVATION, IT WAS DISCOVERED THAT INTERNAL CORROSION, LOCALIZEDPITTING, HAD CAUSED THE LEAK. THE LEAK OCCURRED AT A LOW SPOT IN THE LINE, WHICH SIPPED SLIGHTLY TO AVOID A XITY SEWER LINE. LIQUID AND SOLIDS ACCUMULATING IN THIS SPOT CONTRIBUTED TO THE LEAK. ADHERING TO D.O.T. PROCEDURE, A 15' SECTION OF PIPELINE WAS REMOVED AND REPLACED. HYDROSTATIC PRESSURE TESTING WAS DONE BEFORE PUTTING THE LINE BACK IN SERVICE. TO PREVENT A RE-OCCURRENCE, OR ANY FURTHER CORROSION, IN ADDITION TO OUR NORMAL SCRAPPING AND PIGGINGOF THE PIPELINES, WE WILL INTRODUCE A CORROSION INHIBITING CHEMICAL TO COAT THE INTERNAL WALLS OF THE PIPELINES. ADDITIONALLY, WE WILL INCREASE THE FREQUENCY OF BALL OR POLY PIGGING OF LINES FROM SEMI-ANNUALLY TO MONTHLY.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19920157 | 1992-10-06 | 2796 | CORNING MUNICIPAL UTILITIES |  | ADAMS | IA | 50841 |  | SECT. 22 WASHINGTON TOWNS | 1650 | 1992-09-19 |  | NO |  |  | IA | Null | NO | LEAK | 0 | 0 | 0 | 15000 | 11748.1426 | 25593.6107 | YES | 3 | 10 |  |  | 150 | 150 | BY TEST | 500 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: WELD; PRTFO: BUTT WELD ON ELBOW; MLKD: OTHER; MLKDO: NON SPECIFIED; PRTSY: PIPELINE; PRTYR: 1961; NMDIA: 4; THK: 0.47; SPEC: API 5L GRB; SMYS: 0; MANU: ACME NEWPORT STEEL CO. 1961; MANYR: 1961; LOCLK: OTHER; LOCLO: NON SPECIFIED; PNAME: DEAN R DAVIS - MANAGER; PHONE: 5153223920; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: NO; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | FLOOD WATER WASHED OUT THE PIPELINE RIVER CROSSING AND TRESS CAME DOWN THE RIVER AND HIT THE PIPE IN THE RIVER. THIS CAUSED TO BREAK IN AN ELBOW IN THE REVIER BANK. LINE WAS SHUT DOWN AND BREAK WAS CUT OUT AND A NEW 10 FT. SECTION WAS WELED IN.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19920161 | 1992-10-22 | 19160 | TENNESSEE GAS PIPELINE CO | GULF OF MEXICO | CAMERON | LA |  | MP 507F-501+0.00 |  | 1600 | 1992-09-23 |  | YES | WEST CAMERON | 192B |  | YES | Null | OTHER | 0 | 0 | 0 | 3000000 | 2349628.529 | 5118722.1397 | Null | 0 | 0 |  | 19920923 | 590 | 1232 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: PLATFORM STRUCTURE; MLKD: OTHER; MLKDO: PLATFORM DECK SUPPORT LEG; PRTSY: OTHER; PRTSO: 6-PILE STEEL JACKET PLATF; PRTYR: 1958; NMDIA: 12; THK: 0.41; SPEC: AP1-5L; SMYS: 42000; SEAM: SEAMLESS; MANU: JONES & LAUGHLIN PIPE; MANYR: 1967; LOCLK: UNDER WATER; PNAME: L A SALINAS; PHONE: 7137572871; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: SIGNAGE & NAVIGATION AIDS; STAT: Null; CTEST: Null | PLATFORM LEGS AND PIPELINES. ABOVE WATER PIPELINE RISERS ON CENTRAL GATHERING PLATFORM WERE VISIBLE ON A CLEAR DAY.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19920163 | 1992-10-30 | 22617 | WILLIAMS NATURAL GAS CO | RAYMORE | CASS | MO | 64083 |  | 328+67 | 800 | 1992-10-01 | 1 | NO |  |  |  | Null | Null | OTHER | 0 | 0 | 0 | 50000 | 39160.4755 | 85312.0357 | Null | 17 | 30 |  | 19921001 | 240 | 250 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1946; NMDIA: 12; THK: 0.25; SMYS: 24000; SEAM: EW; MANYR: 0; LOCLK: UNDER WATER; PNAME: WARREN A ETHERIDGE; PHONE: 9185884427; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; MARK: YES; MRKTP: LINE MARKERS/TEMPORARY; STAT: YES; CTEST: Null | CONTRACTOR WAS CLEANING CREEK BOTTOM WITH A HIGH LOADER.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19920164 | 1992-11-02 | 25165 | GULF COAST NATURAL GAS CO | WHARTON | WHARTON | TX | 77488 | MP 106.1 | 5779 + 94 | 915 | 1992-10-14 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 70000 | 54824.6657 | 119436.8499 | Null | 1 | 40 |  | 19921014 | 420 | 505 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1942; NMDIA: 16; THK: 0.28; SPEC: A; SMYS: 843; SEAM: LAP WELD; MANYR: 0; LOCLK: UNDER GROUND; PNAME: ELVIN C LOYD JR. SUPERINTENDENT; PHONE: 4097934391; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: COMPANY STANDARD 10X14 LO; STAT: NO; CTEST: Null | A HEAVY EQUIPMENT OPERATOR USING A 12-G MAINTAINER TO EXCAVATE AN EXITING DRAINAGE DITCH, STRUCK THE PIPELINE CUTTING A 3 X 2.5 INCH HOLE INTO THE PIPE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19920166 | 1992-11-02 | 19570 | TRANSCO GAS PIPELINE CORP | SELMA | DALLAS | AL |  | 867.56 | 4715+20 | 245 | 1992-10-05 | 1 | NO |  |  |  | Null | NO | RUPTURE | 55 | 0 | 0 | 1860900 | 1457474.5765 | 3175143.3432 | Null | 1 | 29 |  | 19921005 | 750 | 780 | BY TEST | 1081 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1950; NMDIA: 30; THK: 0.31; SPEC: API-5LX; SMYS: 52000; SEAM: DSA; MANU: KAISER; MANYR: 1950; LOCLK: UNDER GROUND; PNAME: B P LANDES - STAFF COMPLAINCE ANALYST; PHONE: 7134392001; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | ON THE MORNING OF OCTOBER 5, 1992 AT 2:45 A.M., A PIPELINE RUPTURE AND FIRE OCCURRED ON MAIN LINE "A" AT MILE POST 867.56 IN DALLAS COUNTY, ALABAMA. THELINE SEGMENT WAS ISOLATED BY 4:14 A.M. AND ALLOWED TO BURN ITSELF OUT BY 7:45 A.M. THERE WERE NO REPORTED INJURIES AND DAMAGE WAS LIMITED TO APPROXIMATELY FOUR (4) ACRES OF TIMBER. THERE WAS NO INTERRUPTION OF SERVICE TO ANY OF TRANSCO'S CUSTOMERS. THE APPARENT CAUSE OF THE INCIDENT IS UNDER INVESTIGATION AT THIS TIME. AS SOON AS TRANSCO RECEIVES THE METALURGICAL RESULTS, A SUPPLEMENTAL REPORT INDICATING CAUSE WILL BE PROVIDED TO THE OFFICE OF PIPELINE SAFETY.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19920169 | 1992-11-12 | 19570 | TRANSCO GAS PIPELINE CORP | HIGH ISLAND |  | TX |  | 10.11 | 533+81 | 1810 | 1992-10-20 |  | YES | HI | 206 |  | Null | NO | RUPTURE | 0.5 | 0 | 0 | 100000 | 78320.951 | 170624.0713 | Null | 0 | 20 |  | 19921023 | 1250 | 1440 | BY TEST | 2218 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: UWTV ASSEMBLY; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1976; NMDIA: 6; THK: 0.43; SPEC: A-106; SMYS: 35000; SEAM: SEAMLESS; VALVE: 6" BALL; MANU: U.S STEEL; MANYR: 1976; LOCLK: UNDER WATER; PNAME: B R LANDES - STAFF COMPLAINCE ANALYST; PHONE: 7134392001; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: SURVEY CONTRACTOR ONBOARD; STAT: YES; CTEST: Null | VEHICLE STRUCK BUILDING AND METER SET. THE IMPACT CRACKED THE STRAINER WHICHPRODUCER HAD ABANDONED PRODUCTION FROM HIGH ISLAND 206 AND MADE NEW CONNECTIO IGNITED.N TO SAME TRANSCO UWTV ASSEMBLY FROM HIGH ISLAND 207. PRODUCER HAD COMPLETED DISASSEMBLING THE HIGH ISLAND 206 PLATFORM AND ON OCTOBER 20, 1992 WAS USING A SHRIMP BOAT TO PERFORM MMS REQUIRED BOTTOM GRID SEARCH FOR DEBRIS. WHILEPERFORMING THE GRID SEARCH,THE SHRIMP BOAT'S NET AND CHAIN SNAGGED THE PRODUCER'S VAVLE AND PIPELINE, PULLING IT OVER AND SEVERING TRANSCO'S UWTV ASSEMBLY AT THE WELD FOR 1 110 DEGREE ELL. DUE TO WEATHER AND SEA CONDITIONS, EQUIPMENT AND DIVERS WERE UNABLE TO ACCESS THE DAMAGE UNTIL EARLY ON OCTOBER 23, 1992.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19920173 | 1992-11-19 | 20525 | DELMAR OPERATING, INC | HOUSTON |  | TX |  |  |  | 1641 | 1992-10-20 |  | YES | HIGH ISLAND | 206 |  | YES | NO | OTHER | 0 | 0 | 0 | 302600 | 236999.1976 | 516308.4398 | Null | 0 | 10 |  | 19921020 | 1000 | 1440 | BY TEST | 2160 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1992; NMDIA: 10; THK: 0.37; SPEC: API SL GR B; SMYS: 35000; MANYR: 0; LOCLK: UNDER WATER; PNAME: PEGGY DAVIS - REGULATORY COORDINATOR; PHONE: 7136466649; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; DMGO: SHRIMP TRAWLER DAMAGED PI; NOTIF: YES; MARK: YES; MRKTP: NAVIGATIONAL; STAT: NO; CTEST: Null | THE 10-INCH GEAR OPERATED BALL VALVE INSTALLED ON DELMAR'S TIE-IN ASSEMBLY WAS BURIED TO THE PROPER DEPTH AND WAS COVERED WITH LOOSE SAND WHICH HAD NATURALLY BACK FILLED INTO THE HOLE MADE DURING THE INSTALLATION OF THE ASSEMBLY.AS THE "CAPTAIN JIMMY" WAS LIFTING ITS NETS IN AN ATTEMPT TO RETRIEVE THE DEBRIS SNAGGED IN THE STARBOARD SIDE NET, THE NOW SLACK 3/8" TICKLE CHAIN ON THE PORT SIDE NET, DRAGGED UNDER THE LOOSE SAND AND HOOKED THE GEAR OPERATOR ON THE 10-INCH VALVE. THE TRAWLER, IN AN ATTEMPT TO FREE ITS PORT SIDE NET, CONTINUED RAISING THE NETS AND BEGAN TURNING IN A COUNTERCLOCKWISE DIRECTION. AS A RESULT OF THIS PROCEDURE, TRANSCO'S 6-INCH TIE-IN ASSEMBLY SEVERED AT THE110 DEGREE BEND AND THE 10-INCH PIPELINE WAS BENT BACK OVER ITSELF FORMING ALOOP OF APPROXIMATELY 10 FEET. THE 6-INCH BALL VALVE AT THE 12-INCH TRANSCO PIPELINE TIE-IN AND THE 8-INCH BALL VALVE AT THE ARCO TIE-IN TO THE ASSEMBLY HAVE BEEN CLOSED.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19920174 | 1992-11-19 | 20525 | DELMAR OPERATING, INC | HIGH ISLAND |  | TX |  |  |  | 620 | 1992-10-20 | 1 | YES | HI | 206 |  | YES | NO | OTHER | 0 | 0 | 0 | 202600 | 158678.2467 | 345684.3685 | Null | 8 | 0 |  | 19921106 | 1040 | 1400 | BY TEST | 2160 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: GATHERING SYSTEM; PRTFL: MECHANICAL JOINT; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1992; NMDIA: 10; THK: 0.37; SPEC: API SL GR B; SMYS: 35000; MANYR: 0; LOCLK: UNDER WATER; PNAME: PEGGY DAVIS - REGULATORY COORDINATOR; PHONE: 7136466649; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: MATERIAL; CAULO: HYDROCOUPLE FLANGED AND CONNECTOR CAME OFF PIPE EN; CTEST: YES; TESTD: 19920807; MED: WATER; TMPS: 4; LKPS: 3350
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19920175 | 1992-11-20 | 15105 | PANHANDLE EASTERN PIPELINE CO | HARDESTY | TEXAS | OK | 73944 | 8 MP | 3278 + 59 | 1148 | 1992-10-07 | 1 | NO |  |  |  | Null | NO | RUPTURE | 151 | 0 | 0 | 130000 | 101817.2363 | 221811.2927 | Null | 2 | 32 |  |  | 605 | 625 | BY TEST | 690 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1943 | 26 | 0.25 | AP15L | 45000 | EFW |  | AOS MIL | 1943 | UNDER GROUND |  | C W FERGUSON - AREA SUPERVISOR | 7136275600 | INTERNALLY | GENERAL CORROSION |  | OTHER |  | BARE | Null | 0 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | STILL UNDER INVESTIGATION.THE TGPL SUBSEA TIE-IN VALVE ASSEMBLY AND THE DELMAR PIPELINE WERE REPAIRED AND ON NOVEMBER 6, 1992, THE PIPELINE FROM HIGH ISLAND 207 PLATFORM WAS IN THE PROCESS OF BEING PRESSURED UP BY BACK FLOWING FROM THE SUBSEA TIE-IN ASSEMBLY. APPROXIMATELY 35 MINUTES AFTER THE PIPELINE HAD REACHED OPERATING PRESSURE OF 1040 PSIG, AND AFTER A DIVING INSPECTOR REPORTED NO LEAKS ON VALVE BODIES OR FLANGES, THE PIPELINE RUPTURED, DISCHARGING NATURAL GAS INTO THE GULF OFMEXICO. THE DEPARTING PIPELINE SHUT-DOWN VALVE ON THE HIGH ISLAND 207 PLATFORM WAS CLOSED AT THE TIME OF THE INCIDENT. THE JACK-UP WORK BARGR WHICH WASPERFORMING THE WORK WAS THE GULF ISLAND II. ALL PERSONNEL ON BOARD THE BARGE WERE EVACUATED TO THE WORK VESSEL SEA OX WHICH WAS STANDING BY. THERE WERENO INJURIES OR POLLUTION ASSOCIATED WITH THIS INCIDENT. THE SUPPLY OF GAS USED TP PRESSURE UP THE PIPELINE FROM HIGH ISLAND 207 "A" PLATFORM WAS FORM ALATERAL LINE TIE-IN TO THE SUBSEA VALVE ASSEMBLY. THE CHECK VALVE WAS LOCKED OPEN ON THE HIGH ISLAND 207 LATERAL TIE-IN WHICH ALLOWED THE GAS TO BACK FLOW INTO THE PIPELINE. WHEN THE INCIDENT OCCURRED, TGPL NOTIFIED THE TWO PIPELINES WERE SHUT-IN. TWO HOURS AFTER THE INCIDENT, GAS CONTINUED TO BE DISCHARGED FROM THE RUPTURE WHICH INDICATED THAT THE GAS MUST BE COMING FROM A SOURCE OTHER THAN THE TWO PLATFORMS SUPPLYING GAS TO THEIR MAIN LINE TO SHUT-IN.APPROXIMATELY SIX HOURS LATER, THE GAS BEING DISCHARGED THROUGH THE RUPTURE HAD DECREASED TO A LEVEL WHICH ALLOWED A TGPL DIVER TO CLOSE THE VALVE ON THELATERAL LINE TIE-IN. UPON INSPECTION OF THE RUPTURED PIPELINE, IT WAS DETERMINED THAT THE FLANGED END OF THE HYDROCOUPLE END CONNECTOR MANAUFACTURED BYHYDRO TECH SYSTEMS, INC. HAD COME OFF OF THE PIPELINE. REPAIRS TO THE PIPELINE ARE IN PROGRESS AND WILL BE COMPLETED AS SOON AS PRACTICAL.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19920176 | 1992-11-18 | 5670 | FULTON BOARD OF PUBLIC WORKS | FULTON | CALLAWAY | MO | 65251 |  |  | 1645 | 1992-10-12 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 20 |  | 19921012 | 275 | 300 | BY TEST | 450 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 0; NMDIA: 8; THK: 0.19; SPEC: 5L X 42; SMYS: 42000; SEAM: SEAMLESS; MANYR: 1968; LOCLK: UNDER GROUND; PNAME: DALE TATE - FIELD SUPERVISOR; PHONE: 3146426665; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; MARK: YES; MRKTP: FLAGGING & SIGN POST MARK; STAT: YES; CTEST: Null | LINE WAS MARKED AND LOCATOR HAD GONE TO OFFICE TO CHECK RECORDS FOR DEPTH.CONTRACTOR EXCAVATING FOR NEW STATE HIGHWAY HIT LINE. LINE WAS LOCATED AND MARKED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19920177 | 1992-12-03 | 19570 | TRANSCO GAS PIPELINE CORP | EL CAMPO | WHARTON | TX |  | 6.60 | 348 + 69 | 1040 | 1992-11-10 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 75000 | 58740.7132 | 127968.0535 | Null | 1 | 0 |  | 19921110 | 625 | 800 | BY TEST | 1329 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1981; NMDIA: 24; THK: 0.31; SPEC: API-5LX; SMYS: 52000; SEAM: DSA; MANU: BETHLEHEM; MANYR: 1981; LOCLK: UNDER GROUND; PNAME: B R LANDES - STAFF COMPLAINCE ANALYST; PHONE: 7134392001; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PERMANENT MARKERS; STAT: YES; CTEST: Null | ON NOVEMBER 10, 1992 AN OUTSIDE COMPANY WAS PERFORMING SEISMIC WORK IN THE VICINITY OF TGPL'S 243" MCMULLEN LATERAL. IT APPEARED THAT WHILE PERFOMING THEIR WORK, THE SEISMOGRAP CREW HAD DRILLED A SHOT HOLE DIRECTLY OVER THE TGPL PIPELINE AND PLACED A 1/3 LB. CHARGE IN THE SHOT HOLE. THE DETONATION OF THECHARGE CAUSED A DENT WITH A CRACK IN THE BODY OF THE PIPE, THUS RESULTING INTHE LEAK.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19920179 | 1992-12-03 | 19570 | TRANSCO GAS PIPELINE CORP | OFFSHORE HIGH ISLAND |  | TX |  | 10.11 | 533 + 81 | 830 | 1992-11-17 |  | YES | H.I. | 206 |  | YES | Null | LEAK | 0 | 0 | 0 | 60000 | 46992.5706 | 102374.4428 | Null | 0 | 10 |  | 19921117 | 500 | 1440 | BY TEST | 2218 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: BG-INCH HYDRAULIC CONNECT; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1992; NMDIA: 8; THK: 0.5; SPEC: A-106; SMYS: 35000; MANU: B1MS; MANYR: 1992; LOCLK: UNDER WATER; PNAME: B R LANDES - STAFF COMPLIANCE ANALYST; PHONE: 7134392001; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; MARK: YES; MRKTP: SURVEY CONTRACTOR WITH PR; STAT: YES; CTEST: Null | AS A RESULT OF THE LEAK INCIDENT, REPORTED BY TGPL, ON OCTOBER 20, 1992, (DOT CASE NO. 141753) PRODUCER INSTALLED A MECHANICAL CONNECTOR TO ONE END OF THEIR 1O" PIPELINE. ON NOVEMBER 6, 1992 PRODUCER'S MECHANICAL CONNECTOR FAILEDDURING REPRESSURING OF FACILITY. THE DAMAGE AND LEAK TO THE TGPL HYDRAULIC CONNECTOR WAS NOT DETECTED UNTIL THE FACILITY WAS REPRESSURED AGAIN ON NOVEMBER 17, 1992 AND RESULTED IN THIS REPORTABLE INCIDENT (CASE NO. 145215).
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19920181 | 1992-12-03 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA | BARTLETT | DU PAGE | IL | 60103 |  | 1853 + 51 | 1500 | 1992-11-03 | 3 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 300000 | 234962.8529 | 511872.214 | Null | 0 | 30 |  | 19921103 | 440 | 687 | BY TEST | 1143 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1957; NMDIA: 34; THK: 0.38; SPEC: 5LX; SMYS: 52000; SEAM: DSAW; MANU: U.S. STEEL; MANYR: 1957; LOCLK: UNDER PAVEMENT; PNAME: F ROY FLEET - SENOIR ENGINEER; PHONE: 7086913786; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | VISUAL INSPECTION OF THE CARRIER PIPE FOUND THE EXTERNAL COATING TO BE IN GOOD CONDITION AND NO INTERNAL CORROSION. THE LEAK WAS NOT FOUND. NEW PIPE WAS INSTALLED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19920182 | 1992-12-03 | 19730 | TRUNKLINE GAS CO | GULF OF MEXICO | SHIP SHOAL BLOCK 90 | TX |  |  | 1241 + 59 | 745 | 1992-11-03 |  | YES | SS | 90 |  | YES | NO | RUPTURE | 450 | 0 | 0 | 1000000 | 783209.5097 | 1706240.7132 | Null | 1 | 15 |  | 19921103 | 1070 | 1200 | BY TEST | 1625 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1981; NMDIA: 30; THK: 0.41; SPEC: API 5LX; SMYS: 65000; SEAM: DSAW; MANU: ARMCO; MANYR: 1981; LOCLK: UNDER WATER; PNAME: ROBERT AL MOODY - DIRECTOR; PHONE: 7136275716; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | FAILURE INITIATED IN DENT AT (PIPE POSITION) 12:00. BUT NOT ALL PIPE CAN BE ACCOUNTED FOR.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19920192 | 1992-12-08 | 11680 | LONE STAR GAS CO | SHERMAN |  | TX |  |  | 1834+68 | 1215 | 1992-11-10 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 1 | 2350 | 1840.5423 | 4009.6657 | Null | 0 | 5 |  | 19921110 | 250 | 320 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: MECHANICAL JOINT; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1913; NMDIA: 10; THK: 0.25; SMYS: 24000; MANYR: 0; LOCLK: UNDER GROUND; PNAME: PHILLIP MURDOCK - DIRECTOR; PHONE: 2146702229; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | PIPELINE HAD BEEN REMOVED FROM SERVICE TO INSTALL A REPLACEMENT SECTION. AFTER JOB COMPLETION, PIPELINE SEGMENT WAS PURGED, REPRESSURED AND RETURNED TO NORMAL SERVICE. APPROX. 20 MINUTES LATER A JOINT OF EXISTING PIPE SLIPPED FROM A DRESSER COUPLING AND ALLOWED SEPARATION OF PIPELINE JOINT CONNECTION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19920195 | 1992-12-22 | 21031 | VALERO TRANSMISSION CO |  | WEBB | TX |  |  | 4857+41 TO 4857+03 | 400 | 1992-11-20 | 1 | NO |  |  | TX | Null | NO | RUPTURE | 38 | 0 | 0 | 47000 | 36810.847 | 80193.3135 | Null | 3 | 30 |  | 19921120 | 900 | 1010 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1960; NMDIA: 20; THK: 0.28; SPEC: API5LX-52; SMYS: 1461; MANYR: 1960; LOCLK: UNDER GROUND; PNAME: JOHN SOMMER - MANAGER, ENV & REG; PHONE: 2102462395; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | A METALLURIGICAL ANALYSIS IS BEING CONDUCTED TO DETERMINE THE CAUSE OF THIS FAILURE.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19920196 | 1992-12-22 | 21031 | VALERO TRANSMISSION CO | CORPUS CHRISTI | NUECES | TX |  | 136 + 91 |  | 1715 | 1992-11-16 | 2 | NO |  |  | TX | Null | NO | RUPTURE | 4 | 0 | 2 | 232000 | 181704.6062 | 395847.8455 | Null | 0 | 45 |  | 19921116 | 480 | 1025 | BY TEST | 1425 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1967; NMDIA: 16; THK: 0.22; SPEC: API5LX-52; SMYS: 1424; MANYR: 0; LOCLK: UNDER GROUND; PNAME: JOHN SOMMER - MANAGER ENV & REG; PHONE: 2102462395; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: NO; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | A FAILURE ANALYSIS IS BEING CONDUCTED TO VERIFY THE CAUSE OF THE RUPTURE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19920197 | 1992-12-23 | 22617 | WILLIAMS NATURAL GAS CO | WICHITA | SEDGWICK | KS | 67277 |  | 21 + 19 | 1500 | 1992-11-24 | 1 | NO |  |  |  | Null | Null | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 5 |  | 19921124 | 360 | 460 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 0; NMDIA: 20; THK: 0.25; SMYS: 42000; SEAM: ELECTRIC RESIST; MANYR: 0; LOCLK: OTHER; LOCLO: NON SPECIFIED; PNAME: WARREN A ETHERIDE - SR PIPELINE SAFETY COORD.; PHONE: 9185884427; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: YES; MARK: YES; MRKTP: LINE MARKERS; STAT: YES; CTEST: Null | PIPELINE WAS MARKED; HOWEVER, DUE TO HEAVY EXCAVATION FROM NEW PIPELINE CONSTRUCTION, OPERATOR ACCIDENTALLY HIT EXISTING LINE WHILE SHORING FOR NEW TRENCH
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19920201 | 1992-12-22 | 2714 | CNG TRANSMISSION CORP | LEESBURG | LOUDOUN | VA | 22075 |  |  | 40 | 1992-11-22 | 3 | NO |  |  | VA | Null | NO | OTHER | 0 | 0 | 0 | 54390 | 42598.7652 | 92802.4324 | Null | 0 | 15 |  | 19921122 | 790 | 1250 | BY TEST | 1875 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: ESD SYSTEM; MLKD: OTHER; MLKDO: N/A; PRTSY: COMPRESSOR STATION; PRTYR: 1992; NMDIA: 0; THK: 0; SMYS: 0; LOCLK: ABOVE GROUND; PNAME: JACK L ADAMS - ADMINSTRATOR; PHONE: 3046238410; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | DURING COMMISSIONING OF COMPRESSOR STATION, THE ESD SYSTEM LOST PRESSURE. THE OPERATING SOFTWARE DID NOT ALLOW THE PRESSURE TO BE MADE UP AND THEREFORE A FULL ESD OCCURRED. ABLOCK VALVE DID NOT CLOSE AND HAD TO BE CLOSED MANUALLY. ALL CONDITIONS WERE CORRECTED PRIOR TO PLACING INTO SERVICE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19920202 | 1992-12-22 | 13750 | NORTHERN NATURAL GAS CO (ENRON) | LORRAINE | ELLSWORTH | KS | 67459 | 6.39 |  | 1115 | 1992-10-08 | 1 | NO |  |  |  | Null | NO | RUPTURE | 37 | 0 | 0 | 183000 | 143327.3403 | 312242.0505 | Null | 1 | 0 |  | 19921008 | 835 | 991 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1965 | 30 | 0.34 | API 5LX | 60000 | SUBMERGED ARC W |  | REPUBLIC STEEL | 1965 | UNDER GROUND |  | TILFORD N VIK. - CODES COMPL. ENGR. | 7136467342 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | COATED | YES | 1965 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | YES | YES |  | 19920206 | 1993-01-11 | 19570 | TRANSCO GAS PIPELINE CORP | TILDEN | MCMULLEN | TX |  | 0.00 | 0+00 | 715 | 1992-12-11 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 3 | 0 | 0 | 0 | Null | 0 | 10 |  | 19921211 | 0 | 0 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: NO DATA; PRTFL: OTHER; PRTFO: NON SPECIFIED; MLKD: OTHER; MLKDO: NON SPECIFIED; PRTSY: OTHER; PRTSO: NON SPECIFIED; PRTYR: 0; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: B R LANDES - STAFF COMPLAINCE ANALYST; PHONE: 7134392001; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | WHILE PERFORMING PIGGING OPERATIONS ON DECEMBER 11, 1992, ON THE TGPL 20" SOUTH MCMULLEN LATERAL. LIQUIDS WERE BEING STORED IN FIVE FRAC TANKS SET UP ON TGPL PROPERTY AT STATION 04. ALL OF THE FRAC TANKS WERE FULL AND OVER NIGHT THE ATMOSPHERIC CONDITIONS CHANGED TO THERE WAS NO WIND. THE VAPORS FROM THEFRAC TANK VENTS SETTLED TO THE GROUND, AND APPARENTLY SPREAD TO A TRAVEL TRAILER (CONTRACTOR'S) PARKED NEARBY. AT APPROXIMATELY 7:15 A.M. ON DECEMBER 11. 1992, THE VAPORS WERE IGNITED BY A SOURCE FROM THE TRAILER AND RESULTED IN A "FLASH FIRE" TO THE TRAILER. AT THE TIME OF THE "FLASH FIRE" ONE CONTRACTOR EMPLOYEE WAS INSIDE THE TRAILER, AND TWO TGPL EMPLOYEES WERE WORKING ON THEAREA. ALL THREE MEN RECEIVED BURNS AND WERE TRANSPORTED BY HELICOPTER TO HOSPITAL IN SAN ANTONIO, TEXAS, WHERE ALL THREE WERE ADMITTED FOR TREATMENT. THE ONE CONTRACT WORKER WAS TREATED FOR SECOND AND THIRD DEGREE BURNS OVER APPROXIMATELY 25% OF HIS BODY INCLUDING THE BUTTOCKS AND THE BACKS OF HIS LEGS, WHILE THE OTHER RECEIVED SECOND AND THIRD DEGREE BURNS OVER APPROXIMATELY 18%OF HIS BODY INCLUDING HIS LOWER BACK, BUTTOCKS, EAR, WRIST AND KNEE. THEIR ANTICIPATED STAYS IN THE HOSPITAL ARE SIX AND EIGHT WEEKS, RESPECTIVELY. THERE WAS NO DAMAGE TO ANY OF TGPL'S FACILITIES.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19920208 | 1992-03-10 | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | NEW YORK | NEW YORK | NY | 10021 |  |  | 1530 | 1992-11-20 | 4 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 15 |  | 19921120 | 280 | 350 | BY TEST | 525 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: MECHANICAL JOINT; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1958; NMDIA: 30; THK: 0.5; SPEC: ASTM - A155; SMYS: 0; MANYR: 0; LOCLK: UNDER PAVEMENT; PNAME: RANDY F GOFFRED - SECTION MGR; PHONE: 2124602838; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | A CON EDISON CREW WAS PERFORMING A SCHEDULED REINFORCEMENT OF AN INSULATING CDURING SCHEDULED REINFORCEMENT OF TRANSMISSION MAIN, THE WELDER BURNED HOLE IOUPLING ON A 30-INCH TRANSMISSION MAIN WHEN THE WELDER UNINTENTIONALLY BURNEDN PIPE WALL CAUSING A LEAK. ---- A CON EDISON CREW WAS PERFORMING A SCHEDULE A HOLE IN THE PIPE WALL. A SEGMENT OF THE TRANSMISSION MAIN WAS ISOLATED ASD REINFORCEMENT OF AN INSULATING COUPLING ON A 30-INCH TRANSMISSION MAIN WHEN PART OF THE EMERGENCY PROCEDURE. THE WELDER UNINTENTIONALLY BURNED A HOLE IN THE PIPE WALL. A SEGMENT OF THE TRANSMISSION MAIN WAS ISOLATED AS PART OF THE EMERGENCY PROCEDURES.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19920209 | 1993-01-05 | 20230 | UNITED GAS PIPELINE CO | BERNARD PARISH |  | LA |  | 10.83 | 571 + 55 | 730 | 1992-12-05 | 1 | NO |  |  | LA | Null | NO | RUPTURE | 12 | 0 | 0 | 98000 | 76754.5319 | 167211.5899 | Null | 2 | 10 |  | 19921205 | 589 | 605 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: NON SPECIFIED; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1963; NMDIA: 20; THK: 0.28; SPEC: 5LX-52; SMYS: 0; SEAM: ELECTRIC WELD; MANU: A O SMITH; MANYR: 0; LOCLK: OTHER; PNAME: WAYNE ST. GERMAIN - SR P.L. SAFETY ANALYST; PHONE: 7132295772; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930003 | 1993-01-13 | 22655 | WILLISTON BASIN INTERSTATE PIPELINE CO | POWELL | PARK | WY | 82435 | NE 1/4 SE 1/4 SEC 24 T 58 |  | 2040 | 1992-12-11 | 1 | NO |  |  |  | Null | NO | RUPTURE | 2 | 0 | 0 | 150000 | 117481.4264 | 255936.107 | Null | 1 | 0 |  | 19921211 | 651 | 800 | BY TEST | 1385 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: HEAT EXCHANGE COIL; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1988; NMDIA: 4; THK: 0.24; SPEC: SA106B; SMYS: 135000; SEAM: SEAMLESS; MANU: TULSA TUBE BENDING CO; MANYR: 1988; LOCLK: ABOVE GROUND; PNAME: RONALD H HAUGEBERG - GAS DISPATCHING SUPERINTENDENT; PHONE: 4063597200; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | EXPLOSION AND FIRE RESULTED FROM FAILURE OF HEAT EXCHANGE COIL WITHIN FIRED HEATER FOR THE DRY BED DEHYDRATION SYSTEM.7
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930007 | 1993-01-30 | 13845 | NORTHWEST PIPELINE CORP | SUGARLOAF HILL | OWYHEE | ID |  | 48.8 ON 16" RENO LINE | 2577 + 88 | 1030 | 1993-01-06 | 1 | NO |  |  |  | Null | YES | OTHER | 5 | 0 | 0 | 170000 | 130091.4634 | 283407.3751 | Null | 0 | 40 |  | 19930106 | 904 | 910 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1962; NMDIA: 16; THK: 0.23; SPEC: API 5LX; SMYS: 46000; SEAM: ELECTRIC RESIST; MANU: KAISER; MANYR: 1961; LOCLK: UNDER WATER; PNAME: PAM GARRETT - PIPELINE SAFETY SPECIALIST; PHONE: 8015846963; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; MARK: YES; MRKTP: 0Y; STAT: Null; CTEST: Null | CONTRACT BACKHOE RUPTURED PIPE DURING BACKFILL OPERATION OF NEW LOOP IN SPITE OF PIPE DEPTHS MARKED ON THE IN-SERVICE 16 INCH LINE EVERY 100 FEET. COMPANY INSPECTOR WAS AT PADDING OPERATION ONE-HALF MILE AWAY.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930008 | 1993-01-21 | 2616 | COLUMBIA GAS TRANSMISSION CORP | MARION | FAYETTE | PA | 15174 |  | 971+30 | 825 | 1992-12-29 | 1 | NO |  |  |  | Null | YES | RUPTURE | 41 | 0 | 0 | 165000 | 129229.5691 | 281529.7177 | Null | 1 | 20 |  | 19921229 | 907 | 936 | BY TEST | 1170 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1959 | 20 | 0.25 | API5LX | 52000 | ERW |  | YOUNGSTOWN SHEET & TUBE | 1959 | UNDER GROUND |  | STEVEN J CHOBY - MANAGER, CODES, STANDARDS | 3043572349 | EXTERNALLY | OTHER | 1 1/2" X 11" CORRODED ARE | OTHER | ISOLATED CORROSION CELL | COATED | YES | 1961 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | RELATED CORROSION AREA TOTALED 16 SQUARE INCHES. REMAINING PIPE IN EXCELLENT CONDITION. INVESTIGATION REVEALED THAT A 57.5' SEGMENT OF OPERATOR'S LINE 1804 WAS DAMAGED RESULTING FROM A 41' RUPTURE ATTRIBUTED TO AN ISOLATED CORROSION DEFECT WHICH REDUCED THE PIPE WALL THICKNESS AND RESULTED IN A DUCTILE FRACTURE. THE CORRODED AREA APPEARS TO HAVE BEEN SHIELDED FROM CATHODIC PROTECTION BY A ROCK.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930011 | 1993-02-03 | 4280 | EL PASO NATURAL GAS CO |  | PINAL | AZ |  | 13+ |  | 1415 | 1993-01-14 | 1 | NO |  |  |  | Null | NO | RUPTURE | 1.6 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 10 |  | 19930114 | 370 | 475 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1953; NMDIA: 6; THK: 0.14; SMYS: 0; MANYR: 0; LOCLK: UNDER WATER; PNAME: RICHARD FAVILA - SENIOR ENGINEER; PHONE: 9155412062; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: NON SPECIFIED; NOTIF: NO; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | NUMBER OF OUR PIPELINES IN THAT STATE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930012 | 1993-02-03 | 4280 | EL PASO NATURAL GAS CO | MARICOPA |  | AZ |  | 624.6 |  | 1130 | 1993-01-13 | 1 | NO |  |  |  | Null | NO | RUPTURE | 7.9 | 0 | 0 | 50000 | 38262.1951 | 83355.1103 | Null | 0 | 0 |  | 19930113 | 0 | 1080 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1970; NMDIA: 30; THK: 0.45; SPEC: API 5LX; SMYS: 60000; MANU: U S STEEL; MANYR: 1969; LOCLK: OTHER; PNAME: RICHARD FAVILA - SENIOR ENGINEER; PHONE: 9155412062; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: NON SPECIFIED; NOTIF: NO; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | THIS PIPELINE SEGMENT HAD BEEN BLOWNDOWN ON 1/10/93 AS A PRECAUTION. RECENTOF OUR PIPELINES IN THAT STATE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930013 | 1993-02-03 | 4280 | EL PASO NATURAL GAS CO | PINAL |  | AZ |  | 4+ |  | 1430 | 1993-01-08 | 1 | NO |  |  |  | Null | NO | RUPTURE | 1.7 | 0 | 0 | 50000 | 38262.1951 | 83355.1103 | Null | 1 | 15 |  | 19930108 | 700 | 809 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1958; NMDIA: 6.63; THK: 0.28; SPEC: API 5L; SMYS: 35000; SEAM: SEAMLESS; MANU: YOUNGSTOWN; MANYR: 1957; LOCLK: ABOVE GROUND; PNAME: RICHARD FAVILA - SENIOR ENGINEER; PHONE: 9155412062; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: NON SPECIFIED; NOTIF: NO; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | RECENT RAINS IN THE STATE OF ARIZONA HAVE FLOODED RIVERS, CAUSING DAMAGE TO A NUMBER OF OUR PIPELINES IN THAT STATE. FLOOD WATERS FROM THE SAN PEDRO RIVER WASHED AWAY SOME PEERS FOR A PIPELINE BRIDGE SUPPORTING OUR 6 5/8" LINE2071. THIS CAUSED THE PIPELINE TO FALL AND RUPTURE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930014 | 1993-02-02 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | REED CITY | OSCEOLA | MI | 49677 | MP .82 | 43 + 16 | 1515 | 1992-12-15 | 2 | NO |  |  | MI | Null | NO | LEAK | 0 | 0 | 0 | 50000 | 39160.4755 | 85312.0357 | YES | 1 | 30 |  | 19921215 | 300 | 544 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: 3" DIA STUB; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1939; NMDIA: 3; THK: 0; SMYS: 0; MANYR: 0; LOCLK: UNDER GROUND; PNAME: ED SWANSON - CODES/STANDARDS CONSULTANT; PHONE: 3132566614; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: YES; MARK: YES; MRKTP: STAKES; STAT: YES; CTEST: Null | MICHCON CONTRACTOR'S BACKHOE STRUCK 3" DIS. 3' UNKNOWN STUB ON SIDE OF PIPELINE THAT WAS NOT RECORDED BY PREVIOUS OWNER OF PIPELINE. STAKING LOCATION OFTHE PIPELINE WAS INACURATE
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930015 | 1993-01-29 | 402 | AMERICAN CENTRAL GAS CO INC | MONAHANS | WARD | TX | 79756 | M.P. 16.25 | 1237 + 71 | 1820 | 1992-11-20 | 3 | NO |  |  |  | Null | YES | RUPTURE | 21 | 0 | 0 | 100000 | 78320.951 | 170624.0713 | Null | 0 | 45 |  | 19921120 | 350 | 718 | BY TEST | 1100 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | LONGITUDINAL | STEEL |  | PIPELINE |  | 1960 | 8 | 250 | API 5L X-46 | 46000 | ERW |  | KAISER | 1960 | UNDER PAVEMENT |  | RICHARD STOUT - PIPELINE SPECIALIST | 9153812740 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL |  | YES |  | WATER |  | 8 | 1100 | TESTS REVEAL THAT TGE 8" LINE PIPE INVOLVED FAILED DUE TO INTERNAL OVER-PRESSURIZATION. THE WALL THINNING IN THE ERW WELD SEAM FUSION LINE AT THE ORIGINOF THE BURST WAS THE RESULT OF SULFUR COMPOUNDS CORROSION. THE CORROSION HAD OCCURRED FROM THE I.D. PREFERENTIALLY IN THE FUSION LINE OF THE LONGITUDINAL ERW WELD SEAM. THE FINAL FRACTURE WAS LESS THAN 30% OF THE ORIGINAL WALL THICKNESS. ADDITIONALLY, THE FINAL FRACTURE AREA CONTAINED ERW WELD DEFECTS AT THE FUSION LINE. FLAT, PARTIALLY FUSED AREAS IN THE FUSION LINE ARE CALLED"PASTY" AND ARE THE RESULT OF A COLD WELD, LOW HEAT INPUT. THESE AREAS OFFER VERY LOW TO ALMOST NO STRENGTH AND LOWER THE STRENGTH OF THE PIPE WALL.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930019 | 1993-02-03 | 4280 | EL PASO NATURAL GAS CO | MARICOPA |  | AZ |  | MP 611.1 |  | 110 | 1993-01-21 | 1 | NO |  |  |  | Null | NO | RUPTURE | 600 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 5 |  | 19930121 | 804 | 809 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1950; NMDIA: 30; THK: 0.34; SPEC: API 5L; SMYS: 52000; SEAM: DSAW; MANU: REPUBLIC; MANYR: 1950; LOCLK: ABOVE GROUND; PNAME: RICHARD FAVILA - SENIOR ENGINEER; PHONE: 9155412062; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: MATERIAL; CTEST: NO; MED: NO DATA; TMPS: 0; LKPS: 804 | OUR 30" CALIFORNIA LOOP LINE 1103 RUPTURED DUE TO A SEAM FAILURE. THERE WASA FIRE AND A 600' SEGMENT OF PIPE LINE WAS BLOWN OUT.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930020 | 1993-02-08 | 4280 | EL PASO NATURAL GAS CO | MARICOPA |  | AZ |  | MP 624.6 |  | 2315 | 1993-01-19 | 1 | NO |  |  |  | Null | NO | RUPTURE | 7.9 | 0 | 0 | 50000 | 38262.1951 | 83355.1103 | Null | 1 | 45 |  | 19930120 | 600 | 809 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1992; NMDIA: 26; THK: 0.34; SPEC: API 5L; SMYS: 65000; SEAM: DSAW; MANU: TUBECERO, MEX & NAPA; MANYR: 1992; LOCLK: UNDER WATER; PNAME: RICHARD FAVILA - SENIOR ENGINEER; PHONE: 9155412062; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: NON SPECIFIED; NOTIF: NO; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | OF OUR PIPELINES IN THAT STATE. FLOOD WATERS FROM THE GILA RIVER CAUSED OUR 26" CALIFORNIA LINE 1100 AND OUR 30" CALIFORNIA 1ST LOOP LINE 1103 TO RUPTURE. RELEASED GAS, EXPLODED AND IGNITED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930021 | 1993-02-08 | 4280 | EL PASO NATURAL GAS CO | GREENLEE |  | AZ |  |  |  | 1030 | 1993-01-19 | 1 | NO |  |  |  | Null | NO | RUPTURE | 2.3 | 0 | 0 | 50000 | 38262.1951 | 83355.1103 | Null | 2 | 52 |  | 19930119 | 380 | 650 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1941; NMDIA: 8.63; THK: 0.28; SMYS: 0; MANYR: 0; LOCLK: UNDER WATER; PNAME: RICHARD FAVILA - SENIOR ENGINEER; PHONE: 9155412062; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: NON SPECIFIED; NOTIF: NO; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | OF OUR PIPELINES IN THAT STATE. FLOODS WATERS FROM THE GILA RIVER CAUSED OUR 8 5/8" MORENCI LINE 2006 TO RUPTURE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930022 | 1993-02-08 | 4280 | EL PASO NATURAL GAS CO | GREENLEE |  | AZ |  | MP 4.3 |  | 1455 | 1993-01-19 | 1 | NO |  |  |  | Null | NO | RUPTURE | 1.7 | 0 | 0 | 50000 | 38262.1951 | 83355.1103 | Null | 0 | 10 |  | 19930119 | 445 | 650 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1943; NMDIA: 6.63; THK: 0.28; SMYS: 35000; MANU: REPUBLIC; MANYR: 1943; LOCLK: UNDER WATER; PNAME: RICHARD FAVILA - SENIOR ENGINEER; PHONE: 9155412062; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: NON SPECIFIED; NOTIF: NO; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | RAINS IN THE STATE OF ARIZONA HAVE FLOODED RIVERS, CAUSING DAMAGE TO A NUMBER OF OUR PIPELINES IN THAT STATE. FLOOD WATERS FROM THE GILA RIVER CAUSED OUR 6 5/8" MORENCI LOOP LINE 2007 TO RUPTURE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930023 | 1993-02-09 | 15014 | PACIFIC GAS TRANSMISSION CO | MOYIE SPRINGS | BOUNDARY | ID | 83845 | M.P. 19.3 | 4619 + 98 | 950 | 1993-01-07 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 85000 | 65045.7317 | 141703.6876 | Null | 0 | 0 |  | 19930111 | 781 | 911 | BY TEST | 1142 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: NON SPECIFIED; MLKD: OTHER; MLKDO: NON SPECIFIED; PRTSY: PIPELINE; PRTYR: 1992; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: OTHER; PNAME: THOMAS J CUSWORTH - OPERATIONS MANAGER; PHONE: 5095340657; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | MAINLINE RELIEF VALVE WITH A SET PRESSURE OF 930 PSIG OPENED PREMATURELY AT A LINE PRESSURE OF 781 PSIG. FATIGUE FAILURE OF A 1/4-INCH VALVE PREVENTED AUTOMATIC CLOSING OF THE RELIEF VALVE. DAMAGE TO FACILITIES WAS LESS THAN $1,000 AND CONSISTED ONLY OF A 1/4 INCH VALVE AND A PRESSURE SWITCH, BOTH OF WHICH FAILED IN FATIGUE, PROBABLY DUE TO VIBRATIONS CAUSED BY THE BLOWING GAS.THE AREA WAS NEVER UNSAFE AS THE FACILITY WAS DESIGNED FOR BLOWING GAS TO THE ATMOSPHERE, BUT BECAUSE IT IS A REMOTE LOCATION, IT WAS APPROXIMATELY 1 HOUR AND 15 MINUTES BEFORE THE GAS WAS SHUT OFF. THE INCIDENT OCCURRED AT A NEWFACILITY THAT HAS BEEN IN SERVICE ONLY FOUR MONTHS.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930024 | 1993-02-09 | 19570 | TRANSCO GAS PIPELINE CORP | CAMPBELL | CAMPBELL | VA |  | 1437 89 | 2694 + 40 | 1100 | 1993-01-21 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 54000 | 41323.1707 | 90023.5192 | Null | 24 | 45 |  | 19930121 | 690 | 770 | BY CFR 192.619(A)(3) |  | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1955; NMDIA: 30; THK: 0.31; SPEC: API-5LX; SMYS: 52000; SEAM: DSA; MANU: NATIONAL TUBE; MANYR: 1955; LOCLK: ABOVE GROUND; PNAME: B R LANDES - STAFF COMPLIANCE ANALYST; PHONE: 7134392001; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CAULC: MATERIAL; CTEST: Null; TMPS: 0; LKPS: 0
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930026 | 1993-02-12 | 26330 | ENOGEX INC (EX. MUSTANG FUEL CORP) | ENID | GARFIELD | OK |  |  |  | 630 | 1993-01-10 | 1 | NO |  |  | OK | Null | NO | RUPTURE | 0 | 0 | 0 | 80000 | 61219.5122 | 133368.1765 | Null | 1 | 45 |  | 19930110 | 0 | 30 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: STORAGE TANK; MLKD: STEEL; PRTSY: OTHER; PRTSO: NON SPECIFIED; PRTYR: 0; NMDIA: 0; THK: 0.19; SPEC: SA285C; SMYS: 0; MANU: CONTINENTAL; MANYR: 365; LOCLK: ABOVE GROUND; PNAME: STEVE RUSHING - MGR SAFETY; PHONE: 4055257788; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | ON JANUARY 10, 1993, AT APPROXIMATELY 6:30 A.M., A LOW PRESSURE STORAGE TANKAT THE ENID POWER PLANT STATION FAILED. THE PRESSURE AT WHICH THE FAILURE OCCURRED IS STILL UNKNOWN. THERE WERE NO DEATHS OR INJURIES INVOLVED AND FIREDID NOT OCCUR AS A RESULT OF THIS FAILURE. THE LOCATION OF THE ENID POWER PLANT REGULATOR STATION IS GARFIELD COUNTY, OKLAHOMA, SECTION 19, TOWNSHIP 22 NORTH, RANGE 6 WEST. THE AREA IS PRIMARILY RURAL WITH A FEW INDUSTRAIL BUILDINGS IN THE AREA. DAMAGE TO SURROUNDING BUILDINGS WAS MAINLY BLOWN OUT WINDOWS, LOOSE LIGHT FIXTURES AND MINOR EXTERIOR DAMAGE, ALTHOUGH ONE BUILDING DIDRECEIVE MODERATE INTERIOR DAMAGE. OUR STATION PIPING AND COMPONENTS DID RECEIVE EXTENSIVE DAMAGE IN THE IMMEDIATE AREA WHERE THE STORAGE TANK WAS LOCATED. THE INLET SEPARATOR DUMP VALVE MALFUNCTIONED, CAUSING THE VALVE TO OPEN.IT APPEARS THAT LIQUIDS IN THE EXTERNAL FLOAT DISPLACEMENT CHAMBER BEGAN TO FREEZE AND EXPAND. THIS CAUSED THE DISPLACER TO RISE, SENDING SUPPLY GAS TO THE DUMP VALVE, WHICH THEN BEGAN TO OPEN. WITH THE DISPLACER FROZEN IN A RAISED POSITION, THE DUMP VALVE REMAINED PARTIALLY OR FULLY OPEN, DUMPING WHAT LIQUID WAS IN THE SEPARATOR INTO THE STORAGE TANK AND THEN ALLOWED HIGH PRESSURE GAS TO FILL THE STORAGE TANK, INCREASING ITS INTERNAL PRESSUREEE. THE RELIEF VALVE WAS OPEN AND RELIEVING CONTINOUSLY. AS THE RESULT OF THE LOW AMBIENTAIR TEMPERATURES OF 25 DEGRESS F, HYDRATES FORMED WHICH PLUGGED OFF THE RELIEF VALVE, CAUSING PRESSURE IN THE TANK TO INCREASE UNTIL THE TANK RUPTURED. THE RELIEF VALVE WAS SET AT 35 PSIG AND THE OPERATING PRESSURE OF THE STORAGETANK WAS 30 PSIG. ALTHOUGH THE RELIEF VALVE WAS SET 5 PSIG ABOVE THE STORAGE TANK'S OPERATING PRESSURE, WE DO NOT FEEL THIS CONTRIBUTED TO THE RUPTURE.OWEVER, THIS FINDING DID RAISE A CONCERN ON OUR PART OF THE QUALITY OF WORK BEING DONE BY THE CONTRACTOR PERFORMING RELIEF VALVE TESTING. WE ARE IN THE PROCESS OF REVIEWING ALL OUR RELIEF VALVE SETTINGS TO ENSURE THAT THEY ARE NOT SET ABOVE MAXIMUM ALLOWABLE OPERATING PRESSURES.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930027 | 1993-02-17 | 12270 | M I G C INC | RECHASE | CAMPBELL | WY | 82717 |  |  | 1200 | 1993-01-15 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 100000 | 76524.3902 | 166710.2207 | Null | 0 | 30 |  |  | 250 | 1200 | BY TEST | 1565 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: COMPRESSOR ENGINE & CYL; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1987; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: OTHER; LOCLO: COMPRESSOR STATION; PNAME: R F BECK TRANSMISSION; PHONE: 3076829710; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | ON JANUARY 15, 1993 A FIRE OCCURRED IN A MIGC, INC. COMPRESSOR STATION. DAMAGES OCCURRED TO THE WHITE ENGINE WHICH DRIVES ONE COMPRESSOR. TELEPHONIC MOTICE TO 1-800-424-8802 WAS MADE ON JANUARY 1118, 1993. TELEPHONIC NOTICE TO1-777-7427, STATE OF WYOMING WAS MADE ON JANUARY 18, 1993. MR. JOHN JACQUOT RESPONDED TO THE CALL. THE TIME LAPSE BETWEEN JANUARY 15, DATE OF THE INCIDENT AND JANUARY 18, THE DATE OF REPORTING WAS NECESSARY DUE TO THE DIFFICULTY OF DETERMINING THE AMOUNT OF DAMAGE.
2021-02-26 10:36 | YES | YES | GG (Gas Gathering) | 19930028 | 1993-02-23 | 719 | ASHLAND EXPLORATION CO | TURKEY CREEK | PIKE | KY | 41570 |  |  | 2215 | 1993-01-20 | 3 | NO |  |  | KY | Null | NO | LEAK | 0 | 0 | 1 | 0 | 0 | 0 | Null | 2 | 30 |  | 19930121 | 0 | 0 | NO DATA | 0 | CORROSION | CORROSION | EXTERNAL | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTSO: 1; PRTYR: 0; NMDIA: 2; THK: 0; SMYS: 0; MANYR: 0; LOCLK: UNDER GROUND; PNAME: RICK J - FACILITIES ENGINEER; PHONE: 6063295260; LOC: EXTERNALLY; ADESC: GENERAL CORROSION; CAUCR: GALVANIC; COAT: BARE; PROT: NO; CPYR: 0; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | INVESTIGATORS OF THE SURROUNDING AREA DISCOVERED A LEAK ON AN UNKNOWN SECTION OF ABANDONED PIPELINE OWNED BY AEI. THIS LEAK WAS A POSSIBLE SOURCE OF THEEXPLOSION ALTHOUGH THE ACTUAL SOURCE WAS NEVER CONCLUSIVELY CONFIRMED. INJURED PARTY RELEASED FROM HOSPITAL AND BACK TO WORK WITH NO APPARENT PERMANENT INJURY.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19930029 | 1993-02-23 | 25172 | UNOCAL NORTH AMERICAN OIL & GAS DIV | HIGH ISLAND |  | TX |  |  |  | 1400 | 1993-01-23 |  | YES | HIGH ISLAND | A-334 |  | YES | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 0 |  | 19930125 | 1000 | 1440 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1979 | 6.63 | 0.43 | ASTM-A-53 ASME-SA-53 | 40800 | SEAMLESS |  | U.S STEEL | 1976 | ABOVE GROUND |  | KEVIN L BERRY - PRODUCTION ENGINEER | 3182666919 | EXTERNALLY | GENERAL CORROSION |  | OTHER | SPLASHTRON COATING FAILED | COATED | NO | 0 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | LEAK WAS FOUND IN 6 -5/8" RISER ABOVE THE WATER LEVEL. THE SPLASHTRON COATING WORE OFF IN THE AREA OF THE LEAK ALLOWING CORROSION TO OCCUR. THE SUBJECTPIPE WAS REPLACED AND THE SYSTEM WAS PRESSURE TESTED AND PLACED BACK ON PRODUCTION 1/29/93.7
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930031 | 1993-02-16 | 20230 | UNITED GAS PIPELINE CO | PLAQUEMINES |  | LA |  |  | 4+00 | 745 | 1993-01-13 | 1 | NO |  |  | LA | Null | Null | OTHER | 0 | 0 | 0 | 52000 | 39792.6829 | 86689.3148 | Null | 3 | 15 |  |  | 357 | 815 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: GIRTH; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1977; NMDIA: 12; THK: 0.38; SPEC: X-42; SMYS: 0; SEAM: SMLS; MANYR: 0; LOCLK: UNDER WATER; PNAME: RONALD BLANCHARD; PHONE: 5044675903; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | METULURGICAL REPORT & FURTHER INVESTIGATION IN PROGRESS.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930036 | 1993-02-23 | 19160 | TENNESSEE GAS PIPELINE CO | SANGUS | ESSEX | MA |  | 270C-401+ 0.21 |  | 1700 | 1993-01-24 | 3 | NO |  |  |  | Null | Null | OTHER | 0 | 0 | 0 | 58000 | 44384.1463 | 96691.928 | Null | 1 | 15 |  | 19930124 | 615 | 815 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1951; NMDIA: 10.75; THK: 0.28; SPEC: 5L; SMYS: 42000; MANU: YOUNGSTOWN; MANYR: 1951; LOCLK: UNDER GROUND; PNAME: L A SALINAS - STAFF CIVIL ENGINEER; PHONE: 7137572281; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | PIPELINE BEGAN TO LEAK WHEN THE SOIL OVERBURDEN CAUSED EXCESSIVE PRESSURE ONTHE PIPELINE IN AN AREA OF SOFT, UNSTABLE SOIL. (LARGE VOLUMES OF FILL WEREPLACED ON TOP OF PIPE IN A WET/BOGGY AREA).
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930041 | 1993-03-11 | 101 | TRISTAR GAS COMPANY | VIDOR | ORANGE | TX | 77662 | ENRON METER/REGULATOR STA | 0+00 | 2200 | 1993-01-12 | 3 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 5000 | 3826.2195 | 8335.511 | Null | 1 | 0 |  | 19930119 | 310 | 500 | BY TEST | 750 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | OTHER | NON SPECIFIED | STEEL |  | REGULATOR/METERING SYSTEM |  | 1990 | 2 | 0.15 | API-51X | 42000 | ERW | PRESSURE REDUCI | KIMRAY | 1989 | OTHER |  | MICHAEL W WOOD | 2147395001 | EXTERNALLY | OTHER | NON SPECIFIEDD | OTHER | HIGHLY CORROSIVE SOIL | COATED | YES | 1990 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | ON JANUARY 12, 1993 AT APPROXIMATELY 10:00P.M., THE REGULATOR AT THE GAS SUPPLY SOURCE ON TRISTAR GAS COMPANY'S PIPELINE MALFUNCTION. THIS ALLOWED THE PRESSURE ON TRISTAR'S LINE TO REACH 310 PSIG. THE REGULATOR AT THE DELIVERY POINT TO TRINITY INDUSTRIES FACILITY DIDN'T REACT QUICKLY ENOUGH TO PREVENT TRINITY'S SYSTEM FROM BEING EXPOSED TO THIS PRESSURE. TRINITY HAS NO OVERPRESSURE PROTECTION ON THEIR SYSTEM. THIS AMOUNT OF PRESSURE DAMAGED A PORTION OFTHEIR SYTEM. ON JANUARY 15, 1993 A LEAK WAS DISCOVERED ON TRISTAR'S PIPELINE. DUE TO THE CORROSION EXISTING ON THIS PIPELINE, IT IS SUSPECTED THAT THE HIGH PRESSURE CAUSED THE LEAK.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19930042 | 1993-01-21 | 405 | ANR PIPELINE CO | WEST CAMERON |  | LA |  | X= 1,349,165 | Y= 145,420 | 1325 | 1992-12-28 |  | YES | W.C. | 331 |  | YES | NO | LEAK | 0 | 0 | 0 | 52000 | 40726.8945 | 88724.5171 | Null | 0 | 0 |  | 19921228 | 1000 | 1440 | BY TEST | 2160 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1979 | 12 | 0.38 | API 5LX-52 | 52000 |  |  |  | 0 | UNDER WATER |  | DONALD E CROSS | 3134962460 | INTERNALLY | OTHER | NON SPECIFIED | OTHER | NON SPECIFIED | COATED | YES | 1979 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930045 | 1993-03-09 | 20230 | UNITED GAS PIPELINE CO | REFUGIO | REFUGIO | TX | 78377 | 8.98 | 473 + 91 | 1000 | 1993-02-10 | 1 | NO |  |  | TX | Null | NO | LEAK | 0 | 0 | 0 | 55000 | 42088.4146 | 91690.6214 | Null | 2 | 0 |  | 19930210 | 535 | 780 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1952; NMDIA: 30; THK: 0.38; SPEC: API 5LX; SMYS: 52000; SEAM: ELECTRIC FLASH; MANU: A.O. SMITH; MANYR: 0; LOCLK: UNDER GROUND; PNAME: R.B. CONLY - DIVISION ENGINEER; PHONE: 7132294537; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: MATERIAL; CTEST: YES; MED: GAS; TMPS: 1; LKPS: 980 | THE MATERIAL DEFECT WAS A "HARDSPOT" ON THE PIPE DUE TO THE MANUFACTURE'S PROCESS. THE "HARDSPOT" WAS PREVIOUSLY INDENTIFIED AND REINFORCED WITH A SLEEVE. THE REINFORCING SLEEVE CONTAINED THE DEFECT.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930051 | 1993-03-29 | 18484 | SOUTHERN CALIFORNIA GAS CO |  | SAN BERNARDINO | CA |  | MP 187.29 | 9888+91.2 | 820 | 1993-02-27 | 1 | NO |  |  | CA | Null | NO | RUPTURE | 30 | 0 | 0 | 500000 | 382621.9512 | 833551.1034 | Null | 2 | 35 |  | 19930301 | 584 | 0 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1947; NMDIA: 30; THK: 0.28; SPEC: X-52; SMYS: 52000; SEAM: SEAMLESS; MANYR: 0; LOCLK: UNDER WATER; PNAME: R L RUDZIK - MGR OF TRANSMISSION & UNDERGROUND STORAGE STAFF; PHONE: 2132441200; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: NO; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | ON FEBRUARY 27, 1993, AT 8:20 A.M., WE REALIZED A DROP IN PRESSURE ON LINE 2000. OUR INVESTIGATION REVEALED THAT A LANDSLIDE, ATTRIBUTE TO RECENT RAINS,STRESSED THE LINE TO THE POINT OF FAILURE. PERMANENT REPAIRS WERE COMPLETEDBY RELOCATING 2033' AROUND THE LANDSLIDE AREA. SERVICE WAS INTERRUPTED AT 2:17 P.M. TO SIX CUSTOMERS AND RESTORES WERE COMPLETED AT 10:45 P.M. THERE WERE NO FIRES OR INJURIES ASSOCIATED WITH THIS INCIDENT. GAS LOSS ASSOCIATED WITH THIS INCIDENT WAS 9,801.94 MCF. ESTIMATED COSTS ASSOCIATED WITH THIS INCIDENT WERE $500,000.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930052 | 1993-03-06 | 10030 | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | NE/4- 23-T18S-R16W | RUSH | KS | 67565 |  | 83+85 | 330 | 1993-03-04 | 1 | NO |  |  |  | Null | Null | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 10 |  | 19930304 | 420 | 460 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 0; NMDIA: 12; THK: 0.25; SPEC: API-5LX; SMYS: 52000; SEAM: ERW; MANU: STUPP; MANYR: 1967; LOCLK: UNDER WATER; PNAME: JAMES R PHILLIPS; PHONE: 4024622141; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | FOR EXAMINATION UNTIL WINTER SNOW MELT DECREASES. A TEMPORARY BYPASS LINE HAS BEEN INSTALLED ON AN EXISTING COUNTY ROAD BRIDGE NEARBY. THE PIPELINE SECTION CANNOT BE REMOVED UNTIL THE HEAVY STREAM FLOW RECEDES. THIS AREA HAS RECEIVED CONSIDERABLE AMOUNTS OF SNOW THIS WINTER AND THE SPRING MELTING AND DRAINAGE WILL CONTINUE FOR SOME TIME BEFORE A PERMANENT REPAIR CAN BE MADE. SERVICE WAS TEMPORARILY INTERRUPTED TO 4 RURAL CUSTOMERS.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930053 | 1993-03-18 | 2616 | COLUMBIA GAS TRANSMISSION CORP | MILLERSBURG | HOLMES | OH | 44654 |  | 35+01 | 1000 | 1993-03-01 | 2 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 50000 | 38262.1951 | 83355.1103 | Null | 0 | 25 |  | 19930301 | 106 | 200 | BY TEST | 200 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1951; NMDIA: 7; THK: 0.32; SPEC: API 5A; SMYS: 55000; SEAM: SEAMLESS; MANYR: 0; LOCLK: UNDER GROUND; PNAME: S J CHOBY - MGR, CODES, STANDARDS; PHONE: 3043572349; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PERMANENT LINE MARKER 20"; STAT: YES; CTEST: Null | PRIVATE PROPERTY OWNER'S BULLDOZER BROKE MAINLINE FEED TO TOWN OF MILLERSBURG, OHIO. GAS SERVICE WAS INTERRUPTED TO APPROXIMATELY 1,330 COLUMBIA GAS OF OHIO DISTRIBUTION CUSTOMERS FOR 24-HOUR PERIOD.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930054 | 1993-03-23 | 10030 | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | NW/4 SEC. 35-T2N-R15W | FRANKLIN | NE |  |  | 154+29 | 30 | 1993-03-07 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | Null | 1 | 15 |  | 19930307 | 150 | 150 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1952; NMDIA: 1.13; THK: 0.14; SMYS: 0; MANYR: 0; LOCLK: UNDER WATER; PNAME: JAMES R PHILLIPS; PHONE: 4024622141; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | PIPELINE RUPTURED UNDER FLOWING STREAM. RUPTURED PORTION CAN NOT BE REMOVEDFOR EXAMINATION UNTIL WINTER SNOW MELT DECREASES.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930055 | 1993-03-19 | 18484 | SOUTHERN CALIFORNIA GAS CO | LOS ANGELES | LOS ANGELES | CA |  | M.P. 135.13 |  | 850 | 1993-02-24 | 1 | NO |  |  |  | Null | YES | RUPTURE | 3 | 0 | 0 | 552628 | 422895.2073 | 921287.3583 | Null | 1 | 10 |  | 19930224 | 215 | 317 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: GIRTH; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1931; NMDIA: 26; THK: 0.25; SMYS: 0; MANU: A.O. SMITH; MANYR: 1930; LOCLK: UNDER GROUND; PNAME: R L RUDZIK - MGR TRANS & UNDERGROUND STORAGE STAFF; PHONE: 2132441200; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: NO; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | ON FEBRUARY 24, 1993, AT 9:00 A.M., WE RECEIVED A REPORT THAT LINE 85 HAD RUPTURED AND WAS ON FIRE. OUR INVESTIGATION REVEALED THAT A LANDSLIDE, ATTRIBUTED TO RECENT RAINS, STRESS THE LINE TO THE POINT OF FAILURE AND THE ESCAPINGGAS WAS THEN IGNITED BY OVERHEAD ELECTRICAL FACILITIES. PERMANENT REPAIRS WERE MADE BY CAPPING BOTH ENDS OF THE DAMAGED SECTION. A RELOCATION OF 2100' AROUND THE LANDSIDE AREA IS PLANNED. SERVICE WAS INTERRUPTED AT 10:30 A.M. TO NINETY CUSTOMERS LOCATED AT THE PARADISE RANCH MOBILE HOME PARK AND RESTORES WERE COMPLETED AT 7:30 P.M. THERE WERE NO INJURIES ASSOCIATED WITH THIS INCIDENT. ESTIMATED COSTS ASSOCIATED WITH THIS INCIDENT WERE $552,628. DOT NOTIFICATION 02/24/93, REFERENCE REPORT# 159480.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930059 | 1993-03-15 | 19570 | TRANSCO GAS PIPELINE CORP | MATAGORDA ISLAND |  | TX |  | 19.16 | 1011 + 65 | 1000 | 1993-02-20 |  | YES | MATA 1 | 681 |  | YES | NO | LEAK | 0 | 0 | 0 | 56000 | 42853.6585 | 93357.7236 | Null | 52 | 0 |  | 19930221 | 840 | 1250 | BY TEST | 2117 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | VALVE |  | STEEL |  | PIPELINE |  | 1985 | 0 | 0 |  | 0 |  | 12" ANSI 900 SE | GROVE | 1984 | UNDER WATER |  | B R LANDES - STAFF COMPLIANCE ANALYST | 7134392001 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | 12" ANSI 900# BALL TAP VALVE | YES | 19840811 | WATER |  | 8 | 3295 | AT APPROXIMATELY 10:00 A.M. ON FEBRUARY 20, 1993 ENRON PERSONNEL REPORTED TOTGPL'S GAS CONTROL THAT BUBBLES WERE SIGHTED IN THE VICINITY OF TGPL'S PIPELINE IN MATAGORDA ISLAND BLOCK 681. LATE AFTERNOON IN FEBRUARY 20, 1993, TRANSCO PERSONNEL WERE ABLE TO CONFIRM THAT THE LEAK WAS FROM A TGPL PIPELINE. DIVERS WERE DISPATCHED TO THE LEAK LOCATION DURING THE MORNING OF FEBRUARY 21,1993 AND FOUND THAT THE LEAK WAS COMING FROM THE VENT PLUG ON THE 12' TAP VALVE IN BLOCK 681. WHILE IN THE PROCESS OF CLOSING TO TAP VALVE SO THAT THE MINOR REPAIR COULD BE MADE, THE 1/2" VENT PLUG BEGAN TO LEAK MORE SEVERELY. ATAPPROXIMATELY 3:00 P.M. ON FEBRUARY 21, 1993 THE DECISION WAS MADE TO SHUT-IN AND BLOW DOWN THE 20" PIPELINE FROM MATAGORDA ISLAND BLOCK 669 AND MAKE THENECESSARY REPAIR.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930071 | 1993-04-27 | 11337 | BRAZOS PIPELINE SYSTEM | COLLEGE STATION | BRAZOS | TX | 77840 |  |  | 1945 | 1993-03-18 | 1 | NO |  |  | TX | Null | NO | LEAK | 0 | 0 | 0 | 300000 | 229573.1707 | 500130.662 | Null | 0 | 30 |  | 19930318 | 1175 | 1200 | BY TEST | 1800 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | OTHER | COMPRESSOR | STEEL |  | COMPRESSOR STATION |  | 1991 | 0.59 | 0.59 | ASTM-A-106 | 35000 | SEAMLESS |  |  | 0 | ABOVE GROUND |  | MICHAEL HOWETH | 8173251321 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION | 1/2 INCH HEAVY DUTY PIPE NIPPLE CONNECTING THE CYL | Null |  | NO DATA |  | 0 | 0 | AAA 1/2 INCH HEAVY DUTY PIPE NIPPLE RATED AT 6,125 PSI CRACKED IN THE THREADS CAUSING THE RELEASE OF GAS WHICH IGNITED CAUSING THE RELEASE OF GAS WHICH IGNITED CAUSING THE 1969 WAUKESHA GAS COMPRESSOR TO CATCH ON FIRE. THIS IS A MANUFACTURED COMPONENT.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930075 | 1993-04-26 | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | NEW YORK | NEW YORK | NY | 10034 | VALVES 2065 & 2066 |  | 1720 | 1993-03-23 | 4 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 0 |  | 19930324 | 280 | 350 | BY TEST | 525 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1951; NMDIA: 30; THK: 0.5; SPEC: ASTM A134; SMYS: 0; MANYR: 0; LOCLK: OTHER; PNAME: RANDY F. GOFFRED; PHONE: 2124602838; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | A CRACK DEVELOPED ON A SEGMENT OF THE NEW YORK FACILITIES.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930082 | 1993-05-25 | 13845 | NORTHWEST PIPELINE CORP | CORTEZ | MONTEZUMA | CO |  | 56.5 | 2984 + 57 | 155 | 1993-05-02 | 1 | NO | N |  |  | Null | Null | RUPTURE | 66 | 0 | 0 | 365500 | 279696.6463 | 609325.8566 | Null | 4 | 5 |  | 19930502 | 780 | 809 | BY CFR 192.619(A)(3) | 880 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1955 | 26 | 0.28 | API 5LX | 52000 | DOUBLE SUNMERGE |  | CONSOL, WEST | 1955 | UNDER GROUND |  | JAMES W SMITH - MGR SAFETY & ENVIRO | 8015846906 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL |  | YES | 19560413 | GAS |  | 1 | 878 | PIPE WAS SUBJECTED TO LINEALOG SURVEY IN 1972 AND NO CORROSION WAS IDENTIFIED IN THIS AREA AT THAT TIME. VISUAL EXAMINATION OF THE DAMAGED PIPE FOUND THE INTERNAL AND EXTERNAL CONDITION TO BE GOOD. THEE CAUSE OF THE FAILURE IS STILL BEING INVESTIGATED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930086 | 1993-05-18 | 10030 | K N ENERGY INC(KANSAS NEBRASKA GAS CO) |  | ANTELOPE | NE |  |  | 2 +10 | 1030 | 1993-04-27 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 30 |  | 19930427 | 670 | 1440 | BY TEST | 2100 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1985; NMDIA: 2.38; THK: 0.13; SPEC: API-5L; SMYS: 35000; SEAM: ERW; MANU: LTV; MANYR: 1985; LOCLK: UNDER GROUND; PNAME: JAMES PHILLIPS - MGR CONSTR; PHONE: 4024622141; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; MARK: YES; MRKTP: PIN FLAGS & LINE MARKER; STAT: NO; CTEST: Null | A 2-INCH STEEL, BURIED TRANSMISSION PIPELINE WAS HIT BY A THIRD PARTY CONTRACEXPLOSION DEMOLISHED STRUCTURE. (SUSPECTED OF BEING FUELED BY NATURAL GAS) LETOR IN ANTELOPE COUNTY, NEBRASKA ON APRIL 27, 1993. IGNITION DID NOT OCCUR AAK WAS DETECTED ON SERVICE LINE IN FRONT OF STRUCTURE WITHING 24" OF UNDERPINND THERE WERE NO INJURIES OR FATALITIES RESULTING FROM THE INCIDENT. SERVICENING WITH CAUSE OF LEAK STILL UNDER INVESTIGATION. END OF PIPE, WHERE THREADE WAS TEMPORARILY INTERRUPTED TO 219 CUSTOMERS IN ORCHARD, NE AND 15 RURUL CUSD FOR ATTACHMENT OF SCREW ELL, HAD APPARENT STRESS FRACTURE (AT THREADS CAUSITOMERS. THE PIPELINE DIG-IN WAS CAUSED BY A CONTRACTOR DIGGING HOLES FOR ANNG LEAKAGE. CURRENTLY SUSPECTED CAUSE OF LEAK WAS GROUND SHIFT AND STRUCTUREELECTRIC POLE RELOCATION PROJECT. THE 2-INCH LINE WAS PREVIOUSLY LOCATED ANDSHIFTING DUE TO EXPLOSION. MARKED WITH PIN FLAGS BY A K N EMPLOYEE AND A LINE MARKER WAS LOCATED NEARBY. TELEPHONIC REPORT OF THE INCIDENT WAS MADE ON REPORT NO.170068 TP PETTY OFFICER EVANSON AT THE DEPARTMENT OF TRANSPORTATION ON APRIL 27, 1993. THE CALL WAS MADE OAFTER COMPANY OFFICIALS DETERMINED THAT NOTIFICATION WAS DESIREDEVEN THOUGH THE INCIDENT DID NOT CAUSE OVER $50,000 IN DAMAGE, INCLUDING GASLOSS.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930089 | 1993-05-17 | 19590 | TRANSOK INC | WETUMKA | HUGHES | OK | 74883 | MILE POST 8.5 LINE #15 | 437+32 | 1530 | 1993-05-10 | 1 | NO |  |  | 1 | Null | YES | LEAK | 0 | 0 | 0 | 600000 | 459146.3415 | 1000261.324 | Null | 0 | 30 |  | 19930511 | 341 | 700 | BY TEST | 1405 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: UNKNOWN AT PRESENT; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1979; NMDIA: 24; THK: 0.34; SPEC: WT X-60 GRADE; SMYS: 1720; SEAM: ERW HIGH FREQUE; VALVE: M&J FULL OPERIN; MANU: STUPP; MANYR: 1979; LOCLK: UNDER WATER; PNAME: DAVID J MATHIS - SAFETY SPECIALIST; PHONE: 9185912326; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | ON MAY 10, 1993 AT 15:30 AN OPERATOR AT TRANSOK'S GREASY CREEK PROCESSING PLANT NOTIFIED THE GAS CONTROL CENTER THAT ALL COMPRESSORS HAD SHUTDOWN DUE TO LOW SUCTION PRESSURE. AT THIS SAME TIME GAS CONTROL WAS NOTICING A PRESSURE LOSS ON THE LINE FEEDING THIS PLANT ( A 24" STEEL PIPELINE DESIGNATED AS LINE#15). GAS CONTROL IMMEDIATELY NOTIFIED THE SOUTHEAST DISTRICT SUPERINTENDENT T.J. BOGLE AND NORTHEAST MONITOR PRESSURE AT THESE SITES ON LINE #115 TO ATTEMPT TO IDENTIFY THE SECTION WITH THE POSSIBLE LEAK. UPON ARRIVAL AT THE NORTH CANADIAN VALVE TWO SOUTHEAST DISTRICT EMPLOYEES, MIKE WINTERS AND RICKY SPRKS, NOTED A PLUME OF WATER RISING FROM THE NORTH CANADIAN RIVER IN THE AREAOF THE PIPELINE RIGHT-OF-WAY. AT 16:10 MIKE WINTERS REPORTED BY RADIO TO GAS CONTROL THAT THEY HAD FOUND THE LEAK AND THAT THEY HAAD CLOSED VALVES # 15-21 AND 15-23 TO COMPLETEE THE ISOLATION OF THIS SECTION OF LINE. THE LEAK APPEARS TO BE APPROX. 50 FEET SOUTH OF THE NORTH BANK OF THE NORTH CANADIAN RIVER. THE ESTIMATED DEPTH OF THE WATER OVER THE LOCATION WHERE THE LEAK OCCURRED IS APPROX. 20 FEET. CONDITIONS ON THE RIVER AT WETUMKA ACCORDING TO THE RIVER FORECAST CENTER ON 5/10/93 AT 15:30 WERE 18.1 FEET AND FLOOD STAGE IS 25.1 FEET. THE AREAA OF THE LEAK IS A CLASS 1 LOCATION WITH THE CLOSEST OCCUPIED RESIDENCE APPROX. 1/4 MILE AWAY. ON 5/11/93 THE TRANSOK ENGINEERING AND CONSTRUCTION DEPARTMENTS BEGAN SURVEYING THE CROSSING FOR REPAIRING OR REPLACING. THE OPTION OF REBORING THE RIVER AND INSTALLING NEW PIPE IS THE OPTION PRESENTLY BEING EXAMINED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930093 | 1993-05-13 | 19325 | TEXAS UTILITIES FUEL CO |  | LIMESTONE | TX | 75860 | 1177.3 MILE POST | 9351+70 | 1500 | 1993-04-16 | 1 | NO |  |  | TX | Null | NO | LEAK | 0 | 0 | 0 | 78876 | 60359.378 | 131494.3537 | Null | 0 | 0 |  | 19930416 | 705 | 973 | BY TEST | 1088 | CORROSION | CORROSION | EXTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1960; NMDIA: 24; THK: 0.31; SPEC: X52; SMYS: 1352; SEAM: EAW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: TIM WERNICKE - SUPERVISOR REGULATORY COMPLIANCE; PHONE: 2148121243; LOC: EXTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: OTHER; COAT: COATED; PROT: YES; CPYR: 0; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | TOP COATING AT LEAK SITE WAS DISBONDED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930096 | 1993-06-18 | 384 | AMAERICAN GAS STORAGE CORP | LOOP | GAINES | TX | 79101 |  |  | 502 | 1993-05-06 | 1 | NO |  |  |  | Null | NO | RUPTURE | 0 | 0 | 0 | 3000000 | 2295731.7073 | 5001306.6202 | Null | 0 | 22 |  | 19930506 | 720 | 2160 | BY TEST | 3290 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1982; NMDIA: 4.5; THK: 0.24; SPEC: A-53; SMYS: 35000; SEAM: SEAMLESS GRADEB; VALVE: ANSI 900; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: STEVE BUSTOS - COMPLIANCE COORDINATOR; PHONE: 8063736042; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: MATERIAL; CTEST: YES; MED: WATER; TMPS: 4; LKPS: 3290
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930099 | 1993-06-15 | 4483 | ENSTAR NATURAL GAS CO | MATANUSKA | SUSITNA BOROUGH | AK |  | M.P. 26 | 1321 + 56 | 535 | 1993-05-28 | 1 | NO |  |  | AK | Null | NO | RUPTURE | 300 | 0 | 0 | 3500000 | 2678353.6585 | 5834857.7236 | Null | 2 | 15 |  | 19930528 | 811 | 1050 | BY TEST | 1610 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: UNKNOWN AT THIS TIME; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1984; NMDIA: 20; THK: 0.5; SPEC: API 5LX; SMYS: 52000; SEAM: E.R.W.; MANU: KAWASAKI STEEL CORP; MANYR: 1984; LOCLK: UNDER WATER; PNAME: DAVID W BREDIN - MGR DISTRIBUTION; PHONE: 9072643745; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: NO; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930101 | 1993-06-09 | 22617 | WILLIAMS NATURAL GAS CO | WICHITA | SEDGWICK | KS | 67217 | 387 + 60 |  | 1900 | 1993-05-12 | 1 | NO |  |  |  | Null | NO | RUPTURE | 2 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 30 |  | 19930512 | 360 | 375 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: GIRTH; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1963; NMDIA: 16; THK: 0.31; SPEC: 2030D; SMYS: 52000; SEAM: ELECTRIC WELD; MANU: A O SMITH; MANYR: 1963; LOCLK: UNDER WATER; PNAME: WARREN A ETHERIDGE - PIPELINE SAFETY COORD; PHONE: 9185884427; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: NO; MARK: YES; MRKTP: 0; STAT: Null; CTEST: Null | TURBULENT FLOODWATERS IN THE ARKANSAS RIVER CAUSED THE 16" LINE TO SEPARATE. THE LINE WAS CAPPED ON EACH SIDE OF THE RIVER. THE REPAIRS TO THE LINE WILL BE MADE AFTER THE WATER RECEDES.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930102 | 1993-06-09 | 18152 | SEA ROBIN PIPELINE CO | EAST CAMERON |  | LA |  | 12.98 | 685 + 19 | 1105 | 1993-05-12 |  | YES | E.C. | 270 |  | YES | NO | LEAK | 0 | 0 | 0 | 206000 | 157640.2439 | 343423.0546 | Null | 0 | 0 |  | 19930512 | 1100 | 1306 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1973; NMDIA: 20; THK: 0.44; SPEC: API 5LX; SMYS: 60000; SEAM: ERW; MANYR: 1972; LOCLK: UNDER WATER; PNAME: K PETERS - SUPV. PIPELINE SAFETY COMPLIANCE; PHONE: 2053257632; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | TWO SMALL PINHOLE LEAKS WERE DISCOVERED AT THE 6 O'CLOCK POSITION ON THE PIPE. INSPECTION BY DIVERS REVEALED NO EVIDENCE OF COATING DAMAGE OR EXTERNAL DETERIORATION OF THE PIPE. AN ULTRASONIC THICKNESS GAUGE WAS EMPLOYED TO CHECK THE PIPE WALL THICKNESS AROUND THE CIRCUMFERENCE OF THE PIPE AT THE POINT OF THE LEAKS AND WITHIN SEVERAL FEET EITHERSIDE OF THE LEAK LOCATION. NO METAL LOSS OR EVIDENCE OF DECREASED WALL THICKNESS WAS FOUND AS MIGHT BE EXPECTEDIF THE LEAKS WERE ATTRIBUTABLE TO INTERNAL CORROSION. THE LEAKS WERE NOT INTHE WELD SEAM OF THE PIPE. THE INVESTIGATION PRODUCED NO OTHER EVIDENCE THAT WOULD ALLOW DETERMINATION OF THE CAUSE OF THE LEAKS. A PERMANENT REPAIR WAS MADE BY INSTALLING AN ANSI 900# SERIES MECHANICAL CLAMP.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930103 | 1993-06-09 | 15518 | PIEDMONT NATURAL GAS CO INC | MORGANTON | BURKE | NC | 28655 | 600' EAST OF SR 1769 |  | 1005 | 1993-05-12 | 3 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 100000 | 76524.3902 | 166710.2207 | Null | 2 | 48 |  | 19930512 | 600 | 650 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1958; NMDIA: 6; THK: 0.19; SPEC: API 5 LB; SMYS: 35000; MANYR: 0; LOCLK: UNDER GROUND; PNAME: RONALD W COBB - MGR - MATERIALS MGMT; PHONE: 7043643120; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; MARK: YES; MRKTP: EXPOSED 100' BOTH SIDES O; STAT: YES; CTEST: Null | CONTRACTOR INSTALLING NEW PIPELINE PARALLEL TO EXISTING LINE FOR PIEDMONT DAMAGED EXISTING LINE DURING EXCAVATION. CONTRACTOR WAS OBLIGATED TO LOCATE EXISTING LINE BY EXPOSING IT WAS NEEDED. THE INTERVAL IN THE AREA OF DAMAGE WAS TOO LARGE. AS A RESULT OF THE DAMAGE, SERVICE WAS INTERRUPTED TO 3,368 CUSTOMERS.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930105 | 1993-06-09 | 2620 | COLUMBIA GULF TRANSMISSION CO | EUGENE ISLAND |  | LA |  |  | X = 1,897,315; Y- -50,189 | 1300 | 1993-05-19 |  | YES | EI | 250B |  | YES | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19930519 | 1050 | 1250 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1975 | 24 | 0.44 | API 5L | 60000 | DSAW |  | U S STEEL | 1974 | UNDER WATER |  | S J CHOBY - MGR CODES & STDS. | 3043572349 | INTERNALLY | OTHER | ISOLATED CORROSION CELL | OTHER | UNKNOWN PENDING LAB ANALY | COATED | YES | 1975 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | SCENARIO: LEAK DISCOVERED BY SEA ROBIN HELICOPTER PILOT 5/19/93. DIVING CONTRACTOR MOBILZED MIDNIGHT 5/20/93. LEAK CONFIRMED TO BE COLUMIA PIPELINE 9:00 PM 5/22/93. PINHOLE LEAK REPAIR COMPLETED WITH HYDROTECH SUB-SEA REPAIR CLAMP 7:00 PM 5/25/93.ISOLATED CORROSION CELL SINGLE PIT STATUS WAS DETERMINED FROM RESULTS OFEXTENSIVE ULTRASONIC INSPECTION OF THE AFFECTED AREA. A THIRTY DAYBATERIOLOGICAL COUNT LABORATORY ANALYSIS IS UNDERWAY TO DETERMINE WHETHERTHE CAUSE WAS FROM CHEMICAL ATTACK OR BACTERIOLOGICAL ATTACK.APPROPRIATE INHIBITOR PROGRAM WILL BE INITIATED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930106 | 1993-06-01 | 881 | SELKIRK COGEN PARTNERS | SELKIRK | ALBANY | NY | 12158 | W4 |  | 900 | 1993-05-01 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 40000 | 30609.7561 | 66684.0883 | Null | 55 | 43 |  | 19930503 | 700 | 760 | BY TEST | 1140 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1991; NMDIA: 12; THK: 0.25; SPEC: API - 5L GRADE X-42; SMYS: 42000; SEAM: ELECTRICAL RESI; MANYR: 0; LOCLK: UNDER GROUND; PNAME: MICHAEL J ROZDOLSKI - SYSTEMS MANAGER; PHONE: 5184755157; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: YELLOW PIPE MARKERS AT EA; STAT: Null; CTEST: Null | BECHTEL CORPORATION OF NEVADA EXPOSED AND DAMAGED A 3 FOOT LONG SECTION OF THE PIPELINE DURING EXCAVATION ACTIVITIES ON THE PHASE II SITE. DATE OF NOTIFICATION : 05/03/93. TIME OF NOTIFICATION : 8:00 AM. RESPONSE: UPON NOTIFICATION THAT DAMAGE TO THE PIPELINE HAD OCCURRED, THE SELKIRK COGEN PROJECT OPERATOR MADE ARRANGEMENTS TO ENTER THE EXCAVATION FOR A CLOSER EVALUATION OF THE DAMAGE. THE EXCAVATION WAS ENTERED AND THE DAMAGE WAS INSPECTED BY THE OPERATOR AND BECHTEL CONSTRUCTION AT APPROXIMATELY 13:00 SEVERAL DENTS AND GOUGES OF THE OUTSIDE SURFACE OF THE PIPE WAS FOUND. THE DAMAGES AREAS WERE MEASURED AND THE PHOTOS WERE TAKEN. THE PIPE WAS FOUND TO CONTAIN SEVERAL DENTS,THE LARGEST OF WHICH WAS APPROXIMATELY 5/8 INCH DEEP. THE DAMAGE WAS WITHIN3 FEET OF PIPELINE WELD NUMBER W4. FOLLOWING THE INSPECTION, THE DECISION WAS MADE TO IMMEDIATELY DEPRESSURIZE THE LINE TO ALLOW REPAIR OF THE DAMAGE. THE MAIN ISOLATION VALVE WAS CLOSED AT 16:43. THE PIPELINE WAS ALLOWED TO DEPRESSURIZE BY CONSUMPTION OF THE GAS IN THE PACKAGE BOILERS ON THE COGEN SITEELIMINATING THE NEED TO VENT THE GAS TO ATMOSPHERE. THE GAS LINE PRESSURE HAD BLEED DOWN AND THE COGEN ISOLATION VALVE WAS CLOSED AT 20:15. SKIBACK PIPELINE CO. WAS MOBILIZED AND ARRIVED ON SITE ON 05/05/93 AND PROCEEDED WITH THE REPAIRS WHICH CONSISTED OF REPLACING THE DAMAGED PORTION OF THE PIPE. WELDNUMBER W4 WAS REMOVED WITH THE DAMAGED PIPE AND A PRETESTED SECTION OF REPLACEMENT PIPE WAS INSTALLED WITH WELDS LABELED W4A AND W4B. FOLLOWING THE REPAIR, THE PIPE COATING WAS CLOSELY INSPECTED AND REPAIRED AS REQUIRED. THE PIPE EXPOSED DURING THE DURING THE REPAIR WAS FOUND TO SHOW NO EVIDENCE OF CORROSION AND THE INTERIOR SURFACE OF THE PIPE WAS ALSO CLEAN. THE NEW YORK STATEPUBLIC SERVICE COMMISION WAS NOTIFIED OF THE INCIDENT AND SR. GAS & PETROLEUM INSPECTOR JOHN HENRY MCCAULEY WAS ON SITE TO INSPECT ALL OF THE REPAIRS MADE TO THE PIPELINE AND TO OBSERVE THE BACKFILLING OF THE PIPE AFTER THE REPAIRS WERE COMPLETED. FOLLOWING THE REPAIRS, THE LINE WAS PIGGED AND REFILLED WITH NATURAL GAS. NATURAL GAS SERVICE WAS RESTORED TO THE COGEN PROJECT ON 05/07/93 AT 15:12.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930107 | 1993-06-07 | 22617 | WILLIAMS NATURAL GAS CO | OVERLAND PARK | JOHNSON | KS | 66210 | S. GLAVIN | STATION | 430 | 1993-04-28 | 3 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 30 |  | 19930428 | 435 | 280 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: NON SPECIFIED; MLKD: STEEL; PRTSY: PIPELINE; PRTSO: &REGULATOR/METERING SYSTE; PRTYR: 1948; NMDIA: 26; THK: 0.25; SPEC: 2030D; SMYS: 52000; SEAM: ELECTRIC WELD; MANU: A O SMITH; MANYR: 1948; LOCLK: UNDER GROUND; PNAME: WARREN A ETHERIDGE - SR PIPELINE SAFETY COOR; PHONE: 9185884427; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | UNAUTHORIZED ENTRY OF WNG FACILITIES IN WHICH THE CONTROLLERS ON REGULATORS WERE ADJUSTED RESULTING IN AN OVERPRESSURE SITUATION. THE MAOP OF THE TWO PIPELINES WERE EXCEEDED. THE FBI WAS BROUGHT IN TO INVESTIGATE. TWO 26" PIPELINES WERE OVERPRESSURED FOR APPROXIMATELY 2 HOURS WHEN UNAUTHORIZED ENTRY WASMADE AT WNG'S SOUTH GLAVIN METERING STATION. AN OVERPRESSURE CONDITION WAS CREATED WHEN THE CONTROLLERS ON SEVERAL REGULATORS WERE ADJUSTED ALLOWING THEPIPELINES TO PRESSURE UP TO 435 PSIG. THE FBI AND LOCAL LAW ENFORCEMENT WERE SUBSEQUENTLY NOTIFIED. THE LINES WERE FREQUENTLY PATROLLED WITH FIU'S DURING THE DAYS ENSUING THE INCIDENT.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930109 | 1993-06-29 | 12462 | MID - LOUISIANA GAS CO | VIDALIA | CONCORDIA | LA |  | 90.9 | 4799+50 | 1305 | 1993-06-07 | 1 | NO |  |  | LA | Null | Null | LEAK | 0 | 0 | 0 | 150000 | 114786.5854 | 250065.331 | YES | 3 | 0 |  | 19930607 | 162 | 250 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: SEE COMMENTS; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 0; NMDIA: 10; THK: 0.5; SPEC: API5L; SMYS: 35000; SEAM: SMLS; MANU: J & L; MANYR: 1979; LOCLK: UNDER WATER; PNAME: R L SIMPSON; PHONE: 3186654426; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: SEE COMMENTS; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | PART 3 - STRONG RIVER CURRENT SCOURED CHANNEL BELOW THE PIPE NEAR THE EDGE OF ALEAK OCCURRED IN MISS. RIVER. STRONG CURRENT HAS PREVENTED COMPLETION OF INVOF A SANDBAR CAUSING PIPE TO BECOME SUSPENDED OVER THE BOTTOM. THE FORCE OF THEESTIGATION AND REPAIR. LINE IS SHUT-IN AND SERVICE BEING MAINTAINED BY ADDITCURRENT CAUSED THE SUSPENDED PIPE SWING AND EVENTUALLY BREAK INTO A HEAT AFFECTEIONAL LINES ACROSS THE RIVER SUPPLEMENTAL REPORT TO BE FILED.D ZONE OF A GIRTH WELD. PART 4 - HEAT AFFECTED ZONE ADJACENT TO GIRTH WELD.PART B.1 - CHANNEL BOTTOM SCOUR IN MISSISSIPPI RIVER.
2021-02-26 10:36 | NO | NO |  | 19930110 | 1993-07-13 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | RICHMOND | ST CLAIR | MI | 48062 |  | CAIN #1 GAS WELL | 1200 | 1993-06-15 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 9 | 30 |  | 19930615 | 500 | 0 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: NO DATA; PRTFL: OTHER; PRTFO: NON SPECIFIED; MLKD: STEEL; PRTSY: OTHER; PRTSO: STORAGE GAS WELL; PRTYR: 0; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: EDWARD SWANSON; PHONE: 3132566614; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: NO; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | INGNITION OF GAS VENTING FROM WELL RIG LUBRICATOR BOTTLE DURING ROUTINE WELLWORK TO RETRIEVE A PACKER.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930112 | 1993-07-07 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA |  |  | LA |  |  |  | 1300 | 1993-06-06 |  | YES | WEST CAMERON | 564 |  | YES | NO | LEAK | 0 | 0 | 0 | 500000 | 382621.9512 | 833551.1034 | Null | 9 | 50 |  | 19930606 | 950 | 1200 | BY TEST | 1957 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1977; NMDIA: 24; THK: 0.5; SPEC: 5LX60; SMYS: 60000; SEAM: DSAW; MANU: BETHLEHEM; MANYR: 1977; LOCLK: UNDER WATER; PNAME: F ROY FLEET; PHONE: 7086913786; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; MRKTP: 0N; STAT: Null; CTEST: Null | THE PIPELINE WAS APPARENTLY STRUCK BY A JACK-UP RIG BEING TOWED TO A DRILLING SITE. REPAIRS ARE IN PROGRESS.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930114 | 1993-07-16 | 384 | AMAERICAN GAS STORAGE CORP | LOOP | GAINES | TX |  |  |  | 1249 | 1993-05-31 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 400000 | 306097.561 | 666840.8827 | Null | 0 | 10 |  | 19930531 | 720 | 3165 | BY TEST | 4130 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: 1/2" XH PIPE NIPPLE; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1982; NMDIA: 0.5; THK: 0; SMYS: 0; SEAM: .5" XH STEEL PI; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: STEVE BUSTOS; PHONE: 8063736042; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | 1/2" XH PIPE NIPPLE (SCH 40) BROKE OFF AT THREADS. IF METALURGICAL REPORT DIFFERS FROM INITIAL FINDINGS, A SUPPLEMENTAL REPORT WILL BE SUBMITTED.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19930117 | 1993-07-01 | 19570 | TRANSCO GAS PIPELINE CORP | BILLINGSLEY | CHILTON | AL |  | 891.61 | 5927+48 | 2230 | 1993-06-03 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 30 |  | 19930604 | 719 | 800 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | OTHER | UNKNOWN | OTHER | UNKNOWN | COMPRESSOR STATION |  | 1951 | 0 | 0 |  | 0 |  |  |  | 0 | OTHER | COMPRESSOR BUILDING | B R LANDES | 7134392322 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | COMPRESSOR SHAFT | NO |  | NO DATA | 0 | 0 | 0 | AT APPROXIMATELY 10:30 PM CST ON JUNE 3, 1993, A FIRE OCCURRED AT COMPRESSORSTATION 100 LOCATED NEAR BILLINGSLEY, ALABAMA. THE FIRE OCCURRED ON STEAM TURBINE UNIT #2. TWO EMPLOYEES SUFFERED MINOR INJURIES AND WERE TAKEN TO A LOCAL HOSPITAL. ONE EMPLOYEE WAS TREATED AND RELEASED, THE OTHER EMPLOYEE SUSTAINED SECOND DEGREE BURNS TO HIS LEFT AND AND SMOKE INHALATION AND WAS KEPT IN THE HOSPITAL TWO NIGHTS FOR OBSERVATION AND THEN WAS RELEASED. COMPRESSOR IUNIT #2 HAS EXTENSIVE DAMAGE AND THE COMPRESSOR HUILDING AND ADJACENT COMPRESSOR UNITS ALSO HAVE SOME DAMAGE. THE CAUSE OF THE INCIDENT IS UNKNOWN AT THIS TIME. A TASK GROUP HAS BEEN ESTABLISHED AND IS INVESTIGATING THE INCIDENT. UPON COMPLETION OF THE INVESTIGATION, A SUPPLEMENTAL REPORT WILL BE FILED WITH THE DEPARTMENT OF TRANSPORTATION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930120 | 1993-07-19 | 18484 | SOUTHERN CALIFORNIA GAS CO | MORENO VALLEY | RIVERSIDE | CA | 92355 | 157.00 |  | 1134 | 1993-06-19 | 2 | NO |  |  | CA | Null | NO | RUPTURE | 0.5 | 0 | 0 | 62500 | 47827.7439 | 104193.8879 | Null | 3 | 12 |  | 19930619 | 550 | 584 | BY CFR 192.619(A)(3) | 906 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1947; NMDIA: 30; THK: 0.28; SPEC: API5L; SMYS: 52000; SEAM: DSAW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: G. E. STRANG - VICE PRESIDENT, TRANSMISSION; PHONE: 2132441200; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: 2" PIPE W/12" X 15" SIGN,; STAT: YES; CTEST: Null | ON JUNE 19,1993 , AT APPROXIMATELY 11:34 AM, CASH EQUIPMENT RENTALS DAMAGED LINE 2000 WITH A TOOTH ON THE FRONT BUCKET OF A CATIPILAR MODEL 988 LOADER WHILE EXCAVATING. A 6"X3" HOLE WAS GOUGED IN THE LINE AT ABOUT THE ONE O'CLOCK POSITION. ALL OFF - LINE TAPS, EXCEPT ONE, WERE SECURED. ALL SERVICES WERE RESTORED BY THE NEXT DAY. PERMANENT REPARIS WERE COMPLETED BY INSTALLING A FIELD FABRICATED BAND OVER THE DAMAGED AREA. THERE WERE NO FIRES OR INJURIES ASSOCIATED WITH THIS INCIDENT. GAS LOSS CALCULATION WAS 16,480 MCF. ESTIMATED COSTS ASSOCIATED WITH THIS INCIDENT WERE $62,500. UNDERGROUND SERVICE ALERT WAS NOT NOTIFIED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930121 | 1993-07-19 | 19325 | TEXAS UTILITIES FUEL CO |  | BRAZOS | TX |  | BVO 113 |  | 1838 | 1993-06-15 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 50000 | 38262.1951 | 83355.1103 | YES | 10 | 35 |  | 19930615 | 735 | 940 | BY TEST | 1088 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1960; NMDIA: 24; THK: 0.31; SPEC: X-52; SMYS: 52000; SEAM: ERW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: DANNIE R. MERCER - REGULATORY ENGINEER; PHONE: 2148126870; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: NO; MARK: YES; MRKTP: PAINTED FENCE POSTS WITH; STAT: YES; CTEST: Null | OPERATOR WAS LOADING FILL DIRT WITH A JOHN DEERE 544E FRONT END LOADER ON TUFCO R.O.W. KNOCKED HOLE IN 24" LINE NORTH OF BVO 113 ABOUT 200 YDS.PIPELINE COLORS & TUFCO SINGS.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930124 | 1993-07-23 | 19160 | TENNESSEE GAS PIPELINE CO | WEST MONROE | OUACHITA | LA |  | 47-2+0.34 |  | 1500 | 1993-06-24 | 3 | NO |  |  |  | Null | NO | RUPTURE | 1 | 0 | 0 | 300000 | 229573.1707 | 500130.662 | Null | 1 | 5 |  | 19930624 | 748 | 750 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1974 | 26 | 0.41 | API-5L | 52000 | DSAW |  | U.S. STEEL | 1974 | UNDER GROUND |  | L.A. SALINAS | 7137572408 | INTERNALLY | GENERAL CORROSION |  | OTHER | NOT SPECIFIED | COATED | YES | 1974 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | LINE 100-2, DOWNSTREAM OF COMPRESSOR STATION RUPTURED, CAUSING A FIRE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930130 | 1993-08-24 | 19570 | TRANSCO GAS PIPELINE CORP | OFFSHORE SOUTH PASS |  | LA |  |  |  | 1425 | 1993-07-30 |  | YES | SOUTH PASS | 53 |  | YES | NO | LEAK | 0 | 0 | 0 | 350000 | 267835.3659 | 583485.7724 | Null | 9 | 50 |  | 19930730 | 1326 | 1440 | BY TEST | 2180 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | MECHANICAL JOINT |  | STEEL |  | PIPELINE |  | 1984 | 12 | 0.84 | A106 | 35000 |  | CHK-TOM WHEATLY | BIM | 1984 | UNDER WATER |  | B.R. LANDES - STAFF COMPLIANCE ANALYST | 7134392001 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | BIM MECHANICAL LOCKING SLIP JOINT | YES | 19841003 | WATER | 2180 | 8 | 2180 | THE CHECK VALVE DID NOT CLOSE COMPLETELY WHEN MECHANICAL SLIP JOINT DISENGAGED, ALLOWING THE RELEASE OF GAS PRESSURE.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19930132 | 1993-08-05 | 15014 | PACIFIC GAS TRANSMISSION CO | ROSALIA | SPOKANE | WA |  | 143.5 COMPRESSOR STATION | 5-328 + 1900 | 815 | 1993-07-15 | 1 | NO |  |  | WA | NO | NO | OTHER | 0 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 0 |  | 19930715 | 0 | 911 | BY TEST | 1500 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: NONE SPECIFIED; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1993; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: OTHER; LOCLO: TRENCH; PNAME: THOMAS J. CUSWORTH - OPERATIONS MANAGER; PHONE: 5095340657; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | WHILE REPAIRING A TIE-IN WELD ON NEW 34-INCH STATION PIPING, AN EXPLOSIVEMIXTURE OF GAS BUILT UP INSIDE THE PIPE FROM A LEAKING VALVE RESULTING IN AFLASH FIRE. THE WELDER REPAIRING THE WELD WAS BURNED OVER THE LOWER HALF OFHIS BODY AS THE HOT GASES CAME OUT A 2-INCH VENT INSTALLED AS AN AIR SOURCE
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19930133 | 1993-08-17 | 19570 | TRANSCO GAS PIPELINE CORP | MARKHAM | MATAGORDA | TX |  |  |  | 2023 | 1993-07-13 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 10 |  | 19930713 | 0 | 1250 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: #1 SLUG CATCHER; MLKD: OTHER; MLKDO: SEE ATTACHMENT; PRTSY: OTHER; PRTSO: SEPARATION PLANT; PRTYR: 1984; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: B.R. LANDES - STAFF COMPLIANCE ANALYST; PHONE: 7134392001; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | AT APPROXIMATELY 8:40 PM CST ON JULY 13,1993 A SMALL EXPLOSION AND FLASH FIRE OCCURRED ON THE NUMBER 1 SLUG CATCHER AT COMPRESSOR STATION 24 LOCATED IN MARKHAM, TEXAS. TWO EMPLOYEES SUFFERED INJURIES. ONE EMPLOYEE WAS TREATED AND RELEASED WITH MINOR BRUISES, THE OTHER EMPLOYEE SUSTAINED SECOND DEGREE BURNSTO HANDS, ARMS, AND FACE. NO DAMAGE TO COMPANY FACILITIES OCCURRED OTHER THAN VEHICLES LOCATED NEAR THE SITE. THE SLUG CATCHER WAS ISOLATED AND BLOWN DOWN. A FOAM PLUG WITH PLYWOOD SHIELD WAS INSTALLED TO ISOLATE THE WELDING AREA.WELDING BEGAN TO INSTALL A FLANGE UNTIL A GLOW WAS NOTICED AT THE BOTTOM OF THE FOAM PLUG HAD CAUGHT FIRE AND IGNITED SLUDGE VAPOR FROM THE SLUG CATCHER.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930138 | 1993-08-12 | 19160 | TENNESSEE GAS PIPELINE CO |  | LAFOURCHE | LA |  | M.P. 523A-101.1+.00 |  | 1030 | 1993-07-15 | 2 | NO |  |  | Y | Null | NO | OTHER | 0 | 0 | 0 | 55000 | 42088.4146 | 91690.6214 | Null | 1 | 0 |  | 19930715 | 945 | 1130 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: 1"VALVE (BROKEN OFF); MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1956; NMDIA: 0; THK: 0; SMYS: 0; VALVE: 1" BALL VALVE; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: G.R. ABEL; PHONE: 7137572408; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19930715; MARK: YES; MRKTP: SIGNAGE ON PLATFORM; STAT: Null; CTEST: Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930142 | 1993-08-20 | 4280 | EL PASO NATURAL GAS CO |  | HIDALGO | NM |  | M.P. 45.5 |  | 1930 | 1993-07-24 | 1 | NO |  |  |  | Null | NO | RUPTURE | 1.5 | 0 | 0 | 108000 | 82646.3415 | 180047.0383 | Null | 3 | 10 |  | 19930726 | 789 | 850 | BY TEST | 1407 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1947 | 6 | 0.15 | UNKNOWN | 35000 | SEAMLESS |  | INVASION PIPE | 1947 | UNDER GROUND |  | RICHARD FAVILA - SENIOR ENGINEER | 9155412062 | EXTERNALLY | OTHER | CRACKING | OTHER | ENVIRONMENT, STRESS | COATED | YES | 1939 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | PART 3. ON 7/24 AT 7:30 PM (MDT) A LEAK WAS REPORTED ON OUR PIPLINE. AN 18" RUPTURE WAS DISCOVERED AND THE PIPELINE SEGMENT WAS ISOLATED BY 10:40 PM. THEPIPELINE WAS REPAIRED AND ETURNED TO SERVICE BY 3:38pm on 7/25. AT THE TIME OF THE RUPTURE THIS INCIDENT DID NOT MEET THE COST CRITERIA FOR A TELEPHONIC REPORT TO DOT. SUSEQUENT REVIEW OF METERING CHARTS FOR THE PIPELINE INDICATEDTHAT THE PIPELINE HAD BEEN LEAKING SINCE 6:00 PM ON 7/21; HOWEVER OUR FIRST DISCOVERY OF A LEAK DID NOT OCCUR UNTIL 7/24. THE GAS LOST FROM 7/21 UNTIL THELEAK WAS ISOLATED 7/24 (77 HRS) RESULTED IN A TOTAL PROPERY DAMAGE OVER $50,000 AND CONSEQUENTLY THIS INCIDENT WAS TELEHONICALLY REPORTED OT DOT ON 7/26.SUPPLEMENTAL REPORT ON 3.13.95 INDICATES ADDITIONAL INFORMATION IN PART A -FAILURE WAS DUE TO STRESS CORROSION CRACKING.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930144 | 1993-09-10 | 15105 | PANHANDLE EASTERN PIPELINE CO | BOONVILLE | HOWARD | MO | 65233 | 34, EAST RIVER HEADERS |  | 1100 | 1993-07-30 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  |  | 0 | 0 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: UNKNOWN; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 0; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: UNDER PAVEMENT; PHONE: 7136275117; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: MISSOURI RIVER FLOOD; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | FLOODING ON THE MISSOURI RIVER CAUSED A LEVEE TO BREAK ON THE EAST SIDE OF THE RIVER NEAR PEPL'S FOUR PIPELINES. THE WATER VELOCITY WASHED COVER OFF THE PIPELINE RESULTING IN LINES FLOATING TO THE WATER SURFACE AS WELL AS UNDERMINING VALVE AND PIPING SUPPORT STRUCTURES. PRESSURE WAS REDUCED IN SOME OF THE PIPING AND SOME SEGMENTS WERE REMOVED FROM SERVICE AND BLOWN DOWN WHILE THE PIPING IS BEING STABILIZED AND INSPECTED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930145 | 1993-09-10 | 6141 | GAS CO OF NEW MEXICO | ESPANOLA | RIO ARRIBA | NM |  | BETWEEN 4-5 |  | 450 | 1993-08-01 | 1 | NO |  |  |  | Null | YES | OTHER | 0 | 0 | 0 | 225000 | 172179.878 | 375097.9965 | Null | 1 | 20 |  | 19930801 | 300 | 400 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1964; NMDIA: 8; THK: 0.19; SPEC: 5LX; SMYS: 42000; SEAM: ERW; MANYR: 1964; LOCLK: UNDER WATER; PNAME: STEVEN EMRICK - CHIEF ENGINEER; PHONE: 5058484503; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: RIVER BOTTOM DROPPED; NOTIF: NO; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | LINE BREAK AT RIVER CROSSINGLINE BREAK AT RIVER CROSSING. THEORIZED THAT RIVER BOTTOM LOWERED. THE EROSION OF TH BOTTOM EXPOSED PIPELINE THAT BROKE DUE TO WATER AND MATERIAL FORCES.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930146 | 1993-09-10 | 8200 | INTRATEX GAS CO | FM 3353 AND CR 199, | GUADALUPE | TX |  | 165 | 8700+63 | 152 | 1993-08-04 | 1 | NO |  |  |  | Null | NO | RUPTURE | 97 | 0 | 0 | 614334 | 470115.3476 | 1024157.5671 | Null | 2 | 8 |  | 19930804 | 823 | 938 | BY TEST | 1177 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1970 | 36 | 0.39 | API 5L,X-60 | 60000 | DSAW |  | US STEEL | 1970 | UNDER GROUND |  | DALE L. COATES - DIRECTOR CODE COMPLIANCE | 7136467340 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL |  | YES | 19700610 | WATER |  | 16 | 1177 | PROBABLE CAUSE OF FAILURE WAS A HARD SPOT ON THE BODY OF THE PIPE 29" FROM THE DSAW SEAM AT THE 7:00 O'CLOCK POSITION.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930148 | 1993-08-30 | 2616 | COLUMBIA GAS TRANSMISSION CORP | UNION | BROOME | NY | 13790 |  | 6981+15 | 740 | 1993-08-14 | 1 | NO |  |  |  | Null | NO | RUPTURE | 4 | 0 | 0 | 277000 | 211972.561 | 461787.3113 | Null | 0 | 55 |  | 19930814 | 877 | 926 | BY TEST | 1809 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1953 | 12 | 0.28 | API5L | 35000 | SEAMLESS |  | US STEEL | 1951 | UNDER GROUND |  | S.J. CHOBY - MANAGER CODES & STANDARDS | 3043572349 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | BARE | YES | 1971 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | A CORROSION INDUCED DUCTILE PIPELINE RUPTURE OCCURRED DUE TO AN APPARENT SHIELDING OF CATHODIC PROTECTION CURRENT. GAS IGNITED AND THE SUBSEQUENT FIRE DESTROYED A NEARBY DWELLING.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930158 | 1993-09-23 | 2620 | COLUMBIA GULF TRANSMISSION CO | LAKE PROVIDENCE | EAST CARROLL | LA | 71254 |  | 2288 + 81 | 1030 | 1993-08-24 | 1 | NO |  |  |  | Null | NO | RUPTURE | 34 | 0 | 0 | 50000 | 38262.1951 | 83355.1103 | Null | 1 | 30 |  | 19930824 | 750 | 1008 | BY TEST | 1360 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1960; NMDIA: 24; THK: 0.5; SPEC: API5LX; SMYS: 42000; SEAM: SEAMLESS; MANU: U.S. STEEL - LORAIN; MANYR: 1960; LOCLK: UNDER WATER; PNAME: S.J. CHOBY - MANAGER CODES, STANDARDS & PROCEDURES; PHONE: 3043572349; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | ON AUGUST 24, 1993, BETWEEN 10:30 AND 10:45 AM, COLUMBIA GULF PIPELINE 200 RUPTURED IN A CROSSING OF THE MISSISSIPPI RIVER NEAR LAKE PROVIDENCE, LOUISIANA. GAS ESCAPING FROM THE RUPTURE IGNITED NEAR THE WEST BANK OF THE RIVER. VALVES UPSTREAM AND DOWNSTREAM OF THE RIVER CROSSING WERE CLOSED AND FIRE BURNEDOUT AT 12:15 PM. THE PIPELINE PRESSURE AT THE TIME OF THE RUPTURE WAS 750 PSIG. GAS FLOW IN LINE 200 WAS DIVERTED TO ADJACENT PIPELINES. MISSISSIPPI RIVERTRAFFIC WAS STOPPED BY MEMPHIS COAST GUARD FOR 3 HOURS. AT THE TIME OF THISINCIDENT, THE MISSISSIPPI RIVER WAS AT FLOOD STAGE AND HAS REMAINED AT OR NEAR FLOOD STAGE SINCE THE TIME. FOR THIS REASON, IT HAS NOT BEEN POSSIBLE TO CONDUCT A COMPLETE INVESTIGATION OF THIS INCIDENT TO DETERMINE A POSSIBLE CAUSE. UNDERWATER ELECTRONIC SCANNING DEVICES HAVE BEEN USED TO LOCATE THE RUPTURED PIPELINE. THE CROSSING CONSISTS OF TWO 24 INCH PIPELINES. SCAN DATA SHOWSTHAT THE RUPTURE OCCURRED IN THE NORTH LINE. APPROXIMATELY 1500 FEET OF PIPEIN THREE SECTIONS ARE OUT OF THE DITCH AND LYING ACROSS THE SOUTH LINE. INVESTIGATION OF THE INCIDENT IS CONTINUING, AS RIVER CONDITIONS PERMIT, EFFORTS WILL BE MADE TO RECOVER THE PIPE IN ORDER TO DETERMINE A POSSIBLE CAUSE OF THEFAILURE. AT SUCH TIME AS A PROBABLE CAUSE IS DETERMINED, A SUPPLEMENTAL REPORT WILL BE SUBMITTED. SUPPLEMENTAL 2/29/94 - FURTHER INVESTIGATION OF THISINCIDENT HAS REVEALED THAT THE RUPTURED PIPELINE IS ON THE RIVER BOTTOM AT ADEPTH OF APPROX. 80 FEET. THE ESTIMATED COST TO LIFT THE DAMAGED LINE ISAPPROX. $1,500,000. FOR THIS REASON, COLUMBIA GULF HAS OBTAINED PERMISSIONFROM THE U.S. ARMY CORP OF ENGINEERS TO ABANDON THE LINE IN PLACE. BECAUS WEHAVE BEEN UNABLE TO RECOVER THE DAMAGED PIPELINE, WE ARE UNABLE TO DETERMINETHE CAUSE OF THE FAILURE. COLUMBIA CAN ONLY SPECULATE REGARDING THE ACTUALCAUSE OF THE FAILURE. COLUMBIA PLANS TO REPLACE THE FAILED SECTION WITH ANEW 30" PIPELINE BORED SIGNIFICANTLY BELOW THE RIVER BOTTOM. THE SUPPLEMENTALREPORT WILL CLOSE OUTR FILE ON THIS INCIDENT.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930159 | 1993-09-27 | 19325 | TEXAS UTILITIES FUEL CO |  | MCLENNAN | TX |  | MP 107.5 |  | 523 | 1993-08-21 | 1 | NO |  |  |  | Null | NO | RUPTURE | 17 | 0 | 0 | 952000 | 728512.1951 | 1587081.3008 | YES | 1 | 32 |  | 19930821 | 575 | 775 | BY TEST | 177 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1968 | 30 | 0.44 | GRADE X-52 | 52000 | ERW |  | YOUNGSTOWN | 0 | UNDER WATER |  | DANNIE MERCER - REGULATORY ENGINEER | 2148126870 | INTERNALLY | GENERAL CORROSION |  | OTHER | LIQUIDS IN LINE | COATED | YES | 0 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | PART 3 NARRATIVE - THE RUPTURE WAS WEST OF TRADINGHOUSE POWER PLANT; AND ABOUT TWO HUNDRED YARDS OUT IN LAKE TRADINGHOUSE.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19930162 | 1993-09-27 | 456 | AMOCO GAS CO | TEXAS CITY | GALVESTON | TX | 77592 |  | 0+00 | 1655 | 1993-07-27 | 3 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 4 | 0 | 0 | 0 | Null | 10 | 0 |  | 19930727 | 270 | 738 | BY TEST | 1500 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1988; NMDIA: 12; THK: 0.31; SPEC: API5L GR B; SMYS: 35000; SEAM: ERW; MANU: UNKNOWN; MANYR: 0; LOCLK: UNDER GROUND; PNAME: R.J. HAECHTEN; PHONE: 4099385905; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | PLEASE REFERNCE INVESTIGATION CONDUCTED BY DAVID BORN OF YOUR HOUSTON OFFICE. ON THE MORINGING OF JULY 27, 1993 AMOCO GAS COMPANY REMOVED THE CHOCLATE BAYOU TRANSMISSION LINE FROM SERVICE. LATER THAT MORNING, WE REMOVED FROM SERVICE A LOOP LINE BY COLD CUTTING IT AT OUR TEXAS CITY TERMINAL AND REMOVING A FLANGED TEE JOINING THE LINES APPROXIMATELY 2000 FEET SOUTH OF THE TEXAS CITY TERMINAL AND REPLACING IT WITH A FLANGED SPOOL PIECE. A WELD NECK FLANGE WAS WELDED TO THE LINE THAT WOULD BE PUT BACK IN SERVICE AND BLIND FLANGE BOLTED TO THE WELD NECK FLANGE. AT APPROXIMATELY 4:00 M, WE BEGAN PRESSURING THE LINE THROUGH THE BYPASS ON A MAIN LINE BLOCK VALVE 6 MILES AWAY. AT APPROXIMATELY 4:55 PM, THERE WAS AN EXPLOSION AND FIRE. THE LINE PRESSURE WAS APPROXIMATELY 270 PSIG WHEN THE EXPLOSION OCCURRED. A REVIEW OF THE DEBRIS INDICATES THERE WAS AN EXPLOSION INSIDE THE PIPELINE BEING PRESSURED. THE CAUSE OF THE EXPLOSION HAS NOT BEEN DETERMINED AND IS UNDER INVESTIGATION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930163 | 1993-08-01 | 20230 | UNITED GAS PIPELINE CO | WHITE OAK | GREGG | TX |  | 46.5 | 2491 +82 TO 2492 +04 | 1815 | 1993-08-01 | 1 | NO |  |  | TX | Null | NO | OTHER | 0 | 0 | 0 | 50000 | 38262.1951 | 83355.1103 | Null | 1 | 30 |  | 19930801 | 260 | 332 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 0; NMDIA: 16; THK: 0.31; SPEC: API 5L; SMYS: 24000; SEAM: SEAMLESS; MANU: U.S. STEEL; MANYR: 0; LOCLK: UNDER GROUND; PNAME: W. ST. GERMAIN - REGULATIONS COORD; PHONE: 3168323840; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | PART 3 NARRATIVE - THE CAUSE OF THE FAILURE IS UNDER METALLURGICAL INVESTIGATION. A SUPPLEMENTAL REPORT WILL BE SUBMITTED AS SOON AS POSSIBLE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930164 | 1993-10-12 | 19160 | TENNESSEE GAS PIPELINE CO |  | JEFFERSON DAVIS | LA |  | M.P. 507F - 101+14.05 |  | 1430 | 1993-09-09 | 2 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 50000 | 38262.1951 | 83355.1103 | Null | 0 | 38 |  | 19930909 | 700 | 1010 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | VALVE |  | STEEL |  | PIPELINE |  | 0 | 26 | 0.5 | API-5L | 52000 | DSAW | WKM GATE | A.O. SMITH | 0 | UNDER GROUND |  | L.A. SALINAS | 7137572871 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION | 2 INCH GATE VALVE | YES | 19830627 | WATER |  | 8 | 1495 | PART 3 NARRATIVE - DURING REMOVAL OF WALKER RICE FARM SALES METER, 2 INCH SIDE VALVE 507F - 131 FAILED, CAUSING GAS TO LEAK. IN PULLING VALVE STEM, INCORRECT BOLTS WERE REMOVED CAUSING VALVE TO DISASSEMBLE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930165 | 1993-10-14 | 13750 | NORTHERN NATURAL GAS CO (ENRON) | TESCOTT | OTTAWA | KS | 67484 | 3.587 |  | 1513 | 1993-09-12 | 1 | NO |  |  |  | Null | NO | RUPTURE | 40 | 0 | 0 | 260000 | 198963.4146 | 433446.5738 | Null | 2 | 30 |  | 19930927 | 707 | 860 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1954 | 30 | 0.34 | API - 5LX | 52000 | SUBMERGED ARC |  | A.O. SMITH | 1954 | UNDER GROUND |  | JOHN W. CASKEY - CODE COMPLIANCE ENGR. | 7136467343 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL |  | YES | 19681201 | GAS |  | 0 | 946 | HARD SPOT IN PIPE WALL
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930168 | 1993-10-14 | 2616 | COLUMBIA GAS TRANSMISSION CORP | RURAL GREENBANK DISTRICT | POCAHONTAS | WV | 26268 |  | 457 +95 | 1512 | 1993-09-18 | 1 | NO |  |  |  | Null | YES | RUPTURE | 2 | 0 | 0 | 105000 | 80350.6098 | 175045.7317 | Null | 1 | 5 |  | 19930918 | 1910 | 2110 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | OTHER | STORAGE FIELD LINE DRIP | 1967 | 16 | 0.47 | API5L | 60000 | SEAMLESS |  | UNKNOWN | 0 | UNDER GROUND |  | S.J. CHOBY - MANAGER - CODES, STANDARDS & PROCEDURES | 3043572349 | INTERNALLY | OTHER | CORROSION IN BOTTOM OF DR | OTHER | APPARENT MICROBIOLOGICAL | COATED | YES | 1968 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | AN INTERNAL CORROSION INHIBITOR PROGRAM IS SCHEDULED TO BEGIN AT THE BEGINNING OF THE 1993 STORAGE WITHDRAWAL SEASON.INTERNAL CORROSION CAUSED RUPTURE OF STORAGE LINE DRIP, RESULTING IN IGNITION AND THE BURNING OF APPROXIMATELY 5 ACRES OF TREES.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930169 | 1993-10-11 | 2616 | COLUMBIA GAS TRANSMISSION CORP | RURAL ELK DISTRICT | COCO KANAWHA | WV | 25071 |  | 3 +00 | 1900 | 1993-09-18 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 91000 | 69637.1951 | 151706.3008 | Null | 0 | 45 |  | 19930918 | 1550 | 1800 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1952; NMDIA: 4; THK: 0.34; SPEC: UNKNOWN; SMYS: 24000; SEAM: SEAMLESS; MANYR: 0; LOCLK: UNDER GROUND; PNAME: S.J. CHOBY - MANAGER CODES STANDARDS & PROCEDURES; PHONE: 3043572349; LOC: EXTERNALLY; ADESC: GENERAL CORROSION; CAUCR: GALVANIC; COAT: BARE; PROT: YES; CPYR: 1971; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | PART 3 NARRATIVE - BARE PIPE IS LOCATED ON A 65% GRADE ROCK HILLSIDE WITH 1 FOOT OF UNCONSOLIDATED ROCK COVER. THIS RESULTED IN INEFECTIVE CATHODIC PROTECTION AT THE POINT OF FAILURE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930174 | 1993-10-14 | 1480 | BLACK MOUNTAIN GAS CO | 7TH AVE. & CAREFREE HWY | MARICOPA | AZ | 85331 |  |  | 1120 | 1993-09-23 | 1 | NO |  |  |  | Null | NO | RUPTURE | 0.5 | 0 | 0 | 5000 | 3826.2195 | 8335.511 | Null | 5 | 10 |  | 19930923 | 295 | 300 | BY TEST | 620 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1965; NMDIA: 3; THK: 0.17; SPEC: SCHED. AD, GRADE B; SMYS: 0; SEAM: SEAMLESS; MANYR: 0; LOCLK: UNDER GROUND; PNAME: LOWELL RELKIN - FIELD SUPERVISOR; PHONE: 6024883402; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19930915; MARK: YES; MRKTP: STAKES, BUT INCOMPLETE; STAT: YES; CTEST: Null | BLUE STAKE WAS NOT COMPLETE. CONTRACTOR DUG AFTER DIGGING POTHOLE CONTRACTORASSUMED BLUE STAKE WAS WRONG. BACKHOE HIT LINE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930175 | 1993-09-27 | 21031 | VALERO TRANSMISSION CO | SANTA FE | GALVESTON | TX | 77510 |  | 359+79 | 1355 | 1993-08-09 | 2 | NO |  |  | TX | Null | NO | RUPTURE | 50 | 0 | 0 | 48000 | 36731.7073 | 80020.9059 | Null | 1 | 0 |  | 19930809 | 595 | 656 | BY TEST | 1200 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1965; NMDIA: 16; THK: 0.25; SPEC: API 5LX; SMYS: 42000; SEAM: ERW; MANYR: 1964; LOCLK: UNDER GROUND; PNAME: DUANE KETTERMAN - AREA FOREMAN; PHONE: 7139512191; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | THE PIPELINE RUPTURED AT THIS LOCATION. AT THIS TIME, THE CAUSE OF THE RUPTURE IS NOT KNOWN THE RUPTURED PIPE IS BEING ANALYZED BY A METALLURGIST. WHEN THE RESULTS ARE AVAILABLE A COPY WILL BE SENT TO THE TRRC.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930176 | 1993-09-27 | 21031 | VALERO TRANSMISSION CO | EAST OF KINGSVILLE | KLEBERG | TX |  | M.P. 10.2 | 536+93 | 1500 | 1993-08-25 | 1 | NO |  |  | TX | Null | NO | LEAK | 0 | 0 | 0 | 45000 | 34435.9756 | 75019.5993 | Null | 2 | 0 |  | 19930825 | 950 | 1050 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1967; NMDIA: 20; THK: 0.28; SPEC: API5L; SMYS: 52000; MANU: UNKNOWN; MANYR: 1966; LOCLK: UNDER GROUND; PNAME: KATHY RUTHERFORD - REGULATORY TECH; PHONE: 2102463386; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19930813; MARK: YES; MRKTP: STAKES AND FLAGS; STAT: NO; CTEST: Null | OUR PIPELINE WAS HIT AND PUNCTURED BY A MESQUITE EARTH MOVER WHILE KING RANCH PERSONNEL WERE DIGGING A DRAINAGE DITCH ACROSS THE ROW. VALERO PERSONNEL HAD LOCATED, FLAGGED AND STAKED THE LINE AND HAD MADE DAILY CHECKS UNTIL THE PIPELINE WAS EXPOSED. THE LINE WAS HIT ABOUT 30 FEET FROM WHERE IT WAS EXPOSED AND 10 FEET FROM ONE OF OUR STAKES.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930178 | 1993-10-12 | 8310 | IROQUOIS GAS TRANSMISSION SYSTEM | NY CO-ORDINATE SYSTEM |  | CT |  | L.I.S. 11.0 | L.I.S. 580 +51 | 1700 | 1993-09-04 |  | YES |  |  | CT | Null | NO | LEAK | 0 | 0 | 0 | 91000 | 69637.1951 | 151706.3008 | Null | 0 | 0 |  | 19930910 | 0 | 1440 | BY TEST | 2160 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: GREASE FITTING; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1991; NMDIA: 0.5; THK: 0; SPEC: AISI 316; SMYS: 0; MANU: PRECISION GENERAL; MANYR: 0; LOCLK: UNDER WATER; PNAME: RICHARD MCGREGOR - SUPRV. ENGINEER; PHONE: 2039257257; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | ON SEPTEMBER 4, 1993, AT APPROXIMATELY 17:30 HOURS A SURVEY CREW UNDER CONTRACT TO IROQUOIS TO PERFORM A MARINE HYDROGRAPHIC AND GEOPHYSICAL SURVEY OF OUR OFFSHORE PIPELINE DISCOVERED AN ACOUSTIC DISTURBANCE IN THE WATER COLUMN. UPON FURTHER INVESTIGATION SMALL BUBBLES WERE FOUND RISING TO THE SURFACE OF THE WATER. USING AN UNDERWATER CAMERA MOUNTED ON A REMOTE OPERATED VEHICLE (ROV) IT WAS DETERMINED THAT THE BUBBLES WERE ORIGINATING FROM THE SEA FLOOR IMMEDIATELY ABOVE A BURIED SUBSEA TEE AND VALVE ASSEMBLY IN APPROXIMATELY 70 FEET OF WATER. THIS ASSEMBLY HAD BEEN INSTALLED DURING ORIGINAL CONSTRUCTION OF THE MAINLINE IN 1991 TO CONNECT A FUTURE CUSTOMER. THE MAGNITUDE OF THE LEAKWAS MINIMAL AND IT WAS NOT CONSIDERED TO PRESENT A SAFETY HAZARD TO THE PUBLIC. THE ACTUAL DATE AND TIME THAT THE LEAK ORIGINATED IS UNKNOWN. THE OPERATING PRESSURE OF THE MAINLINE AT POINT AND TIME OF DISCOVERY WAS APPROXIMATELY 800 PSIG. A WORK BOAT AND DIVING CREW WERE MOBILIZED ON SEPTEMBER 26, 1993, AND BEGAN EFFORTS TO UNCOVER THE VALVE ASSEMBLY THE NEXT DAY. AFTER THE ASSEMBLY WAS UNCOVERED IT WAS DETERMINED THAT THE SOURCE OF THE LEAKAGE WAS A GREASE FITTING ON THE DOWNSTREAM SEAT OF A 16" BALL VALVE. THE CAP ON THE GREASE FITTING WAS MISSING THE BALL CHECKS IN THE FITTING WERE ALLOWING A SMALL AMOUNT OF GAS TO ESCAPE. IT IS BELIEVED THAT THE CAP WAS NEVER REPLACED AFTER VALVE WAS SERVICED FOLLOWING FINAL HYDROSTATIC TEST IN 1991. THE LEAK WAS REPAIRED BY REPLACING THE CAP ON THE GREASE FITTING. REPAIR ACTIVITIES WERE COMPLETED AND THE ASSEMBLY BACKFILLED ON OCTOBER 6, 1993. THIS LEAK IS BEING REPORTEDBECAUSE THE COST OF MOBILIZING AND OPERATING THE MARINE VESSEL TO SUPPORT THE REPAIR CREW OF SUBSEA WORK IS EXPECTED TO EXCEED $50,000. THERE WAS NO PROPERTY DAMAGE AND THE COST OF GAS LOST WAS MINIMAL. TELEPHONIC NOTICE WAS GIVENTO THE NRC ON SEPTEMBER 10, 1993, BECAUSE IT WASN'T UNTIL THEN THAT IT WAS DETERMINED THAT THE COST OF INVESTIGATION AND REPAIR COULD EXCEED $50,000.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930180 | 1993-10-29 | 2620 | COLUMBIA GULF TRANSMISSION CO | GULF OF MEXICO |  | LA |  |  | X=1886449.08 Y=105418.45 | 215 | 1993-10-04 |  | YES | EI | 287 |  | YES | NO | LEAK | 0 | 0 | 0 | 50000 | 38262.1951 | 83355.1103 | Null | 0 | 0 |  | 19931004 | 1150 | 1250 | BY TEST | 2160 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1971 | 12 | 0.41 | X-52 | 52000 | SEAMLESS |  | UNKNOWN | 0 | UNDER WATER |  | S.J. CHOBY - MANAGER CODES STANDARDS | 3043572767 | INTERNALLY | OTHER | UNKNOWN | OTHER | UNKNOWN | COATED | YES | 1971 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930181 | 1993-10-26 | 2620 | COLUMBIA GULF TRANSMISSION CO | GULF OF MEXICO |  | LA |  |  | X-1662722.07 Y=-64491.85 | 1450 | 1993-09-27 |  | YES | V | 187 |  | YES | NO | LEAK | 0 | 0 | 0 | 50000 | 38262.1951 | 83355.1103 | Null | 0 | 0 |  | 19930927 | 1050 | 1440 | BY TEST | 2160 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: BLEEDER VALVE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1989; NMDIA: 6; THK: 0.5; SPEC: GRADE B; SMYS: 35000; SEAM: SEAMLESS; VALVE: BLEEDER VALVE; MANU: PLEECO; MANYR: 1989; LOCLK: UNDER WATER; PNAME: S.J. CHOBY - MANAGER CODES STANDARDS; PHONE: 3043572349; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; MRKTP: 0N; STAT: Null; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930185 | 1993-11-08 | 19160 | TENNESSEE GAS PIPELINE CO | COOKEVILLE | PUTNAM | TN | 38501 | 3106A-101+0.20 |  | 1530 | 1993-10-22 | 2 | NO |  |  |  | Null | NO | RUPTURE | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 15 |  | 19931022 | 503 | 720 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1952; NMDIA: 4.5; THK: 0.19; SPEC: A106; SMYS: 35000; MANU: U.S. STEEL; MANYR: 1952; LOCLK: UNDER GROUND; PNAME: L.A. SALIAS - STAFF CIVIL ENGINEER; PHONE: 7137572781; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: Null; MARK: YES; MRKTP: LATHES WITH RIBBON; STAT: YES; CTEST: Null | CONSTRUCTION CREW PERFORMING CONSTRUCTION OF 10' OFFSET LINE STRUCK 4 INCH LATERAL LINE WITH BACKHOE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930186 | 1993-11-10 | 2616 | COLUMBIA GAS TRANSMISSION CORP | NEW MILTON | DODDRIDGE | WV | 26411 |  | 1280 +64 | 120 | 1993-10-07 | 1 | NO |  |  |  | Null | NO | RUPTURE | 62 | 0 | 0 | 91000 | 69637.1951 | 151706.3008 | Null | 1 | 45 |  | 19931007 | 869 | 944 | BY TEST | 1118 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1947 | 20 | 0.31 | API-5-L | 42000 | ERW |  | YOUNGTOWN SHEET/TUBE | 1946 | UNDER GROUND |  | S.J. CHOBY - MANAGER | 3043572349 | EXTERNALLY | OTHER | SELECTIVE SEAM | GALVANIC |  | BARE | YES | 1970 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | A 62 FT. SECTION OF PIPELINE SUSTAINED A RUPTURE AS THE RESULT OF SELECTIVE SEAM CORROSION.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930187 | 1993-11-15 | 2620 | COLUMBIA GULF TRANSMISSION CO | LAKE ARTHUR | CAMERON | LA |  | 13.02 ON 16" | 699 +41 | 1745 | 1993-10-15 | 1 | NO |  |  | LA | Null | YES | LEAK | 0 | 0 | 0 | 100000 | 76524.3902 | 166710.2207 | Null | 4 | 0 |  | 19931112 | 860 | 1014 | BY TEST | 1470 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1954; NMDIA: 16; THK: 0.25; SPEC: API 5 LX 52; SMYS: 52000; SEAM: ERW; MANU: YOUNGSTOWN S & T; MANYR: 1953; LOCLK: UNDER WATER; PNAME: S.J. CHOBY - MANAGER; PHONE: 3043572349; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: NO; MARK: YES; MRKTP: RIVER XING SIGN N MALLARD; STAT: NO; CTEST: Null | PIPE APPEARS TO HAVE BEEN SNAGGED BY OUTSIDE FORCE, EITHER A BARGE OR A TUG, AND PULLED OFF DITCH LINE APPROXIMATELY 12' CAUSING A BUCKLE AND CRACK IN THE PIPE ALONG A FIELD GIRTH WELD RESULTING IN A LEAK.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19930190 | 1993-11-16 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA |  | MEADE | KS |  | 77 |  | 830 | 1993-10-12 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 2 | 0 | 0 | 0 | Null | 3 | 0 |  | 19931012 | 0 | 712 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: NIGHTCAP; MLKD: OTHER; MLKDO: ALUMINIUM NIGHTCAP; PRTSY: OTHER; PRTSO: CROSSOVER; PRTYR: 1958; NMDIA: 24; THK: 0; SMYS: 0; MANU: MALONEY; MANYR: 0; LOCLK: UNDER GROUND; PNAME: F.R. FLEET SR - ENGINEER; PHONE: 7086913786; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | PART 3 NARRATIVE - VENTED 24" NIGHT CAP EXITTED PIPE DUE TO A PRESSURE DIFFERENTIAL OF UNKNOWN SIZE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930192 | 1993-11-08 | 12576 | MISSISSIPPI RIVER TRANSMISSION CORP | NEELYVILLE | BUTLER | MO | 63954 | 288.5 |  | 1020 | 1993-10-12 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 192000 | 146926.8293 | 320083.6237 | Null | 0 | 0 |  | 19931012 | 0 | 450 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: MECHANICAL JOINT; MLKD: OTHER; MLKDO: UNKNOWN; PRTSY: OTHER; PRTSO: UNKNOWN; PRTYR: 1929; NMDIA: 22; THK: 0.31; SPEC: A30; SMYS: 30000; SEAM: SMITH WELD; MANYR: 0; LOCLK: UNDER GROUND; PNAME: RAUL G. ESPINOSA - MANAGER DOT COMP.; PHONE: 3184293924; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | DRESSER COUPLING FAILED WHILE REPAIRING A LEAK. PIPE PULLED FROM THE COUPLING. UNEVEN TERRAIN PLUS NORMAL AND AXIAL FORCES CONTRIBUTED TO THE FAILURE.PART 2 OTHER- DRESSER COUPLING.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930193 | 1993-11-08 | 17620 | ROCKY MOUNTAIN NATURAL GAS CO INC | GARFIELD |  | CO |  |  |  | 610 | 1993-08-05 | 1 | NO |  |  |  | Null | YES | LEAK | 0 | 0 | 0 | 930000 | 711676.8293 | 1550405.0523 | Null | 1 | 10 |  | 19930805 | 310 | 0 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: UNKNOWN; MLKD: OTHER; MLKDO: UNKNOWN; PRTSY: COMPRESSOR STATION; PRTYR: 0; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: VIRGINIA S. MATTHEWS - SECRETARY; PHONE: 04873443; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930196 | 1993-11-04 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA | OFFSHORE LOUISIANA |  | LA |  |  |  | 935 | 1993-10-02 |  | YES | WEST | 564 |  | YES | NO | LEAK | 0 | 0 | 0 | 100000 | 76524.3902 | 166710.2207 | Null | 48 | 0 |  | 19931002 | 950 | 1200 | BY TEST | 1957 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | MECHANICAL JOINT |  | STEEL |  | PIPELINE |  | 1993 | 24 | 0 | ANSI 900# CLASS | 0 |  |  | BIG INCH MARINE SYSTEM | 1993 | UNDER WATER |  | F. ROY FLEET - SENIOR ENGINEER | 7086913786 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION | 24" FLANGE ON BIG INCH MAR BALL FLANGE CONECTOR | YES | 19930725 | GAS | 0 | 1 | 950 | LEAKING FLANGE CONNECTION ON 24" BALLFLANGE CONNECTOR.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930197 | 1993-11-08 | 19160 | TENNESSEE GAS PIPELINE CO | EAST CAMERON |  | LA |  | 507F-301+13.11 |  | 1330 | 1993-10-05 |  | YES | E.C. | 71 |  | YES | NO | LEAK | 0 | 0 | 0 | 50000 | 38262.1951 | 83355.1103 | Null | 2 | 0 |  | 19931005 | 0 | 1247 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1958; NMDIA: 16; THK: 0.41; SPEC: API 5L; SMYS: 42000; SEAM: DSAW; MANU: U.S. STEEL; MANYR: 1958; LOCLK: UNDER WATER; PNAME: L.A. SALINAS - STAFF CIVIL ENGINEER; PHONE: 7137572781; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | LEAK DISCOVERED AFTER BUBBLES, OIL SHEEN DETECTED AT SURFACE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930198 | 1993-11-27 | 12462 | MID - LOUISIANA GAS CO |  | ADAMS | MS | 39121 |  |  | 2250 | 1993-11-16 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 46000 | 35201.2195 | 76686.7015 | YES | 2 | 0 |  | 19931117 | 162 | 250 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: MECHANICAL JOINT; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1927; NMDIA: 22; THK: 0; SMYS: 24000; MANYR: 1926; LOCLK: UNDER WATER; PNAME: RAMON L. SIMPSON - SUPT. PIPELINE OPER.; PHONE: 3186654426; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | PART 3 NARRATIVE - HEAVY RAINFALL RUNOFF WASHED OUT SUPPORTING SOIL AROUND 1OR MORE DRESSER COULINGS IN A NORMALLY DRY CREEK BOTTOM RESULTING IN PIPE MOVEMENT AND PULLOUT FROM AN EXPOSED MECHANICAL COUPLING.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19930200 | 1993-11-17 | 5304 | FLORIDA GAS TRANSMISSION CO | CUTLER RIDGE | DADE | FL |  | 2.034 | 107 + 37 | 1130 | 1993-10-26 | 3 | NO |  |  |  | Null | NO | RUPTURE | 0 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 30 |  | 19931026 | 665 | 975 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1961; NMDIA: 4; THK: 0.13; SPEC: API - 5L; SMYS: 35000; SEAM: ERW; MANU: TEX - TUBEE; MANYR: 1961; LOCLK: UNDER GROUND; PNAME: MERLIN MOSEMAN - CODE COMPLIANCE ENR.; PHONE: 7136467344; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PERMANENT; STAT: YES; CTEST: Null | PART 3 NARRATIVE - PIPELINE HIT BY CONTRACTOR WITH AN AUGER WHILE INSTALLINGOCCUPANT UTILIZED PROPANE CYLINDERS INSIDE HOUSE FOR SPACE/WATER HEATING PARTGUARD RAIL POSTS ALONG ROADWAY.2 APPARENT CAUSE- D LEAKING PROPANE CYLINDER.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19930202 | 1993-11-28 | 602 | ARKLA ENERGY RESOURCES | WILBURTON | LATIMER | OK | 74578 |  |  | 1500 | 1993-10-21 | 3 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 2 | 40000 | 30609.7561 | 66684.0883 | Null | 1 | 0 |  | 19931021 | 0 | 1000 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: BEARING IN BLOWER; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1967; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: RAUL G. ESPINOSA - MANAGER DOT; PHONE: 3184293924; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | MECHANICAL FAILURE OF BEARING (IN BLOWER) IGNITED OIL (LUB) STARTING A FIRE IN THE CRANKCASE WHICH RESULTED IN AN EXPLOSION INJURING 2 COMPANY EMPLOYEES.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930211 | 1993-12-08 | 2616 | COLUMBIA GAS TRANSMISSION CORP | SANDYVILLE | JACKSON | WV | 25275 |  | 23 + 56 | 959 | 1993-11-04 | 1 | NO |  |  |  | Null | NO | RUPTURE | 16 | 0 | 0 | 250000 | 191310.9756 | 416775.5517 | Null | 0 | 31 |  | 19931104 | 914 | 975 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | OTHER | DRIP RESERVOIR | STEEL |  | PIPELINE |  | 1955 | 20 | 0.38 | API 5LX | 42000 | SEAMLESS |  |  | 1954 | UNDER GROUND |  | S.J. CHOBY - MANAGER CODES, STANDARDS | 3043572349 | INTERNALLY | OTHER | BOTTOM OF DRIP RESEVIOP | OTHER | POSS CO2 RELATED | COATED | YES | 1956 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | PART 3 - INTERNAL CORROSION CAUSED RUPTURE OF A PIPELINE DRIP RESERVOIR; THERESULTING FIRE DESTROYED ONE HOUSE TRAILER, DAMAGED OTHER DWELLINGS, AND DESTROYED MULTIPLE VEHICLES. PART A CORROSION #2 OF DRIP RESERVOIR.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930215 | 1993-12-12 | 19570 | TRANSCO GAS PIPELINE CORP | OFFSHORE - BRAZOS |  | TX |  | 0.01 |  | 205 | 1993-11-16 |  | YES | BRAZOS | A-76 |  | YES | NO | RUPTURE | 108 | 0 | 0 | 1500000 | 1147865.8537 | 2500653.3101 | Null | 4 | 0 |  | 19931116 | 1120 | 1250 | NO DATA | 2360 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | MECHANICAL JOINT |  | STEEL |  | PIPELINE |  | 1990 | 20 | 0.63 | ANSI 900#END CONNECT | 0 |  |  | HYDROTECH | 1990 | UNDER WATER |  | B.R. LANDES - STAFF COMPLIANCE ANALYST | 7134392001 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | 20" 900# END CONNECTOR W/RTJ FLANGE | YES | 19900509 | WATER |  | 4 | 3350 | CAUSE IS UNKNOWN AT THIS TIME. A COMPLETE EXAMINATION WILL BE PERFORMED TODETERMINE THE REASON FOR THE FAILURE. A SUPPLEMENTAL REPORT WILL BE FILEDUPON COMPLETION OF THE INVESTIGATION. PART 3 NARRATIVE- 20" 900 # ENDCONNECTOR GAVE WAY CAUING THE RUPTURE AND FIRE. THE REASON FOR THE INCIDENTIS UNKNOWN AT THIS TIME. SUPPLEMENTAL REPORT 8/22/94 INDICATES THAT A 20" ENDCONNECTOR FAILED, CAUSING THE PIPELINE TO RUPTURE AND FIRE. INSPECTION OF THECONNECTOR AND 20" PIPE INDICATES THAT THE CONNECTOR DID NOT ADEQUATELY ENGAGE,ALLOWING SLIPPAGE AT THE POINTS OF CONNECTION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19930218 | 1993-12-16 | 2795 | CORNERSTONE NATURAL GAS CO | ARLINGTON | TARRANT | TX |  |  | 787 + 50 | 1630 | 1993-10-28 | 1 | NO |  |  | TX | Null | NO | RUPTURE | 0.25 | 0 | 0 | 52000 | 39792.6829 | 86689.3148 | Null | 3 | 0 |  | 19931028 | 600 | 1350 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 0; NMDIA: 16; THK: 0.25; SPEC: AP15LXGRX - 60; SMYS: 60000; SEAM: ELECTRIC RESIST; MANU: STUPP CORP; MANYR: 1989; LOCLK: UNDER GROUND; PNAME: PHILLIP W. LOCKWOOD; PHONE: 2146915536; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19930219 | 1993-12-16 | 19570 | TRANSCO GAS PIPELINE CORP | EAST BERNARD | WHARTON | TX |  | 274.18 | 1447 +75 | 2159 | 1993-11-15 | 1 | NO |  |  |  | Null | NO | RUPTURE | 340 | 0 | 0 | 229000 | 175240.8537 | 381766.4053 | Null | 2 | 50 |  | 19931115 | 760 | 800 | BY CFR 192.619(A)(3) | 1179 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1950; NMDIA: 30; THK: 0.32; SPEC: API 5 LX; SMYS: 52000; SEAM: DSA; MANU: CONS. WESTERN - KAISER; MANYR: 1949; LOCLK: UNDER GROUND; PNAME: B.R. LANDES - STAFF COMPLIANCE ANALYST; PHONE: 7134392001; PROT: Null; CAULK: EARTH MOVEMENT: SUBSIDENCE; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | RUPTURE OCCURRED IN BODY OF 30" LINE PIPE OUTSIDE OF THE FILLET WELD OF A WELD SADDLE USED TO REINFORCE A 6" BRANCH CONNECTION. MCI"S INVESTIGATIVE REPORT ON THE RUPTURE CONCLUDED THAT THERE WAS NO METALLURGICAL CAUSE OF THE FAILURE. THE SUSPECTED CAUSE OF TH FAILURE IS EXCESSIVE STRESSES DUE TO MOVEMENT OF THE 30" PIPELINE BY SOIL SUBSIDENCE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940018 | 1993-12-20 | 405 | ANR PIPELINE CO | HIGH ISLAND |  | TX |  | X=3,689,601.73 Y=163,471 |  | 730 | 1993-11-17 |  | YES | HI | 323 |  | Null | NO | LEAK | 0 | 0 | 0 | 2500000 | 1913109.7561 | 4167755.5168 | Null | 0 | 0 |  | 19931117 | 908 | 1440 | BY TEST | 1827 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1977; NMDIA: 36; THK: 0.75; SPEC: 5LX60; SMYS: 60000; SEAM: DSAW; MANU: STELCO; MANYR: 1977; LOCLK: UNDER WATER; PNAME: DONALD E. CROSS - SR. CODES ANALYST; PHONE: 3134962460; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; MRKTP: 0N; STAT: Null; CTEST: Null | PIPELINE WAS STRUCK BY LEGS OF JACKUP RIG THAT WAS DRAGGED OVER THE 36" LINE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19940019 | 1994-01-24 | 10030 | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | SEC 1, T, 7 N, R.23W | GOSPER | NE |  |  |  | 900 | 1993-12-20 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 45 |  | 19931220 | 400 | 500 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1949; NMDIA: 2; THK: 0.15; SMYS: 0; MANYR: 1949; LOCLK: ABOVE GROUND; PNAME: LEROY PETERSEN - POLICY & COMPLIANCE; PHONE: 3037633260; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: 1; STAT: NO; CTEST: Null | THERE WAS A PIPELINE MARKER WITHIN 100 FT. OF BREAK. THE INCIENT OCCURRED WHEN THE BUCKET OF A FRONTEND LOADER ACCIDENTLY HOOKED THE LINE AS A FARMER CLEARED SNOW FROM AN AREA IN PREPARATION TO GRINDING HAY. THE TOP OF GROUND LINETRAVERSES THE FARMERS LAND, WITH THE EXACT LOCATION WELL MARKED WITH PERMANENT PIPELINE MARKERS. THE LOCATION HAS BEEN WELL KNOWN BY THE FARMER FOR MANY YEARS. THE PRIME FACTOR IN THIS INCIDENT WAS THE SNOW COVER. THE ACTUAL BREAKOCCURRED APPROXIMATELY 100 FEET FROM THE POINT WHERE CONTACT WAS MADE BY THEPIECE OF MACHINERY. NO ONE WAS IN THE AREA OF THE BREAK, THERE WAS NO FIRE AND THERE WERE NO INJURIES. REPAIRS WERE MADE TO THE PIELINE AND THE LINE WAS PLACEDF BACK INTO SERVICE AT APPROXIMATELY 12:00, NOON. GAS SERVICE WAS RESTORED TO ALL CUSTOMERS WITHOUT FURTHER INCIDENT.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940020 | 1994-01-17 | 13750 | NORTHERN NATURAL GAS CO (ENRON) | MELLEN | ASHLAND | WI | 54546 | 19.20 |  | 530 | 1993-12-20 | 1 | NO |  |  |  | Null | NO | RUPTURE | 5 | 0 | 0 | 750000 | 573932.9268 | 1250326.6551 | Null | 3 | 30 |  | 19931220 | 925 | 1095 | BY TEST | 1523 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1968 | 10 | 0.17 | API 5LX | 52000 | ERW |  | REPUBLIC | 1968 | UNDER GROUND |  | JOHN W. CASKEY - CODE COMPLIANCE ENGR. | 7136467343 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1969 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19940021 | 1994-02-24 | 405 | ANR PIPELINE CO | SULPHUR SPRINGS | HENRY | IN |  | 781.55 | 9350+37 | 1900 | 1993-11-23 | 1 | NO |  |  | IN | Null | NO | RUPTURE | 63 | 0 | 0 | 58000 | 44384.1463 | 96691.928 | Null | 1 | 22 |  | 19931123 | 832 | 858 | BY TEST | 1230 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1956; NMDIA: 30; THK: 0.34; SPEC: API5LX; SMYS: 52000; MANU: A.O. SMITH; MANYR: 0; LOCLK: UNDER GROUND; PNAME: DONALD CROSS SR. - CODES ANALYST; PHONE: 3134962460; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; MRKTP: 0Y; STAT: Null; CTEST: Null | PIPELINE WAS STRUCK BY A TRENCHING MACHINE USED TOLAY DRAINAGE TILE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19940023 | 1994-02-24 | 19160 | TENNESSEE GAS PIPELINE CO | EAST CAMERON BLOCK 71 |  | LA |  | 507F-301 +10.1 |  | 1500 | 1994-01-15 |  | YES | E.C. | 71 |  | YES | NO | LEAK | 0 | 0 | 0 | 50000 | 37446.7178 | 81578.5735 | Null | 1 | 0 |  | 19940115 | 530 | 1247 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1958; NMDIA: 16; THK: 0.41; SPEC: API 5L; SMYS: 42000; SEAM: DSAW; MANU: U.S. STEEL; MANYR: 1958; LOCLK: UNDER WATER; PNAME: L.A. SALINAS - STAFF CIVIL ENGINEER; PHONE: 7137572781; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | LEAK DISCOVERED AFTER BUBBLES, OIL SHEEN DETECTED AT SURFACE. PARTT 2 D- UNDER INVESTIGATION POSSIBLE PINHOLE LEAK.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19940024 | 1994-01-26 | 22617 | WILLIAMS NATURAL GAS CO | EDMOND | LOGAN | OK | 73034 | 4615 +56 |  | 445 | 1993-12-22 | 1 | NO |  |  | OK | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 30 |  | 19931223 | 368 | 595 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | GIRTH (ACETYLENE) | OTHER | AT WELD | PIPELINE |  | 1930 | 20 | 0.34 | NOT KNOWN | 420000 | SEAMLESS |  | NATIONAL TUBE | 0 | UNDER GROUND |  | WARREN A. ETHERIDGE - PIPELINE | 9185884427 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION | ACETYLENE GIRTH WELD FAILED | Null |  | NO DATA |  | 0 | 0 | AN ACETYLENE GIRTH WELD FAILED COMPLETELY. THE BASE METAL REMAINED INTACT THE FRACTURE WAS ENTIRELY IN THE WELD METAL AND OCCURRED SYMMETRICALLY BETWEEN THE ADJACENT JOINTS .
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940025 | 1994-01-18 | 2714 | CNG TRANSMISSION CORP | FARMINGTON | TIOGA | PA | 16922 | TIOGA STATION |  | 420 | 1993-12-16 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 155000 | 118612.8049 | 258400.842 | Null | 0 | 0 |  | 19931222 | 850 | 1000 | BY TEST | 1719 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: AIR LINE (FREEZE OFF); MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1989; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: JACK L. ADAMS - ADMINSTRATOR CODES & STANDARDS; PHONE: 3046238410; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | SUPPLY LINE TO ESD POWER OPERATOR ON 8" BLOWOFF FROZE OFF FROM MOISTURE IN LINERESULTING IN VALVE OPENING AND DSICHARGING GAS TO ATMOSPHERE.GAS WAS BEING DISCHARGED THROUGH BLOWOFF DESIGNED TO DISCHARGE GAS SAFELY.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940026 | 1994-01-21 | 13750 | NORTHERN NATURAL GAS CO (ENRON) | CLIFTON CLAY |  | KS | 66937 |  |  | 2230 | 1993-12-27 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 750000 | 573932.9268 | 1250326.6551 | YES | 9 | 30 |  | 19931228 | 0 | 0 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: TURBINE DRIVER; MLKD: OTHER; MLKDO: UNKNOWN; PRTSY: COMPRESSOR STATION; PRTYR: 1967; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: OTHER; LOCLO: BUILDING; PNAME: JOHN W. CASKEY - CODE COMP. ENGR; PHONE: 7136467343; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | APPARENTLY A FOREIGN OBJECT DAMAGED THE DRIVER TURBINE. VIBRATION RESULTED, CAUSING TURBINE DESTRUCTION AND A FIRE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940027 | 1994-02-04 | 18516 | SOUTHERN NATURAL GAS CO | 15 MILES WEST |  | MS | 39090 | 39.170 ON 24" 2ND NORTH |  | 1345 | 1994-01-14 | 1 | NO |  |  |  | Null | NO | RUPTURE | 108 | 0 | 0 | 1187500 | 889359.5482 | 1937491.1196 | Null | 0 | 55 |  | 19940114 | 730 | 750 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1952 | 24 | 0.25 |  | 52000 | SUBMERGED ARC |  | REPUBLIC | 1952 | UNDER GROUND |  | KURT REGULSKI - MANAGER TECHNICAL SUPPORT | 6019363040 | EXTERNALLY | OTHER | VISIBLE EXTERNAL CRACKS | OTHER | NOT GIVEN | COATED | YES | 1952 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | STRESS CORROSION CRACKING IN THE BODY OF THE PIPE IN CONJUNCTION WITH CORROSION FATIGUE PROPAGATED INTO A FAILURE AND PIPELINE RUPTURE WITH NATURAL GAS IGNITION. PART A - CORROSION PRELIMINARY BATTELLE INVESTIGATION INDICATES LOW PH STRESS CORROSION CRACKING IN ASSOCIATION WITH CORROSION FATIGUE AT INTITALPOINT OF FAILURE.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19940028 | 1993-01-07 | 10030 | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | NW/4 SECTION 16-T20S-R15W | BARTON | KS |  |  |  | 845 | 1993-12-02 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 10 |  | 19931206 | 800 | 0 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: LIQUID TRANSFER LINE; MLKD: STEEL; PRTSY: OTHER; PRTSO: STORAGE FIELD LN; PRTYR: 1972; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: LEROY A PETERSEN - POLICY AND COMPLIANCE; PHONE: 3037633455; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | A 1" DISCHARGE LINE ON AN INLINE DRIP BROKE OFF AS AN APPARENT FREEZE BROKE LOOSE. THE FIELDMAN WAS STRUCK ON THE HEAD BY THE PIECE OF 1" PIPE CAUSING ANINJURY THAT REQUIRED SEVERAL DAYS INT HE HOSPITAL. THERE WAS NO FIRE OR FURTHER DAMAGE. THE FIELDMAN OPENED THE VALVE ON THE DRIP TOO MUCH TO CLEAR AN APPARENT FREEZE. THIS WAS ROUTINE OPERATION TO CLEAR LIQUID FROM THE DRIP.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19940029 | 1993-12-21 | 15007 | PACIFIC GAS & ELECTRIC CO | SAN JOSE | SANTA CLARA | CA | 95122 | V-141.9 | 7.68 | 330 | 1993-11-22 | 3 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 1 |  | 19931122 | 190 | 200 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: MECHANICAL JOINT; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1929; NMDIA: 20; THK: 0.28; SPEC: A.O.SMITH; SMYS: 33000; SEAM: SINGLE SUBMERGE; VALVE: PLUG; MANU: NORDSTROM; MANYR: 0; LOCLK: UNDER PAVEMENT; PNAME: JAMES H. POPE - VICE PRESIDENT - T &CS; PHONE: 4159736999; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | A 20" LINE WAS CUT & CAPPED DOWNSTREAM OF A DRESS COUPLING. A 7' SECTION OF PIPE & THE WELDED CAP WAS BLOWN OUT OF THE DRESSER COUPLING WHEN THE LINE WASPRESSURIZED TO 190 PSIG. A COMPANY EMPLOYEE WAS INJURED.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19940030 | 1993-12-21 | 19235 | TEXAS EASTERN GAS PIPELINE CO | MABEN | OKTIBBEHA | MS |  | 50.54 | 2669 +00 | 930 | 1993-11-24 | 1 | NO |  |  | MS | Null | NO | OTHER | 0 | 1 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19931124 | 825 | 1000 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: NOT GIVEN; MLKD: OTHER; MLKDO: VALVE HANDWHEEL VALVE OPR; PRTSY: OTHER; PRTSO: PIG LAUNCHER/RECEIVER FAC; PRTYR: 1964; NMDIA: 0; THK: 0; SMYS: 0; VALVE: GATE 30"; MANU: WKM; MANYR: 1964; LOCLK: ABOVE GROUND; PNAME: DWAYNE TESCHENDORF - SENIOR ENGINEER; PHONE: 7136275573; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | EMPLOYEE D.L. BURROUGHS WAS APPARENTLY STRUCK BY A PIPELINE VALVE HANDWHEEL WHILE THE PIPELINE CREW WAS LAUNCHING A CLEANING PIG. TEXAS EASTERN BELIEVES THAT THE GAS DRIVEN MOTOR OPERATOR FOR THE VALVE ENGAGED AND THE UNSECURED HANDWHEEL STRUCK THE EMPLOYEE. ALTHOUGH PERSONNEL WERE IN THE IMMEDIATE VICINITY OF THE ACCIDENT, THERE WERE NO KNOWN EYE WITNESSES.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19940033 | 1994-02-24 | 19160 | TENNESSEE GAS PIPELINE CO | EAST CAMERON BLK 24 |  | LA |  | 507A-3101+2.5 |  | 1245 | 1994-02-12 |  | YES | EC | 24 |  | Null | NO | LEAK | 0 | 0 | 0 | 50000 | 37446.7178 | 81578.5735 | Null | 1 | 0 |  | 19940212 | 910 | 1440 | BY TEST | 2165 | CORROSION | CORROSION | INTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1972; NMDIA: 16; THK: 0.38; SPEC: API 5L; SMYS: 52000; MANU: U.S. STEEL; MANYR: 1972; LOCLK: UNDER WATER; PNAME: L.A. SALINAS - STAFF CIVIL ENGINEER; PHONE: 7137572781; LOC: INTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: GALVANIC; COAT: COATED; PROT: Null; CPYR: 1972; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | PART 3 - DURING PIGGING OPERATIONS, LEAK DISCOVERED BY HELICOPTER CREW (BUBBLES AT SURFACE).
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940035 | 1994-03-04 | 13845 | NORTHWEST PIPELINE CORP | MTN HOME | ELMORE | ID |  | 0.1717 RENO 16" LINE | 9+07.3 | 1645 | 1994-02-22 | 1 | NO |  |  |  | Null | NO | RUPTURE | 22 | 0 | 0 | 170200 | 127468.6275 | 277693.4641 | Null | 0 | 40 |  | 19940222 | 890 | 910 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1962 | 16 | 0.23 | API5LX | 46000 | ELECTRIC RESIS |  | KAISER | 1962 | UNDER GROUND |  | JAMES W. SMITH - MANAGER SAFETY & ENVIRONMENTAL | 8015846906 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | COATED | YES | 1962 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | THE INCIDENT OCCURRED AT 1645 HOURS ON FEBRUARY 22, 1994 AT MILEPOST 0.1717 ON NORTHWEST'S RENO 16 INCH LINE. THE SITE IS IN A 21 MILE VALVE SECTION THATCONSISTS OF CULTIVATED LAND AND DESERT. THE LINE IS NOT LOOPED IN THIS SECTION AND NORTHWEST INTERRUPTED SERVICE AT THE FLYING H FARMS DELIVERY POINT WHERE INTERMOUNTAIN GAS, A LOCAL DISTRIBUTION COMPANY, SERVES A RESIDENTIAL AREAOF MOUNTAIN HOME AIR FORCE BASE, WHICH HAS A POPULATION OF APPROXIMATELY 1000 PEOPLE. THE INCIDENT APPEARS TO HAVE BEEN THE RESULT OF THE PIPE COATING (COAL TAR ENAMEL WITH FELT OUTER WRAP) BEING DISBONDED AND SHIELDING THE PIPE FROM CATHODIC PROTECTION IN A THREE FOOT SECTION. IN THE FAILURE INITIATION AREA, EXTERNAL CORROSION HAD REDUCED THE PIPE WALL THICKNESS TO THE POINT OF COMPROMISING THE PIPE STRENGTH. THE ERW PIPE SEAM WAS NOT AFFECTED AND THE PIPEAND COATING ADJACENT TO THE CORRODED AREA WAS IN GOOD CONDITION. APPROXIMATELY 60 FEET OF PIPE WAS REPLACED. THERE WERE NO INJURIES OR FIRE ASSOCIATED WITH THE RUPTURE AND THE LINE WAS RESTORED TO SERVICE BY 0750 HOURS ON FEBRUARY23, 1994. FULL SERVICE WAS RESUMED AT THE FLYING H FARMS DELIVERY POINT BY 1030 HOURS THE SAME DAY. PART3 - DISBONDED PIPE COATING SHIELDED THE PIPE FROMCATHODIC PROTECTION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19940040 | 1994-01-19 | 22182 | WASHINGTON GAS LIGHT CO | BOWIE | PRINCE GEORGES | MD | 20715 |  |  | 915 | 1994-01-19 | 3 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 0 | 317465 | 19940119 | 10 | 260 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: OTHER; PRTFO: NOT GIVEN; MLKD: OTHER; MLKDO: NO MATERIAL INVOLVED; PRTSY: OTHER; PRTSO: NOT GIVEN; NMDIA: 0; THK: 0; SMYS: 0; LOCLK: OTHER; LOCLO: NOT GIVEN; PNAME: WM. A. HINDE - SAFETY SUPERVISOR; PHONE: 7037507687; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | ON THE EVENING OF JANUARY 18, 1994, THE TEMPERATURE DROPPED TO SINGLE DIGITSOF NINE DEGREES AT 6:00 P.M. AND CONTINUED TO DROP TO A LOW OF FOUR BELOW ZERO BY 6:00 A.M. ON THE MORNING OF JANUARY 19, 1994. THIS EXTREME WEATHER CONDITION CREATED AND EXCESS DEMAND AND REDUCED PRESSURES ON THE FAR END OF WASHINGTON GAS TRANSMISSION SYSTEM. WHEN PRESSURES ON BOWIE'S DISTRIBUTION REGULATOR SYSTEM REACHED A LOW OPERATING LEVEL ON THE MORNING OF JANUARY 19, 1994, SELECTED SECTIONS WERE SHUT OFF (APPROXIMATELY 1,700 METERS) IN ORDER TO PREVENT THE PRESSURE LOSS TO ANOTHER 10,000 METERS THAT COULD HAVE POSSIBLY BEEN AFFECTED. THIS WAS DONE AT THE EXTREME END OF THE TRANSMISSION SYSTEM AND SERVICE WAS RESTORED TO ALL OUTAGES AT THE FIRST SIGN OF A PRESSURE INCREASE ON THE TRANSMISSION SYSTEM. ADDITIONALLY, 577 METERS WERE VALVED OFF IN WALDORF, MARYLAND, SOME 15 MILES SOUTH OF BOWIE. AT THE TIME OF TELEPHONIC REPORTING, THE CAUSE FOR THIS PRESSURE PROBLEM WAS UNKNOWN. FURTHER INVESTIGATION UNCOVERED A FROZEN DISTRIBUTION REGULATOR THAT WAS RELATED TO WEATHER CONDITIONS AND NOT THE BOWIE PRESSURE PROBLEM.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19940056 | 1994-02-03 | 30548 | UNION ISLAND PIPELINE CO | TRACY | SAN JOAQUIN | CA | 95201 | UNION ISLAND | 0+00 | 800 | 1994-01-13 | 1 | NO |  |  | CA | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 0 |  | 19940113 | 0 | 1000 | BY TEST | 1800 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: ODORANT PUMP SEAL; MLKD: OTHER; MLKDO: MERCAPTAN ODORANT; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1991; NMDIA: 12; THK: 0.25; SPEC: API 5L-X52; SMYS: 0; SEAM: ERW; MANYR: 0; LOCLK: OTHER; LOCLO: NOT GIVEN; PNAME: PATRICK A. ARMSTRONG - DIST. SUPERVISOR; PHONE: 8055477200; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | THE PUMP SEAL ON THE ODORANT INJECTION SYSTEM PUMP FAILED CAUSING THE RELEASETHE PHILADELPHIA FIRE DEPATMENT HAS INVESTIGATED THIS INCIDENT WHICH WAS INIT OF APPROXIMATELY ONE QUART OF CAPTAN 50 ODORANT. THE MERCAPTAN ODORANT TRAVEIALLY BELIEVED TO BE A HOUSE FIRE FROM AN INTERNAL SOURCE ON JANUARY 25, 1994LED DOWNWIND APPROXIMATELY 1.3 MILES TO THE DELTA ISLAND ELEMENTARY SCHOOL. T. THE RESULTS OF THE PHILDELPHIA FIRE DEPARTMENT INVESTIGATION, OF WHICH THEHE SCHOOL STAFF DETECTED THE ODDORANT INSIDE ONE OF THE SCHOOL BUILDINGS, ANDSPECIFIC HAVE NOT BEEN RELEASED TO THE PHILADELPHIA GAS WORKS, INDICATES THAT SUSPECTING A GAS LEAK, EVACUATED THEIR FIRST THROUGH FOURTH GRADES TO A NEAR THE CAUSE OF THE FIRE WAS DUE TO THE MIGRATION OF NATURAL GS INTO THE BASEMEBY BUILDING. ONE TEACHER REPORTED SHORTNESS OF BREATH AND WAS SENT BY AMBULANNT OF 2452 S. PHILIP STREET WHICH WS IGNITED BY THE HEATER IN THAT BASEMENT.CE TO A HOSPITAL. SHE WAS EVALUATED AND RELEASED THAT DAY. THE SCHOOL CHILDRETHE PHILADELPHIA GAS WORKS DISPUTES THESE FINDINGS AT THIS TIME. INITIAL INVEN RETURNED TO THIER CLASSROOMS WITHIN TWO HOURS.STIGATION PON ARIVAL FOUND NO INDICATION OF GAS MIGRATION INTO THE RESIDENCES AT 2450, 2452, 2454. AT NO TIME WERE READINGS LEL FOUND INSIDE DURING THE INVESTIGATION AND REPAIR OF THE 6" GAS MAIN. THE RESULTS OF THE INVESTIGATION WERE GIVEN BY PHONE TO THE PHILADELPHIA GAS WORKS ON JANUARY 2, 1994 AT 1330 HOURS TELEPHONIC NOTICE WAS MADE TO THE NATIONAL RESPONSE CENTER, SERIAL #219022 ON JANUARY 27, 1994.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19940057 | 1994-02-02 | 12642 | MOBILE GAS SERVICE CORP | THEODORE | MOBILE | AL | 36582 |  |  | 243 | 1994-01-25 | 3 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 3 | 11 |  | 19940125 | 270 | 270 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | WELD | GIRTH | STEEL |  | PIPELINE |  | 1966 | 18 | 0.31 | API 5L | 42000 | ERW |  |  | 0 | UNDER GROUND |  | JIMMIE L. BUTLER - MANAGER/ENGINEERING | 2054762720 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION | END CAP | YES | 19921214 | GAS |  | 24 | 270 | A LEAK OCCURRED WHEN AN END CAP BLEW OFF THE END OF AN 18" STEEL PIPE AT RANGELINE ROAD AND HAMILTON BOULEVARD.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19940060 | 1994-01-28 | 22365 | WESTAR TRANSMISSION CO | FRIONA | PARMER | TX |  |  | LINE # 143-000 | 1554 | 1993-12-27 | 1 | NO |  |  |  | Null | NO | RUPTURE | 8 | 0 | 0 | 45430 | 34765.0305 | 75736.4533 | Null | 0 | 50 |  | 19931227 | 320 | 400 | BY TEST | 1100 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1929; NMDIA: 8.58; THK: 0.19; SPEC: GRD B; SMYS: 1526; MANU: ANSI 720; MANYR: 0; LOCLK: UNDER GROUND; PNAME: STEVE BUSTOS - COMPLIANCE COORDINATOR; PHONE: 8063736042; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PERMANENT PIPELINE MARKER; STAT: NO; CTEST: Null | LINE CUT BY FARMER WHILE DEEP PLOWING.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19940061 | 1994-02-04 | 11680 | LONE STAR GAS CO | CHILDRESS | COTTLE | TX |  | 650+83 |  | 800 | 1994-01-02 | 1 | NO |  |  | TX | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 0 |  | 19940102 | 270 | 350 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: MECHANICAL JOINT; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 0; NMDIA: 4; THK: 0.2; SPEC: GRADE A; SMYS: 30000; SEAM: LAP WELD; MANYR: 0; LOCLK: UNDER GROUND; PNAME: PHILLIP MURDOCK; PHONE: 2146702229; LOC: EXTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: GALVANIC; COAT: BARE; PROT: YES; CPYR: 1974; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | A CORROSION LEAK ON 4" DRESSER COUPLING CAUSED THE LEAK. THE LEAK WAS ADJACENT TO STATE HWY. 83.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19940062 | 1994-02-08 | 1552 | BLUE DOLPHIN PIPELINE CO | FEDERAL OFFSHORE WATER | GALVESTON AREA | TX |  |  |  | 700 | 1994-01-24 |  | YES | GA | 286 |  | YES | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19940124 | 475 | 600 | BY TEST | 750 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1965 | 20 | 0.5 | API 5LX | 52000 | SEAMLESS |  |  | 1965 | UNDER GROUND | UNDER WATER | VERNON R. LUNING | 7136213993 | INTERNALLY | LOCALIZED PITTING |  | GALVANIC | 0 | COATED | YES | 1965 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | PINHOLE GAS LEAK CAUSED BY APPARENT LOCALIZED INTERNAL CORROSION. LEAK WAS REPAIRED BY INSTALLATION OF 1500 PSIG WP BOLTED PIPELINE CLAMP. PART A - 250 #ZINC ANODES WERE INSTALLED ON 1/4 MILE SPACING DURING THE INITIAL CONSTRUCTION IN 1965. IMPRESSED CURRENT IS SUPPLIED TO BOTH THE OFFSHORE AND ONSHORE ENDS OF THE PIPELINE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940069 | 1994-02-16 | 2620 | COLUMBIA GULF TRANSMISSION CO | RAYNE | ACADIA | LA | 70578 |  | 3+73 | 605 | 1994-01-20 | 2 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 331000 | 247897.272 | 540050.1563 | Null | 1 | 10 |  | 19940120 | 932 | 1008 | BY TEST | 1285 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: RENTAL LIQUID PUMP; MLKD: OTHER; MLKDO: PORTABLE PUMP EQUIPMENT; PRTSY: PIPELINE; PRTYR: 1958; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: S.J. CHOBY - MANAGER CODES STANDARDS; PHONE: 3043572349; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | IN PREPARATION FOR A PIGGING OPERATION ON LINE 200, COLUMBIA EMPLOYEES WERE PUMPING A CLEANING SOLUTION INTO THE PIPELINE. UNANTICIPATED ACTUATION OF A LIQUID RELIEF VALVE LOCATED ON THE PORTABLE TRIPLEX PUMPING UNIT RESULTED IN THE RELEASE AND IGNITION OF NATURAL GAS. A 5,460 GALLON TANKER, TRACTOR AND PORTABLE TRIPLEX PUMPING UNIT WERE LOCATED ADJACENT TO THE LINE 200 BLOW DOWN STACK, THE BLOW DOWN STACK AND PUMP WERE CONNECTED BY A TWO-INCH 5000 PSIG ARMORED HOSE. PRELIMINARY INVESTIGATION CONCLUDES THAT THE PORTABLE PUMPING UNIT'S LIQUID OVERPRESSURE RELIEF VALVE ACTUATED, RESULTING IN AN INITIAL RELEASEOF CLEANING SOLUTION AND SUBSEQUENT RELEASE OF NATURAL GAS. THE GAS IGNITED,RESULTING IN THE DESTRUCTION OF THE TANKER, TRACTOR AND PORTABLE PUMPING UNIT AND INJURY OF THREE EMPLOYEES. TWO INJURED EMPLOYEES SUFFERED FIRST DEGREE BURNS TO THE FACE AND THE THIRD SUFFERED FIRST AND SECOND DEGREE BURNS TO THEHANDS. ALL INJURED EMPLOYEES RETURNED TO WORK IMMEDIATELY AFTER EMERGENCY TREATMENT. THE IGNITION SOURCE IS SPECULATIVE AND REMAINS UNKNOWN. THE GAS BURNED FOR 1 HOUR AND 10 MINUTES UNTIL IT COULD BE SHUT OFF. THE SUBJECT PIPELINEWAS RETURNED TO SERVICE 45 MINUTES AFTER EXTINGUISHING THE FIRE. THERE WAS NODAMAGE TO THE UNDERGROUND STRUCTURE. SUBSEQUENT ACTION INCLUDED REPLACEMENT OF THE ABOVE GROUND CROSSOVER PIPING AS A PRECAUTIONARY MEASURE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940070 | 1994-02-22 | 19570 | TRANSCO GAS PIPELINE CORP | ROCKVILLE | MONTGOMERY | MD |  | 1610.158 | 326 + 46 | 830 | 1994-02-01 | 3 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 70000 | 52425.4049 | 114210.0028 | Null | 4 | 36 |  | 19940201 | 605 | 650 | BY TEST | 1070 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1955; NMDIA: 30; THK: 0.31; SPEC: API - 5LX; SMYS: 52000; SEAM: DSA; MANU: NATIONAL TUBE; MANYR: 1955; LOCLK: UNDER GROUND; PNAME: B.R. LANDES - STAFF COMPLIANCE ANALYST; PHONE: 7134392001; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19940131; MARK: YES; MRKTP: PERMNT MARKERS & TEM. STA; STAT: YES; CTEST: Null | PART 3- THIRD PARTY CONTRACTOR'S BACKHOE PUNCTURED THE PIPELINE WHILE PERFORMING WORK ADJACENT TO THE R.O.W.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19940082 | 1994-03-22 | 19570 | TRANSCO GAS PIPELINE CORP | VERMILION |  | LA |  | 0.551 |  | 1530 | 1994-02-20 |  | YES | VERM | 67 |  | YES | NO | LEAK | 0 | 0 | 0 | 60000 | 44936.0614 | 97894.2882 | Null | 48 | 45 |  | 19940221 | 820 | 1168 | BY TEST | 1500 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1958 | 16 | 0.31 | API-5LX | 52000 | FLASH WELD |  | A.O. SMITH | 1958 | UNDER WATER |  | B.R. LANDES - STAFF COMPLIANCE ANALYST | 7134392722 | INTERNALLY | OTHER | UNKNOWN | OTHER | UNKNOWN | COATED | YES | 1958 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940089 | 1994-03-31 | 19570 | TRANSCO GAS PIPELINE CORP | GIBSON | TERREBONNE | LA |  | 107.31 | 5666+07 | 920 | 1994-03-08 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 120000 | 89872.1228 | 195788.5763 | Null | 8 | 0 |  | 19940308 | 775 | 990 | BY CFR 192.619(A)(3) | 1090 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | LONGITUDINAL | STEEL |  | PIPELINE |  | 1959 | 20 | 0.31 | API-5LX | 52000 | ERW |  | YOUNGSTOWN | 1959 | UNDER GROUND |  | B.R. LANDES - STAFF COMPLIANCE ANALYST | 7134392001 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL |  | YES | 19940321 | WATER |  | 12 | 1090 | LACK OF FUSION IN LONGITUDINAL SEAM
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19940090 | 1994-04-06 | 19160 | TENNESSEE GAS PIPELINE CO | EAST CAMERON BLK 24 |  | LA |  | 507A-3101+2.5 |  | 730 | 1994-03-05 | 1 | YES | EC | 24 |  | Null | NO | LEAK | 0 | 0 | 0 | 65000 | 48680.7332 | 106052.1455 | Null | 1 | 30 |  | 19940305 | 950 | 1440 | BY TEST | 2165 | CORROSION | CORROSION | INTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1972; NMDIA: 16; THK: 0.38; SPEC: API 5L; SMYS: 52000; MANU: U S STEEL; MANYR: 1972; LOCLK: UNDER WATER; PNAME: LOUIS SALINAS; PHONE: 7137572408; LOC: INTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: GALVANIC; COAT: COATED; PROT: YES; CPYR: 1972; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19940102 | 1994-02-09 | 18516 | SOUTHERN NATURAL GAS CO | LOUISVILLE | WINSTON | MS | 39339 | M.P.56.79 ON 24" 2ND N.M |  | 430 | 1994-01-21 | 2 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 4 | 0 |  | 19940121 | 705 | 780 | BY TEST | 975 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | GIRTH WELD | STEEL |  | PIPELINE |  | 1952 | 24 | 0.25 | REP.SPEC. M-13 | 52000 | SUBMERGED ARC W |  | REPUBLIC/GADSDEN | 1952 | UNDER GROUND |  | NEAL A. MATTHEWS - MANAGER TECHNICAL SUPPORT | 2053253981 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION |  | YES |  | WATER |  | 0 | 975 | GIRTH WELD FAILURE: X-RAYS MADE AFTER INCIDENT REVEALED SEVERAL "BURNS THROUGH" AND THE LACK OF WELD MATERIAL PENETRATION OVER 50% OF THE JOINT CIRCUMFERENCE. THE X-RAYS SHOWED THAT THE REMAINDER OF THE GIRTH WELD WAS SATISFACTORY.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19940103 | 1994-02-07 | 11680 | LONE STAR GAS CO | DODSON | COLLINGSWORTH | TX |  | #1 | 329+36 | 930 | 1994-01-26 | 1 | NO |  |  | TX | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 10 |  | 19940126 | 175 | 310 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: THREADS ON COLLAR; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1955; NMDIA: 2; THK: 0.15; SPEC: GRADE A; SMYS: 30000; SEAM: LAP WELD; MANYR: 0; LOCLK: UNDER GROUND; PNAME: PHILLIP MURDOCK - DIRECTOR; PHONE: 2146702229; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19940105; MARK: YES; MRKTP: FLAGS; STAT: NO; CTEST: Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940104 | 1994-04-12 | 19160 | TENNESSEE GAS PIPELINE CO | EAST CAMERON BLK 24 |  | LA |  | 507A-3101+2.5 |  | 1048 | 1994-03-18 | 1 | YES | EC | 24 |  | Null | NO | LEAK | 0 | 0 | 0 | 125000 | 93616.7945 | 203946.4336 | Null | 0 | 30 |  | 19940318 | 950 | 1440 | BY TEST | 2165 | CORROSION | CORROSION | INTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1972; NMDIA: 16; THK: 0.38; SPEC: API 5L; SMYS: 52000; MANU: U S STEEL; MANYR: 1972; LOCLK: UNDER WATER; PNAME: LOUIS SALINAS; PHONE: 7137572781; LOC: INTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: GALVANIC; COAT: COATED; PROT: YES; CPYR: 1972; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | INTERNAL CORROSION LEAK DISCOVERED BY CONOCO PERSONNEL LARGER REPAIR CLAMP INSTALLED ENCOMPASS EARLIER LEAKS (2-12-94) ULTRASONICS REVEALED NO FURTHER LOCALIZED PITTING.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940106 | 1994-04-11 | 405 | ANR PIPELINE CO | BIG RAPIDS | MECOSTA | MI |  | M.P.1051.41 (MLV 68) |  | 735 | 1994-02-27 | 1 | NO |  |  | MI | Null | NO | RUPTURE | 23 | 0 | 0 | 1500000 | 1123401.5345 | 2447357.2038 | Null | 0 | 45 |  | 19940227 | 760 | 845 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: FILLET; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1962; NMDIA: 24; THK: 0.41; SPEC: API 5LXC; SMYS: 60000; SEAM: FLASH WELDED; MANU: A.O. SMITH; MANYR: 1962; LOCLK: ABOVE GROUND; PNAME: DONALD CROSS - SR. CODES ANALYST; PHONE: 3134962460; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | THE PIPE RUPTURE WAS CAUSED BY A CRACK AT THE TOE OF A WELD JOINTING A WELDOLET TO THE BODY OF THE PIPE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19940109 | 1994-04-15 | 405 | ANR PIPELINE CO | WASHTENAW |  | MI |  | M.P. 961.55 (MLV 75) | 1006 + 71.3 | 1130 | 1994-03-15 | 1 | NO |  |  | MI | Null | NO | LEAK | 0 | 0 | 0 | 57000 | 42689.2583 | 92999.5737 | Null | 2 | 10 |  | 19940315 | 760 | 858 | BY TEST | 1235 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: 1/2" NIPPLE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1956; NMDIA: 0.5; THK: 0.11; SMYS: 0; SEAM: SEAMLESS; MANYR: 1956; LOCLK: UNDER GROUND; PNAME: DONALD E. CROSS - SR. CODES ANALYST; PHONE: 3134962460; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19940111 | 1994-04-20 | 19160 | TENNESSEE GAS PIPELINE CO | EAST CAMERON BLK. 97 |  | LA |  | 507F-4401+10.0 |  | 1530 | 1994-03-30 |  | YES | EC | 97 |  | Null | NO | LEAK | 0 | 0 | 0 | 10000 | 7489.3436 | 16315.7147 | YES | 1 | 0 |  | 19940330 | 410 | 1440 | BY TEST | 2163 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1978; NMDIA: 16; THK: 0.38; SPEC: API 5L; SMYS: 52000; MANU: US STEEL; MANYR: 1978; LOCLK: UNDER WATER; PNAME: L.A. SALINAS - STAFF CIVIL ENGINEER; PHONE: 7137572781; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19940112 | 1994-04-20 | 19160 | TENNESSEE GAS PIPELINE CO | EAST CAMERON BLK 48 |  | LA |  | 507F-4601+2.31 |  | 705 | 1994-03-17 |  | YES | EC | 48 |  | Null | NO | LEAK | 0 | 0 | 0 | 20000 | 14978.6871 | 32631.4294 | Null | 1 | 0 |  | 19940317 | 560 | 1440 | BY TEST | 2165 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | FITTING | FLANGE | STEEL |  | PIPELINE |  | 1982 | 4.5 | 0.34 | API 5L | 35000 |  |  | US STEEL | 1982 | UNDER WATER |  | L.A. SALINAS - STAFF CIVIL ENGINEER | 7137572781 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | FLANGE AT SUBSEA TIE-IN | YES |  | WATER |  | 0 | 0 | LEAK DISCOVERED BY CONOCO. GAS BOIL REPORTED IN EC48. SLIGHT BROKEN SHEEN ONWATER.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19940113 | 1994-04-22 | 25165 | GULF COAST NATURAL GAS CO | INEZ | VICTORIA | TX |  | 52MP | 2769+53 | 338 | 1994-04-07 | 1 | NO |  |  |  | Null | NO | RUPTURE | 5 | 0 | 0 | 66278 | 49637.8713 | 108137.2938 | Null | 2 | 35 |  | 19940408 | 540 | 617 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1942; NMDIA: 14; THK: 0.25; SPEC: GRADE A; SMYS: 24000; SEAM: LAP WELD; MANYR: 0; LOCLK: UNDER GROUND; PNAME: STEVE MARTS - ENGINEERING TECH; PHONE: 7139513460; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | CAUSE OF RUPTURE IS CURRENTLY UNKNOWN, TEST ARE BEING CONDUCTED ON FAILEDSECTION OF 14" PIPE REMOVED AFTER INCIDENT TO DETERMINE CAUSE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940114 | 1994-04-20 | 19270 | TEXAS GAS TRANSMISSION CORP | RURAL AREA | TUNICA | MS |  | MILEPOST 178 | R11W, T4S | 1625 | 1994-03-22 | 1 | NO |  |  |  | Null | NO | RUPTURE | 3 | 0 | 0 | 125500 | 93991.2617 | 204762.2194 | Null | 2 | 7 |  | 19940322 | 490 | 500 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1946; NMDIA: 18; THK: 0.25; SPEC: GRADE B; SMYS: 35000; SEAM: SEE REMARKS; MANU: YOUNGSTOWN; MANYR: 1946; LOCLK: OTHER; LOCLO: NOT GIVEN; PNAME: SHEILA DUNBAR - SR. PIPELINE SAFETY ANALYST; PHONE: 5029268686; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | ON MARCH 22, 1994, AT APPROXIMATELY 4:25 P.M. CST, A PROPETY OWNER NOTIFIEDTEXAS GAS OF AN APPARENT RUPTURE ON HIS LAND IN A RURAL AREA NEAR THE TOWN OFTUNICA, MISSISSIPPI. DISTRICT PERSONNEL WERE DISPATCHED IMMEDIATELY TO THERUPTURE SITE AS WELL AS TO BLOCK VALVE LOCATIONS UPSTREAM AND DOWNSTREAM OFTHE RUPTURE SITE. THE LINE WAS THEN ISOLATED AND BLOWN DOWN WITH NO RESULTINGFIRE OR PERSONAL INJURY. A METALLURGICAL REVIEW IS CONTINUING AT THIS TIME;HOWEVER, THE PRELIMINARY INVESTIGATION INDICATES THE FAILURE ORIGINATED IN ADENT CONTAINING A GOUGE. GROUND COVER AT THE POINT OF FAILURE WASAPPROXIMATELY FOUR FEET (4'). ALTHOUGH THE FAILURE OCCURRED ON AGRICULTURALLAND, THERE WAS NO EVIDENCE OF RECENT TILLING OR EXCAVATING ACTIVITIES IN THEAREA OF THE FAILURE. THE AGE OF THE DENT AND GOUGE HAVE NOT BEEN DETERMINED.IT IS POSSIBLE THEY MAY HAVE OCCURRED DURING ORIGINAL CONSTRUCTION (1946).REPLACEMENT OF THE FAILED SECTION IS CURRENTLY UNDERWAY; HOWEVER, EXCESSIVERAINFALL HAS PREVENTED COMPLETION. IT IS ANTICIPATED THE 18" NO.2 LINE WILL BERETURNED TO SERVICE IN THE NEAR FUTURE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940115 | 1994-04-19 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA | OFFSHORE |  | LA |  |  |  | 750 | 1994-03-19 |  | YES | EC | 322 |  | YES | Null | LEAK | 0 | 0 | 0 | 150000 | 112340.1535 | 244735.7204 | Null | 12 | 30 |  | 19940319 | 815 | 1200 | BY TEST | 1800 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1982 | 6 | 0.34 | 5LX | 52000 |  |  | REPUBLIC | 0 | UNDER WATER |  | F. ROY FLEET - SR. ENGINEER | 7086913786 | INTERNALLY | LOCALIZED PITTING |  | OTHER | SUSPECTED BACTERIA | COATED | YES | 1982 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19940116 | 1994-04-22 | 19235 | TEXAS EASTERN GAS PIPELINE CO | EDISON TOWNSHIP | MIDDLESEX | NJ | 08817 | 29.96 | 1582+07 | 2357 | 1994-03-23 | 3 | NO |  |  | NJ | Null | NO | RUPTURE | 79 | 0 | 2 | 25000000 | 18723358.9088 | 40789286.7292 | Null | 2 | 28 |  | 19940324 | 970 | 975 | BY TEST | 2199 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1961; NMDIA: 36; THK: 0.68; SPEC: API 5LX; SMYS: 52000; SEAM: DSAW; MANU: BETHLEHEM; MANYR: 1961; LOCLK: UNDER GROUND; PNAME: DWAYNE TESCHENDORF - SR. ENGINEER; PHONE: 7136275573; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: SEE REMARKS; STAT: NO; CTEST: Null | THE CAUSE OF THE INCIDENT IS UNDER INVESTIGATION BY THE NTSB.PIPELINE MARKERIS PRESENT ON ROAD AND NEAR PLANT GATE ENTRANCE TO THE ASPHALT PLANT WHERE THEINCIDENT OCCURRED. CASING VENT MARKERS ARE ALSO PRESENT NEAR WHERE THEPIPELINE EXITS THE ASPHALT PLANT.THE COMPANY IS UNABLE TO ESTIMATE AT THISTIME THE EXTENT OF THIRD PARTY PROPERTY DAMAGES ASSOCIATED WITH THIS INCIDENT.SUPPLEMENTAL REPORT 5/2/1995 INDICATES THAT NTSB DETERMINED THAT THE PROBABLECAUSE OF THE INCIDENT WAS MECHANICAL DAMAGE TO THE EXTERIOR SURFACE OF THEPIPELINE. AN ATTACHMENT INDICATES THAT THIRD PARTY PROPERTY DAMAGES ASSOCIATEDWITH THIS INCIDENT ARE INCOMPLETE AND UNSUBSTANTIATED. THE NTSB ESTIMATEDPROPERTY DAMAGES OF $25 MILLION. THERE IS A LETTER ATTACHED TO REPORT THATEXPLAINS IN DETAIL THE DIFFICULTIES IN ESTIMATING THE THIRD PARTY PROPERTYDAMAGE. SUPPLEMENTAL REPORT 5/2/1995 INDICATES A CHANGE IN PROPERTY DAMAGEFROM 1,750,000 TO 25,000,000. THIRD PARTY PROPERTY DAMAGES ASSOCIATED WITHTHIS INCIDENT ARE INCOMPLETE AND UNSUBSTANTIATED. THE NTSB ESTIMATED PROPERTYDAMAGES OF 25 MILLION. NTSB DETERMINED THAT THE PROBABLE CAUSE OF THEINCIDENT WAS MECHANICAL DAMAGE TO THE EXTERIOR SURFACE OF THE PIPELINE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940118 | 1994-04-22 | 12462 | MID - LOUISIANA GAS CO | MISS. RIVER NEAR VIDALIA | CONCORDIA | LA |  | 90.9 T-1LOOP | 4799+50+ | 855 | 1994-04-17 | 1 | NO |  |  | LA | Null | NO | LEAK | 0 | 0 | 0 | 165000 | 123574.1688 | 269209.2924 | YES | 2 | 15 |  | 19940417 | 159 | 250 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: HEAT AFFECTED ZONE ADJACE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 0; NMDIA: 10; THK: 0.5; SPEC: API5L; SMYS: 35000; SEAM: SMLA; MANU: J&L; MANYR: 1979; LOCLK: UNDER WATER; PNAME: R.L. SIMPSON - SUPER. PIPELINE OPER; PHONE: 3186654426; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: BOTTOM SCOUR MISSISSIPPI; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | STRONG RIVER CURRENT CAUSED SCOURING TO OCCUR WHICH EXPOSED THE PIPE NEAR THEEDGE OF A SAND BAR CAUSING A SECTION TO BECOME SUSPENDED ABOVE THE CHANNELBOTTOM. THE FORCE APPLIED BY THE CURRENT CAUSED THE PIPE TO SWING OR VIBRATEAND EVENTUALLY BREAK AT GIRTH WELD.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940120 | 1994-05-11 | 19570 | TRANSCO GAS PIPELINE CORP | ST. FRANCISVILLE | WEST FELICIANA | LA |  | 583.34 | 7796+28 | 2044 | 1994-04-17 | 1 | NO |  |  |  | Null | NO | RUPTURE | 0 | 0 | 0 | 5000000 | 3744671.7818 | 8157857.3458 | Null | 0 | 1 |  | 19940418 | 560 | 780 | NO DATA | 882 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: UNABLE TO DETERMINE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1961; NMDIA: 30; THK: 0.5; SPEC: API-5LX; SMYS: 52000; SEAM: DSA; MANU: NATIONAL TUBE; MANYR: 1961; LOCLK: UNDER WATER; PNAME: B.R. LANDES; PHONE: 7134392322; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | RUPTURED OCCURRED IN A 30" MISSISSIPPI RIVER CROSSING WHILE THE RIVER WAS ABOVE FLOOD STAGE. BECAUSE OF THE RIVER CURRENTS AND THE LOCATION OF RUPTURE, THE PRIMARY CAUSE OF THE INCIDENT CANNOT BE DETERMINED. TRANSCO WILL NOT ATTEMPT ANY REPAIR OF THE 30" CROSSING. THE 30" CROSSING WILL BE ABANDONED IN PLACE AND REPLACED WITH A NEW DIRECTIONAL DRILLED CROSSING, THE COST OF WHICH IS INCLUDED IN THE ESTIMATED COST OF DAMAGE/LOSS/REPAIR.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940121 | 1994-05-11 | 15014 | PACIFIC GAS TRANSMISSION CO | KLAMATH FALLS |  | OR | 97603 | 567.7 | 2366.20 | 1715 | 1994-04-26 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 150000 | 112340.1535 | 244735.7204 | Null | 0 | 0 |  | 19940426 | 620 | 911 | BY TEST | 1140 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | GIRTH | STEEL |  | PIPELINE |  | 1992 | 42 | 0.46 | 5LX65 & 5LX70 | 70000 | DOUBLE SUBMERGE | DNA | OREGON STEEL .409=1991: .456=1992 | 1991 | UNDER GROUND |  | G.F. MCKINNEY | 5095362751 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION |  | YES | 19921021 | WATER |  | 8 | 1140 | A SMALL CRACK DEVELOPED IN A FIELD WELD BETWEEN TWO DIFFERENT SPECIFICATIONSOF PIPE INSTALLED IN 1992 WHICH RESULTED IN A MINOR GAS LEAK. INCIDENT IS REPORTABLE ONLY BECAUSE COST OF REPAIRS, INCLUDING COST OF GAS BLOWN TO ATMOSPHERE, EXCEEDED $50,000. CAUSE OF FAILURE IS UNDER INVESTIGATION.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940129 | 1994-04-13 | 19730 | TRUNKLINE GAS CO | KAPLAN | STINGRAY | LA |  |  | X=164312.5 Y-1593330.82 | 900 | 1994-03-17 |  | YES | VE | 340 |  | Null | NO | LEAK | 0 | 0 | 0 | 95000 | 71148.7639 | 154999.2896 | Null | 10 | 30 |  | 19940318 | 900 | 1200 | BY TEST | 2407 | CORROSION | CORROSION | INTERNAL | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1978 | 12 | 0.38 | API 5LX | 52000 | SMLS |  | U.S.S | 1978 | UNDER WATER |  | ROY VALLERY - CORROSION ENGINEER | 7136275400 | INTERNALLY | LOCALIZED PITTING |  | OTHER | UNKNOWN | COATED | YES | 1978 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940131 | 1994-04-26 | 19160 | TENNESSEE GAS PIPELINE CO | ALLEN PARISH |  | LA |  | 823-1+11.01 |  | 1300 | 1994-03-23 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 75000 | 56170.0767 | 122367.8602 | Null | 2 | 0 |  | 19940323 | 925 | 936 | BY TEST | 1329 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | FITTING | DRIP | STEEL |  | PIPELINE |  | 1975 | 26 | 0.5 |  | 60000 |  |  |  | 1975 | OTHER | NOT GIVEN | LOUIS A SALINAS - STAFF CIVIL ENGINEER | 7137572781 | INTERNALLY | LOCALIZED PITTING |  | OTHER | NOT GIVEN | COATED | YES | 1975 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | 1/4" PIN HOLE DISCOVERED AT BOTTOM OF 26" O.D. PIPELINE DRIP.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940140 | 1994-06-06 | 5304 | FLORIDA GAS TRANSMISSION CO | DICKINSON | GALVESTON | TX |  | 309.0 |  | 2210 | 1994-05-02 | 1 | NO |  |  |  | Null | NO | RUPTURE | 26 | 0 | 0 | 520000 | 389445.8653 | 848417.164 | Null | 2 | 50 |  | 19940503 | 890 | 975 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1958; NMDIA: 24; THK: 0.5; SPEC: API-5LX; SMYS: 52000; SEAM: ELEC.FLASH WELD; MANU: A.O. SMITH; MANYR: 0; LOCLK: UNDER WATER; PNAME: MORLIN H. MOSEMAN; PHONE: 7136467344; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; MRKTP: 0; STAT: Null; CTEST: Null | PIPELINE DAMAGED BY BOAT TRAFFIC IN A SHALLOW, INLAND NAVIGABLE WATERWAY. THE PIPELINE RUPTURE RESULTED FROM DAMAGE CAUSED BY BOAT TRAFFIC IN A SHALLOW,INLAND WATERWAY.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940142 | 1994-06-02 | 19570 | TRANSCO GAS PIPELINE CORP | MERMENTAU | ACADIA | LA |  | 8.47 | 447+40 | 630 | 1994-05-06 | 1 | NO |  |  |  | Null | NO | RUPTURE | 7 | 0 | 0 | 888205 | 665207.24 | 1449169.9368 | Null | 2 | 0 |  | 19940506 | 715 | 910 | NO DATA | 1075 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1958; NMDIA: 12; THK: 0.28; SPEC: API-5LX; SMYS: 42000; SEAM: SEAMLESS; MANU: YOUNGSTOWN STEEL; MANYR: 1958; LOCLK: UNDER WATER; PNAME: B.R. LANDES; PHONE: 7134392722; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: SEE REMARKS; STAT: Null; CTEST: Null | OIL TRANSPORT BARGE BEING PUSHED BY TUG BOAT RAN INTO THE 12" PIPELINE ON THE EAST SIDE OF THE BAYOU. (BAYOU DE CANNES). PART B- PERMANENT PIPELINE CROSSING MARKERS.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19940145 | 1994-06-21 | 19160 | TENNESSEE GAS PIPELINE CO | EAST CAMERON BLK. 24 |  | LA |  | 507A-3101+2.5 |  | 800 | 1994-05-27 |  | YES | EC | 24 |  | Null | NO | LEAK | 0 | 0 | 0 | 52000 | 38944.5865 | 84841.7164 | Null | 1 | 25 |  | 19940527 | 863 | 1440 | BY TEST | 2165 | CORROSION | CORROSION | INTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 0; NMDIA: 16; THK: 0.38; SPEC: API 5L; SMYS: 52000; MANU: U.S. STEEL; MANYR: 1972; LOCLK: UNDER WATER; PNAME: L.A. SALINAS; PHONE: 7137572408; LOC: INTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: GALVANIC; COAT: COATED; PROT: Null; CPYR: 1972; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | LEAK DISCOVERED BY HELICOPTER CREW (BUBBLES AT SURFACE).
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940146 | 1994-06-21 | 2620 | COLUMBIA GULF TRANSMISSION CO | EUGENE ISLAND |  | LA |  | X-1885246.60 Y=105495.21 |  | 1130 | 1994-05-25 |  | YES | EI | 287-D |  | YES | NO | LEAK | 0 | 0 | 0 | 150000 | 112340.1535 | 244735.7204 | Null | 0 | 0 |  | 19940525 | 1108 | 1250 | BY TEST | 2160 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1971 | 12 | 0.41 | APISLX | 52000 | SEAMLESS |  |  | 0 | UNDER WATER |  | S.J. CHOBY | 3043572349 | INTERNALLY | OTHER | UNKNOWN | OTHER | UNKNOWN | COATED | YES | 1971 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | TWO SMALL INTERNAL CORROSION PIN HOLE LEAKS (18'APART) WERE REPAIRED WITH DASPIT CLAMPS. PART 1 B). X=1885229.89 Y=105490.26
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940151 | 1994-05-16 | 13750 | NORTHERN NATURAL GAS CO (ENRON) |  | GUTHRIE | IA |  | MP 52.94 |  | 340 | 1994-04-18 | 1 | NO |  |  |  | Null | NO | RUPTURE | 30 | 0 | 0 | 100000 | 74893.4356 | 163157.1469 | Null | 2 | 30 |  | 19940418 | 500 | 500 | NO DATA | 0 | CORROSION | CORROSION | EXTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1962; NMDIA: 24; THK: 0.25; SMYS: 42000; MANYR: 0; LOCLK: UNDER GROUND; PNAME: JOHN W. CASKEY; PHONE: 7136467343; LOC: EXTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: GALVANIC; COAT: COATED; PROT: YES; CPYR: 0; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | SHORT COATED REPLACEMENT SECTION IN A BARE, DRESSER COUPLED LINE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940153 | 1994-05-19 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA | FORD | FORD | KS | 67842 | 140, AM#2 |  | 1400 | 1994-04-14 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 138600 | 103802.3018 | 226135.8056 | Null | 1 | 55 |  | 19940414 | 608 | 712 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1941; NMDIA: 18; THK: 0.38; SPEC: GRADE A; SMYS: 30000; SEAM: SEAMLESS; MANU: NATIONAL TUBE; MANYR: 1941; LOCLK: UNDER PAVEMENT; PNAME: F. ROY FLEET; PHONE: 7086913786; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | UNDER INVESTIGATION. PIPE SECTION HAS BEEN ISOLATED BUT NOT YET REMOVED FROMITS CASING.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19940154 | 1994-05-19 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA |  |  | LA |  |  |  | 1220 | 1994-04-12 |  | YES | WEST CAMERON | 165 | LA | YES | NO | LEAK | 0 | 0 | 0 | 400000 | 299573.7425 | 652628.5877 | Null | 5 | 0 |  | 19940412 | 890 | 1200 | BY TEST | 1950 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 0 | 16 | 0.38 | 5LX | 52000 | SEAMLESS |  | UNKNOWN | 1967 | UNDER WATER |  | F. ROY FLEET | 7086913786 | INTERNALLY | OTHER | NOT APPLICABLE | OTHER | UNKNOWN | COATED | YES | 1968 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | PIPE SEGMENT ABANDONED. NO FLOW IN THE AFFECTED SEGMENT.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940155 | 1994-05-17 | 19160 | TENNESSEE GAS PIPELINE CO | SOUTH PASS BLOCK 54 |  | LA |  | 527A-1301+1.3 |  | 1505 | 1994-04-20 |  | YES | SP | 54 |  | YES | NO | LEAK | 0 | 0 | 0 | 400000 | 299573.7425 | 652628.5877 | Null | 0 | 30 |  | 19940420 | 974 | 1440 | BY TEST | 2160 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 0; NMDIA: 12.75; THK: 0.5; SPEC: A.P.I. 5L; SMYS: 42000; MANU: U.S. STEEL; MANYR: 1983; LOCLK: UNDER WATER; PNAME: L.A. SALINAS; PHONE: 7137572781; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; MRKTP: 0N; STAT: Null; CTEST: Null | WORK BOAT DROPPED ANCHOR. LEAK DISCOVERED BY TEXACO PERSONNEL. WORK BOAT ANCHOR SNAGGED T.G.P. 12" PIPELINE IN SOUTH PASS BLK 54.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19940158 | 1994-07-22 | 2731 | CHEVRON PIPELINE CO | LA OUTER CONT. SHELF |  | LA |  |  |  | 1200 | 1994-06-19 |  | YES | WD | 79 |  | YES | NO | LEAK | 0 | 0 | 0 | 69000 | 51676.4706 | 112578.4314 | Null | 24 | 0 |  | 19940619 | 580 | 780 | BY TEST | 2128 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1970 | 22 | 0.5 | API 5LX | 52000 | SEAMLESS | ANSI 600 | US STEEL | 1969 | UNDER GROUND | UNDER WATER | ALBERT S. BANTA | 5045927516 | INTERNALLY | GENERAL CORROSION |  | OTHER | BACTERIAL | COATED | YES | 1970 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940166 | 1994-07-26 | 19160 | TENNESSEE GAS PIPELINE CO | PLAQUE MINE PARISH |  | LA |  | 526A-101+3.59 |  | 1600 | 1994-06-23 | 1 | NO |  |  |  | Null | NO | RUPTURE | 0 | 0 | 0 | 650000 | 486807.3316 | 1060521.455 | Null | 0 | 55 |  | 19940623 | 900 | 1133 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: NOT GIVEN; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1956; NMDIA: 20; THK: 0.38; SPEC: API 5L; SMYS: 52000; MANYR: 0; LOCLK: UNDER WATER; PNAME: LOUIS SALINAS; PHONE: 7137572781; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | PIPELINE RUPTURED ON 20 IN. 526A-100 LINE IN MOUTH OF GRAND BAYOU, LOUISIANA.APPROXIMATELY 200 FEET OF PIPELINE HAD BECOME EXPOSED DUE TO THE WASHOUT & ERROSION.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19940167 | 1994-07-18 | 19590 | TRANSOK INC | WETUMKA | HUGHES | OK |  |  | W 141 + 21 | 1755 | 1994-06-22 | 1 | NO |  |  |  | Null | NO | RUPTURE | 9 | 0 | 0 | 63500 | 47557.3316 | 103604.7883 | Null | 0 | 38 |  | 19940623 | 686 | 843 | BY TEST | 1206 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1981 | 12 | 0.22 | APL 5L 30TH ADDT | 1443 | HF ERW |  | US STEEL | 1980 | UNDER GROUND |  | DAVID MATHIS | 9185912326 | INTERNALLY | LOCALIZED PITTING | GENERAL CORROSION | OTHER | CHEMICAL ACTION | COATED | YES | 1981 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | ON JUNE 22, 1994 AT 17:55 TRANSOK'S GREASY CREEK PROCESSING PLANT RECEIVED SEVERAL CALLS FROM PRIVATE CITIZENS ABOUT A LOUD NOISE IN THE STORAGE FIELD. AT THE SAME TIME TELEMETRY WAS SHOWING A RAPID PRESSURE DROP. MILTON JOHNSON (OPERATOR) NOTIFIED RICK RAMSEY (FIELD OPERATOR) AND GAS CONTROL CENTER OF THELEAK IN THE SOUTH END OF THE STORAGE FIELD. RICK RAMSEY PROCEEDED TO THE LEAK AREA FOUND THE LEAK TO BE ON THE 12" LATERAL AND ISOLATED THE WELLS ATTACHED TO THIS LINE AND MAINLINE VALVE. SITUATION WAS UNDER CONTROL AT 18:33. THE LEAK OCCURRED IN HUGHES COUNTY SW 1/4 OF SE 1/4 SECTION 36 TOWNSHIP 8N RANGE 11E. GAS LOSS WAS FIGURED AT 20,271MCF. THE AREA OF THE LEAK IS IN A CLASS 1 LOCATION WITH THE CLOSEST OCCUPIED RESIDENCE APPROX. 400 FEET AWAY.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940168 | 1994-07-18 | 19570 | TRANSCO GAS PIPELINE CORP | CULPEPER | CULPEPER | VA |  | 1549.153 | 8569+22 | 1215 | 1994-06-30 | 1 | NO |  |  |  | Null | NO | RUPTURE | 45 | 0 | 0 | 250000 | 187233.5891 | 407892.8673 | Null | 1 | 30 | 246898 | 19940630 | 790 | 800 |  | 1115 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1950 | 30 | 0.32 | API-5LX | 52000 | DSA |  | KAISER | 1950 | UNDER GROUND |  | B.R. LANDES | 7134392722 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | COATED | YES | 1952 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19940176 | 1994-08-08 | 2731 | CHEVRON PIPELINE CO | LA OUTER CONTINENTAL SHEL |  | LA |  |  |  | 1250 | 1994-07-21 |  | YES | W/D | 79 | LA | YES | NO | LEAK | 0 | 0 | 0 | 75000 | 56170.0767 | 122367.8602 | Null | 24 | 0 |  | 19940723 | 580 | 780 | BY TEST | 2128 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1970 | 22 | 0.5 | API 5LX | 52000 | SEAMLESS | ANSI 600 | U.S. STEEL | 1960 | UNDER GROUND | UNDER WATER | A.S. BANTA | 5045927516 | INTERNALLY | GENERAL CORROSION |  | OTHER | BACTERIAL | COATED | YES | 1970 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19940180 | 1994-09-13 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA |  |  | LA |  |  |  | 1440 | 1994-08-10 |  | YES | WC | 225 |  | Null | NO | LEAK | 0 | 0 | 0 | 226012 | 169268.1517 | 368754.7309 | Null | 2 | 20 |  | 19940810 | 956 | 1300 | BY TEST | 1950 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1968 | 12 | 0.31 | 5LX | 52000 | ERW |  |  | 0 | UNDER WATER |  | F. ROY FLEET | 7086913786 | INTERNALLY | LOCALIZED PITTING |  | OTHER | POSSIBLE BACTERIA | COATED | YES | 1968 | NO DATA |  | Null |  | Null |  | Null | MATERIAL |  | Null |  | NO DATA |  | 0 | 0 | PENDING INVESTIGATION. THE AFFECTED PIPE SECTION IS ISOLATED. REPAIRS ANDFURTHER INVESTIGATION ARE NOT COMPLETE. SUPPLEMENTAL REPORT 3/21/95 INDICATESTHAT XRAY CONFIRMED INTERNAL CORROSION. LOCALIZED INTERNAL PITTING SHOWN BYXRAY. INSTALLED LEAK CLAMP.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940182 | 1994-09-13 | 19570 | TRANSCO GAS PIPELINE CORP | THERIOT | TERREBONNE | LA |  | 123.31 | 655+29 | 1130 | 1994-08-10 | 1 | NO |  |  |  | Null | NO | RUPTURE | 115 | 0 | 0 | 500000 | 374467.1782 | 815785.7346 | Null | 1 | 10 |  | 19940810 | 840 | 990 | NO DATA | 1090 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1959 | 20 | 0.31 | API-5L | 52000 | ERW |  | YOUNGSTOWN | 1959 | UNDER WATER |  | B.R. LANDES | 7134392001 | INTERNALLY | LOCALIZED PITTING |  | OTHER | UNKNOWN | COATED | YES | 1959 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | FAILURE INITIATED IN THE LONG SEAM AS A RESULT OF INTERNAL PITTING CORROSIONON BOTH SIDES AND IN THE LONG SEAM.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940183 | 1994-09-06 | 2620 | COLUMBIA GULF TRANSMISSION CO | GULF OF MEXICO |  | LA |  |  | X=1399,701.6 Y=46897.60 | 1500 | 1994-08-21 |  | YES | WC | 479 |  | YES | NO | OTHER | 0 | 0 | 0 | 100000 | 74893.4356 | 163157.1469 | Null | 0 | 0 |  | 19940821 | 1050 | 1440 | BY TEST | 2160 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1978; NMDIA: 6; THK: 0.43; SPEC: GR. B; SMYS: 35000; SEAM: SEAMLESS; MANU: UNITED STATES STEEL; MANYR: 1978; LOCLK: UNDER WATER; PNAME: S.J. CHOBY; PHONE: 3043572349; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; MRKTP: 0N; STAT: Null; CTEST: Null | SPECULATION INDICATES THAT A 20' SEGMENT OF 6" PIPE AND VALVE HAD BEEN SEVERED BY A SURFACE VESSEL FISHING NET OR ANCHOR IN ROUGH SEAS.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940184 | 1994-09-09 | 2620 | COLUMBIA GULF TRANSMISSION CO | GULF OF MEXICO |  | LA |  | 1.25 MILES NW OF EI 2861 | LAT.20 22' LONG .91 41' | 1400 | 1994-08-16 |  | YES | EI | 287-D |  | YES | NO | LEAK | 0 | 0 | 0 | 150000 | 112340.1535 | 244735.7204 | Null | 0 | 0 |  | 19940816 | 1108 | 1250 | BY TEST | 2160 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1971 | 12 | 0.41 | API5LX | 52000 | SEAMLESS |  | UNKNOWN | 0 | UNDER WATER |  | S.J. CHOBY | 3043572349 | INTERNALLY | OTHER | UNKNOWN | OTHER | UNKNOWN | COATED | YES | 1971 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | ONE SMALL INTERNAL CORROSION PIN HOLE LEAK WAS REPAIRED WITH A LEAK CLAMP. AT 7:40 AM, AUGUST 14, 1994, A BUBBLE LEAK WAS REPORTED BY A HELICOPTER TRANSPORT SERVICE DISPATCHER. WITHIN HOURS, SEVERAL PIPELINES WERE SHUT-IN. FURTHERINVESTIGATION AND EVALUATION RESULTED IN A DETERMINATION THAT THE LEAK WAS ON A COLUUMBIA GULF PIPELINE. AN ESTIMATED REPAIR COST EXCEEDING $50,000 WAS THE INCIDENT REPORT TRIGGER MECHANISM RESULTING IN THE AUGUST 16, 1994 NATIONAL RESPONSE CENTER TELEPHONE REPORT. ONE SMALL INTERNAL CORROSION PIN HOLE LEAK WAS REPAIRED WITH A PIPELINE CLAMP ON AUGUST 27, 1994. MINERAL MANAGEMENT SERVICE WAS DULY NOTIFIED AND THERE WERE NO ENVIRONMENTAL UPSETS. THE PIPELINEIS BACK IN SERVICE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19940185 | 1994-09-06 | 19730 | TRUNKLINE GAS CO |  |  | TX |  | VALVE SECTION 318 | LONG-9059.52; LAT-2905.37 | 940 | 1994-08-05 |  | YES | SS | 39 |  | Null | NO | LEAK | 0 | 0 | 0 | 59000 | 44187.127 | 96262.7167 | Null | 9 | 40 |  | 19940808 | 1000 | 1200 | BY TEST | 2160 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: FLANGE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1983; NMDIA: 6; THK: 0; SPEC: ANSI CLASS 900; SMYS: 0; VALVE: BALL VALVE; MANU: CAMERON; MANYR: 0; LOCLK: UNDER WATER; PNAME: DAVID W. SHELLHOUSE; PHONE: 7136276015; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | LEAKING FLANGE DISCOVERED ON 6" BALL VALVE ON 12" FUTURES TAP OF TGC 300-1 (30") LINE. FUTURES WAS BLOWN DOWN, 6" VALVE REMOVED AND NEW 6" BLIND FLANGE W/BLEEDER VALVE INSTALLED.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19940186 | 1994-09-06 | 19610 | TRANSWESTERN PIPELINE CO | BELEN | VALENCIA | NM |  | M.P.32.4/MLV 7011 |  | 1450 | 1994-08-20 | 2 | NO |  |  |  | Null | NO | RUPTURE | 2547 | 0 | 1 | 2200000 | 1647655.584 | 3589457.2322 | Null | 1 | 30 |  | 19940820 | 967 | 1008 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1960; NMDIA: 30; THK: 0.5; SPEC: API 5LX; SMYS: 52000; SEAM: SAW; MANU: REPUBLIC STEEL; MANYR: 1959; LOCLK: UNDER GROUND; PNAME: ANTHONY R. ROCK; PHONE: 7136467346; PROT: Null; CAULK: EARTH MOVEMENT: SUBSIDENCE; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | DIFFERENTIAL SETTLING OF PIPELINE AND ABOVE GROUND APPURTENCES CAUSED UNDUE STRESS OF BELOW GROUND BRANCH CONNECTION LEADING TO FAILURE OF THE WELDED BRAN
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940189 | 1994-07-05 | 13750 | NORTHERN NATURAL GAS CO (ENRON) | WEST OF CLARION | WRIGHT | IA |  | 51.832 |  | 320 | 1994-05-30 | 1 | NO |  |  |  | Null | NO | RUPTURE | 5 | 0 | 0 | 70000 | 52425.4049 | 114210.0028 | Null | 3 | 0 |  | 19940530 | 485 | 500 | NO DATA | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1931 | 20 | 0.28 | API 5L | 30000 | ERW |  | A.O. SMITH | 1931 | UNDER GROUND |  | JOHN W. CASKEY | 7136467341 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | HOT SPOT PROTECTED WITH ANODES
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19940192 | 1994-08-29 | 898 | SAGINAW PIPELINE COMPANY, L.C. |  | CLAY | TX |  | 32 M.P |  | 1400 | 1994-08-01 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 3 | 30 |  |  | 400 | 750 | BY TEST | 1000 | CORROSION | CORROSION | EXTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1920; NMDIA: 6; THK: 0.28; SMYS: 0; MANYR: 0; LOCLK: UNDER GROUND; PNAME: R.M. KENNEMER; PHONE: 8173329209; LOC: EXTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: OTHER; CAUCO: NOT GIVEN; COAT: BARE; PROT: NO; CPYR: 0; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | SUSPECTED LEAK REPORTED BY AERIAL FLYOVER
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19940193 | 1994-08-29 | 898 | SAGINAW PIPELINE COMPANY, L.C. |  | CLAY | TX |  | 19 M.P |  | 800 | 1994-08-12 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 30 |  |  | 390 | 750 | BY TEST | 1000 | CORROSION | CORROSION | EXTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 0; NMDIA: 6; THK: 0.28; SMYS: 0; MANYR: 0; LOCLK: UNDER GROUND; PNAME: R.M. KENNEMER; PHONE: 8173329209; LOC: EXTERNALLY; ADESC: OTHER; DESCO: NOT GIVEN; CAUCR: OTHER; CAUCO: NOT GIVEN; COAT: BARE; PROT: YES; CPYR: 1994; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | AERIAL FLYOVER REPORTED SUSPECTED LEAK.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19940194 | 1994-10-26 | 6141 | GAS CO OF NEW MEXICO | ALBUQUERQUE | BERNALILLO | NM | 87158 |  | 11+50 | 900 | 1994-09-25 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 1 | 647 | 484.5605 | 1055.6267 | Null | 6 | 0 |  | 19940926 | 2 | 500 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | FITTING | PIN-OFF | STEEL |  | PIPELINE |  | 0 | 6 | 0.25 | API 5LX | 42000 | EW |  | UNKNOWN | 1960 | OTHER | BELL HOLE | JUAN JOJOLA | 5058484578 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | DEFECTIVE PIN-OFF TEE | Null |  | NO DATA |  | 0 | 0 | CONSTRUCTION EMPLOYEES MAKING TAP ON PIPELINE, VAPORS FROM THE PIPELINE FILLELINE WAS BEING RETIRED. ON 09/25/94 FOUTZ 7 BURSUM (CONTRACTOR WORKING FOR GCD THE BELLHOLE. WHEN WELDERS STARTED WELDING, THE VAPORS IGNITED IN FLASH FIRNM) WAS RETIRING A 16" TRANSMISSION MAIN AT COORS BY-PASS & 7 BAR LOOP ROAD.AT APPROXIMATELY 0900 HRS. MR. LEROY MARTINEZ OF FOUTZ & BURSUM WAS HOLDING A STEEL PLATE, TO BE WELDED, OVER THE END OF THE 16" LINE. LEAKING GAS IGNITED CAUSING A FLASH FIRE THAT BURNED MR. MARTINEZ. HE WAS HOSPITALIZED FOR 2ND.DEGREE BURNS HE SUSTAINED. THE LEAKING GAS WAS TRACED BACK TO A 2" PIPE THATWAS CONNECTED TO THE 16" MAIN FROM A 10" MAIN. THE GAS CAME FROM A 2" PIN-OFF TEE THAT WAS IN THE CLOSED POSITION BUT DID NOT GIVE A POSITIVE SHUT-OFF. THIS 2" LINE HAS SINCE BEEN RETIRED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19940199 | 1994-09-29 | 20245 | MID CON TEXAS PIPELINE CORP |  | CHAMBERS | TX |  | INDEX 166,MP 15.83 | TX BLOCK 132 | 1635 | 1994-08-29 |  | YES | GALVESTON BAY |  |  | Null | NO | LEAK | 0 | 0 | 0 | 66500 | 49804.1347 | 108499.5027 | Null | 3 | 25 |  | 19940829 | 670 | 1065 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1959; NMDIA: 10; THK: 0.25; SPEC: 5LX; SMYS: 42000; SEAM: SEAMLESS; MANU: NATIONAL; MANYR: 1959; LOCLK: UNDER WATER; PNAME: F.ROY FLEET; PHONE: 7086913786; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; MRKTP: IN GALVESTON BAY; STAT: NO; CTEST: Null | A BARGE SET A STABILIZING LEG ON THE PIPELINE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940200 | 1994-10-06 | 13061 | NATIONAL FUEL GAS DISTRIBUTION CORP | 450 EAST OF NYS RTE.16 | ERIE | NY |  | 1.5 | 79+43 | 1636 | 1994-09-07 | 2 | NO |  |  | NY | Null | NO | RUPTURE | 0 | 0 | 0 | 111135 | 83232.8197 | 181324.6952 | YES | 0 | 50 |  | 19940907 | 897 | 915 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1953 | 16 | 0.38 |  | 35000 | SEAMLESS |  | UNKNOWN | 1953 | UNDER GROUND |  | DAVID M. BIMBER | 7166493121 | EXTERNALLY | GENERAL CORROSION |  | OTHER | INADEQUATE CONTACT W/ SOI | BARE | YES | 1972 | NO DATA |  | Null |  | Null |  | Null | MATERIAL |  | YES | 19531112 | WATER | 0 | 14 | 0 | ON 09/07/1994, AT 4:36 P.M., LINE C-46 RUPTURED AND IGNITED. LINE IS STORAGELINE FOR COLDEN STORAGE. STORAGE WAS ON INJECTION AT 897 PSIG. NATIONAL FUELNOTIFIED AT 4:40 P.M. RESPONDED, SHUTTING VALVE TZ56,CLOSING LINE DOWN. FIREOUT AT 5:18 P.M. ALL SECTIONS OF LINE INVOLVED ARE TO BE SHIPPED TO BATTELLELABS FOR ANALYSIS. DAMAGE TO 3.5 ACRES OF FOREST. NO INJURIES TO PERSONS.LINE RUPTURED, IGNITED. SUPPLEMENTAL REPORT 1/10/95 INDICATES CHANGES TOPROPERTY DAMAGE: TOTAL OF $111,135.00, WITH GAS LOST AMOUNT = $44,460, PROPERTYDAMAGE = $10,066 AND REPLACEMENT COST $56,429. ALSO NARRATIVE CHANGES INCLUDE:LINE INSTALLED 1953. BARE, 16", GR. B SEAMLESS .375 WALL PIPE. LAID ON SHALEAT THIS SITE. CORROSION HAD REDUCED THE WALL AT THE RUPTURE SITE AND FAILUREAND FIRE OCCURRED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19940201 | 1994-10-04 | 15105 | PANHANDLE EASTERN PIPELINE CO | RURAL, 2MILES SW WAVERLY | MORGAN | IL | 62692 |  | 6 +83 | 440 | 1994-09-03 | 1 | NO |  |  | IL | Null | Null | OTHER | 0 | 0 | 0 | 47300 | 35424.5951 | 77173.3305 | YES | 1 | 20 |  | 19940903 | 830 | 852 | BY TEST | 1190 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | WELD | LONGITUDINAL | STEEL |  | PIPELINE |  | 1965 | 16 | 0.25 | API - 5LX | 52000 | FRW |  | BETHLEHEM | 1965 | UNDER GROUND |  | JOHN C. KELLY | 7136275600 | INTERNALLY | LOCALIZED PITTING |  | OTHER | INVESTIGATION UNDERWAY | COATED | YES | 1965 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | FAILURE OCCURRED DUE TO LOCALIZED INTERNAL CORROSION. AN INVESTIGATION IS CURRENTLY UNDERWAY.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19940202 | 1994-10-03 | 11680 | LONE STAR GAS CO | THROCKMORTON | THROCKMORTON | TX |  | MM12 | 612+04 | 1655 | 1994-08-26 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 10 |  | 19940826 | 455 | 500 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1967; NMDIA: 3; THK: 156; SPEC: GRADE A; SMYS: 30000; SEAM: LAP WELD; MANU: UNK; MANYR: 0; LOCLK: OTHER; LOCLO: ON TOP OF GROUND; PNAME: MARVIN IMBODEN; PHONE: 2146702779; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: YES; NOTDT: 19940808; MARK: YES; MRKTP: WOOD STAKES; STAT: NO; CTEST: Null | LONE STAR CREW WAS BACKFILLING A PIPELINE. THE TRACK OF A CATAPILLAR HIT THIS PIPELINE AND PUNCHED A HOLE IN IT. GAS IGNITED BURNING THE OPERATOR AND CATAPILLAR.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940203 | 1994-09-30 | 19160 | TENNESSEE GAS PIPELINE CO | EAST CAMERON BLK. 24 |  | LA |  | 507A-3101+2.5 |  | 821 | 1994-09-04 |  | YES | EC | 24 |  | Null | NO | LEAK | 0 | 0 | 0 | 200000 | 149786.8713 | 326314.2938 | Null | 1 | 0 |  | 19940904 | 910 | 1440 | BY TEST | 2165 | CORROSION | CORROSION | INTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1972; NMDIA: 16; THK: 0.38; SPEC: API 5L; SMYS: 52000; MANU: U.S. STEEL; MANYR: 1972; LOCLK: UNDER WATER; PNAME: L.A. SALINAS; PHONE: 7137572781; LOC: INTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: GALVANIC; COAT: COATED; PROT: YES; CPYR: 1972; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | DURING PIGGING OPERATIONS, LEAK DISCOVERED BY SONAT CREW (BUBBLES AT SURFACE)
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19940205 | 1994-09-28 | 13750 | NORTHERN NATURAL GAS CO (ENRON) | ST. LOUIS |  | MN |  | MP 29.5 |  | 2115 | 1994-08-27 | 1 | NO |  |  |  | Null | NO | RUPTURE | 50 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 44 |  | 19940827 | 813 | 832 | NO DATA | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | LONGITUDINAL | STEEL |  | PIPELINE |  | 1961 | 16 | 0.22 | API 5LX | 52000 | ERW |  | REPUBLIC | 1961 | UNDER GROUND |  | JOHN W. CASKEY | 7136467343 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL |  | YES |  | WATER |  | 8 | 1250 | LONGITUDINAL SEAM FAILURE
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940207 | 1994-10-18 | 19730 | TRUNKLINE GAS CO | JOHNSONVILLE | WAYNE | IL | 62850 | GC 112 |  | 205 | 1994-09-22 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 123000 | 92118.9258 | 200683.2907 | Null | 0 | 40 |  | 19940922 | 826 | 900 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: ESD SYSTEM; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1956; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: ROBERT AL MOODY; PHONE: 7136275716; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | MALFUNCTION OF COMPRESSOR STATION EMERGENCY SHUT DOWN SYSTEM OPENNED BLOW-OFFS WITHOUT ISOLATING THE STATION YARD PIPING.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19940210 | 1994-11-28 | 2616 | COLUMBIA GAS TRANSMISSION CORP | GLADY | RANDOLPH | WV | 26268 |  | 5442+17 | 145 | 1994-10-23 | 1 | NO |  |  |  | Null | NO | RUPTURE | 40 | 0 | 0 | 50000 | 37446.7178 | 81578.5735 | Null | 1 | 15 |  | 19941023 | 792 | 809 | BY TEST | 1110 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1949 | 26 | 0.28 | API 5L | 52000 | FLASH WELD |  | A.O. SMITH | 1949 | UNDER GROUND |  | S.J. CHOBY | 3043572349 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1956 | OUTSIDE/THIRD PARTY |  | NO |  | YES | LINE MARKERS | YES |  |  | Null | [5 empty] | THE RUPTURE OCCURRED AT A CORRODED AREA ON THE PIPE WHERE CATHODIC PROTECTIONCURRENT APPEARS TO HAVE BEEN SHIELDED BY A LARGE ROCK. THE FRACTURE MECHANISM EVALUATION IS NOT YET AVAILABLE FROM COLUMBIA'S METALLURGICAL CONSULTANT.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19940216 | 1994-10-31 | 21031 | VALERO TRANSMISSION CO |  | MATAGORDA | TX | 77457 |  |  | 1000 | 1994-09-07 |  | YES |  | 519 | TX | Null | NO | LEAK | 0 | 0 | 0 | 40000 | 29957.3743 | 65262.8588 | Null | 3 | 0 |  | 19940909 | 850 | 1315 | NO DATA | 0 | CORROSION | CORROSION | EXTERNAL | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1966; NMDIA: 16; THK: 0.28; SPEC: API 5LX52; SMYS: 52000; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: DUANE KETTERMAN; PHONE: 7139512191; LOC: EXTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: OTHER; CAUCO: NOT GIVEN; COAT: COATED; PROT: YES; CPYR: 1966; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | FIELD PERSONNAL HAD BEEN OUT 3 DAYS PRIOR TO 09/07/94. THERE WAS NO LEAK AT THAT TIME. WHEN THEY WERE OUT AGAIN ON 09/07/94, A PINHOLE LEAK, PROBABLY DUETO EXTERNAL CORROSION, WAS FOUND ON THE 3" RISER OFF THE 16" PORTION OF LINE#27. THE LEAK WAS REPAIRED ON 09/11/94.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19940218 | 1994-10-31 | 21031 | VALERO TRANSMISSION CO | CHANNELVIEW | HARRIS | TX | 77530 |  | 785+84 | 1545 | 1994-10-20 | 1 | NO |  |  |  | Null | NO | RUPTURE | 494 | 0 | 0 | 800000 | 599147.4851 | 1305257.1753 | Null | 1 | 0 |  | 19941020 | 538 | 706 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: GIRTH; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1952; NMDIA: 12; THK: 0.34; SPEC: API5LX; SMYS: 42000; SEAM: WELD; MANU: UNKNOWN; MANYR: 0; LOCLK: UNDER GROUND; PNAME: JOHN SOMMER; PHONE: 2102462395; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: FLOODING; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | AT APPROXIMATELY 10:45 A.M. ON OCTOBER 20, 1994, VALERO'S PEARLAND FIELD OPERATIONS OFFICE BECAME AWARE VIA RADIO AND TV NEWSCASTS OF AN INCIDENTS INVOLVING A POSSIBLE RUPTURE OF A COLONIAL PIPELINE IN THE VICINITY OF THE SAN JACINTO RIVER. BECOAUSE VALERO'S 12" SINCO NATURAL GAS PIPELINE CROSSES THE SAN JACINTO RIVER IN CLOSE PROXIMITY TO THE COLONIAL PIPELINE, VALERO IMMEDIATELY BEGAN MONITORING THE GAS PRESSURE ON ITS 12" SINCO LINE TO PROVIDE AN IMMEDIATE INDICATION OF FAILURE. IN ADDITION, VALERO'S GAUGERS WERE DISPATCHED TO MLBV'S ON EACH SIDE OF THE RIVER AND PLACED ON STANDBY NOTICE TO CLOSE THE VALVES AND ISOLATE THE RIVER CROSSING IN CASE OF THE LINE FAILURE. AT 3:45 P.M., ASUBSTANTIAL DROP IN PRESSURE ON THE 12"SINCO PIPELINE WAS NOTED BY VALERO'SGAS CONTROL. VALERO'S GAUGERS WERE INSTRUCTED TO CLOSE THE MLBV'S AND ISOLATETHE PIPELINE SECITON THAT CROSSES THE SAN JACINTO RIVER. VALERO'S GAUGER SHUT THE ARCO LYONDELL MLBV INSIDE THE ARCO LYONDELL FACILITY ON SHELDON ROAD,LOCATED ON THE WEST SIDE OF THE SAN JACINTO RIVER, AT 4:30 PM. WHILE INSIDE THE LYONDELL FACILITY, THE GAUGER ALSO SHUT IN THE ARCO CHEMICAL MLBV AT 4:45P.M. VALERO'S GAUGER SHUT IN THE CROSBY EAST MLBV, LOCATED ON THE EAST SIDE OF THE SAN JACINTO RIVER AT 4:45 P.M. AS AN ADITIONAL PRECAUTION, VALERO'S GAUGER SHUT-IN THE NORTH SHIP CHANNEL MLBV AT 4:15 P.M. AT APPROXIMATELY 5:00 P.M., VALERO PERSONNEL NOTIFIED THE TRRC EMERGENCY NOITICATION HOTLINE OF THE 12" SINCO RUPTURE. AT APPROXIMATELY 6:00 P.M. DEAN SCOATT WITH THE TRRC CALLEDAND DISCUSSED THE INCIDENT WITH VALERO'S ENVIRRONMENTAL AND REGULATORY PERSONNEL AND ADVISED THAT THE TRRC WOULD NOTIFY VALERO IF FURTHER INFORMATION ORACTION WAS REQUIRED. AT 6:30 P.M., VALERO'S FIELD MANAGEMENT PERSONNEL INSPECTED THE 12" SINCO RUPTURE SITE WITH LYONDELL PETRO CHEMICAL AND ARCO CHEMICALPERSONNEL; HOWEVER, DUE TO THE FLOOD WATER DEPTH, NO PHYSICAL ON-SITE CONFIRMATION OF THE 12" SINCO RUPTURE WAS POSSIBLE UNTIL THE FLOOD WATERS RECEDE. AT APPROXIMATELY 7:00 P.M., MARY MCDANIEL WITH TRRC CALLED AND DISCUSSED THE INCIDENT WITH VALERO'S ENVIRONMENTAL AND REGULATORY PERSONNEL AND ADVISED THATTHE TRRC WOULD NOTIFY VALERO IF FURTHER INFORMATION OR ACTION WAS REQUIRED.AT APPROXIMATELY 10:00 P.M. JAMIE HERNANDEZ WITH THE TRRC CALLED AND DISCUSSED THE INCIDENT WITH VALERO'S PEARLAND FIELD OPERATIONS PERSONNEL. VALERO PLANS TO LEAVE THE RIVER SECTION ISOLATED AND OUT OF SERVICE UNTIL THE FLOOD WATERS RECEDE AND REPAIRS CAN BE MADE. SUPPLEMENTAL REPORT 11/22/94 INDICATES THATVALERO IS CURRENTLY REPLACING THE DAMAGED RIVER CROSSING IN ACCORDANCE WITHPLANS SUBMITTED TO THE TRRC. TELEPHONE CONVERSATION WITH MR. SOMMER INDICATESTHAT THIS WAS COMPLETED 12/94.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19940219 | 1994-10-31 | 15033 | PAIUTE PIPELINE CO |  | WASHOE | NV | 89442 | 225.52 |  | 1240 | 1994-10-17 | 1 | NO |  |  | NV | Null | NO | OTHER | 0 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 5 |  | 19941017 | 550 | 960 | BY TEST | 1200 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | OTHER | 2" THREADED VENT STACK | STEEL |  | OTHER | TEMPORARY VENT STACK | 1994 | 2 | 0.15 | ASTM A-53 | 0 | UNKNOWN |  | UNKNOWN | 0 | ABOVE GROUND |  | JEFF MAPLES | 7028872814 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | VENT STACK-TEMPORARY ASSEMBLEY USED TO BLOW-DOWN | Null |  | NO DATA |  | 0 | 0 | FAILURE OCCURRED AT THREADED CONNECTION ON VENT STACK. INCIDENT OCCURRED WHILE BLOWING-DOWN A TEMPORARY BY-PASS PIPE. VENT STACK FAILED AT THREADED CONNECTION. VENT PIPE HIT EMPLOYEE IN LEFT ARM AND LEG. EMPLOYEE REQUIRED OVER-NIGHT STAY IN HOSPITAL.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19940226 | 1994-11-03 | 602 | ARKLA ENERGY RESOURCES | WASHINGTON | HEMPSTEAD | AR | 71835 | 804 +24 |  | 1515 | 1994-10-10 | 1 | NO |  |  |  | Null | NO | RUPTURE | 4 | 0 | 4 | 25000 | 18723.3589 | 40789.2867 | Null | 1 | 20 |  | 19941010 | 580 | 720 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1929; NMDIA: 14; THK: 0.22; SPEC: X - 46; SMYS: 46000; MANYR: 0; LOCLK: UNDER GROUND; PNAME: PAUL G. ESPINOSA; PHONE: 3184293924; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19940928; MARK: YES; MRKTP: EXIST;MARKERS,CROS,METER; STAT: YES; CTEST: Null | CONTRACTOR LAYING PHONE CABLE HIT NGT'S LINE AM-46,14" OD. PIPELINE ROW WAS CLEARLY MARKED. TELEPHONE COMPANY'S CONTRACTOR WAS OFF OF THEIR ASSIGNED ROW.COVER ON PIPELINE WAS OVER 36", A METER STATION WAS CLEARLY VISIBLE A POINT WERE CONTRACTOR DEVIATED FROM THEIR ASSIGNED ROW.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19940227 | 1994-12-06 | 22617 | WILLIAMS NATURAL GAS CO | PECULIAR | CASS | MO | 64078 |  | 2227+07 | 825 | 1994-11-16 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 17000 | 12731.8841 | 27736.715 | YES | 3 | 0 |  | 19941116 | 410 | 570 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1930; NMDIA: 12; THK: 0.28; SPEC: API-5L; SMYS: 60000; SEAM: SMLS; MANU: NAT'AL TUBE; MANYR: 1930; LOCLK: UNDER GROUND; PNAME: JOE FREISBERG; PHONE: 9185616186; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: Line Markers; STAT: YES; CTEST: Null | DOZER HIT PIPELINE WHILE WORKING IN AREA.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19940229 | 1994-12-08 | 2620 | COLUMBIA GULF TRANSMISSION CO | GULF OF MEXICO |  | LA |  |  | 28 31.5'N,93 12.2'W | 2130 | 1994-10-27 |  | YES | WC | 480 | LA | YES | NO | OTHER | 0 | 0 | 0 | 50000 | 37446.7178 | 81578.5735 | Null | 0 | 0 |  | 19941028 | 1100 | 1440 | BY TEST | 2160 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: MECHANICAL JOINT; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1978; NMDIA: 6; THK: 0.43; SPEC: GR.B; SMYS: 35000; SEAM: SEAMLESS; MANU: U.S. STEEL; MANYR: 1978; LOCLK: UNDER WATER; PNAME: S.J. CHOBY; PHONE: 3043572349; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | NO REMARKS. SUPPLEMENTAL REPORT 1/31/95 INDICATES CHANGE IN PART 3 -MARRATIVE DESCRIPTION. TEXAS EASTERN TRANSMISSION CORPORATION'S 16" GRIPPERINTERCONNECTION FAILED RESULTING IN DAMAMGE TO COLUMBIA'S 6" PIPELINE AT THETIE-IN POINT.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19940230 | 1994-12-08 | 5304 | FLORIDA GAS TRANSMISSION CO | WIGGINS | PERRY | MS | 39577 | 126.161 | 3239+39 | 1508 | 1994-11-21 | 1 | NO |  |  |  | Null | NO | RUPTURE | 30 | 0 | 1 | 75000 | 56170.0767 | 122367.8602 | Null | 0 | 27 |  | 19941121 | 848 | 975 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1959; NMDIA: 24; THK: 0.31; SPEC: API -5LX; SMYS: 52000; MANU: REPUBLIC; MANYR: 1959; LOCLK: UNDER GROUND; PNAME: MERLIN MOSEMAN; PHONE: 7136467344; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | PIPELINE HIT BY BULLDOZER BLADE WHILE CONSTRUCTING EROSION TERRACES OVER PIPELINE RIGHT OF WAY.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19940232 | 1994-08-03 | 2001 | CABOT OIL & GAS CORP | GLASGOW | KANAWHA | WV | 25286 |  | 22+02 | 1600 | 1994-07-21 | 3 | NO |  |  |  | Null | NO | RUPTURE | 40 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 15 |  | 19940721 | 700 | 220 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1962; NMDIA: 12; THK: 0.25; SMYS: 42000; SEAM: ERW; MANU: UNKNOWN; MANYR: 1962; LOCLK: UNDER WATER; PNAME: ALAN HAGGERTZ; PHONE: 3045955015; LOC: EXTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: GALVANIC; COAT: BARE; PROT: YES; CPYR: 1962; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | THE PIPELINE WAS SUBMERGED IN A CREEK CROSSING AND OVER THE YEARS DEBRISHITTING THE PIPE HAD DAMAGED THE COATING CAUSING LOCALIZED CORROSION. ON JULY21, 1994 WHILE TESTING TO ESTABLISH A NEW MAOP ON PIPELINE #A-30, A SECTION OFPIPE THAT RUNS THROUGH KELLY'S CREEK RUPTURED. THE SEQUENCE OF EVENTS THATLED UP TO THIS INCIDENTS ARE AS FOLLOWS: PRIOR TO TESTING THIS SEGMENT OFPIPELINE, APPROXIMATELY 4026 FEET IN LENGTH, OF WHICH 1700 FEET IS CLASS III,SEVEN TEEN DIG-OUTS WERE PERFORMED IN ORDER TO ESTABLISH THE WALL THICKNESS OFTHE PIPE. IN ADDITION, SEVEN COUPONS WERE CUT OUT FROM THESE DIG-OUTLOCATIONS AN D WERE SENT TO A LAB TO BE METALLURGICALLY TESTED. ON THE DAY OFTHE TEST, THE PIPELINE WAS PURGED OF NATURAL GAS WITH NITROGEN AND THENON-EXISTENCE OF NATURAL GAS WAS VERIFIED WITH A COMBUSTIBLE GAS INDICATOR. A500 PSI MAOP WAS TO BE ESTABLISHED WITH A TEST PRESSURE OF 750 PSI. IN ORDERTO OBTAIN THE 750 PSI TEST PRESSURE, THE DIFFERENCE BETWEEN THE TEST PRESSUREAND THE ESTABLISHED MAOP OF 220 PSI WAS DIVIDED INTO FOURTHS GIVING 175 PSITEST PRESSURE SEGMENTS. THE FIRST STAGE OF THE TEST WAS TO PRESSURIZE THELINE TO THE ESTABLISHED MAOP OF 220 PSI. THIS PRESSURE WAS MAINTAINED FORAPPROXIMATELY 15 MINUTES WHILE THIS SECTION OF PIPELINE, APPROXIMATELY 4026FEET, WAS BEING WALKED. THE SECOND STAGE OF THE TEST WAS TO PRESSURIZE THELINE TO 395 PSI AND MAINTAIN THIS PRESSURE WHILE THE LINE WAS BEING WALKED.THE THIRD STAGE REQUIRED PRESSURIZING THE PIPELINE TO 570 PSI. THIS TESTPRESSURE WAS ALSO MAINTAINED FOR APPROXIMATELY 15 MINUTES WHILE THE LINE WASBEING WALKED. THE FOURTH, AND FINAL STAGE OF THE TEST, REQUIRED THAT THEPIPELINE BE PRESSURIZED TO 750 PSI. UPON ACHIEVING A TEST PRESSURE OFAPPROXIMATLEY 700 PSI, THE PIPELINE RUPTURED IN A CREEK CROSSING. AS ARESULT OF THIS RUPTURE, TWO INDIVIDUALS, WHICH ARE NON-EMPLOYEES, WERETRANSPORTED TO THE HOSPITAL, ONE OF WHICH WAS TREATED FOR HIGH HEART RATE ANDTHEN RELEASED APPROXIMATELY 3 HOURS LATER. THE SECOND INDIVIDUAL SUSTAINED ACONCUSSION AND WAS HOSPITALIZED FOR TWO DAYS. ALSO, AS A RESULT OF THISRUPTURE, 5 HOUSE TRAILERS, APPROXIMATELY 6 AUTOMOBILES AND 2 CAMPERS RECEIVEDDAMAGE. ONE OF THE HOUSE TRAILERS RECEIVED EXTENSIVE DAMAGE WHILE THE OTHERFOUR RECEIVED DAMAGE RANGING FROM BROKEN WINDOWS TO DENTED OUTER SHELLS. THEDAMAGE TO THE AUTOMOBILES AND CAMPERS RANGED FROM BROKEN WINDSHIELDS TODENTED HOODS.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19950001 | 1994-12-27 | 11683 | LONE STAR GAS CO OF TEXAS, INC | GARLAND | DALLAS | TX |  |  | 3753+44 | 1245 | 1994-11-29 | 3 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 43000 | 32204.1773 | 70157.5732 | Null | 0 | 25 |  | 19941129 | 380 | 400 | BY TEST | 720 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1949; NMDIA: 20; THK: 0.28; SPEC: API5LX; SMYS: 42000; SEAM: EW; MANU: UNKNOWN; MANYR: 0; LOCLK: UNDER GROUND; PNAME: M.L. IMDODEN; PHONE: 2146702779; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PERMANENT P/L MARKERS; STAT: NO; CTEST: Null | CONTRACTOR INSTALLING NATURAL GAS DISTRIBUTION MAIN HIT PIPELINE WITH A TRENCHING MACHINE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19950002 | 1994-12-27 | 5304 | FLORIDA GAS TRANSMISSION CO | AMITE | TANGIPAHOA | LA |  | 34.72 | 1835+70 | 1820 | 1994-12-04 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 52000 | 38944.5865 | 84841.7164 | Null | 1 | 0 |  | 19941204 | 850 | 975 | BY TEST | 1515 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | OTHER | FLANGE GASKET | OTHER | FIBER COMPOSITION | PIPELINE |  | 1994 | 12 | 0 | ANSI B16.21 | 0 |  |  |  | 0 | UNDER GROUND |  | MERLIN MOSEMAN | 7136467344 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION | FLANGE GASKET | NO |  | NO DATA |  | 0 | 0
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19950004 | 1994-12-27 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA | LINDEN | CASS | TX | 75563 | 478 | 25219 +13.4 | 1018 | 1994-11-11 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 110941 | 83087.5264 | 181008.1704 | Null | 5 | 37 |  | 19941111 | 780 | 858 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: UNKNOWN; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1951; NMDIA: 30; THK: 0.34; SPEC: 5LX; SMYS: 52000; SEAM: FLASH WELD; MANU: AO SMITH; MANYR: 1951; LOCLK: UNDER PAVEMENT; PNAME: F ROY FLEET; PHONE: 7086913786; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | NATURAL GAS WAS BLOWING FROM THE VENT OF A CASED CROSSING. THE CARRIER PIPEWAS REMOVED AND REPLACED WITH PRETESTED PIPE. BECAUSE HYDROTESTING FAILED TOID ENTIFY THE SOURCE OR CAUSE OF THE LEAK, THE CARRIER PIPE WAS RETIRED.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19950008 | 1994-12-16 | 19160 | TENNESSEE GAS PIPELINE CO |  |  | LA |  | 5246-401+1.04 |  | 230 | 1994-12-02 |  | YES | BAY MERCHAND | 5 |  | Null | NO | RUPTURE | 0 | 0 | 7 | 0 | 0 | 0 | Null | 2 | 0 |  | 19941202 | 1000 | 1069 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1961; NMDIA: 16; THK: 0.41; SPEC: API-SL; SMYS: 0; SEAM: SEAMLESS; MANU: NATIONAL TUBE; MANYR: 1961; LOCLK: OTHER; LOCLO: NOT GIVEN; PNAME: LOUIS A. SALINAS; PHONE: 7137572781; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: 0; STAT: NO; CTEST: Null | JACK-UP RIG, IN APPARENT EMERGENCY LOWERED A LEG AND SET DOWN ON 16IN. TGP PIPELINE, CAUSING RUPTURE AND SUBSEQUENT FIRE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19950009 | 1994-12-19 | 19570 | TRANSCO GAS PIPELINE CORP | GALVESTON |  | TX |  | 22.75 | 1201+20 | 1600 | 1994-11-20 |  | YES | GALV | 237 |  | YES | NO | RUPTURE | 120 | 0 | 0 | 390000 | 292084.399 | 636312.873 | Null | 4 | 0 |  | 19941120 | 1000 | 1440 | BY TEST | 2218 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1977; NMDIA: 12; THK: 0.38; SPEC: API-5L; SMYS: 42000; SEAM: SEAMLESS; MANU: U.S. STEEL; MANYR: 1977; LOCLK: UNDER WATER; PNAME: B.R. LANDES; PHONE: 7134392002; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: YES; CTEST: Null | A TUG TOWING A SEMI-SUBMERSIBLE RIG IN THE GALVESTON 237 AREA, EXPECTING BADWEATHER, SAT THE RIG ON THE BOTTOM. THE RIG SAT DOWN ON THE 12" PIPELINE DRIVING IT 6 FEET INTO THE MUD AND SEVERING THE LINE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19950011 | 1994-12-27 | 11683 | LONE STAR GAS CO OF TEXAS, INC | TUCKER | ANDERSON | TX |  | 5363+50 | 5364+24 | 945 | 1994-11-15 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 30 |  | 19941115 | 360 | 425 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1936; NMDIA: 20; THK: 0.28; SPEC: GRADE B; SMYS: 35000; SEAM: EW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: M.L. IMBODEN; PHONE: 2146702779; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PAINTED POST 30'; STAT: NO; CTEST: Null | DAMAGE BY ROAD GRADER.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19950019 | 1995-01-18 | 2564 | COLORADO INTERSTATE GAS CO | AURORA | ADAMS | CO | 80019 |  | 11765+75 | 308 | 1994-12-20 | 1 | NO |  |  |  | Null | NO | RUPTURE | 36 | 0 | 0 | 467000 | 349752.3444 | 761943.8761 | Null | 0 | 56 |  | 19941220 | 914 | 920 | BY TEST | 1217 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1950; NMDIA: 20; THK: 0.28; SPEC: API 5LX; SMYS: 460000; SEAM: ERW; MANU: YOUNGSTOWN; MANYR: 1950; LOCLK: UNDER GROUND; PNAME: RICHARD H. FLINT; PHONE: 7195204350; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | CIG'S PIPELINE NUMBER 2B-20" RUPTURED AT 3:08 AM ON 12/20/94; THE RUPTUREEXTENDED FOR APPROXIMATELY 36 FEET ALONG THE PIPE. ESCAPING NATURAL GASIGNITED AND, IN ADDITION TO THE FORCE OF THE RUPTURE, SERIOUSLY DAMAGED CIG'SGRIMM AND FIRST CREEK METER STATIONS WHICH ARE LOCATED ADJACENT TO THEPIPELINE ROW. SERVICE WAS RESTORED TO THE CUSTOMERS SERVED BY THE METERSTATIONS AND THE 2B PIPELINE WAS RETURNED TO SERVICE AT 5 PM ON 12/21/1994.SUBSEQUENT INVESTIGATION DETERMINED THAT THE FRACTURE ORIGINATED ON THEOUSTIDE SURFACE OF THE PIPE BODY AT THE TOE OF THE REINFORCEMENT FOR A 4"BRANCH CONNECTION. AT THIS LOCATION, THERE WAS EVIDENCE OF A SHALLOW,PREEXISTING CRACK ALONG THE OUTSIDE SURFACE OF THE PIPE. THE CAUSE OF THEFAILURE HAS BEEN DETERMINED TO BE SLOW CRACK GROWTH. THE POSSIBLE CAUSE OF THESLOW CRACK GROWTH IS FATIGUE, HOWEVER, THE EXACT NATURE OF THIS GROWTH ISSTILL UNDER DETERMINATION. ADDITIONAL INFORMATION FOR CLASSIFICATION OF PART 2- APPARENT CAUSE - FATIGUE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19950020 | 1994-01-18 | 19570 | TRANSCO GAS PIPELINE CORP | GALVESTON |  | TX |  | 22.786 | 1203+15 | 810 | 1994-12-16 |  | YES | GALV | 237 |  | YES | NO | RUPTURE | 145 | 0 | 0 | 250000 | 187233.5891 | 407892.8673 | Null | 1 | 15 |  | 19941216 | 1150 | 1440 | BY TEST | 2218 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1977; NMDIA: 12; THK: 0.38; SPEC: API-5L; SMYS: 42000; SEAM: SEAMLESS; MANU: U.S. STEEL; MANYR: 1977; LOCLK: UNDER WATER; PNAME: B.R. LANDES; PHONE: 7134392001; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: Null; CTEST: Null | THE RUPTURE ON THE 12" PIPELINE WHICH OCCURRED ON DECEMBER 16, 1994 AT M.P.22.786 WAS CAUSED BY THE SAME OUTSIDE PARTY DAMAGE THAT CAUSED THE RUPTURE OFTHE 12" PIPELINE AT M.P.22.75 WHICH WAS REPORTED TO THE NATIONAL RESPONSECENTER ON NOVEMBER 20, 1994 (REPORT NO. 270374). THE OUTSIDE PARTY DAMAGE WASCAUSED BY A TUG TOWING A SEMI-SUBMERSIBLE RIG IN THE GALVESTON 237 ARA,EXPECTING BAD WEATHER, SAT THE RIG ON THE BOTTOM. THE RIG SAT DOWN ON THE 12"PIPELINE WITH TWO PADS HITTING THE LINE AT TWO SEPARATE LOCATIONS. BECAUSE OFTHE DISTANCE BETWEEN THE TWO DAMAGED AREAS, THE DAMAGE AT M.P. 22.786 WAS NOTDETECTED DURING THE INITIAL INVESTIGATION AND REPAIR OF THE ORIGINAL RUPTUREINCIDENT (N OVEMBER 20, 1994).
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19950021 | 1995-01-18 | 4483 | ENSTAR NATURAL GAS CO | KENAI PENINSULA BOROUGH |  | AK |  | MP 40.5 |  | 1200 | 1994-12-15 | 1 | NO |  |  |  | Null | YES | LEAK | 0 | 0 | 0 | 50000 | 37446.7178 | 81578.5735 | Null | 2 | 0 |  | 19941215 | 640 | 1000 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1960 | 12 | 0.25 | API 5 LX | 46000 | SEAMLESS |  | STEWARTS & LLOYDS LIMITED | 1960 | UNDER GROUND |  | DAVID W. BREDIN | 9072643745 | EXTERNALLY | LOCALIZED PITTING |  | OTHER |  | COATED | YES | 1961 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | 10 FOOT SECTION OF PIPE CUT OUT AND REPLACED FOR PERMANENT REPAIR. COATINGDAMAGED DURING CONSTRUCTION. LOCALIZED CORROSION CAUSED PITTING TO OCCUR.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19950022 | 1995-01-12 | 22617 | WILLIAMS NATURAL GAS CO | PERRY | NOBLE | OK | 74018 | #130 | 2631+67 | 615 | 1994-12-20 | 1 | NO |  |  |  | Null | Null | OTHER | 0 | 0 | 0 | 80000 | 59914.7485 | 130525.7175 | Null | 1 | 45 |  | 19941220 | 575 | 595 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1929 | 20 | 0.25 | API-5L | 33000 | EW |  | A.O. SMITH | 1929 | UNDER GROUND |  | JOE FREISBERG | 9185886186 | INTERNALLY | LOCALIZED PITTING |  | OTHER | BACTERIAL | BARE | YES | 0 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | FAILED JOINT BLEW OUT - SENDING PIPE SPECIMEN FOR ANALYSIS. FURTHERCLASSIFICATION OF PART 2 - APPARENT CAUSE - STATES THAT THIS FAILURE IS UNDERINVESTIGATION. SUPPLEMENTAL REPORT 3/27/1995 INDICATES THAT FURTHERINVESTIGATION CHANGED CAUSE TO CORROSION (INTERNAL). SUPPL - PART A - ALSO IDOF PIPE BARE, OD IS INEFFECTIVELY COATED - COUPLED SECTION.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19950024 | 1995-02-07 | 4904 | EXXON CO USA | MOBILE BLOCK 62 ST. WATER |  | AL |  |  |  | 1300 | 1995-01-01 |  | YES | MOBILE | 62 | AL | Null | NO | LEAK | 0 | 0 | 0 | 210000 | 153994.1569 | 335479.9666 | Null | 0 | 0 |  | 19950103 | 600 | 1480 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: VALVE; MLKD: OTHER; MLKDO: PACKING; PRTSY: PIPELINE; PRTYR: 1993; NMDIA: 3; THK: 0.3; SPEC: ASTM A312; SMYS: 0; VALVE: BALL VALVE; MANU: CAMERON; MANYR: 0; LOCLK: UNDER WATER; PNAME: V.W. HENLEY; PHONE: 5045614680; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | ON DECEMBER 28, 1994, BUBBLES WERE OBSERVED PERCOLATING NEAR THE PIPELINESWHICH TRAVERSE BETWEEN EXXON'S "A" PLATFORM IN MOBILE BLOCK 62 AND THE SSTILOCATED IN THE SAME BLOCK. DUE TO SEA CONDITIONS AND THE SIZE OF THE BUBBLES,THE BUBBLES WERE UNABLE TO BE OBSERVED FROM THE AIR. ALTHOUGH THERE WAS NOPOLLUTION, CHANGE IN OPERATING CONDITIONS OR PIPELINE PRESSURE, PRECAUTIONARYMEASURES WERE TAKEN TO ASCERTAIN THE SOURCE OF THE BUBBLES. AFTER NOTIFYINGTHE ALABAMA PUBLIC SERVICE COMMISSION, ALABAMA OIL AND GAS BOARD, MOBILE MSOOF THE USCG, AND CORPS OF ENGINEERS OF EXXON'S PLANS TO ASCERTAIN THE SOURCEOF THE BUBBLES, WORK BEGAN TO UNCOVER THE PIPELINES ON DECEMBER 30 1994. ONJANUARY 1, 1995 AFTER UNCOVERING THE PIPELINES, DIVERS DISCOVERED A SMALL LEAKAROUND THE BALL VALVE ON THE "3" FUEL GAS PIPELINE. IT IS BELIEVED THAT THEPACKING AND THE SEALANT BECAME EXPOSED TO PRESSURE WHEN THE HALL VALVE WASNOT FULLY OPENED. AFTER DIVERS ENSURED THAT THE VALVE WAS FULLY OPENED,PACKING WAS INJECTED AND THE PACKING AROUND THE STEM OF THE BALL VALVE WASTIGHTENED. REPAIR WORK WAS COMPLETED ON JANUARY 4, 1995. UPON COMPLETION OFOTHER UNRELATED MAINTENANCE WORK ON OTHER PIPELINES, THE 3" FUEL GAS PIPELINEWAS COVERED ON JANUARY 12, 1995.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19950025 | 1995-02-06 | 30012 | ARAN ENERGY CORPORATION | OFFSHORE PLAQUEMINES PAR. |  | LA |  |  |  | 800 | 1995-01-19 |  | YES | SP | 37 |  | YES | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 0 |  |  | 0 | 0 | NO DATA | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | OTHER | NOT GIVEN | PIPELINE |  | 0 | 8 | 0.5 |  | 0 | ERW |  |  | 1961 | OTHER | ON RISER ABOVE WATER | JIM WIBLE | 7137590176 | EXTERNALLY | GENERAL CORROSION |  | OTHER | NOT GIVEN | COATED | YES | 0 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | EXTERNAL CORROSION OVER TIME.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19950026 | 1995-02-01 | 7027 | HALL-HOUSTON OIL COMPANY |  |  | LA |  |  |  | 130 | 1994-12-12 |  | YES | MU | 783 |  | YES | NO | OTHER | 0 | 0 | 0 | 417975 | 313035.8376 | 681956.0848 | Null | 0 | 30 |  | 19941212 | 1440 | 1250 | BY TEST | 2160 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: GATHERING SYSTEM; PRTFL: OTHER; PRTFO: SSTI; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1994; NMDIA: 6; THK: 0.28; SPEC: API 5-L GR B; SMYS: 45700; SEAM: SEAMLESS; MANYR: 0; LOCLK: UNDER WATER; PNAME: KATHY CAMP; PHONE: 7132280711; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: AS-BUILT TO NOAA FOR MAPP; STAT: YES; CTEST: Null | NO ONE WITNESSED INCIDENT. REPORT INDICATED ANCHOR DRAGGED ACROSS PIPELINE SEGMENT. PART B - TYPE OF MARKING- AS-BUILT WAS SUBMITTED TO NOAA FOR MAPPING & PIPELINE BURIED ACCORDING TO DOT/DOI REGULATIONS.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19950042 | 1995-02-23 | 30624 | DALEN RESOURCES OIL & GAS CO. | OFFSHORE CALHOUN |  | TX |  |  |  | 1030 | 1995-01-08 |  | YES | ST | 628L | TX | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | Null | 4 | 0 |  | 19950113 | 800 | 1380 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1976; NMDIA: 10; THK: 0.28; SPEC: APT5LX-42; SMYS: 0; SEAM: ERW; MANYR: 0; LOCLK: UNDER WATER; PNAME: JIM LAFEVERS; PHONE: 2147503988; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | PIPE APPEARED TO DEVELOP SPLIT 1/2" X 1/16" ON TOP SIDE. SUSPECT POSSIBLE DEFECTIVE PIPE. LEAK REPAIRED WITH CLAMP
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19950043 | 1995-02-14 | 4904 | EXXON CO USA | MOBILE BLOCK 62 ST.WATER |  | AL |  |  |  | 1600 | 1995-01-09 |  | YES | MOBILE | 62 | AL | Null | NO | LEAK | 0 | 0 | 0 | 110000 | 80663.606 | 175727.6016 | Null | 0 | 0 |  | 19950110 | 1100 | 1933 | BY TEST | 2900 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: GATHERING SYSTEM; PRTFL: OTHER; PRTFO: INJECTION PORT ON VALVE; MLKD: OTHER; MLKDO: INJECTION PORT; PRTSY: PIPELINE; PRTYR: 1993; NMDIA: 10; THK: 0.46; SPEC: API-5L; SMYS: 0; VALVE: BALL VALVE; MANU: CAMERON; MANYR: 0; LOCLK: UNDER WATER; PNAME: VERNARD HENLEY; PHONE: 5045614680; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | ON JANUARY 9, 1995 WHILE PERFORMING MAINTENANCE WORK ON THE 10" PRODUCED GASPIPELINE FROM MOBILE BLOCK 62 "A" TO MOBILE BLOCK 62 SSTI, DIVERS DISCOVEREDBUBBLES PERCOLATING FROM THE SEALANT INJECTION PORT ON THE BALL VALVE. THEREWAS NO POLLUTION AS A RESULT OF THE RELEASE OF BUBBLES. NOTIFICATION WAS MADETO THE ALABAMA PUBLIC SERVICE COMMISSION (APSC) AND THE ALABAMA OIL AND GASBOARD (AO GB) ON JANUARY 9, 1995. AFTER DETERMINING THE EXTENT OF THE REPAIRWORK, THE NATIONAL RESPONSE CENTER (NRC) WAS CONTACTED ON JANUARY 10, 1995.ALL FACILITIES IN THE FIELD WERE SHUT IN AND THE PRODUCED GAS PIPELINESYSTEM WAS DEPRESSURIZED BEFORE PROCEEDING WITH REPAIRING THE INJECTION PORT.THE PIPELINE WAS REPAIRED BY INJECTING SEALANT AND PLUGGING THE INJECTIONPORT. THIS WORK WAS COMPLETED ON JANUARY 10, 1995. UPON COMPLETION OF OTHERUNRELATED MAINTENANCE WORK ON OTHER PIPELINES, THE 10" PRODUCED GAS PIPELINEWAS COVERED ON JANUARY 12,1995.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19950044 | 1995-02-14 | 19570 | TRANSCO GAS PIPELINE CORP | SOUTH MARSH ISLAND |  | LA |  | 8.27 | 436+66 | 847 | 1995-01-24 |  | YES | SMI | 38 |  | YES | NO | LEAK | 0 | 0 | 0 | 255000 | 186992.9048 | 407368.5309 | Null | 6 | 17 |  | 19950124 | 1211 | 1300 | BY TEST | 2175 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | OTHER | HYDROCOUPLE END CONNECTOR | STEEL |  | PIPELINE |  | 1972 | 12 | 0 |  | 0 | 900#END CONN. |  | HYDRO TECH | 1972 | UNDER WATER |  | B.R. LANDES | 7134392001 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | HYDROCOUPLE END CON.,USAS 900#,BULL PLUG TYPE,S.AC | YES | 19720321 | WATER |  | 8 | 3000 | THE HYDROCOUPLE END CONNECTOR SLIPPED OFF THE END OF THE 12" PIPELINE DURINGAN ABNORMAL PRESSURE CONDITION. THEIS ABNORMAL PRESSURE CONDITION DID NOT EXCEED THE MAOP OF THE PIPELINE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19950045 | 1995-02-27 | 5304 | FLORIDA GAS TRANSMISSION CO | GAINESVILLE | ALACHUA | FL |  | 16.93 | 893+93 | 1835 | 1995-01-31 | 3 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 29000 | 21265.8598 | 46328.1859 | YES | 2 | 25 |  | 19950131 | 760 | 763 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1959; NMDIA: 8; THK: 0.19; SPEC: API - 5L; SMYS: 35000; SEAM: SEAMLESS; MANU: REPUBLIC; MANYR: 0; LOCLK: UNDER GROUND; PNAME: MERLIN MOSEMAN; PHONE: 7136467344; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: NO; MARK: Null; MRKTP: 0; STAT: NO; CTEST: Null
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19950048 | 1995-03-02 | 4461 | ENRON OIL & GAS CO | MATAGORDA |  | TX |  |  |  | 940 | 1995-02-01 |  | YES | MI | 527 |  | YES | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | Null | 1 | 0 |  | 19950201 | 360 | 1440 | BY TEST | 0 | CORROSION | CORROSION | EXTERNAL | GATHERING SYSTEM | FITTING | 90 ELL NEXT TO WELD | STEEL |  | PIPELINE |  | 0 | 4.5 | 0.24 |  | 0 |  |  |  | 0 | OTHER | ABOVE WATER | M.A. GARRED | 7138533457 | EXTERNALLY | GENERAL CORROSION |  | OTHER | NOT GIVEN | COATED | NO | 0 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | CORROSIVE SPOT ON DEPARTING LINE (LOCALIZED ) DEVELOPED SMALL HOLE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19950049 | 1995-03-17 | 2616 | COLUMBIA GAS TRANSMISSION CORP | ISLAND CREEK | LOGAN | WV | 25649 |  | 1473+00 | 1530 | 1995-02-07 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 50000 | 36665.2755 | 79876.1825 | Null | 1 | 30 |  | 19950207 | 870 | 1183 | BY TEST | 1483 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1980; NMDIA: 16; THK: 0.22; SPEC: API5LX; SMYS: 60000; SEAM: ELECTRIC WELD; MANU: UNITED STATES STEEL; MANYR: 1980; LOCLK: UNDER GROUND; PNAME: S.J. CHOBY; PHONE: 3043572349; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: CLEARED RIGHT -OF- WAY; STAT: YES; CTEST: Null | THIRD PARTY CONTRACTOR DOZER PUNCTURED COLUMBIA'S PIPELINE WHILE CLEARINGINTERSECTING RIGHT-OF-WAY FOR ANOTHER OPERATOR'S NEW PIPELINE CONSTRUCTIONPROJECT.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19950053 | 1995-03-23 | 2714 | CNG TRANSMISSION CORP | TAMARACK | CLINTON | PA | 17764 | FINNEFROCK STATION |  | 2245 | 1995-02-23 | 3 | NO |  |  | PA | Null | NO | RUPTURE | 1.8 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 8 |  | 19950224 | 750 | 1000 | BY TEST | 1500 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | OTHER | PULSATION BOTTLE BODY | STEEL |  | COMPRESSOR STATION |  | 1986 | 30 | 0.88 | SA-516-70 | 0 |  |  | PEERLESS | 1986 | ABOVE GROUND |  | MICHAEL D. FREDERICK | 7177234431 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION | SUCTION BOTTLE | YES | 19930813 | WATER |  | 1 | 1500 | SPECULATION PENDING FINAL ANALYSIS
2021-02-26 10:36 | YES | YES | GG (Gas Gathering) | 19950054 | 1995-03-30 | 1130 | BASIN PIPELINE CORP | BROWN TOWNSHIP | MANISTEE | MI | 49660 | BROWN 19 PLANT | 0+00 | 1230 | 1995-02-25 | 1 | NO |  |  |  | Null | NO | RUPTURE | 0 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 15 |  | 19950225 | 1150 | 1200 | BY TEST | 2482 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | GATHERING SYSTEM | MECHANICAL JOINT |  | OTHER | FLANGE GASKET | PIPELINE |  | 1994 | 8 | 0.32 | ANSI B16.5 | 0 |  |  | GARLOCK | 1994 | ABOVE GROUND |  | DANIEL M. COOPER | 6164523279 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | GASKET FURNISHED BY NATIONAL OILWELL IN FLANGE | NO |  | NO DATA |  | 0 | 0 | ADDITIONAL INFORMATION IS BEING COLLECTED TO ALLOW DETERMINATION OF THE CAUSE OF THE FAILURE. GASKET FAILED IN INSULATING FLANGE AT PIG RECEIVER WHILE PUMPING METHANOL INTO LINE TO REMOVE HYDRATE PLUG. GASKET FURNISHED BY NATIONALOILWELL IN FLANGE INSULATION KIT REPORTEDLY PACKAGED BY FLANGE PROTECTION, INC. W/GASKET REPORTEDLY MANUFACTURED BY GARLOCK.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19950059 | 1995-04-07 | 19570 | TRANSCO GAS PIPELINE CORP | CHIPOLA | ST HELENA | LA |  | 616.53 | 9555 +79 | 1715 | 1995-03-19 | 2 | NO |  |  |  | Null | NO | RUPTURE | 275 | 0 | 0 | 619000 | 453916.1102 | 988867.1397 | Null | 2 | 30 |  | 19950319 | 726 | 780 | BY TEST | 1179 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1956; NMDIA: 36; THK: 0.41; SPEC: API-5L; SMYS: 520000; SEAM: DSA; MANU: BETHLEHEM; MANYR: 1956; LOCLK: UNDER GROUND; PNAME: B.R. LANDES; PHONE: 7134392001; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: POST WITH SIGNS; STAT: YES; CTEST: Null | SIZE, SHAPE, AND SEVERITY OF THE GOUGE (44") INDICATES IT WAS CAUSED BY ALARGE PIECE OF EXCAVATION EQUIPMENT (PROBABLY) A BACKHOE. FAILURE INITIATED INA GOUGE OF UNKNOWN ORIGIN.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19950060 | 1995-04-07 | 12622 | MOBIL EXPLORATION & PRODUCING US INC | GRAND CHENIER | CAMERON | LA | 70643 | 21.8 |  | 1000 | 1995-03-14 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 50000 | 36665.2755 | 79876.1825 | YES | 1 | 0 |  | 19950314 | 980 | 1440 | BY TEST | 2160 | CORROSION | CORROSION | INTERNAL | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1965; NMDIA: 16; THK: 0.5; SPEC: API 5XL - 52; SMYS: 52000; MANYR: 0; LOCLK: UNDER GROUND; PNAME: CEDRIC D. SMITH; PHONE: 7137752323; LOC: INTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: OTHER; CAUCO: INTERNAL CORROSION; COAT: COATED; PROT: YES; CPYR: 1965; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | EXTERIOR SURFACE OF PIPE WAS FREE AND CLEAR OF ANY SIGNS OF EXTERNAL CORROSION. PIPE-TO-SOIL READING AT THIS LOCATION WAS -1.053 VDC.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19950061 | 1995-04-10 | 13845 | NORTHWEST PIPELINE CORP | CASTLE ROCK | COWLITZ | WA |  | 1272.72 MAINLINE 1400 | 10986 +84 | 1340 | 1995-03-06 | 1 | NO |  |  |  | Null | NO | RUPTURE | 0 | 0 | 0 | 719000 | 527246.6611 | 1148619.5047 | Null | 1 | 20 |  | 19950306 | 660 | 809 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1956; NMDIA: 26; THK: 0.28; SPEC: API-5L X52; SMYS: 520000; SEAM: DSA; MANU: CONSOL WEST; MANYR: 1955; LOCLK: UNDER GROUND; PNAME: BILL CLARK SR; PHONE: 8015846906; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: NO; MARK: Null; MRKTP: 0; STAT: NO; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19950067 | 1995-04-24 | 26127 | CHEVRON PIPELINE CO | LA HABRA | LOS ANGELES | CA |  | OLD EMERY LEASE |  | 1500 | 1995-04-12 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 5000 | 3666.5275 | 7987.6183 | Null | 0 | 15 |  | 19950412 | 140 | 210 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 0; NMDIA: 8; THK: 0.32; SMYS: 0; SEAM: LAP WELD; MANYR: 0; LOCLK: UNDER GROUND; PNAME: ERNEST BROWNING; PHONE: 7142281501; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19950123; MARK: YES; MRKTP: MARKER POSTS; STAT: YES; CTEST: Null | THE INCIDENT OCCURRED AT 1340 PST ON MARCH 6, 1995 IN A REMOTE AREA AT MILEPOST 1272. 7 NEAR CASTLE ROCK WASHINGTON. THE FAILURE OCCURRED ON NORTHWEST PIPELINE CORPORATION'S 26 INCH IGNACIO, COLORADO TO SUMAS, WASHINGTON MAINLINE.IN THE ACCIDENT AREA THE LINE IS PARALLELED BY NORTHWEST'S 30 INCH LOOPLINE AND A 14 INCH PRODUCTS LINE OWNED BY OLYMPIC PIPELINE COMPANY. NORTHWEST'S 26INCH PIPE RUPTURED OR BUILDING DAMAGE. NEITHER OF THE ADJACENT LINES WERE DAMAGED REPAIRS WERE COMPLETE BY REPLACEMENT OF 201 FEET OF 26 INCH PIPE AND THE LINE WAS PURGED ON SATURDAY MARCH, 11, 1995. THE LINE WAS NOT RETURNED TO FULL SERVICE UNTIL MARCH 15, 1995 PENDING GEOTECHNICAL ASSESSMENTS OF THE SLIDE AREA AND EXCAVATION OF THE 26 AND 30 INCH LINES TO RELIEVE STRESSES. NATURAL GAS SERVICE WAS INTERRUPTED TO TWO INDUSTRIAL USERS FOR 3 HOURS AT ONE LOCATION AND 5 HOURS AT THE OTHER. GEOTECHNICAL ENGINEERING ASSESEMENT OF THE SITE AREA CONCLUDES THAT THE PIPELINES WERE IMPACTED BY A RECENT LANDSLIDE THAT EXTENDS APPROXIMATELY 1000 FEET UPSLOPE FROM THE PIPELINES. PRELIM8INARY REPORTS OF LABORATORY ANALYSIS OF SELECTED SAMPLES OF THE FAILED PIPE INDICATE THE FAILURE WAS DUE TO RADICAL MOVEMENT OF THE BURIED LINE INDUCING A BUCKLE. THE BUCKLING AND THE STRESS ASSOCIATED WITH THE MOVEMENT CAUSED THE PIPE TO RUPTURE AT THE BUCKLE. APPROXIMATELY 495 FEET OF 26 INCH LINE AND 268 FEET OF 30 INCH LINE WAS EXCAVATED AND LEFT FREE TO ENABLE FREE MOVEMENT OF THE LANDSLIDE. SUBSEQUENT INSPECTIONS OF THE TWO LINES CONFIRMED THAT THEIR SERVICEABILITY IS NOT IMPAIRED. THE SITE IS SECURED AND THE PIPELINES ARE OBSERVED DAILY. SURFACE DISPLACEMENT MEASUREMENTS ARE BEING TAKEN THREE TIMES PER WEEK AT THIS TIME. PLANS FOR LONG TERM REMEDIATION OF THE SITE WILL BE DEPENDENT ON CONTINUED EVALUATION OF THE CHARACTER AND EXTENT OF THE LANDSLIDE.CONTRACTOR WAS REMOVING PIPELINES IN AREA OF CHEV. DRY GAS LINE; CONTR. HADSTOCKPILED SOIL OVER THE GAS LINE. CONTRACTOR, WHILE REMOVING DIRT, FORGOTWHERE ORIGINAL GRADE WAS; THEY EXCAVATED TOO DEEPLY & PUNCTURED ACTIVE LINE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19950068 | 1995-04-26 | 13750 | NORTHERN NATURAL GAS CO (ENRON) | GUTHERIE |  | IA |  | MP 50.25 |  | 222 | 1995-03-24 | 1 | NO |  |  |  | Null | NO | RUPTURE | 120 | 0 | 0 | 75000 | 54997.9132 | 119814.2738 | Null | 1 | 38 |  | 19950324 | 688 | 800 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | OTHER | AT BRANCH CONNECTION | STEEL |  | PIPELINE |  | 1950 | 26 | 0.28 | 5LX | 52000 | DSA |  | A.O. SMITH | 1950 | UNDER GROUND |  | JOHN W. CASKEY | 7136467343 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | 4" BRANCH CONNECTION | NO |  | NO DATA |  | 0 | 0 | SUPPLEMENTAL REPORT WILL FOLLOW WHEN FAILURE CAUSE IS KNOWN.FAILURE THROUGH A 4" BRANCH CONNECTION ON 26" PIPE. EXACT CAUSE OF FAILURE NOT KNOWN YET.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19950069 | 1995-04-27 | 15518 | PIEDMONT NATURAL GAS CO INC | HUNTERSVILLE | MECKLENBURG | NC | 28078 |  |  | 915 | 1995-03-27 | 3 | NO |  |  |  | Null | NO | RUPTURE | 0.5 | 0 | 1 | 0 | 0 | 0 | Null | 3 | 0 |  | 19950327 | 730 | 780 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1959; NMDIA: 10; THK: 0.28; SPEC: API-5L GR.B; SMYS: 35000; SEAM: SEAMLESS; MANYR: 1959; LOCLK: OTHER; LOCLO: NO ENTRY; PNAME: RONALD W. COBB; PHONE: 7043643120; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19950322; MARK: YES; MRKTP: 1; STAT: YES; CTEST: Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19950071 | 1995-05-15 | 18484 | SOUTHERN CALIFORNIA GAS CO | LA CONCHITA | VENTURA | CA | 93001 | 25.40 | 1340+90.0 | 1705 | 1995-04-19 | 1 | NO |  |  |  | Null | NO | RUPTURE | 5 | 0 | 0 | 150000 | 109995.8264 | 239628.5476 | Null | 1 | 34 |  | 19950420 | 285 | 460 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: GIRTH; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1931; NMDIA: 16; THK: 0.25; SPEC: X-30; SMYS: 30000; MANU: A.O. SMITH; MANYR: 1930; LOCLK: UNDER GROUND; PNAME: G.D. LAFEYERS; PHONE: 2132443245; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: NO; MARK: Null; MRKTP: 0; STAT: NO; CTEST: Null | ON APRIL 19, 1995, AT APPROXIMATELY 5:05 P.M., A LARGE MUD SLIDE IN BIG VCANYON CAUSED THE SOUTHERN CALIFORNIA GAS COMPANY'S 116" TRANSMISSION LINE1003 TO RUPTURE IN THE BOTTOM OF THE CANYON. COMPANY PERSONNEL WEREIMMEDIATELY DISPATCHED TO IDENTIFY THE LOCATION AND ISOLATE THE BREAK. VALVESMLV 1003-27. 83-0 AND MLV 1003-23.85 WERE CLOSED AND GAS BROUGHT UNDER CONTROLAT 6:39 P.M. THE INCIDENT RESULTED IN TEMPORARY LOSS OF GAS SERVICE TO 3RESIDENTAL CUSTOMERS THERE WERE NO INJURIES, EVACUATIONS OR STREET CLOSURES.THE AREA OF RUPT URE IS COVERED WITH LANDSLIDE MATERIAL AND CANNOT BE VISUALLYINSPECTED AT THIS TIME. FIELD OBSERVATIONS INDICATE THAT ONE OR MORE WELDLOCATIONS BROKE DUE TO THE EARTH MOVEMENT. THE AREA IS CURRENTLY BEINGEVALUATED TO DETERMINE A SAFE ALIGNMENT FOR RELOCATION OF THE PIPELINE. WE AREIN THE PROCESS OF DETERMINING HOW LONG THE PIPELINE CAN BE OUT OF SERVICE ANDIF INSTALLATION OF A TEMPORARY BYPASS IS REQUIRED UNTIL PERMANENT REPAIRS CANBE MADE. THE AMOUNT OF DAMAGE TO COMPANY FACILITIES IS CURRENTLY ESTIMATED AT$150,000. PER MESSAGE FR. G. LAFEVERS 5/26, RUPTURE LENGTH IS APPROX. 5 FT.THE PIPE HAS BROKEN AT WELD AND SEPARATION IS APPROX. 5FT. RUPTURED SECTION ISSTILL BURIED UNDER LAND SLIDE MATERIAL.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19950072 | 1995-05-04 | 22617 | WILLIAMS NATURAL GAS CO | EDMOND | OKLAHOMA | OK | 73034 |  |  | 555 | 1995-04-17 | 3 | NO |  |  | OK | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 30 |  | 19950417 | 392 | 418 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: ESD SYSTEM; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1952; NMDIA: 0; THK: 0; SMYS: 0; VALVE: SHAFER OPERATOR; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: KEN YAGER; PHONE: 9185884447; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | A GAS DETECTOR SENSOR MALFUNCTIONED AND ACTIVATED THE EMERGENCY SHUT DOWN SYSTEM. OUR SCADA SYSTEM INDICATED THAT THE INTAKE VALVE DID NOT CLOSE COMPLETELY.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19950073 | 1995-05-04 | 22617 | WILLIAMS NATURAL GAS CO | BURDEN | COWLEY | KS |  |  | 1740+55 | 1811 | 1995-04-08 | 1 | NO |  |  |  | Null | NO | RUPTURE | 11 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 34 |  | 19950408 | 200 | 250 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1917; NMDIA: 16; THK: 0.25; SMYS: 24000; SEAM: ERW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: KEN YAGER; PHONE: 9185884447; LOC: EXTERNALLY; ADESC: GENERAL CORROSION; CAUCR: GALVANIC; COAT: BARE; PROT: YES; CPYR: 1974; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | HOT SPOT SURVEY - COUPLED LINE
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19950074 | 1995-05-02 | 13845 | NORTHWEST PIPELINE CORP |  | ELMORE | ID |  | M.P. 2.49 | 132+76.5 | 820 | 1995-03-31 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 303000 | 222191.5693 | 484049.6661 | Null | 0 | 0 |  | 19950405 | 890 | 911 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | LONGITUDINAL | STEEL |  | PIPELINE |  | 1962 | 16 | 0.23 | API5LX-X46 | 46000 | ELECTRIC RESIS |  | KAISER | 1962 | UNDER GROUND |  | JAMES W. SMITH | 8015846906 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL |  | YES | 19620601 | GAS |  | 1 | 1055 | THREE QUARTER INCH SPLIT LONGITUDINAL SEAM. SPLIT CLOSED WHEN PRESSURE WASREDUCED DELAYING LEAK IDENTIFICATION AND REPORTING. REPAIRS WERE MADE BYREPLACING 73 FEET OF PIPE DURING STOPPLE BYPASS OPERATION TO MAINTAINCONTINUITY OF SERVICE. SPLIT IN LONG SEAM (3/4 INCH) ERW PIPE IDENTIFIED BYDEAD VEGETATION DURING LEAK SURVEY. INITIALLY DETERMINED TO BE NON-REPORTABLE,STOPPLE/BYPASS REPAIRS ESCALATED COSTS ABOVE REPORTING THRESHOLD.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19950080 | 1995-05-18 | 19570 | TRANSCO GAS PIPELINE CORP | SHIP SHOAL |  | LA |  | 0.67 | 35 + 38 | 730 | 1995-04-25 |  | YES | SS | 269 |  | YES | NO | LEAK | 0 | 0 | 0 | 250000 | 183326.3773 | 399380.9126 | Null | 2 | 0 |  | 19950425 | 1050 | 1250 | BY TEST | 2910 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | OTHER | MID-RISER CONNECTOR | STEEL |  | PIPELINE |  | 1973 | 16 | 0 |  | 0 | 900# MID RISER |  | CAMERON | 1973 | UNDER WATER |  | BILL R. LANDES | 7134392001 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | MID RISER CONNECTOR | YES | 19730928 | WATER |  | 8 | 2910 | THE CLAMP ON THE MID RISER CONNECTOR ASSEMBLY ON THE 16" RISER FAILED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19950081 | 1995-05-18 | 18516 | SOUTHERN NATURAL GAS CO | NEW HEBRON | JEFFERSON DAVIS | MS | 39140 | 0.000 SOUTH MAIN PIPELINE |  | 1614 | 1995-04-19 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 750000 | 549979.1319 | 1198142.7379 | YES | 0 | 20 |  | 19950421 | 887 | 1200 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | OTHER | TURBINE COMPRESSOR ENGINE | OTHER | COMPONENTS CONTAINED | COMPRESSOR STATION |  | 1963 | 0 | 0 |  | 0 |  |  | SOLAR | 1963 | ABOVE GROUND |  | H.M. BERGLUND | 6018471182 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | NO DATA | SOLAR T1001S-15 SATURN TURBINE NAT.GAS COMPRESSOR | NO |  | NO DATA |  | 0 | 0 | TURBINE UNIT WAS PRESSURE TESTED BY THE MANUFACTURER PURSUANT TO INDUSTRYDESIGN SPECIFICATION APPLICABLE AT THE TIME OF MANUFACTURING.SOLAR T1001S-15SATURN TURBINE NATURAL GAS COMPRESSOR ENGINE RATED @1080 HORSEPOWER. A FIREOCCURED IN A TURBINE COMPRESSOR UNIT. CAUSE OF THE FIRE IS PRESENTLY UNKNOWN,BUT INVESTIGATION IS CONTINUING. THERE WAS NO EXPLOSION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19950084 | 1995-06-19 | 4070 | EAST TENNESSEE NATURAL GAS CO | JOHNSON CITY | WASHINGTON | TN | 37601 | 3307C-202+2.90 | 153+64 | 2030 | 1995-05-19 | 1 | NO |  |  | TN | Null | YES | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 30 |  | 19950519 | 0 | 0 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1962; NMDIA: 6.63; THK: 0.28; SPEC: API GRADE B; SMYS: 35000; MANYR: 0; LOCLK: UNDER GROUND; PNAME: A.T. RICHARDSON; PHONE: 7137574292; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | THUNDER STORM WITH HEAVY LIGHTNING MOVED THROUGH THE AREA JUST BEFORE FIRE WAS REPORTED.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19950085 | 1995-06-20 | 15007 | PACIFIC GAS & ELECTRIC CO | SAN PABLO | CONTRA COSTA | CA | 94802 | SAN PABLO STATION |  | 2136 | 1995-06-02 | 3 | NO |  |  | CA | Null | NO | OTHER | 0 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 0 |  | 19950607 | 0 | 135 | BY TEST | 250 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: NOT GIVEN; MLKD: OTHER; MLKDO: NOT GIVEN; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1930; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: JAMES H. POPE; PHONE: 4159736999; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | VANDAL ENTERED REGULATION FACILITY BY SCALING FENCE. OPERATED 14 VALVES THATWERE LOCKED IN POSITION BY CHAINS. RELIEF VALVE OPENED DUE TO OVERPRESSURE ASA RESULT OF VALVE CHANGES. GAS RELEASED THROUGH RELIEF VALVE WAS IGNITED BY VANDAL, RESULTING IN INJURY.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19950092 | 1995-07-06 | 2616 | COLUMBIA GAS TRANSMISSION CORP | BLUE CREEK | KANAWHA | WV | 25026 |  | 379+72 | 1600 | 1995-06-27 | 2 | NO |  |  |  | Null | NO | RUPTURE | 16.5 | 0 | 0 | 0 | 0 | 0 | YES | 3 | 0 |  | 19950627 | 83 | 190 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1966 | 12 | 0.2 | API5L | 52000 | ERW |  | UNKNOWN | 1966 | UNDER GROUND |  | S.J. CHOBY | 3043472349 | INTERNALLY | GENERAL CORROSION |  | OTHER | BACTERIAL | COATED | YES | 1966 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | LOCAL SUPERVISOR RESPONDED TO VERIFY A LEAK CALLED IN BY NEARBY RESIDENT. PIPE RUPTURED WHILE SUPERVISOR WAS RETURNING TO OFFICE. EMERGENCY ACTION INCLUDED ISOLATING AREA AND EVACUATING THREE RESIDENTS. ISOLATION COMPLETED BY 1900HOURS.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19950093 | 1995-07-05 | 21252 | VIKING GAS TRANSMISSION CO | MILACA | MILLE LACS | MN | 56353 | 2217-1+2.61 | 137 + 80 | 1245 | 1995-06-25 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 10 |  | 19950625 | 0 | 877 | BY TEST | 971 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: NOT GIVEN; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1960; NMDIA: 24; THK: 0.28; SPEC: API-5L X52; SMYS: 52000; SEAM: DSA; MANU: N.T. (ORANGE); MANYR: 1960; LOCLK: OTHER; LOCLO: CONSTRUCTION TRENCH; PNAME: MARK A. MICKELBERG; PHONE: 6122292269; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | WELDER'S HELPER RECEIVED FLASH BURN WHEN GRINDING WELD BEVEL ON 24" PIPE. ONSUNDAY, JUNE 25, 1995 APPROXIMATELY 12:45 P.M., EARL STEINBRENNER (CONTRACTWELDERS HELPER) WAS GRINDING A BEVEL ON A 24" NATURAL GAS PIPELINE. THE BEVEL WAS ON THE OPEN END OF THE DOWNSTREAM PIPE THAT JUST HAD A NITE-CAP REMOVED. THE WELDER WAS ASKED IF THEY WANTED THE AIR MOVERS TURNED ON, AND DECIDED TO TEST THE INSIDE OF PIPE WITH A COMBUSTIBLE GAS DETECTOR AND STATED IT WAS O.K. (O % LEL). THE WELDERS'S HELPER PROCEEDED WITH THE BEVEL PREPARATION AND HAD BEEN GRINDING ON THE 24" PIPE END FOR APPROXIMATELY 10 MINUTES PRIPR TO THE INCIDENT. THE WELDER'S HELPER WAS GOING TO TOUCH UP A SPOT ON THE BEVEL WHEN THE FLASH OCCURRED. THE FLASH WAS INSTANTANEOUS AND SELF-EXTINGUISHED IMMEDIATELY. HE WAS WEARING A FACE SHIELD AND SAFETY GLASSES. THE WELDER'S HELPERRECEIVED MINOR BURNS TO THE FACE AND NECK AREA WHICH REQUIRED MEDICAL ATTENTION. THE VICTIM WAS TAKEN TO HENNEPIN COUNTY MEDICAL CENTER FOR A REQUIRED 24HOUR OBSERVATION PERIOD, THAN RELEASED ON THE MORNING OF JUNE 26TH WITH NO SERIOUS INJURIES.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19950094 | 1995-07-10 | 15007 | PACIFIC GAS & ELECTRIC CO | GREENFIELD | MONTEREY | CA | 93927 | 31.71 (LINE 187) |  | 207 | 1995-04-25 | 2 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 270000 | 197992.4875 | 431331.3856 | Null | 2 | 23 |  | 19950425 | 313 | 313 | BY TEST | 313 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1952; NMDIA: 8.63; THK: 0.19; SPEC: AP1 5L X 42; SMYS: 42000; SEAM: ERW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: JAMES H. POPE; PHONE: 4159736999; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19950421; MARK: Null; STAT: Null; CTEST: Null | THE THIRD-PARTY WAS WORKING AND STRUCK THE LINE AT A LOCATION 3,000 FEET AWAY FROM WHERE THEY SAID THE WERE GOING TO BE WORKING. A FARMER PLOWING A FIELDSOUTH OF GREENFIELD STRUCK A GAS TRANSMISSION MAIN WITH A RIPPER. SERVICE WASDISRUPTED TO APPROXIMATELY 2,455 CUSTOMERS. NO INJURIES OR FATALITIES OCCURRE
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19950096 | 1995-07-17 | 11680 | LONE STAR GAS CO | AUSTIN | TRAVIS | TX |  |  | 2227+25 TO 2230+05 | 815 | 1995-06-02 | 1 | NO |  |  |  | Null | NO | RUPTURE | 0 | 0 | 0 | 100000 | 73330.5509 | 159752.3651 | Null | 1 | 30 |  | 19950602 | 500 | 800 | BY TEST | 1235 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1969; NMDIA: 20; THK: 0.5; SPEC: GRADE B; SMYS: 35000; SEAM: EW SMLS; MANYR: 0; LOCLK: UNDER WATER; PNAME: M.L. IMBODEN; PHONE: 2146702779; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: FLOOD WATERS; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | LINE P DAMAGED FROM FLOOD WATERS OF THE COLORADO RIVER CAUSING RUPTURE AT BOTH ENDS OF THE RIVER CROSSING.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19950099 | 1995-07-17 | 30703 | YOUNG GAS STORAGE COMPANY., LTD. | YOUNG COMPRESSOR STATION | MORGAN | CO | 80701 |  |  | 745 | 1995-06-16 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 15 |  | 19950616 | 400 | 2160 | BY TEST | 3240 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: VALVE; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1995; NMDIA: 0; THK: 0; SMYS: 0; VALVE: 16" ANSI CLASS; MANU: KF INDUSTRIES; MANYR: 1994; LOCLK: ABOVE GROUND; PNAME: R.H. FLINT; PHONE: 7195204350; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | GAS ESCAPED FROM THE BODY CAVITY VENT OF A 16", ANSI CLASS 900 BALL VALVE ASTHE VALVE WAS BEING OPENED DURING ROUTINE MAINTENANCE. THE GAS IGNITED AND BURNED AN EMPLOYEE WHO WAS ATTEMPTING TO STOP THE FLOW OF GAS BY CLOSING THE 16" VALVE. INVESTIGATION DETERMINED THAT THE 1" THREADED PLUG ASSOCIATED WITH THE VENT, WHICH IS LOCATED NEAR THE BOTTOM OF THE VALVE BODY, HAD NOT BEEN REPLACED IN THE VENT OPENING AFTER THE VALVE WAS DRAINED SUBSEQUENT TO THE ORIGINAL, POST-CONSTRUCTION HYDROSTATIC TEST, AND THAT THIS VALVE DESIGN PERMITS LINE PRESSURE TO BE IN THE BODY CAVITY AT ALL TIMES EXCEPT WHEN THE 16" VALVEIS FULLY CLOSED. FACTORS CONTRIBUTING TO THE ACCIDENT INCLUDE THE FAILURE TOREPLACE THE VENT PLUG AFTER HYDROSTATIC TESTING, AND THE EMPLOYEE'S DECISIONTO REENTER THE AREA IN AN ATTEMPT TO STOP THE FLOW OF ESCAPING GAS.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19950104 | 1995-08-01 | 19730 | TRUNKLINE GAS CO | TUNNEL HILL | JOHNSON | IL | 62991 | M.P. 23 | 131 + 84 | 1130 | 1995-07-01 | 1 | NO |  |  |  | Null | NO | RUPTURE | 800 | 0 | 0 | 1750000 | 1283284.6411 | 2795666.3884 | Null | 1 | 35 |  | 19950701 | 886 | 900 | BY TEST | 1320 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1951 | 26 | 3.13 | API-5L | 52000 | DSWA |  | KAISER | 1951 | UNDER GROUND |  | ROBERT AL MOODY | 7136275716 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1951 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | Isolated corroded area was small enough so as not to be readily identifiablewith close interval cathodic protection survey equipment and techniques available today. No other corrosion observed. Pipeline came to rest on a rock ledge which damaged the coating. Failure originated at 6:00 position. Brittle pipe is suspected.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19950105 | 1995-08-02 | 13845 | NORTHWEST PIPELINE CORP | DINGLE | BEAR LAKE | ID |  | MP 504.4 | 5941+21 | 55 | 1995-06-28 | 1 | NO |  |  |  | Null | NO | RUPTURE | 350 | 0 | 0 | 700000 | 513313.8564 | 1118266.5554 | Null | 1 | 35 |  | 19950628 | 780 | 850 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1956; NMDIA: 22; THK: 0.25; SPEC: 5L X52; SMYS: 52000; SEAM: DSAW; MANU: CONSOL-WEST; MANYR: 1956; LOCLK: UNDER GROUND; PNAME: KENT HIRSCHI; PHONE: 8015846718; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: MATERIAL; CTEST: YES; MED: WATER; TMPS: 1; LKPS: 994 | Laboratory analysis identified the origin of the failure as a longitudinal gouge, .150" deep and one foot in length located in the 5:00 position of the pipe. The long seam was located in the 6:00 position. The gouge was the result of mechanical damage made during the original 1956 construction. Theincident occurred at 12:55 a.m. MDT on June 28, 1995 in a remote wetland areanear Dingle, Idaho, which is located in the southwestern part of the state.The 22 inch pipeline rupture ignited and damaged 350 feet of pipe. There wereno injuries and property damage was limited to brush and a small grove oftrees. The 18 mile line segment was isolated within 55 minutes and the firewas extinguished within 95 minutes. Natural gas service was interrupted toIntermountain Gas Company, the local natural gas distribution company servingthe city of Montpelier, Idaho, and the surrounding area. Approximately 1000Intermountain customers were affected by the service interruption. Servicewas restored to Intermountain within 22 hours using a temporary bypass.Approximately 415 feet of 22 inch pipe was replaced and the 22 inch mainlinewas returned to full service on July 2, 1995. Laboratory analysis of thefailed pipe specimens identified the origin of the failure as a longitudinalgouge .150" deep, and one foot in length. The gouge, located in the 5 o'clockposition, was the result of outside force mechanical damage made during theoriginal 1956 construction of the line.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19950106 | 1995-07-27 | 19160 | TENNESSEE GAS PIPELINE CO | GULF OF MEXICO |  | LA |  | 509A-401+2.03 |  | 1630 | 1995-06-27 |  | YES | EC | 254B |  | YES | NO | LEAK | 0 | 0 | 0 | 226000 | 165727.0451 | 361040.345 | Null | 0 | 0 |  | 19950627 | 1073 | 1440 | BY TEST | 2165 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1974 | 16 | 0.38 | API5L | 52000 |  |  | U.S. STEEL | 1974 | UNDER WATER |  | DENISE BENTHAM | 7137578835 | INTERNALLY | OTHER | NONE GIVEN | OTHER | NONE GIVEN | COATED | YES | 1974 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | Unknown factors - suspected internal corrosion
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19950107 | 1995-07-31 | 902 | TECO GAS GATHERING COMPANY | HARGIL | HIDALGO | TX |  | TET METER STATION | 9-8064-1 | 2200 | 1995-05-30 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 139250 | 102112.7922 | 222455.1683 | Null | 2 | 10 |  | 19950531 | 814 | 1072 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: ELBOW ON DUMP LINE; MLKD: STEEL; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1989; NMDIA: 2; THK: 0.15; SPEC: GRADE B; SMYS: 0; SEAM: SEAMLESS; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: JOHN A. KALER, II; PHONE: 5128840731; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: LIGHTNING; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | On May 30, 1995, at approximately 2200 hours, Teco Pipeline Company receivedan emergency call from Texas One Call concerning a fire near our pipeline. Teco personnel immediately responded and upon arrival discovered a fire at our meter station near Hargil, Texas. Apparent cause of the accident was lightning hitting a fiberglass tank in the station yard. The tank ignited also causing a 2" dump line and a 1/2" nipple off of the separator to break and ignite. All inlet points to the pipeline system were immediately shut in and thefire was brought under control. The fire was completely out by 0010 hours on 31 May, 1995, two (2) hours and ten (10) minutes after the lightning had struck. Repair work at the station began immediately. All valves, controls, and meters that were affected by the heat were either replaced or repaired.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19950108 | 1995-08-03 | 13302 | NATIONAL GAS & OIL CORP | ZANESVILLE | MUSKINGUM | OH | 43701 | ZANE STORAGE COMPRESSOR |  | 700 | 1995-07-01 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 285000 | 208992.0701 | 455294.2404 | Null | 0 | 10 |  | 19950701 | 240 | 675 | BY TEST | 1013 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: NIPPLE; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1978; NMDIA: 1; THK: 0.13; SPEC: A106B; SMYS: 35000; SEAM: SEAMLESS; MANYR: 0; LOCLK: UNDER GROUND; LOCLO: WITHIN BUILDING; PNAME: DAVID K. DETTY; PHONE: 6143442102; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | On July 1, 1995, a fire occured at an unattended National Gas & Oil corporation storage compressor station damaging a metal building and engine/compressor. A one inch pipe fitting located on the compressor failed releasing gas into the building that was ignited by the engine. The Emergency Shutdown Device(ESD) was activated and the gas fire was extinguuished in approximately 10 minutes. No personal injuries were sustained and damage to the facility was estimated at approximately $285,000. No company employees were considered a contributing factor to the incident and therefore were not alcohol or drug tested following the incident.The cause of the incident was the failure of a one inch pipe nipple located on the interstage manifold of the compressor. The pipe nipple connected a relief valve to the interstage manifold between the first stage and second state compressor cylinders. The physical appearance of the fitting indicates that the failure resulted from metal fatigue.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19950112 | 1995-08-15 | 14211 | ONG TRANSMISSION CO | ALVA | WOODS | OK |  |  | NW/4 SEC. 15 26N 13W | 15 | 1995-07-22 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 65000 | 47664.8581 | 103839.0373 | Null | 2 | 19 |  | 19950722 | 546 | 800 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: OTHER; PRTSO: METER SETTING PROD.EQUIP; PRTYR: 1987; NMDIA: 2; THK: 0.15; SPEC: GRADE B; SMYS: 135000; SEAM: SMLS; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: GERRY LYNN; PHONE: 9185887600; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | LIGHTNING STRUCK GAS PURCHASE METER SETTING RESULTING IN A FIRE WHICH DESTROYED VARIOUS PIECES OF PRODUCTION EQUIPMENT.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19950113 | 1995-08-14 | 2620 | COLUMBIA GULF TRANSMISSION CO | CORINTH | ALCORN | MS | 38834 | 85.2 | 4489 + 53 | 530 | 1995-07-31 | 3 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 5 |  | 19950731 | 905 | 1008 | BY TEST | 1560 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: TURBINE/COMPRESSOR; MLKD: OTHER; MLKDO: LUBE OIL CONTROL SYSTEM; PRTSY: COMPRESSOR STATION; PRTYR: 1966; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: OTHER; LOCLO: COMPRESSOR BUILDING; PNAME: S.J. CHOBY; PHONE: 3043572349; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | THE PRECISE MECHANISM AND ROOT CAUSE OF THIS FAILURE REMAINS UNDETERMINED. APPARENTLY, NUMBER 5 TURBINE AND COMPRESSOR LUBE OIL SYSTEM SHUT DOWN DUE TO ANUNDETERMINED FAULT. SUBSEQUENTLY, THE SEAL OIL DRAINED THROUGH THE COMPRESSOR SEALS, WHICH CAUSED THE SEAL OIL LEVEL TO DROP AND GAS TO MIGRATE FROM THECOMPRESSOR CASE TO THE OIL SUMP RESERVOIR. THE MIGRATING GAS ATOMIZED THE SUMP OIL, AND A MIXTURE OF OIL MIST/VAPOR AND NATURAL GAS WAS RELEASED INTO THECOMPRESSOR BUILDING. AN EXPLOSION AND FIRE RESULTED. THE IGNITION SOURCE IS UNKNOWN. NUMBER 5 UNIT AUTOMATICALLY SHUT DOWN. WHEN AN EMPLOYEE RESPONDED,IGNITION AND EXPLOSION OCCURRED WHEN HE OPENED THE COMPRESSOR BUILDING DOOR.THIS RESULTED IN 1ST, 2ND AND 3RD DEGREE BURNS AND HOSPITALIZATION OF THEEMPLOYEE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19950114 | 1995-08-14 | 2620 | COLUMBIA GULF TRANSMISSION CO | GULF OF MEXICO | VERMILION BLOCK 96 | LA |  | N 29 11' 06" W 92 21' 00" |  | 1730 | 1995-07-22 |  | YES | VERMILION 96 |  |  | YES | NO | LEAK | 0 | 0 | 0 | 50000 | 36665.2755 | 79876.1825 | Null | 0 | 0 |  | 19950722 | 850 | 1440 | BY TEST | 2160 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | AT HOT TAP CONNECTION | STEEL |  | PIPELINE |  | 1986 | 6 | 0.43 | A106 GR.B | 35000 | SEAMLESS | N/A | UNKNOWN | 1986 | UNDER WATER |  | S.J. CHOBY | 3043572349 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | SEE COMMENTS | NO |  | NO DATA |  | 0 | 0 | LEAK OCCURRED AT FILLET WELD ON THE 6" LEG OF 6" X 36 EXTRUDED STRONGBACK ENCIRCLEMENT SADDLE AT UNDERSEA HOT TAP TIE IN CONNECTION. PIN HOLE LEAK AT 12:00 POSITION ON FILLET WELD. EXACT LEAK MECHANISM HAS NOT BEEN DETERMINED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19950115 | 1995-08-08 | 15105 | PANHANDLE EASTERN PIPELINE CO | OLPE | LYON | KS | 66865 | MP 3 | 153 +66 | 915 | 1995-07-07 | 1 | NO |  |  |  | Null | NO | RUPTURE | 24.5 | 0 | 0 | 220000 | 161327.212 | 351455.2031 | Null | 1 | 20 |  | 19950707 | 883 | 900 | BY TEST | 1250 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1949; NMDIA: 26; THK: 0.31; SPEC: API - 5LX; SMYS: 52000; SEAM: SEAMLESS; MANU: NATIONAL TUBE; MANYR: 1948; LOCLK: UNDER GROUND; PNAME: JOHN C. KELLY; PHONE: 7136275600; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | FIVE SCC CRACKS, LINEARLY ALIGNED, LINKED TOGETHER TO FORM A FLAW APPROXIMATELY FOUR (4) INCHES LONG RESULTING IN THE RUPTURE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19950122 | 1995-09-12 | 20044 | PRAXAIR, INC | MOSS BLUFF | LIBERTY | TX |  | 30.2 | 1594 +86.8 | 345 | 1995-08-12 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 25000 | 18332.6377 | 39938.0913 | Null | 13 | 15 |  | 19950812 | 780 | 1100 | BY TEST | 1700 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: AUTO ACCIDENT; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1992; NMDIA: 10; THK: 0.19; SPEC: API 5L X-52; SMYS: 52000; VALVE: BALL; MANU: CAMERON; MANYR: 1992; LOCLK: ABOVE GROUND; PNAME: PATRICK J. CONNELLY; PHONE: 7168797417; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: Null; MRKTP: 0; STAT: NO; CTEST: Null | DAMAGE CAUSES BY FIRE FROM OUTSIDE SOURCE AS A RESULT OF CAR ACCIDENT. A CARIS ENGULFED IN FLAMES AND BLACK SMOKE AFTER A GAS LINE EXPLODED EARLY SATURDAY ALONG FM 563 SOUTH OF LIBERTY. THREE PEOPLE WERE INJURED IN THE EXPLOSION.OFFICIALS ALSO EVACUATED FOUR OTHER HOMES DURING THE FIRE, WHICH OCCURRED AFTER A DRIVER RAN OFF THE ROAD AND STRUCK A VALVE. TWO WOMEN BURNED IN THE EXPLOSION WERE REPORTED IN CRITICAL CONDITION SATURDAY NIGHT.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19950128 | 1995-10-02 | 2616 | COLUMBIA GAS TRANSMISSION CORP | BARNABUS | LOGAN | WV | 25609 |  | 721 +00 | 1650 | 1995-09-13 | 1 | NO |  |  |  | Null | NO | RUPTURE | 6 | 0 | 0 | 50000 | 36665.2755 | 79876.1825 | Null | 4 | 0 |  | 19950913 | 1170 | 1183 | BY TEST | 1863 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1992; NMDIA: 16; THK: 0.28; SPEC: API 5L; SMYS: 60000; SEAM: ERW; MANU: U.S. STEEL; MANYR: 1992; LOCLK: UNDER GROUND; PNAME: S.J. CHOBY; PHONE: 3043572349; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: LINE MARKER; STAT: YES; CTEST: Null | PRELIMINARY INVESTIGATION INDICATES THE PIPELINE WAS DAMAGED BY A COAL STRIPPING OPERATOR'S DOZER TRACK TURNING AROUND IN WET, SOUPY DRAINAGE DITCH LOCATION ON THE PIPELINE RIGHT-OF-WAY. CRACK PROPOGATION IN THE RESULTING DENT/GOUGE AREA CAUSED THE RUPTURE.
2021-02-26 10:36 | YES | YES | GG (Gas Gathering) | 19950129 | 1995-09-28 | 30552 | TRIDENT NGL PLANT | WHITE OAK | GREGG | TX | 75693 | 1 MILE SOUTH OF HWY 80 |  | 1040 | 1995-08-15 | 1 | NO |  |  | TX | Null | NO | LEAK | 0 | 0 | 1 | 10000 | 7333.0551 | 15975.2365 | Null | 0 | 45 |  | 19950815 | 5 | 60 | BY TEST | 90 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1971 | 6 | 0.08 | UNKNOWN/GRB | 24000 | ERW |  |  | 0 | UNDER GROUND |  | JEAN C. PITTMAN | 9037599417 | INTERNALLY | GENERAL CORROSION |  | OTHER | WET GAS/TRACE | COATED | YES | 0 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | CORROSION COUPONS AT PLANT INLET SHOWED NO SIGNIFICANT CORROSION.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19950130 | 1995-09-22 | 2731 | CHEVRON PIPELINE CO | MAIN PASS 41 "B" STRUCTUR |  | TX |  | 16" PIG LAUNCHER |  | 1045 | 1995-08-24 |  | YES | MP | 42 |  | YES | NO | OTHER | 0 | 2 | 0 | 50000 | 36665.2755 | 79876.1825 | Null | 15 | 0 |  | 19950824 | 1020 | 1207 | BY TEST | 1207 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: PIPE CLOSURE; MLKD: STEEL; PRTSY: OTHER; PRTSO: PIG LAUNCHER; PRTYR: 1969; NMDIA: 18; THK: 0.94; SPEC: A193 GR B7 STUDS; SMYS: 105000; VALVE: VERTICAL PIG TR; MANU: TUBE TURN CO; MANYR: 1969; LOCLK: OTHER; LOCLO: DECK OF PLATFORM; PNAME: MICHAEL P. OWEN; PHONE: 5045926062; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | TWO CHEVRON U.S.A. PRODUCTION CO., INC. OPERATORS WERE IN THE PROCESS OF OPENING A PIG LAUNCHER ON A 16" PIPELINE OWNED BY CHANDELEUR PIPLINE COMPANY, A WHOLLY OWNED SUBSIDIARY OF CHEVRON PIPE LINE COMPANY. THE PIG LAUNCHER WAS LOCATED ON CHEVRON U.S.A. PRODUCTION CO., INC.'S MAIN PASS BLOCK 41 "B" PLATFORM. THE OPERATORS HAD BEEN REQUESTED TO BLEED DOWN THE PRESSURE ON THE SEGMENTOF CHANDELEUR PIPE LINE COMPANY'S 16" PIPELINE EXTENDING FROM "B" TO "L" PLATFORMS. FOR REASONS CURRENTLY UNKNOWN, THE OPERATORS BEGAN OPENING THE LAUNCCHER CLOSURE BEFORE BLEEDING PRESSURE OFF THE LAUNCHER. AS ONE OF THE OPERATORS WAS IN THE PROCESS OF LOOSENING THE BOLTS WHICH SECURED THE CLAMP ON THE LAUNCHER CLOSURE, THE HIGH PRESSURE GAS (1020 PSI) CONTAINED IN THE LAUNCHER ESCAPED CAUSING FATAL INJURIES TO BOTH OPERATORS AND CAUSED DAMAGE TO THE CLOSURE ASSEMBLY. THERE WERE NO EYEWITNESSES TO THE INCIDENT. CHEVRON U.S.A. PRODUCTION CO., INC. IS CURRENTLY CONDUCTING AN INVESTIGATION INTO THE INCIDENT. ASUPPLEMENTAL REPORT WILL BE SUBMITTED WHEN THE INVESTIGATION HAS BEEN COMPLETED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19950133 | 1995-10-10 | 2616 | COLUMBIA GAS TRANSMISSION CORP | MARTIN | FLOYD | KY | 41649 |  | 192+13 | 1410 | 1995-09-25 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 50000 | 36665.2755 | 79876.1825 | Null | 0 | 30 |  | 19950925 | 360 | 438 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1965; NMDIA: 12; THK: 0.25; SPEC: API 5L; SMYS: 42000; SEAM: ERW; MANYR: 1965; LOCLK: UNDER GROUND; PNAME: S.J. CHOBY; PHONE: 3043572349; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: LINE MARKER; STAT: YES; CTEST: Null | COAL OPERATOR'S DOZER GOUGED 2 FOOT HOLE IN PIPELINE WHILE WORKING HAUL ROADFOR STRIPPING OPERATIONS.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19950134 | 1995-10-11 | 19730 | TRUNKLINE GAS CO | OCS LOUISIANA |  | LA |  | BLOCK V-340 | X=1642916.4; Y=-159639.5 | 1515 | 1995-09-01 |  | YES | VE | 340 |  | YES | NO | LEAK | 0 | 0 | 0 | 150000 | 109995.8264 | 239628.5476 | Null | 10 | 0 |  | 19950908 | 822 | 1200 | BY TEST | 2407 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: 1/2" NPT NIPPLE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1978; NMDIA: 0.5; THK: 0.28; SPEC: A-105-EXHWY; SMYS: 25000; SEAM: SLMS; MANU: 1/2" NPT NIPPLE; MANYR: 0; LOCLK: UNDER WATER; PNAME: ROBERT A. MOODY; PHONE: 7136275716; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; MRKTP: OFFSHORE; STAT: NO; CTEST: Null | DAMAGE CAUSE UNKNOWN - CRACK IN 1/2" NPT NIPPLE EXTRA HEAVY. NIPPLE AND VALVEWAS BLEEDER ASSEMBLY ON HYDROTECH REPAIR CLAMP. CAUSE OF INCIDENT IS UNKNOWN.DUE TO UNDERWATER LOCATION AND NO VISIBLE POLLUTANT, VERIFICATION OF LEAK ONLINE 1004-B-1100 WAS NOT CONFIRMED UNTIL 8:00 A.M. ON 09/08/95. REPAIRSCOMPLETED AT 7:25 A.M. ON 09/14/95. DUE TO UNDERWATER LOCATION AND NO VISIBLEPOLLUTANT, VERIFICATION OF LEAK IN LINE 1004-B-1100 WAS NOT CONFIRMED UNTIL9/8/1995. REPAIRS COMPLETED AT 7:25AM ON 9/14/1995.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19950135 | 1995-10-23 | 2616 | COLUMBIA GAS TRANSMISSION CORP | HANOVER | YORK | PA | 17331 |  | 175 + 18 | 755 | 1995-09-29 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 35 |  | 19950929 | 325 | 427 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1950; NMDIA: 8; THK: 0.28; SPEC: API 5L; SMYS: 35000; SEAM: SEAMLESS; MANYR: 1950; LOCLK: UNDER GROUND; PNAME: STEVEN BURNLEY; PHONE: 3043573575; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PERMANENT MARKERS; STAT: YES; CTEST: Null | EXCAVATION CONTRACTOR OPERATING A RIPPER ON A BULLDOZER IN EARTH MOVING OPERATION STRUCK LINE., ONE 200' +/- NORTH, ONE 229' +/- SOUTH.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19950136 | 1995-10-16 | 4161 | EASTEX GAS TRANSMISSION CO | SPRING | HARRIS | TX | 77389 | 22400 ROTHWOOD RD |  | 1800 | 1995-09-27 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 3500 | 2566.5693 | 5591.3328 | YES | 1 | 30 |  | 19950928 | 1200 | 2198 | BY TEST | 3298 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | OTHER | FLOWLINE | 1988 | 6.63 | 0.28 | API 5LX-52 ERW | 0 |  |  | DIXIE PIPE | 1987 | UNDER GROUND |  | STEVE TWARDONOSKY | 7133508826 | INTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1993 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | 6" GAS LINE WAS BEING UTILIZED AS A FLOWLINE FROM PRODUCING WELL (OIL-SALTWATER) SAMPLES OF SALTWATER FROM LINE INDICATED REASON FOR CORROSION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19950141 | 1995-11-01 | 18516 | SOUTHERN NATURAL GAS CO | SOUTH PASS BLOCK 60 |  | LA |  | 0.11 | 6 + 00 | 0 | 1995-10-04 |  | YES | SOUTH PASS | 60 |  | YES | NO | OTHER | 0 | 0 | 0 | 50000 | 36665.2755 | 79876.1825 | Null | 0 | 0 |  | 19951006 | 650 | 1238 | BY TEST | 1548 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: MECHANICAL JOINT; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1993; NMDIA: 18; THK: 0.5; SMYS: 0; MANU: BIMS; MANYR: 1993; LOCLK: UNDER WATER; PNAME: TED Y. MCLANAHAN; PHONE: 5046826212; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | SHEAR JOINT (INSTALLED ON PIPELINE IN 1993) SEPARATION CAUSED BY MUDSLIDE DURING HURRICANE OPAL.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19950145 | 1995-11-06 | 405 | ANR PIPELINE CO | HIGH ISLAND |  | TX |  | x=3649242.65 y=230449.14 |  | 1430 | 1995-10-06 |  | YES | H.I. | A283 |  | YES | NO | LEAK | 0 | 0 | 0 | 150000 | 109995.8264 | 239628.5476 | Null | 0 | 0 |  | 19951006 | 1000 | 1440 | BY TEST | 2612 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: EXTRUDED TEE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1979; NMDIA: 12; THK: 0.69; SMYS: 35000; MANU: U.S.STEEL; MANYR: 1979; LOCLK: UNDER WATER; PNAME: DONALD E. CROSS; PHONE: 3134962460; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | PIPELINE WAS STRUCK BY 1" CABLE THAT WAS DRAGGED OVER OUR 12" LATERAL LINE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19950146 | 1995-11-09 | 19235 | TEXAS EASTERN GAS PIPELINE CO | MAIN PASS BLOCK 178 |  | LA |  | 5.76 | 303+95 | 2330 | 1995-10-03 |  | YES | MP | 178 | LA | YES | NO | OTHER | 0 | 0 | 0 | 980000 | 718639.399 | 1565573.1775 | Null | 0 | 0 |  | 19951108 | 660 | 1440 | BY TEST | 3250 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: TEE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1988; NMDIA: 6; THK: 0.43; SPEC: 5L; SMYS: 35000; SEAM: SEAMLESS; MANYR: 0; LOCLK: OTHER; LOCLO: NOT GIVEN; PNAME: ALAN LAMBETH; PHONE: 7136274891; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: HURRICANE; NOTIF: NO; MARK: NO; MRKTP: 0; STAT: NO; CTEST: Null | TEXAS EASTERN SUBSEA TAP VALVE ASSEMBLY MUST BE REPLACED. BOAT ANCHORS PULLEDA 6" PIPELINE, OWNED BY UNITED MERIDIAN CORPORATION, AWAY FROM ITSCONNECTION TO TEXAS EASTERN DURING HURRICANE OPAL, RESULTING IN THE LOSS OFGAS IN THE TEXAS EASTERN PIPELINE. (BOAT OWNER HAS NOT BEEN IDENTIFIED).
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19950150 | 1995-11-24 | 30063 | VASTAR RESOURCES, INC. | MAIN PASS BLOCK 77 |  | LA |  |  |  | 1342 | 1995-10-23 |  | YES | MP | 77 | LA | YES | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19951024 | 90 | 3680 | BY TEST | 5520 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1995; NMDIA: 4; THK: 0.44; SPEC: API 5L,GRADEB; SMYS: 35000; SEAM: SEAMLESS; VALVE: ANSI 1500; MANYR: 0; LOCLK: UNDER WATER; PNAME: MICHAEL R. SCOGGINS; PHONE: 7135843599; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: MUD SLIDE; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | AFTER UNSUCCESSFUL ATTEMPT TO PRESSURE UP LINE, LEAK WAS NARROWED DOWN BY BOATBY LOCATING BUBBLES. SUBSEQUENTLY, A SIDE SCAN SONAR AND MAGNETOMETER SURVEYWERE CONDUCTED- BREAK IS AT X=2,771, 360 AND Y=192,090.LINE PARTED DUE TO AMUD SLIDE IN THE VICINITY OF THE LINE. SUSPECT HURRICANE OPAL TRIGGERED THEMUD SLIDE THE LINE WAS NOT IN SERVICE AT THE TIME OF THE INCIDENT BECAUSEOTHE R REPAIRS WERE NECESSARY IN ANOTHER PORTION OF THE LINE. LINE PART WASDISCOVERED WHEN GAS WAS FLOWED INTO THE LINE BUT UNABLE TO PRESSURE UP> 90PSIG.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19950151 | 1995-11-27 | 8200 | INTRATEX GAS CO | BAKERSFIELD | PECOS | TX | 79752 | MP - 446 | 23546+50 | 1430 | 1995-10-14 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 0 |  | 19951014 | 0 | 1050 | BY TEST | 1975 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: ELECTRICAL CONNECTION; MLKD: OTHER; MLKDO: ELECTRICAL WIRE; PRTSY: COMPRESSOR STATION; PRTYR: 1972; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: JOSE L DE LA FUENTE; PHONE: 7136467885; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | IN THE PROCESS OF RETURNING THE 30" SUCTION VALVE TO SERVICE, THE TECHNICIANHOOKED UP THE ELECTRICAL CONNECTION TO THE VALVE ACTUATOR AND PROCEEDED TO OPEN THE VALVE, BUT THEN THE ELECTRICAL CONNECTION FAILED, CAUSING THE PILOT GAS VALVE TO VENT A SMALL QUANTITY OF GAS WHICH MAY HAVE IGNITED BY ELECTRICALARCING.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19950152 | 1995-11-27 | 21031 | VALERO TRANSMISSION CO | RACHAL | BROOKS | TX |  |  |  | 824 | 1995-10-28 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 45000 | 32998.7479 | 71888.5643 | Null | 0 | 30 |  | 19951028 | 770 | 1063 | BY TEST | 1479 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: COMPRESSOR VALVE; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1974; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: KATHY RUTHERFORD; PHONE: 2102463386; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | THE CENTER BOLT THAT RETAINS THE VALVE CHAIR LOOSENED AND PERMITTED GAS TO ESCAPE AND IGNITE. THE ESD SYSTEM ACTIVATED AND EXTINGUISHED THE FIRE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19950153 | 1995-11-27 | 7605 | HOUSTON PIPELINE CO | PORT NECHES | JEFFERSON | TX | 77651 | MP 10 | 34 +87 | 745 | 1995-10-21 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 5000 | 3666.5275 | 7987.6183 | Null | 0 | 0 |  | 19951021 | 569 | 1063 | BY TEST | 1393 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | GIRTH | STEEL |  | PIPELINE |  | 1960 | 17.75 | 0.31 | API-5L-X-42 | 42000 | ERW |  | KANE | 1959 | UNDER GROUND |  | JOSE L DE LA FUENTE | 7136467347 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION |  | YES | 19920407 | WATER |  | 8 | 1393 | SMALL CRACK IN CIRCUMFERENTIAL WELD.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19950154 | 1995-11-27 | 4900 | TEJAS GAS PIPELINE COMPANY | ANAHUAC | CHAMBERS | TX | 77514 | 0.7 | 36+70 | 1740 | 1995-10-25 | 1 | NO |  |  |  | Null | Null | LEAK | 0 | 0 | 0 | 24000 | 17599.3322 | 38340.5676 | Null | 3 | 30 |  | 19951025 | 655 | 900 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1947; NMDIA: 8; THK: 0.32; SPEC: UNKNOWN; SMYS: 24000; SEAM: LAPWELD; MANYR: 0; LOCLK: OTHER; LOCLO: EXPOSED IN BOTTOM DITCH; PNAME: ROBERT L. BROWN JR; PHONE: 7139513460; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: NO; MARK: YES; MRKTP: ROAD CROSSING SIGN; STAT: NO; CTEST: Null | A CONTRACTOR WAS EMPLOYED BY THE OPERATOR TO MOW THE PIPELINE RIGHT-OF-WAY. THE MOWER STRUCK AN EXPOSED SEGMENT OF PIPELINE IN THE BOTTOM OF A ROAD DRAINAGE DITCH. PIPE WAS NOT VISIBLE DUE TO PRESENCE OF VEGETATION BEING MOWED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19950155 | 1995-11-27 | 22435 | WEST TEXAS GAS INC | PECOS | REEVES | TX | 79772 |  |  | 530 | 1995-04-18 | 1 | NO |  |  | TX | Null | NO | RUPTURE | 4 | 0 | 0 | 10000 | 7333.0551 | 15975.2365 | Null | 2 | 0 |  | 19950418 | 759 | 720 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1955; NMDIA: 8; THK: 0.35; SPEC: X-42; SMYS: 0; MANYR: 0; LOCLK: UNDER GROUND; PNAME: RICHARD HATCHETT; PHONE: 9156824349; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: MATERIAL; CTEST: NO; MED: NO DATA; TMPS: 0; LKPS: 0 | PIPE JOINT WOULD PROBABLY NOT HAVE FAILED IF DELHI RELIEF VALVES HAD PROPERLYOPERATED.ANALYSIS REVEALED INTERNAL STRESS LINES IN LINE WITH THE STEP WISEFLOW ON THE PIPE JOINT. EXCESS PRESSURE ON PIPELINE DUE TO FAILURE OF RELIEFVALVES ON DELHI PIPELINE.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19950162 | 1995-12-18 | 12180 | MARSHALL COUNTY GAS DISTRICT | SCOTTSBORO | JACKSON | AL | 35768 | 85 |  | 930 | 1995-12-06 | 3 | NO |  |  | AL | Null | NO | LEAK | 0 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 1 |  | 19951206 | 1 | 350 | BY TEST | 720 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: VALVE; MLKD: STEEL; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1965; NMDIA: 4; THK: 0.24; SPEC: API 5LX42; SMYS: 0; SEAM: WELDED; VALVE: GATE; MANU: OKADEE; MANYR: 1965; LOCLK: ABOVE GROUND; PNAME: RICHARD T. LAWSON; PHONE: 2055825641; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | OKADEE 4" GATE VALVE LEAKING THROUGH SLIGHTLY (<1PSI). ATTEMPTING TO CHANGE OUT A 4" AXIAL FLOW WITH AN IMPACT WRENCH. LOW OVERCAST, LOW BAROMETRIC PRESSURE, LOW WIND, TYPE OF DAY. EMPLOYEES WERE ATTEMPTING TO IMPACT REMOVE THE LAS BOLT WHEN IGNITION OCCURRED. FOUR MEN WERE PRESENT AT THE SITE (INTERMEDIATE RUN AT NORANDAL REGULATOR STATION). PRESENT WERE MARSHALL COUNTY GAS DISTRICT EMPLOYEES: DAVID BROWN, CARL RICE, LEONARD KIRKLAND, AND PAUL BOWDEN. THREE WERE SLIGHTLY BURNED ON HANDS AND FACE AREA BUT NONE OF WHICH RECEIVED TREATMENT. HOWEVER, PAUL BOWDEN, 37 YEAR OLD WHITE MALE, RECEIVED SLIGHT FIRST DEGREE BURNS TO UPPER FACIAL AREA AND BOTH HANDS REQUIRING IN-PATIENT HOSPITALIZATION AND WAS RELEASED THE NEXT DAY (12-7-95). ALL FOUR EMPLOYEES RECEIVED DRUG TESTS WITHIN 32 HOURS. AT THIS TIME, THE LAB HAS THE SAMPLES AND THE RESULTS SHOULD BE RETURNED TO THE MRO NEXT WEEK. INCIDENT WAS REPORTED TO DOT AT 3:00 P.M., 12-6-95, BY RICHARD T. LAWSON, MANAGER. REPORT #3163240.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19950166 | 1995-12-22 | 19235 | TEXAS EASTERN GAS PIPELINE CO | EAST CAMERON BLOCK 263 |  | LA |  | 7.41 | 391 + 25 | 550 | 1995-11-23 |  | YES | EC | 263 | LA | YES | NO | OTHER | 0 | 0 | 0 | 250000 | 183326.3773 | 399380.9126 | Null | 0 | 0 |  | 19951123 | 1210 | 1440 | BY TEST | 2290 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: REDUCER, GIRTH; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1994; NMDIA: 6; THK: 0.43; SPEC: API-5L; SMYS: 35000; MANU: NOT AVAILABLE; MANYR: 0; LOCLK: UNDER WATER; PNAME: DWAYNE TESCHENDORF; PHONE: 7136275573; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | OCCURRED IN OUTER CONTINENTAL SHELF, OFFSHORE LOUISIANA. A SHRIMPING NET PULLED A PRODUCER'S 6" LATERAL LOOSE FROM TEXAS EASTERN'S 30" LINE 41-A-7 TAP ASSEMBLY CAUSING A LOSS OF NATURAL GAS IN LINE 41-A-7.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960001 | 1996-01-03 | 20211 | UNITED CITIES GAS CO | MURFREESBORO | RUTHERFORD | TN |  | 4.35 |  | 930 | 1995-12-13 | 3 | NO |  |  |  | Null | NO | RUPTURE | 0.5 | 0 | 0 | 25000 | 18332.6377 | 39938.0913 | YES | 1 | 30 |  | 19951213 | 425 | 550 | BY TEST | 825 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: OTHER; PRTFO: NOT GIVEN; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1952; NMDIA: 4; THK: 1.45; SMYS: 0; MANYR: 0; LOCLK: UNDER GROUND; PNAME: CONRAD A. BARGER JR.; PHONE: 6153735310; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19951110; MARK: YES; MRKTP: TEMPORARY STAKES; STAT: YES; CTEST: Null | SECTION OF PIPE DAMAGED WAS NOT MARKED. SECTION THAT WAS DAMAGED WAS STUBOUT LEFT FROM LAST RELOCATION TO SERVE FARM TAP. WAS NOT MARKED BY LOCATOR. HE WAS NOT AWARE OF THIS SECTION. TRACK-HOE HIT 4" STEEL LINE CAUSING LINE CUT.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960002 | 1996-01-04 | 288 | ALGONQUIN GAS TRANSMISSION CO | NORTH ATTLEBORO | BRISTOL | MA | 02760 | 13.49 G-1 SYS. | 712 +17 | 1330 | 1995-12-09 | 2 | NO |  |  |  | Null | NO | RUPTURE | 3.5 | 0 | 0 | 320000 | 234657.7629 | 511207.5682 | Null | 1 | 42 |  | 19951209 | 510 | 750 | BY TEST | 1506 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1953; NMDIA: 16; THK: 0.31; SPEC: API 5L; SMYS: 42000; SEAM: EW; MANU: YOUNGSTOWN; MANYR: 1952; LOCLK: UNDER GROUND; PNAME: ANDREW G. DAVIDSON; PHONE: 6175601496; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19951006; MARK: YES; MRKTP: PERM.MRKRS & TEMP.STAKES; STAT: YES; CTEST: Null | GENERAL AREA OF INCIDENT WAS ON-GOING SHOPPING CENTER DEVELOPMENT. AT TIME OFINCIDENT OPERATOR WAS GRADING ADJACENT TO ROW UNDER CONTRACTOR DIRECTION. EQUIPMENT OPERATOR DECIDED ON HIS OWN TO EXTEND WORK INTO ROW. AGREED UPON NOTIFICATION WAS NOT GIVEN TO ALGONQUIN FOR APPROVAL OF GRADING AND DISPATCH OF STAND-BY PERSONNEL. PIPELINE STRUCK AND RUPTURED BY DOZER EQUIPPED WITH RIPPERDURING UNAUTHORIZED GRADING OPERATION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960008 | 1996-01-24 | 2616 | COLUMBIA GAS TRANSMISSION CORP | SMITHFIELD | MONROE | PA | 18360 | LINE 1278 | 5948 + 17 | 1635 | 1996-01-06 | 2 | NO |  |  |  | Null | NO | RUPTURE | 25 | 0 | 0 | 50000 | 35989.3486 | 78403.6597 | Null | 0 | 45 |  | 19960106 | 1075 | 1200 | BY TEST | 1807 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1948 | 14 | 0.31 | API 5LX | 45000 | SEAMLESS |  | NATIONAL TUBE USS | 1947 | UNDER GROUND |  | S.J. CHOBY | 3043572349 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | BARE | YES | 1970 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | THERE ARE INDICATIONS THAT CATHODIC PROTECTION CURRENT SHIELDING FROM SHALE ROCK RESULTED IN LOCALIZED PITTING AND PIPE WALL LOSS TO A POINT WHERE A COMBINATION OF DUCTILE AND BRITTLE FRACTURES OCCURRED RESULTING IN A RUPTURE OF THE PIPE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960009 | 1996-01-18 | 2564 | COLORADO INTERSTATE GAS CO |  | ELBERT | CO | 80828 |  | 8791 + 50 | 1245 | 1995-12-21 | 1 | NO |  |  |  | Null | NO | RUPTURE | 133 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 15 |  | 19951222 | 800 | 920 | BY TEST | 1014 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1951 | 20 | 0.25 | API 5LX | 52000 | ERW |  | YOUNGSTOWN | 1951 | UNDER GROUND |  | RICHARD H. FLINT | 7194204350 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL |  | YES | 19820527 | GAS |  | 8 | 1014 | MATERIAL DEFECT IN PIPE DUE TO FAULTY MANUFACTURING PROCESS. CIG'S PIPELINE NO. 2B-20" RUPTURED AT 12:45PM ON 12/21/95 IN RURAL EASTERN COLORADO. THE RUPTURE EXTENDED FOR APPROXIMATELY 133 FEET ALONG THE PIPE; ESCAPING NATURAL GASDID NOT IGNITE. THERE WERE NO INJURIES TO EMPLOYEES OR THE MEMBERS OF THE PUBLIC, AND NO SIGNIFICANT PROPERTY DAMAGE OCCURRED. ALSO, THERE WAS NO INTERRUPTION OF SERVICE TO ANY CUSTOMERS. EXAMINATION OF THE FAILURE SITE, AND PRELIMINARY METALLURGICAL ANALYSIS OF PIECES OF THE FAILED PIPE, DETERMINED THAT THEFRACTURE ORIGINATED IN THE BODY OF THE PIPE AT A LAMINATION IN THE PIPE WALL. A SUPPLEMENTARY REPORT WILL BE SUBMITTED IF THE FINAL METALLURGICAL ANALYSIS INDICATES A DIFFERENT CAUSE OF FAILURE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960018 | 1996-01-25 | 18516 | SOUTHERN NATURAL GAS CO | MAIN PASS BLOCK 151 |  | LA |  | 5.358 ON MAINBLOCK 72 P/L |  | 1000 | 1995-12-10 |  | YES | MAIN PASS | 151 | LA | YES | NO | OTHER | 0 | 0 | 0 | 280000 | 205325.5426 | 447306.6221 | Null | 0 | 0 |  | 19951210 | 925 | 1728 | BY TEST | 2160 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: MECHANICAL JOINT; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1980; NMDIA: 6.63; THK: 0.38; SMYS: 35000; MANYR: 0; LOCLK: UNDER WATER; PNAME: TED MCLANAHAN; PHONE: 5046826212; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; DMGO: UNDERWATER MUDSLIDE; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | MUDSLIDE AT TIE-IN OF MAIN PASS BLOCK 72 PIPELINE IN MAIN PASS BLOCK 151 SEPARATED "BREAKWAY" JOINT. TAP COORDINATES ARE 2911.6, 8,852.6.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960019 | 1996-01-31 | 20230 | KOCH GATEWAY PIPELINE COMPANY |  | PANOLA | TX |  | 17.8 | 939+ 78 | 1105 | 1996-01-07 | 1 | NO |  |  | TX | Null | NO | RUPTURE | 32 | 0 | 0 | 138035 | 99355.7948 | 216448.9833 | Null | 2 | 55 |  | 19960107 | 695 | 800 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | LONG | STEEL |  | PIPELINE |  | 1947 | 20 | 0.31 | API 5LX | 46000 | ELEC. RES. WELD |  | YOUNGSTOWN | 1947 | UNDER GROUND |  | WARREN FUSILIER | 3168286969 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | SEE COMMENTS | Null |  | NO DATA |  | 0 | 0 | THE CAUSE OF THE RUPTURE HAS NOT YET BEEN CONFIRMED. THE PIPE IS TO BE ANALYZED BY METTALLURIGICAL CONSULTANTS INC. SINCE THE RUPTURE OCCURRED IN THE LONGITUDINAL SEAM OF THE PIPE, A MATERIAL DEFECT IS SUSPECTED. A SUPPLEMENTAL REPORT WILL BE FILED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960020 | 1996-02-02 | 809 | ARCO PIPE LINE CO | JONES CREEK | BRAZORIA | TX | 77541 | 0 |  | 1515 | 1995-12-22 | 1 | NO |  |  | TX | Null | NO | RUPTURE | 9 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 30 |  | 19951223 | 250 | 0 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1976; NMDIA: 24; THK: 0.31; SPEC: X-60; SMYS: 0; MANYR: 0; LOCLK: UNDER GROUND; PNAME: ROBERT H. GLAZE; PHONE: 7139865339; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: NO; MARK: Null; MRKTP: 0; STAT: NO; CTEST: Null | WEATHER CONDITIONS INCLUDING MUD AND WATER, QUESTIONABLE INTERGITY OF EXISTING UNDERGROUND PIPING (CONDUCTING TEST) LOCATION OF BARRICADE FENCE, DRESSER TD-4 H DOZER
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960021 | 1996-01-31 | 26330 | ENOGEX INC (EX. MUSTANG FUEL CORP) | OKLAHOMA | OKLAHOMA | OK |  |  |  | 800 | 1996-01-12 | 3 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 30 |  | 19960112 | 0 | 350 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: FILLET; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1949; NMDIA: 12.75; THK: 0.22; SPEC: GRADE B; SMYS: 35000; SEAM: ERW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: STEVEN B. RUSHING; PHONE: 4055575235; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: LINE MARKERS IN PLACE; STAT: YES; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960031 | 1996-02-14 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA | BEECHER | FAYETTE | IL | 60401 | LATERAL #9 | 00+0 | 1215 | 1996-01-14 | 1 | NO |  |  |  | Null | NO | RUPTURE | 25.5 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 30 |  | 19960114 | 1096 | 1675 | BY TEST | 2436 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1967 | 8 | 0.2 | 5LX52 | 52000 | ERW |  | YOUNGSTOWN | 1966 | UNDER GROUND |  | F ROY FLEET | 7086913786 | INTERNALLY | OTHER | SEAM CORROSION | OTHER | SOUR GAS LIQUIDS | COATED | YES | 1967 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | UNDER INVESTIGATION. WILL BE FILING SUPPLEMENTAL. SUPPLEMENTAL RECEIVED 4/22/96 INDICATES CHANGE IN CAUSE FROM OTHER TO CORROSION. PIPE WAS USED UNDER CONDITIONS WHERE GAS WAS WET. THIS PROMOTED INTERNAL CORROSION OF THE LONGITUDINAL SEAM.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960032 | 1996-02-12 | 18516 | SOUTHERN NATURAL GAS CO | BAYOU | JEFFERSON | LA |  | 0.5 ON 8" |  | 20 | 1996-01-10 | 1 | NO |  |  |  | Null | NO | RUPTURE | 3 | 0 | 0 | 372000 | 267760.7538 | 583323.2282 | Null | 2 | 0 |  | 19960110 | 750 | 1035 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1957; NMDIA: 8.63; THK: 0.25; SPEC: API,5LX; SMYS: 42000; SEAM: ERW; MANU: AMERICAN MANNEX; MANYR: 1957; LOCLK: UNDER WATER; PNAME: TED MCLANAHAN; PHONE: 5046826212; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | PIPELINE RUPTURED AND GAS IGNITED. CAUSE UNKNOWN AT THIS TIME. SUPPLEMENTALREPORT FILED 6/10/1996 UPDATES CAUSE TO DAMAGE BY OUTSIDE FORCES, ANDINCREASES PROPERTY DAMAGE TO $372,000, PER ERIC E. THOMAS. COMMENTS STATETHAT ALTHOUGH THE CAUSE OF THE RUPTURE IS NOT KNOWN TO A HIGH DEGREE OFCERTAINTY, SCARRING INDICATES THE LIKELIHOOD THAT THE PIPE WAS STRUCK BY ANEXTERNAL SOURCE AT SOME TIME IN THE PAST, PRODUCING A STRESS RISER THATULTIMATELY RESULTED IN FAILURE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960033 | 1996-02-12 | 19270 | TEXAS GAS TRANSMISSION CORP | GREENVILLE | WASHINGTON | MS |  | VALVE 11B-34 | R1E,T17N | 2026 | 1996-01-12 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 104000 | 74857.8451 | 163079.6122 | Null | 1 | 29 |  | 19960115 | 747 | 674 | BY TEST | 1049 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: RELIEF VALVE; MLKD: STEEL; PRTSY: OTHER; PRTSO: RELIEF VALVE; PRTYR: 1992; NMDIA: 26; THK: 0.28; SPEC: API 6D; SMYS: 1440; VALVE: BALL; MANU: WKM; MANYR: 1992; LOCLK: ABOVE GROUND; PNAME: SCOTT D. CUTLIP; PHONE: 5026886681; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | ON JANUARY 12, 1996, AT APPROXIMATELY 8:26 P.M. A RELIEF VALVE LOCATED APPROXIMATELY 10 MILES SOUTH OF GREENVILLE, MISSISSIPPI, OPENED ON TEXAS GAS 26-INCH, NO.1 LINE. THE RELIEF VALVE IS INSTALLED TO PROVIDE OVERPRESSURE PROTECTION ON TWO SECTIONS OF THE 26-INCH LINE THAT HAVE AN MAOP OF 674 PSIG. THESE TWO SECTION ARE LOCATED FROM MILE 110.35 TO 111.74 AND MILO 113.52 TO 113.90 ON TEXAS GAS MAINLINE SYSTEM. PIPE MATERIAL SPECIFICATIONS IN THESE SECTIONS ARE A.O. SMITH, 26" O.D. X 0.282" W.T. GRADE X-52. THE RELIEF VALVE IS LOCATEDIN A RURAL AREA AT MILE 104.3 AND HAS A SET PRESSURE OF 741 PSIG (10% ABOVE MAOP). CALCULATED CAPACITY OF THE WKM RELIEF VALVE IS 35.7 MMCF/H. THE FOLLOWING IS A SUMMARY OF EVENTS THAT RESULTED IN ACTIVATION OF THE RELIEF VALVE. 4:00 PM-TEXAS GAS PERSONNEL AT CLARKSDALE COMPRESSOR STATION (MILE 171) REPORTED TO GAS CONTROL IN OWENSBORO, KENTUCKY THAT THE STATION'S GENERAL ELECTRIC TURBINE HAD SHUT DOWN. 5:00 PM SINCE THEY WERE UNABLE TO RESTART THE TURBINE AS ANTICIPATED, PERSONNEL AT CLARKSDALE STATION NOTIFIED GAS CONTROL OF THAT FACT AND INFORMED GAS CONTROL THAT ADDITIONAL PERSONNEL WERE ENROUTE TO ASSIST. GAS CONTROL RELAYED THIS INFORMATION TO PERSONNEL AT GREENVILLE AND LAKE CORMORANT STATIONS AND ADVISED TO ADJUST OPERATING CONDITITONS ACCORDINGLY. 5:47 PM GAS CONTROL RECEIVED A HIGH PRESSURE ALARM OF 675 PSIG INDICATING THAT THE 674 PSIG MAOP ON TWO SECTIONS OF THE 26-INCH, NO.1 LINE HAD BEEN EXCEEDED. 8:05 PM. ALTHOUGH ENCOUNTERING UNEXPECTED PROBLEMS, CLARKSDALE PERSONNEL CONTINUED IN THEIR EFFORTS TO RESTART THE GENERAL ELECTRIC TURBINE WHILE ADDITIONAL CLARKSDALE PERSONNEL WERE WORKING TO BRING A PRATT & WHITNEY TURBINE ON LINE. 8:26 PM GAS CONTROL RECEIVED AN ALARM INDICATING THAT THE RELIEF VALVE AT MILE 104.3 HAD OPENED. A TEXAS GAS EMPLOYEE WAS SENT TO THE RELIEF VALVE SITE. 9:20 PM CLARKSDALE PERSONNEL REPORTED TO GAS CONTROL THAT THE PRATT & WHITNEY TURBINE HAD BEEN SUCCESSFULLY STARTED. 9:55 PM GAS CONTROL NOTIFIED BY THE FIELD THAT THE RELIEF VALVE AT MILE 104.3 WAS CLOSED. 1O:45 PM GAS CONTROL RECEIVED SYSTEM NOTIFICATION THAT PRESSURE ON THE 26-INCH, NO.1 LINE HAD FALLEN BELOW THE MAOP OF 674 PSIG. THIS EVENT RESULTED IN A CALCULATED GAS LOSSOF 43.3 MMCF AT AN ESTIMATED COST OF $104,000.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960034 | 1996-02-15 | 19730 | TRUNKLINE GAS CO | WAKARUSA | ST JOSEPH | IN | 46573 | VS 137-1 | 416 + 90 | 725 | 1995-12-26 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 100000 | 73330.5509 | 159752.3651 | Null | 3 | 20 |  | 19951226 | 751 | 900 | BY TEST | 990 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | GIRTH | STEEL |  | PIPELINE |  | 1960 | 26 | 0.31 | API 5LX-52 | 52000 | DSAW |  | REPUBLIC | 1959 | UNDER GROUND |  | ROBERT A. MOODY | 7136275716 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION | GIRTH WELD | YES |  | GAS |  | 24 | 990 | DURING THE REMOVAL OF THE FAILED WELD, THE PIPE SEPARATED VERTICALLY BY SEVERAL INCHES NECESSITATING ADDITIONAL EXCAVATION FOR LINE UP SO AS TO MINIMIZE FUTURE RESIDUAL STRESS. GIRTH WELD FRACTURED FROM 9:00 TO 3:00 POSITION. PIPELINE APPEARED TO BE UNDER HIGH RESIDUAL STRESS AT WHAT MAY HAVE BEEN A ROAD CROSSING (CASED, NOT SHORTED) TIE-IN DURING ORIGINAL CONSTRUCTION.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960035 | 1996-02-20 | 20230 | KOCH GATEWAY PIPELINE COMPANY | BAY ST. LOUIS | HANCOCK | MS | 39520 | 13.13 | 531 + 77 | 1400 | 1996-01-13 | 1 | NO |  |  | MS | Null | NO | OTHER | 0 | 0 | 0 | 125000 | 89973.3716 | 196009.1493 | Null | 36 | 0 |  | 19960113 | 195 | 230 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1948; NMDIA: 4.63; THK: 0.24; SPEC: B; SMYS: 0; SEAM: SEAMLESS; MANU: US STEEL; MANYR: 0; LOCLK: UNDER WATER; PNAME: F.T. WALDROP; PHONE: 6018329351; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; STAT: Null; CTEST: Null | PIPELINE WAS FOUND TO BE KINKED WITH A LARGE BOAT ANCHOR BENEATH THE PIPELINE. DAMAGE APPEARS TO HAVE BEEN CAUSED BY THE PIPELINE BEING HOOKED AND LIFTEDBY A LARGE BOAT ANCHOR. THE ANCHOR WAS ABANDONED AND IN CLOSE CONTACT WITH PIPELINE. THE PIPELINE WAS INDENTED BY ANCHOR RESULTING IN A LEAK.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960036 | 1996-02-20 | 19160 | TENNESSEE GAS PIPELINE CO | EUGENE ISLAND BLOCK 18 |  | LA |  | 519A - 101+19.11 |  | 250 | 1996-01-18 |  | YES | EI | 18 | LA | Null | NO | RUPTURE | 4 | 0 | 0 | 200000 | 143957.3945 | 313614.6388 | Null | 2 | 40 |  | 19960118 | 1100 | 1256 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1959; NMDIA: 10.75; THK: 0.28; SPEC: 5LX; SMYS: 52000; SEAM: SEAMLESS; MANU: LONE STAR; MANYR: 1959; LOCLK: UNDER WATER; PNAME: ALBERT T. RICHARDSON; PHONE: 7137574292; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | EVIDENCE INDICATES UNKNOWN OUTSIDE PARTY DAMAGED PIPE SEVERAL YEARS PRIOR TOTHE RUPTURE. SHELL PLATFORM AT E.I. - 18 CALLED GAS CONTROL AT 2:50 PM TO REPORT PRESSURE DROP FROM 1100 T0 200 PSI - ALSO LARGE BALL OF FIRE 2-5 MILES NEOF PLATFORM. D524 BEGAN CHECKING PRESSURES, ETC. AT 3:15 AM VERIFIED THAT SHELL E.I. 18 HAD BEEN SHUT IN AND 5194-102 MLV CLOSED, ADDITIONAL PRODUCERS WILL HAVE TO BE SHUT IN - UNMANNED PLATFORMS AND WELLS. NO LIQUIDS SUSPECTED INLINE. INVOLVED-PIPE HAD SCRAPES AND GOUGES COVERED BY BARNACLES.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960037 | 1996-02-22 | 405 | ANR PIPELINE CO |  | CAMERON | LA |  | 36.28 |  | 1908 | 1996-01-19 | 1 | NO |  |  | LA | Null | NO | LEAK | 0 | 0 | 0 | 420000 | 302310.5285 | 658590.7415 | Null | 1 | 25 |  | 19960119 | 165 | 175 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: TURBINE ENGINE; MLKD: OTHER; MLKDO: ALUMINUM; PRTSY: COMPRESSOR STATION; PRTYR: 1967; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: DONALD E. CROSS; PHONE: 3134962460; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | THE ACCIDENTAL OVERTEMPERATURE OF LUBE OIL AND FUEL VALVE COMPONENTS BY THE BACKFLOW OF 900 DEGREE F. EXHAUST GASES DUE TO A FRACTURED 6TH STAGE BLEED AIRVALVE OUTLET FLANGE. EXHAUST GAS ESCAPING FROM THE 6TH STAGE BLEED AIR VALVEOUTLET DUCT IMPINGED ON A FUEL GAS VALVE. THE HOT TURBINE EXHAUST MELTED THESEALS ON THE FUEL VALVE RESULTING IN A RELEASE OF GAS AND IGNITION. THETURBINE EXHAUST, WHICH WAS THE SOURCE OF IGNITION, WAS AT A TEMPERATURE ABOVETHE AUTO IGNITION OF NATURAL GAS.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19960038 | 1996-02-29 | 13750 | NORTHERN NATURAL GAS CO (ENRON) | PAMPA | ROBERTS | TX | 79066 | STA.P3 |  | 1130 | 1996-01-26 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 1 |  | 19960126 | 0 | 0 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: OPEN JOINT; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 0; NMDIA: 24; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: JOHN WM. CASKEY; PHONE: 7136467343; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | WELDER ASSISTING DURING TACK WELDING OF 24" END CAP. WELDING ARC CAUSED ANDIGNITION. WELDER WAS HIT BY MOVING END CAP. CAUSE LISTED AS IGNITION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960049 | 1996-02-21 | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | NEW YORK | NEW YORK | NY | 10010 |  |  | 1355 | 1996-01-23 | 4 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19960123 | 280 | 350 | BY TEST | 525 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: FITTING; PRTFO: COUPLING; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1965; NMDIA: 16; THK: 0.38; SPEC: API 5L GRADE B; SMYS: 0; MANU: U.S. TESTING; MANYR: 1965; LOCLK: UNDER PAVEMENT; PNAME: RANDY F. GOFFRED; PHONE: 2124602838; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: EXTERNAL LOADING; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | STEEL BEAM FOUND IN CONTACT WITH TOP BRACE USED FOR REINFORCEMENT OF A COMPRESSION COUPLING.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960050 | 1996-03-04 | 2616 | COLUMBIA GAS TRANSMISSION CORP | PERRY TOWNSHIP | LAWRENCE | OH | 45680 |  | 4518 + 23 | 1547 | 1996-02-18 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | Null | 1 | 30 |  | 19960218 | 763 | 900 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1948; NMDIA: 20; THK: 0.31; SPEC: API 5L; SMYS: 42000; SEAM: SEAMLESS; MANU: USS NATIONAL TUBE; MANYR: 1948; LOCLK: UNDER GROUND; PNAME: S.J. CHOBY; PHONE: 3043572349; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | FAILURE SITE EVALUATION DETERMINED THAT A BRITTLE FRACTURE OCCURRED AT A WRINKLE BEND. THE RELEASE OF GAS IGNITED RESULTING IN MINIMAL COLLATERAL DAMAGE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960051 | 1996-03-04 | 602 | NORAM GAS TRANSMISSION | FAULKNER |  | AR |  |  | 6522 + 73 | 500 | 1996-02-04 | 1 | NO |  |  |  | Null | YES | LEAK | 0 | 0 | 0 | 50000 | 35989.3486 | 78403.6597 | Null | 0 | 50 |  | 19960204 | 340 | 501 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1955; NMDIA: 12; THK: 0.25; SPEC: X-46; SMYS: 48000; MANYR: 0; LOCLK: UNDER GROUND; PNAME: WALTER L. FERGUSON; PHONE: 3184293210; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: POWER LINES; NOTIF: Null; MARK: YES; MRKTP: EXISTING MAKERS, ROAD CRO; STAT: Null; CTEST: Null | POWER LINE BREAK AT A ROAD CROSSING (HWY 50) DROPING ON TO NORAM VENT PIPE CAUSING AN ELECTRICAL CONNECTION WHICH ARCED FROM THE BURIED CASING ONTO THE CARRIER PIPE. THE ARCING BURNED THROUGH THE PIPE WALL CAUSING A LEAK WHICH IGNITED. THE FLAMES WERE RISING OUT OF OUR VENT PIPE ON ONE SIDE CAUSING THE HWYTO BE CLOSED AND THE LINE TO BE SHUTIN.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19960052 | 1996-03-04 | 30012 | ARAN ENERGY CORPORATION | OFFSHORE PLAQUEMIENS PAR. |  | LA |  |  |  | 700 | 1995-10-05 |  | YES | SP | 37 |  | YES | NO | RUPTURE | 12.5 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 0 |  |  | 0 | 0 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: OTHER; MLKDO: NOT GIVEN; PRTSY: PIPELINE; PRTYR: 1961; NMDIA: 8.63; THK: 500; SMYS: 0; SEAM: ERW; MANYR: 1961; LOCLK: UNDER WATER; PNAME: SCOTT RICKS; PHONE: 7137590176; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | GAS LINE WAS SEVERED DURING AN APPARENT MUD SLIDE CAUSED BY HURRICANE OPAL.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960053 | 1996-03-06 | 18516 | SOUTHERN NATURAL GAS CO | MAIN PASS BLOCK 151 |  | LA |  | 2.072 ON MAIN PASS BLOCK |  | 1610 | 1996-02-06 |  | YES | MP | 151 |  | NO | NO | OTHER | 0 | 0 | 0 | 50000 | 35989.3486 | 78403.6597 | Null | 0 | 5 |  | 19960206 | 1000 | 1730 | BY TEST | 2163 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: MECHANICAL JOINT; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1984; NMDIA: 10.75; THK: 0.5; SMYS: 42000; SEAM: SEAMLESS; VALVE: MECHANICAL JOIN; MANU: BIMS; MANYR: 1984; LOCLK: UNDER WATER; PNAME: TED MCLANAHAN; PHONE: 5046826212; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19960201; MARK: YES; MRKTP: SURVEY DATA BASE; STAT: NO; CTEST: Null | 4 POINT DIVE BOAT WAS WORKING TO REPAIR AN ADJACENT P/L. WHILE SETTING ANCHORS, ONE OF THE ANCHOR CABLES SNAGGED VALVE IN MAIN PASS 77 LINE AND PULLED P/L APART AT A LOAD LIMITING CONNECTOR NEAR VALVE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960054 | 1996-03-08 | 30008 | THREE RIVERS PIPELINE | WEST MIFFLIN BORO | ALLEGHENY | PA |  | 268.2 | 14184 + 00 | 1800 | 1996-02-08 | 3 | NO |  |  |  | Null | Null | RUPTURE | 1 | 0 | 0 | 31400 | 22601.3109 | 49237.4983 | YES | 1 | 0 |  | 19960209 | 650 | 1030 | BY TEST | 1584 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1946; NMDIA: 8.63; THK: 0.32; SPEC: GRADE B; SMYS: 0; SEAM: SEAMLESS; MANYR: 0; LOCLK: UNDER GROUND; PNAME: ALAN R. BARKER; PHONE: 4123275420; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; DMGO: SETTLEMENT OF DITCHLINE; NOTIF: Null; MARK: Null; STAT: NO; CTEST: Null | INCIDENT OCCURED APPROX 6 YEARS AFTER 3RD PARTY DAMAGE. DENT REDUCED WALL THICKNESS TO 0.200". IN ADDITION, POSSIBLE SETTLING STRESSES ASSOCIATED WIT IMPROPER SUPPORT AND THERMAL EXPANSION MAY HAVE CONTRIBUTED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960055 | 1996-03-21 | 4060 | EAST OHIO GAS CO | WARREN TOWNSHIP | TUSCARAWAS | OH |  | 3107 + 31 |  | 1750 | 1996-02-22 | 1 | NO |  |  |  | Null | NO | RUPTURE | 10 | 0 | 0 | 200000 | 143957.3945 | 313614.6388 | Null | 6 | 0 |  | 19960223 | 267 | 256 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1910; NMDIA: 18; THK: 0.31; SMYS: 0; MANYR: 0; LOCLK: UNDER GROUND; PNAME: ROBERT J. BRADACH; PHONE: 2167366872; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | A BLOCKAGE OCCURRED IN TRANSMISSION PIPELINE (TPL) #5 DUE TO THE FREEZE-UP OF LIQUIDS WHICH HAD ACCUMLATED IN THE LINE. AS A RESULT OF THE BLOCKAGE, THE UPSTREAM SECTION OF THIS PIPELINE OVER-PRESSURIZED, AND A RUPTURE OCCURRED ATPIPE STATION 3107+31.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960061 | 1996-03-29 | 2620 | COLUMBIA GULF TRANSMISSION CO | GULF OF MEXICO |  | LA |  | X=1,876,833.16FT | Y=134,041.15FT | 730 | 1996-02-26 |  | YES | EI | 309-C |  | YES | NO | LEAK | 0 | 0 | 0 | 50000 | 35989.3486 | 78403.6597 | Null | 0 | 0 |  | 19960226 | 1100 | 1250 | BY TEST | 2000 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | FITTING | SWIVEL FLANGE | OTHER | MICARTA RING | OTHER | OFFSHORE PLATFORM | 1969 | 26 | 0.56 | API 5L | 52000 | SEAMLESS | FLANGE (ASA 600 | UNKNOWN | 0 | OTHER | ABOVE WATER | S.J. CHOBY | 3043572349 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | SWIVEL FLANGE 26" TRJ ASA 600 | YES | 19690828 | WATER |  | 4 | 2000 | A MICARTA RING WAS REPLACED WITH A STAINLESS STEEL RING AND THE PIPELINE WASRETURNED TO SERVICE. A LEAK WAS DISCOVERED AT A SWIVEL FLANGE CONNECTING THESUB-SEA PIPELINE TO THE OFFSHORE PLATFORM
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960062 | 1996-03-25 | 30769 | MISSOURI GAS ENERGY | KANSAS CITY | JACKSON | MO | 66131 | LINE MARKER 2346 |  | 152 | 1996-02-26 | 3 | NO |  |  |  | Null | NO | RUPTURE | 5 | 0 | 0 | 60000 | 43187.2184 | 94084.3916 | YES | 1 | 58 |  | 19960226 | 252 | 235 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1961; NMDIA: 26; THK: 0.31; SPEC: HOOP YIELD 57000; SMYS: 20000; SEAM: ELECTRIC FLASH; MANU: YOUNGSTOWN STEEL; MANYR: 1961; LOCLK: UNDER GROUND; PNAME: WILLIAM R. DEAN; PHONE: 8163605673; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PERMANENT MARKER; STAT: YES; CTEST: Null | AN 18" CLAY TILE STORM SEWER HAD BEEN INSTALLED ACROSS THE TOP OF THE 26" GAS LINE AT THE POINT OF RUPTURE. INSTALLATION DATE OF THE STORM SEWER UNKNOWN.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960063 | 1996-03-29 | 18516 | SOUTHERN NATURAL GAS CO | HEFLIN | CLEBURNE | AL | 36264 | 403.328 N. MAIN PIPELINE |  | 1920 | 1996-02-28 | 1 | NO |  |  |  | Null | Null | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 17 |  | 19960228 | 450 | 1003 | BY TEST | 1181 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | TRANSMISSION SYSTEM | OTHER | NOT GIVEN | OTHER | NOT GIVEN | OTHER | PIPELINE GATE VALVE SETT | 1986 | 20 | 0.28 | API 5LX | 60000 | ERW | BALL | GROVE | 1986 | ABOVE GROUND |  | JAMES F. JOHNSON | 2058311131 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 | NO |  |  | Null | [5 empty] | VANDALS CUT LOCKED CHAINS OFF OF THE OPERATORS FOR THE 20" TALLAPOOSA GATE BLOCK VALVE AND THE TWO 6" BLOWOFF VALVES LOCATED ON EITHER SIDE OF THE BLOCK VALVE. THE VANDAL'S DID NOT ALTER THE POSITION OF THE 20" VALVE, WHICH WAS OPEN, BUT DID OPEN THE 6" BLOWOFF VALVES WHICH WERE PREVIOUSLY IN THE CLOSED POSITION. PRIOR TO OPENING THE 6" VALVES, SMALL THREADED VENT PLUGS LOCATED BETWEEN THE BLOWOFF CAP CLOSURE FITTINGS AND THE VALVES WERE REMOVED. THIS ALLOWED NATURAL GAS TO ESCAPE TO THE ATMOSPHERE THROUGH THE SMALL VENTS AT A PRESSURE OF 450 PSIG AFTER THE BLOWOFF VALVES WERE OPENED. THE VANDALS POURED GASOLINE ON THE GROUND FROM THE BLOWOFFS TO THE EDGE OF A COUNTY ROAD CREATING A TRAIL TO ACT AS A "FUSE" FOR A DISTANCE OF ABOUT 60 FEET. THE GASOLINE TRAIL WAS IGNITED; CAUSING A SMALL GRASS FIRE UP TO THE BLOWOFFS. IT APPEARED THAT THE VANDAL'S INTENT WAS TO CREATE A NATURAL GAS EMERGENCY, BUT THE NATURAL GAS,BEING LIGHTER THAN AIR, NEVER IGNITED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960077 | 1996-04-16 | 405 | ANR PIPELINE CO | EUGENE ISLAND |  | LA |  |  | X=1922,669.85 Y=213,023.3 | 1517 | 1996-03-19 |  | YES | EUGENE ISLAND | 42 |  | YES | NO | LEAK | 0 | 0 | 0 | 75000 | 53984.0229 | 117605.4896 | Null | 0 | 45 |  | 19960319 | 905 | 1300 | BY TEST | 1646 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | GIRTH | STEEL |  | PIPELINE |  | 1985 | 6 | 0.31 | API-5L | 35000 | ERW |  | LING TIMKO VOUGHT | 1985 | UNDER WATER |  | DONALD E. CROSS | 3134962460 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION |  | YES | 19850825 | WATER |  | 24 | 1646 | ONE-INCH WIDE CRACK IN A GIRTH WELD RUNNING FROM THE 12'OCLOCK POSITION TOTHE 8 O'CLOCK POSITION. THE APPARENT CAUSE WILL NOT BE DETERMINED UNTIL AFTERTHE 30 DAY DEADLINE FOR REPORTING - A SUPPLEMENTAL REPORT WILL FOLLOW.SUPPLEMENTAL REPORT RECEIVED 2/21/96 INDICATES CHANGE IN CAUSE FROM OTHER TOCONSTRUCTION/MATERIAL DEFECT (C).
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960081 | 1996-05-13 | 14211 | ONG TRANSMISSION CO | NORMAN | CLEVELAND | OK | 73069 |  |  | 1045 | 1996-04-13 | 1 | NO |  |  | OK | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 3 | 10 |  | 19960413 | 450 | 550 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: OTHER; PRTFO: ONE-INCH SERVICE; MLKD: STEEL; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1981; NMDIA: 1; THK: 0.13; SPEC: A-25; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: GERRY LYNN; PHONE: 9185887600; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: CAR ACCIDENT; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | HIGH SPEED VEHICLE ACCIDENT RESULTED IN ONE VEHICLE STRIKING METER AND REGULATOR SETTING. HIGH SPEED VEHICLE ACCIDENT RESULTED IN FOUR FATALITIES. ONE OFTHE VEHICLES HIT THE METER SETTING CAUSING GAS LEAK AND FIRE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960082 | 1996-05-28 | 5304 | FLORIDA GAS TRANSMISSION CO | FT. MEADE | POLK | FL |  | 5.594 | 295+40 | 1100 | 1996-04-29 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 69000 | 49665.3011 | 108197.0504 | Null | 1 | 50 |  | 19960430 | 750 | 1014 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1994; NMDIA: 12; THK: 0.19; SPEC: API-5L; SMYS: 60000; SEAM: ERW; MANU: STUPP; MANYR: 1994; LOCLK: UNDER GROUND; PNAME: MERLIN MOSEMAN; PHONE: 7136467344; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: Null; STAT: Null; CTEST: Null | PIPELINE HIT BY THIRD PARTY WITH BACKHOE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960090 | 1996-06-03 | 5304 | FLORIDA GAS TRANSMISSION CO | HOMESTEAD | DADE | FL |  | 4.39 | 232 + 05 | 1510 | 1996-05-06 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 116000 | 83495.2888 | 181896.4905 | Null | 2 | 10 |  | 19960506 | 650 | 975 | BY TEST | 1463 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1985; NMDIA: 6; THK: 0.19; SPEC: API-5L; SMYS: 35000; SEAM: ERW; MANYR: 1984; LOCLK: UNDER GROUND; PNAME: MERLIN MOSEMAN; PHONE: 7136467344; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19960423; MARK: YES; MRKTP: PAINT; STAT: YES; CTEST: Null | PIPELINE HIT BY THIRD PARTY WITH POST HOLE AUGER.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960091 | 1996-06-04 | 19160 | TENNESSEE GAS PIPELINE CO | PEABODY | ESSEX | MA | 01960 | 270C - 103 + 0.89 |  | 1300 | 1996-05-03 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 80000 | 57582.9578 | 125445.8555 | Null | 3 | 54 |  | 19960503 | 563 | 730 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1951; NMDIA: 8.63; THK: 0.25; SPEC: 02; SMYS: 42000; MANU: 08 JONES LA; MANYR: 0; LOCLK: UNDER GROUND; PNAME: LORI L. SCHULTZ; PHONE: 7137577805; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: VENT MARKING AT RAILROAD; STAT: YES; CTEST: Null | A THIRD PARTY CONTRACTOR, NOT WORKING FOR TENNESSEE GAS, ACCIDENTALLY DUG INTO THE LINE WHILE WORKING IN A GRAVEL YARD. VENT MARKING AT RAILROAD CROSSING, APPROXIMATELY 432FT. UPSTREAM AND MARKING APPROXIMATELY 350FT. DOWNSTREAM.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960092 | 1996-06-10 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA |  | CAMERON PARISH | LA |  |  |  | 1245 | 1996-05-10 |  | YES | HI | 71 |  | YES | NO | LEAK | 0 | 0 | 0 | 171388 | 123362.8497 | 268748.9286 | Null | 0 | 0 |  | 19960510 | 980 | 1200 | BY TEST | 1800 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | GIRTH | STEEL |  | PIPELINE |  | 1973 | 16 | 0.31 | API5LX52 | 52000 | SEAMLESS |  | U.S. STEEL | 1971 | UNDER WATER |  | HILLARY S. SCHNEIDER | 7086913457 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION | LEAK IS DUE TO PIN HOLE IN GIRTH WELD | YES | 19730807 | WATER |  | 9 | 1880 | A PIN HOLE LEAK IN GIRTH WELD CAUSED GAS AND CONDENSATE TO ESCAPE. PRESSUREESSEL SLEEVE AND STRUCTURAL CLAMP SYSTEM INSTALLED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960094 | 1996-06-13 | 2714 | CNG TRANSMISSION CORP |  | HARRISON | WV |  |  | 315 +99 | 2100 | 1996-05-09 | 1 | NO |  |  | WV | Null | NO | LEAK | 0 | 0 | 0 | 50000 | 35989.3486 | 78403.6597 | Null | 2 | 0 |  |  | 488 | 1050 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1976; NMDIA: 20; THK: 0.28; SMYS: 0; SEAM: SEAMLESS; MANU: US STEEL; MANYR: 1976; LOCLK: UNDER GROUND; PNAME: JACK L. ADAMS; PHONE: 3046238410; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | HEAVY & CONSECUTIVE RAINS CAUSED GROUND TO SLIP WHICH RESULTED IN PIPELINE DEVELOPING A "WRINKLE BEND" RESULTING IN A LEAK.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960095 | 1996-06-20 | 13480 | NIAGARA MOHAWK POWER CORP | CHARLTON | SARATOGA | NY | 12020 |  |  | 655 | 1996-05-25 | 1 | NO |  |  |  | Null | NO | RUPTURE | 2 | 0 | 0 | 60000 | 43187.2184 | 94084.3916 | Null | 1 | 35 |  | 19960525 | 490 | 490 | BY TEST | 750 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1962; NMDIA: 16; THK: 0.25; SPEC: API-5LX (42); SMYS: 37; SEAM: ERW; MANU: BETHLEHEM OR REPUBLIC; MANYR: 1964; LOCLK: UNDER GROUND; PNAME: DANIEL THURN; PHONE: 5184333535; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: WITNESS POSTS; STAT: YES; CTEST: Null | PIPELINE WAS DAMAGED UNKNOWN YEARS AGO PREVIOUS TO INCIDENT AND NOT REPORTEDTO NIAGARA MOHAWK. FINAL VERIFICATION THAT DAMAGE CAUSED ULTIMATELY LED TO PIE FAILURE BEING PERFORMED BY BATTELLE MEMORIAL INSTITUTE. PRELIMINARY INVESTIGATION INDICATES DAMAGE BY A THIRD PARTY SEVERAL YEARS AGO CAUSED PIPE TO FAIL AT PRESSURE APPROACHING MAOP. BATTELLE INSTITUTE VERIFYING CAUSE OF FAILURE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960101 | 1996-07-03 | 18516 | SOUTHERN NATURAL GAS CO | HEFLIN | CLEBURNE | AL | 36264 | 399.824 ON 24" NORTH. MAI |  | 1730 | 1996-06-05 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 3 | 0 |  | 19960605 | 440 | 500 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1948 | 24 | 0.25 | API 5L | 52000 | SUBMERGED ARC |  | REPUBLIC | 1948 | UNDER GROUND |  | DOUG DUHON | 2058311131 | EXTERNALLY | OTHER | VISIBLE EXTERNAL CRACKS | OTHER | SCC | COATED | YES | 1972 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | PRELIMINARY METALLURGICAL EXAMINATION INDICATES THAT STRESS CORROSION CRACKING IS MOST LIKELY OF THE LOW PH VARIETY. COATING AT THIS PARTICULAR POINT ON THE PIPELINE WAS POOR. HOWEVER, COATING ON ADJACENT PORTIONS OF THE PIPELINE WAS REPORTED TO BE GOOD. ALTHOUGH METALLURGICAL TESTING IS NOT YET COMPLETE, PRELIMINARY INDICATION IS THAT STRESS CORROSION CRACKING CONTRIBUTED TO THE INCIDENT. CORROSION IN A DENT OF THE PIPE RESULTED IN AN APPROXIMATE 1-1/2"LONG CRACK THROUGH WHICH GAS LEAKED. SUPPLEMENTAL REPORT SUBMITTED 11/27/96INDICATES STRESS CORROSION CRACKING CONTRIBUTED TO THE INCIDENT. CORROSION INA DENT OF THE PIPE RESULTED IN AN APPROXIMATE 1 1/2 INCH LONG CRACK THROUGHWHICH GAS LEAKED. VISIBLE EXTERNAL CRACKS - COATING AT THIS PARTICULAR JOINTON THE PIPELINE WAS POOR. HOWEVER COATING ON THE ADJACENT PORTIONS OF THEPIPELINE WAS REPORTED TO BE GOOD. FINAL METTALURGICAL ANALYSIS INDICATES THATTHE STRESS CORROSION CRACKING IS OF THE HIGH PH VARIETY.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19960102 | 1996-07-01 | 21031 | VALERO TRANSMISSION CO | SONORA | SUTTON | TX | 76950 | SONORA COMPRESSOR STA. | 19 MI. SOUTH ON US 277 | 2145 | 1996-05-20 | 1 | NO |  |  | TX | Null | NO | OTHER | 0 | 0 | 1 | 4000000 | 2879147.8902 | 6272292.7762 | Null | 6 | 15 |  | 19960520 | 694 | 1005 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: UNKNOWN; MLKD: OTHER; MLKDO: UNKNOWN; PRTSY: COMPRESSOR STATION; PRTYR: 1969; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: OTHER; LOCLO: NOT GIVEN; PNAME: JOHN SOMMER; PHONE: 2102462395; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | FORENSIC ENGINEERING AND METALLURGICAL EXPERTS ARE CURRENTLY REVIEWING THEINCIDENT TO DETERMINE THE CAUSE OF THE NATURAL GAS RELEASE AND FIRE. ASUPPLEMENTAL REPORT WILL BE FILED UPON COMPLETION OF THE INVESTIGATION. ASUPPLEMENTAL REPORT RECEIVED 1/24/97 INDICATES THAT THE INVESTIGATION INTO THECAUSE OF THE FIRE THAT OCCURRED AT THE SONORA COMPRESSOR STATION ON MAY 20,1996 IS STILL OPEN AND IT APPEARS THAT WE WILL NEVER BE ABLE TO CONCLUSIVELYDETERMINE THE SEQUENCE OF EVENTS THAT CAUSED THE FIRE. A TEAM COMPOSED OF (1)A FORENSIC ENGINEERING CONSULTANT, BEARD ENGINEERING; (2) METALLURGICALEXPERTS, BRYANT/LEE ASSOCIATES AND METALLURGICAL CONSULTANTS; AND (3) COMPANYPERSONNEL HEADED BY JOHN SOMMER CONDUCTED AN EXHAUSTIVE INVESTIGATION OF THEFIRE AND CONCLUDED THAT THE MOST PROBABLE CAUSE OF THE INCIDENT WAS THEMECHANICAL FAILURE OF AN 1/2" TUBING CONNECTION ON THE UNIT 612 VALVE OPERATORPOWER GAS SUPPLY MANIFOLD. FORENSIC AND METALLURGICAL TESTS OF ALL OTHERMECHANICALLY FAILED EQUIPMENT REVEALED THAT THE FAILURES WERE CAUSED BY THEINTENSE HEAT OF THE FIRE AND WERE NOT THE CAUSE OF THE INCIDENT. PROPERTYDAMAGE FOR THIS INCIDENT ROSE FROM $3,250,000 TO $4,000,000.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960110 | 1996-07-08 | 22655 | WILLISTON BASIN INTERSTATE PIPELINE CO | WOLFPOINT | ROOSEVELT | MT | 59201 | VALVE #14 | 4807 + 05 | 1015 | 1996-06-13 | 1 | NO |  |  | MT | Null | NO | OTHER | 0 | 0 | 0 | 184000 | 132440.8029 | 288525.4677 | Null | 1 | 0 |  | 19960613 | 548 | 750 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: MECHANICAL JOINT; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1940; NMDIA: 8; THK: 0.22; SMYS: 42000; SEAM: ERW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: CRAIG WAGNER; PHONE: 4063597216; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: Null; MARK: Null; STAT: NO; CTEST: Null | ON JUNE 13, 1996, WILLISTON BASIN EMPLOYEES WERE COMPLETING A 3800 FOOT RELOCATION ON WILLISTON BASIN'S SACO TO MORGAN CREEK EIGHT INCH PIPELINE TO ACCOUMMODATE FUTURE HIGHWAY RECONSTRUCTION. THE RELOCATION PROJECT WAS NEARLY COMPLETE EXCEPT FOR THE TIE-INS TO THE EXISTING LINE AT EACH END. AT 7:00 AM AN EIGHT INCH VALVE (VALVE #14) WAS CLOSED ON THE NORTH END AND AT 9:30 AM TWO MAINLINE EIGHT INCH VALVES WERE SHUT TO ALLOW TIE-IN AT THE SOUTH END. THE VALVES WERE GREASED TO STOP ANY LEAKAGE AND THE LINE WAS BLOWN DOWN. THE NORTH TIE-IN WAS TO BE LOCATED WITHIN THIRTY FEET OF A VALVE BOX WHICH HOUSED VALVE #14. LINE PRESSURE WAS APPROXIMATELY 548 PSIG UPSTREAM OF VALVE #14 AT THE TIME OF THE INCIDENT. THE VALVE BOX ALSO CONTAINED A THREE INCH PIPELINE TAKEOFFWHICH SUPPLIES GAS TO THE TOWN OF POPLAR, MONTANA, APPROXIMATELY SIXTEEN MILES NORTHEAST. TIE-IN WORK PROCEEDED WITH A CREW AT EACH END OF THE RELOCATION. THE CREW ON THE NORTH SIDE OF THE RIVER PROCEEDED WITH THE TIE-IN BY MAKINGTWO CIRCUMFERENTIAL CUTS APPROXIMATELY 4-5 INCVHES APART. THE WELDER THEN PROCEEDED DOWN THE PIPELINE APPROXIMATELY 15-18 FEET AND MADE ANOTHER CUT. THE WELDER THEN RETURNED TO THE ORIGINAL CUTS AND WITH A HAND TORCH STARTED CUTTING THE SMALL SEGMENT INTO THREE PIECES. THE TWO SEGMENTS ON TOP OF THE PIPE WERE KNOCKED OUT FIRST. AT APPROXIMATELY 10:15 AM WHEN THE BOTTOM SEGMENT WAS KNOCKED OUT THE TWO OPEN ENDS OF THE PIPELINE SLAMMED TOGETHER. THE CREW IMMEDIATELY REALIZED THAT SOMETHING HAD PARTED UPSTREAM AND THERE WAS A LOUD ROARFROM GAS BEING RELEASED ON THE OTHER SIDE OF THE VALVE BOX. THE CREW EVACUATED THE AREA IMMEDIATELY. THE GAS IGNITED WITHIN SECONDS OF THE RELEASE CONSUMING THE VALVE BOX AND ASSOCIATED PIPELINE EQUIPMENT THAT WAS PARKED ADJACENT TO THE WORK AREA. CREWS IMMEDIATELY RESPONDED BY SHUTTING THE EIGHT INCH PIPELINE IN UPSTREAM AT THE NEXT VALVE APPROXIMATELY SIX MILES AWAY AT VALVE NUMBER 13 AT THE WOLFPOINT TAKEOFF. ANOTHER CREW ALSO SHUTIN THE THREE INCH PIPELINE THAT RUNS TO POPLAR MONTANA AT THE CLOSEST MAINLINE VALVE APPROXIMATELY TWO MILES AWAY. AT 10:35 AM THE PIPELINE WAS SHUTIN AND WAS BLOWING DOWN. AT 10:45 AM LAW ENFORCEMENT OFFICALS ARRIVED AND STARTED CONTROLLING TRAFFIC SINCE THIS LOCATION IS APPROXIMATELY 200 FEET FROM MONTANA HIGHWAY 13. THE LOCAL FIRE DEPARTMENT ARRIVED AT 10:45 AM AND WERE INSTRUCTED TO STANDBY UNTIL THE PIPELINE HAD BLOWN DOWN. AT 11:00 AM THE FIRE DEPARTMENT PUT OUT SOME GRASS FIRES AND AT 11:15 AM THE FIRE DEPARTMENT EXTINGUISHED THE FIRES ASSSOCIATED WITH PIPELINE EQUIPMENT AND THE VALVE BOX. AT APPROXIMATELY 11:50 AM COMPANY PERSONAL BEGAN SURVYING THE AREA AND DISCOVERED A CRATER ABOUT FIFTEEN FEET INDIAMETER AND SIX FEET DEEP WITH A SHORT STYLE 38 DRESSER COUPLING PARTED FROM THE PIPELINE AT THE BOTTOM OF THE CRATER. THE LOCATION WHERE THE COUPLING PARTED WAS APPROXIMATELY THIRTEEN FEET UPSTREAM FROM THE VALVE BOX THAT HOUSEDTHE POPLAR TAKEOFF AND VALVE #14.THE NORTH CREW CONSISTED OF SEVEN COMPANY EMPLOYEES. ONLY ONE MINOR PERSONAL INJURY WAS REPORTED AS A RESULT OF THIS INCIDENT WHICH CONSISTED OF A JAMMED FINGER RECEIVED WHILE AN EMPLOYEE WAS EVACUATING THE SCENE. AT 5:10 PM TEMPORARY REPAIRS WERE MADE, WELDS WERE X-RAYED AND PURGING BEGAN. THE LINE WAS PRESSURED TO 120 PSIG AND HELD THERE UNTIL A LEAK SURVEY WAS COMPLETED ON APPROXIMATELY 800 FEET OF PIPELINE UPSTREAM OF THE LOCATION OF THE INCIDENT. NO PROBLEMS WERE FOUND AND AT THIS POINT ALL VALVES WERE OPENED AND THE PIPELINE WAS RETURNED TO NORMAL SERVICE. THE ONLY INTERRUPTION OF SERVICE WAS ASSOCIATED WITH FARMTAP CUSTOMERS ALONG THE RIGHT-OF-WAY. DAMAGES WERE SIGNIFICANT DUE TO THE GAS IGNITING, PROBABLY DUE TO STATICELECTRICITY OF FLYING DEBRIS CREATING A SPARK, AND THE CLOSE PROXIMITY OF PARKED COMPANY EQUIPMENT. DAMAGES AMOUNTED TO $184,000 WITH THE MAJORITY OF EXPENSES ASSOCIATED WITH FIRE DAMAGE TO TWO WELDING TRUCKS, A BACKHOE/LOADER, A TRUCK MOUNTED CRANE, AND A PICKUP.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960111 | 1996-07-17 | 19730 | TRUNKLINE GAS CO | KOUNTZE | HARDIN | TX | 77625 | 40 | A.C. BIGELOW A-912 | 215 | 1996-05-21 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 86100 | 61973.6583 | 135011.102 | Null | 1 | 21 |  | 19960522 | 582 | 875 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: ESD CONTROL SYSTEM; MLKD: OTHER; MLKDO: DEVICE MALFUNCTION; PRTSY: COMPRESSOR STATION; PRTYR: 1955; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: DENNIS ODUM; PHONE: 7139892822; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | #4025-B4 SUCTION EMERGENCY SHUT DOWN SYSTEM BLOWDOWN VALVE OPENED DUE TO A DEVICE FAILURE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960112 | 1996-07-17 | 19160 | TENNESSEE GAS PIPELINE CO | CLAY CITY |  | KY | 40312 |  |  | 1023 | 1996-06-19 | 1 | NO |  |  |  | Null | Null | LEAK | 0 | 0 | 0 | 412500 | 296912.1262 | 646830.1925 | Null | 0 | 20 |  | 19960619 | 749 | 750 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: COMPRESSOR UNIT; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1952; NMDIA: 0; THK: 0; SMYS: 0; MANU: CLARK; MANYR: 1952; LOCLK: ABOVE GROUND; PNAME: LORI SCHULTZ; PHONE: 7137577805; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: MATERIAL; CAULO: COMPRESSOR ROD; CTEST: Null; MED: NO DATA; TMPS: 0; LKPS: 0 | COMPRESSOR ROD BROKE, DAMAGING THE PACKING, RESULTING IN THE RELEASE OF GAS INTO THE COMPRESSOR BUILDING.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960115 | 1996-07-25 | 602 | NORAM GAS TRANSMISSION | FARMERVILLE | UNION | LA |  |  | 1098+59 | 2015 | 1996-06-25 | 1 | NO |  |  |  | Null | NO | RUPTURE | 0 | 0 | 0 | 22000 | 15835.3134 | 34497.6103 | YES | 2 | 1 |  | 19960625 | 200 | 500 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1929; NMDIA: 10; THK: 0.31; SMYS: 0; MANYR: 0; LOCLK: UNDER GROUND; PNAME: WALTER L. FERGUSON; PHONE: 3184293210; LOC: EXTERNALLY; ADESC: GENERAL CORROSION; CAUCR: OTHER; CAUCO: NOT GIVEN; COAT: BARE; PROT: NO; CPYR: 0; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | FAILURE BEGAN FROM PIT ON BOTTOM OF PIE AND PROPAGATED VERTICALLY AROUND THECIRCUMFERENCE OF PIPE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960116 | 1996-07-23 | 22617 | WILLIAMS NATURAL GAS CO | BUFFALO | HARPER | OK |  | .5 MI E OF FLY MARKER 110 | 5858 + 78 | 529 | 1996-06-16 | 1 | NO |  |  | OK | Null | NO | RUPTURE | 40 | 0 | 0 | 100000 | 71978.6973 | 156807.3194 | Null | 3 | 30 |  | 19960616 | 542 | 765 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | WELD | LONGITUDINAL | STEEL |  | PIPELINE |  | 0 | 26 | 0.25 |  | 56000 | EW |  | A.O. SMITH | 1943 | OTHER | GRASSLAND-PASTURE | JOE FREISBERG | 9185884193 | EXTERNALLY | OTHER | NOT GIVEN | OTHER | NOT GIVEN | COATED | Null | 1948 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | PIPE SEGMENT FAILURE ANALYST TO BE COMPLETED BY 07/30/96. GENERAL CORRISION OF WELD SEAM- FAILURE ANALYST NOT COMPLETED AS OF THIS DATE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960117 | 1996-07-26 | 19160 | TENNESSEE GAS PIPELINE CO | HOUMA |  | LA | 70363 | 102+01 | 526A-1100 | 219 | 1996-06-24 |  | YES | S. PASS | 40 | LA | Null | NO | OTHER | 0 | 0 | 0 | 110000 | 79176.567 | 172488.0513 | Null | 0 | 50 |  | 19960624 | 1000 | 1133 | BY TEST | 2160 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1985; NMDIA: 6.63; THK: 0.38; SMYS: 0; MANU: NATIONAL TUBE PIPE; MANYR: 0; LOCLK: UNDER WATER; PNAME: LORI SCHULTZ; PHONE: 7137577805; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: NO; MARK: Null; STAT: NO; CTEST: Null | THE PIPELINE CROSSES BURRWOOD BAYOU. THIS BAYOU HAS ENLARGED FROM 100'WIDE AND 15' DEEP TO OVER 1100' WIDE AND 30' DEEP. THE LINE WAS SUSPENDED IN THE BAYOU AND THEN FAILED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960118 | 1996-07-29 | 15105 | PANHANDLE EASTERN PIPELINE CO |  | RENO | KS |  | MP7 | 315 +83 | 520 | 1996-06-28 | 1 | NO |  |  | KS | Null | NO | RUPTURE | 75 | 0 | 0 | 430000 | 309508.3982 | 674271.4734 | Null | 1 | 25 |  | 19960628 | 860 | 900 | BY TEST | 1199 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1962 | 30 | 0.31 | API-5LX-60 | 60000 | EFW |  | A.O. SMITH | 1962 | UNDER GROUND |  | DAVID L. BERLIN | 3166261308 | EXTERNALLY | LOCALIZED PITTING |  | OTHER | UNDER INVESTIGATION | COATED | YES | 1962 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | UNDER INVESTIGATION
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960129 | 1996-08-09 | 19160 | TENNESSEE GAS PIPELINE CO | KINDER |  | LA | 70648 | 823X-101+0.55 |  | 1330 | 1996-07-07 |  | YES | E. CAMERAN | 281 |  | YES | NO | LEAK | 0 | 0 | 0 | 80000 | 57582.9578 | 125445.8555 | Null | 0 | 15 |  | 19960708 | 1065 | 1440 | BY TEST | 2175 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1975 | 16 | 0.38 | API 5LX | 52000 | SEAMLESS |  | U.S. STEEL | 0 | UNDER WATER |  | L. SCHULTZ | 7137577805 | INTERNALLY | OTHER | NONE SPECIFIED | OTHER | UNKNOWN | COATED | YES | 1975 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | Bubbles were discovered by the Producer 100 yards off platform. Leak was a pin hole at the 6 o'clock position caused by internal corrosion. Leak was at 6o'clock position - pin hole leak.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960139 | 1996-09-13 | 19730 | TRUNKLINE GAS CO |  |  | LA |  |  |  | 2205 | 1996-08-12 |  | YES | ST | 148 | LA | Null | NO | RUPTURE | 0 | 0 | 0 | 830000 | 597423.1872 | 1301500.7511 | Null | 12 | 59 |  | 19960813 | 1032 | 1630 | BY TEST | 1800 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1972; NMDIA: 12; THK: 0.38; SPEC: 5LX-52; SMYS: 52000; SEAM: SMLS; MANU: YOUNGSTOWN; MANYR: 0; LOCLK: UNDER WATER; PNAME: JC KELLY; PHONE: 7136275600; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: COORDINATE SURVEY; STAT: YES; CTEST: Null | ANCHOR FROM DIVE BOAT RUPTURED 12" LINE 319B-1500.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960140 | 1996-09-10 | 20230 | KOCH GATEWAY PIPELINE CO | SEC 28.T-15-S,R14-E | PLAQUEMINES | LA |  | 20.45 | 1080+00 | 500 | 1996-08-28 | 1 | NO |  |  |  | Null | NO | RUPTURE | 0 | 0 | 0 | 264014 | 190033.8378 | 413993.2763 | Null | 5 | 30 |  | 19960828 | 516 | 605 | BY CFR 192.619(A)(3) | 5 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1952; NMDIA: 16; THK: 0.31; SPEC: 5LX; SMYS: 46000; SEAM: ERW; MANU: AO SMITH; MANYR: 1950; LOCLK: UNDER WATER; PNAME: SANDY GIESEMANN; PHONE: 5044695903; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PIPELINE MARKER SIGN; STAT: NO; CTEST: Null | 16" VENICE JCT-CHALMETTE LINE RUPTURED ON LAKE PETIT, LAT 29DEG43.4', LONG 89DEG47.6, SEC 28, T-15-S, R-14-E, PLAQUEMINES PARISH, LA. INSPECTION OF FAILED PIPE REVEALED MECHANICAL DAMAGE AT MULTIPLE POINTS IN CENTER OF NAVIGATIONAL CHANNEL. LIKELY CAUSED FROM CONTACT WITH MARINE TRAFFIC AT SOME PREVIOUS TIM
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960145 | 1996-09-30 | 19730 | TRUNKLINE GAS CO | EL CAMPO | WHARTON | TX |  | VS 24-1 | 436 + 95 | 1215 | 1996-08-29 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 65000 | 46786.1532 | 101924.7576 | Null | 1 | 55 |  | 19960829 | 720 | 875 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1951; NMDIA: 20; THK: 0.25; SPEC: API-5LX; SMYS: 52000; SEAM: DSAW; MANU: KAISER; MANYR: 1951; LOCLK: UNDER GROUND; PNAME: JC KELLY; PHONE: 7136275600; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19960829; MARK: YES; MRKTP: MILE MARKER - IN SIGHT; STAT: YES; CTEST: Null | 8/29/96 10:15 A.M. - NOTIFIED OF CROSSING LOCATION AND SCHEDULED TO MEET ON SITE 9/30/96 TO LOCATE AND MARK FACILITIES. TRANS TEXAS STRUCK 20" LINE 100-1WITH TRENCHER WHILE CROSSING TRUNKLINE FACILITIES.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960146 | 1996-09-30 | 19730 | TRUNKLINE GAS CO |  |  | LA |  |  |  | 1430 | 1996-09-03 |  | YES | VE | 329 | LA | Null | NO | LEAK | 0 | 0 | 0 | 250000 | 179946.7431 | 392018.2985 | Null | 49 | 0 |  | 19960903 | 856 | 1200 | BY TEST | 2364 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 0 | 12 | 0.38 | API 5LX | 52000 | SMLS |  | US STEEL | 1978 | UNDER WATER |  | JC KELLY | 7136275600 | INTERNALLY | OTHER | PIPE BODY 1/4" HOLE AT 6 | OTHER | INTERNAL CORROSION | COATED | YES | 1978 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | PIPE BODY 1/4" HOLE AT 6 O'CLOCK. CATHODIC P/S .982V - BATCH TREAT WITH BIOCIDE ON AN AS NEEDED BASIS. LEAK ON 12" LINE 1000 - 4B - 1100.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960147 | 1996-10-04 | 12690 | MONTANA POWER CO | RED LODGE | CARBON | MT | 59068 | 3.1 | 161+92 | 1050 | 1996-08-29 | 1 | NO |  |  |  | Null | NO | RUPTURE | 2 | 0 | 0 | 93000 | 66940.1884 | 145830.807 | Null | 0 | 45 |  | 19960829 | 585 | 720 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: GIRTH; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1931; NMDIA: 4.5; THK: 0.19; SMYS: 24000; MANU: REPUBLIC; MANYR: 1931; LOCLK: UNDER GROUND; PNAME: JAY WATERMAN; PHONE: 4064972441; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19960828; MARK: YES; MRKTP: MARKED ADJACENT PIPELINE; STAT: YES; CTEST: Null | THIRD PARTY DOZER WITH RIPPER TOOTH SNAGGED MONTANA POWER COMPANY 4" RED LODGE NATURAL GAS TRANSMISSION PIPELINE. LINE PARTED AT GIRTH WELD. NO INJURIES.NO DAMAGE AT SITE. MONTANA POWER HAD TO RELIGHT TOWN OF RED LODGE. 1500 CUSTOMERS. STATUTE REQUIRES THEY CONTACT 1-CALL.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19960148 | 1996-10-16 | 4280 | EL PASO NATURAL GAS CO | ROSWELL | CHAVES | NM |  | 123+3299 |  | 1530 | 1996-09-10 | 1 | NO |  |  |  | Null | NO | RUPTURE | 26 | 0 | 1 | 240000 | 172748.8734 | 376337.5666 | Null | 1 | 30 |  | 19960910 | 719 | 836 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1953 | 30 | 0.34 | API5L-X52 | 52000 | EFW |  | A.O. SMITH | 1953 | UNDER GROUND |  | RICHARD FAVILA | 9155412062 | INTERNALLY | LOCALIZED PITTING |  | OTHER | LIQUID INTERFACE | COATED | YES | 1953 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | A SEGMENT OF OUR LINE NO. 1300 RUPTURED, BLOWING OUT 26 FEET OF PIPE, MOST OF IT IN A SINGLE SEGMENT WHICH LANDED 100 FEET FROM THE PIPELINE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960149 | 1996-10-16 | 13750 | NORTHERN NATURAL GAS CO (ENRON) | VIOLA | LACROSSE | WI | 54601 | 7.614 |  | 1730 | 1996-09-17 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 5 |  | 19960918 | 670 | 960 | BY TEST | 1422 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1966; NMDIA: 6; THK: 0.16; SPEC: API5L; SMYS: 35000; SEAM: ERW; MANU: INTERLAKE; MANYR: 1966; LOCLK: UNDER GROUND; PNAME: JOHN CASKEY; PHONE: 7136467343; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PERMANENT MARKERS; STAT: YES; CTEST: Null | CONTRACTOR BUILDING A LOGGING ROAD DID NOT CALL ONE-CALL AND TORE A HOLE IN THE PIPE WITH A DOZER BLADE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960150 | 1996-10-17 | 11680 | LONE STAR GAS CO | TRINIDAD | HENDERSON | TX |  | 62 | 4035+20 TO 4039+59 | 2015 | 1996-09-04 | 1 | NO |  |  |  | Null | NO | RUPTURE | 439 | 0 | 0 | 50000 | 35989.3486 | 78403.6597 | Null | 1 | 30 |  | 19960904 | 270 | 425 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1935; NMDIA: 20; THK: 0.28; SPEC: GRADE B; SMYS: 35000; SEAM: EW SMLS; MANYR: 0; LOCLK: UNDER GROUND; PNAME: ML IMBODEN; PHONE: 2146702779; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: MATERIAL; CTEST: NO; MED: NO DATA; MEDO: 0; TMPS: 0; LKPS: 0 | FAILURE APPEARS TO HAVE OCCURED AT A MECHANICAL COUPLING AND INCLUDED FAILUREOF ALL OR MOST OF THE 439 FT. SEGMENT.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960151 | 1996-10-21 | 15007 | PACIFIC GAS & ELECTRIC CO | COLUSA | COLUSA | CA | 95932 | 13.38 | 701+37 | 640 | 1996-09-28 | 1 | NO |  |  | CA | Null | NO | RUPTURE | 10 | 0 | 0 | 500000 | 359893.4863 | 784036.597 | Null | 2 | 2 |  | 19960928 | 760 | 800 | BY TEST | 880 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1957; NMDIA: 18; THK: 0.25; SPEC: APL 5L-X52; SMYS: 52000; SEAM: DSAW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: KEN RIDINGS; PHONE: 4159735965; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: NO; MARK: YES; MRKTP: 0Y; STAT: Null; CTEST: Null | THE PIPELINE PRESSURE WAS SLOWLY BEING RAISED FROM 575 PSIG TO ACCOMMODATE AFUTURE SHUTDOWN. THE PIPELINE RUPTURED WHEN THE PRESSURE REACHED 760 PSIG. THE NORMAL OPERATING PRESSURE FOR THIS LINE RANGES FROM 550 TO 800 PSIG. THE RUPTURED LINE DID HAVE EXTERNAL THIRD PARTY DAMAGE. THE ACTUAL FAILURE CAUSE AND SOURCE OF EXTERNAL DAMAGE IS CURRENTLY UNDER INVESTIGATION.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19960164 | 1996-11-19 | 3230 | DELHI GAS PIPELINE CORP | PECOS | REEVES | TX | 79772 |  | VAN HORN 1584 | 1115 | 1996-10-12 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 1 | 0 | 0 | 0 | 0 | Null | 2 | 0 |  | 19961012 | 670 | 720 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1966; NMDIA: 6; THK: 0.16; SPEC: API5LX; SMYS: 42000; SEAM: ERW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: ROBERT WALKER; PHONE: 9159431131; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: 192.707 MARKER; STAT: YES; CTEST: Null | 49 USC SECTION 60123(D)
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960166 | 1996-11-06 | 13750 | NORTHERN NATURAL GAS CO (ENRON) | YOUNG AMERICA | CARVER | MN | 55394 | 0.82 |  | 1400 | 1996-10-04 | 1 | NO |  |  | MN | Null | NO | OTHER | 0 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 0 |  | 19961004 | 800 | 950 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1963; NMDIA: 4; THK: 0.16; SMYS: 42000; SEAM: ERW; MANU: REPUBLIC; MANYR: 1963; LOCLK: UNDER GROUND; PNAME: JOHN CASKEY; PHONE: 7136467343; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PERMANENT MARKERS; STAT: YES; CTEST: Null | CONTRACTOR HIT PIPELINE WITH A TILING MACHINE. DID NOT CALL "ONE-CALL".
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19960167 | 1996-11-06 | 19269 | TEXAS GAS GATHERING INC | JONESVILLE | HARRISON | TX | 75659 |  |  | 2300 | 1996-10-02 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 1 | 2000 | 1439.5739 | 3136.1464 | Null | 1 | 0 |  | 19961002 | 480 | 1140 | BY TEST | 1640 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: SEE REPORT; MLKD: OTHER; MLKDO: NONE SPECIFIED; PRTSY: COMPRESSOR STATION; PRTYR: 1990; NMDIA: 16; THK: 0.23; SPEC: X52; SMYS: 0; SEAM: ERW; MANU: AMERICAN STEEL; MANYR: 1989; LOCLK: ABOVE GROUND; PNAME: ROBERT PALMER; PHONE: 9036872541; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | PIGGING THE 16 INCH LINE (TEXAS GAS GATHERING). FLOWING CONDENSATE AND PIG WASTES INTO 3 FRAC TANKS AND 2 STOCK TANKS FROM SLUDGE CATCHER, AT BULLARD JUNCTION COMPRESSOR STATION-TGG. FILLED UP ALL FRAC TANKS AND STOCK TANKS WITH FLUID, FROM SLUDGE CATCHER. SHUT SLUDGE CATHCHER IN. (NO FLOW TO TANKS). BEFORE BRINGING IN HAUL TRUCKS, LET GAS VAPOR AROUND TANKS DISSIPATE. (APPROX 45 MINUTES TO 1 HOUR). C&S TRUCK (HAUL TRUCK) PULLED UP TO FRAC TANKS, TO HAUL OUT OF MIDDLE FRAC TANK. TRUCK WAS 90% LOADED. A BLUE FLAME COULD BE SEEN LOW TO THE GROUND COMING AROUND REAR OF FRAC TANK. THE FLAME COULD BE SEEN GOING UP EXHAUST STACK ON MACK TRUCK. THE FLAME THEN PROCEEDED TO COME UP FROM UNDERTHE TRUCK AND THEN FLASH BURN, THE DRAFT INTO WOODS. (LASTED APPROX 2 SECONDS). AN EMPLOYEE WAS CAUGHT UP IN THE FLASH BURN, RECEIVED 2ND DEGREE BURNS TO15% OF HIS BODY. CAUSE OF ACCIDENT: 1. WEATHER CONDITIONS (VERY HUMID, AND NO WIND). 2. ONLY IGNITION SOURCE LOCATED WAS THE EXHAUST MANIFOLD ON THE MACKTRUCK. 3. STATIC ELECTRICITY.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960168 | 1996-11-06 | 567 | VASTAR RESOURCES, INC |  |  | LA |  | 0.11 | 6 + 00 | 1700 | 1996-10-06 |  | YES | SOUTH PASS | 60 | LA | YES | NO | OTHER | 0 | 0 | 0 | 50000 | 35989.3486 | 78403.6597 | Null | 0 | 0 |  | 19961009 | 870 | 1200 | BY TEST | 1500 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: MECHANICAL JOINT; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1996; NMDIA: 18; THK: 0.5; SMYS: 0; MANYR: 1996; LOCLK: UNDER WATER; PNAME: JR THIBODEAUX; PHONE: 3182644279; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; DMGO: UNDERWATER MUDSLIDE; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | SHEAR JOINT (INSTALLED AUG. 1996) SEPARATION CAUSED BY MUDSLIDE DURING HURRICANE JOSEPHINE.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19960169 | 1996-11-08 | 567 | VASTAR RESOURCES, INC |  |  | LA |  |  |  | 0 | 1996-10-06 |  | YES | MP | 77 | LA | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19961009 | 0 | 3680 | BY TEST | 5520 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: GATHERING SYSTEM; PRTFL: FITTING; PRTFO: DESIGNED BREAKAWAY JOINT; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1995; NMDIA: 4; THK: 0.44; SPEC: API 5L, GRADE B; SMYS: 35000; SEAM: SEAMLESS; VALVE: ANSI 1500; MANYR: 0; LOCLK: UNDER WATER; PNAME: MICHAEL SCOGGINS; PHONE: 7135843599; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: MUD SLIDE; NOTIF: NO; MARK: Null; STAT: NO; CTEST: Null | DIVERS INSPECTED BREAK ON 10/21/96 & CONFIRMED THAT LINE PARTED @ THE DESIGNED WEAK LINK (BREAK-AWAY JOINT). MUD SLIDES LEFT APPROX 100' AND SEPARATION. ONE END OF THE LINE WAS BURIED DEEPER & WAS NOT LOCATED BECAUSE OF THE ONSET OF BAD WEATHER. THE BREAK-AWAY JOINT WILL BE REPLACED & A REPLACEMENT SECTIONOF PIPE WILL BE FABRICATED. PART 3 - LINE PARTED @ A BREAK-AWAY JOINT INSTALLED IN THE LINE. BELIEVED TO HAVE BEEN CAUSED BY A MUD SLIDE TRIGGERED BY TROPICAL STORM JOSEPHINE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960170 | 1996-11-14 | 20230 | KOCH GATEWAY PIPELINE CO | PANOLA |  | TX |  | STA. #986+26 TPL 63 | STA. #986+26 TPL 63 | 1000 | 1996-10-04 | 1 | NO |  |  | TX | Null | NO | RUPTURE | 0 | 0 | 0 | 500000 | 359893.4863 | 784036.597 | Null | 4 | 0 |  | 19961005 | 486 | 445 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1924; NMDIA: 16; THK: 0.34; SMYS: 24000; SEAM: SEE COMMENTS; MANYR: 1924; LOCLK: UNDER GROUND; PNAME: WARREN FUSILIER; PHONE: 3168286969; LOC: EXTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: OTHER; CAUCO: RESULTS NOT RECEIVED.; COAT: COATED; PROT: YES; CPYR: 1950; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | DAMAGED PIPE SENT TO METALLURGIST CONSULTANT TO DETERMINE CAUSE OF RUPTURE. RESULTS NOT RECEIVED. ADDITIONAL INFORMATION IS BEING OBTAINED TO HELP US ASSESS THE CAUSE AND FACTORS CONTRIBUTING TO THE INCIDENT, AND UPON RECEIVING, WE WILL PROVIDE A NARRATIVE DESCRIPTION OF THE RESULTS.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960171 | 1996-11-22 | 13750 | NORTHERN NATURAL GAS CO (ENRON) | BLACK RIVER FALLS | JACKSON | WI | 54615 | 108.164 |  | 430 | 1996-10-13 | 1 | NO |  |  |  | Null | NO | RUPTURE | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19961013 | 800 | 1077 | BY TEST | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 0; NMDIA: 6; THK: 0.16; SPEC: API5LX; SMYS: 42000; SEAM: ERW; MANU: INTERLAKE; MANYR: 1969; LOCLK: UNDER GROUND; PNAME: DAVID JOHNSON; PHONE: 7136467589; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PERMANENT MARKERS; STAT: Null; CTEST: Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960172 | 1996-11-21 | 18436 | SOUTH GEORGIA NATURAL GAS CO | AMERICUS | SUMTER | GA | 31709 | SEE COMMENTS |  | 240 | 1996-10-20 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 125000 | 89973.3716 | 196009.1493 | Null | 2 | 30 |  | 19961020 | 150 | 1082 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: DAMAGED INSTRUMENT LINES; MLKD: STEEL; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1969; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: JOHN MCCUTCHEN; PHONE: 9122264744; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: SEE COMMENTS; STAT: YES; CTEST: Null | A VEHICLE WHOSE DRIVER LOST CONTROL, LEFT THE HIGHWAY AND PASSED THROUGH EXISTING BARRICADES, PENETRATING AMERICUS #1 METER STATION'S CHAIN LINK FENCE. THE VEHICLE STRUCK THE RTU MOUNTING POST, BREAKING OFF INSTRUMENTATION LINES, IGNITING THE ESCAPING GAS. THE NEARBY REGULATOR WAS EVENTUALLY DAMAGED BY THEFIRE CAUSING A REGULATOR FAILURE AND ACTIVATION OF THE OVERPRESSURE RELIEF VALVE RESULTING IN AN ADDITIONAL IGNITION SOURCE. THE METER STATION, CONSUMED IN FIRE, WAS EXTENSIVELY DAMAGED. THE DRIVER OF THE VEHICLE ESCAPED UNHARMED.MILE POST: 16.891 ON LINE #6 - AMERICUS #1 METER STATION. ESTIMATED PRESSURE: INLET 950 PSIG - DELIVER 150 PSIG. PART B -DAMAGE BY OUTSIDE FORCES 2(b): P/L MARKERS, SIGNS ON FACILITY FENCE, BARRICADES. ADDITIONAL INFO: INCIDENT RESULTED FROM VEHICULAR ACCIDENT. PRIOR NOTIFICATION PROCEDURE WAS NOT APPLICABLE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960173 | 1996-11-20 | 19730 | TRUNKLINE GAS CO | WEST CARROLL PARISH |  | LA |  | 0.83 | 43 + 84 | 2100 | 1996-10-18 | 1 | NO |  |  |  | Null | NO | RUPTURE | 77 | 0 | 0 | 67400 | 48513.642 | 105688.1333 | Null | 1 | 30 |  | 19961018 | 1154 | 1440 | BY TEST | 1804 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | OTHER | STORAGE FIELD | 1979 | 18 | 0.28 | 5LX | 65000 | DSAW |  | KAISER | 1979 | UNDER GROUND |  | J WADE | 7136275117 | INTERNALLY | LOCALIZED PITTING |  | OTHER | SALT WATER | COATED | YES | 1980 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960174 | 1996-11-29 | 405 | ANR PIPELINE CO | HIGH ISLAND | SOUTH ADDITION | TX |  | X=3,442,580.20 | Y=125,143.50 | 1415 | 1996-10-26 |  | YES | H.I. | 533 |  | YES | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | Null | 81 | 15 |  | 19961026 | 890 | 1440 | BY TEST | 1922 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: UNKNOWN AT THIS TIME; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1981; NMDIA: 16; THK: 0.44; SPEC: API-5LX; SMYS: 42000; MANYR: 0; LOCLK: UNDER WATER; PNAME: DONALD CROSS; PHONE: 3134962460; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | THE CAUSE OF THE LEAK HAS NOT YET BEEN DETERMINED. WE ARE PRESENTLY EVALUATING VARIOUS REPAIR OPTIONS. A SUPPLEMENTAL REPORT WILL FOLLOW UPON RESOLUTION OFTHESE UNKNOWN ISSUES.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960175 | 1996-11-29 | 19160 | TENNESSEE GAS PIPELINE CO | HOUMA |  | LA | 70363 | 117+13 | 526A-301 | 500 | 1996-10-23 | 1 | NO |  |  |  | Null | NO | RUPTURE | 6 | 0 | 0 | 225000 | 161952.0688 | 352816.4687 | Null | 1 | 30 |  | 19961023 | 930 | 1058 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1957; NMDIA: 12.75; THK: 0.31; SPEC: ASTM A106; SMYS: 42000; SEAM: SEAMLESS; MANU: NATIONAL TUBE; MANYR: 1957; LOCLK: UNDER WATER; PNAME: DARON MOORE; PHONE: 7137574023; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19961018; MARK: YES; MRKTP: PILINGS; STAT: NO; CTEST: Null | DREDGER NOTIFIED OPERATOR ON 10/18/96 FOR DREDGING ON 10/19/96 AND 10/20/96.THEY DID NOT NOTIFY OPERATOR THAT THEY HAD MOVED BACK TO AREA ON 10/23/96. NARRATIVE DESC: SPUD ON DREDGER HIT LINE 526A-300 (12"). GAS CAUGHT FIRE, DREDGE WAS BURNING.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960176 | 1996-12-02 | 12690 | MONTANA POWER CO | MISSOULA | MISSOULA | MT | 59801 | 16.5 | 871+09 | 1310 | 1996-11-01 | 1 | NO |  |  |  | Null | NO | RUPTURE | 0.16 | 0 | 0 | 50000 | 35989.3486 | 78403.6597 | Null | 0 | 35 |  | 19961101 | 390 | 623 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1957; NMDIA: 8; THK: 0.19; SPEC: AL1 5L GRADE "B"; SMYS: 35000; SEAM: ERW; VALVE: SEE COMMENTS; MANU: BEALL PIPE & TANK; MANYR: 1957; LOCLK: UNDER GROUND; PNAME: JAY WATERMAN; PHONE: 4064972441; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19960923; MARK: YES; MRKTP: PAINT, FLAGS; STAT: YES; CTEST: Null | REPORT OF TRANSMISSION PIPELINE INCIDENT WHICH OCCURRED ON THE MONTANA POWERCOMPANY NATURAL GAS TRANSMISSION SYSTEM NEAR MISSOULA, MONTANA ON NOVEMBER 1, 1996. THE INCIDENT WAS SUBJECT TO TELEPHONIC REPORTS MADE TO JOEL TIERNEY OF THE MONTANA PUBLIC SERVICE COMMISSION AND TO THE NATIONAL RESPONSE CENTER (UNDER INCIDENT #366368) ON NOVEMBER 1, 1996. THIRD PARTY CONTRACTOR EXCAVATING FOR NEW PARKING LOT, PUNCTURED MPC 8" BONNER-STONE NATURAL GAS TAPLINE WITHA FRONT END LOADER. NO FIRE, EXPLOSION, OR INJURIES. VALVE, TYPE: V4-8" FIG 34449 1/2 ROCKWELL. MT CODE ANNOTATED: TITLE 69 CHAPTER 4 PART 5 "EXCAVATIONSNEAR UNDERGROUND FACILITIES".
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960182 | 1996-12-16 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA |  | BEAVER | OK | 73931 | 9 | 3995+00 | 450 | 1996-11-16 | 1 | NO |  |  |  | Null | NO | RUPTURE | 39 | 0 | 0 | 100000 | 71978.6973 | 156807.3194 | Null | 0 | 45 |  | 19961116 | 706 | 712 | BY TEST | 1000 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1948 | 26 | 0.25 | API5LX52 | 52000 | EFW |  | A.O. SMITH | 1948 | UNDER GROUND |  | HILLARY SCHNEIDER | 6306913457 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1948 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | PIPELINE RUPTURE OF NO.2 - 26" MAINLINE DUE TO EXTERNAL CORROSION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960183 | 1996-12-16 | 13750 | NORTHERN NATURAL GAS CO (ENRON) | MAUSTON | JUNEAU | WI |  | 0.6304 |  | 1430 | 1996-11-29 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 53750 | 38688.5498 | 84283.9342 | Null | 0 | 30 |  | 19961129 | 960 | 960 | BY TEST | 1354 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1966; NMDIA: 4.5; THK: 0.16; SPEC: API-5L; SMYS: 35000; SEAM: SEAMLESS; MANU: LONE STAR; MANYR: 1966; LOCLK: UNDER GROUND; PNAME: MERLIN MOSEMAN; PHONE: 7136467344; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PIPELINE MARKING SIGNS; STAT: YES; CTEST: Null | LINE HIT BY A BACKHOE ENLARGING A DRAIN DITCH.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960184 | 1996-12-10 | 4280 | EL PASO NATURAL GAS CO | BUCKEYE | MARICOPA | AZ | 85329 | M.P. 607 ON LINE NO.1103 | 260+70.7 | 1630 | 1996-11-11 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 60000 | 43187.2184 | 94084.3916 | YES | 6 | 15 |  | 19961111 | 650 | 809 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: METER STATION; MLKD: STEEL; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1950; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: RICHARD FAVILA; PHONE: 9154962062; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | THE BUCKEYE RURAL FIRE DEPT. RESPONDED TO A FIRE AT THE RAINBOW VALLEY METERSTATION. THE FIRE CONTINUED TO BURN UNTIL VALVE SECTION VA 72 AND VA 73 ON LINE NO. 1103 WAS SHUT IN. INVESTIGATION REVEALED THAT THE INCIDENT WAS A RESULT OF VANDALISM. THE COUNTY SHERIFF'S DEPT. IS INVESTIGATING THE INCIDENT. SINCE VANDALISM WAS INVOLVED, EL PASO REPORTED THE INCIDENT TO THE FBI; HOWEVER, BECAUSE THE SHERIFF'S DEPT. IS ALREADY INVESTIGATING THE INCIDENT THEY DECLINED TO PROCEED WITH ANY FURTHER INVESTIGATION. VANDALISM REPORTED TO THE FBI.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960185 | 1996-12-09 | 567 | VASTAR RESOURCES, INC. | SOUTH PASS |  | LA |  |  |  | 1530 | 1996-11-17 |  | YES | SP | 6 | LA | Null | NO | LEAK | 0 | 0 | 0 | 50000 | 35989.3486 | 78403.6597 | Null | 0 | 30 |  | 19961117 | 1082 | 1440 | BY TEST | 2220 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: UNKNOWN; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1983; NMDIA: 6; THK: 0.38; SPEC: API5L GRADE B; SMYS: 35000; SEAM: ERW; MANYR: 0; LOCLK: UNDER WATER; PNAME: MICHAEL SCOGGINS; PHONE: 2815843599; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | AN APPARENT RELEASE FROM THE PIPELINE WAS DETECTED DUE TO WATER TURBULENCE SPOTTED DURING A HELICOPTER FLY-OVER OF THE LINE. THERE WERE NO INJURIES OR FATALITIES ASSOCIATED WITH THE SUNDAY, NOVEMBER 17, 1996 APPARENT RELEASE, AND TEH CAUSE HAS NOT YET BEEN DETERMINED. DIVERS BEGAN THE PROCESS OF ATTEMPTINGTO LOCATE THE PIPELINE IN THE VICINITY OF THE APPARENT RELEASE ON MONDAY, NOVEMBER 18, 1996 TO DETERMINE ITS CAUSE. IN ATTEMPTING TO DO SO, THE FATALITY OF A DIVER OCCURRED ON THURSDAY NOVEMBER 28, 1996. WHILE NOT RESULTING FROM THE PIPELINE LEAK OR REPAIR, AND NOT BELIEVED TO FALL WITHIN THE REPORTING REQUIREMENTS OF 49 CFR SECTION 191.5 OR 191.15, THIS FATALITY IS BEING REPORTED TO ENSURE COMPLETION OF DOT RECORDS.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960186 | 1996-12-09 | 405 | ANR PIPELINE CO | SHIP SHOAL |  | LA |  | X=2,077,384.50 | Y=141,392.04 | 1900 | 1996-11-11 |  | YES | SHIP SHOAL | 276 |  | YES | NO | LEAK | 56 | 0 | 0 | 135000 | 97171.2413 | 211689.8812 | Null | 11 | 0 |  | 19961111 | 815 | 1300 | BY TEST | 1714 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1978; NMDIA: 10; THK: 0.31; SPEC: API 5L; SMYS: 42000; MANU: AMERICAN STEEL; MANYR: 0; LOCLK: UNDER WATER; PNAME: DON CROSS; PHONE: 3134962460; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | ANCHOR HIT PIPELINE, GOUGE IN DENT WAS LEAKING AT 3 O'CLOCK POSITION, WHICHRESULTED IN THE LEAK. REPLACE D WITH 22'-4" OF 10" PIPE, 0.348 W.T. OCCURRED11/11/96, 1900 HOURS EST.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960190 | 1996-12-23 | 19160 | TENNESSEE GAS PIPELINE CO | HOUMA |  | LA | 70363 | 523M-2901+0.01 | 523M-2900 | 1500 | 1996-11-19 |  | YES | SS | 168A |  | YES | YES | LEAK | 0 | 0 | 0 | 80000 | 57582.9578 | 125445.8555 | Null | 0 | 0 |  | 19961125 | 1050 | 1200 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | VALVE |  | STEEL |  | PIPELINE |  | 1982 | 0 | 0 |  | 0 |  | BALL, CLASS 900 | GROVE | 1982 | UNDER WATER |  | DARON MOORE | 7137574023 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | SEE COMMENTS | YES | 19820906 | WATER |  | 4 | 2162 | CLAMP ON VALVE OPERATOR LEAKING AND POSSIBLE CRACK IN BODY OF THE VALVE. BUBBLES DISCOVERED AT OR NEAR 523M-2901 SUBSEA ASSEMBLY. DIVE BOAT ON SITE 11/20/96 AND ABLE TO LOCATE AREA ONLY. CHEVRON, JACK DUPRE INITIALLY NOTICED BUBBLES. TGP - ALLEN ASHLEY 3:00PM 11/21/96 LOOKED LIKE TGP. REPORTED 11/25/96 WAITED BECAUSE OF NOT BEING SURE IF LEAK WOULD BE GREATER THAN $50,000.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19960191 | 1996-12-24 | 18516 | SOUTHERN NATURAL GAS CO | ANNISTON | CALHOUN | AL |  | 381.785 M.P. ON | 24" N MAIN 2ND LOOP PIPE | 650 | 1996-11-24 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 30 |  | 19961124 | 650 | 750 | BY TEST | 1125 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: THREADED CONNECTION; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1979; NMDIA: 1; THK: 0.14; SMYS: 0; MANYR: 0; LOCLK: UNDER PAVEMENT; PNAME: DOUG DUHON; PHONE: 2058311131; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | A LEAK OCCURRED IN THE PIPE THREADS OF 1" PIPE AT ITS CONNECTION TO A 1" THREADED COUPLING. NEARBY RESIDENTS REPORTED THE LEAK TO THE LOCAL FIRE DEPARTMENT, WHICH PROMPLTY EVACUATED THE AREA. THE CAUSE OF THE LEAK IS UNKNOWN AT THIS TIME.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960192 | 1996-12-27 | 13750 | NORTHERN NATURAL GAS CO (ENRON) | BYRON | OLMSTED | MN |  | 34.30 |  | 2330 | 1996-11-28 | 1 | NO |  |  |  | Null | NO | RUPTURE | 34 | 0 | 0 | 100000 | 71978.6973 | 156807.3194 | Null | 3 | 30 |  | 19961129 | 370 | 490 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | NONE SPECIFIED | STEEL |  | PIPELINE |  | 1932 | 10 | 0.25 |  | 25000 | ERW |  | REPUBLIC | 1932 | UNDER GROUND |  | MERLIN MOSEMAN | 7136467344 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | SEE COMMENTS | NO |  | NO DATA |  | 0 | 0 | PIPE SUBMITTED FOR METALLURGICAL ANALYSIS TO DETERMINE CAUSE OF FAILURE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19960195 | 1998-09-08 | 405 | ANR PIPELINE CO | BRITTON | LENAWEE | MI |  | 944.6 | 112+55 TO 112+87 | 1100 | 1996-02-10 | 1 | NO |  |  | MI | Null | NO | RUPTURE | 31.5 | 0 | 0 | 450000 | 323904.1376 | 705632.9373 | Null | 0 | 30 |  | 19960210 | 769 | 858 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1966; NMDIA: 30; THK: 0.3; SPEC: API-5LX; SMYS: 60000; SEAM: DSAW; MANU: US STEEL; MANYR: 1966; LOCLK: UNDER GROUND; PNAME: DONALD E. CROSS SR; PHONE: 3134962460; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | THE FAILURE WAS THE RESULT OF EXTERNAL DAMAGE TO THE PIPELINE THAT MOSTPROBABLY OCCURRED FOUR MONTHS EARLIER DURING OUR OWN MAINTENANCE ACTIVITIESTHAT WE CONDUCTED IN THIS AREA.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19970005 | 1996-12-30 | 15007 | PACIFIC GAS & ELECTRIC CO | COALINGA | FRESNO | CA | 93210 | 374.5 | 19780+86 | 1115 | 1996-12-07 | 1 | NO |  |  | CA | Null | NO | RUPTURE | 0.5 | 0 | 0 | 78000 | 56143.3839 | 122309.7091 | Null | 1 | 15 |  | 19961207 | 655 | 840 | BY TEST | 983 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1958; NMDIA: 34; THK: 0.41; SPEC: API -5L; SMYS: 52000; SEAM: DSAW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: HEIDI LYDON; PHONE: 4159735191; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19961202; MARK: YES; MRKTP: SEE COMMENTS; STAT: YES; CTEST: Null | PART B- WOODEN LATHES WITH YELLOW RIBBON. A TRACK-WHEELED CATERPILLAR WITH A6' RIPPER DUG INTO TRANSMISSION LINE 300A AT APPROX MILE POST 374.5, HARRISRANCH, RURAL AREA NEAR COALINGA. EXCAVATOR WAS WORKING FOR HARRIS RANCH.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19970006 | 1997-01-09 | 15007 | PACIFIC GAS & ELECTRIC CO | ARBUCKLE | COLUSA | CA | 95912 | L172-MP 37.55 |  | 1700 | 1996-07-22 | 1 | NO |  |  |  | Null | NO | RUPTURE | 10 | 0 | 1 | 64000 | 46066.3662 | 100356.6844 | Null | 2 | 0 |  | 19960722 | 575 | 800 | BY TEST | 880 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1957; NMDIA: 20; THK: 0.28; SPEC: API5LX52; SMYS: 52000; SEAM: DSAW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: JEFF BORDERS; PHONE: 4159735568; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PIPELINE MARKERS IN PLACE; STAT: YES; CTEST: Null | OPERATOR OF TRACTOR/RIPPER RIPPED INTO TRANSMISSION LINE CAUSING TRACTOR TO BE BLOWN INTO AIR. OPERATOR WAS INJURED AND TAKEN TO HOSPITAL. OPERATOR RELEASED FROM HOSPITAL 7/23/96.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19970007 | 1997-01-02 | 21031 | VALERO TRANSMISSION CO | FREER | DUVAL | TX | 78357 |  |  | 1530 | 1996-12-03 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 100000 | 71978.6973 | 156807.3194 | Null | 1 | 0 |  | 19961203 | 645 | 1055 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: GAS COMPRESSOR; MLKD: OTHER; MLKDO: SEE COMMENTS; PRTSY: COMPRESSOR STATION; PRTYR: 1965; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: JOHN SOMMER; PHONE: 2102462395; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | GAS COMPRESSOR UNIT 98 HAD A VALVE COVER BLOW OFF CAUSING A FIRE. THE FIRE BLEW ACROSS UNIT 94 CAUSING THE COVER ON THE COMPRESSOR CRANKCASE TO BLOW OFF.UNITS 98, 94 AND 188 HAD FIRE DAMAGE. THE COMPRESSOR BUILDING WAS HEAVILY DAMAGED. MATERIALS INVOLVED: COMPRESSOR UNITS & COMPRESSOR BUILDING
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19970008 | 1997-01-02 | 20230 | KOCH GATEWAY | EIGHT MILE | MOBILE | AL | 36613 | .98 | 51 + 89 | 1100 | 1996-12-23 | 1 | NO |  |  |  | Null | Null | OTHER | 0 | 0 | 0 | 81425 | 58608.6542 | 127680.3598 | Null | 0 | 0 |  |  | 357 | 0 | BY TEST | 743 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: VALVE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1948; NMDIA: 16; THK: 0.34; SMYS: 24; SEAM: ELEC FUSION WEL; MANYR: 0; LOCLK: UNDER GROUND; PNAME: FRED CROSS; PHONE: 3344522862; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PERMANENT MARKERS; STAT: YES; CTEST: Null | CONTRACTOR WAS CAUTIONED TO NOTIFY KOCH PRIOR TO WORKING ON ROW, HOWEVER THEY DID BEGIN WORKING PRIOR TO NOTIFYING KOCH. CONTRACTOR WORKING OVER KOCH'S ROW WITHOUT PRIOR APPROVAL FROM KOCH. ALSO, CONTRACTOR HAD REMOVED SIGN PRIOR TO DIGGING.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19970009 | 1997-01-13 | 22617 | WILLIAMS NATURAL GAS CO | TONGANOXIE | LEAVENWORTH | KS | 66086 |  | 180 + 86 | 1647 | 1996-12-10 | 1 | NO |  |  |  | Null | Null | RUPTURE | 25 | 0 | 0 | 0 | 0 | 0 | YES | 3 | 20 |  | 19961210 | 484 | 720 | BY TEST | 900 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | OTHER | 20" "T" DRIP | STEEL |  | OTHER | NONE SPECIFIED | 1954 | 20 | 0.25 | API5LX | 52000 | EW |  | A.O. SMITH | 1953 | UNDER GROUND |  | JOE FREISBERG | 9185884193 | INTERNALLY | LOCALIZED PITTING |  | OTHER | NONE SPECIFIED | COATED | YES | 1954 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | FAILURE ANALYSIS TO BE COMPLETED IN 4 TO 6 WEEKS; 20' "T" DRIP FAILED ON LINE "EJ"
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19970015 | 1997-01-21 | 19590 | TRANSOK INC | CADDO | BRYAN | OK |  | L25-56 |  | 155 | 1997-01-10 | 2 | NO |  |  |  | Null | Null | OTHER | 0 | 0 | 0 | 58064 | 41064.7181 | 89460.4739 | Null | 1 | 0 |  | 19970110 | 836 | 1200 | BY TEST | 1800 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: RELIEF PILOT VALVE; MLKD: STEEL; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1996; NMDIA: 0; THK: 0; SMYS: 0; MANU: ANDERSON GREENWOOD; MANYR: 1996; LOCLK: ABOVE GROUND; PNAME: FRED DENNIS; PHONE: 9185912462; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | PILOT REGULATOR ON RELIEF VALVE FAILED CAUSING RELIEF VALVE TO OPEN.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19970016 | 1997-01-22 | 6660 | GREAT LAKES GAS TRANSMISSION CO | ST. CLAIR | ST. CLAIR | MI | 48079 | M.P. 969.88 | 8137+22 | 858 | 1996-10-30 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 0 | 135000 | 97171.2413 | 211689.8812 | Null | 0 | 0 |  | 19961030 | 850 | 974 | BY TEST | 1353 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: NO FAILURE; MLKD: OTHER; MLKDO: NO FAILURE; PRTSY: PIPELINE; PRTYR: 0; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: ROBERT CADORIN; PHONE: 3135964669; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | THERE WAS NO ADVERSE IMPACT ON PERSONS OR PROPERTY FROM THE VENTED GAS. IN ADDITION, IT WAS NOT ANTICIPATED IMMEDIATELY FOLLOWING THE EVENT THAT THE COSTOF CLEANUP WOULD EXCEED $50,000. HOWEVER, SINCE THE NUMBER OF CLAIMS MADE TOGREAT LAKES FOR CLEANUP OF THE LIQUID HAS ESCALATED, ESTIMATED EXPENDITURES BY GREAT LAKES TO REMOVE THE LIQUID FROM THE AREA ARE NOW IN THE RANGE OF $135,000. (IT IS LIKELY THAT ACTUAL DAMAGES TO PROPERTY, LOSS IN VALUE FROM THE INCIDENT, ARE LESS THAN $50,000, THOUGH THE CLEAN-UP AND INSPECTION COSTS AREHIGHER.) THIS REVISION IN ESTIMATED EXPENDITURES, THEREFORE, HAS PROMPTED GREAT LAKES TO FILE THE INCIDENT REPORT MENTIONED ABOVE, IN THE EVENT THE REPORTMIGHT OTHERWISE BE REQUIRED. SEE ORIGINAL REPORT FOR DETAILS OF EVENTS.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19970017 | 1997-01-28 | 14210 | OKLAHOMA NATURAL GAS CO | TULSA | TULSA | OK | 74037 |  |  | 1150 | 1996-12-27 | 2 | NO |  |  | OK | Null | NO | LEAK | 0 | 0 | 0 | 80798 | 58157.3478 | 126697.1779 | Null | 4 | 10 |  | 19961227 | 412 | 440 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1953; NMDIA: 18; THK: 0.25; SPEC: X-42; SMYS: 42000; SEAM: ERW; MANU: U.S. STEEL; MANYR: 1952; LOCLK: UNDER GROUND; PNAME: RL GAMBRELL; PHONE: 9185887404; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19961227; MARK: YES; MRKTP: PERMANENT; STAT: YES; CTEST: Null | CONSTRUCTION WAS NOT SUPPOSE TO BEGIN UNTIL 12/31/96. ONE-CALL WAS NOTIFIED AT 9:00 12/29/96 AND LINE WAS HIT AT 11:50 ON 12/29/96. LANDOWNER MADE A ONE-CALL REQUEST FOR WORK BEGINNING 12/31/96. CONTRACTOR STARTED WORK EARLY AND HIT THE LINE WHILE BURYING BRUSH. SUPPLEMENTAL REPORT RECEIVED 3/4/97 CHANGESONE CALL NOTIFICATION TO 9:00 ON 12/27/1996 AND LINE WAS HIT AT 11:50 ON12/27/1996.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19970019 | 1997-02-03 | 19570 | TRANSCO GAS PIPELINE CORP | CITRONELLE | MOBILE | AL |  | 70.034 | 3697+81 | 1100 | 1997-01-02 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 75515 | 53406.6235 | 116347.611 | Null | 3 | 0 |  | 19970102 | 900 | 1300 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1987; NMDIA: 30; THK: 0.39; SPEC: API 5L; SMYS: 70000; SEAM: DSA; MANU: ITALSIDER; MANYR: 1987; LOCLK: UNDER GROUND; PNAME: BR LANDES; PHONE: 7132152001; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: POSTED WITH SIGNS; STAT: YES; CTEST: Null | THE SIZE AND SHAPE OF THE GAUGE (12") INDICATES IT WAS CAUSED BY A LARGE PIECE OF EXCAVATION EQUIPMENT (PROBABLY) A BACKHOE. LEAK INITIATED IN GAUGE OFUNKNOWN ORIGIN.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19970020 | 1997-02-03 | 18516 | SOUTHERN NATURAL GAS CO | BOWDEN | CARROLL | GA | 30108 | 410.0 NORTH MAIN PIPELINE |  | 545 | 1997-01-07 | 1 | NO |  |  |  | Null | NO | RUPTURE | 38 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 30 |  | 19970107 | 480 | 500 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | MECHANICAL JOINT |  | STEEL |  | PIPELINE |  | 1930 | 20 | 0.31 |  | 30000 | BESSEMERLAPWELD |  | NATIONAL | 1930 | UNDER GROUND |  | WILLIAM MCCAIN | 7704786405 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | 20" DRESSER MECHANICAL COUPLING | YES | 19470101 | GAS |  | 0 | 498 | SEAL IN COUPLING APPEARS TO HAVE FAILED RESULTING IN A LEAK WHICH, AFTER A SHORT PERIOD OF TIME, BLEW ENOUGH SOIL AWAY TO DECREASE OVERBURDEN ALLOWING PIPE TOPULL OUT OF COUPLING. IT IS BELIEVED THAT A SEAL FAILED IN A MECHANICALCOUPLING RESULTING IN A LEAK WHICH, OVER A SHORT PERIOD OF TIME, REMOVED THESOIL COVER OVER THE PIPE. THIS DECREASED THE OVERBURDEN LOAD THAT KEPT IN PIPEAND COUPLING INTACT, ALLOWING THE PIPE TO BLOW OUT OF THE COUPLING, RELEASINGNATURAL GAS. THERE WAS NO GAS IGNITION.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19970027 | 1997-02-19 | 15105 | PANHANDLE EASTERN PIPELINE CO | FREEMAN | CASS | MO |  | 4.1 | 214+39 | 1653 | 1996-07-22 | 1 | NO |  |  | MO | Null | NO | RUPTURE | 89.1 | 0 | 0 | 180000 | 129561.6551 | 282253.1749 | Null | 0 | 30 |  | 19960722 | 770 | 800 | BY TEST | 1002 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1937 | 24 | 0.28 |  | 48000 | SMLS |  | NATIONAL TUBE | 1937 | UNDER GROUND |  | ROBERT MOODY | 7136275716 | EXTERNALLY | GENERAL CORROSION |  | OTHER | SEE COMMENTS | COATED | YES | 1957 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | GENERAL EXTERNAL CORROSION IN AN AREA OF DISBONDED COATING. INCIDENT LOCATION: 1/2 MI EAST & 1/2 MI SOUTH OF KANSAS-MISSOURI LINE & HIGHWAY 2.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19970028 | 1997-02-21 | 15007 | PACIFIC GAS & ELECTRIC CO | APTOS | SANTA CRUZ | CA | 95003 | ANZAL STATION, LINE 1813 |  | 916 | 1997-01-26 | 2 | NO |  |  |  | Null | NO | RUPTURE | 2 | 0 | 0 | 100000 | 70723.1987 | 154072.1857 | Null | 5 | 15 |  | 19970126 | 500 | 0 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; PRTFO: ELBOW/GIRTH; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1958; NMDIA: 10; THK: 0.22; SPEC: API5L GRADE B; SMYS: 35000; SEAM: ERW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: SHAN BHATTACHARYA; PHONE: 4159736998; PROT: Null; CAULK: NO DATA; DMGO: NONE SPECIFIED; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | HEAVY RAINFALL CAUSED LARGE MUDSLIDE THAT CAUSED LINE RUPTURED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19970029 | 1997-02-19 | 2714 | CNG TRANSMISSION CORP | QUINCY | KANAWHA | WV |  |  | 5+50 ON TL-272 PIPELINE | 730 | 1997-01-20 | 3 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 83200 | 58841.7013 | 128188.0585 | Null | 2 | 0 |  |  | 340 | 560 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1994; NMDIA: 12.75; THK: 0.38; SPEC: X-42 GR-B; SMYS: 0; SEAM: SEAMLESS; MANU: US STEEL; MANYR: 1994; LOCLK: UNDER GROUND; PNAME: MARTIN SCHWOEBIE; PHONE: 3046238408; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19960429; MARK: YES; MRKTP: WOODEN LINE STAKES; STAT: YES; CTEST: Null | BATTLE RIDGE CONSTRUCTION COMP CALLED THE MORNING OF 1/20/97 AND REPORTED THEY SMELLED GAS NEAR THEIR CONSTRUCTION AREA. CNGT PERSONNEL INVESTIGATED AND FOUND LEAK BLOWING ON TL-272. ISOLATED SECTION, EVACUATED GAS, FOUND SPLIT INPIPE APP. 2"LX1/4W. FAILURE WAS CAUSED BY LARGE SPOIL PILE ON LINE BY CONTRACTOR. COMP PRODUCTION: $45,950.00 - GATHERING: $3200.00.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19970030 | 1997-02-19 | 2714 | CNG TRANSMISSION CORP | WAYNESBURG | GREENE | PA |  | CRAYNE STATION | 1192+07 | 1415 | 1997-01-19 | 1 | NO |  |  | PA | Null | NO | OTHER | 0 | 0 | 0 | 62475 | 44184.3184 | 96256.598 | Null | 0 | 99 |  |  | 723 | 960 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | TRANSMISSION SYSTEM | OTHER | RELIEF VALVE | STEEL |  | COMPRESSOR STATION |  | 1989 | 0 | 0 |  | 0 |  | SEE COMMENTS | AXELSON | 1989 | ABOVE GROUND |  | MARTIN SCHWOEBLE | 3046238408 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | AXELSON 6" X 8" RELIEF VALVE | YES | 19960901 | OTHER | NITROGEN | 0 | 1008 | A COMBINATION OF CONDENSATION AND EXTREMELY COLD TEMPERATURES CAUSED THE AXELSON R/V TO FAIL @ A PRESSURE BELOW THE SET POINT OF 1008 PSIG. R/V COULD NOTRE-SEAT DUE TO A ROLLED O-RING. APPARENT CAUSE: WEATHER CONDITIONS. RELIEFVALVE, TYPE H-L, SN#8632.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19970037 | 1997-02-24 | 13845 | NORTHWEST PIPELINE CORP | KALAMA | COWLITZ | WA |  | MP 1254.3 | 10020+39.8 | 1930 | 1997-02-09 | 2 | NO |  |  |  | Null | NO | RUPTURE | 0.5 | 0 | 0 | 195000 | 137910.2375 | 300440.7621 | Null | 1 | 10 |  | 19970209 | 700 | 809 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: GIRTH; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1956; NMDIA: 26; THK: 0.28; SPEC: API 5L; SMYS: 52000; SEAM: DSAW; MANU: CONSOLIDATED WEST; MANYR: 1956; LOCLK: UNDER GROUND; PNAME: MOLLY MCANALLY; PHONE: 8015846797; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: LONG TERM CREEP; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | AXIAL SOIL LOADING ON THE PIPE CREATED LOADING IN EXCESS OF THE GIRTH WELD STRENGTH, PULLING THE PIPELINE APART WITH A CLEAN BREAK AT THE GIRTH WELD WHICH RESULTED IN RAPID GAS LOSS AND IGNITION.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19970038 | 1997-02-24 | 13845 | NORTHWEST PIPELINE CORP | EVERSON | WHATCOM | WA |  | MP 1474.34 | 21645+27 TO 21646+02 | 2320 | 1997-02-08 | 1 | NO |  |  |  | Null | NO | RUPTURE | 75 | 0 | 0 | 375000 | 265211.9952 | 577770.6964 | Null | 0 | 52 |  | 19970209 | 700 | 809 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1956; NMDIA: 26; THK: 0.28; SPEC: API 5L; SMYS: 52000; SEAM: DSAW; MANU: KAISER; MANYR: 1956; LOCLK: UNDER GROUND; PNAME: MOLLY MCANALLY; PHONE: 8015846797; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | LAND MOVEMENT FROM SIDE SLOPE PLACED LATERAL LOAD ON PIPELINE WHICH EXCEEDEDTHE YIELD STRENGTH, CAUSING THE PIPELINE TO RUPTURE. THE LINE RUPTURE OCCURRED ON 2/8/97, AT 11:20PM, MST. THE TELEPHONIC NOTICE WAS MADE AT 1:05 AM, MST02/09/97.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19970039 | 1997-03-07 | 1734 | BRIDGELINE GAS DISTRIBUTION CO |  | ST. MARY | LA |  | SEE COMMENTS | 6 + 00 | 530 | 1997-02-08 |  | YES | STATE LEASE | 300 | LA | Null | NO | RUPTURE | 100 | 0 | 0 | 200000 | 141446.3974 | 308144.3714 | Null | 0 | 45 |  | 19970208 | 960 | 1440 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1972; NMDIA: 20; THK: 0.35; SPEC: API-5LX; SMYS: 60000; SEAM: ERW; MANYR: 0; LOCLK: UNDER GROUND; LOCLO: UNDER WATER 10' BELOW`; PNAME: CHARLES HEBERT; PHONE: 3189373351; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19970201; MARK: YES; MRKTP: CANE POLES; STAT: YES; CTEST: Null | ATHENA SPUD BARGE SPUDDED DOWN NEAR THE 20" PIPELINE. INCLEMENT WEATHER MOVEDTHE SPUD BARGE INTO THE PIPELINE CAUSING THE RUPTURE. THE LEAK OCCURRED IN THE ATCHAFALAYA BAY IN ST. MARY PARISH, LA AT APPROX 5:30 A.M. FROM A 20" NATURAL GAS PIPELINE. THE LEAK WAS THE RESULT OF DAMAGE INCURRED FROM A "JACK-UP"TYPE BARGE DURING INCLEMENT WEATHER AS SHOWN ON THE ATTACHED REPORT FROM RSPA F7100.2. ESTIMATES OF REPAIRS ARE $200,000. THERE WERE NO INJURIES, FATALITIES, OR POLLUTION, AND AT NO TIME WAS THERE A THREAT TO THE COMMUNITY OR THEENVIRONMENT. MILE POST/VALVE STATION: 600' SW OF RABBIT ISLAND "D" PLATFORM.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19970046 | 1997-04-03 | 14026 | OASIS PIPELINE CO | OZONA | CROCKETT | TX | 76943 |  | 19776+17 | 200 | 1997-03-04 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 85140 | 60213.7314 | 131177.0589 | Null | 2 | 15 |  | 19970304 | 775 | 1050 | BY TEST | 2000 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: NONE SPECIFIED; MLKD: OTHER; MLKDO: NONE SPECIFIED; PRTSY: COMPRESSOR STATION; PRTYR: 1972; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: CLIFTON REED; PHONE: 2108753352; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | OZONA COMPRESSOR STATION BLOW DOWN VALVE OPENED INADVERTANTLY CAUSING A LOSSOF GAS WITHIN THE COMPRESSOR SITE. OTHER: CONTRO FUNCTION - GAS RELEASE
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19970047 | 1997-03-15 | 1007 | K N INTERSTATE GAS TRANSMISSION CO | FULLERTON | NANCE | NE | 68638 | MP25.81 | 1362+69 | 1355 | 1997-02-22 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 240000 | 169735.6769 | 369773.2457 | Null | 1 | 30 |  | 19970222 | 820 | 0 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: GIRTH; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1951; NMDIA: 10; THK: 0.5; SPEC: API; SMYS: 42000; SEAM: SEAMLESS; MANU: J & L STEEL; MANYR: 0; LOCLK: OTHER; LOCLO: RIVER; PNAME: STEVE HAWES; PHONE: 3037633457; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: ICE IN RIVER; NOTIF: Null; MARK: YES; MRKTP: PERMANENT MARKERS; STAT: NO; CTEST: Null | PIPELINE SEPARATED AT GIRTH WELD IN LOUP RIVER X-ING. UNABLE TO DETERMINEEXACT CAUSE BECAUSE OF LOCATION OF FAILED SEGMENT IN LOUP RIVER. RIVERCROSSING FAILED AT OR NEAR GIRTH WELD. POSSIBLY DUE TO ICE FLOW IN RIVER.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19970050 | 1997-04-08 | 22655 | WILLISTON BASIN INTERSTATE PIPELINE CO | FAIRVIEW | RICHLAND | MT | 59221 | 5176+67 | T24N,R59E,E1/2N1/2 SEC.36 | 2036 | 1997-03-20 | 1 | NO |  |  |  | Null | NO | RUPTURE |  | 0 | 0 | 0 | 0 | 0 | YES | 0 | 39 |  | 19970320 | 415 | 450 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | TEMPERATURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: GIRTH; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1930; NMDIA: 12; THK: 0.25; SPEC: A-O SMITH CORP; SMYS: 30000; SEAM: SMITH WELD; VALVE: NOT APPLICABLE; MANU: A-O SMITH CORP; MANYR: 0; LOCLK: UNDER GROUND; PNAME: CRAIG WAGNER; PHONE: 4063597216; PROT: Null; CAULK: EARTH MOVEMENT: FROST; DMGO: SUBSIDENCE; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | GIRTH WELD FAILED ON BURIED 12-INCH PIPELINE DUE TO SETTLING AND FROST HEAVE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19970051 | 1997-04-08 | 22655 | WILLISTON BASIN INTERSTATE PIPELINE CO | DEADWOOD | LAWRENCE | SD | 57732 | 270+81 | T6N,R3E,SE1/4NE1/4/SEC.35 | 1055 | 1997-03-19 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 0 | 0 | 0 | YES | 3 | 7 |  | 19970319 | 180 | 200 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1928; NMDIA: 8; THK: 0.25; SPEC: UKNOWN; SMYS: 24000; SEAM: UKNOWN; VALVE: N/A; MANU: UKNOWN; MANYR: 0; LOCLK: UNDER GROUND; PNAME: CRAIG WAGNER; PHONE: 4063597216; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: MARKER POSTS IN SIGHT OF; STAT: YES; CTEST: Null | A D-7 CRAWLER-TRACTOR WAS BEING USED FOR RECLAMATION WORK NEAR OUR 8-INCHPIPELINE WHEN IT RIPPER TOOTH HOOKED AND PUNCTURED THE TOP OF THE PIPE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19970052 | 1997-04-07 | 2204 | CENTRAL ILLINOIS PUBLIC SERVICE | ASHMORE | COLES | IL | 61912 | VLV.350-T-138 |  | 1240 | 1997-03-13 | 2 | NO |  |  | IL | NO | NO | LEAK |  | 0 | 0 | 750000 | 530423.9903 | 1155541.3927 | Null | 1 | 15 |  | 19970313 | 210 | 250 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | OTHER | GAS COMPRESSOR | STEEL |  | COMPRESSOR STATION |  | 1971 | 0 | 0 |  | 0 |  |  |  | 0 | OTHER | INSIDE COMPRESSOR BLDG | J.L. DAVIS | 2175255326 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION | WHITE SUPERIOR NATURAL GAS ENGINE/COMPRESSOR-#3 | YES | 19961210 | GAS |  | 1 | 143 | THE WHITE/SUPERIOR NATURAL GAS ENGINE/COMPRESSOR (UNIT #3) WAS OVERHAULED BYCOOPER ENERGY SERVICES, CURRENT OEM, IN 1996. THE OVERHAUL WORK WAS COMPLETED12/14/96. THE UNIT #3 HAD OPERATED 612 HOURS FROM START-UP UNTIL THE MARCH 13,1997 INCIDENT. PRELIMINARY INVESTIGATION REVEALED THAT THE BALANCE NUT ON THE#3 COMPRESSOR CYLINDER ASSEMBLY ON UNIT #3 WAS NOT TIGHT AGAINST THE ASSEMBLYCROSSHEAD. THE POSITION OF THE BALANCE NUT ALLOWED THE NUT TO BREAK THE WIPERPACKING GLAND OUT OF ITS PROPER POSITION. THE CONTINUED BEATING, OF THEBALANCE NUT ON THE WIPER PACKING GLAND WEB, EVENTUALLY BROKE THE JOINT WHERETHE #3 COMPRESSOR CYLINDER ASSEMBLY DISTANCE PIECE BOLTED TO THE COMPRESSORFRAME. MOVEMENT OF THE #3 COMPRESSOR CYLINDER ASSEMBLY AWAY FROM THECOMPRESSOR FRAME, OPENED THE SUCTION AND DISCHARGE FLANGE CONNECTIONS TO THECOMPRESSOR CYLINDER. THE LOOSE FLANGE CONNECTIONS ALLOWED GAS TO ESCAPE INTOTHE COMPRESSOR BUILDING. PRELIMINARY INVESTIGATION REVEALED NO FAILURE ORINTERNAL DAMAGE TO THE #3 COMPRESSOR CYLINDER.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19970056 | 1997-04-18 | 4280 | EL PASO NATURAL GAS CO | EL PASO | EL PASO | TX | 79978 | M.P.4+1771 ON LINE NO2058 | E.S.22+943 | 820 | 1997-03-21 | 3 | NO |  |  |  | Null | NO | RUPTURE | 54 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 40 |  | 19970321 | 660 | 763 | BY TEST | 1495 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: LONGITUDINAL; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1955; NMDIA: 8.63; THK: 0.19; SPEC: API5L; SMYS: 42000; SEAM: ERW; MANU: YOUNGSTOWN; MANYR: 0; LOCLK: UNDER GROUND; PNAME: RICHARD FAVILA; PHONE: 9154962062; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19970305; MARK: YES; MRKTP: METAL PIPELINE MARKERS; STAT: YES; CTEST: Null | AT APRROX. 8:20 AM ON 3/21/97 ELPASO'S 8-5/8 ELECTRIC CO LOOP LINE NO 2058RUPTRUED. THE SITE OF THE RUPTURE IS ON A CONSTUCTION SITE ON PROPERTY AT THENORTHWEST CORNER OF RESLER DR. AND REDD RD. IN EL PASO. FOUR PEOPLE WEREHOSPITLALIZED AND 2 WERE TREATED ON SITE. THE GAS DID NOT IGNITE AND THEREWERE NO FIRES DUE TO THE RUPTURE. THE PIPELINE SEGMENT WAS SHUT IN BY 9:00 AM.IT WAS FIRST BELEIVED THAT THE RUPTURE WAS DUE TO THE PIPELINE BEING HIT BYHEAVY CONSTRUCTION EQUIP. HOWEVER SUBSEQUENT INVESTIGATION REVEALED THATTHERUPTURES WAS STREES RELATED AND THAT THE PIPELINE RUPTUREDDUE TO THE WEIGHT OFA D-9 BULLDOZER PARKED ON TOP OF THE PIPELINE. THE PIPELINE WAS PROPERLYMARKED. THE PIPELINE WAS REPAIRED BY REPLACING 78.4 FEET OF PIPELINE AND WASBACK IN SERVICE BY 5:30 PM OF THE SAME DAY.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19970058 | 1997-04-23 | 405 | ANR PIPELINE CO | WEST CAMERON 182 |  | LA |  | X=1,385,532.56 | Y=252,915.57 | 1600 | 1997-03-21 | 1 | YES | WEST CAMERON | 182 | LA | YES | NO | LEAK |  | 0 | 0 | 90000 | 63650.8788 | 138664.9671 | Null | 0 | 0 |  | 19970321 | 1043 | 1440 | BY TEST | 2333 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | GATHERING SYSTEM | FITTING | 1/2" SEALENT PLUG | STEEL |  | OTHER | HOT TAP ASSSEMBY | 1997 | 0 | 0 |  | 0 |  |  |  | 0 | UNDER WATER |  | DON CROSS,SR | 3134962460 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | 1/2-INCH HYDRAULIC SEALANT PLUG | YES | 19970114 | WATER |  | 4 | 2333 | LEAKING 1/2" HYDRAULIC SEALANT FITTING (PLUG) ON SUBSEA HYDROTECH HOT TAPASSEMBLY.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19970059 | 1997-05-01 | 18516 | SOUTHERN NATURAL GAS CO | MT ZION | CARROLL | GA | 30150 | 414.045 NORTH MAIN PIPELI |  | 1125 | 1997-04-12 | 1 | NO |  |  |  | Null | NO | RUPTURE | 29.5 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 55 |  | 19970412 | 470 | 500 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | MECHANICAL JOINT |  | STEEL |  | PIPELINE |  | 1930 | 20 | 0.31 |  | 30000 | BESSEMER LAP WD |  | NATIONAL | 1930 | UNDER GROUND |  | WILLIAM MCCAIN | 7704786405 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | DRESSER MECHANICAL COUPLING | YES | 19470101 | GAS |  | 0 | 498 | IT IS BELIEVED THAT A SEAL FAILED IN A MECHANICAL COUPLING RESULTING IN APRESSURE RELEASE AND SUBSEQUENT PIPELINE RUPTURE AT THE COUPLING JOINT. THEREWAS NO GAS IGNITION.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19970061 | 1997-05-06 | 18516 | SOUTHERN NATURAL GAS CO | BIRMINGHAM |  | AL | 35203 | M.P 316.530 NORTH MAIN |  | 1500 | 1997-04-08 | 1 | NO |  |  |  | NO | NO | OTHER |  | 0 | 1 | 0 | 0 | 0 | Null | 0 | 1 |  | 19970408 | 150 | 200 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: 2" BULL PLUG; MLKD: STEEL; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1969; NMDIA: 2; THK: 0.22; SMYS: 0; MANYR: 0; LOCLK: NO DATA; PNAME: CYRUS HARPER; PHONE: 2053252260; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | EMPLOYEE REMOVED A 2" BULL PLUG NOT REALIZING THAT GAS PRESSURE WAS STILLPRESENT IN A SHORT PUP OF PIPE BEHIOND THE PLUG. THE PLUG BLEW OUT STRIKINGEMPLOYEE IN THE FACE. EMPLOYEE WAS HOSPITALIZED OVERNIGHT AFTER SUGICALREPAIR OF LACERATED TONGUE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19970062 | 1997-05-05 | 405 | ANR PIPELINE CO | HIGH ISLAND BLK 555 |  | TX |  | X=3,496,710.29 | Y=95,083.00 | 1130 | 1997-04-03 | 1 | YES | HIGH ISLAND | 555 | TX | YES | NO | LEAK |  | 0 | 0 | 700000 | 495062.391 | 1078505.2999 | Null | 0 | 0 |  | 19970403 | 1035 | 1440 | BY TEST | 2880 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; PRTFO: 2" BULL PLUG; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1981; NMDIA: 20; THK: 0.56; SPEC: API 5LX; SMYS: 52000; SEAM: ERW; MANYR: 0; LOCLK: UNDER WATER; PNAME: JOHN P LUCIDO; PHONE: 3134962460; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | 20" SUBSEA TAP WAS PULLED APART BY THE ANCHOR OF THE SHIP.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19970063 | 1997-05-08 | 6660 | GREAT LAKES GAS TRANSMISSION CO | RUDYARD | CHIPPEWA | MI | 49780 | MP 26.6 | 1347+32-1355+66 |  | 1997-04-07 | 1 | NO |  |  | MI | Null | NO | OTHER |  | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19970408 | 800 | 1142 | BY TEST | 1569 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: NO FAILURE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1968; NMDIA: 11; THK: 0.21; SPEC: API 5LX; SMYS: 42000; SEAM: ERW; MANU: REPUBLIC; MANYR: 1968; LOCLK: UNDER GROUND; PNAME: MARK DOMKE; PHONE: 3135964669; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | ON OR ABOUT APRIL 7 1997, GREAT LAKE S GAS TRANSMISSION COMPANY RECIEVED INFO.THAT A LARGE SCTION OF HILLSIDE HAD SUBSIDED IN THE AREA OF ITS SOO LATERAL 103/4 INCH MAINLINE AND 12 3/4 INCH LOOPLINE IN CHIPPEWA COUNTY, MICHIGAN ANDTHAT THE PIPELINES WERE PARTIALLY EXPOSED. GREAT LAKES IMMEDIATELY SENTPERSONNEL TO THE SITE TO INVESTIGATE AND FOUND THAT AN APPROXIMATELY 970 FEETOF MAIN AND LOOP LINE MOVED BETWEEN 45 AND 50 FEET LATERALLY AND 25 TO 30 FEETVERTICALLY. THE OPERATING PRESSURE OF BOTH LINES WAS SUBSEQUENTLY LOWERED FROMAPPROXIMATELY 800 PSIG TO 600 PSIG AT THE LOCATION AND PERSONNEL WEREDISPATCHED TO MAN BLOCK VALVES ON EITHER SIDE OF THE LANDSIDE AREA IN THEEVENT THAT THE LINES RUPTURED. AFFECTED CUSTOMERS WERE NOTIFIED OF THESITUATION ON APRIL 8, 1997. GREAT LAKES ALSO NOTIFIED THE DEPARTMENT OFTRANSPORTATION OFFICE LOCAL AUTHORITIES AND THE NATIONAL RESPONSE CENTER(NRC).NRC NOTIFICATION (CONFORMATION NO. 383039) WAS MADE T EDT O TUESDAY APRIL 8 ,1997. GRAT LAKES ALSO COMMISIONED A GEOTECHNICAL SURVEY TO ASSESS SOILSTABILITY AND ASSIST IN LOCATING PERMANENT REPLACEMENT PIPELINES. UPONINITITLA INVESTIGATION IT APPEARED THAT THE LANDSIDE WAS THE RESULT OFLATERALLY UNSTABLE SOILS DUE TO HIGH MOISTURE CONTENT AND A POSSIBLE LOSS OFLATERAL SUPPORT DUE TO EROSION SIDE CUTTING OF THE RIVER CHANNEL AT THE BASEOF THE SLOPE. THE PRELIMANARY INVESTIGATION ALSO REVEALED THAT THE AREA HADNOT YET STABILIZED AND FURTHER SHIFTS MIGFHT OCCUR. EFFORTS BEGAN TO STABILIZETHE SITE BY DIRECTING EXCESS AWAY FROM THE LANDSLIDE AREA. GREAT LAKES SOOLATERAL MAINLINE AND LOOPLINE PROVIDE THE SOLE TRANSPORTATION SOURCE FORNATURAL GSA TO THE COMMUNITIES OF RUDYARD AND SAULT STE. MARIE, MICHIGAN, ANDSAULT STE. MARIE ONTARIO, CANADA. THIS NECESSITATED GREAT LAKES TO BEGINEMERGENCY EFFORTS TO MAINTAIN TRANSPORTATION THROUGH THIS AREA OF ITS PIPELINESYSTEM. TO MAINTAIN SERVICE, GREAT LAKES INSTALLED IN A TEMPORARILY STABILIZEDAREA AN ABOVE-GROUND, 12 3/4 INCH DIAMETER EMERGENCY BYPASS LINE APPROX. 834FEET IN LENGHT THAT WOULD ALLOW FOR THE ISOLATION AND REMOVAL FROM SERVICE OFTHE IMPACTED MAINLINE AND LOOPLINE. ON SUNDAY APRIL 13,1997 TH EEXISTING 123/4 INCH LOOPLINE WAS REMOVED FROM SERVICE AND THE NEW 12 3/4 INCH TEMPORARYBYPASS LINE WHICH WAS PRESSURE TESTED THE PREVIOUS DSAY WAS PLACED INTOSERVICE AT 75% OF NORMAL OPERATING PRESSURE THE EXISTING 10 3/4 INCH MAINLINEWAS THEN SHUT IN AND BLOWN DOWN. FOLLOWING COMPLETION OF THE TEMPORARY BYPASS,GREAT LAKES BEGAN CONSTRUCTION OF A PERMANENT REROUTE AROUND TO THE SOUTHEASTOF THE LANDSLIDE AREA. THE TOTAL LENGHT OFHTE PERMANENT BYPASS IS APPROX. 1235FEET FOR BOTH THE 10 3/4 INCH MAINLINE AND THE 12 3/4 INCH LOOP. THE PERMANENT10 3/4 INCH MAINLINE BYPASS PRESSURE WAS COMPLETED ON SUNDAY, APRIL 20, 1997,AND WAS THEN TIED-IN AND PLACED INTO SERVICE ON TUESDAY, APRIL 22, 1997.AFTER THE MAINLINE WAS PLACED INTO SERVICE, THE TEMPORARY 12 3/4 INCH BYPASSWAS REMOVED FROM SERVICE AND THE PIPE SECTION BLOWN DOWN. THE PERMANENT 123/4 INCH LOOPLINE BYPASS PRESSURE TEST WAS COMPLETED ON MONDAY APRIL 21,1997, AND WAS THEN TIED IN AND PLACED INTO SERVICE ON WED., APRIL 23, 1997.FOLLOWING COMPLETION OG THE PERMANENT BYPASS CONSTRUCTION, THE TEMPORARY 123/4 INCH BYPASS AND THE IMPACTED PORTIONS OF THE MAINLINE AND LOOPLINE WERECUT INTO SECTIONS AND REMOVED FROM THE SITE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19970064 | 1997-05-05 | 21031 | VALERO TRANSMISSION CO | LA REFORMA | STARR | TX |  | 39.6 TO 39.7 | 2092+47 TO 2098+49 | 830 | 1997-03-26 | 1 | NO |  |  |  | Null | NO | RUPTURE | 602 | 0 | 0 | 250000 | 176807.9968 | 385180.4642 | Null | 1 | 30 |  | 19970326 | 981 | 1020 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1959 | 20 | 2.81 | API5LX52 | 52000 | DSAW |  |  | 0 | UNDER GROUND |  | KEVIN SEHY | 2102463215 | EXTERNALLY | OTHER | LIGHT SURFACE PITTING | OTHER | STRESS CORR. | COATED | YES | 1960 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19970065 | 1997-05-02 | 15105 | PANHANDLE EASTERN PIPELINE CO | CENTRALIA | BOONE | MO | 65240 |  | 75+07 | 420 | 1997-04-20 | 1 | NO |  |  |  | Null | NO | RUPTURE | 40 | 0 | 0 | 500000 | 353615.9936 | 770360.9285 | Null | 1 | 15 |  | 19970420 | 898 | 900 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1948 | 26 | 0.31 | API-5L | 52 | SEAMLESS | N/A | U.S. STEEL | 1948 | UNDER GROUND |  | DAVID L BERLIN | 3166261308 | EXTERNALLY | OTHER | STRESS CORROSION CRACKING | OTHER | UNDER INVESTIGATION | COATED | YES | 1951 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | UNDER INVESTIGATION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19970066 | 1997-05-13 | 2620 | COLUMBIA GULF TRANSMISSION CO | BANNER | CALHOUN | MS | 38965 | VALVE STATION BANNER STA |  | 2040 | 1997-04-18 | 3 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 60000 | 42433.9192 | 92443.3114 | Null | 0 | 3 |  | 19970419 | 875 | 935 | NO DATA | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: COMPRESSER; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1954; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 1954; LOCLK: ABOVE GROUND; PNAME: HENRY WANG; PHONE: 7132674371; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: MATERIAL; CAULO: PROBLEM WITH ORIGINAL EQUIPMENT; CTEST: NO; MED: NO DATA; TMPS: 0; LKPS: 0 | THE VALVE PLUG FROM SUCTION SIDE CLEARANCE POCKET CAME OFF FROM VALVE STEMCAUSING COMPRESSOR HEAD STRIPPED OFF FROM COMPRESSOR. CONSTRUCTION DEFECT:CAUSE OTHER: PROBLEM WITH ORIGINAL EQUIPMENT.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19970067 | 1997-05-12 | 21031 | VALERO TRANSMISSION CO | LA REFORMA | STARR | TX | 78536 | 42.4T TO 42.5 | 2241+26 TO 2245+18 | 1600 | 1997-04-14 | 1 | NO |  |  |  | Null | NO | RUPTURE | 315 | 0 | 0 | 125000 | 88403.9984 | 192590.2321 | Null | 1 | 0 |  | 19970414 | 975 | 1020 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1959 | 20 | 2.5 | API52X52 | 52000 | DSAW |  |  | 0 | UNDER GROUND |  | KEVIN SEHY | 2102462395 | EXTERNALLY | OTHER | LIGHT SURFACE PITTING | OTHER | STRESS CORROSION | COATED | YES | 1960 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | LINE FAILURE DUE TO STRESS CORROSION CRACKING.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19970077 | 1997-06-03 | 18516 | SOUTHERN NATURAL GAS CO | MT ZION | CARROLL | GA |  | 414-035 NORTH MAIN PIPE |  | 1050 | 1997-05-03 | 1 | NO |  |  |  | Null | NO | RUPTURE | 36 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 15 |  | 19970503 | 470 | 500 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | MECHANICAL JOINT |  | STEEL |  | PIPELINE |  | 1930 | 20 | 0.31 |  | 30000 | BESSEMER LAP |  | NATIONAL | 1930 | UNDER GROUND |  | WILLAIM MCCAIN | 7704786405 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | 20 INCH DRESSER MECH COUPLING | YES | 19470101 | GAS |  | 0 | 498 | A PIPE CONNECTION IN A MECHANICAL COUPLING FAILED, RESULTING IN A PRESSURERELEASE AND SUBSEQUENT PIPELINE RUPTURE AT THE COUPLING JOINT. THE GAS IGNITEDAND BURNED SURROUNDING VEGETATION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19970078 | 1997-06-10 | 2564 | COLORADO INTERSTATE GAS CO |  | ALBANY | WY |  |  | 7107+50 | 8 | 1997-05-14 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 51000 | 36068.8313 | 78576.8147 | Null | 0 | 0 |  | 19970515 | 765 | 850 | BY TEST | 935 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | LONGITUDINAL | STEEL |  | PIPELINE |  | 1956 | 22 | 0.25 | API 5LX | 52000 | ERW DIRECT CURR |  | YOUNGSTOWN | 1955 | UNDER GROUND |  | RICHARD FLINT | 7195204350 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL |  | YES | 19700710 | GAS |  | 0 | 935 | C.1. LKEAK WAS AT A SMALL 1/4 LONG CRACK IN THE LONGITUDINAL WELD. C.3.C. TESTDURATION IS UNKNOWN. LEAK WAS DISCOVERED BY A GAS DETECTION INSTRUMENT DURINGA ROUTINE LEAK SURVEY. ALTHOUGH ONLY 44 FEET OF PIPE WAS REPLACED, THE REPAIRCOSTS EXCEEDED $50,000 DUE TO THE ADDITIONAL TIME, PERSONNEL. AND EQUIPMENTNECESSITATED BY THE HIGH WATER TABLE AT THE REPAIR SITE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19970079 | 1997-06-11 | 4900 | TEJAS GAS PIPELINE CO |  | RUSK | TX | 75682 | 426'EAST OF LONDON JCT | 1810+38 | 2005 | 1997-05-05 | 1 | NO |  |  |  | Null | NO | RUPTURE | 37 | 0 | 0 | 48523 | 34317.0177 | 74760.4467 | Null | 0 | 40 |  | 19970505 | 700 | 820 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | WELD | LONGITUDINAL | STEEL |  | PIPELINE |  | 1955 | 10 | 0.25 | X42 | 42000 | ERW |  | LONG STAR STEEL | 1955 | UNDER GROUND |  | GARY PARK | 9036573113 | INTERNALLY | OTHER | PITTING PATH | OTHER | ERW SEAM | COATED | YES | 1955 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | INTERNAL CORROSION PIT ON ERW SEAM, AND THE SEAM WAS NOT IN THE NEUTRAL ZONEAT A FIELD BEND. (SEAM WAS AT 5:30) SEAM INSTALLED AT THE 5:30 POSITION ANDWAS IN A LOW SPOT (LIQUID TRAP).
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19970080 | 1997-06-10 | 19035 | TALCO ASPHALT OIL CO | WASKOM | HARRISON | TX | 77569 |  |  | 800 | 1997-05-27 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 0 | 0 | 0 | Null | 0 | 10 |  | 19970527 | 180 | 1440 | BY TEST | 2160 | CORROSION | CORROSION | INTERNAL | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: NO DATA; PRTSY: NO DATA; PRTYR: 0; NMDIA: 45; THK: 0.19; SPEC: TGGF3X42; SMYS: 0; MANYR: 0; LOCLK: NO DATA; PNAME: NICK MAYFILED; PHONE: 9036872541; LOC: INTERNALLY; ADESC: NO DATA; CAUCR: NO DATA; COAT: COATED; PROT: YES; CPYR: 1987; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19970081 | 1997-06-25 | 11680 | LONE STAR PIPELINE CO (TRANSMISSION DIVISION) | TATUM | RUSK | TX | 75201 | 91 | 4827+21 | 758 | 1997-05-13 | 1 | NO |  |  |  | Null | NO | RUPTURE | 8 | 0 | 1 | 110000 | 77795.5186 | 169479.4043 | Null | 1 | 15 |  | 19970513 | 830 | 1200 | BY TEST | 1590 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1946; NMDIA: 14; THK: 0.26; SPEC: NONSTAD; SMYS: 45000; SEAM: ERW; MANYR: 1946; LOCLK: UNDER GROUND; PNAME: ED OSTROVICH; PHONE: 2145733158; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PIPELINE MARKERS 5' E & 2; STAT: NO; CTEST: Null | LINE WAS STRUCK BY MOTOR GRADER OPERATED BY RUSK COUNTY, TX. PERSONNEL
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19970082 | 1997-06-25 | 13480 | NIAGARA MOHAWK POWER CORP | RT. 22A | ELLISBURG | NY |  | P.L. 39-11 VALVE |  | 1130 | 1997-05-05 | 2 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 60000 | 42433.9192 | 92443.3114 | Null | 1 | 39 |  | 19970505 | 450 | 470 | BY TEST | 1200 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1962; NMDIA: 12; THK: 0.25; SMYS: 26; SEAM: ERW; VALVE: PLUG; MANU: BETHLEHEM; MANYR: 1962; LOCLK: UNDER GROUND; PNAME: THOMAS GILBERT; PHONE: 3154601148; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: Null; MARK: Null; MRKTP: PIPELINE MARKERS VISIBLE; STAT: YES; CTEST: Null
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19970083 | 1997-06-25 | 19133 | TPC SERVICES, INC. | HOUSTON | HARRIS | TX | 77079 |  |  | 1036 | 1997-05-20 |  | YES | MI | 485 |  | Null | NO | LEAK |  | 0 | 0 | 0 | 0 | 0 | Null | 24 | 0 |  | 19970520 | 1100 | 1228 | BY TEST | 1560 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | WELD | GIRTH | STEEL |  | PIPELINE |  | 1977 | 20 | 0.41 | API 5LX-42 | 42000 | DSAW |  |  | 0 | UNDER WATER |  | J HAYNES BLANK | 2815976200 | INTERNALLY | GENERAL CORROSION |  | NO DATA |  | COATED | YES | 1977 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | AT 10:30 AM MAY 20 1997 A CALL WAS RECIEVED AT TPC'S OPERATIONS CENTER STATINGTHAT BUBBLES WERE REPORTED IN MATAGORDA ISLAND BLOCK 485 APPROX. ONE HALF MILETO THE NORTH TO TPC'S MI 485 MAINFOLD PLAT FORM. A TECHNICIAN WAS SENT OUT BYHELICOPTER TO OVERFKY THE AREA WHERE THE BUBBLES WERE SPOTTED AND TO GETACCUATRE COORDINATES ON THE LEAK. AT 11:30 THE TECHNICIAN REPORTED THAT THEBUBBLES WERE A[PPROX. ONE HALF MILE NORHT OF OUR 485 MAINFOLD PLATFORM ANDTHAT THERE WAS NO VISIBLE SHEEN. BECAUSE WE HAVE TWO 20" NATURAL GAS PIPELINES THAT PASS VERY CLOSE TO THE BUBBLE SITE, THE VICTORIA OFFICE BEGAN TO LINEUP A DIVE BOAT AND DIVERS T GO OUT AND INVESTIGATE THE LEAK SORCE.NOTIFICATION CALLS WERE MADE TO NRC TEXAS RAILROAFD COMMISIOIN , TEXAS GENERALLAND OFFICE, AND THE U.S. COAST GUARD IN PORT LAVACA. THE DIVERS AND DIVE BOATWERE SET UP TO LEAVE PORT O'CONNER TEXAS AT 3:00 PM MAY 20 1997. BY 4:00 PMDIVERS ARRIVED AT THE LEAK SITE AND BEGAN PREPARATIONS TO DIVE ON THE LEAK.THE LEAK WAS LOCATED AT 6:45 PM, LEAK SITE COORDINATES WERE TAKEN AND IT WASDETERMINED THAT THE LEAK WAS ON ONE OF TWO 20" PIPELINES. ONCE THE SITECOORDINATES WERE CALLED IN THE LEAK SITE WAS PLOTTED AND IT WAS DETERMINEDTHAT THE LEAK WAS PROBABLY COMING FROM THE 20" EL GODO PIPELINE AND TO BLOWTHE PIPELLINE DOWN. THIS WAS SCHEDULED TO OCCUR AT 6:00 AM JUNE 21 1997. INADDITION , AMERICAN OILFIELD DIVERS, WAS CONTACTED TO DETERMINE THEAVAILABILITY OF A 20" REPAIR CLAMP, A FOUR POINT DIVE BOAT , AND A DIVE TEAM.AOD RESPONDED THAT THEY WOULD HAVE A DIVE BOAT , DIVERS, AND ALL THENECCESSARY EQUIPMENT READY TO DEPART PORT O'CONNER AT 3:00 AM ON MAY 22 1997.ON WED. MORNING THEY CALLED BACK TO CHANGE THE TIME TO 12:00 AM MAY 22 1997AND CHANGE THE DEPARTURE LOCATION TO THE GRASSO DOCKS AT FREEPORT TEXAS. ATAROUND 8:00 AM WED. MORNING THE TEXAS GENERAL LAND OFFICE CALLED FOR AN UPDATEAND THE COAST GUARD WAS UPDATED ON THE SITUATION, A COURTESY CALL WAS ALSOPLACED TO THE TNRCC TO REPORT THE VENTING OF THE GAS AT OYSTER LAKE DURINGTHE BLOW OF THE EL GORDO PIPELINE/ THE LEAK SITE WAS OVERFLOWN AND NO SHEENCOULD BE DETECTED ON THE WATER. BY 10:15 AM MAY 22, 1997 TH EDIVE BOAT ADCREW WERE ON THE LAKE SITE. THE BUBBLES HAD DIMINSHED GREATLY HOWEVER, ASMALL SHEEN HAD FORMED. COORDINATES OF THE LEAK SITE WERE CALLED IN AND WEREX2907009.71 AND Y217878.13. THESE COORDINATES CONFIRMED THAT THE LEAK WAS ONTHE EL GORDO PIPELINE. THE DIVERS SPENT MOST OF THE DAY TRYING TO REMOVE THECONCRETE OFF THE PIPE. BY 6:37 AM MAY 23, 1997 SUFFICENT CONCRETE AND MASTICHAD BEEN REMOVED AT THE LEAK LOCATION ON THE PIPE TO INSTALL THE REPAIR CLAMP.AFTER THE REPAIR CLAMP WAS INSTALLED THE PIPELINE WAS REPRESSURED UP ANDADIVER WAS SENT DOWN TO CHECK THE REPAIR CLAMP FOR LEAKS. NO GAS BUBBLES WEREDETECTED COMING FROM THE REPAIR CLAMP, SO THE DIVER APPLIED A PROTECTIVECOATINGOF SYNTHOGLASS TO ALL EXPOSED AREWWAS OF PIPE. AT 9:00 AM MAY 24, 1997THE DIVE BOAT DEPARTED THE JOB SITE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19970088 | 1997-06-25 | 6141 | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | SANTA FE | SANTA FE | NM | 87504 | 52 |  | 1130 | 1997-05-01 | 3 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 50000 | 35361.5994 | 77036.0928 | YES | 1 | 15 |  | 19970501 | 480 | 600 | BY CFR 192.619(A)(3) | 900 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; NMDIA: 12; THK: 0.2; SPEC: 5LX; SMYS: 42000; SEAM: ERW; LOCLK: UNDER GROUND; PNAME: KELLY BOUSKA; PHONE: 5052414414; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19970501; MARK: YES; MRKTP: ROOSTER TAILS/PAINT; STAT: YES; CTEST: Null | MCC, CONTRACTOR INSTALLING A WATER LINE HAD PHONED FOR LINE SPOTS TO NEWMEXICO ONE CALL SYSTEM(#97043007440022). LINE SPOTS WERE COMPLETED BY PNMGAS SERVICES USING ROOSTER TAILS AND PAINT AT 8:50 AM ON 5-1-97. AT 11:30AM MCC KNOCKED A 2' PURGING TEE OFF THE 12" SANTA FE TRANSMISSION LINE.THIS DAMAGE OCCURED BECAUSE MCC DIDNT USE CAUTION AND MAINTAIN 18"CLEARENCE FROM THE TRANSMISSION LINE WHILE EXCAVATING. THREE MCC CREWMEMBERS WERE TAKEN TO THE HOSPITAL FOR MINOR INJURIES BUT WERE NOTADMITTED. THE BLOWING LINE WAS CONTROLLED AT 12:45 PM.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19970089 | 1995-01-31 | 144 | AJAX PIPELINE CO | DUNBAR | KANAWHA | WV | 25064 | 2043 WILSON STREET |  | 1300 | 1994-08-14 | 3 | NO |  |  |  | Null | NO | RUPTURE |  | 0 | 3 | 0 | 0 | 0 | YES |  |  |  | 19940814 | 30 | 60 | BY CFR 192.619(A)(3) | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; MLKD: OTHER; MLKDO: PLASTIC; PRTYR: 1994; NMDIA: 4; LOCLK: UNDER GROUND; PNAME: RUSSEL LYON; PHONE: 3043432201; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | GAS IGNITED WHEN IGNITED LINE WAS BEING PUMPED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19970090 | 1997-06-26 | 602 | NORAM GAS TRANSMISSION, A NORAM ENERGY COMPANY | CANADIAN | HEMPHILL | TX |  | 7 | 512+71 | 230 | 1996-08-26 | 1 | NO |  |  |  | Null | NO | RUPTURE | 96 | 0 | 0 | 66000 | 47505.9402 | 103492.8308 | Null | 1 | 30 |  | 19960826 | 995 | 1000 | BY TEST | 1800 | CORROSION | CORROSION | INTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1972; NMDIA: 12; THK: 2.5; SPEC: ERW; SMYS: 46000; LOCLK: UNDER GROUND; PNAME: TED VANDE KAMP; PHONE: 3184293606; LOC: INTERNALLY; ADESC: GENERAL CORROSION; COAT: COATED; PROT: YES; CPYR: 1972; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | FAILURE OCCURRED IN PITTED AREA LOCATED ON BOTTON QUADRANT INSIDE PIPE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19970091 | 1996-06-26 | 12576 | MISSISSIPPI RIVER TRANSMISSION CORP | ALICIA | LAWERENCE | AR | 72410 | 234 | 778+58 | 1200 | 1996-12-14 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 56664 | 40786.009 | 88853.2995 | Null | 1 | 30 |  |  | 605 | 720 | BY TEST | 1100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1996; NMDIA: 2.38; THK: 0.22; SPEC: GNB; SMYS: 35000; SEAM: SMLS; LOCLK: UNDER GROUND; PNAME: TED VANDE KAMP; PHONE: 3184293606; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | P
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19970092 | 1997-06-30 | 6580 | GRANITE STATE GAS TRANSMISSION INC | SOUTH BERWICK | YORK | ME | 03908 |  | 125+00 | 815 | 1997-05-20 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 0 | 0 | 0 | Null | 0 | 0 |  |  | 375 | 500 | BY TEST | 900 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: NO DATA; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1968; NMDIA: 8.63; THK: 0.16; SPEC: 1266; SMYS: 0; SEAM: ERW; MANU: REPUBLIC STEEL; MANYR: 1968; LOCLK: UNDER WATER; PNAME: KENNETH BYRD; PHONE: 6034360310; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: 3; STAT: YES; CTEST: Null | TRAVELED HEAVY TRACK EQUIPMENT ACROSS PIPELINE ROW THRU YEAR ROUNDWETLANDAREA. MACHINE SANK IN SOFT SOIL COMING INTO CONTACT WITH PIPE.PIPELINE WAS TAKEN OUT OF SERVICE AND DAMAGED SECTION REPLACED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19970093 | 1997-06-30 | 19730 | TRUNKLINE GAS CO | WEST CARROLL PARISH |  | LA | 59 | 1.04 | 54+99 | 35 | 1997-05-23 | 1 | NO |  |  |  | Null | NO | RUPTURE | 22 |  |  | 125000 | 88403.9984 | 192590.2321 | Null | 1 | 45 |  | 19970523 | 1135 | 1440 | BY TEST | 1855 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | OTHER | STORAGE FEILD | 1979 | 12 | 0.22 | 5LX | 60000 | ERW |  | US STEEL | 1979 | UNDER GROUND |  | DWAYNE TESCHENDORF | 7136275573 | INTERNALLY | LOCALIZED PITTING |  | OTHER | SALT WATER | COATED | YES |  | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | NO DATA
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19970094 | 1997-07-15 | 602 | NORAM GAS TRANSMISSION, A NORAM ENERGY COMPANY | HARELTON | HARRISON | TX |  |  | 834+60 | 1200 | 1997-06-17 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 158500 | 112096.27 | 244204.4143 | Null | 2 | 4 |  | 19970617 | 720 | 1000 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1947; NMDIA: 8; THK: 2.8; SMYS: 24000; MANYR: 0; LOCLK: OTHER; LOCLO: EDGE OF CREEK; PNAME: TED VANDE KAMP; PHONE: 3184293606; LOC: EXTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: GALVANIC; COAT: COATED; PROT: YES; CPYR: 1955; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | THERE WERE 2 LEAKS WITHIN 3' AREA ON BOTTOM SIDE OF PIPE. ONE ABOUT THE SIZEOF 1 1/2" & THE OTHER MAYBE 1/8". IN NORROW CREEK 2' WIDER & 1' DEEP. PIPELINEWAS FOUND TO BE PARTIALLY EXPOSED IN CREEK, COATING FOUND TO BE DETERIORATED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19970095 | 1997-07-07 | 405 | ANR PIPELINE CO | COASTAL WATERS | LOUISIANA | LA |  | M.P.5 | 608+10 | 2000 | 1997-06-08 | 1 | YES | VERMILION BAY |  | LA | NO | NO | LEAK |  | 0 | 0 | 50000 | 35361.5994 | 77036.0928 | Null | 0 | 0 |  | 19970608 | 848 | 1100 | BY TEST | 1645 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1966 | 12 | 0.25 | API5LX | 42000 | ERW |  | STUPP | 1966 | UNDER WATER |  | DON CROSS | 3134962460 | INTERNALLY | NO DATA |  | NO DATA |  | COATED | YES | 1966 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | PIPELINE WAS CONCRETE COATED WITH SOMATIC WRAP. INTERNAL CORROSION - PIN HOLELEAK AT 7 OCLOCK POSITION.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19970096 | 1997-07-07 | 19160 | TENNESSEE GAS PIPELINE CO | BAY | ST LOUIS | MS | 39558 |  | 530 | 443 | 1997-06-02 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 3500000 | 2475311.9549 | 5392526.4994 | Null | 0 | 27 |  | 19970602 | 893 | 936 | BY TEST | 1350 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: MECHANICAL JOINT; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1962; NMDIA: 0; THK: 0; SMYS: 0; MANU: INGERSOL RAND; MANYR: 1962; LOCLK: OTHER; LOCLO: COMPRESSOR BUILDING; PNAME: DARON MOORE; PHONE: 7137574023; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | BOLT FAILURE ON COMPRESSOR VALVE CAP ALLOWED GAS TO BE RELEASED RESULTING INTHE FIRE AND EXPLOSION IN BUILDING A AT STATION 530.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19970105 | 1997-08-18 | 18516 | SOUTHERN NATURAL GAS CO | ST. BERNARD PARISH |  | LA |  | 10.726 ON 6" ELOI BAY PIP | X= 2,621, 317; Y=400, 031 | 1805 | 1997-07-19 |  | YES | ACTUALLY IN ST. WATR |  | LA | Null | NO | OTHER |  | 0 | 0 | 75000 | 53042.399 | 115554.1393 | Null | 0 | 0 |  | 19970719 | 900 | 1050 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: METER STATION PIPING; MLKD: STEEL; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1958; NMDIA: 6.63; THK: 0.25; SPEC: API 5L GRADE B; SMYS: 35000; SEAM: ERW; MANU: LUCEY; MANYR: 1958; LOCLK: OTHER; LOCLO: ABOVE WATER; PNAME: KENNETH PETERS; PHONE: 2053257632; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: HURRICANE DANNY; NOTIF: NO; MARK: Null; MRKTP: 0; STAT: NO; CTEST: Null | STORM FORCES FROM HURRICANE DANNY NDAMAGED THE PLATFORM SUPPORT FOR THE METERRUNS AT MILEPOST 10.762 ON THE 6" ELOI BY PIPELINE SUCH THAT METER PIPING WASSEVERED CAUSING A RELEASE OF GAS. THERE WAS NO IGNITION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19970108 | 1997-08-14 | 22365 | WESTAR TRANSMISSION CO | TERRY COUNT SECTION 155 |  | TX |  | LINE 0471-000 |  | 910 | 1997-07-24 | 1 | NO |  |  |  | Null | NO | RUPTURE |  | 0 | 0 | 50000 | 35361.5994 | 77036.0928 | Null | 10 | 35 |  | 19970724 | 320 | 659 | BY TEST | 725 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; PRTFO: METER STATION PIPING; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1956; NMDIA: 4.5; THK: 2.37; SPEC: RGADE B; SMYS: 3686; SEAM: SEAMLESS; VALVE: ANSI 600; MANU: 455; MANYR: 1956; LOCLK: UNDER GROUND; PNAME: STEVE BUSTOS; PHONE: 8067473037; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PERMANENT P/L MARKERS; STAT: NO; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19970109 | 1997-08-25 | 2364 | CINCINNATI GAS & ELECTRIC CO | UNION TWP | BUTLER | OH | 45069 |  |  | 1015 | 1997-07-14 | 4 | NO |  |  | OH | Null | NO | LEAK |  | 0 | 0 | 50000 | 35361.5994 | 77036.0928 | Null | 6 | 20 |  | 19970715 | 150 | 175 | BY TEST | 175 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1962; NMDIA: 20; THK: 0.28; SMYS: 0; MANU: YOUNGSTOWN STEEL; MANYR: 1962; LOCLK: UNDER GROUND; PNAME: WILLIAM HOBITZELL; PHONE: 5132873921; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19970710; MARK: YES; MRKTP: YELLOW PAINT AND TEMPORAR; STAT: YES; CTEST: Null | STILL UNDER INVESTIGATION AND WILL BE PROVIDED BY A SUPPLEMENTAL REPORT.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19970116 | 1997-08-29 | 8040 | ILLINOIS POWER CO | HIGHLAND | MADISON | IL | 62249 |  |  | 1430 | 1997-07-29 | 3 | NO |  |  | IL | NO | NO | OTHER |  | 0 | 0 | 151000 | 106792.0301 | 232649.0004 | Null | 9 | 40 |  | 19970731 | 632 | 850 | BY TEST | 1310 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1961; NMDIA: 10; THK: 0.25; SPEC: X-42; SMYS: 42000; SEAM: ERW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: DON JOHNSON; PHONE: 2174247001; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PAINT; STAT: YES; CTEST: Null | ON JULY 29, 1997 AT APPROX. 1450 HRS A THIRD PARTY DUG INTO THE 10" MAIN ATHIGHLAND AND CUT IN THE PIPE APPROX. 6" BY 3'. THE APPROPRIATE PERSONNEL WERENOTIFIED AND BEGAN TO RESTORE TO NORMAL CONDITIONS. BECAUSE GAS WAS VENTING TOATMOSPHERE, GAS SUPPLY DISPATCHERS TOOK APPROPRIATE ACTION TO REDUCE PRESSUREON THE DAMAGED LINE.AT 1710 HRS. THE BULLDOZER WAS STILL IN THE LINE ANDCATHODIC PROTECTION PERSONNEL HAD BEEN REQESTED TO SHUT OFF RECTIFIERSTATIONS. AT 1800 HRS. THE LINE WAS SHUT DOWN TO 105 PSI. AT 1910 HRS.PERSONNEL WERE CALLED TO BRING IN THE CNG TRAILOR AS A BACKUP FOR ST. JACOB.TH NUMBER OF CUSTOMERS THAT WOULD BE AFFECTED HAQD AN OUTAGE OCCURRED WASAPPROX. 500 IN ST. JACOB AND 384 IN HIGHLAND. DECISION WAS MADE TO MAKE ATEMPORARY REPAIR USING A DRESSER SLEEVE RATED FOR 500 PSI. AT 2310 HRS. THEAREA BEGAN LOWERING THE LINE TO 60 PSI. ON JULY 30 1997, APPROX. 0130 HRS.TEMPORARY REPAIRS WERE COMPLETED. FOR OPERATIONS THE VALVE AT HIGHLAND WASCLOSED AND PETERS#2 WAS PUT ON BYPASS. ALL THE GAS SERVING THE AREA WAS COMINGFROM HOFFMAN, THROUGH THE HILLSBORO TRANSFER STATION DOWN THROUGH FRANKLIN ST.IN SUMMARY TEMPORARY REPAR WAS COMPLETED WITHOUT INJURY OR NO CUSTOMER OUTAGE.PERMANENT REPAIR WAS COMPLETED AND THE LINE RETURNED TO NORMAL OPERATION ONAUGUST 8.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19970122 | 1997-09-05 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA |  |  | LA |  |  |  | 830 | 1997-08-09 |  | YES | WC 165 | 165 | LA | YES | NO | LEAK |  | 0 | 0 | 51232 | 36232.9092 | 78934.2622 | Null | 0 | 0 |  | 19970809 | 1000 | 1300 | BY TEST | 2299 | CORROSION | CORROSION | INTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1977; NMDIA: 12; THK: 0.38; SMYS: 52000; SEAM: SEAMLESS; MANU: ARMCO; MANYR: 1977; LOCLK: UNDER WATER; PNAME: STEPHEN COFFMAN; PHONE: 6306913788; LOC: INTERNALLY; ADESC: NO DATA; CAUCR: NO DATA; COAT: NO DATA; PROT: Null; CPYR: 0; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19970128 | 1997-08-18 | 2392 | CITIZENS GAS & COKE UTILITY | INDIANAPOLIS | MARION | IN | 46250 |  |  | 1437 | 1997-07-21 | 3 | NO |  |  |  | Null | NO | RUPTURE | 6.11 | 1 | 1 | 1000000 | 707231.9871 | 1540721.857 | Null | 0 | 28 |  | 19970721 | 310 | 913.5 | BY TEST | 1643 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1982; NMDIA: 20; THK: 0.28; SPEC: 20".D.X.281 APL -5L; SMYS: 65000; SEAM: ERW; MANYR: 0; LOCLK: NO DATA; PNAME: EARLE STEVENSON; PHONE: 3179274626; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19970132 | 1997-09-10 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA |  |  | LA |  |  |  | 900 | 1997-08-21 |  | YES | WC | 165 | LA | YES | NO | LEAK |  | 0 | 0 | 0 | 0 | 0 | Null | 0 | 0 |  |  | 960 | 1300 | BY TEST | 2299 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 0 | 12 | 0.38 |  | 52000 | SEAMLESS | N/A | ARMCO | 1977 | UNDER WATER |  | STEPHEN COFFMAN | 6306913788 | INTERNALLY | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19970134 | 1997-09-10 | 12243 | MIDGARD ENERGY COMPANY | DUMAS | MOORE | TX | 79029 |  | SW1/4 SEC.391;BLK 44; | 1830 | 1997-08-21 | 1 | NO |  |  | TX | Null | NO | LEAK |  | 0 | 0 | 0 | 0 | 0 | YES | 0 | 30 |  | 19970821 | 55 | 100 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; MLKD: OTHER; MLKDO: PVC-PLASTIC; PRTSY: PIPELINE; PRTYR: 0; NMDIA: 2; THK: 0; SMYS: 0; MANYR: 0; LOCLK: UNDER GROUND; PNAME: JOHNNY WEST; PHONE: 8069358878; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: MATERIAL; CAULO: PVC TO STEEL ADAPTER; CTEST: Null; MED: NO DATA; TMPS: 0; LKPS: 0
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19970135 | 1997-09-10 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA | MAZON | GRUNDY | IL | 60941 | 1184 | 62493+13 | 1030 | 1997-08-11 | 1 | NO |  |  | IL | Null | Null | LEAK |  | 0 | 0 | 0 | 0 | 0 | Null | 2 | 0 |  | 19970813 | 650 | 858 | BY TEST | 1160 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | WELD | GIRTH | STEEL |  | PIPELINE |  | 1975 | 36 | 0.43 | API5LX60 | 60000 | DSAW |  | BETHLEHEM | 0 | UNDER GROUND |  | STEPHEN COFFMAN | 6306913788 | INTERNALLY | OTHER | PIN HOLE | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19970137 | 1997-09-15 | 12576 | MISSISSIPPI RIVER TRANSMISSION CORP | AVISTON | CLINTON | IL |  | MP 58.5 | 3118 + 59 | 1330 | 1997-07-01 | 1 | NO |  |  | IL | Null | Null | RUPTURE | 1 | 0 | 0 | 55000 | 38897.7593 | 84739.7021 | Null | 0 | 0 |  | 19970908 | 425 | 960 | BY TEST | 1376 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; PRTFO: GIRTH; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1961; NMDIA: 18; THK: 2.5; SPEC: GR B; SMYS: 35000; MANYR: 0; LOCLK: UNDER GROUND; PNAME: TED VANDE KAMP; PHONE: 3184293606; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; MRKTP: 0; STAT: YES; CTEST: Null | WATER LINE CONTRACTOR TRENCHING TO INSTALL WATER LINE. THE TRENCHER WASCUTTING 60" DEEP DITCH, PIPELINE DEPTH WAS 3' - 3".
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19970140 | 1997-09-16 | 405 | ANR PIPELINE CO | WEST CAMERON 332 | OFFSHORE LA, FEDERAL WAT | LA |  | X= 1340,939 | Y= 144,555 | 1745 | 1997-08-12 | 1 | YES | WEST CAMERON 332 |  | LA | YES | NO | LEAK |  | 0 | 0 | 130000 | 91940.1583 | 200293.8414 | Null | 0 | 0 |  | 19970812 | 1170 | 1440 | BY TEST | 2150 | CORROSION | CORROSION | INTERNAL | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1979; NMDIA: 12; THK: 0.5; SPEC: API 5LX; SMYS: 42000; MANYR: 1979; LOCLK: UNDER WATER; PNAME: JOHN LUCIDO; PHONE: 3134962460; LOC: INTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: OTHER; COAT: COATED; PROT: YES; CPYR: 1979; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | INTERNAL CORROSION - 3 PINHOLE LEAKS WITHIN A 23 INCH SECTION OF THE PIPE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19970144 | 1997-09-22 | 25165 | GULF COAST NATURAL GAS CO | HANKAMER COMMUNITY | LIBERTY | TX | 77560 | SYSTEM 903 EAST SIDE | 486+40 T4 #03260 | 1130 | 1997-08-04 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 335000 | 236922.7157 | 516141.8221 | Null | 2 | 30 |  | 19970804 | 0 | 0 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: PIPING TO LIQUID TANK; MLKD: STEEL; PRTSY: OTHER; PRTSO: FRAC TANKS; PRTYR: 1997; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: WILFRED JURECEK; PHONE: 7136536247; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | HAD AN EXPLOSION IN FRAC TANKS AT MOSS BLUFF ON THE 16" LINE, SYSTEM 903 NEARHANKAMER, AT 11:30 AM ON 8/04/97. TEMPORARY PIG TRAPS WERE INSTALLED ON BOTHENDS AND PIG WAS BEING PUSHED FROM THE NORTH END TO THE SOUTH. LIQUIDS WERECAUGHT IN FOUR FRAC TANKS.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19970146 | 1997-10-07 | 18516 | SOUTHERN NATURAL GAS CO | OFFSHORE |  | LA |  | MAIN PASS BLOCK 59 | LAT.29,21'34 LONG 88 55' | 1425 | 1997-09-09 |  | YES | MAIN PASS | 59 |  | YES | NO | OTHER |  | 0 | 0 | 75000 | 53042.399 | 115554.1393 | Null | 0 | 0 |  | 19970909 | 1125 | 1440 | BY TEST | 2160 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: METER STATION; MLKD: STEEL; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1989; NMDIA: 0; THK: 0; SPEC: API5L & A106; SMYS: 0; MANYR: 0; LOCLK: OTHER; LOCLO: ON OFFSHORE PLATFORM; PNAME: KENNETH PETERS; PHONE: 2053257554; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: Null; MARK: NO; STAT: Null; CTEST: Null | A FIRE OF UNKNOWN ORIGIN OCCURRED IN PRODUCER'S EQUIPMENT ON THE MAIN PASSBLOCK 59 PLATFORM ALSO OWNED BY PRODUCER. THE FIRE SPREAD TO PRODUCER'S METERSTATION, WHICH WAS OPERATED BY SOUTHERN, DAMAGING METER PIPING, ELECTRONICMEASUREMENT EQUIPMENT, AND RELATED DEVICES AND MATERIAL. THE PLATFORM ESDSYSTEM ACTIVATED SHUTTING DOWN GAS FLOW BUT WHETHER A GAS RELEASE OCCURREDCANNOT BE DETERMINED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19970154 | 1997-10-14 | 11808 | LOUISIANA INTRASTATE GAS CO, L.L.C. | OSSUN | LAFAYETTE PARISH | LA |  | NEAR HWY 723 | 159+ 76 | 928 | 1997-09-16 | 2 | NO |  |  |  | Null | NO | RUPTURE | 10 | 0 | 0 | 50000 | 35361.5994 | 77036.0928 | Null | 1 | 15 | 403805 | 19970916 | 784 | 854 | BY TEST | 1200 | CORROSION | CORROSION | INTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1966; NMDIA: 16; THK: 0.22; SPEC: API 5L X52; SMYS: 0; SEAM: ERW; MANYR: 1966; LOCLK: UNDER GROUND; PNAME: WILLIAM BYRD; PHONE: 3184458225; LOC: INTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: OTHER; COAT: COATED; PROT: YES; CPYR: 1966; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | UNKNOWN AT THIS TIME. ADDITIONAL INFORMATION WILL BE CONTAINED IN SUPPLEMENTALREPORT.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19970155 | 1997-10-14 | 1007 | K N INTERSTATE GAS TRANSMISSION CO | STERLING | LOGAN | CO | 80751 |  |  | 1655 | 1997-09-14 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 0 | 0 | 0 | YES | 0 | 30 |  | 19970914 | 550 | 1250 | BY TEST | 1875 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: PLANNED PURGE; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1997; NMDIA: 24; THK: 0.63; SPEC: API 5L; SMYS: 52000; SEAM: SEAMLESS; VALVE: NONE; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: STEVE HAWES; PHONE: 3037633457; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | GAS IGNITED WHILE PURGING 24" SUCTION HEADER AT KN STERLING COMPRESSORSTATION. FIRE IGNITED LUMBER, PLASTIC AND CARDBOARD AND BURNED GRASS INSIDEAND OUTSIDE OF STATION FENCE. FIRE DEPARTMENT WAS CALLED. SUPPLY VALVE WASIMMEDIATELY CLOSED, EXTINGUISHING FIRE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19970156 | 1997-10-24 | 12243 | MIDGARD ENERGY COMPANY | STRATFORD | SHERMAN | TX | 79084 |  | SW 1/4 SEC.146 BLK IC | 1700 | 1997-10-06 | 1 | NO |  |  | TX | Null | NO | LEAK |  | 0 | 0 | 1228 | 868.4809 | 1892.0064 | Null | 0 | 30 |  | 19971006 | 178 | 182 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: 2 1"X3" NIPPLES; MLKD: STEEL; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1979; NMDIA: 1; THK: 0.13; SPEC: API 5L; SMYS: 0; SEAM: SEAMLESS; VALVE: ROCKWELL; MANU: ROCKWELL; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: VERNON STAFFORD; PHONE: 8069358875; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | A TRUCK HAULING FEED WAS HIT BY A PICK-UP, CAUSING THE TRUCK TO RUN OFFHIGHWAY 15 AND RUN OVER OUR REGULATOR/METER STATION. ABOVE GROUND EQUIPMENTWAS DAMAGED WHEN HIT BY TRUCK.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19970157 | 1997-10-17 | 12414 | MICHIGAN GAS STORAGE CO |  | OSCEOLA | MI | 49665 | LATERAL 51-S | NORTH SIDE OF VALVE 51-4 | 1045 | 1997-09-19 | 1 | NO |  |  |  | Null | NO | RUPTURE | 48 | 0 | 0 | 23000 | 16266.3357 | 35436.6027 | Null | 1 | 42 |  | 19970919 | 760 | 800 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | WELD | LONGITUDINAL | STEEL |  | OTHER | STORAGE FIELD | 1947 | 10 | 0.22 | API 5L | 35000 | ERW |  | REPUBLIC | 1946 | UNDER GROUND |  | JAMES PHILO | 5177880509 | INTERNALLY | NO DATA |  | NO DATA |  | COATED | YES | 1952 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | CREVICE IN LONG SEAM LOCATED ON BOTTOM ALLOWED CORROSION PRODUCTS TOACCUMULATE CAUSING PITTING AND FOR PITS TO LINK UP.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19970169 | 1997-11-28 | 2616 | COLUMBIA GAS TRANSMISSION CORP | STANDARDSVILLE | GREENE | VA | 22973 |  | 11+60 | 1530 | 1997-10-27 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 300000 | 212169.5961 | 462216.5571 | Null | 0 | 45 |  | 19971027 | 570 | 767 | BY TEST | 1247 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1950; NMDIA: 18; THK: 0.25; SPEC: 5LX; SMYS: 46000; SEAM: ERW; MANU: YOUNGSTOWN; MANYR: 1950; LOCLK: UNDER GROUND; PNAME: STEVEN P. BURNLEY, ADMINISTRATOR PIPELINE SAFETY; PHONE: 3043573575; PROT: Null; CPYR: 0; CAULK: OPERATOR ACTION; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null; TMPS: 0; LKPS: 0 | CONTRACTOR'S D6 BULLDOZER SLID INTO A DITCH PUNCTURING EXPOSED PIPE RESULTINGIN A FIRE. ACCORDING TO THE EQUIPMENT OPERATOR, THE CAUSE WAS LIKELY ACOMBINATION OF BOTH WET AND SLIPPERY SOIL CONDITIONS AND OPERATION TOO CLOSETO THE DITCH.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19970170 | 1997-11-25 | 30990 | CCNG GAS GATHERING, L.P. | HOLIDAY BEACH | ARANSAS | TX | 78382 | 4.39 | 231+26 | 1600 | 1997-10-28 | 1 | NO |  |  |  | Null | Null | LEAK |  | 0 | 0 | 44000 | 31118.2074 | 67791.7617 | YES | 6 | 30 |  | 19971028 | 450 | 845 | BY TEST | 1410 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 0 | 12 | 0.25 | AP15LX42 | 42000 | ERW |  |  | 0 | OTHER | UNDERGROUND IN WETLANDS | BILL W. BELL, JR. VICE PRESIDENT | 5122990001 | INTERNALLY | LOCALIZED PITTING |  | OTHER | BACTERIA/SUPPORTIVE STREA | COATED | YES | 1992 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | PROGRESSIVE ISOLATE CONE-SHAPED PIT PERFORATION IN PIPE WALL OF APPROXIMATELYPROGRESSIVE ISOLATED CONE-SHAPED PIT PERFORATION IN PIPE WALL OF APPROXIMATELYFORT-FIVE YEARS OF MONITORED PIPELINE QUALITY GAS SERVICE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19970171 | 1997-11-25 | 6660 | GREAT LAKES GAS TRANSMISSION CO | DEER RIVER | ITASCA | MN | 56636 | 206.25 | 267+44 | 1415 | 1997-10-24 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 100000 | 70723.1987 | 154072.1857 | Null | 0 | 0 |  | 19971024 | 850 | 974 | BY TEST | 1384 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: GIRTH; MLKD: OTHER; MLKDO: WELD MATERIAL; PRTSY: PIPELINE; PRTYR: 1968; NMDIA: 36; THK: 0.38; SPEC: API 5LX; SMYS: 65000; SEAM: DSAW; MANU: US STEEL; MANYR: 1968; LOCLK: UNDER GROUND; PNAME: ROBERT J. CADORIN, CODES AND PROCEDURES SPECIALIST; PHONE: 3135964669; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | THE LEAK WAS DISCOVERED DURING A ROUTINE SURVEY. INVESTIGATION REVEALED ACRACKED GIRTH WELD THAT WAS LEAKING. THE CRACK WAS CIRCUMFERENTIALLYORIENTATED AT APPROXIMATELY THE 6:00 POSITION AND WAS MEASURED TO BE 4.25INCHES LONG, RESULTING IN PIPE REPLACEMENT. PART D - BRIEF DESCRIPTION: ASMENTIONED IN PART 3, ABOVE, THE CRACK IN THE WELD EITHER WAS NOT PRESENT ORWAS NOT DETECTED DURING THE ORIGINAL CONSTRUCTION IN 1968 EVEN THOUGH ALLPRODUCTION WELDS WERE NONDESTRUCTIVELY TESTED AT THAT TIME. GREAT LAKES ISINVESTIGATING THE FAILURE AND HAS RETAINED THE SERVICES OF A CONSULTANT TOEXAMINE THE DEFECTIVE WELD REMOVED FROM SERVICE IN AN ATTEMPT TO DETERMINE THECAUSE OF THE DEFECT (CIRCUMFERENTIAL CRACK). IT SHOULD BE NOTED THAT THEPIPELINE SECTION WAS SHUT IN AND THEN BLOWN DOWN PRIOR TO REMOVAL OF A SEGMENTOF PIPE CONTAINING THE LEAKING WELD. A REPLACEMENT PIPE SEGMENT WAS THENINSTALLED AND PLACED INTO SERVICE. THE NRC WAS CONTACTED AT APPROXIMATELY1710 HOURS ON OCTOBER 24, 1997, (NRC CASE NO, 408825)
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19970173 | 1997-11-20 | 18516 | SOUTHERN NATURAL GAS CO |  |  | LA |  | LAT 29:15':31.3" | LONG 88:26':30.9" | 1530 | 1997-10-22 |  | YES | 3.109 MAIN PASS | 289 | LA | YES | NO | LEAK |  | 0 | 0 | 200000 | 141446.3974 | 308144.3714 | Null | 0 | 0 |  | 19971022 | 1130 | 1343 | BY TEST | 2015 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | OTHER | PIPING ON PLATFORM | 1978 | 3.5 | 0.3 | API5L | 30000 | SEAMLESS |  | US STEEL | 1977 | OTHER | ON OFFSHORE PLATFORM | KENNETH C. PETERS - SUPERVISOR, PIPELINE | 2053257554 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | NO | 0 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | PART A - PIPING WAS ABOVE THE WATERLINE OFFSHORE. PART 3 - TWO VERY SMALL"PINHOLE LEAKS WERE DISCOVERED IN 3" PIPING ON OFFSHORE PLATFORM. NOSIGNIFICANT EVENT WAS LINKED TO THE LEAKS. ESTIMATED COST OF REPAIR IS THEREASON FOR CLASSIFYING AS AN INCIDENT.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19970174 | 1997-11-19 | 19235 | TEXAS EASTERN GAS PIPELINE CO | EASTON | GREGG | TX |  | 47.96 | 2532+45 | 2050 | 1997-10-23 | 1 | NO |  |  | TX | Null | NO | RUPTURE |  | 0 | 0 | 150000 | 106084.7981 | 231108.2785 | Null | 2 | 0 |  | 19971023 | 970 | 975 | BY TEST | 1560 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1954 | 20 | 0.28 | API-5L | 52000 | ELECTRIC WELD |  | A.O. SMITH | 1954 | UNDER GROUND |  | DWAYNE TESCHENDORF, SR ENGINEER | 7136275573 | INTERNALLY | OTHER | INTERNAL | OTHER | NOT YET DETERMINED | COATED | YES | 1954 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | PIPELINE RUPTURE FROM APPARENT INTERNAL CORROSION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19970176 | 1997-11-18 | 13750 | NORTHERN NATURAL GAS CO. | MANCHESTER | FREEBORN | MN |  | MP 1.97 |  | 1345 | 1997-10-18 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 0 | 0 | 0 | YES | 1 | 0 |  | 19960918 | 440 | 960 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1932; NMDIA: 4.5; THK: 0.24; SMYS: 24000; MANYR: 0; LOCLK: UNDER GROUND; PNAME: WILL BURKS, SR. PROJECT ENGINEERING (P/L SAFETY); PHONE: 7136467966; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PERMANENT MARKERS; STAT: NO; CTEST: Null | FARMER WAS CHISEL PLOWING THE FIELD WHEN THE PLOW STRUCK THE PIPELINE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980019 | 1997-12-18 | 7605 | HOUSTON PIPELINE CO | EAST COLUMBIA | BRAZORIA | TX |  | 27.973 |  | 11 | 1997-11-05 | 1 | NO |  |  |  | Null | NO | RUPTURE |  | 0 | 0 | 20000 | 14144.6397 | 30814.4371 | Null | 0 | 25 |  | 19971105 | 700 | 825 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | INTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1963; NMDIA: 16; THK: 0.25; SPEC: X-52; SMYS: 52000; SEAM: ERW; MANYR: 0; LOCLK: UNDER WATER; PNAME: DAVID J. TONSALL; PHONE: 7136466389; LOC: INTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: OTHER; COAT: NO DATA; PROT: YES; CPYR: 0; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | INTERNAL CORROSION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980020 | 1997-12-24 | 602 | NORAM GAS TRANSMISSION, A NORAM ENERGY COMPANY | EL DORADO | UNION | AR | 71730 | 2041+94 |  | 1050 | 1997-11-12 | 1 | NO |  |  |  | Null | NO | RUPTURE | 100 | 0 | 0 | 63000 | 44555.6152 | 97065.477 | Null | 0 | 45 |  |  | 285 | 375 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: MECHANICAL JOINT; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1930; NMDIA: 16; THK: 0.25; SPEC: GRADE B; SMYS: 35000; MANYR: 1930; LOCLK: UNDER GROUND; PNAME: DARREL VINSON; PHONE: 8708623453; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | PIPE PULLED OUT OF COUPLING BECAUSE OF WASHOUT AREA.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980022 | 1998-01-21 | 2620 | COLUMBIA GULF TRANSMISSION CO | EUGENE ISLAND | BLOCK 286/287 | LA |  |  |  | 830 | 1997-12-17 |  | YES |  | 286 |  | Null | NO | LEAK |  | 0 | 0 | 80000 | 56578.559 | 123257.7486 | Null | 0 | 0 |  | 19971217 | 1050 | 1250 | NO DATA | 0 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1971 | 12 | 0.41 | 5LX | 52000 | SEAMLESS | BALL |  | 1971 | UNDER WATER |  | HENRY H. WANG | 7132674371 | INTERNALLY | LOCALIZED PITTING |  | NO DATA |  | COATED | YES | 1971 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | PIN HOLE LEAK AT 9 O'CLOCK POSITION. POSSIBLE CAUSE: INTERNAL CORROSION ORMATERIAL DEFECT. A CLAMP WAS INSTALLED TO STOP LEAK. X=1,885,229.89Y=105,490.26. SMALL PINHOLE LEAK AT 9:00 POSITION.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980024 | 1997-12-30 | 2620 | COLUMBIA GULF TRANSMISSION CO | EUGENE ISLAND | OFFSHORE | LA |  | EI 273B TO 26" TIE-IN | EI 285 TIE-IN | 8000 | 1997-12-02 |  | YES | E.I. | 285 |  | Null | NO | LEAK |  | 0 | 0 | 200000 | 141446.3974 | 308144.3714 | Null | 0 | 0 |  | 19971202 | 1094 | 1250 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: PIPE NIPPLE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1970; NMDIA: 0; THK: 0; SMYS: 0; MANU: UNKNOWN, 1/2" PIPE NIPPLE; MANYR: 0; LOCLK: UNDER WATER; PNAME: HENRY H. WANG; PHONE: 7132674371; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; MRKTP: 0; STAT: NO; CTEST: Null | A TRAWLING NET PULLED A 1/2" POWER GAS NIPPLE OFF FROM THE 18" VALVE. THEREMAINDER OF THE 1/2" NIPPLE WAS REMOVED AND A PIPE PLUG WAS INSTALLED. ATRAWLING NET PULLED A 1/2" POWER GAS NIPPLE OFF THE PIPELINE VALVE. THEREMAINDER OF THE 1/2" PIPE NIPPLE WAS REMOVED AND A 1/2" PIPE PLUG WASINSTALLED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980025 | 1998-01-12 | 405 | ANR PIPELINE CO | HIGH ISLAND BLK A489 |  | TX |  |  |  | 1100 | 1997-12-07 | 1 | YES | HIGH ISLAND | A489 | TX | YES | NO | LEAK |  | 0 | 0 | 170000 | 120229.4378 | 261922.7157 | Null | 0 | 0 |  | 19971207 | 1000 | 1440 | BY TEST | 2160 | CORROSION | CORROSION | INTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1980; NMDIA: 16; THK: 0.44; SPEC: API 5LX; SMYS: 52000; MANYR: 0; LOCLK: UNDER WATER; PNAME: DON CROSS; PHONE: 3134962460; LOC: INTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: OTHER; COAT: COATED; PROT: YES; CPYR: 1980; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | PIN HOLE LEAK AT 6:30 POSITION CONSISTENT WITH INTERNAL CORROSION.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980027 | 1998-02-03 | 31058 | MARATHON ASHLAND PIPE LINE LLC | CENTERVILLE | ST. MARY PARISH | LA |  | 99.6 | 5259 + 23 | 835 | 1997-12-28 | 1 | NO |  |  | LA | Null | NO | LEAK |  | 0 | 0 | 100000 | 70723.1987 | 154072.1857 | Null | 0 | 20 |  | 19980129 | 1050 | 1440 | BY TEST | 2160 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: SWAGE-3/4"X1/2"; MLKD: STEEL; PRTSY: OTHER; PRTSO: PIG RECEIVER; PRTYR: 0; NMDIA: 0.75; THK: 0; SPEC: A106 GR-B; SMYS: 0; SEAM: SMLS; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: EARL F DAUTERIVE; PHONE: 7132962428; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | ON DECEMBER 28, 1998 AT APPROXIMATELY 8:35 A.M., A SPHERE ARRIVED AT THEGARDEN CITY FACILITY AND BECAME STUCK IN THE 30" RADIAL FLOW TEE UPSTREAM OFTHE PIG TRAP (I.E., RECEIVER). IT IS BELIEVED THAT ONE OR TWO PREVIOUSSPHERES WERE ALREADY SETTING IN THE TEE. THE DOWNSTREAM DELIVERY PRESSURE TOEXXON DROPPED RAPIDLY AND DELIVERIES TO EXXON AND THE PIPELINE DISCHARGEFACILITY (PDF) WERE STOPPED. THE SPHERES WERE BELIEVED TO BE STUCK DUE TOHYDRATE FORMATION AT THE DOWNSTREAM END OF THE RADIAL FLOW TEE. SINCE THEREWAS NO METHANOL READILY AVAILABLE AND NO PLACE TO INJECT METHANOL NEAR THERADIAL FLOW TEE, THE OPERATOR DECIDED TO USE DIFFERENTIAL PRESSURE TO TRY TOFREE THE STUCK SPHERES. A VALVE ON THE UPSTREAM SIDE OF THE RECEIVER WASCLOSED AND THE PRESSURE ON THE RECEIVER WAS REDUCED TO CREATE A DIFFERENTIALPRESSURE TO MOVE THE SPHERE. WHEN THE VALVE WAS OPENED, ONE OR TWO SPHERESDISLODGED, MOVED RAPIDLY INTO THE RECEIVER AND CREATED A PRESSURE SURGE ON THESCRAPER TRAP PIPING AND APPURTENANCES. A 3/4" X 1/2" SWAGE FITTING, WHICH WASLOCATED BETWEEN THE TOP OF THE RECEIVER LEVEL INDICATOR AND THE 1/2"PLUGGED BLOWDOWN VALVE, FAILED AT THE TOP OF THE 3/4" THREADS ALLOWING A SMALLAMOUNT OF CONDENSATE TO BE BLOWN INTO THE AIR AS A MIST THAT MOVED IN ANORTHERNLY DIRECTION AND COATED SOME PIPING, GRAVEL AND CANE STUBBLE. AS THEPIPING WAS BEING SHUT IN AND SECURED, IT WAS NOTICED THAT THE MOTOR- OPERATEDVALVE ACTUATOR ON ONE OF THE TWO 30" BLOCK VALVE TO THE RECEIVER WASHYDROSTATICALLY TESTED FOR ONE HOUR PRIOR TO RETURNING TO SERVICE. ANEMERGENCY RESPONSE CONTRACTOR WAS CALLED OUT TO CLEAN UP THE CONDENSATERESIDUE USING ABSORBANT PADS.ADDITIONAL OPERATIONAL CORRECTIVE ACTIONS TAKENINCLUDE: INSTALLATION OF METHANOL INJECTION PORTS NEAR BOTH THE UPSTREAM ANDDOWNSTREAM ENDS OF THE RADIAL FLOW TEE; A GUIDELINE FOR HANDLING SITUATIONSWHERE SPHERES BECOME STUCK IN RADIAL FLOW TEES AS PREPARED, IMPLEMENTED ANDREVIEWED WITH STATION OPERATIONS PERSONNEL; AND, ACCURACY OF THE WATERMONITORING INSTUMENTS WAS CHECKED AND VERIFIED. PRESSURE SAFETY SWITCHESWILL BE INSTALLED TO PROHIBIT THE VALVE FROM ACTUATING WHEN A SPECIFIEDPRESSURE DIFFERENTIAL IS EXCEEDED. ALSO, A SAFETY REVIEW TRAINING SESSION ISPLANNED WITH OPERATIONS PERSONNEL CONCERNING POTENTIAL ENERGY HAZARDSASSOCIATED WITH A HIGH PRESSURE GAS FACILITY.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980028 | 1998-02-09 | 1007 | K N INTERSTATE GAS TRANSMISSION CO | HARVEYVILLE | WABAUNSEE | KS | 66431 | 82.05 | 4332+24 | 1438 | 1997-10-21 | 1 | NO |  |  |  | Null | NO | NO DATA |  | 0 | 0 | 50000 | 35361.5994 | 77036.0928 | Null | 0 | 7 |  | 19971022 | 450 | 973 | BY TEST | 1222 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: NOT A FAILURE; MLKD: STEEL; PRTSY: OTHER; PRTSO: VALVE SET; PRTYR: 1954; NMDIA: 24; THK: 0.31; SPEC: GR. X52; SMYS: 52000; SEAM: SEAMLESS; VALVE: ANSI 600 BALL; MANU: NORDSTROM; MANYR: 1997; LOCLK: ABOVE GROUND; PNAME: STEVE HAWES; PHONE: 3037633457; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | USING GEL PIG TO REMOVE CONTAMINATION FROM PIPELINE. OPENED DOWNSTREAMBLOWDOWNS TO PROVIDE PRESSURE DIFFERENTIAL TO MOVE PIG TRAIN. PRODUCT FROMEARLIER PIG RUN WAS INSIDE OF PIPE AND ESCAPED AS A MIST APPROX. 1.5 HOURSAFTER BLOWDOWNS WERE OPENED. CLOSED BLOWDOWN APPROX. 7 MINUTES AFTER MISTINGBEGAN. MIST AFFECTED ORCHARD, STOCK POND, CATFISH POND, PUBLIC ROAD ANDDWELLING.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980029 | 1998-02-11 | 25169 | SOUTH CAROLINA PIPELINE CORP | TIRZAH | YORK | SC | 29745 | 11-90 | 1292+04 TO 1292+66 | 1741 | 1997-11-15 | 3 | NO |  |  | SC | Null | NO | RUPTURE | 44 | 0 | 0 | 74000 | 52335.167 | 114013.4174 | Null | 0 | 45 |  |  | 1046 | 821 | BY TEST | 1150 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: LONGITUDINAL; MLKD: NO DATA; PRTSY: NO DATA; PRTYR: 1958; NMDIA: 10.75; THK: 0.22; SPEC: API-5L; SMYS: 42000; SEAM: ERW; MANU: JONES & MC LAUGHLIN; MANYR: 1957; LOCLK: NO DATA; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: MATERIAL; CTEST: YES; TESTD: 19580320; MED: WATER; TMPS: 24; LKPS: 1150 | DURING THE CALENDAR YEARS OF 1995 AND 1996,SOUTH CAROLINA PIPELINE CORPORATION(SCPC) INSTALLED EIGHTY FIVE (85) MILES OF 16' NATURAL GAS TRANSMISSION MAINWITH A DESIGNED M.A.O.P. OF 1200 PSIG IN PARALLEL WITH AN EXISTING 12"REDUCING TO 10" LINE A SYSTEM FOR INCREASED SAFETY AND TO ALLOW SCPC TOACCOMMODATE ADDITIONAL CONTRACT VOLUMES OF GAS FROM ONE OF TWO INTERSTATESUPPLIERS, TRANSCONTENTIAL PIPE LINE COMPANY. THE LINE A SYSTEM WAS INSTALLEDIN 1957 AND 1958 AND SCPC HAD CONCERNS ABOUT THE 12" PORTION OF THIS LINE ANDDECIDED TO INTELLIGENTLY SURVEY (SMART PIG) APPROXIMATELY TWENTY - FIVE MILESOF PIPE. AFTER THE APRIL 1996 SURVEY, IT WAS DECIDED TO TAKE THE 12" PORTIONOUT OF SERVICE UNTIL FURTHER TESTING COULD BE CONDUCTED. IN ORDER TO TAKETHIS SECTION OF PIPE OUT OF SERVICE, CROSSOVER PIPING AND VALVES WEREINSTALLED FROM THE NEW 16" PIPE TO THE REMAINING 60 MILES OF 10" LINE SYSTEMFOR CONTINUED SERVICE TO SCPC'S SALE FOR RESALE AND INDUSTRIAL CUSTOMERS.THE 16" AND 10" PIPELINES OPERATED IN PARRALLEL WITH THE CROSSOVERS OPENLIMITED TO THE M.A.O.P. OF THE 10" SECTION FROM APRIL1996 TILL NOVEMBER 1997,SCPC COMPLETED THE CONSTRUCTION OF THE GROVER COMPRESSOR STATION WHICH WASDESIGNED TO DISCHARGE INTO THE NEW 16" LINE. THE MANAGER OF MEASUREMENT ANDCOMPRESSION ASSIGNED RESPONSIBILITIES TO MEASUREMENTS TECHNICIANS TO SEPERATETHE 16" FROM THE 10" EXCEPT AT ONE REGULATED CROSSOVER FROM THE 16" ATREGULATING STATION 11 - 70 TO ALLOW FOR THE GROVER COMPRESSOR STATION TOINCREASE THE PRESSURE ON THE 16" LINE TO THE M.A.O.P. THE WORK WAS REPORTEDTO BE COMPLETED AT ALL CROSSOVER 0N NOVEMBER 14TH AND THE GROVER COMPRESSORSTATION STARTED ADDITIONAL UNITS TO RAISE THE PRESSURE ON THE 16" PORTION TOAPPROXIMATELY 950 PSIG. AFTER THE REGULATED CROSSOVER AT STATION 11 - 70WAS CHECKED TO INSURE PROPER OPERATION ON THE MORNING OF NOVEMBER 15TH THE16" PIPELINE WAS CLEARED FOR OPERATION UP TO THE M.A.O.P. THE INCIDENTOCCURRED ON THE 10" LINE A SYSTEM IN A FIELD IN THE MIDDLE OF A DAIRY FARMNEAR STATION 11 - 90 AS A RESULT OF INADVERTENTLY LEAVING A 4" CROSSOVER VALVEOPEN AT REGULATING STATION 11 - 30. THIS VALVE BEING OPENED ALLOWEDUNRESTRICTED FLOW OF NATURAL GAS FROM THE 16" LINE TO A 10" SECTION OF LINEWITH A M.A.O.P. OF 821 PSIG. THE LINE RUPTURED AT AN ESTIMATED 1046 PSIGWHICH RESULTED IN THE LONGITUDINAL WELD OPEN ON FOR AN ESTIMATED DISTANCE OFFORTY FOUR FEET. A METALLURGICAL WAS CONDUCTED ON THE RUPTURED SECTION ANDIS ATTACHED FOR REVIEW. AS A RESULT OF HIS INCIDENT, SCPC NOW REQUIRES AWRITTEN PROCEDURE FOR ALL MAJOR PIPELINE MODIFICATIONS. THE LONG TIME,COMPETENT EMPLOYEES WHO WERE INVOVED IN THE INCIDENT HAVE BEEN DECIPLINEDAND ALL OTHER OPERATIONAL EMPLOYEES HAVE BEEN BRIEFED ON THIS INCIDENT TOHELP INSURE AN EVENT NEVER HAPPENS AGAIN.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980030 | 1998-02-03 | 18536 | SOUTHWEST GAS CORP | LAUGHLIN | CLARK | NV | 89029 | M.P. 5.4 | 116+00 | 1815 | 1998-01-05 | 1 | NO |  |  | NV | Null | NO | OTHER |  | 0 | 0 | 129860 | 90709.2579 | 197612.2953 | Null | 0 | 48 |  | 19980106 | 500 | 720 | BY TEST | 1080 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: 90DEGREE ELBOW; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1996; NMDIA: 20; THK: 0.31; SPEC: API5L; SMYS: 52000; SEAM: ERW; MANU: AMERICAN STEEL; MANYR: 1996; LOCLK: UNDER GROUND; PNAME: JOE CLEMENT; PHONE: 7023652014; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19971001; MARK: YES; MRKTP: FIBERGLASS P/L MARKER; STAT: YES; CTEST: Null | ENCLOSED IS A GAS TRANSMISSION INCIDENT REPORT FOR AN INCIDENT WHICH OCCURREDON JANUARY 5, 1998. THE INCIDENT REPORT NUMBER PROVIDED TO SOUTHWEST GAS FROMDOT WHEN WE MADE OUR TELEPHONIC REPORT IS 418580. IF YOU HAVE ANY QUESTIONS,PLEASE GIVE ME A CALL.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980031 | 1998-02-10 | 19160 | TENNESSEE GAS PIPELINE CO |  | HOUMA | LA |  | 524G - 100 | 524G - 101+9.98 | 1000 | 1998-01-09 |  | YES | HOUMA | BAY M5 | LA | NO | NO | LEAK |  | 0 | 0 | 385000 | 268928.5714 | 585867.3469 | Null | 0 | 65 |  | 19980109 | 900 | 1235 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1968; NMDIA: 16; THK: 0.38; SPEC: API5LX; SMYS: 52000; SEAM: SEAMLESS; MANU: US STEEL; MANYR: 1968; LOCLK: UNDER WATER; PNAME: DARON K MOORE; PHONE: 7137574523; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; MRKTP: 0; STAT: Null; CTEST: Null | UNKNKOWN THIRD PARTY WHO CAUSED DAMAGE. LOCATION IS NOT A WATER CROSSING, BUTIS OFFSHORE IN STATE WATERS.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980033 | 1998-02-13 | 792 | ATLANTA GAS LIGHT CO | SMYRNA | COBB | GA | 30080 | ATLANTA RD SOUTH OF I285 |  | 800 | 1998-01-08 | 3 | NO |  |  | GA | Null | NO | RUPTURE | 0.35 | 0 | 0 | 47546 | 33211.6308 | 72352.3347 | YES | 0 | 30 |  |  | 240 | 300 | BY TEST | 700 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1983; NMDIA: 24; THK: 0.31; SPEC: API - 5LX; SMYS: 42000; SEAM: SEAMLESS; MANU: USS; MANYR: 0; LOCLK: UNDER GROUND; PNAME: PHYLISS W STALINGS; PHONE: 7704235720; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: SETTLEMENT DUE TO WATER; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | A 24" STEEL NATURAL GAS MAIN DEVELOPED A 4 1/4" STRESS CRACK AT A 12" STEELBRANCH CONNECTION WHEN THE FILLMATERIAL SUPPORT WAS WASHED AWAY DURING A WATERMAIN BREAK.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980034 | 1998-02-18 | 22365 | WESTAR TRANSMISSION CO | FORSAM | HOWARD | TX | 79733 | LINE #860-000 |  | 1217 | 1998-01-21 | 1 | NO |  |  |  | Null | NO | RUPTURE | 15 | 0 | 0 | 8500 | 5937.384 | 12934.7336 | YES | 1 | 25 |  | 19980121 | 40 | 120 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 0; NMDIA: 4.5; THK: 0.15; SPEC: GRADE B; SMYS: 35000; SEAM: SEAMLESS; VALVE: ANSI150; MANU: UNK; MANYR: 0; LOCLK: UNDER GROUND; PNAME: STEVE HAWES; PHONE: 3037633457; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: Null; MARK: YES; MRKTP: STANDARD P/L MARKERS; STAT: NO; CTEST: Null | ATTTACHED IS RSPA FORM F 7100.2 COVERING AN INCIDENT THAT OCCURRED NEARFORSAN, TEXAS ON JANUARY 21 1998. WE REPORTED THE INCIDENT TO THE NATIONALRESPONSE CENTER AT APPROXIMATELY 1602 HOURS CST ON JANUARY 21 1998 AND THEINCIDENT NUMBER ASSIGNED WAS 420718. WE REPORTED THIS INCIDENT BASED UPONOPERATOR JUDGMENT AT THE TIME IT WAS DISCOVERED. THE INCIDENT OCCURRED WHEN AROAD MAINTAINER OPERATED BY HOWARD COUNTY RD DEPARTMENT STRUCK OUR LINE. THERESULTING DAMAGE CAUSED A LOSS OF SERVICE TO APPROXIMATELY 97 ENERGASCUSTOMERS. THERE WERE NO FIRES, EXPLOSIONS, INJURIES OR FATALITIES AND THETOTAL PROPERTY DAMAGE IS ESTIMATED TO BE $8500. IF YOU REQUIRE INFORMATION,PLEASE FEEL FRE TO CALL ME AT (303)7633457
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980035 | 1998-02-18 | 602 | NORAM GAS TRANSMISSION, A NORAM ENERGY COMPANY | MOUNTAINBURG | CRAWFORD | AR |  |  | 2096+74 | 930 | 1998-01-16 | 1 | NO |  |  | AK | Null | NO | RUPTURE |  | 0 | 0 | 600000 | 419109.462 | 913040.0212 | Null | 13 | 10 |  |  | 850 | 1000 | BY TEST | 1250 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: GIRTH; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1967; NMDIA: 20; THK: 0.25; SMYS: 60000; MANYR: 0; LOCLK: UNDER GROUND; PNAME: TED VANDEKAMP; PHONE: 3184293606; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: CONSTRUCTION; CAULO: WELD; CTEST: YES; TESTD: 19680609; MED: WATER; TMPS: 8; LKPS: 1250
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980036 | 1998-02-13 | 602 | NORAM GAS TRANSMISSION, A NORAM ENERGY COMPANY | LAVACA | SEBASTAIN | AR | 72941 |  | 0+00 | 1800 | 1998-01-16 | 1 | NO |  |  | AR | Null | NO | OTHER |  | 0 | 0 | 0 | 0 | 0 | YES | 0 | 45 |  |  | 0 | 0 | NO DATA | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: 1/4" NIPPLE; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1964; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: UNDER GROUND; PNAME: TED VANDEKAMP; PHONE: 3184293606; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: MATERIAL; CAULO: XS NIPPLE 1/4"; CTEST: NO; MED: NO DATA; TMPS: 0; LKPS: 0 | PIPE NIPPLE ON OIL FILTER CASE SAMPLE PROBE BROKE AND VENTED OIL ONTO EXHAUSTMANIFOLD OF ENGINE #3 AND IGNITED. SAFETY SHUTDOWNS OPERATED AND SHUT DOWNENGINE. FIRE EXTINGUISHED BY STATION EMPLOYEE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980037 | 1998-02-23 | 18152 | SEA ROBIN PIPELINE CO | EAST CAMERON BLOCK334 |  | LA |  | MP1.900 WEST CAMERON BLOC | 100 + 18.63 | 1500 | 1998-01-26 |  | YES | FAST | 334 |  | YES | NO | RUPTURE | 5 | 0 | 0 | 2500000 | 1746289.4249 | 3804333.4217 | Null | 0 | 0 |  | 19980126 | 1050 | 1780 | BY TEST | 2225 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1996; NMDIA: 16; THK: 0.5; SPEC: API 5LX; SMYS: 60000; SEAM: SUBMERGED ARC; MANU: NAPA PIPE CORP.; MANYR: 1996; LOCLK: UNDER WATER; PNAME: TOM HIGGINS; PHONE: 3189375007; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; MRKTP: 0; STAT: NO; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980038 | 1998-02-23 | 4280 | EL PASO NATURAL GAS CO | SALT FLAT | HUDSPETH | TX | 79847 | MP117ON LINE 1103 |  | 145 | 1998-01-27 | 1 | NO |  |  |  | Null | NO | RUPTURE | 92 | 0 | 0 | 50000 | 34925.7885 | 76086.6684 | Null | 2 | 0 |  | 19980127 | 830 | 836 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1950 | 30 | 0.34 | API 5L | 52000 | DSAW |  | REPUBLIC | 1950 | UNDER GROUND |  | GILBERT ARAGON | 9154962624 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | COATED | YES | 1950 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980039 | 1998-02-09 | 13845 | NORTHWEST PIPELINE CORP | WOLF CREEK | JOSEPHINE | OR |  | 112.29 | 5928.79 | 622 | 1998-01-13 | 1 | NO |  |  |  | Null | NO | RUPTURE | 8.5 | 0 | 0 | 200000 | 139703.154 | 304346.6737 | Null | 2 | 12 |  | 19980113 | 847 | 896 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1963 | 10.75 | 0.19 | 5LX API | 42000 | ERW |  | KAISER | 1963 | UNDER GROUND |  | ED COMPTON | 8015846776 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL |  | YES | 19631113 | WATER |  | 1 | 781 | ATTACHED IS AN INCIDENT REPORT, FORM 7100.2,CONCERNING A RUPTURE ON OUR GRANTSPASS LATERAL LOCATED IN JOSEPHINE COUNTY, OREGON. THE RUPTURE INFORMATION ISNECESSARY, PLEASE CONTACT ME.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980040 |  | 20230 | KOCH GATEWAY PIPELINE CO | LUCEDALE | GEORGE | MS |  |  | 517 + 90 | 525 | 1997-10-21 | 1 | NO |  |  |  | Null | NO | NO DATA |  | 0 | 0 | 140000 | 99012.4782 | 215701.06 | Null | 3 | 0 |  | 19971121 | 566 | 0 | NO DATA | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1949; NMDIA: 20; THK: 0.25; SMYS: 46000; SEAM: ERW; MANU: YOUNGSTOWN; MANYR: 1949; LOCLK: UNDER GROUND; PNAME: WAYNE F ST. GERMAIN; PHONE: 3189887102; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: NO DATA; CTEST: Null; MED: NO DATA; TMPS: 0; LKPS: 0 | ATTACHED PLEASE FIND YOUR REQUESTED RESUBMISSION OF THE WRITTEN REPORT FOR ALEAK WHICH OCCURRED ON OUR BAXTERVILLE 20" LINE. THE REPORT WAS MADE11/30/1997 TO LT. KOSHAR OF THE NATIONAL RESPONSE CENTER. THE REPORT NUMBER IS409967. WE APOLOGIZE FOR SENDING THE REPORT TO YOU TO INITIALLY ON ANINCORRECT FORM. SHOULD YOU REQUIRE ADDITIONAL INFORMATION PLEASE CALL ME AT(312)9887102.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980041 | 1998-02-27 | 20230 | KOCH GATEWAY PIPELINE CO | BENDALE | GEORGE | MS |  | 53.8 | 2482+82 | 2200 | 1997-01-11 | 1 | NO |  |  | MS | Null | NO | LEAK |  | 0 | 0 | 60397 | 42714.6903 | 93054.978 | Null | 48 | 0 |  | 19971103 | 500 | 680 | NO DATA | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: GIRTH; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1949; NMDIA: 20; THK: 0.25; SMYS: 46000; SEAM: SUBMERGED ARC W; MANU: YOUNGSTOWN; MANYR: 1949; LOCLK: UNDER WATER; PNAME: WAYNE F ST GERMAIN; PHONE: 3189887102; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: CONSTRUCTION; CTEST: Null; MED: NO DATA; TMPS: 0; LKPS: 0 | ATTACHED PLEAS FIND YOUR REQUESTED RESUBMISSION OF THE WRITTEN REPORT FOR ALEAK WHICH OCCURRED ON OUR PIPELINE NEAR LUCEDALE, MISSISSIIPPI, IN GEORGECOUNTY. THE REPORT WAS MADE AT 7:24 AM.CENTRAL TIME, ON 10/21/1997 TO LT.KOSHAR OF THE NATIONAL RESPONSE CENTER. THE REPORT NUMBER 408257. WEAPOLOGIZE FOR SENDING THE REPORT TO YOU INITIALY ON AN INCORRECT FORM.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19980042 | 1998-03-04 | 4510 | EQUITABLE RESOURCES (A.K.A EQUITABLE GAS CO) | OCS FEDERAL WATERS GOM |  | LA |  |  |  | 701 | 1998-01-30 |  | YES | WC | 198 | LA | Null | NO | OTHER | 5 | 0 | 0 | 700000 | 488961.039 | 1065213.3581 | Null | 0 | 0 |  | 19980130 | 1183 | 1440 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 0 | 8.63 | 0.5 | API 5L GRB | 4057 | SEAMLESS | ANSI 600 | VARIOUS | 1977 | UNDER WATER |  | SHARON PEREZ | 2815783388 | INTERNALLY | LOCALIZED PITTING |  | OTHER | AGE & PRODUCT SHIPPED | COATED | YES | 1977 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | PIPELINE REPAIR PROCEDURE WEST CAMERON 198 02/02/1998 JET OUR ATOUND THE PIPEAT THE LEAK LOCATION TO VERIFY ORIGIN OF LEAK. ULTRASONICALLY INSPECT THEPIPE AT VARIOUS LOCATION TDETERMINE GENERAL CONDITION OF PIPE MATERIAL.INSTALL A NEW PRE-TESTED PIPE SPOOL COMPLETE WITH FLANGS AT THE LEAKLOCATION. OPEN THE SUB-SEA VALVES AT THE TEXAS EASTERN TIE-IN AND PLACESYSTEM BACK IN SERVICE. MONITOR AND INSPECT FOR LEAKS DURING REPRESURIZATIONAND FOR SEVERAL DAYS THEREAFTER.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19980043 | 1998-03-04 | 4510 | EQUITABLE RESOURCES (A.K.A EQUITABLE GAS CO) | OCSFEDERAL WATERS GOM | OFFSJORE | LA |  |  |  | 1330 | 1998-01-26 |  | YES | WC | 198 | LA | Null | NO | LEAK |  | 0 | 0 | 200000 | 139703.154 | 304346.6737 | Null | 0 | 0 |  | 19980127 | 1100 | 1440 | NO DATA | 0 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 0 | 8.63 | 0.5 | API 5L GRB | 4057 | SEAMLESS | ANSI 600 | VARIOUS | 1977 | UNDER WATER |  | SHARON PEREZ | 2815783388 | INTERNALLY | NO DATA | LOCALIZED PITTING | OTHER | AGE & PRODUCT SHIPPED | COATED | YES | 1977 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | PIPELINE REPAIR PROCEDURE WEST CAMERON 198 1/27/1998 BLOWN DOWN THE 12"PIPELINE BACK TO THE 198 "A" PLATFORM. REMOVE CONCRETE COATING, CLEAN PIPE TOBARE METAL, AND ULTRASONICALLY INSPECT AT VARIOUS LOCATION OF PIPE TODETERMINE GENERAL CONNDITION OF PIPE MATERIAL; INSTALL REPAIR CLAMP. OPENTHE SUB-SEA VALVES AT THE TEXAS EASTERN TIE IN AND PLACE SYSTEM BACK INSERVICE. MONITOR AND INSPECT FOR LEAKS DURING REPRESSURIZATION AND FORSEVERAL DAYS THERE AFTER.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980044 | 1998-03-04 | 2616 | COLUMBIA GAS TRANSMISSION CORP | ELKVIEW | KANAWHA | WV | 25071 |  |  | 530 | 1998-02-07 | 3 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 100000 | 69851.577 | 152173.3369 | Null | 0 | 15 |  | 19980212 | 750 | 1000 | BY TEST | 1650 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | OTHER | HEATER | STEEL |  | COMPRESSOR STATION |  | 1980 | 4 | 0.24 | A-106 | 35000 | SEAMLESS |  |  | 0 | OTHER | INTERIOR OF DIRECT FIRED | STEVEN P BURNLEY | 3043573575 | EXTERNALLY | LOCALIZED PITTING |  | OTHER | CONDENSATE | BARE | NO | 0 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | HEATER COIL IN A DIRECT FIRED HEATER.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980045 | 1997-12-29 | 2620 | COLUMBIA GULF TRANSMISSION CO |  | ST MARY PARISH | LA | 70522 | 56.8 V1206-1207 | 2998+44 EL 300 | 1545 | 1997-11-19 | 1 | NO |  |  | LA | Null | NO | LEAK |  | 0 | 0 | 50000 | 35361.5994 | 77036.0928 | NO | 2 | 0 |  | 19971120 | 767 | 1008 | NO DATA | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | HEATER | STEEL |  | PIPELINE |  | 1986 | 30 | 0.32 | 5-LX | 65000 | DSAW | BALL | KAISER | 1964 | UNDER GROUND |  | HENRY H WANG | 7132674371 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION | 4" TO 30" HOT TAP FITTING | YES | 19860501 | WATER |  | 8 | 1505 | UNDERCUT ON THE HOT TAP WELD AND STRESS ON THE BRANCH PIPING CAUSING A 3"CRACK ON THE PIPELINE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980046 | 1998-03-09 | 859 | GPM GAS CORP | OKLAHOMA CITY | CANADIAN | OK |  | 1/2 MILE E OF SW 89TH&CIM | SW/4 S35-11N-6W | 1020 | 1997-10-08 | 1 | NO |  |  | OK | Null | NO | OTHER |  | 0 | 0 | 70000 | 49506.2391 | 107850.53 | Null | 0 | 40 |  | 19971008 | 0 | 1025 | BY TEST | 1680 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1983; NMDIA: 6; THK: 0.16; SPEC: API 5L GRADE X-42; SMYS: 42000; SEAM: SEAMLESS ERW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: G A SANDS; PHONE: 4052708175; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | ON OCTOBER 8,1997, A COMPANY MAINTENANCE CREW BEGAN WORK TO REMOVE A NONUSED 6INCH TIE IN FROM A 12 INCH NATURAL GAS GATHERING SYSTEM DISCHARGE LINE. THELINE HAD BEEN ISOLATED AND DEPRESSURED ON OCTOBER 5, 1997. AN OPEN VENT WASLOCATED AT EACH ISOLATION VALVE AND AT THE WORK SITE. THE WORK WAS INITIATEDBY MONITORING THE OPEN VENT AT THE WORK SITE ON THE END OF THE 6INCH TIE IN.ONLY TESIDUAL HYDROCARBON VAPORS WERE OBSERVED. AS A RESULT, THE CREW LIT THETOP OF THE VENT WITH A CUTTING TORCH AND THEN BEGAN REMOVING THE 6 INCH PIPE.THE NON-USED TIE-IN WOULD BE CUT OFF WITH THE TORCH ALLOWING A WELD CAP TO BEINSTALLED TO CAP THE 12INCH LINE. AFTER CUTTING APPROXIMATELY 3/4 OF THE6INCH PIPE, THE CONTROLLED FIRE BEGAN TO INCREASE ABRUPTLY. AS A RESULT, ALLWORKERS AT THE SITE WERE ORDERED TO EVACUATE UPWIND. SECONDS LATER, A LARGEUNCONTROLLED FIRE DESTROYED AN UNMANNED BACKHOE TRACTOR PARKED AT THE EDGE OFTHE EXCAVATION AND HEAT DAMAGED APPROXIMATELY 20 FEET OF EXCAVATED 12 INCHPIPE. THERE WERE NO INJURIES OR OTHER DAMAGES OCCURRED. THE FIRE WASALLOWED TO BURN ITSELF OUT.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980069 | 1998-04-01 | 4483 | ENSTAR NATURAL GAS CO | ANCHORAGE |  | AK | 99501 |  |  | 1032 | 1998-03-01 | 3 | NO |  |  |  | Null | Null | LEAK |  | 0 | 0 | 2000000 | 1397031.5399 | 3043466.7373 | Null | 4 | 3 |  | 19980301 | 230 | 275 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1961; NMDIA: 6; THK: 0.19; SMYS: 0; MANYR: 0; LOCLK: UNDER GROUND; PNAME: JOHN LAU MANAGER TRANSMISSION OPERATIONS; PHONE: 9072643736; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: Null; MARK: NO; STAT: NO; CTEST: Null | ON SUNDAY MORNING MARCH 1, 1998, AT 9:46 AM AST, ENSTAR WAS NOTIFIED BY THEANCHORAGE FIRE DEPARTMENT ( AFD OF A POWER POLE FIRE AND NATURAL GAS LEAK ATFIRST STREET AND POST ROAD, ANCHORAGE, ALASKA. A SERVICE MAN WAS DISPATCHEDTO THE LOCATION. A SUPERVISOR AND A DISTRIBUTION CREW ALSO RESPONDED. A 34.5KV ELECTRICAL TRANSMISSION LINE HAD BEEN SEVERED ON POLE AND ELECTRIC CURRENTFROM THE DOWNED POWER LINE OR POLE SWITCHING GEAR CARSED A FAILURE IN A 2"HDPE, 60 PSI, NATURAL GAS DISTRIBUTION MAIN ADJACENT TO THE POLE. AT 10:32 AM,AFD WAS NOTIFIED OF AN EXPLOSION AND FIRE AT MUNICIPAL LIGHT & POWER'S (ML&P)POWER PLANT BUILDING LOCATED APROXIMATELY 1 BLOCK WEST OF THE POLE FIRE.ADDITIONAL ENSTAR EMPLOYEES AND SUPERVISORS WERE CALLED IN TO SHUT DOWN TWO,275 PSI, 6" STEEL TRANSMISSION LINES FEEDING THE POWER PLANT. NATURAL GAS TOTHE POWER PLANT WAS SHUT DOWN AT 2:35 PM AND THE FIRE WAS CONTAINED. UPONINVESTIGATION, IT WAS DETERMINED THAT A LINE TO GROUND FAULT ON THE ML&P34.5 KV ELECTRICAL SYSTEM TRAVELED THE PATH OF LEAST RESISTANCE, THE ENSTARSTEEL TRANSMISSION PIPELINE, BACK TO THE GROUND GRID AT THE ML&P POWER PLANT.THE POWER POLE WAS IN CLOSE PROXIMITY TO ENSTAR'S STEEL TRANSMISSIONPIPELINE. EVIDENCE OF ELECTRICAL CURRENT ENTERING THE STEEL PIPELINE NEAR THEPOWER POLE AS WELL AS EXITING THE PIPELINE THE PIPELINE NEAR THE POWER PLANTWAS DISCOVERED. PRESSURE TESTING OF THE PIPELINES REVEALED THE SOUTHERN 6",275 PSI WAS INTACT. NO LEAKS WERE FOUND IN IT. IT WAS PRESSURE TESTED TO 425PSI AND PLACED BACK IN SERVICE. THE NORTHERN 6", 275 PSI PIPELINE AND 3/4"STEEL, 275 PSI SERVICE LINE CONNECTED TO IT FAILED A 100 PSI PRESSURE TEST.THEY WERE ABANDONED IN PLACE. AT LEAST ONE IDENTIFIED HOLE, AND ONE OR MOREADDITIONAL HOLES WERE BURNED IN THE 275 PSI 6" STEEL PIPELINE AND 3/4" STEELSERVICE LINE FEEDING THE POWER PLANT WHEN THE 34.5 KV POWER LINE FAILED.NATURAL GAS LEAKED UNDERGROUND THOUGH THESE HOLES BEFORE THE EXPLOSION ATML&P POWER PLANT. IT IS BELIEVED THAT NATURAL GAS ENTERED THE BUILDINGTHROUGH UNDERGROUND ELECTRICAL CONDUITS AND OR AROUND THE LOOSE FITTINGSIDING OF THE BUILDING WHERE IT WAS IGNITED BY ONE OF NUMEROUS IGNITIONSOURCES INSIDE THE BUILDING.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980070 | 1998-03-18 | 4280 | EL PASO NATURAL GAS CO | DUMAS | MOORE | TX |  | 11+3761 ON LINE NO. 1102 | 608+74 | 1317 | 1997-11-10 | 1 | NO |  |  | TX | Null | NO | LEAK |  | 0 | 0 | 57843 | 40908.4198 | 89119.9744 | Null | 2 | 0 |  | 19971110 | 573 | 780 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1948; NMDIA: 24; THK: 0.25; SPEC: API5L; SMYS: 52000; SEAM: F.W.; MANU: A.O. SMITH; MANYR: 1948; LOCLK: UNDER GROUND; PNAME: RICHARD FAVILA, PRINCIPAL ENGINEER; PHONE: 9154962062; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PIPELINE MARKERS; STAT: NO; CTEST: Null | AT1:17 PM ON NOVEMBER 10 1997, EL PASO'S" DUMAS LINE NO. 1102 DUMAS NO. 1102WAS HIT AND PUNCTURED BY A SEISMOGRAPH CREW LOCKHARG GEOPHYSICAL CO. WORKINGIN THE VICINITY OU PIPELINE APPROXIMATELY 12 MILES SOUTH OF OUR DUMAS PLANT.A HOLE 1-1/2 IN DIAMETER WAS MUNCTURED IN OUR DUMAS AND AMARILLO PLANTS WERESHUT DOWN AND THE PIPELINE SEGMENT WAS ISOLATED WITH IN 2 HOURS OFDISCOVERY. 14 MILES OF PIPELINE WERE BLOWN DOWN AND THE PIPELINE WASREPAIRED WITH A 5 FOOT PUP AND WAS BACK IN SERVICE BY THE NEXT DAY.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19980071 | 1998-03-13 | 26040 | FOREST OIL CORP | SHIP SHOAL BLOCK |  | LA |  |  |  | 700 | 1998-01-11 |  | YES | 55 | 277A | LA | Null | NO | LEAK |  | 0 | 0 | 0 | 0 | 0 | Null | 0 | 0 |  |  | 850 | 1440 | BY TEST | 1440 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: GATHERING SYSTEM; PRTFL: VALVE; MLKD: NO DATA; PRTSY: OTHER; PRTSO: HOT TAP #3; PRTYR: 0; NMDIA: 0; THK: 0; SMYS: 0; VALVE: BULL PLUG; MANYR: 0; LOCLK: UNDER WATER; PNAME: L.E. FANTENOT; PHONE: 3038121656; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980072 | 1998-03-18 | 994 | WILLIAM FIELD SERVICES | MISSISSIPPI RIVER | ST. JAMES PARISH | LA |  | 65.54 | 3460+51 | 645 | 1998-02-25 | 1 | NO |  |  | LA | Null | NO | OTHER |  | 0 | 0 | 50000 | 34925.7885 | 76086.6684 | Null | 0 | 30 |  | 19980225 | 770 | 995 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: UNKNOWN; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1958; NMDIA: 20; THK: 0.5; SPEC: API 5 L; SMYS: 46000; SEAM: SEAMLESS; MANU: US STEEL/NATIONAL TUBE; MANYR: 1958; LOCLK: UNDER WATER; PNAME: JAMES C MASON - SENIOR COMPLIANCE; PHONE: 7132153022; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | ON FEBRUARY 25, 1998 AT APPROXIMATELY 6:45 AM, WILLIAMS FIELD SERVICES COMPANY(WFS) PERSONNEL WERE NOTIFIED BY A LOCAL CITIZEN THAT GAS WAS VENTING AT VALVESETTING 62-40 (LOCATED ON THE NORTH END OF DUAL 20" PIPELINES CROSSING THEMISSISSIPPI RIVER). WFS PERSONNEL WERE DISPATCHED TO VALVE SETTING 62 - 40 TOINVESTIGATE AND DISCOVERED THAT THE AUTOMATED VALVES ON THE TWO (2) 20" RIVERCROSSING LINES WERE CLOSED.PERSONNEL WERE THEN DISPATCHED TO VALVE ON THE MOSTWESTERLY 20" PIPELINE WAS DOWN TO 75 PSIG AND FALLING AND THE PIPELINE WASSECURED AND ISOLATED. THE EASTERLY PIPELINE WAS HOLDING WAS PRESSURE ANDRETURNED TO SERVICE. AT THE PRESENT TIME, RIVER DEPTH AND CURRENTS HAVEPREVENTED AN INVESTIGATION OF THE WESTERLY 20" PIPELINE CROSSING. WFS PLANS AFULL INVESTIGATION AS SOON AS RIVER CONDITIONS ALLOW. A SUPPLEMENTAL INCIDENTREPORT WILL BE SUBMITTED UPON COMPLETION OF THE INVESTIGATION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980073 | 1998-03-20 | 20230 | KOCH GATEWAY PIPELINE CO | VICKSBURG |  | MS |  | 1.93 | 101+20 | 1700 | 1998-02-20 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 59433 | 41514.8878 | 90441.1793 | Null | 9 | 30 |  | 19980221 | 381 | 445 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1966; NMDIA: 20; THK: 0.28; SPEC: 5; SMYS: 60000; SEAM: ERW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: WAYNE F ST. GERMAIN EH&S COORDINATOR; PHONE: 3189887102; PROT: Null; CAULK: EARTH MOVEMENT: SUBSIDENCE; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980075 | 1998-03-30 | 19160 | TENNESSEE GAS PIPELINE CO | EAST BERNARD |  | TX | 77435 | 166+47M.P. 17-1+3.15 | 17 | 355 | 1998-02-26 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 78000 | 54484.2301 | 118695.2028 | Null | 0 | 30 |  | 19980226 | 710 | 750 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | GIRTH | STEEL |  | PIPELINE |  | 1944 | 24 | 0.25 | API 5LX | 50000 | FLASH WELD | A.O. SMITH | A.O. SMITH | 1944 | UNDER GROUND |  | DARON K MOORE PRINCIPAL | 7137574023 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION | CRACK IN PRESSURE WELD. | YES | 19890603 | WATER |  | 8 | 1025
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980084 | 1998-04-06 | 18516 | SOUTHERN NATURAL GAS CO | COLLEGE PARK | FULTON | GA | 30337 | 448.514 ON NORTH PIPELINE |  | 920 | 1998-03-08 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 60000 | 41910.9462 | 91304.0021 | Null | 1 | 40 |  | 19980308 | 450 | 720 | BY TEST | 1085 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: METER RUN; MLKD: OTHER; MLKDO: RUN SWITCHING EQUIPMENT; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1986; NMDIA: 8; THK: 0.5; SPEC: API 5L GRADE B; SMYS: 35000; MANU: DANIEL INDUSTRIES; MANYR: 1986; LOCLK: ABOVE GROUND; PNAME: BILL MCCAIN; PHONE: 7704786405; PROT: Null; CAULK: NO DATA; DMGO: LIGHTENING; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null | RUN SWITCHING INSTRUMENTATION EQUIPMENT AT FULTON INDUSTRIAL METER STATIONWAS STRUCK BY LIGHTENING CAUSING A SMALL FIRE WHICH MIGRATED TO THE STATION'SMETER RUNS DUE TO MELTED SEAL COMPONENTS. A LARGER FIRE ENSUED RESULTING INSIGNIFICANT STATION DAMAGE. THE FIRE WAS CONTAINED AND EXTINGUISHED WITH NOINJURIES, AND NO DAMAGE TO PROPERTY OTHER THAN SOUTHERN'S.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980085 | 1998-04-14 | 2620 | COLUMBIA GULF TRANSMISSION CO | EUGENE ISLAND |  | LA |  | EI 273A TO 26" TIE-IN | EI285 TIE-IN,LAT28.24 LON | 1500 | 1998-03-20 |  | YES | E.I. | 285 |  | NO | NO | LEAK |  | 0 | 0 | 50000 | 34925.7885 | 76086.6684 | Null | 0 | 0 |  | 19980320 | 1094 | 1250 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: VALVE OPERATOR PIPING; MLKD: STEEL; PRTSY: OTHER; PRTSO: VALVE OPERATOR PIPING; PRTYR: 1970; NMDIA: 0; THK: 0; SMYS: 0; MANU: 1" VALVE OPERATOR PIPING; MANYR: 1970; LOCLK: UNDER WATER; PNAME: HENRY H. WANG MANAGER; PHONE: 7132674371; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; MRKTP: 0; STAT: NO; CTEST: Null | A TRAWLING NET BROKE THE 1" POWER GAS LINE FROM THE VALVE OPERATOR. THEBROKEN POWER GAS LINE WAS REMOVED AND THE 1" UNIONS WERE PLUGGED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980089 | 1998-04-22 | 18516 | SOUTHERN NATURAL GAS CO | SOUTH PASS BLOCK 62 |  | LA |  | MILEPOST 0 SOUTH PASS 62 | X=164,347.53 LONG 88 | 15 | 1998-03-28 |  | YES | SOUTH PASS | 62 |  | NO | NO | LEAK |  | 0 | 0 | 202000 | 141100.1855 | 307390.1405 | Null | 10 | 0 |  | 19980328 | 1125 | 1525 | BY TEST | 1795 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1970 | 20 | 0.5 | API 5LX | 52000 | SEAMLESS |  | US STEEL | 1970 | OTHER | ON OFFSHORE PLATFORM | KENNETH C PETERS | 2053257554 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | NO | 0 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | CORRODED PART WAS ABOVE WATER ON PLATFORM
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980090 | 1998-04-28 | 14026 | OASIS PIPELINE CO | LA GRANGE | FAYETTE | TX | 78945 | 107 | 5656+68 | 1115 | 1998-03-20 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 227400 | 158842.4861 | 346042.168 | Null | 8 | 35 |  | 19980320 | 9120 | 10500 | BY TEST | 13950 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1970 | 36 | 0.44 | API 5L X 60 | 60000 | SAW |  | MANNESMANN | 1970 | UNDER GROUND |  | CLIFTON R. REED | 8308753352 | [6 empty] | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 19980115 | YES | 1 | NO |  |  | Null |  |  |  | 0 | 0
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980091 | 1998-06-09 | 19160 | TENNESSEE GAS PIPELINE CO | CLAY CITY |  | KY | 40312 | 107-3+0.625 | MP 32+99.7 | 1530 | 1998-04-02 | 1 | NO |  |  | KY | Null | NO | LEAK |  | 0 | 0 | 64000 | 44705.0093 | 97390.9356 | Null | 2 | 30 |  | 19980402 | 730 | 810 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | GIRTH | STEEL |  | PIPELINE |  | 1950 | 26 | 0.28 | API 5LX | 52000 | DSAW |  | A. O. SMITH | 1950 | UNDER GROUND |  | DARON K MOORE | 7137574023 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION | CRACK IN THE GIRTH WELD | YES | 19861107 | WATER |  | 8 | 1016 | TENNESSE WAS INVESTIGATING A LOW POTENTEAL AREA WHEN WORKERS HEARD GAS LEAK ATTHIS LOCATION AND ISOLATED VALVE SECTION 107-3 TO 108-3.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980092 | 1998-06-09 | 22435 | WEST TEXAS GAS INC | DUMAS | MOORE | TX |  |  |  | 945 | 1998-05-08 | 1 | NO |  |  |  | Null | Null | LEAK |  | 0 | 0 | 0 | 0 | 0 | YES | 1 | 30 |  | 19980508 | 230 | 260 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1929; NMDIA: 22; THK: 0.38; SMYS: 0; MANYR: 0; LOCLK: UNDER PAVEMENT; PNAME: RICHARD D HATCHETT; PHONE: 9156824493; LOC: EXTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: GALVANIC; COAT: BARE; PROT: NO; CPYR: 0; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19980093 | 1998-06-09 | 22435 | WEST TEXAS GAS INC | DUMAS | MOORE | TX |  |  |  | 430 | 1998-05-12 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 1 | 50000 | 34925.7885 | 76086.6684 | Null | 1 | 30 |  | 19980512 | 200 | 260 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: FITTING; PRTFO: DRESSER COUPLING; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1929; NMDIA: 22; THK: 0.38; SMYS: 0; MANYR: 0; LOCLK: UNDER GROUND; PNAME: RICHARD D HATCHETT; PHONE: 9156824349; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: CONSTRUCTION; CTEST: Null; MED: NO DATA; TMPS: 0; LKPS: 0 | METHOD OF PIPELINE CONNECTION CAUSED 22" PIPELINE JOINT TO SEPARATE FROMDRESSER COUPLING.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980094 | 1998-06-08 | 19240 | TEXAS EASTERN TRANSMISSION CORP | BEALLSVILLE | MONROE | OH |  | 697.08 | 368+86 | 110 | 1998-05-06 | 1 | NO | OHIO |  | OH | Null | Null | RUPTURE | 30 | 0 | 0 | 3400000 | 2374953.6178 | 5173893.4535 | Null | 1 | 49 |  | 19980506 | 870 | 1000 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: GIRTH; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1952; NMDIA: 30; THK: 0.38; SPEC: API-5L; SMYS: 52000; SEAM: DSAW; MANU: NATIONAL TUBE; MANYR: 1952; LOCLK: UNDER GROUND; PNAME: DWAYNE TESCHENDORF; PHONE: 7136275123; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: SOIL SLIPPAGE; NOTIF: Null; MARK: Null; MRKTP: 1; STAT: Null; CTEST: Null | THE PIPELINE RUPTURE WAS DUE TO THE FORCES OF A SOIL SLIPPAGE ALONG AHILLSIDE.TEXAS EASTERN IS RELOCATING THE PIPELINE OUTSIDE THE AREA OF THE SOILSLIP.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980095 | 1998-05-14 | 5304 | FLORIDA GAS TRANSMISSION CO | BAYOU SORREL |  | LA |  | 4.71 | 248+80 | 2000 | 1998-04-08 | 1 | NO |  |  | LA | Null | NO | LEAK |  | 0 | 0 | 0 | 0 | 0 | YES | 2 | 0 |  | 19980409 | 873 | 968 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1963; NMDIA: 10; THK: 0.25; SPEC: API5LX; SMYS: 42000; MANYR: 1963; LOCLK: UNDER WATER; PNAME: MERLIN H MOSEMAN; PHONE: 7136457344; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | THE PORTION OF THE LATERAL WITH LEAK HAS BEEN TAKEN OUT OF SERVICE UNTIL AREPAIR CAN BE MADE. THE CAUSE OF THE LEAK WILL REMAIN UNKNOWN UNTIL THEREPAIR WORK COMMENCES DUE TO THE DEPTH OF THE WATER OVER THE PIPELINE AT THELEAK LOCATION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980096 |  | 7605 | HOUSTON PIPELINE CO | HOUSTON |  | TX |  |  |  |  | 1998-03-24 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 45000 | 31433.2096 | 68478.0016 | Null | 0 | 1 |  | 19980325 | 650 | 745 | NO DATA | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: MECHANICAL JOINT; MLKD: OTHER; MLKDO: GASKET; PRTSY: COMPRESSOR STATION; PRTYR: 1963; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: DAVID J TONSALL; PHONE: 7136466389; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: NO DATA; CTEST: Null; MED: NO DATA; TMPS: 0; LKPS: 0 | GASKET FAILURE
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19980097 | 1998-03-25 | 6141 | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | DEXTER | CHAVES | NM | 88201 | 6 MILES EAST OF MP #4 |  | 430 | 1998-03-07 | 1 | NO |  |  |  | Null | NO | OTHER | 0 | 0 | 1 | 10000 | 6985.1577 | 15217.3337 | Null | 2 | 20 | 427286 | 19980308 | 330 | 348 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: VALVE; MLKD: STEEL; PRTSY: PIPELINE; NMDIA: 20; THK: 0.16; SPEC: 5L; SMYS: 35000; SEAM: ERW; VALVE: PLUG; MANU: NORDSTROM 800 PSIG VALVE; LOCLK: ABOVE GROUND; PNAME: JOEL LEVINE; PHONE: 5052414527; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | UPON ARRIVAL I OBSERVED THAT A VEHICLE FULLY ENGULFED IN FLAMES AND THE DRIVEROF THE VEHICLE HAD BEEN TRANSPORTED TO THE HOSIPTAL IN ROSWELL, NM. FURTHERINVESTIGATION SHOWED THANT THE VEHICLE WAS TRAVELING EASTBOUND ON STATE ROAD560. FOR AN UNKNOWN REASON THE VEHICLE TRAVELED OFF THE ROAD AND INTO THEWEST BOUND BARDITCH. THE VEHICLE THEN STRUCK A GAS PIPE LINE VALVE AND THENAN ELECTRIC POLE. WHEN THE VEHICLE STRUCK THE GAS PIPE LINE VALVE, IT KNOCKEDTHE VALVE OFF THE PIPE. A SPARK FROM THE VEHICLE IGNITED THE GAS AND FULLYENGULFED THE VEHICLE. THE DRIVER MANAGED TO ESCAPE FROM THE VEHICLE. THEDRIVER SUSTAINED BURNS ON HIS ARMS AND LEGS. THE VEHICLE WAS BURNEDCOMPLETELY AND NO IDENTIFICATION COULD BE MADE OF THE VEHICLE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980098 | 1998-05-06 | 602 | NORAM GAS TRANSMISSION, A NORAM ENERGY COMPANY | COALGATE | COAL | OK | 74827 | 171+80 |  | 1115 | 1998-04-02 | 1 | NO |  |  |  | Null | NO | RUPTURE | 8 | 0 | 0 | 50000 | 34925.7885 | 76086.6684 | Null | 2 | 0 |  | 19980402 | 550 | 1114 | BY TEST | 1550 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1980; NMDIA: 16; THK: 0.28; SPEC: X-60; SMYS: 60000; SEAM: ERW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: TED VANDEKAMP; PHONE: 3184293606; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: NO DATA; CTEST: Null; MED: NO DATA; TMPS: 0; LKPS: 0 | these are the remarks
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980099 | 1998-05-29 | 602 | NORAM GAS TRANSMISSION, A NORAM ENERGY COMPANY | COALGATE | COAL | OK | 74827 | 172+00 |  | 830 | 1998-04-08 | 1 | NO |  |  |  | Null | NO | RUPTURE | 16 | 0 | 0 | 400000 | 279406.308 | 608693.3475 | Null | 0 | 35 |  | 19980408 | 712 | 1114 | BY CFR 192.619(A)(3) | 1550 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1980; NMDIA: 16; THK: 0.28; SPEC: X-60; SMYS: 60000; SEAM: ERW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: TED VANDEKAMP; PHONE: 3184293606; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: OVERBURDEN CAUSED LINE; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | FAILURE OCCURRED IN BEND THAT WRINKLED DUE TO OVERBURDEN LOAD IN HIGH BANK OFMUDDY BOGGY CREEK.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980100 | 1998-05-27 | 405 | ANR PIPELINE CO | VERMILION |  | LA |  | MP 9.7 | 360+68 | 1150 | 1998-04-20 | 1 | NO |  |  | LA | NO | NO | LEAK |  | 0 | 0 | 100000 | 69851.577 | 152173.3369 | Null | 0 | 0 |  | 19980420 | 848 | 1100 | NO DATA | 1645 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: MECHANICAL JOINT; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1966; NMDIA: 12; THK: 0.25; SPEC: API5LX; SMYS: 42000; SEAM: ERW; MANU: STUPP; MANYR: 1966; LOCLK: UNDER WATER; PNAME: DON CROSS; PHONE: 3134962460; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | A REPAIR SLEEVE INSTALLED ON AUGUST 31, 1990 WAS LEAKING. FOUND HAIRLINECRACK ON PIPE HAD OPENED AND PROPAGATED. THE REPAIR SLEEVE WAS UNABLE TOCONTAIN THE PRESSURE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980101 | 1998-05-26 | 13750 | NORTHERN NATURAL GAS CO (ENRON) |  |  | TX |  |  |  | 1330 | 1998-05-05 |  | YES | MATAGORDA | 638 |  | YES | NO | LEAK |  | 0 | 0 | 300000 | 209554.731 | 456520.0106 | Null | 0 | 50 |  | 19980505 | 1142 | 1350 | BY TEST | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: FLANGE GASKET; MLKD: OTHER; MLKDO: STAINLESS STEEL; PRTSY: PIPELINE; PRTYR: 1989; NMDIA: 16; THK: 0; SMYS: 0; MANYR: 0; LOCLK: NO DATA; PNAME: MERLIN MOSEMAN; PHONE: 7136467344; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: NO DATA; CAULO: LEAK WAS THE RESULT OF A RING JOINT FLANGE GASKET.; CTEST: Null; MED: NO DATA; TMPS: 0; LKPS: 0
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980102 | 1998-05-18 | 13750 | NORTHERN NATURAL GAS CO (ENRON) | BELMOND | WRIGHT | IA |  |  |  | 1740 | 1998-04-10 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 58000 | 40513.9147 | 88260.5354 | Null | 1 | 5 |  | 19980410 | 380 | 500 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: MECHANICAL JOINT; PRTFO: METER/VALVE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1933; NMDIA: 4; THK: 0.24; SMYS: 24000; MANU: NATIONAL TUBE; MANYR: 0; LOCLK: UNDER GROUND; PNAME: WILL BURKS JR; PHONE: 7136467966; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: UNKNOWN MOVEMENT; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19980103 | 1998-05-22 | 15007 | PACIFIC GAS & ELECTRIC CO | AROMAS | SAN BENITO | CA | 95076 | 10.0 |  | 922 | 1998-04-22 | 1 | NO |  |  | CA | Null | Null | RUPTURE | 700 | 0 | 1 | 4000000 | 2794063.0798 | 6086933.4747 | Null | 0 | 16 |  | 19980422 | 300 | 300 | BY TEST | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; PRTFO: METER/VALVE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1930; NMDIA: 10; THK: 0.19; SPEC: API 5L; SMYS: 31500; SEAM: LAP WELD; MANYR: 0; LOCLK: UNDER GROUND; PNAME: SHAN BHATTACHARYA; PHONE: 4159736998; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19980113 | 1998-06-15 | 405 | ANR PIPELINE CO | HIGH ISLAND |  | TX |  | X=3,766,441.78 | Y=102,372.94 | 1610 | 1998-05-11 | 1 | YES | HIGH ISLAND BLK 368 |  | TX | YES | NO | LEAK |  | 0 | 0 | 325000 | 227017.6252 | 494563.3448 | Null | 0 | 0 |  | 19980511 | 940 | 1440 | NO DATA | 2279 | CORROSION | CORROSION | EXTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1983 | 12 | 0.38 | API 5LX | 42000 | ERW |  | STUPP | 1983 | ABOVE GROUND |  | DON CROSS SR | 3134962460 | EXTERNALLY | LOCALIZED PITTING |  | OTHER |  | COATED | YES | 1983 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19980114 | 1998-06-10 | 405 | ANR PIPELINE CO | HIGH ISLAND |  | TX |  | MP 2.2 |  | 1730 | 1998-05-04 | 1 | YES | HIGH ISLAND BLK A271 |  | TX | Null | NO | LEAK |  | 0 | 0 | 50000 | 34925.7885 | 76086.6684 | Null | 0 | 0 |  | 19980504 | 923 | 1440 | NO DATA | 2175 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: GATHERING SYSTEM; PRTFL: FITTING; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1997; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: UNDER WATER; PNAME: DON CROSS SR; PHONE: 3134962460; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19980115 |  | 2616 | COLUMBIA GAS TRANSMISSION CORP | RIPLEY | JACKSON | WV | 25275 |  |  | 1030 | 1998-05-19 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 1 | 0 | 0 | 0 | Null | 0 | 0 |  | 19980519 | 0 | 0 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: METER/VALVE; MLKD: OTHER; MLKDO: METER/VALVE; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1954; NMDIA: 4; THK: 0; SPEC: ANSI 900; SMYS: 0; VALVE: PLUG NORDSTROM; MANU: DANIELS SENIOR OFFICE; MANYR: 1958; LOCLK: ABOVE GROUND; PNAME: STEVEN P BURNLEY; PHONE: 3043573575; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19980119 | 1998-05-11 | 31129 | BASIN EXPLORATION INC |  |  | LA |  |  |  | 2105 | 1998-03-27 |  | YES | WEST CAMERON | 45 | LA | YES | NO | RUPTURE | 13 | 0 | 0 | 600000 | 419109.462 | 913040.0212 | Null | 0 | 0 |  | 19980330 | 790 | 1440 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; PRTFO: METER/VALVE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1958; NMDIA: 16; THK: 0.84; SMYS: 7385; SEAM: SEAMLESS; MANU: PIPE DISTRIBUTERS, INC; MANYR: 1998; LOCLK: UNDER WATER; PNAME: CONNIE GOERS; PHONE: 2815883388; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; MRKTP: 0; STAT: NO; CTEST: Null
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19980124 | 1998-06-23 | 30940 | WILLIAMS ENERGY GROUP-FIELD SERVICES | HIGH ISLAND |  | TX |  | 6.72 | 355+00 | 1700 | 1998-05-18 |  | YES | HIGH ISLAND | 109 |  | YES | NO | LEAK |  | 0 | 0 | 75000 | 52388.6827 | 114130.0027 | Null | 72 | 0 |  | 19980521 | 930 | 1440 | BY TEST | 2160 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1990 | 12.7 | 0.38 | API 5L | 42000 | SEAMLESS | N/A | UNKNOWN | 1990 | UNDER WATER |  | CHRIS MASON | 7132153022 | INTERNALLY | OTHER | UNKNOWN | OTHER | UNKNOWN | COATED | YES | 1990 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980126 | 1998-06-30 | 18516 | SOUTHERN NATURAL GAS CO | WHITE CASTLE | IBERVILLE | LA | 70788 | 30.74 | LAT 30" 11' 48" N LONG 91 | 1900 | 1998-06-02 | 1 | NO |  |  | LA | Null | NO | OTHER |  | 0 | 0 | 0 | 0 | 0 | YES | 0 | 45 |  | 19980602 | 884 | 1100 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: REXNARD GAS DETECTOR; MLKD: NO DATA; PRTSY: COMPRESSOR STATION; PRTYR: 1953; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: KENNETH C PETERS; PHONE: 2053257360; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | A CATALYTIC GAS SENSOR IN A COMPRESSOR BUILDING GAS DETECTOR MALFUNCTIONED,INDICATING A FALSE PRESENCE OF NATURAL GAS AT A LEVEL WHICH CAUSED THEAUTOMATED COMPRESSOR STATION'S EMERGENCY SHUTDOWN (ESD) SYSTEM TO ACTIVATE.THIS RESULTED IN A RELEASE OF GAS TO THE ATOMOSPHERE THROUGH THE STATION'SBLOWDOWN PIPING. THE ASSOCIATED NOSE OF THE HIGH PRESSURE GAS RELEASEATTRACTED THE ATTENTION OF LOCAL EMERGENCY RESPONSE PERSONNEL WHO INITIATED APRECAUTIONARY EVACUATION OF NEARBY RESIDENTS AND BLOCKED TRAFFIC ON A PARISHROAD. THE EMERGENCY RESPONSE PERSONEL ACTED OF THEIR OWN ACCORD WITHOUT ANYDECLARTION OF AN EMERGENCY FROM SOUTHERN'S COMPRESSOR STATION EMPLOYEES.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980130 |  | 21031 | PG & E TEXAS PIPELINE, L.P. | PHARR | HIDALGO | TX | 78577 | MP 86.5 | 4458+30 | 943 | 1998-06-06 | 3 | NO |  |  | TX | Null | NO | OTHER |  | 0 | 0 | 5000 | 3492.5788 | 7608.6668 | YES | 3 | 0 |  | 19980608 | 365 | 420 | BY TEST | 193 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1927; NMDIA: 12; THK: 0.25; SMYS: 0; SEAM: LAP WELD; VALVE: 2" MUELLER; MANU: MUELLER; MANYR: 0; LOCLK: UNDER GROUND; PNAME: KEVIN SEHY; PHONE: 2105284202; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19980504; MARK: YES; MRKTP: 3; STAT: Null; CTEST: Null | PAVING COMPANY USING A MAINTAINER AT THE INTERSECTION OF POLK ST & I ROAD INPHARR, TEXAS HIT A 2" TAP ON A 12" TRANSMISSION LINE. THIS IN TURN SPLIT THEWELD ON THE 2" TO 12" CONNECTION. LINE PRESSURE WAS REDUCED TO 20#'S AND A12" SPLIT-SLEEVE CLAMP WAS INSTALLED.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19980136 | 1998-07-06 | 18409 | SOUTH CAROLINA PIPELINE CORP | AIKEN | AIKEN | SC |  | BETWEEN 12-10 & 12-20 | 39+70 | 1302 | 1998-05-30 | 3 | NO |  |  |  | Null | NO | RUPTURE | 30 | 0 | 1 | 100000 | 69851.577 | 152173.3369 | Null | 0 | 45 |  | 19980530 | 1001 | 1014 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | LONGITUDINAL | STEEL |  | PIPELINE |  | 1961 | 10.75 | 0.22 | API-5L | 42000 | ERW |  | LONE STAR STEEL | 0 | UNDER GROUND |  | JOHN TROY BLALOCK | 8036995811 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL |  | Null |  | NO DATA |  | 0 | 0 | FAILURE OCCURRED IN ERW WELD. METALLURGICAL CONSULTANTS INC HAS DETERMINEDTHE MOST PROBABLE CAUSE TO BE HOOK CRACKS IN THE ERW WELD AREA. ON MAY 30,1998, AT APPROXIMATELY 1:02 PM, SOUTH CAROLINA PIPEINE CORPORATION EXPERIENCEDA FAILURE ON 10" LINE L IN AIKEN COUNTY BETWEEN OUR SOUTHERN COMPRESSORSTATION 12-10 AND AIKEN NORTH COMPRESSOR STATION 12-20. THE SPECIFIC LOCATIONOF THE FAILURE WAS ON THE DOWNSTREAM SIDE OF THE CASING BENEATH HWY #421 NEAR#118 BYPASS. SIX PEOPLE HAVE BEEN TREATED FOR INJURIES AS A RESULT OF THEFAILURE. FOUR OF THE INJURIES WERE A RESULT OF A FAMILY TRAVELING IN ANAUTOMOBILE DOWN HWY #421 AT THE TIME OF THE FAILURE. THE FORCE OF THE NATURALGAS ESCAPING FROM THE FAILED PIPE HURLED DEBRIS AND MUD ONTO THE CAR. ANOTHERINDIVIDUAL INJURED HER FOOT WHILE LEAVING HER HOUSE AFTER SHE HEARD THE NOISEAS RESULT OF THE FAILURE. ONE PERSON WAS HOSPITALIZED OVERNIGHT AS A RESULTOF THE INCIDENT DUE TO A COMPLAINT OF FUMES FROM THE ESCAPING NATURAL GAS.AT THE TIME OF THE INCIDENT, SCPC WAS RUNNING THREE SOLAR SATURN TURBINESCOMPRESSING NATURAL GAS INTO THE NORTH SYSTEM IN PREPARTION FOR EXPECTEDELECTRIC TURBINNE GENERATION LATER THAT DAY. THE PRESSURE AND FLOW RATE PRIORTO THE INCIDENT ON THE DISCHARGE SIDE OF SOUTHERN COMPRESSOR STATION INTO THENORTH SYSTEM WAS 1000.5 AND FLOWING 4785.94 MCFH AT 1:01 PM.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980137 | 1998-07-10 | 26316 | GAYLORD CONTAINER LTD | BAXTERVILLE | LAMAR | MS |  |  |  | 1030 | 1998-06-19 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 3000 | 2095.5473 | 4565.2001 | YES | 3 | 0 |  | 19980622 | 350 | 750 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; PRTFO: LONGITUDINAL; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1960; NMDIA: 8.63; THK: 0.25; SMYS: 0; MANYR: 0; LOCLK: UNDER GROUND; PNAME: FRANK HARRIS; PHONE: 5047328594; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: 3; STAT: YES; CTEST: Null | ROAD GRADING MACH WAS DIGGING DITCH ALONGSIDE OF ROAD AND CUT TO DEEP ANDSTRUCK 8" GAS LINE WITH BLADE, CUTTING A 3" X 1/4" INCH GASH IN PIPELINE
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980138 | 1998-06-18 | 18152 | SEA ROBIN PIPELINE CO |  |  | LA |  |  |  | 1350 | 1998-05-19 |  | YES | SOUTH MARSH ISLAND | 210 | LA | YES | NO | LEAK |  | 0 | 0 | 150000 | 104777.3655 | 228260.0053 | Null | 12 | 0 |  | 19980519 | 850 | 1440 | BY TEST | 2170 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | FITTING | REDUCING TEE | STEEL |  | PIPELINE |  | 1998 | 2 | 0.22 | ASME B16.9 | 35000 |  |  |  | 0 | UNDER WATER |  | KENNETH C PETERS | 2053257554 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION | 6"X6" X 2" WELD REDUCING TEE XSTG GRADE B | YES | 19980410 | WATER |  | 4 | 2170 | A RECENTLY INSTALLED SUBSEA ASSEMBLY DEVELOPED A LEAK IN THE HEAT EFFECTEDWELD ZONE NEAR THE GIRTH WELD ON THE 2" BRANCH OF A 6X6X2 REDUCING TEE. THELEAK WAS DUE TO A TEAR IN THE TEE MATERIAL APPARENTLY CAUSED DURINGSAND-CEMENT BAG COVER INSTALLATION. A METALLURGICAL ANALYSIS IS UNDERWAY TOBETTER DETERMINE THE CAUSE OF THE TEAR.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980139 | 1998-07-06 | 1039 | TRANSTEXAS TRANSMISSION CORP |  | GALVESTON | TX |  | 29 27' 48",94 53' 54" | #4 BUOY DICKINSON CHANNEL | 1630 | 1998-06-15 |  | YES | GALV | 331 | TX | Null | NO | LEAK |  | 0 | 0 | 0 | 0 | 0 | Null | 2 | 30 |  | 19980615 | 750 | 1240 | BY TEST | 1860 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1998; NMDIA: 20; THK: 0.26; SPEC: 5L X 65 ERW; SMYS: 65000; SEAM: ERW; VALVE: BALL VALVE; MANU: STUPP STEEL; MANYR: 1997; LOCLK: UNDER WATER; PNAME: DANA W JORDAN; PHONE: 2819878600; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; MRKTP: 0; STAT: NO; CTEST: Null | DAMAGE WAS APPARENTLY CAUSED BY UNKNOWN FORCES (PERHAPS SHRIMP NETS) DRAGGINGOFF THE ANCHOR WEIGHTS OF THE PIPELINE, ALLOWING IT TO FLOAT UP NEAR THESURFACE WHERE AN UNKNOWN MOTOR VESSEL CAUSED EXTENSIVE PROPERTY DAMAGE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980140 |  | 20230 | KOCH GATEWAY PIPELINE CO | VENICE |  | LA | 70091 |  | 79 + 73 | 1000 | 1998-06-06 | 1 | NO |  |  | LA | Null | NO | LEAK |  | 0 | 0 | 0 | 0 | 0 | YES | 8 | 0 |  | 19980618 | 450 | 982 | BY TEST | 1082 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: NO DATA; MLKD: NO DATA; PRTSY: PIPELINE; PRTYR: 1952; NMDIA: 10; THK: 0.5; SMYS: 35000; MANYR: 0; LOCLK: UNDER WATER; PNAME: WAYNE F ST GERMAIN; PHONE: 3189687102; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | MINOR BUBBLES DISCOVERED MISS. RIVER REMOTE X-ING NEAR BANK. UNABLE TO VERIFYCAUSE/POSSIBLE FUTURE REPAIR COSTS W/O JEOPARDIZING DIVER SAFETY. BECAUSE OFLIMITED NEED FOR LINE, WE MAY NOT REPAIR IT OR PUT IT BACK IN SERVICE.REPORTED TO NRC JUST IN CASE WE DO & COSTS JUSTIFY REPORTING.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980156 | 1998-07-27 | 12462 | MID LOUISIANA GAS CO | VIDALIA |  | LA | 71373 | 90.0 T-1 MAIN | 4799+50 APPROX | 1220 | 1998-07-23 | 1 | NO |  |  | LA | Null | NO | LEAK |  | 0 | 0 | 0 | 0 | 0 | YES | 1 | 30 |  | 19980724 | 153 | 949 | BY TEST | 1044 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: NO DATA; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1979; NMDIA: 10; THK: 0.5; SPEC: API 5L; SMYS: 35000; SEAM: SEAMLESS; MANU: J & L; MANYR: 1979; LOCLK: UNDER WATER; PNAME: RAMON L. SIMPSON; PHONE: 3186654426; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: CHANNEL BOTTOM SCOUR; NOTIF: Null; MARK: Null; MRKTP: 1; STAT: Null; CTEST: Null | SUPPLEMENTAL REPORT TO BE FILED AFTER PIPE IS INSPECTED & REPAIR ATTEMPTED.INSPECTION & REPAIR WILL BE DELAYED UNTIL RIVER LEVEL FALLS TO LEVEL SAFE FORDIVER TO WORK.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980157 | 1998-07-15 | 12462 | MID LOUISIANA GAS CO | VIDALIA | CONCORDIA | LA | 71373 | 90.9, T-1 LOOP | 4799+50 APPROX | 915 | 1998-07-07 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 0 | 0 | 0 | YES | 1 | 30 |  | 19980707 | 153 | 949 | BY TEST | 1044 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: NO DATA; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1979; NMDIA: 10; THK: 0.5; SPEC: API 5L; SMYS: 35000; SEAM: SEAMLESS; MANU: J & L; MANYR: 1979; LOCLK: UNDER WATER; PNAME: RAMON L SIMPSON; PHONE: 3186654426; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: CHANNEL BOTTOM SCOUR; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | SUPPLEMENTAL REPORT TO BE FILED AFTER PIPE IS INSPECTED AND REPAIR ATTEMPTED.INSPECTION AND REPAIR WILL BE DELAYED UNTIL RIVER LEVEL FALLS TOLEVEL SAFE FOR DIVER TO WORK.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19980158 | 1998-08-17 | 11680 | LONE STAR PIPELINE CO (TRANSMISSION DIVISION) | FORT WORTH | TARRANT | TX |  | LINE CA6(16') AERIAL MARK |  | 1420 | 1998-07-07 | 1 | NO |  |  |  | Null | NO | OTHER |  | 1 | 0 | 450000 | 314332.0965 | 684780.0159 | Null | 0 | 30 |  | 19980707 | 260 | 500 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: NO DATA; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1971; NMDIA: 16; THK: 0.25; SPEC: API 5LX-60; SMYS: 1878; SEAM: EW SMLS; MANYR: 0; LOCLK: UNDER GROUND; PNAME: P. E. TUCKER; PHONE: 2148125550; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19980528; MARK: YES; MRKTP: 0; STAT: YES; CTEST: Null | THIRD PARTY CONTRACTOR CUT THE PIPELINE WHILE TRENCHING.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980159 | 1998-08-14 | 22655 | WILLISTON BASIN INTERSTATE PIPELINE CO | GILLETTE | CAMPBELL | WY |  | 0+00 | 0+00 | 1813 | 1998-07-21 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 415350 | 290128.525 | 632051.9547 | Null | 0 | 57 |  | 19980721 | 830 | 1000 | BY TEST | 1200 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: THIRD PARTY EQUIPMENT; MLKD: STEEL; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1997; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: CRAIG WAGNER; PHONE: 4063654351; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | THIS INCIDENT OCCURRED AT A RECEIPT POINT WITH A GATHERING SYSTEM OPERATOR. ARELIEF VALVE ON THE GATHERING SYSTEM OPERATED AND CAUGHT FIRE. THE HEAT FROMTHE FIRE DESTROYED WILLISTON BASIN'S RECEIPT STATION. PIPELINE HAS BEENREPAIRED AND SYSTEM IS BACK TO NORMAL.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980160 | 1998-08-13 | 602 | NORAM GAS TRANSMISSION, A NORAM ENERGY COMPANY | EL DORADO | UNION | AR | 71730 | DETROIT T.B. STATION |  | 1811 | 1998-07-15 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 80000 | 55881.2616 | 121738.6695 | Null | 0 | 34 |  | 19980715 | 270 | 300 | BY TEST | 1500 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: INSULATING GASKET; MLKD: OTHER; MLKDO: GASKET; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 0; NMDIA: 4; THK: 0.24; SPEC: GRADE B; SMYS: 35000; SEAM: SEAMLESS; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: TED VANDE KAMP; PHONE: 3184293606; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | LIGHTNING STRUCK METER STATION PIPING. THE INSULATING GASKET ON THE OUTLETSIDE OF THE LOWER METER TUBE ISOLATION VALVE FAILED. IGNITION OCCURRED WHERETHE GASKET FAILED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980161 | 1998-08-13 | 2714 | CNG TRANSMISSION CORP | HUNDRED | WETZEL | WV |  | 490' S. LAMBERT JCT | 1023+99 | 800 | 1998-07-11 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 50000 | 34925.7885 | 76086.6684 | Null | 1 | 30 |  | 19980711 | 700 | 960 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1959; NMDIA: 24; THK: 0.31; SPEC: X-52; SMYS: 52000; SEAM: SEAMLESS; MANU: US STEEL; MANYR: 1959; LOCLK: UNDER GROUND; PNAME: MARTIN C SCHWOEBLE; PHONE: 3046238408; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19980421; MARK: YES; MRKTP: 2; STAT: Null; CTEST: Null | WHILE EXCAVATING FOR A NEW PIPELINE IL-492, A PACE PIPELINE TRACK HOE OPERATORWAS BACKFILLING NEW DITCH. SPOIL PILE WAS LOCATED OVER TOP OF EXISTING IL-342WHICH PARALLELS PLANNED TL-492. WHILE REQUIRING DIRT FROM SPOIL PILE, THEEQUIPMENT OPERATOR DUG INTO EXISTING TL-342.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19980162 | 1998-08-13 | 2688 | CONECUH - MONROE COUNTIES GAS DIST | CASTLEBERRY | CONECUH | AL | 36432 | US HWY 31, MP 79.7 |  | 1710 | 1998-07-15 | 3 | NO |  |  | AL | Null | NO | LEAK |  | 0 | 1 | 170000 | 118747.6809 | 258694.6727 | Null | 0 | 20 |  | 19980715 | 320 | 600 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: TAPPING TEE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1962; NMDIA: 6; THK: 0.19; SPEC: API5L; SMYS: 35000; SEAM: ERW; MANYR: 1962; LOCLK: UNDER GROUND; PNAME: JERRY B PARKER; PHONE: 3345782740; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19980608; MARK: YES; MRKTP: 3; STAT: YES; CTEST: Null | AT 4:50 PM THE GAS DISTRICT RECEIVED NOTICE BY TELEPHONE OF A GAS LEAK FROMTHE OCCUPANT OF 45687 HIGHWAY 31. THE LOCATION WAS SOUTH OF CASTLEBERRY INCONECUH COUNTY, ALABAMA. SEVERAL DISTRICT PERSONNEL LEFT THE OFFICE TORESPOND TO THE SCENE. THEY DISCOVERED THAT A CREW INSTALLING FIBER OPTICCABLE USING A BULLDOZER WITH VIBRATORY PLOW UNIT HAD DAMAGED THE GAS LINE ONTHE EAST SIDE OF HIGHWAY 31 AT APPROXIMATELY MILEPOST 79.7. GAS WAS LEAKINGAND ESCAPING UP THROUGH THE GROUND. IT WAS UNSURE AT THIS TIME IF MAIN ORSERVICE WAS DAMAGED. THE PRESSURE ON THE LINE WAS APPROXIMATELY 320 PSI. TWOEMPLOYEES PULLED THEIR TRUCKS INTO POSITION TO HELP BLOCK TRAFFIC ON HWY 31.ANOTHER EMPLOYEE UNLOADED A TRENCHER FROM ITS TRAILER AND PULLED IT CLOSE TOTHE LEAK AREA. AT APPROXIMATELY 5:10, THE GAS IGNITED CAUSING A FIRE. THEFIRE BURNED THE EMPLOYEE ON THE TRENCHER. AN AMBULANCE WAS CALLED AND HE WASTAKEN TO THE HOSPITAL IN BREWTON, ALABAMA. THE FIRE ALSO DAMAGED THEDISTRICT'S TRENCHER, AND HEAVILY DAMAGED THE CONTRACTOR'S BULLDOZER AND ROLLOF FIBER OPTIC CABLE. OTHER DISTRICT PERSONNEL CLOSED MAIN LINE VALVES TOSTOP THE GAS FLOW, WHILE OTHERS BEGAN GOING TO CUSTOMER METERS AND LOCKING THESERVICE VALVES. A TOTAL OF 52 CUSTOMERS WAS AFFECTED. ALSO RESPONDING TO THESITE WAS THE CONECUH COUNTY EMERGENCY MANAGEMENT AGENCY DIRECTOR AND UNITSFROM SEVERAL LOCAL FIRE DEPARTMENT. AT 6:10 PM THE INCIDENT WAS REPORTED TOTHE NATIONAL RESPONSE CENTER IN WASHINGTON, D.C. THE ALABAMA PUBLIC SERVICECOMMISSION WAS ALSO CONTACTED. LAW ENFORCEMENT PERSONNEL BLOCKED THE HIGHWAYUNTIL ALABAMA DEPARTMENT OF TRANSPORTATION PERSONNEL STARTED DETOURING TRAFFICAROUND THE INCIDENT SITE. THE FIRE WAS ALLOWED TO BURN UNTIL THE SUPPLY OFGAS WAS EXHAUSTED. ON THURSDAY MORNING, 7/16/1998, AT 9:00 PM, DISTRICPERSONNEL BEGAN EXCAVATING THE AREA AROUND THE DAMAGED PIPELINE. IT WASDISCOVERED THAT THE PLOW HAD TWISTED AND BROKEN LOOSE A 3/4' SERVICE LINE FROMITS TAPPING TEE. THE SERVICE LINE SERVES THE RESIDENCE AT 45687 HIGHWAY 31.WHEN THE GAS FLAME HAD SUBSIDED ENOUGH, DISTRICT PERSONNEL SHUT OFF THETAPPING TEE AND WELDED THE SERVICE LINE TO THE TEE. SINCE IT APPEARED THATTHE PLOW HAD CROSSED THE GAS MAIM PRIOR TO STRICKING THE SERVICE LINE,DISTRICT PERSONNEL DUG OUT ALONG THE LENGTH OF THE MAIN TO SEE IF THERE WASANY MORE DAMAGE TO THE LINE OR COATING DAMAGE. IT WAS DISCOVERED THE PLOW HADMADE A GOUGE NEAR THE TAPPING TEE 0.050' DEEP, AND A 26'-27' LONG INDENTION ATLEAST 3/4' DEEP AT THE DEEPEST POINT. COATING DAMAGE WAS ALSO EVIDENT ALONG65'-70 OF THE LINE. THE DECISION WAS MADE AT THIS TIME TO REPLACEAPPROXIMATELY 74' OF 6' STEEL PIPE. THE SITE WAS EXCAVATED ON THURSDAYAFTERNOON. ON FRIDAY MORNING 7/17/1998, DISTRIC PERSONNEL BEEN PREPARING THEMAIN FOR INSTALLATION OF TWO STOPPER FITTINGS. THROUGHOUT FRIDAY AND SATURDAY,STOPPER FITTINGS WERE INSTALLED, GAS FLOW STOPPED, THE DAMAGED SECTION OFPIPELINE WAS REMOVED, AND THE NEW SECTION WAS WELDED INTO PLACE. A NEWTAPPING TEE AND SECTION OF 3/4' SERVICE LINE INSTALLED FOR THE SERVICE TO45687 HIGHWAY 31. BY 6:00 PM SATURDAY 7/18/98, NORMAL PIPELINE OPERATION WASRESUMED AND THE SITE BACKFILLED AND LEVELED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980163 | 1998-08-07 | 8070 | INDIANA GAS CO INC | HARRODSBURG | MONROE | IN | 47434 | 9303 S HARRODSBURG RD |  | 1300 | 1998-07-17 | 3 | NO |  |  | IN | Null | NO | LEAK |  | 0 | 0 | 150000 | 104777.3655 | 228260.0053 | Null | 1 | 15 |  | 19980720 | 275 | 420 | BY TEST | 630 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: BODY OF PIPE; PRTFO: TAPPING TEE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1946; NMDIA: 8; THK: 0.25; SPEC: B; SMYS: 24000; MANYR: 1945; LOCLK: UNDER GROUND; PHONE: 3173210518; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19980427; MARK: NO; MRKTP: 0; STAT: YES; CTEST: Null | A CONTRACTOR WORKING FOR THE MONROE COUNTY HIGHWAY DEPARTMENT WAS INSTALLINGGUARD RAILING FOR A COUNTY BRIDGE. A TRUCK-MOUNTED PILE DRIVER WAS BEING USEDTO INSTALL ALUMINUM POSTS TO WHICH THE GUARD RAILING WOULD BE ATTACHED. ATAPPROXIMATELY 1:00 PM ON JULY 17, 1998, ONE OF THE ALUMINUM POSTS THEY WEREINSTALLING STRUCK AND DAMAGED AN INDIANA GAS CO. 8-INCH STEEL PIPELINE, WITH ANORMAL OPERATING PRESSURE OF 275 PSIG. NATURAL GAS BEGAN TO ESCAPE FROM THE3-INCH X .5 INCH HOLE IN THE PIPELINE AND FOUND A SOURCE OF IGNITION IN THECONTRACTOR'S TRUCK ENGINE. THE RESULTANT FIRE DESTROYED THE TRUCK, ANDDAMAGED OVER HEAD TELEPHONE LINES. AS THE SYSTEM WAS ISOLATED BY TWO (2)VALVES, 97 CUSTOMERS LOST GAS SERVICE. SERVICE WAS RESTORED AFTER REPAIRSWERE MADE. FACILITY LOCATE REQUESTS WERE MADE ON APRIL 27, 1998. INDIANA GASCO. MARKED THE FACILITIES AS REQUESTED ON APRIL 28, 1998. NO SUBSEQUENTLOCATE REQUESTS WERE MADE. THE TIME FRAME BETWEEN THE ONLY LOCATE REQUEST ANDTHE ACTUAL CONSTRUCTION WAS EIGHTY (80) DAYS. INDIANA LAW STATES THAT THENOTICE OF INTENT TO EXCAVATE IS VALID FOR A PERIOD FROM TWO TO TWENTY CALENDARDAYS AFTER THE REQUEST IS RECEIVED. A NEW NOTICE IS REQUIRED AFTER TWENTYCALENDER DAYS IF THE EXCAVATION HAS NOT STARTED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980164 | 1998-08-05 | 15014 | PACIFIC GAS TRANSMISSION CO | STANFIELD |  | OR | 97838 | 282.76 | 8-89+820 | 1415 | 1998-07-06 | 1 | NO |  |  | OR | Null | NO | LEAK |  | 0 | 0 | 139000 | 97093.692 | 211520.9382 | Null | 0 | 30 |  | 19980706 | 900 | 911 | BY TEST | 1086 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: VALVE; PRTFO: TAPPING TEE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1970; NMDIA: 36; THK: 0.44; SPEC: API5LX52; SMYS: 52000; SEAM: DSAW; VALVE: 1 1/4 MUELLER; MANU: MUELLER COMPANY; MANYR: 1970; LOCLK: UNDER GROUND; PNAME: DAVID H STITT; PHONE: 5038334711; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | 14:15-A PG&E GT-NW EMPLOYEE DOING ROUTINE MAINTENANCE DISCOVERED A NATURAL GASLEAK NEAR THE STANFIELD, OREGON CITY METER STATION MAINLINE "A" TAP. IT WASNOT APPARENT IF THE LEAK WAS COMING FROM THE MAINLINE OR THE METER STATIONSERVICE PIPING. PHYSICAL SIGNS AT THE LEAK SITE REVEALED AN APPROXIMATE 9'DIAMETER SOIL DISTRUBANCE AT THE GROUND SURFACE BLOWING NATURAL GAS. THEREWERE NO OTHER PHYSICAL SIGNS OF GROUND DISTURBANCE AT THE SITE. PG&E GT-NWWAS AT THIS SITE ON 7/3/98 DOING ROUTINE MAINTENANCE AND THERE WAS NOINDICATION OF A LEAK. 14:30- PG&E GT=NW GAS CONTROL WAS INFORMED OF THELEAK. PIPELINE EMERGENCY PROCEDURES AND NOTIFICATIONS WERE INTITATED. THEDECISION WAS MADE TO ISOLATE AND BLOWDOWN MAINLINE "A" FROM MLV 8-2 TO MLV 8-3AND TO CONTINUE SERVICE OF THE STANFIELD METER THROUGH THE MAINLINE "B" TAP.CREWS WERE DISPATCHED TO MLV 8-2 AND MLV 8-3 WHICH WERE 5.3 MILES UPSTREAM AND12.4 MILES DOWNSTREAM RESPECTIVELY TO PREPARE FOR VALVE SECTION ISOLATIONPROCEDURES. 14:45-PG&E GT-NW CREWS SECURED THE LEAK SITE BY MANNING THE SITEON A CONTINOUS BASIS. THE LEAK SITE IS A RURAL LOCATION CLASS 1 AREA.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980166 | 1998-08-25 | 405 | ANR PIPELINE CO |  |  | TX |  | X=3,496,710.29 | Y=95,083.00 | 1630 | 1998-07-23 |  | YES | HIGH ISLAND BLK | 555 | TX | Null | NO | LEAK |  | 0 | 0 | 150000 | 104777.3655 | 228260.0053 | Null | 0 | 0 |  | 19980723 | 1035 | 1440 | BY TEST | 2425 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | VALVE |  | STEEL |  | PIPELINE |  | 1980 | 20 | 0 |  | 0 |  | CHECK VALVE | C. WHEATLEY STREAM FLOW | 1980 | UNDER WATER |  | DON CROSS, SR | 3134962460 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | 20' CHECK VALVE | YES | 19791209 | WATER |  | 24 | 2425 | PACKING ON 20' CHECK VALVE STEM WAS LEAKING, 30I-20 TAP.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980168 | 1998-08-21 | 19160 | TENNESSEE GAS PIPELINE CO | CAMERON |  | LA |  | 507F-4200 | 507F-4201+4.2 | 1700 | 1998-07-23 |  | YES | FC | 48I |  | YES | NO | LEAK |  | 0 | 0 | 70000 | 48896.1039 | 106521.3358 | Null | 0 | 0 |  | 19980723 | 600 | 1440 | BY TEST | 2166 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | VALVE |  | OTHER | STEM PACKING | PIPELINE |  | 1976 | 0 | 0 |  | 0 |  | ANSI CLASS 900 | TOM WHEATLEY | 0 | UNDER WATER |  | R. BRUCE LONG | 7134202603 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | LEAK DEVELOPED IN STEM PACKING ON CHECK VALVE | Null |  | NO DATA |  | 0 | 0 | LEAK DEVELOPED IN STEM PACKING ON A SUBSEA CHECK VALVE.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19980169 | 1998-08-20 | 15105 | PANHANDLE EASTERN PIPELINE CO | WAVERLY | MORGAN | IL | 62692 |  |  | 1000 | 1998-07-17 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 1 | 0 | 0 | 0 | Null | 0 | 10 |  |  | 0 | 960 | BY TEST | 1440 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: VALVE; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1962; NMDIA: 75; THK: 0; SPEC: A-212-B; SMYS: 0; VALVE: PLUG; MANU: BLACK, SIVALLS & BRYSON; MANYR: 1962; LOCLK: ABOVE GROUND; PNAME: MITCHELL D. PUTNAM; PHONE: 3178793000; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | DUE TO A LEAKING VALVE, GAS ACCUMULATED IN A DEHY CONTRACTOR TOWER WHERE ANOUTSIDE CONTRACTOR WAS USING A CUTTING TORCH.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980175 | 1998-08-27 | 4280 | EL PASO NATURAL GAS CO | SONOITA | PIMA | AZ |  | MP 15.7 LINE 2122 | MP 15 + 3921 | 1145 | 1998-07-27 | 1 | NO |  |  | AZ | Null | NO | OTHER |  | 0 | 0 | 25000 | 17462.8942 | 38043.3342 | Null | 3 | 0 |  | 19980727 | 630 | 809 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1957; NMDIA: 4.5; THK: 0.18; SPEC: API 5L; SMYS: 35000; SEAM: ERW; MANYR: 1957; LOCLK: UNDER GROUND; PNAME: GILBERT ARAGON; PHONE: 9154962624; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; MRKTP: 1; STAT: Null; CTEST: Null | A ROAD GRADER OPERATED BY THE BUREAU OF LAND MANAGEMENT STRUCK THE 4 1/2 INCHLINE 2122 CAUSING A SIX INCH CUT ON THE PIPELINE. THERE WERE TWO TAPS THATWERE SHUT IN. THE PIPE WAS REPAIRED BY INSTALLING A 12-FOOT SECTION OF PIPE.THIS LINE WAS BACK IN SERVICE BY 7:05 PM. DOT CASE #447798
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19980176 | 1998-08-31 | 405 | ANR PIPELINE CO | CAMERON |  | LA |  | X=1,340,939 | Y=144,555 | 1610 | 1998-08-08 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 58000 | 40513.9147 | 88260.5354 | Null | 0 | 0 |  | 19980808 | 1183 | 1440 | BY TEST | 2510 | CORROSION | CORROSION | INTERNAL | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1979; NMDIA: 12; THK: 0.38; SPEC: API 5LX; SMYS: 52000; MANU: ARMCO STEEL; MANYR: 1979; LOCLK: UNDER WATER; PNAME: DON CROSS SR; PHONE: 3134967115; LOC: INTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: OTHER; COAT: COATED; PROT: YES; CPYR: 1979; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | INTERNAL CORROSION - PINHOLE LEAT AT 9 O'CLOCK POSITION.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980184 | 1998-09-08 | 5304 | FLORIDA GAS TRANSMISSION CO | FORT PIERCE |  | FL | 34945 | 781.7 |  | 2130 | 1998-08-03 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 263000 | 183709.6475 | 400215.876 | Null | 2 | 5 |  | 19980803 | 0 | 0 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: ESD BLOWDOWN SILENCER; MLKD: STEEL; PRTSY: OTHER; PRTSO: BLOWDOWN SILENCER; PRTYR: 1997; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: MERLIN MOSEMAN; PHONE: 7136467344; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | LIGHTING STORM IN VICINITY OF COMPRESSOR STATION INITIATED A STATION ESD ANDIGNITED GAS RELEASED AT BLOWDOWN SILENCER UNITS.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980186 | 1998-09-02 | 18516 | SOUTHERN NATURAL GAS CO | MOODY | ST. CLAIR | AL | 35004 | 341.5 N MAIN LOOP | LAT 33" 35' 47" LONG 86" | 930 | 1998-08-02 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 65500 | 45752.7829 | 99673.5356 | Null | 2 | 40 |  | 19980802 | 450 | 500 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; PRTFO: ESD BLOWDOWN SILENCER; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1948; NMDIA: 24; THK: 0.25; SPEC: API 5L; SMYS: 52000; SEAM: SAW; MANU: REPUBLIC; MANYR: 1948; LOCLK: UNDER GROUND; PNAME: KEN PETERS; PHONE: 2053257632; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | SOUTHERN'S CONTRACTOR, WORKING ON REPLACEMENT OF A PIPELINE ADJACENT TO THEONE DAMAGED, WAS PLACING PAD DIRT WITH A FRONT END LOADER. DURING A TURN, THEMACHINERY'S BUCKET CUT INTO THE SPOIL AT THE 24" NORTH MAIN LOOP PIPELINE. ATOOTH ON THE BUCKET GOUGED A HOLE INTO THE LINE ALLOWING GAS TO RELEASE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980187 | 1998-09-08 | 14026 | OASIS PIPELINE CO | GERONIMO | GUADALUPE | TX | 78115 | MP167.3/MLV-6 | 8836+79 | 1950 | 1998-08-02 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 347361 | 242637.1364 | 528590.8247 | Null | 9 | 20 |  | 19980802 | 879 | 938 | BY TEST | 1170 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | VALVE | ESD BLOWDOWN SILENCER | STEEL |  | OTHER | MAINLINE VALVE | 1970 | 36 | 0 | A105 | 35000 |  | GATE | M & J VALVE | 1970 | UNDER GROUND |  | CLIFTON R. REED | 8308753352 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | M & J ANSI 600# GATE VALVE | YES | 19700606 | WATER |  | 24 | 1170 | LEAK RESULTED FROM A CRACK WHICH DEVELOPED IN THE BODY OF A MAINLINE VALVE.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19980188 | 1998-09-18 | 5304 | FLORIDA GAS TRANSMISSION CO | PERRY | TAYLOR | FL | 32347 | 468.7 |  | 1440 | 1998-08-14 | 2 | NO |  |  |  | Null | NO | OTHER |  | 0 | 1 | 14738000 | 10294725.4174 | 22427306.3875 | Null | 6 | 20 | 450594 | 19980814 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: VALVE OPERATOR CONTROL; MLKD: STEEL; PRTSY: COMPRESSOR STATION; NMDIA: 0; THK: 0; SMYS: 0; LOCLK: ABOVE GROUND; PNAME: MERLIN MOSEMAN; PHONE: 7136467344; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | A COMPRESSOR STATION ESD WAS INITIATED DURING A LIGHTNING STORM IN THEVICINITY OF THE STATION. A LIGHTNING IGNITED THE GAS RELEASED AT THE ESDBLOWDOWN SILENCER UNITS.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980189 | 1998-09-17 | 31027 | AIR LIQUIDE AMERICA CORP. | CORPUS CHRISTI | NUECES | TX |  | 33.28 |  | 2208 | 1998-08-28 | 3 | NO |  |  |  | Null | NO | RUPTURE | 2 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 0 |  | 19980829 | 686 | 740 | BY TEST | 925 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE | VALVE OPERATOR CONTROL | STEEL |  | PIPELINE |  | 1936 | 6.66 | 0.19 | GRADE B | 35000 | SEAMLESS |  |  | 0 | UNDER GROUND |  | RONALD W SPEER | 7138680536 | EXTERNALLY | LOCALIZED PITTING |  | NO DATA |  | COATED | YES | 0 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | DETAILED METALLURGICAL FAILURE ANALYSIS BEING CONDUCTED ON FAILED SECTION OFPIPELINE. SUPPLEMENTAL REPORT WILL BE ISSUED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980194 | 1998-09-18 | 15350 | PEOPLES NATURAL GAS CO | CONEMAUGH | CAMBRIA | PA | 15909 | NO 2-2 | 1774+66 | 815 | 1998-08-18 | 3 | NO |  |  | PA | Null | NO | OTHER |  | 0 | 0 | 60000 | 41910.9462 | 91304.0021 | Null | 2 | 45 |  | 19980818 | 200 | 400 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1950; NMDIA: 14; THK: 0.38; SMYS: 0; SEAM: SEAMLESS; MANU: NATIONAL TUBE; MANYR: 0; LOCLK: UNDER GROUND; PNAME: J C DAILEY; PHONE: 4124975668; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19980813; MARK: NO; MRKTP: 0; STAT: YES; CTEST: Null | LINE LOCATOR AND CONSTRUCTION COMPANY THAT CAUSED DAMAGE DISAGREE OVER WHETHERACCURATE SITE LOCATION WAS SUBMITTED BY CONSTRUCTION COMPANY.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980195 | 1998-09-24 | 20110 | UNION LIGHT HEAT & POWER CO | ERLANGER | BOONE | KY | 41018 |  |  | 1350 | 1989-08-22 | 4 | NO |  |  | KY | Null | NO | RUPTURE | 0.5 | 0 | 0 | 84396 | 72735.6632 | 158456.3878 | Null | 2 | 15 |  | 19980822 | 350 | 392 | BY CFR 192.619(A)(3) | 750 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1956; NMDIA: 24; THK: 0.28; SPEC: API 5 LX; SMYS: 40; SEAM: ELECTRIC WELD; MANU: A O SMITH CORPORATION; MANYR: 1955; LOCLK: UNDER GROUND; PNAME: SUSAN M GILB; PHONE: 5132872751; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | WHILE EXCAVATING, A CONTRACTOR DUG INTO A TRANSMISSION PRESSURE GAS MAIN.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980196 | 1998-09-29 | 405 | ANR PIPELINE CO | VERMILION |  | LA |  | X=1,783,036.80 | Y=382,151.09 | 1207 | 1998-08-28 | 1 | NO |  |  | LA | Null | NO | LEAK |  | 0 | 0 | 98400 | 68733.9518 | 149738.5635 | Null | 0 | 0 |  | 19980828 | 848 | 1100 | BY TEST | 1645 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1966 | 12 | 0.25 | API 5LX | 42000 | ERW |  | STUPP | 1966 | UNDER WATER |  | DON CROSS, SR | 3134962460 | INTERNALLY | LOCALIZED PITTING |  | OTHER |  | COATED | YES | 1966 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | A PINHOLE LEAK AT 5 O'CLOCK POSITION CONSISTENT WITH INTERNAL CORROSION.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980197 | 1998-09-28 | 19160 | TENNESSEE GAS PIPELINE CO | EAST CAMERON |  | LA |  | 509A-400 | 509A-401+1.92 | 1200 | 1998-08-26 |  | YES | EC | 254B | LA | YES | NO | LEAK |  | 0 | 0 | 250000 | 174628.9425 | 380433.3422 | Null | 0 | 0 |  | 19980826 | 970 | 1440 | BY TEST | 2312 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1973 | 16 | 0.38 | API 5LX | 52000 | SEAMLESS |  | US STEEL | 0 | UNDER WATER |  | K BRUCE LONG | 7134202603 | INTERNALLY | OTHER | NONE | OTHER | C02 | COATED | YES | 1973 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | LEAK CAUSED BY INTERNAL CORROSION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980208 | 1998-10-06 | 22435 | WEST TEXAS GAS INC | DEL RIO | VAL VERDE | TX |  |  |  | 300 | 1998-08-25 | 1 | NO |  |  | TX | Null | NO | OTHER |  | 0 | 0 | 50000 | 34925.7885 | 76086.6684 | Null | 0 | 0 |  | 19980825 | 205 | 400 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 0; NMDIA: 8; THK: 0.25; SMYS: 0; MANYR: 0; LOCLK: UNDER WATER; PNAME: RICHARD D HATCHETT; PHONE: 9156824349; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: Null; MARK: Null; MRKTP: 1; STAT: Null; CTEST: Null | UNDERGROUND CREEK CROSSING WAS WASHED OUT AND PIPELINE SEPARATION WAS CAUSEDBY THE FORCE OF THE WATER OR DEBRIS BEING TAKEN DOWNSTREAM.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980209 | 1998-10-07 | 6660 | GREAT LAKES GAS TRANSMISSION CO | CLOQUET | CARLTON | MN | 6636-- | 283.01 | 722+60 | 2135 | 1998-09-06 | 1 | NO |  |  |  | Null | NO | RUPTURE | 15 | 0 | 0 | 1414000 | 987701.2987 | 2151730.9833 | Null | 0 | 17 |  | 19980906 | 930 | 974 | BY TEST | 1467 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; MLKD: OTHER; MLKDO: WELD MATERIAL; PRTSY: PIPELINE; PRTYR: 1972; NMDIA: 36; THK: 0.38; SPEC: API 5LX; SMYS: 65000; SEAM: DSAW; MANU: SOCIETE VALLOUREC FRANCE; MANYR: 1972; LOCLK: UNDER GROUND; PNAME: ROBERT J CADORIN; PHONE: 3135964669; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | AS STATED ABOVE, THE RUPTURE OCCURRED DUE TO FAILURE IN THE LONG SEAM OF THEPIPE DETERMINED TO BE AT THE SITE OF A CRACK. GREAT LAKES CONTINUES TO HAVEITS CONSULTANTS INVESTIGATE THE FAILURED PIPE SEGMENTS UNTIL A DEFINITVE CAUSECAN BE DETERMINED. IT SHOULD BE NOTED THAT THE REPAIRED PIPE SEGMENT, AS WELLAS THE ENTIRE VALVE SECTION, WAS SUCCESSFULLY HYDROSTATICALLY PRESSURE TESTEDAND SUBSEQUENTLY PLACED INTO SERVICE ON SEPTEMBER 21, 1998.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980215 | 1998-10-19 | 19160 | TENNESSEE GAS PIPELINE CO | CAMERON |  | LA |  | 507K-801+10.7 | 507K-800 | 163 | 1998-09-17 |  | YES | WC | 137 | LA | YES | NO | LEAK |  | 0 | 0 | 105000 | 73344.1558 | 159782.0037 | Null | 0 | 0 |  | 19980917 | 895 | 1403 | BY TEST | 2165 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1972 | 16 | 0.38 | API 5LX | 52000 | SEAMLESS |  | US STEEL | 1972 | UNDER WATER |  | R BRUCE LONG | 7134202603 | INTERNALLY | OTHER | NONE | OTHER | CO2 | COATED | YES | 1972 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | LEAK CAUSED BY INTERNAL CORROSION
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980216 | 1998-10-19 | 19160 | TENNESSEE GAS PIPELINE CO | EAST CAMERON BLOCK 60 |  | LA |  | 507F-301+5.14 | 507F-300 | 1515 | 1998-09-20 |  | YES | EC | 60 |  | YES | NO | LEAK |  | 0 | 0 | 65000 | 45403.525 | 98912.669 | Null | 0 | 0 |  | 19980920 | 780 | 1247 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: VALVE; MLKD: OTHER; MLKDO: LOCKING LEVER; PRTSY: PIPELINE; PRTYR: 1993; NMDIA: 0; THK: 0; SMYS: 0; VALVE: ANSI CLASS 600; MANU: TOM WHEATLY; MANYR: 1993; LOCLK: UNDER WATER; PNAME: MY-LINH LAUD; PHONE: 7134202496; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: NO DATA; CTEST: Null; MED: NO DATA; TMPS: 0; LKPS: 0 | LEAK DEVELOPED IN LOCKING LEVER OF A SUBSEA CHECK VALVE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980221 | 1998-10-20 | 19160 | TENNESSEE GAS PIPELINE CO | SOUTH PASS |  | LA |  | 527A-701+10.77 | 527A-700 | 1100 | 1998-09-30 |  | YES | SP | 77 |  | Null | NO | LEAK |  | 0 | 0 | 3000000 | 2095547.3098 | 4565200.106 | Null | 0 | 0 |  | 19980930 | 750 | 1440 | BY TEST | 2161 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1981; NMDIA: 26; THK: 0.63; SPEC: API 5LX; SMYS: 60000; SEAM: ARC WELD; MANU: BETHLEHEM; MANYR: 1981; LOCLK: UNDER WATER; PNAME: MY-LINH LAUD; PHONE: 7134202496; PROT: Null; CAULK: OPERATOR ACTION; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | HURRICANE GEORGES CAUSED MUDSLIDE WHICH DAMAGED PIPE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980222 | 1998-10-27 | 22462 | WESTERN GAS INTERSTATE CO | SEC 33 -T4 -R16 | TEXAS | OK |  |  |  | 1700 | 1998-09-29 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 50000 | 34925.7885 | 76086.6684 | Null | 1 | 40 |  | 19980929 | 617 | 850 | BY TEST | 1530 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1995; NMDIA: 8; THK: 0.22; SMYS: 0; MANYR: 0; LOCLK: UNDER GROUND; PNAME: RICHARD D HATCHETT; PHONE: 9156824349; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19980925; MARK: YES; MRKTP: 0; STAT: YES; CTEST: Null | DIRT CONTRACTOR MOVED LOCATIONS WITHOUT GIVING OPERATOR NOTICE OF CHANGE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980223 | 1998-10-27 | 18516 | SOUTHERN NATURAL GAS CO |  |  | LA |  | 0.000 | LAT 29" 11'55" LONG. 88 | 905 | 1998-10-02 |  | YES | MAIN | 77 | LA | YES | NO | OTHER |  | 0 | 0 | 50000 | 34925.7885 | 76086.6684 | Null | 0 | 0 |  | 19981002 | 1000 | 1730 | BY TEST | 2163 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: MECHANICAL JOINT; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1989; NMDIA: 10.75; THK: 0.5; SPEC: API5LX; SMYS: 52000; SEAM: BIMS; MANU: US STEEL; MANYR: 1989; LOCLK: UNDER WATER; PNAME: MARC BELLIZZI; PHONE: 5046826200; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: Null; MARK: Null; MRKTP: 1; STAT: Null; CTEST: Null | SHEER JOINT/LOAD LIMITING CONNECTOR (INSTALLED ON PIPELINE IN 1989) FAILED DUETO MUDSLIDE LOADS DURING HURRICANE GEORGES.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980224 | 1998-10-27 | 18516 | SOUTHERN NATURAL GAS CO | PLAQUEMINES |  | LA |  | T17S, R16E, LAT N29" 34' | LON W 89"32'22" | 830 | 1998-10-06 | 1 | NO |  |  | LA | Null | NO | RUPTURE |  | 0 | 0 | 50000 | 34925.7885 | 76086.6684 | Null | 1 | 30 |  | 19981006 | 900 | 1060 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1958; NMDIA: 10.75; THK: 0.31; SPEC: API5L:X42; SMYS: 42000; SEAM: SEAMLESS; MANU: NATIONAL TUBE, PA; MANYR: 1958; LOCLK: UNDER GROUND; PNAME: MARK BELLIZZI; PHONE: 5046826200; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: 1; STAT: YES; CTEST: Null | A THIRD PARTY WORK BARGE BROKE FREE DUE TO HURRICANE GEORGES AND RAN AROUNDON STONE ISLAND IN BLACK BAY, LA. THE BARGE RESTED OVER SOUTHERN'S 10" BLACKBAY PIPELINE AND ITS WEIGHT ULTIMATELY CAUSED IT TO REST ON THE PIPELINERESULTING IN A RUPTURE AND SUBSEQUENT FIRE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980225 | 1998-10-14 | 31084 | DUKE ENERGY CORP |  |  | LA |  | 0.41 | 21+64 | 1130 | 1998-09-23 |  | YES | B5 | 53 | LA | YES | NO | LEAK |  | 0 | 0 | 100000 | 69851.577 | 152173.3369 | Null | 142 | 30 |  | 19980924 | 1015 | 1440 | BY TEST | 2160 | CORROSION | CORROSION | INTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1970; NMDIA: 10; THK: 0.37; SPEC: API 5L; SMYS: 35000; MANYR: 0; LOCLK: UNDER WATER; PNAME: J P WADE; PHONE: 7136275117; LOC: INTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: OTHER; COAT: COATED; PROT: YES; CPYR: 1970; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | EFFORTS TO LOCATE, ISOLATE, AND REPAIR THE LEAK WERE IMPACTED BY HURRICANEGEORGES.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19980239 | 1998-11-05 | 30826 | WILLIAMS FIELD SERVICES | HIGH ISLAND |  | TX |  | 6.68 | 352+64 |  | 1998-10-06 |  | YES | H. I. | 109 |  | YES | NO | LEAK |  | 0 | 0 | 200000 | 139703.154 | 304346.6737 | Null | 72 | 0 |  | 19981008 | 930 | 1440 | BY TEST | 2160 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1990 | 12.75 | 0.38 | API 5L | 42000 | SEAMLESS |  |  | 1990 | UNDER WATER |  | JAMES C MASON | 7132153022 | INTERNALLY | OTHER | UNKNOWN | OTHER | UNKNOWN | COATED | YES | 1990 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | INTERNAL CORROSION
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980240 | 1998-10-20 | 20230 | KOCH GATEWAY PIPELINE CO | ROSENBERG | FT BEND | TX |  | MP 128.48 | 6763+74.4 | 30 | 1998-09-03 | 1 | NO |  |  | TX | Null | NO | RUPTURE | 20 | 0 | 0 | 250000 | 174628.9425 | 380433.3422 | Null | 1 | 20 |  | 19980903 | 868 | 936 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | INTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: DRIP; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 0; NMDIA: 26; THK: 0; SMYS: 0; MANYR: 0; LOCLK: UNDER GROUND; PNAME: DALE MCBRIDE; PHONE: 4093652280; LOC: INTERNALLY; ADESC: NO DATA; CAUCR: NO DATA; COAT: COATED; PROT: YES; CPYR: 0; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | CORROSION CAUSED REDUCTION OF THE WALL THICKNESS TO THE POINT OF FAILURE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980242 | 1998-11-13 | 19160 | TENNESSEE GAS PIPELINE CO | ST LOUIS | HANCOCK | MS | 39520 | STATION 530 |  | 815 | 1998-10-12 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 0 | 0 | 0 | YES | 0 | 5 |  | 19981012 | 0 | 300 | BY TEST | 450 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: VALVE; MLKD: OTHER; MLKDO: FISHER VALVE; PRTSY: COMPRESSOR STATION; PRTYR: 1959; NMDIA: 0; THK: 0; SMYS: 0; VALVE: PISTON ACTIVATE; MANU: FISHER; MANYR: 1959; LOCLK: ABOVE GROUND; PNAME: DARON MOORE; PHONE: 7134204023; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: NO DATA; CTEST: Null; MED: NO DATA; TMPS: 0; LKPS: 0 | VALVE LEAKED RESULTING IN GAS ENTERING WORK AREA.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19980243 | 1998-11-16 | 11680 | LONE STAR PIPELINE CO (TRANSMISSION DIVISION) | FAIRFIELD | FREESTONE | TX |  | 266+29 |  | 300 | 1998-10-12 | 1 | NO |  |  |  | Null | NO | RUPTURE | 10 | 0 | 0 | 54986 | 38408.5881 | 83674.031 | Null | 1 | 45 |  | 19981012 | 720 | 800 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1969; NMDIA: 8.63; THK: 0.19; SPEC: API5LX42; SMYS: 42000; SEAM: EW; MANYR: 0; LOCLK: UNDER WATER; PNAME: STEVE ENGLISH; PHONE: 2146702700; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | 8" PIPELINE BLEW OUT (END TO END).
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980244 | 1998-11-16 | 12350 | MINNEGASCO INC | ST. MICHAEL | WRIGHT | MN | 55376 |  |  | 1215 | 1998-10-08 | 3 | NO |  |  | MN | Null | NO | LEAK |  | 0 | 0 | 60000 | 41910.9462 | 91304.0021 | Null | 4 | 0 |  | 19981008 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: FITTING; PRTFO: NORMAC TEE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1971; NMDIA: 1.25; THK: 0.14; SMYS: 0; MANYR: 0; LOCLK: UNDER GROUND; PNAME: EUGENE F SCHULTZ; PHONE: 6123214756; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19980930; MARK: YES; MRKTP: 3; STAT: YES; CTEST: Null | ROAD GRADER ON REPAVING PROJECT CUT GRADE DOWN TO LEVEL OF PIPE AND HIT TEE,PULLING PIPE OUT OF NORMAC FITTING.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19980248 | 1998-11-26 | 13750 | NORTHERN NATURAL GAS CO (ENRON) | TAMA | TAMA | IA |  |  |  | 730 | 1998-10-26 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 52000 | 36322.82 | 79130.1352 | Null | 2 | 0 |  | 19981026 | 910 | 960 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1966; NMDIA: 0; THK: 0.16; SPEC: API 5L; SMYS: 35000; SEAM: ERW; MANU: INTERLAKE; MANYR: 0; LOCLK: UNDER GROUND; PNAME: WILL BURKS; PHONE: 7136467966; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; MRKTP: 0; STAT: YES; CTEST: Null | A 3RD PARTY CONTRACTOR SEVERED THE LINE WHILE EXCAVATING IN A FARMERS FIELD,NNG WAS NOT NOTIFIED OF THE EXCAVATION ACTIVITES.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19980249 | 1998-11-27 | 19270 | WILLIAMS GAS PIPELINE - TEXAS GAS | JACKSON | MADISON | TN |  | #1 MP 33+2612 |  | 1519 | 1998-10-29 | 1 | NO |  |  |  | Null | NO | RUPTURE |  | 0 | 0 | 96838 | 67642.8701 | 147361.616 | Null | 1 | 0 | 461866 | 19981029 | 793 | 1279 | BY TEST | 1599 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1978; NMDIA: 8.625; THK: 0.219; SPEC: GRADE B; SMYS: 1777; SEAM: ERW; MANU: JONES & LAUGHLIN; MANYR: 1978; LOCLK: UNDER GROUND; PNAME: SHELIA L DUNBAR; PHONE: 5026886962; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PERMANENT PIPELINE MARKER; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | ON THURSDAY, OCTOBER 29, 1998, AT 3:19 PM, CENTRAL STANDARD TIME, WILLIAMS GAS PIPELINE, TEXAS GAS SUSTAINED AN IN-SERVICE FAILURE ON ITS RIPLEY JACKSON 8" NO. 1 LINE IN MADISON COUNTY, TENNESSEE. THE LOCATION OF THE INCIDENT WAS APPROXIMATELY 2.5 MILES WEST OF THE CITY OF JACKSON, TENNESSEE. THE FAILURE OCCURRED IN THE CENTER OF CUB CREEK AT LINE MILEPOST 33+2612, WHICH IS 5.22 MILES FROM THE TERMINUS OF THE 8"LINE. SERVICE WAS INTERRUPTED TO TWO OF WGP-TEXAS GASS DELIVERY POINTS. FROM CONVERSATIONS WITH THE LOCAL DISTRIBUTION COMPANY, WE UNDERSTAND 628 LDC CUSTOMERS, INCLUDING 6 OR 8 INDUSTRIAL USERS, LOST GAS SERVICE. FULL GAS SERVICE WAS RESTORED TO THE WGP-TEXAS GAS DELIVERY POINTS BY 7:32AM CST, ON OCTOBER 30, 1998. AN ONGOING METALLURICAL INVESTIGATION HAS CONCLUDED THE FOLLOWING. THE FAILURE INITIATED IN A SEGMENT OF PIPE CONTAINING A DENT AND GOUGES CREATED BY OUTSIDE FORCES. THE DENT AND GOUGE DAMAGE, PRESUMABLY CAUSED BY EXCAVATING EQUIPMENT, EXTENDED 111" IN LENGTH ALONG THE LONGITUDINAL AXIS OF THE 8" PIPE. THE FAILURE RESULTED IN A 25" LENGTH OF PIPE BEING SEPARATED FROM THE CONTIGUOUS PIPELINE SYSTEM. THE LINE PIPE WAS CATHODICALLY PROTECTED. MINERAL DEPOSITS STRONGLY SUGGEST A LONG-TERM, UNDERGROUND EXPOSURE AFTER THE OUTSIDE-FORCE DAMAGE OCCURRED. THE METALLURGICAL EVALUATION HAS RULED OUT ANY INVOLVEMENT OF THE LONGITUDINAL OR GIRTH WELD SEAMS. PROPERTY DAMAGE WAS CONFINED TO TEXAS GAS FACILITIES. THE INCIDENT OCCURRED IN A CREEK BED LOCATED IN AN AGRICULTURAL AREA BEING UTLIZED AS PASTURE GROUND. PERMANENT REPAIRS TO THE PIPELINE, INCLUDING CLEANUP AND BANK RESTORATION WERE COMPLETED ON NOVEMBER 6, 1998. THE COMPANYS ONE-CALL RECORDS DO NOT INDICATE NOTIFICATION OF PLANNED EXCAVATIONS IN THIS AREA. LINE MARKERS ARE MAINTAINED AT THE CREEK CROSSING. THESE MARKERS CONTAIN WARNING LANGUAGE, THE COMPANY NAME, AND 24-HOUR TELEPHONE INFORMATION.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19980255 | 1998-12-16 | 2325 | CHEVRON USA INC |  |  | LA |  |  |  | 1200 | 1998-09-29 |  | YES | WD | 79 |  | YES | NO | OTHER |  | 0 | 0 | 600000 | 419109.462 | 913040.0212 | Null | 24 | 0 |  | 19980930 | 700 | 1182 | BY TEST | 2160 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | GATHERING SYSTEM | MECHANICAL JOINT |  | STEEL |  | PIPELINE |  | 1998 | 20 | 0.5 | X-52 | 52000 | ERW |  |  | 0 | UNDER WATER |  | CARLOS M GONZALEZ | 5045927178 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | NO DATA | MECHANICAL 'SMART FLANGE' LOST INTEGRITY/UNKNOWN | YES | 19930401 | WATER |  | 1 | 2000 | UNDER STATIC CONDITIONS AFTER HURRICANE GEORGES, MECHANICAL FLANGE CONNECTIONSEPARATED FROM PIPELINE RESULTING IN NATURAL GAS RELEASE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990005 | 1999-01-07 | 19160 | TENNESSEE GAS PIPELINE CO | WEST CAMERON BLOCK 137 |  | LA |  | 507K-801+10.89 | 507K-800 |  | 1998-11-30 |  | YES | WC | 137 | LA | YES | NO | LEAK |  | 0 | 0 | 82000 | 57278.2931 | 124782.1362 | Null | 14 | 0 |  | 19981130 | 1200 | 1403 | BY TEST | 1544 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1972 | 16 | 0.38 | API 5LX | 52000 | SEAMLESS |  | US STEEL | 1971 | UNDER WATER |  | BRUCE LONG | 7134202603 | INTERNALLY | LOCALIZED PITTING |  | NO DATA |  | NO DATA | YES | 1972 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | INTERNAL CORROSION LEAK
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990006 | 1999-01-07 | 4280 | EL PASO NATURAL GAS CO | TOP OF THE WORLD | MCKINLEY | NM |  | MP 368 | 2127+13.3 | 558 | 1998-12-13 | 2 | NO |  |  | NM | Null | NO | RUPTURE | 1 | 0 | 0 | 150000 | 104777.3655 | 228260.0053 | YES | 4 | 0 |  | 19981213 | 700 | 836 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: VALVE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1983; NMDIA: 36; THK: 0.56; SPEC: API 5L; SMYS: 60000; VALVE: GATE; MANU: M & J; MANYR: 1951; LOCLK: UNDER GROUND; PNAME: GILBERT ARAGON; PHONE: 9154962624; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | A RATE CHANGE WAS NOTICED AT BLUEWATER COMPRESSOR STATION AND THEN A FIRE WASDISCOVERED ON THE PIPELINE RIGHT-OF-WAY AT THE SAME TIME. A RUPTURE OCCURREDON THE TIE-IN TO A MAINLINE VALVE ON LINE 1300. THE FIRE BURNED FORAPPROXIMATELY 4 HOURS CAUSING DAMAGE TO POWER LINES, A CELL PHONE TOWER, AND ASTORAGE SHED. SERVICE WAS CURTAILED TO APPROXIMATELY 75 HOMES IN THE TOP OFTHE WORLD SUBDIVISION.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990007 | 1999-01-05 | 19160 | TENNESSEE GAS PIPELINE CO |  |  | LA |  | 527A-301+6.43 | 339+50 | 330 | 1998-12-06 | 1 | NO |  |  | LA | Null | Null | RUPTURE | 80 | 0 | 0 | 750000 | 523886.8275 | 1141300.0265 | Null | 3 | 0 |  | 19981206 | 1150 | 1200 | BY TEST | 1946 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1979; NMDIA: 30; THK: 0.5; SPEC: API 5LX; SMYS: 60000; SEAM: DSAW; VALVE: DIAPHRAGM ACTUATED; MANU: US STEEL; MANYR: 1979; LOCLK: UNDER WATER; PNAME: DARON MOORE; PHONE: 7134204023; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | UNKNOWN DUE TO DAMAGED PIPE BEING UNRECOVERABLE FROM SITE DURING RUPTUREINVESTIGATION.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19990008 | 1998-12-31 | 31286 | ONEOK GAS TRANSPORTATION, LLC |  | MCCLAIN | OK | 73080 |  |  | 1340 | 1998-12-02 | 1 | NO |  |  | OK | Null | NO | OTHER |  | 0 | 1 | 0 | 0 | 0 | Null | 0 | 1 |  | 19981215 | 0 | 843 | BY TEST | 1402 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: NO DATA; MLKD: OTHER; MLKDO: ENDURO PIG; PRTSY: OTHER; PRTSO: PIG RECEIVER; PRTYR: 1975; NMDIA: 20; THK: 0.38; SPEC: X-52; SMYS: 52000; SEAM: DSAW; VALVE: ROCKWELL A; MANU: ROCKWELL; MANYR: 1975; LOCLK: ABOVE GROUND; PNAME: GREG PHILLIPS; PHONE: 9185887550; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | AT APPROXIMATELY 1:40PM CST ON DECEMBER 2, 1998, AN EMPLOYEE OF ONEOK GASTRANSPORTATION, LLC. (OGT) WAS INJURED BY A 20" PIPELINE CLEANING PIG THATRAPIDLY EXITED A 20" RECEIVER BARREL ON PIPELINE A-1300, LOCATED NORTWEST OFPURCELL, OKLAHOMA. PLEASE NOTE ATTACHEMENT "A" DESIGNATING ITEM NUMBERSREFERENCED BELOW, AND ATTACHMENT "B" WHICH IS AN ISOMETRIC ENGINEERING DRAWINGOF THE RECEIVER. THREE OGT EMPLOYEES, BOBO RENEGAR, LINDSEY SOUTHWARD, ANDJOHN FRYAR, WERE PIGGING A SECTION OF A-1300 20" FROM MAYSVILLE JUNCTION TOPURCELL JUNCTION. THEY ARRIVED AT PURCELL JUNCTION AND PULLED THE 20" FROMCUP PIG, AN ENDURO ADV-3CC-BL (36" O.A.L.), INTO THE RECEIVER, TRIPPING THEPIG SIGNAL (3) AT ABOUT 1:20PM CST. THE A-1300 SIDE VALVE (1) WAS OPENED, ANDTHE 20"RECEIVER VALVE (2) WAS CLOSED. THE 8" KICKER GAS VALVE (6) WAS ALSOCLOSED. BLOWOFF VALVE (4) WAS OPEN ONE-HALF WAY, AND BLOWOFF VALVE (5) WASOPENED COMPLETELY. THE RECEIVER CLOSURE (7) WAS OPENED AND MOVED TO ONESIDE. AFTER FIVE MINUTES LINDSAY SOUTHWARD LOOKED INTO THE RECEIVER BARRELFROM A DISTANCE OF APPROXIMATELY 12 FEET DIRECTLY AWAY AND 6 FEET TO THE SIDEOF THE RECEIVER CLOSURE. HE NOTED THAT THE PIG WAS VISIBLE IN THE TRAP. WEESTIMATE THE DISTANCE FROM THE RECEIVER CLOSURE THREADS TO THE PIG NOSE TO BE3-4 FEET. BOB RENEGAR LOOKED INTO THE RECEIVER BARREL FROM THE IMMEDIATE EDGEOF THE CLOSURE OPENING, AND PUT HIS HEAD DOWN TO INSPECT THE AMOUNT OF SLUDGE,ETC., THAT THE PIG HAD MOVED. BOB MADE A COMMENT ON THE AMOUNT OF FLUIDS THATHAD BEEN MOVED. BOB MADE A COMMENT ON THE AMOUNT OF FLUIDS THAT HAD BEENMOVED, AND AT THAT TIME THE PIF SHOT OUT OF THE END OF THE RECEIVER HITTINGTHE GROUND AT APPROXIMATELY 23 FEET AND ROLLING TO A STOP AT 57 FEET FROM THERECEIVER. LINDSEY SOUTHWARD DESCRIBED THE NOISE THAT OCCURRED AS A DEEP CORKPOPPING SOUND. BOB RENEGAR FELL ON HIS BACK, HIT ABOVE THE RIGHT EYE BY THEPIG AND BLEEDING SEVERELY. NEITHER LINDSEY SOUTHWARD OR JOHN FRYAR WERESTANDING IN A POSITION TO BE STRUCK BY THE PIG, AND WERE INJURED. LINDSEYSOUTHWARD AND JOHN FRYAR PROVIDED ASSISTANCE TO BOB RENEGAR UNTIL MEDICALPERSONNEL ARRIVED, AND TRAVELED TO THE HOSPITAL WITH HIM, WHERE HE WASADMITTED FOR TREATMENT OF SEVERE HEAD INJURIES WHICH ULTIMATELY REQUIREDCORRECTIVE SURGERY. SCOTT HARDY, AN EMPLOYEE OF ONEOK, INC. ARRIVED AT THESITE TO SECURE THE SITE BY CLOSING THE RECEIVER CLOSURE (7) AND CLOSINGBLOWOFF (4) AND (5). FOLLOWING THE ACCIDENT, OGT HAS PERFORMED ANINVESTIGATION TO DETERMINE THE CAUSE OF THE ACCIDENT. INPUT HAS BEEN SOUGHTFROM THE OKLAHOMA CORPORATION COMMISSION'S PIPELINE SAFETY STAFF, AS SEVERALOF THEIR INSPECTORS HAVE SIGNIFICANT PIPELINE OPERATIONS EXPERIENCE. ALSO,REPRESENTATIVES FROM NORSTROM VALVES, INC AND MYLON C. JACOBS SUPPLY HAVEINSPECTED THE 20" RECEIVER VALVE (2). THE INITIAL REPORT FROM NORSTROMINDICATES THAT THE RECEIVER VALVE (2) DOES HAVE MINIMAL LEAKAGE, BUT ISOPERATING PROPERLY AND EFFECTIVELY CONTROLS GAS FLOW FROM THE PURPOSES OFPIGGING OUR PIPELINES. FURTHER, THE BLOWOFF VALVE (4) WAS STILL COMPLETELYOPEN AND WOULD HAVE VENTED ANY GAS THAT HAD LEAKED PAST THE RECEIVER VALVE (2)IS OPERATING PROPERLY. DESPITE OUR EFFORTS TO DETERMINE THE CAUSE OF THEACCIDENT, WE HAVE NOT FOUND THE ANSWER.
2021-02-26 10:36 | NO | NO |  | 19990009 | 1998-12-29 | 30712 | CENTRAL OKLAHOMA OIL & GAS CO. | STUART | HUGHES | OK |  |  |  | 1330 | 1998-12-10 | 1 | NO |  |  | OK | Null | NO | OTHER |  | 0 | 0 | 20000 | 13970.3154 | 30434.6674 | YES | 26 | 30 |  | 19981211 | 300 | 15000 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: NO DATA; PRTFL: OTHER; PRTFO: STORAGE WELL; MLKD: NO DATA; PRTSY: OTHER; PRTSO: STORAGE WELL; PRTYR: 0; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: JAY C JIMERSON; PHONE: 4052350993; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | ON DECEMBER 10, 1998, CENTRAL OKLAHOMA OIL AND GAS CORP. (OPERATOR) WAS IN THEPROCESS OF REWORKING ONE OF ITS EXISTING UNDERGROUND NATURAL GAS STORAGE WELLSLOCATED IN THE STUART NATURAL GAS STORAGE FACILITY IN HUGHES COUNTY,OKLAHOMA. AT APPROXIMATELY 1:30 PM, WHILE THE OPERATOR WAS PULLING ITS 5 1/2INCH PRODUCTION STRING OUT OF THE WELL. OPERATOR EXPERIENCED A GAS "KICK" INTHE WELL. IN ORDER TO MAINTAIN WELL CONTROL, OPERATOR IMMEDIATELY CLOSED THEPIPE RAM (HYDRILL) BLOWOUT PREVENTER AROUND THE JOINT OF PIPE WAS BEING PULLEDFROM THE WELL. IMMEDIATELY AFTER THE PIPE RAM BLOWOUT PREVENTER WAS CLOSED,OPERATOR INSTALLED A SWEDGE (CAP) ON THE TOP OF THE EXPOSED JOINT OF PIPEEXTENDING THROUGH THE RIG FLOOR. HOWEVER, SOME THE THREADS AT THE TOP OF THEJOINT OF PIPE WERE CRIMPED, AND THUS THE SWEDGE COULD NOT BE COMPLETELYSCREWED DOWN ONTO THE PIPE. AS A RESULT, THE SWEDGE DID NOT HOLD; AND THUS ITWAS BLOWN OFF THE TOP OF THE PIPE AS A RESULT OF THE GAS PRESSURE IN THEPIPE. OPERATOR THEN CLOSED THE BLIND RAM BLOWOUT PREVENTER. HOWEVER, BECAUSEOPERATOR WAS REMOVING A BLAST JOINT AT THE TIME OF THE GAS "KICK", WHICH ISTHICKER THAN THE NORMAL PRODUCTION LINER THAT WAS BEING REMOVED, THE BLINDRAMS DID NOT SHEER OFF THE PIPE AND SEAL THE WELL. AS A RESULT, THE WELLFLOWED INTO THE ATMOSPHERE UNTIL THE WELL WAS BROUGHT BACK INTO CONTROL. APRESSURE CONTROL COMPANY WAS CONTACTED TO ASSIST OPERATOR IN BRINGING THE WELLBACK INTO CONTROL. BECAUSE IT WAS NEARLY DARK BY THE TIME THE PRESSURECONTROL COMPANY ARRIVED, A DECISION WAS MADE TO WAIT UNTIL DAYBREAK THE NEXTMORNING TO RIG UP EQUIPMENT TO BRING THE WELL BACK INTO CONTROL. THE WELL WASBROUGHT BACK INTO CONTROL BY 4PM THE FOLLOWING DAY. THERE WERE NO FIRES, NOPERSONAL INJURIES AND NO PROPERTY DAMAGE OTHER THAN THE LOSS OF AN ESTIMATED7-10 MMCF OF GAS. AS A SAFETY PRECAUTION, DURING THE ENTIRE INCIDENT, ASAFETY PERIMETER OF APPROXIMATELY ONE (1) MILE WAS ESTABLISHED AROUND THEWELL. OTHER THAN NECESSARY PERSONNEL, NO ONE WAS PERMITTED WITHIN AREA.MOREOVER, WITHIN AN AREA APPROXIMATELY THREE (3) MILES DOWNWIND, APPROXIMATELYTHRITY-FOUR (34) PERSONS WERE EVACUATED UNTIL THE WELL WAS BROUGHT BACK INTOCONTROL. DURING THE ENTIRE INCIDENT, DETECTION EQUIPMENT WAS USED TO MONITORTHE AREA AROUND THE WELLBORE TO ENSURE THAT THE GAS WAS DISSIPATING AND NOTSETTLING IN LOW AREAS. LOCAL SHERIFF AND POLICE DEPARTMENTS ASSISTED INPROTECTING THE AREA, AND FIRE EQUIPMENT WAS ALSO AVAILABLE. LOCAL AND AREAOFFICALS PROVIDED PROMPT ASSISTANCE AND SUPPORT DURING THIS TIME. ALTHOUGHTHE FOREGOING INCIDENT DID NOT OCCUR ON OPERATOR'S PIPELINE, THE FOREGOINGWELL IS A PART OF OPERATOR'S TOTAL STORAGE SYSTEM. THEREFORE, OPERATOR ISSUBMITTING THIS INCIDENT REPORT IN THE EVENT IT IS REQUIRED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990010 | 1999-01-13 | 18484 | SOUTHERN CALIFORNIA GAS CO | BURRELL | KING | CA |  |  |  | 213 | 1998-12-10 | 1 | NO |  |  |  | Null | NO | RUPTURE | 1 | 0 | 0 | 350000 | 244480.5195 | 532606.679 | Null | 2 | 52 |  | 19981210 | 350 | 400 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1945; NMDIA: 8; THK: 0.25; SPEC: GRADE A; SMYS: 23; MANYR: 0; LOCLK: NO DATA; PNAME: JEFF KOSKIE; PHONE: 2132443283; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19981203; MARK: YES; MRKTP: 0; STAT: YES; CTEST: Null | PIPELINE WAS MISLOCATED. SPECIAL EQUIPMENT REQUIRED TO MOVE BULL DOZER OFF OFDAMAGED PIPELINE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990011 | 1998-12-22 | 15329 | PEOPLES GAS LIGHT & COKE CO | FISHER | CHAMPAIGN | IL | 61843 |  |  | 515 | 1998-11-14 | 1 | NO |  |  | IL | Null | NO | RUPTURE | 55 | 0 | 0 | 345000 | 240987.9406 | 524998.0122 | Null | 0 | 55 |  | 19981114 | 1750 | 2000 | BY TEST | 2400 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | WELD | LONGITUDINAL | STEEL |  | PIPELINE |  | 1972 | 12 | 0.38 | 5LX60 | 60000 | ERW |  | US STEEL | 1972 | UNDER GROUND |  | T KOLLER | 2178977100 | INTERNALLY | LOCALIZED PITTING |  | OTHER | PITTING CORROSION | COATED | YES | 1972 | NO DATA |  | Null |  | Null |  | Null |  |  | Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990012 | 1999-01-12 | 19730 | TRUNKLINE GAS CO |  | WHARTON | TX |  | VALVE SECTION 23 | 259+92 | 1710 | 1998-09-23 | 1 | NO |  |  | TX | Null | NO | LEAK |  | 0 | 0 | 400000 | 279406.308 | 608693.3475 | Null | 4 | 15 |  |  | 755 | 875 | BY TEST | 1301 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE | LONGITUDINAL | STEEL |  | PIPELINE |  | 1951 | 20 | 0.25 | API-5L | 52000 | DSAW |  | KAISER | 1951 | UNDER WATER |  | DWAYNE TESCHENDORF | 7136275573 | INTERNALLY | LOCALIZED PITTING |  | OTHER | UNKNOWN | COATED | YES | 1951 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | LEAK OCCURRED DUE TO LOSS OF WALL THICKNESS RESULTING FROM INTERNAL CORROSION.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990013 | 1999-01-12 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA | ESSEX | KANKAKEE | IL | 60935 | 12 | 543+45 | 2350 | 1998-12-07 | 1 | NO |  |  | IL | Null | NO | RUPTURE | 33 | 0 | 0 | 396100 | 276682.0965 | 602758.5873 | Null | 1 | 30 |  | 19981208 | 620 | 858 | BY TEST | 1201 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | OTHER | C DRIP | STEEL |  | PIPELINE |  | 1983 | 24 | 0.38 | 5LX | 52000 | DSAW |  | CONTRACTOR | 1983 | UNDER GROUND |  | STEPHEN C COFFMAN | 3039147808 | INTERNALLY | GENERAL CORROSION |  | OTHER | BACTERIAL | COATED | YES | 1983 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | FAILURE OF THE 24' DIAMETER CLASS "C" DRIP RESULTED IN A FIRE. INTENSE HEATFROM THE FIRE EVENTUALLY CAUSE THE 36" DIAMETER CARRIER PIPE TO RUPTURE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990014 | 1998-12-24 | 10030 | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | RIVERTON | FREMONT | WY | 82501 | 4 | 199+23 | 805 | 1998-11-23 | 1 | NO |  |  |  | Null | YES | LEAK |  | 0 | 0 | 100000 | 69851.577 | 152173.3369 | Null | 0 | 25 |  | 19981123 | 575 | 673 | BY TEST | 740 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | GIRTH | STEEL |  | PIPELINE |  | 1958 | 16 | 0.25 | GRADE B | 35000 | ERW |  |  | 0 | UNDER GROUND |  | STEPHEN C COFFMAN | 3039147808 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | CONSTRUCTION | WELD FAILURE | YES | 19980719 | GAS |  | 8 | 766 | ON NOVEMBER 23, 1998 AT 1:12PM, AN AGENT OF KN ENERGY, MR. DOUG THACKER,REPORTED TO YOU A GAS LEAK ON THE NORTHERN GAS COMPANY (NGC) 16' INTRASTATEPIPELINE. AT 11:30AM ON NOVEMBER 23,1998 THE GAS LEAK WAS CONFIRMED ON THENGC 16' INTRASTATE PIPELINE IN FREMONT COUNTY, SOUTHEAST OF THE TOWN OFRIVERTON. THE GAS LEAK WAS REPAIRED WITH REPLACEMENT PIPE AND PLACED BACK INSERVICE ON NOVEMBER 25, 1998 AT 8AM. EVEN THOUGH THIS INCIDENT DID NOTREQUIRE FEDERAL REPORTING, IT WAS ALSO TELEPHONICALLY REPORTED TO THE NATIONALRESPONSE CENTER BY MR. DOUG THACKER, AS PER YOR RECOMMENDATION.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990015 | 1999-01-11 | 2714 | CNG TRANSMISSION CORP | PLUM CREEK TOWNSHIP | ARMSTRONG | PA | 15736 |  | 276+26 | 2240 | 1998-12-17 | 1 | NO |  |  | PA | Null | NO | RUPTURE | 29 | 0 | 0 | 500000 | 349257.885 | 760866.6843 | Null | 1 | 15 |  | 19981218 | 917 | 1000 | BY TEST | 1349 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE | C DRIP | STEEL |  | PIPELINE |  | 1968 | 26 | 0.31 | API 5L | 60000 | DSAW |  | REPUBLIC STEEL CORP | 1968 | UNDER GROUND |  | MARTIN C SCHWOEBLE | 3046238408 | EXTERNALLY | NO DATA |  | NO DATA |  | COATED | YES | 1969 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | THIS LETTER PRESENTS MY PRELIMINARY FINDINGS REGARDING THE CAUSE OF THERUPTURED OF CNG'S 26-INCH PIPELINE WHICH OCCURRED ON DECEMBER 17, 1998 NEARELDERTON, PENNSYLVANIA. THE RUPTURE WAS CAUSED BY EXTERNAL CORROSION WHICHHAD TAKEN PLACE ON THE BOTTOM OF THE PIPELINE. THE MOST SEVERELY CORRODEDAREA, WHICH CORRESPONDS TO ORIGIN OF THE RUPTURE, WAS ONLY ABOUT 13 INCHES INLENGTH. OTHER THINNED AREAS, NOT AS SEVERELY AFFECTED, WERE FOUND OVER ABOUTA 6-FOOT LONG REGION ALONG THE BOTTOM OF THE PIPE. MEASUREMENTS OF THEREMAINING WALL THICKNESS WITHIN THE ORIGIN REGION PRODUCED VALVES IN SOMELOCATIONS AS SMALL AS 0.087 RO 0.099 INCH. MY RSTRENG CALCULATION BASED ONTHE MEASUREMENTS OVER THE 13-INCH ORIGIN REGION INDICATED A BURST PRESSURE OF876 PSIG. THIS AGREES REASONABLY WELL WITH THE PRESSURE LEVEL AT THE TIME OFTHE INCIDENT 917 PSIG (STATED BY CNG PERSONNEL AT THE RUPTURE SITE). A ROUGH,PRELIMINARY MAP OF REMAINING WALL THICKNESS CONTOURS IS ATTACHED AS IS ADIAGRAM OF THE OVERALL RUPTURE. ABOUT 33.7 FEET OF PIPE INVOLVING TWO JOINTSWERE AFFECTED.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19990039 | 1999-01-20 | 2436 | AQUILA SOUTHWEST (EX. CLAJON GAS CO) | DIMMIT |  | TX |  | BRAY BLOCK VALVE |  | 1030 | 1998-12-16 | 1 | NO |  |  | TX | Null | NO | OTHER |  | 0 | 2 | 15000 | 10477.7365 | 22826.0005 | Null | 0 | 10 |  | 19981216 | 890 | 1200 | BY TEST | 1273 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | FITTING | PIG TRAP DOOR | STEEL |  | OTHER | PIG STATION | 1978 | 0 | 0 |  | 0 |  | PIG TRAP DOOR | PECO | 1970 | ABOVE GROUND |  | CHARLES HAYS | 2104761100 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | PIG TRAP DOOR OR ENCLOSURE | Null |  | WATER |  | 0 | 0
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19990040 | 1999-01-28 | 19730 | TRUNKLINE GAS CO | BEAUREGARD |  | LA |  | VALVE SETTING 48 | 40 & 49 | 945 | 1999-01-17 | 1 | NO |  |  | LA | Null | NO | LEAK |  | 0 | 0 | 50000 | 34482.533 | 75121.0258 | Null | 3 | 50 |  | 19990120 | 711 | 900 | BY TEST | 1248 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; PRTFO: PIG TRAP DOOR; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1951; NMDIA: 26; THK: 0.31; SPEC: API-5L; SMYS: 52000; SEAM: DSAW; MANU: KAISER; MANYR: 1951; LOCLK: UNDER GROUND; PNAME: DWAYEN TESCHENDORF; PHONE: 7136275573; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990041 | 1999-01-29 | 13845 | NORTHWEST PIPELINE CORP |  | UMATILLA | OR |  | 1017.05 | 324+25.8 | 925 | 1999-01-02 | 1 | NO |  |  | OR | Null | NO | RUPTURE |  | 0 | 0 | 500000 | 344825.3304 | 751210.2578 | Null | 1 | 10 |  | 19990102 | 735 | 850 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | BODY OF PIPE | PIG TRAP DOOR | STEEL |  | PIPELINE |  | 1956 | 22 | 0.25 | API5LX52 | 1181 | DSA |  | KAISER | 1956 | UNDER GROUND |  | EDWIN COMPTON SR | 8015846776 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL |  | YES | 19560710 | WATER |  | 1 | 929
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19990042 | 1999-02-05 | 15014 | PG&E GAS TRANSMISSION-NORTHWEST | MADRAS | JEFFERSON | OR | 97741 | 425.1 | 11-2,+200 | 650 | 1998-12-21 | 1 | NO |  |  | OR | Null | YES | LEAK |  | 0 | 0 | 57000 | 39815.3989 | 86738.802 | Null | 0 | 0 |  | 19981227 | 843 | 1000 | BY TEST | 1500 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: FILLET; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1993; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: KEVIN COWAN; PHONE: 5038334711; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990050 | 1999-02-18 | 2620 | COLUMBIA GULF TRANSMISSION CO | WEST CAMERON BLOCK 630 | OFFSHORE LA | LA |  | WC 630 | X=1367988.65 Y=2311850.28 | 330 | 1999-01-17 |  | YES | WC | 630 | LA | Null | NO | LEAK | 0 | 0 | 0 | 350000 | 241377.7313 | 525847.1804 | Null | 0 | 0 |  | 19990117 | 910 | 1440 | NO DATA | 0 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1978 | 20 | 0.05 | 5LX | 60000 | DSAW |  |  | 1978 | UNDER WATER |  | HENRY H WANG | 7132674371 | INTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1979 | NO DATA |  | Null |  | Null | 1 | Null |  |  | Null | [5 empty] | SUSPECT BACTERIA CORROSION. INSTALLED TWO REPAIR CLAMPS AT X=231850.28 ANDX=1367347.55 Y=235176.30.
2021-02-26 10:36 | NO | NO |  | 19990051 | 1999-02-16 | 2304 | CHILDERSBURG GAS BOARD | LINCOLN | TALLADEGA | AL | 35096 |  |  | 730 | 1999-02-02 |  | NO |  |  | AL | Null | NO | OTHER |  | 0 | 0 | 0 | 0 | 0 | YES | 0 | 30 |  | 19990203 | 0 | 0 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: NO DATA; PRTFL: NO DATA; MLKD: NO DATA; PRTSY: OTHER; PRTSO: INSIDE CUTOMER BUILDING; PRTYR: 1999; NMDIA: 0; THK: 0; SMYS: 0; MANYR: 0; LOCLK: OTHER; LOCLO: INSIDE CUSTOMER BUILDING; PNAME: MICHEAL S MADDOX; PHONE: 2563786064; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | AT APPROXIMATELY 7:45 AM, THE BOARD AFTER HOURS OPERATOR WAS NOTIFIED BY THECHILDERSBURG POLICE THAT LINCOLN POLICE HAD CALLED REPORTING AN EXPLOSION ATTHE HOLIDAY INN EXPRESS IN LINCOLN. AT APPROXIMATELY 7:50 AM, BOARDEMPLOYEES, JERRY CARPENTER, GENERAL FOREMAN, AND TONY KELLEY, SERVICETECHNICIAN, DISPATCHED EN ROUTE TO THE SCENE. UPON ARRIVING, JERRY CARPENTERWAS TOLD THAT ONE PERSON HAD BEEN TRANSPORTED TO TALLADEGA HOSPITAL. BOARDEMPLOYEES, MICHEAL MADDOX, GENERAL MANAGER, AND DAVID MARTIN, ASSISTANT TO THEFOREMAN, LEFT AT APPROXIMATELY 8:05 AM. UPON ARRIVING AT THE SCENE, JERRYCARPENTER CHECKED THE GAS METER FOUND ABSOLUTELY NO GAS FLOWING THROUGH THEMETER AND NO EVIDENCE OF FIRE OR GAS LEAK. TURNED THE GAS OFF AND LOCKED OFFAT METER AT 8:13 AM BY JERRY CARPENTER. AT 8:35 AM MICHAEL MADDOX CALLED THEOFFICE AND TOLD EMPLOYEES TO NOTIFY THE PUBLIC SERVICE COMMISSION OFFICE OFPIPELINE SAFETY THAT THERE HAD BEEN SOME TYPE OF EXPLOSION AT THE HOLIDAY INNAT LINCOLN. AT 8:50 AM THE OFFICE WAS CONTACTED BY HAROLD DUNSON OF THEPUBLIC SERVICE COMMISSION AND TOLD THAT HE WAS EN ROUTE TO THE SCENE. ATAPPROXIMATELY 8:40 AM MICHAEL MADDOX AND JERRY CARPENTER FROM THE BOARDACCOMPANIED OFFICER DENNIS ALLBRITTON OF THE CITY OF LINCOLN POLICE DEPARTMENTTO TALLADEGA HOSPITAL TO GET A STATEMENT AND WITNESS THE CONDITIONOF THE INJURED PERSON. UPON ARRIVAL AT THE HOSPITAL THE INJURED PERSON WASINTERVIEWED BY OFFICER ALLBRITTON. HIS NAME IS TIMOTHY JAMES OF DAMRONPLUMBING INC. OF CHATTANOOGA, TENNESSEE. MR. JAMES TOLD THE INVESTIGATORTHAT HE WAS PREPARING TO LIGHT THE WATER HEATERS IN THE UITLITY ROOM OF THEHOTEL. HE STATED THAT HE WAS TOLD BY MR. GAYA TO TURN THE GAS ON AT THEMETER AND BEGIN POURING THE PLUMBING LINES. HE STATED THAT HE HAD TAKEN THEPIPING APART IN THE ROOM AND PURGED THE LINES FOR 2 TO 3 MINUTES. HE THENSAID THAT HE TURNED THE VALVE IN THE BUILDING OFF. HE THEN ATTEMPTED TO PLUGINTO AN ELECTRICAL OUTLET THE ELECTIC IGNITOR FOR THE WATER HEATERS. THEEXPLOSION OCCURRED AT THAT TIME. AB EXACT COPY OF THE STATEMENT CAN BEOBTAINED FROM THE POLICE DEPARTMENT OF THE CITY OF LINCOLN, PHONE NUMBER(205)763-7777. ACCORDING TO THE DOCTOR, MR. JAMES HAD RECEIVED SUPERFICIALBURNS ON HIS NECK, HANDS, AND FACE. HE IS EXPECTED TO RECOVER FULLY WITHOUTCOMPLICATION OR SCARS. MR. JAMES WAS RELEASED AROUND 11 AM. HE RETURNED TOTHE JOB SITE AND GAVE FURTHER STATEMENTS TO PUBLIC SERVICE COMMISSIONREPRESENTATIVE, HAROLD DUNSON, AND THE STATE FIRE MARSHALL. MICHAEL MADDOXAND JERRY CARPENTER RETURNED TO THE SCENE AND AWAITED THE ARRIVAL OF THEPUBLIC SERVICE COMMISSION AND THE STATE FIRE MARSHALL WAS ALREADY ON THESCENE. MR. JOHN, THE STATE FIRE MARSALL, AND HAROLD DUNSON WITH THE PUBLICSERVICE COMMISSION DECIDED IT WOULD BE BETTER FOR AN INDEPENDENT PERSON TO DOTHE PRESSURE TEST ON THE PLUMBING INSIDE THE BUILDING. ALABAMA GAS INTALLADEGA WAS CONTACTED AND ASKED TO RUN THE PRESSURE TEST. THE GASTECHNICIAN TESTED THE PLUMBING AT 6 INCH WATER COLUMN FOR APPROXIMATELY 10MINUTES, NO LEAKS WERE FOUND. RESULTS FROM THESE TEST CAN ALSO BE OBTAINEDFROM THE OFFICE OF PIPELINE SAFETY, STATE OF ALABAMA PUBLIC SERVICE COMMISSIONOR STATE OF ALABAMA OFFICE OF STATE FIRE MARSHALL. AFTER EXAMINING THE METERAT THE SITE, IT WAS APPARENT THAT ABOUT 300 CUBIC FEET OF GAS HAD PASSEDTHROUGH THE METER. BY THE STATEMENT GIVEN AND THE EVIDENCE SEEN, IT ISCONCLUDED THAT AN EXCESS AMOUNT OF GAS WAS ALLOWED INTO THE UTILITY ROOM ANDPROPER TIME NOT ALLOWED FOR VENTING. AS A RESULT, INSERTION OF THEELECTRICAL PLUG CREATED A SPARK WHICH IGNITED THE GAS IN THE ROOM.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990055 | 1999-03-02 | 20245 | MIDCON TEXAS PIPELINE CORP. | GOODRICH | POLK | TX | 77335 | 49 | 2512+60 | 1145 | 1999-01-25 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 100000 | 68965.0661 | 150242.0516 | Null | 1 | 30 |  | 19990125 | 640 | 1032 | NO DATA | 1717 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1982; NMDIA: 24; THK: 0.49; SPEC: 5LX; SMYS: 60000; SEAM: DSAW; MANU: VALLOUREC; MANYR: 0; LOCLK: UNDER GROUND; PNAME: STEPHEN C COFFMAN; PHONE: 303914708; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | EXTEME VARIATIONS IN TRINITY RIVER WATER ELEVATIONS MAY HAVE BEEN ACONTRIBUTING FACTOR.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990056 | 1999-03-01 | 19136 | TEJAS GAS CORP | EASTON | GREGG | TX | 75641 | 478+50 |  | 945 | 1999-02-02 | 1 | NO |  |  | TX | Null | NO | RUPTURE | 0 | 0 | 0 | 150000 | 103447.5991 | 225363.0773 | Null | 0 | 30 |  | 19990202 | 740 | 1150 | BY TEST | 1706 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1991 | 20 | 0.31 | API 5L X-60 | 1872 | ERW |  | STUPP | 1980 | UNDER GROUND |  | FRED L DENNIS | 7132303175 | INTERNALLY | LOCALIZED PITTING |  | OTHER | MICROBIOLOGICAL | COATED | YES | 1981 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | MICROALLOYING INTERNATIONAL, INC. WAS COMMISSIONED TO INVESTIGATE THE FAILUREOF A NATURAL GAS PIPELINE FOR TEJAS LLS. THE PIPELINE IS FABRICATED FROM 20OF A NATURAL GAS PIPELINE FOR TEJAS LLC. THE PIPELINE IS FABRICATED FROM 20INCH DIAMETER, 0.312 INCH WALL API 5L GRADE X-60 ERW PIPE. THE PIPE WASMANUFACTURED BY STUPP AND INSTALLED IN JANUARY 1981. ON FEBRUARY 2, 1999 AT9:45 AM LOCATED AT 2,000 FEET NORTHEAST OF THE INTERSECTION OF HIGHWAY 149 ANDFM 2906 IN GREGG COUNTY, TEXAS. OPERATING PRESSURE AT THE TIME OF FAILURE WAS740 PSIG AND THE GAS FLOW RATE AT THE TIME OF FAILURE WAS REPORTED TO BE 10MMCF. SYSTEM DESIGN PRESSURE IS 1348 PSIG. ON SITE INVESTIGATION, BY BOTHTRANSOK AND MICROALLOYING PERSONNEL, REVEALED THAT IN EXCESS OF 20 FEET OF THEPIPELINE WAS TORN FROM THE ORIGINAL INSTALLATION. THE ACTUAL DEBRIS CONSISTEDON ONE SECTION OF PIPE WHICH UNRAVELED IN A SPIRAL PATTERN AS SHOWN INF FIGURE1. THE PRELIMINARY ON SITE INVESTIGATION SHOWED THAT THE RUPTURE MOST LIKELYINITIATED AT THE LOWEST POINT OF THE INSTALLATION WHERE CONDENSATION ANDMOISTURE WOULD BE EXPECTED TO COLLECT. THIS REGION IS SHOWN IN FIGURE 2 WHICHALSO SHOWS THAT SEVERE LOCALIZED CORROSION IS ALIGNED AT THE BOTTOM (SIXO'CLOCK INSTALLED POSITION) OF THE PIPE. THE LOCALIZED CORROSION EXTENDEDAPPROXIMATELY 18 INCHES ALONG THE BOTTOM OF THE PIPE AND WAS SEVERAL INCHESACROSS AT THE WIDEST SECTION. THE ERW WELD ON THIS PARTICULAR SEGMENT WASALIGNED NEAR THE ELEVEN O'CLOCK IN THE INSTALLED POSITION. THE SPIRAL TEAREXHIBITED A DUCTILE FRACTURE SURFACE WITH LOCALIZED DISTORTION NEAR THEFRACTURE SURFACE AND A 45 DEGREE SHEAR SEPARATION ANGLE ALONG THE LENGTH OFTHE TEAR. THERE WERE NO SIGNS OF CORROSION ALONG THE SPIRAL TEAR. THREESECTIONS OF THE DAMAGED PIPE WERE DISPATCHED TO HOUSTON FOR FURTHER ANALYSIS.THE SECTIONS ANALYZED INCLUDE THE LOW POINT REGION WITH LOCALIZED CORROSION,AND TWO SECTIONS REMOVED FROM THE SPIRAL TEAR SEGMENT.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990057 | 1999-03-04 | 18516 | SOUTHERN NATURAL GAS CO | MONTICELLO | EAST CARROLL PARISH | LA |  | 37.70 NORTH MAIN PIPELINE | LAT32^42'20" LON91^20"54" | 720 | 1999-01-30 | 1 | NO |  |  | LA | Null | NO | LEAK | 0 | 0 | 0 | 165000 | 113792.359 | 247899.3851 | Null | 3 | 40 |  | 19990130 | 436 | 500 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: GIRTH; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1930; NMDIA: 22; THK: 0.31; SPEC: API 5L; SMYS: 35000; SEAM: FUSION WELD; MANU: AO SMITH; MANYR: 1929; LOCLK: UNDER WATER; PNAME: KENNETH C PETERS - SUPERVISOR; PHONE: 2053257554; PROT: Null; CAULK: EARTH MOVEMENT: OTHER; DMGO: FLOOD CONDTIONS; NOTIF: Null; MARK: Null; MRKTP: 1; STAT: Null; CTEST: Null | COMPANY WAS NOTIFIED BY THE PUBLIC OF A LARGE COLUMN OF WATER BLOWING IN THEAIR IN EAST CARROLL PARISH LOUISIANA. EMPLOYEES DISPATCHED TO THE SITEDETERMINED THE CAUSE TO BE A LEAK ON THE 22" NORTH MAIN PIPELING IN LONG LAKEBAYOU. THE AREA HAD RECEIVED 8" OF RAIN PRIOR TO THE LEAK CAUSING FLASHFLOODING AND RAPID CURRENTS IN THE BAYOU. IT IS BELIEVED THAT THE HIGH WATERCONDITIONS CAUSED EXCESSIVE STRESSES ON AND ULTIMATE CRACKING OF A GIRTH WELD30' EAST OF THE BAYOU'S WEST BANK. DIVERS LATER CONFIRMED A 1/2" WIDE CRACKIN THE GIRTH WELD, APPROXIMATELY 17" LONG. THE DECISION WAS MADE TO LEAVE THELINE OUT OF SERVICE UNTIL APRIL 1999, WHEN REPLACEMENT OF LINE HAD BEENPREVIOUSLY SCHEDULED. A METALLURGICAL ANALYSIS WILL BE PERFORMED ON THECRACKED WELD WHEN THE FAILED SEGMENT CAN BE REMOVED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990062 | 1999-03-10 | 20245 | MIDCON TEXAS PIPELINE CORP. | GOODRICH | POLK | TX | 77335 | 49 | 2515+80 | 140 | 1999-01-13 | 1 | NO |  |  | TX | Null | NO | LEAK |  | 0 | 0 | 200000 | 137930.1321 | 300484.1031 | Null | 1 | 30 |  | 19990113 | 619 | 1032 | NO DATA | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1982; NMDIA: 24; THK: 0.49; SPEC: 5LX; SMYS: 60000; SEAM: DSAW; MANU: VALLOUREC; MANYR: 0; LOCLK: UNDER GROUND; PNAME: STEPHEN C COFFMAN; PHONE: 3039147808; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | EXTREME VARIATIONS IN TRINITY RIVER WATER ELEVATIONS MAY HAVE BEEN ACONTRIBUTING FACTOR.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990063 | 1999-01-21 | 4070 | EAST TENNESSEE NATURAL GAS CO | WYTHEVILLE | WYTHE | VA | 24382 | MLV 3314 |  | 200 | 1999-01-03 | 2 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 125000 | 86206.3326 | 187802.5644 | Null | 3 | 15 |  | 19990103 | 905 | 915 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: FLANGE; MLKD: OTHER; MLKDO: INSULATING FLANGE; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1965; NMDIA: 0; THK: 0; SMYS: 0; LOCLK: NO DATA; PNAME: DARON MOORE; PHONE: 7134204023; PROT: Null; CPYR: 0; CAULK: NO DATA; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | FIRE FROM NEARBY NATURAL GAS PIPELINE FACILITY DAMAGED EAST TENNESSEE NATURALGAS METER STATION.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990069 | 1999-03-11 | 13063 | NATIONAL FUEL GAS SUPPLY CORP | GENESSEE | POTTER | PA | 16923 |  |  | 1931 | 1999-02-24 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 5000000 | 3448253.3037 | 7512102.5775 | YES | 0 | 25 |  | 19990224 | 1261 | 2250 | NO DATA | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | VALVE | FLANGE | STEEL |  | COMPRESSOR STATION |  | 1965 | 0 | 0 |  | 0 |  | PLUG | ROCKWELL 3" | 1965 | ABOVE GROUND |  | DAVID M BIMBER | 7166469360 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | VALVE ON COMPRESSOR VOLUME BOTTLE | NO |  | NO DATA |  | 0 | 0 | GASKET ON BACK OF VALVE FAILED. THIS FILLED THE COMPRESSOR STATION WITH GAS.THE GAS IGNITED AND BURNT IN THE COMPRESSOR STATION.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990070 | 1998-04-15 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA | MOSCOW | POLK | TX | 75960 | 330 GULF COAST 3 PIPELINE | 17833+12 | 2240 | 1998-03-29 | 1 | NO |  |  |  | Null | NO | RUPTURE | 159 | 0 | 0 | 112036 | 78258.9128 | 170488.9197 | Null | 1 | 20 |  | 19980330 | 824 | 858 | BY TEST | 1080 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE | FLANGE | STEEL |  | PIPELINE |  | 1967 | 36 | 0.33 | 5LX65 | 65000 | FLASH WELD |  | A O SMITH | 1967 | UNDER GROUND |  | STEPHEN C COFFMAN | 6306913788 | EXTERNALLY | OTHER | LOCAL CRACKING | OTHER | UNDEFINED | COATED | YES | 1967 | NO DATA |  | Null |  | Null |  | Null |  |  | Null | [5 empty] | COMPLEX INTERACTION OF SOIL ENVIRONMENT, PIPE MATERIALS, AND OPERATINGCONDITIONS.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990074 | 1999-03-24 | 13845 | NORTHWEST PIPELINE CORP | STEVENSON | SKAMANIA | WA | 98648 | 1194.7 | 6891+32.2 | 2020 | 1999-02-26 | 1 | NO |  |  | WA | Null | NO | RUPTURE |  | 0 | 0 | 4000000 | 2758602.6429 | 6009682.062 | Null | 1 | 0 |  | 19990227 | 682 | 809 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1956; NMDIA: 26; THK: 0.34; SPEC: API5LX52; SMYS: 1376; SEAM: DSA; MANU: REPUBLIC; MANYR: 1956; LOCLK: UNDER GROUND; PNAME: ED COMPTON; PHONE: 8015846776; PROT: Null; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: Null; MARK: Null; MRKTP: 0; STAT: Null; CTEST: Null | EXCESSIVE RAIN. LAND MOVEMENT
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990080 | 1999-04-07 | 2748 | CONSUMERS POWER CO | PLAINWELL |  | MI | 49080 |  | 1396+14 | 1940 | 1999-03-07 | 1 | NO |  |  |  | Null | NO | RUPTURE | 16.5 | 0 | 0 | 700000 | 482755.4625 | 1051694.3609 | YES | 2 | 27 |  | 19990307 | 791 | 800 | BY TEST | 1200 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | LONGITUDINAL | STEEL |  | PIPELINE |  | 1957 | 12 | 0.25 | API 5LX | 42000 | ELECTRIC RESIST |  | JONES & LAUGHLIN STEEL CORP | 1957 | UNDER GROUND |  | WAYNE J DEVRIES | 5177881201 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL |  | YES | 19770615 | WATER |  | 24 | 1262 | CAUSE OF FAILURE WAS LACK OF FUSION IN THE LONGITUDINAL WELD OF A LENGTH OF12" PIPE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990081 | 1999-03-29 | 19570 | TRANSCO GAS PIPELINE CORP | LIVINGSTON | ESSEX | NJ |  | 1816.50 |  | 1300 | 1999-03-03 | 3 | NO |  |  | NJ | Null | NO | LEAK |  | 0 | 0 | 80000 | 55172.0529 | 120193.6412 | Null | 11 | 30 |  | 19990303 | 610 | 638 | BY TEST | 1370 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1985; NMDIA: 36; THK: 0.5; SPEC: API 5L; SMYS: 52000; SEAM: DSA; MANU: BETHLEHEM; MANYR: 0; LOCLK: UNDER GROUND; PNAME: B R LANDES; PHONE: 7132152001; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CAULC: NO DATA; CTEST: Null; MED: NO DATA; TMPS: 0; LKPS: 0 | INVESTIGATION FOUND THE LEAK TO BE IN A CRACK IN THE WALL OF THE 36" LINE PIPEWHERE THE HOT TAP NIPPLE IS CONNECTED. THE HOT TAP CONNECTION INCLUDING THELINE PIPE CONTAINING THE PIPE IS BEING SENT TO THE METALLURGIST. RESULTS OFTHE METALLURGICAL EXAMS WILL BE FORWARDED IN A SUPPLEMENTAL REPORT DESCRIBINGTHE CAUSE OF THE LEAK.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19990082 | 1999-03-22 | 31287 | WILD GOOSE STORAGE INC | GRIDLEY | BUTTE | CA | 95948 |  | 14V-17-17N-O-E | 1500 | 1999-02-28 | 1 | NO |  |  | CA | NO | NO | LEAK |  | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19990301 | 1580 | 2035 | BY TEST | 2544 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: GATHERING SYSTEM; PRTFL: MECHANICAL JOINT; MLKD: OTHER; MLKDO: WEEPING AROUND GASKET; PRTSY: PIPELINE; PRTYR: 1998; NMDIA: 18; THK: 0.5; SMYS: 0; MANYR: 0; LOCLK: ABOVE GROUND; PNAME: WAYNE MARDIAN; PHONE: 5308467350; PROT: Null; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null | WE HAD BEEN OPERATING THE PIPELINE FOR 6 MONTHS AT 1400 PSI. BECAUSE THEOPERATING PRESSURE WOULD BE INCREASING IN THE NEAR FUTURE THE DECISION WASMADE TO BLOCK IN THE WELLS ALLOWING THE PIPELINE PRESSURE TO INCREASE TO ITSMAXIMUM WORKING PRESSURE. WHEN THE PIPELINE REACHED A PRESSURE OF 1580 WEDISCOVERED A LEAK BETWEEN TWO FLANGES. THE PRESSURE WAS REDUCED INTO PG&E'SDISTRIBUTION LINE. THE GASKET WAS IN EXCELLENT CONDITION , THE LEAK MAY HAVEBEEN CAUSED BY IMPROPER TARQUING METHODS. FLANGES WERE HYDRAULICALLY TARQUEDUSING SPECIAL EQUIPMENT.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19990086 |  | 2620 | COLUMBIA GULF TRANSMISSION CO | VERMILLION BLOCK 248 |  | LA |  | VERMILLION 248 | X=1680, 186 Y=28772 | 230 | 1999-03-23 |  | YES | VERMILLION | 248 |  | Null | NO | LEAK |  | 0 | 0 | 70000 | 48275.5463 | 105169.4361 | Null | 0 | 0 |  | 19990323 | 1138 | 1250 | NO DATA | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: VALVE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1972; NMDIA: 16; THK: 375; SPEC: 5LX; SMYS: 52000; SEAM: DSAW; VALVE: 16" CHECK VALVE; MANYR: 1972; LOCLK: UNDER WATER; PNAME: HENRY H WANG; PHONE: 7132674371; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; MRKTP: 0; STAT: NO; CTEST: Null | A TRAWLING NET DAMAGED THE BLEEDER VALVE ON THE 16" CHECK VALVE SHAFT COVERAND PULLED THE OPERATOR OFF THE 12" VALVE THEREFORE DAMAGING THE VALVESYSTEM. THE BLEEDER VALVE AND NIPPLE ON THE 16" CHECK VALVE WERE REPLACED ANDTHE STEM AND OPERATOR ON THE 12" VALVE WERE REPLACED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19990100 | 1999-06-09 | 20245 | MIDCON TEXAS PIPELINE CORP. | PORT NECHES | ORANGE | TX | 77651 | 81.18 | 4286+66 | 1745 | 1999-05-13 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 45000 | 31034.2797 | 67608.9232 | Null | 4 | 30 |  | 19990513 | 450 | 500 | NO DATA | 0 | CORROSION | CORROSION | EXTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1952; NMDIA: 20; THK: 0.5; SPEC: API 5LX; SMYS: 35000; SEAM: ERW; MANYR: 1952; LOCLK: UNDER WATER; PNAME: STEPHEN C COFFMAN; PHONE: 3039147808; LOC: EXTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: GALVANIC; COAT: COATED; PROT: YES; CPYR: 1952; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19990101 | 1999-06-09 | 13750 | NORTHERN NATURAL GAS CO (ENRON) |  | GREEN | WI |  | MP 5.543 |  | 1359 | 1999-05-12 | 1 | NO |  |  |  | Null | Null | OTHER |  | 0 | 0 | 50000 | 34482.533 | 75121.0258 | Null | 2 | 0 |  | 19990512 | 700 | 960 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1963; NMDIA: 3; THK: 0.16; SPEC: API 5LX; SMYS: 42000; SEAM: ERW; MANYR: 0; LOCLK: UNDER GROUND; PNAME: PATRICK L VAUGHAN SR; PHONE: 7136467346; PROT: Null; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19990507; MARK: YES; MRKTP: 3; STAT: YES; CTEST: Null
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19990104 | 1999-06-25 | 31286 | ONEOK GAS TRANSPORTATION, LLC |  | GRADY | OK |  | SE/2, T5N, R8W |  | 10 | 1999-05-28 | 1 | NO |  |  | OK | Null | NO | RUPTURE | 2 | 0 | 0 | 70000 | 48275.5463 | 105169.4361 | Null | 2 | 0 | 485403 | 19990528 | 680 | 960 | BY TEST | 1546 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | OTHER | UNSURE-LAB TEST PENDING | STEEL |  | OTHER | PIPELINE DRIP | 1976 | 169 | 0.38 | X-52 DSAW | 52000 | DSAW |  | UNKNOWN |  | UNDER GROUND |  | G A PHILLIPS, MGR FIELD OPERATIONS | 9185887928 | INTERNALLY | LOCALIZED PITTING |  | OTHER | TEST PENDING | COATED | YES | 1976 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | APPARENT CAUSE- INTERNAL CORROSION. LAB TESTING PENDING. TELEPHONIC REPORT#485403APPARENT CAUSE-- INTERNAL CORROSION. LAB TEST PENDING. TELEPHONIC REPORT #485403
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19990105 | 1999-06-28 | 2620 | COLUMBIA GULF TRANSMISSION CO | CAMERON |  | LA |  | WC 643A | X=1450630 Y=245231 | 930 | 1999-05-20 | 1 | YES | WC | 643A |  | Null | NO | LEAK |  | 0 | 0 | 60000 | 41379.0396 | 90145.2309 | Null | 0 | 0 |  | 19990520 | 905 | 1440 | NO DATA | 0 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | VALVE | UNSURE-LAB TEST PENDING | STEEL |  | OTHER | VALVE | 1975 | 24 | 0.06 | 5LX | 60000 | DSAW | SWING CHECK VAL | TOM WHEATLEY VALVE CO | 1975 | UNDER WATER |  | HENRY H WANG | 7132674371 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  | Null | MATERIAL | 24" CHECK VALVE NEAR BOTTOM OF RISER | NO |  | NO DATA |  | 0 | 0 | DEFECT ON 24" CHECK VALVE AT BOTTOM OF RISER.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19990108 |  | 13710 | NORTHERN ILLINOIS GAS CO | ANCONA | LIVINGSTON | IL | 61364 |  |  | 155 | 1999-06-13 | 2 | NO |  |  |  | Null | NO | RUPTURE | 10 | 0 | 0 | 1800000 | 1241371.1893 | 2704356.9279 | Null | 0 | 20 | 487294 | 19990613 | 980 | 1440 | BY TEST | 2160 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | OTHER | DRIP | 1973 | 12 | 0.38 | API 5LX X60 | 41 | ELECTRIC WELDED |  | REPUBLIC STEEL | 1972 | UNDER GROUND |  | GEORGE WALDVOGEL | 6309838676 | INTERNALLY | LOCALIZED PITTING |  | OTHER | SEE #6 | COATED | YES | 1973 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | AT THE ANCONA STATION, A 12" NATURAL GAS DRIP RUPTURED AND IGNITED RESULTING IN PROPERTY DAMAGE TO THE STATION FACILITIES. THE DRIP IS USED TO COLLECT LIQUIDS FROM THE GATHERING SYSTEM. PRELIMINARY INVESTIGATION SHOWS INTERNAL CORROSION AS THE CAUSE OF THE FAILURE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990116 | 1999-07-23 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA | BECKVILLE | PANOLA | TX | 75633 | 424 | 22327+85 | 2109 | 1999-07-10 | 1 | NO |  |  |  | Null | NO | RUPTURE | 35 | 0 | 0 | 361000 | 248963.8885 | 542373.8061 | Null | 2 | 0 | 490844 | 19990710 | 829 | 858 | BY TEST | 1150 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1983 | 30 | 0.31 | 5LX | 60000 | DSAW |  | A O SMITH | 1961 | UNDER GROUND |  | STEPHEN C COFFMAN | 3039147808 | INTERNALLY | LOCALIZED PITTING |  | OTHER | BACTERIAL | COATED | YES | 1961 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | INTERNAL CORROSION OF THE CARRIER PIPE
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990125 | 1999-08-09 | 2616 | COLUMBIA GAS TRANSMISSION CORP |  | BROOKE | WV | 26070- |  |  | 1117 | 1999-07-18 | 1 | NO |  |  | WV | Null | NO | OTHER |  | 0 | 0 | 80000 | 55172.0529 | 120193.6412 | Null | 1 | 43 | 491766 | 19990718 | 240 | 76 | BY TEST | 114 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: VALVE; MLKD: OTHER; MLKDO: PACKING OR GASKET; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1983; NMDIA: 4; SPEC: ANSI 300; SMYS: 0; VALVE: PLUG; MANU: NORDSTROM; LOCLK: ABOVE GROUND; PNAME: JOHN S ZURCHER; PHONE: 3043572669; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19990136 | 1999-09-08 | 18594 | SPUR, CITY OF |  | KENT | TX |  | BETWEEN ODORIZER & VALVE |  | 445 | 1999-08-26 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 0 | 0 | 0 | Null | 0 | 45 |  | 19990826 | 100 | 150 |  |  | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; NMDIA: 4; THK: 0.122; SMYS: 0; SEAM: WELD; VALVE: GATE; MANU: UNKNOWN; MANYR: 1966; LOCLK: UNDER GROUND; PNAME: JOSH FLUD; PHONE: 8062713316; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: MARKER; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | STATE CONTRACTOR WAS WIDENING ROAD AND CUTTING A BAR DITCH AND HIT LINE WITH THE CATERPILLAR.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19990137 | 1999-09-22 | 2616 | COLUMBIA GAS TRANSMISSION CORP |  | MARSHALL | WV | 2 6033 |  | 107+66 | 755 | 1999-08-23 | 1 | NO |  |  | WV | Null | NO | RUPTURE | 43 | 0 | 0 | 71000 | 48965.1969 | 106671.8566 | Null | 0 | 39 | 496023 | 19990823 | 742 | 860 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | WELD |  | STEEL |  | PIPELINE |  |  | 16 | 0.25 | API 5LX | 46000 | ERW | PLUG | REPUBLIC STEEL | 1960 | UNDER GROUND |  | STEVEN BURNLEY/JOHN S ZURCHER | 3043572669 | INTERNALLY | OTHER | SEAM | OTHER | SEAM | COATED | YES | 1963 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | ON 8/23/99 16" STORAGE LINE 29104 RUPTURED, WITH AN ENSUING FIRE. PRELIMINARY ASSESSMENT OF THE DAMAGE IS 5-7 ACRES OF FARMLAND BURNED, HEAT DAMAGE TO A GARAGE, ROOF DAMAGE TO A MOBILE HOME, AND DAMAGE TO A GRAVEL STATE ROAD (FISH RIDGE ROAD). THERE WERE NO INJURIES.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990138 | 1999-09-13 | 19730 | TRUNKLINE GAS CO | EDNA | JACKSON | TX | 7 7957 | LINE NUMBER 100-1 MP 229. |  | 1350 | 1999-08-14 | 1 | NO |  |  | TX | Null | NO | OTHER |  | 0 | 0 | 500000 | 344825.3304 | 751210.2578 | Null | 0 | 15 | 495259 | 19990816 | 50 | 936 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1951; NMDIA: 20; THK: 0.25; SPEC: API 5L; SMYS: 52000; SEAM: ELECTRIC WELD; MANU: KAISER; MANYR: 1951; LOCLK: UNDER GROUND; PNAME: ERIC J AMUNDSEN; PHONE: 7139897460; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | THE PIPELINE FAILED IN A COMPRESSIVE MODE AS A RESULT OF THE PIPELINE HEATING AND EXPANDING APPROXIMATELY 30 INCHES. THE HEATING WAS CAUSED BY THE PRESENCE OF IRON SULFIDE INSIDE THE PIPELINE AND A SUBSEQUENT EXOTHERMIC REACTION THAT RESULTED WHEN AIR WAS INTRODUCED DURING EVACUATION OF THE PIPELINE FOR MAINTENANCE WORK. THE DISCOVERY THAT THE PIPELINE HAD FAILED IN THIS MODE WAS MADE AFTER THE MAINTENANCE WORK WAS COMPLETED AND DURING THE PURGING OPERATION WITH GAS AT APPROXIMATELY 50 PSIG. THE PIPELINE WAS FOUND TO HAVE FAILED IN TWO LOCATIONS APPROXIMATELY 1,300 FEET APART.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990139 | 1999-09-16 | 6660 | GREAT LAKES GAS TRANSMISSION CO | WAKEFIELD | GOGEBIC | MI | 49968- | MP 416.18/MLV 7-0-1 | 7 | 630 | 1999-08-16 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 163000 | 112413.0577 | 244894.544 | Null | 0 | 0 | 496056 | 19990823 | 713 | 958 | BY TEST | 1976 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | TRANSMISSION SYSTEM | FITTING | EXTRUDED TEE | STEEL |  | OTHER | MAIN LINE VALVE BLOWOFF | 1968 | 12 | 0.638 | ANSI B31.8 | 35000 | NONE |  | UNKNOWN | 1968 | ABOVE GROUND |  | ROBERT J CADORIN | 3135964669 | [6 empty] | Null | 0 | EARTH MOVEMENT: OTHER | LIGHTNING STRIKE | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | A LIGHTNING STRIKE CAUSED THE MAIN LINE VALVE (WHICH IS NORMALLY CLOSED) TO CYCLE PARTIALLY OPEN. THIS PARTIALLY OPEN CONDITION CAUSED VIBRATION IN THE MAIN LINE VALVE ASSEMBLY TO OCCUR. THIS VIBRATION SUBSEQUENTLY CAUSED A CRACK TO DEVELOP IN THE HEAT-AFFECTED ZONE ADJACENT TO A 2-INCH GIRTH WELD ON A 12"X12" EXTRUDED TEE FITTING SITUATED ON THE VALVE BLOWOFF. THE PROPERTY DAMAGE ESTIMATE INCLUDES $154,423 FOR THE COST OF GAS BLOWN DOWN AND PURGED TO FACILITATE THE REPAIR.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19990151 | 1999-09-27 | 22175 | DYNEGY MIDSTREAM SERVICES, L.P. | CRANE | CRANE | TX | 7 9731 |  |  | 1700 | 1999-08-11 | 1 | NO |  |  |  | Null | NO | RUPTURE | 4 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 15 | 494775 | 19990812 | 690 | 680 | BY TEST | 1200 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  |  | 12 | 0.25 | API 5LX X52 | 0 | ERW |  | U S STEEL |  | UNDER GROUND |  | TIM BOGGS | 9155583996 | INTERNALLY | OTHER | INSIDE PITTING ON TOP | OTHER | ACID CORROSION | COATED | YES | 1997 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | THERE WERE NO SIGNS OF OUTSIDE PIPELINE CORROSION OR DAMAGE OF ANY TYPE. CORROSION COUPONS DO NOT INDICATE ANY PROBLEMS ASSOCIATED WITH THE CORROSION PROGRAM. PIPELINE OPERATION WAS NORMAL, NO PRESSURE FLUCTUATIONS WERE NOTED AT THE TIME OF FAILURE. ACCORDING TO THE METALLURGICAL INVESTIGATION, MILD ACIDIC. CORROSION ATTACKED THE PIPE WALL FROM THE INSIDE THINNING THE WALLS OF THE PIPE AT THE 12 OCLOCK POSITION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19990152 | 1999-09-27 | 31129 | BASIN EXPLORATION INC |  |  | LA |  |  |  | 1355 | 1999-09-23 |  | YES | WC | WC 45 | LA | Null | NO | LEAK |  | 0 | 0 | 0 | 0 | 0 | Null | 0 | 15 |  | 19990923 | 1440 |  | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | UNSPECIFIED CORROSION | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1958; NMDIA: 16; SMYS: 0; MANU: TRANSCONTINENTAL GAS PIPELINE; LOCLK: UNDER WATER; PNAME: K W PRICHETT, PROJECT MANAGER; PHONE: 2815783388; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990153 | 1999-09-21 | 12462 | MID LOUISIANA GAS CO | VENICE | PLAQUEMINES | LA |  |  | 21+20 | 2445 | 1999-08-15 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 100000 | 68965.0661 | 150242.0516 | Null | 1 | 0 | 495123 | 19990815 | 900 | 1320 | BY TEST | 1716 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; NMDIA: 6; THK: 0.188; SPEC: API 5LX; SMYS: 42000; MANU: J&L; MANYR: 1975; LOCLK: UNDER WATER; PNAME: GARY GILBERT; PHONE: 3186654426; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19990809; MARK: YES; MRKTP: SIGNS ON POST; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | DRAGLINE CAUGHT PIPE WITH ONE TOOTH OF BUCKET.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19990158 | 1999-10-01 | 4280 | EL PASO NATURAL GAS CO | EL PASO | HUDSPETH | TX |  | HUECO COMPRESSOR STA |  | 1630 | 1999-09-01 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 3 | 50000 | 34482.533 | 75121.0258 | Null | 0 | 3 | 497288 | 19990902 | 0 | 809 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: NO DATA; MLKD: STEEL; PRTSY: PIPELINE; SMYS: 0; LOCLK: ABOVE GROUND; PNAME: GILBERT ARAGON, MANAGER; PHONE: 9154962624; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | AT APPROXIMATELY 4:30 PM, SEPT 1, 1999 THREE EL PASO NATURAL GAS EMPLOYEES RECEIVED SECOND DEGREE BURNS TO THEIR FACES AND WRISTS WHEN A FLASH FIRE OCCURRED AFTER PLACING A BLIND FLANGE BACK ON A 6-INCH BLOWOFF. A 12-INCH BYPASS BEING INSTALLED WHEN GAS WAS IGNITED WHEN WELDING A PUP TO LEVEL A 2-INCH VALVE OPERATOR TO VALVE 20 1/2. THE EMPLOYEES WERE TREATED ON SITE AND RUSHED TO THE HOSPITAL WHERE THEY STAYED OVERNIGHT.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 19990159 | 1999-10-01 | 4280 | EL PASO NATURAL GAS CO | TUCSON | GREENLEE | AZ |  | MP 17+4191 LINE 2007 | ES 938 + 11.2 | 930 | 1999-09-13 | 3 | NO |  |  |  | Null | NO | RUPTURE |  | 0 | 0 | 50000 | 34482.533 | 75121.0258 | Null | 1 | 45 | 498554 | 19990913 | 640 | 650 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1955; NMDIA: 6.625; THK: 0.1875; SMYS: 0; SEAM: ERW; MANU: REPUBLIC; MANYR: 1943; LOCLK: UNDER GROUND; PNAME: GILBERT ARAGON, MANAGER; PHONE: 9154962624; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PIPELINE METAL SIGNS; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | AT 9:30 AM A FARMER PLOWING A FIELD HIT AND PUNCTURED THE 6 5/8 INCH PIPELINE BETWEEN VALVE 2 AND VALVE 3. BOTH VALVES WERE SHUT-IN TO ISOLATE THE SEGMENT. HIGHWAY 75 FROM MILE MARKERS 395 TO 400 WAS CLOSED AND THE NEARBY VALLEY VIEW TRAILER PARK WAS EVACUATED. AT 11:15 AM, THE LINE WAS BLOWN DOWN AND THE AREA MADE SAFE. THE HIGHWAY WAS THEN REOPENED AND THE RESIDENTS WERE LET BACK INTO THEIR HOMES BY 11:30.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990160 | 1999-10-01 | 4280 | EL PASO NATURAL GAS CO | GALLUP | SAN JUAN | NM |  | MP 37.7 LINE 1201 |  | 1938 | 1999-09-12 | 1 | NO |  |  |  | Null | NO | RUPTURE | 25 | 0 | 0 | 174800 | 120550.9355 | 262623.1061 | Null | 2 | 30 | 498467 | 19990912 | 775 | 845 | BY TEST | 1560 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1954; NMDIA: 24; THK: 0.281; SMYS: 60000; SEAM: EFW; MANU: UNKNOWN; LOCLK: UNDER GROUND; PNAME: GILBERT ARAGON, MANAGER; PHONE: 9154962624; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CAULC: MATERIAL; CTEST: YES; TESTD: 19810225; MED: WATER; TMPS: 8; LKPS: 1560 | ON SEPT 12, 1999, GAS CONTROL RECEIVED A CALL AT 8:05 PM FROM THE SHIPROCK POLICE ABOUT A RUPTURE ON OUR PIPELINE. EPNG PERSONNEL RESPONDED TO THE CALL AND ISOLATED THE SEGMENT BEWTEEN VALVES 2 1/2 AND VALV3 3. REPAIR CREWS WERE ON SITE THE NEXT MORNING AND REPLACED THE SEGMENT WITH 2 JOINTS OF PIPE. THE LINE WAS BACK IN SERVICE BY THE EVENING OF SEPT. 13. NRC # 498467
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990165 | 1999-10-15 | 13750 | NORTHERN NATURAL GAS CO (ENRON) |  |  | TX |  |  |  | 1215 | 1999-09-08 |  | YES | MUSTANG ISLAND | 758 | TX | YES | NO | LEAK |  | 0 | 0 | 150000 | 103447.5991 | 225363.0773 | Null | 0 | 0 | 497979 | 19990908 | 940 | 1440 | BY TEST | 2237 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: THREADED; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1981; NMDIA: 2; THK: 0.344; SMYS: 0; LOCLK: UNDER WATER; PNAME: MERLIN MOSEMAN; PHONE: 7136467344; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null; TMPS: 0; LKPS: 0 | A 2" THREADED PIPE NIPPLE AND VALVE THAT WAS ATTACHED TO A 12" PIPELINE TEE AND FLANGE WAS CAUGHT BY A FISHING NET. THE PIPE NIPPLE WAS BENT SLIGHTLY AT ITS THREADED CONNECTION, RESULTING IN A SMALL LEAK.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990171 | 1999-10-25 | 19270 | WILLIAMS GAS PIPELINE - TEXAS GAS | KENTON | OBION | TN | 38233- | 26" MLS-2, MP 346+5181 |  | 100 | 1999-09-23 | 1 | NO |  |  |  | Null | NO | RUPTURE | 29 | 0 | 0 | 312750 | 215688.2441 | 469882.0162 | Null | 1 | 0 | 499904 | 19990923 | 815 | 840 | BY CFR 192.619(A)(3) | 1166 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1952; NMDIA: 26; THK: 0.281; SPEC: API 5L; SMYS: 52000; SEAM: FLASHWELD; MANU: A O SMITH; MANYR: 1952; LOCLK: NO DATA; PNAME: SHEILA DUNBAR, STAFF PIPELINE; PHONE: 2706886962; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | ON THURSDAY, SEPTEMBER 23, 1999, AT 1:00 A.M. CENTRAL STANDARD TIME. WILLIAMS GAS PIPELINE-TEXAS GAS SUSTAINED AN IN-SERVICE FAILURE ON ITS 26" MAINLINE SYSTEM. NO. 2 PIPELINE IN OBION COUNTY, TENNESSEE. THE LOCATION OF THE INCIDENT WAS MILEPOST 346+5181, WHICH IS APPROXIMATELY 2.75 MILES NORTHEAST OF THE CITY OF KENTON, TENNESSEE, AND APPROXIMATELY ONE MILE DOWNSTREAM OF TEXAS GAS KENTON, TN, COMPRESSOR STATION. THERE WERE NO INJURIES OR FATALITIES RESULTING FROM THIS INCIDENT. THERE WERE NO SERVICE INTERUPTIONS AS A RESULT OF THE FAILURE. TEXAS GAS STAFF METALLURGIST HAS DETERMINED THE FAILURE WAS INITIATED BY A STRESS CORROSION CRACK THAT EXTENDED 5 5/8" ALONG THE LONGITUDINAL AXIS OF THE PIPE. THE FAILURE RESULTED IN A 29-FOOT LENGTH OF PIPE BEING SEPARATED FROM THE CONTIGOUS PIPELINE SYSTEM. THE PIPELINE SYSTEM HAS BEEN UNDER CATHODIC PROTECTION SINCE ITS CONSTRUCTION IN 1952. THE LINE HAD BEEN HYDROSTATICALLY TESTED IN 1964 AND 1985. PROPERTY DAMAGE WAS CONFINED TO TEXAS GAS FACILITIES. THE INCIDENT OCCURRED IN A FIELD DEDICATED TO CROP FARMING WHERE THERE WERE NO DWELLINGS WITHIN THE PIPELINE CORRIDOR. ESTIMATED COST OF REPAIR AND GAS LOSS ARE DEFINED AS FOLLOWS: GAS LOSS: $305,000, MATERIAL $4,000, LABOR $3,000, EQUIPMENT $750, X-RAY $600, TOTAL COST OF DAMAGE AND REPAIR - 312,750. AFTER THE IN-SERVICE FAILURE DESCRIBED ABOVE, COMPANY PERSONNEL HYDROSTATICALLY RETESTED TWO BLOCK VALVE SECTIONS (APPROX. 20 MILES) OF THE LINE PIPE DOWNSTREAM OF THE KENTON COMPRESSOR STATION. ONE TEST FAILURE OCCURRED WHICH WAS ATTRIBUTED TO STRESS CORROSION CRACKING. THE ENTIRE 20-MILE SEGMENT WAS SUCCESSFULLY RETESTED TO 100% SPECIFIED MINIMUM YIELD STRENGTH BY OCTOBER 18, 1999. PERMANENT REPAIRS AT THE SITE OF THE SERVICE FAILURE CONSISTED OF REPLACEMENT OF APPROXIMATELY 80 OF LINE PIPE. POST-TEST CLEAN-UP ACTIVITIES ARE UNDERWAY. IT IS ANTICIPATED THE LINE WILL BE RETURNED TO SERVICE WITHIN A WEEK.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990172 | 1999-10-20 | 18152 | SEA ROBIN PIPELINE CO |  |  | LA |  |  |  | 1415 | 1999-09-25 |  | YES | EAST CAMERON BLK | 267 | LA | YES | NO | LEAK |  | 0 | 0 | 200000 | 137930.1321 | 300484.1031 | Null | 1 | 15 |  | 19990925 | 1090 | 1815 | BY CFR 192.619(A)(3) | 1997 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1972 | 20 | 0.438 | API 5LX | 60000 | SUBMERGED ARC |  | UNITED STATES STEEL | 1971 | UNDER WATER |  | CHRIS BRADBERRY, TRANSMISSION SUPERVISOR | 3189375007 | INTERNALLY | LOCALIZED PITTING |  | OTHER | OPERATED AS A WET SYSTEM | COATED | YES | 1972 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | A PINHOLE LEAK WAS DETECTED VISUALLY AS BUBBLES ON THE WATER SURFACE. ISOLATION VALVES WERE CLOSED TO INACTIVATE THE PIPELINE. A REPAIR CLAMP WAS INSTALLED WAS COST OF REPAIRS ONLY.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990173 | 1999-10-28 | 18536 | SOUTHWEST GAS CORP | LAS VEGAS | CLARK | NV |  | SUNSET RD WEST OF DURANGO |  | 856 | 1999-10-05 | 1 | NO |  |  | NV | Null | NO | OTHER |  | 0 | 0 | 182100 | 125585.3853 | 273590.7759 | Null | 0 | 50 | 501339 | 19991005 | 200 | 300 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1958 | 8.625 | 0.188 | API5L-B | 35000 | ERW |  | REPUBLIC STEEL | 1955 | UNDER GROUND |  | PAUL JOHNSON, ENGINEERING SUPERVISOR | 7023652102 | [6 empty] | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 19990927 | YES | PERMANENT MARKERS | YES |  |  | Null |  |  |  | 0 | 0 | WHILE AN OPERATOR WITH ACME ELECTRIC WAS OPERATING A FRONT END LOADER, HE STRUCK AND DAMAGED AN 8" STEEL PSIG GAS MAIN. THE CONTRACTOR DID HAVE A CURRENT USA (ONE CALL) TICKET BUT WAS WORKING OUTSIDE OF THE SPECIFIED AREA. THE GAS MAIN LOCATE WAS CORRECT AND PERMANENT LINE MARKERS WERE VISIBLE. THERE WAS NO IGNITION OF GAS OR INJURIES AS A RESULT OF THE INCIDENT. A TOTAL OF 128,891 THERMS OF GAS LOST. THERE WERE 62 CUSTOMER OUTAGES INCLUDING THE JAMES HARDIE GYPSUM PLANT DUE TO THE DAMAGE. THE JAMES HARDIE GYPSUM PLANT IS MAKING AN ALLEGED LOSS OF PRODUCTION CLAIN OF $141,130.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990174 | 1999-10-27 | 12690 | MONTANA POWER CO | BOULDER | JEFFERSON | MT |  | VALVE #6 @ MP 26.6 | 1404+76.5 | 1015 | 1999-09-20 | 1 | NO |  |  |  | Null | NO | RUPTURE | 1 | 0 | 0 | 114000 | 78620.1753 | 171275.9388 | Null | 1 | 12 | 499423 | 19990920 | 385 | 500 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1962; NMDIA: 4; THK: 0.156; SPEC: API 5L B; SMYS: 35000; SEAM: ERW; MANU: NATIONAL TUBE; MANYR: 1961; LOCLK: ABOVE GROUND; PNAME: JAY WATERMAN, MANAGER TRANS ENGINEERING; PHONE: 4064972441; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PAINTED FENCE POST; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | A SEMI TRACTOR TRAILER RIG ROLLED FROM A TRUCK STOP DOWN AN EMBANKMENT AND INTO THE CITY GATE STATION AT MP 26.6 ON THE MPC 4" EAST HELENA-BOULDER NATURAL GAS TRANSMISSION LINE. THE IMPACT DESTROYED THE GATE STATION BUILDING AND BROKE PIPING INSIDE THE YARD. HIGH PRESSURE GAS BLEW BUT DID NOT IGNITE. THE TOWN OF BOULDER (500 CUSTOMERS) WAS RENDERED OUT OF GAS AND HAD TO BE RELIT. NO INJURIES OCCURRED.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19990179 | 1999-11-16 | 2529 | COASTAL OIL & GAS CORP (SUBSIDIARY OF ANR PROD CO) |  |  | TX |  | X=3,788,174.10 | Y=100,632.56 | 1345 | 1999-10-16 |  | YES |  |  | TX | Null | NO | LEAK |  | 0 | 0 | 74287 | 51232.0786 | 111610.3128 | Null | 0 | 0 | 505595 | 19991016 | 980 | 1440 | BY TEST | 2290 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: GATHERING SYSTEM; PRTFL: FITTING; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1999; NMDIA: 12; THK: 0.562; SPEC: API 5LX; SMYS: 35000; LOCLK: UNDER WATER; PNAME: JOHN P LUCIDO; PHONE: 3134967115; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | FITTING WAS NOT PROPERLY TIGHTENED AT THE NEW PIPELINE TIE-IN
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 19990190 | 1999-11-30 | 994 | WILLIAM FIELD SERVICES | JOHNSON BAYOU | CAMERON | LA | 70631- | 14.2 | 233+14 | 1715 | 1999-10-27 | 1 | NO |  |  | LA | Null | NO | LEAK |  | 0 | 0 | 250000 | 172412.6652 | 375605.1289 | Null | 9 | 0 | 503884 | 19991027 | 870 | 1440 | BY TEST | 1855 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | WELD |  | STEEL |  | PIPELINE |  | 1977 | 24 | 0.406 | API 5L | 60000 | SEAMLESS |  | NATIONAL TUBE | 1977 | OTHER | MARSH AREA | CHRIS MASON | 7132153022 | INTERNALLY | LOCALIZED PITTING |  | OTHER | BACTERIAL | COATED | YES | 1977 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | LEAK WAS CAUSED BY INTERNAL BACTERIAL CORROSION AT THE 5:30 POSITION.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 19990191 | 1999-11-30 | 994 | WILLIAM FIELD SERVICES |  |  | TX |  | 24.23 |  | 1730 | 1999-10-26 |  | YES | MATAGORDA | 669B | TX | Null | Null | LEAK |  | 0 | 0 | 60000 | 41379.0396 | 90145.2309 | Null | 0 | 0 |  | 19991101 | 850 | 1250 | BY TEST | 3269 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: GATHERING SYSTEM; PRTFL: VALVE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1985; SMYS: 0; VALVE: ANSI 900 BELL VALVE; MANU: GROVE; MANYR: 1985; LOCLK: UNDER WATER; PNAME: CHRIS MASON; PHONE: 7132153022; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CAULC: MATERIAL; CAULO: THREADS ON VALVE BODY BLEED SCREW FAILED; CTEST: YES; MED: WATER; TMPS: 8; LKPS: 3269 | A 12" VALVE BODY BLEED ORIFICE HAD BEGUN TO LEAK AS A RESULT OF FLATTENED THREADS ON THE ORIFICE SCREW. THE AFFECTED VALVE WAS 12" TAP VALVE. THE VALVE BODY ORIFICE THREADS WERE RE-DRILLED TO ACCEPT A LARGER 3/4" SCREW TO SECURE THE ORIFICE FROM LEAKING.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990195 | 1999-12-06 | 26330 | ENOGEX INC (EX. MUSTANG FUEL CORP) |  | BRYAN | OK |  | BENNINGTON COMPRESSOR STA |  | 700 | 1999-11-03 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 73000 | 50344.4982 | 109676.6976 | Null | 0 | 15 |  | 19991104 | 940 | 1000 | BY TEST | 1700 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: VALVE; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1997; SMYS: 0; VALVE: ANSI; MANU: ROCKWELL/BETTIS; MANYR: 1996; LOCLK: ABOVE GROUND; PNAME: ERIC R SPERLING; PHONE: 4055257788; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | DIAPHRAM RUPTURE DUE TO WEATHER FATIGUE CAUSED DUMP VALVE FAILURE ON ESD VENT VALVE, CAUSING ESD VENT TO OPEN AND RELEASE GAS.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990196 | 1999-12-02 | 1541 | BP EXPLORATION ( ALASKA), INC | NORTH SLOPE |  | AK |  | 479+96.6 |  | 1950 | 1999-11-13 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 100000 | 68965.0661 | 150242.0516 | Null | 0 | 30 |  | 19991115 | 1200 | 3440 | BY TEST | 4300 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | TRANSMISSION SYSTEM | WELD |  | STEEL |  | PIPELINE |  | 1998 | 6 | 0.375 | API 5L | 65000 | SEAMLESS |  | NIPPON STEEL | 1997 | ABOVE GROUND |  | LES OWEN, TECHNICAL & REGULATORY | 9075645586 | [6 empty] | Null | 0 |  |  | Null |  | Null |  | Null | CONSTRUCTION | CRACK IN GIRTH WELD - CAUSE UNKNOWN AT THIS TIME | YES | 19980713 | WATER |  | 8 | 4300 | CRACK IN A GIRTH WELD. A FAILURE ANALYSIS WILL BE PERFORMED ON WELD TO DETERMINE CAUSE. SUPPLEMENTAL INFO:WIND INDUCED VIBRATION OF THE ELEVATED PIPELINE CREATED HIG CYCLIC STRESSES CAUSING A FATIGUE FAILURE OF A GIRTH WELD. THE WIND INDUCED VIBRATION WAS OF THE SECOND MODE, ONE THOUGHT TO EXIST BUT HAD NEVER BEEN WITNESSED ON NORTH SLOPE ALASKA PIPELINES. A COPY OF THE COMPLETE FAILURE ANALYSIS HAS BEEN ENCLOSED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990197 | 1999-12-07 | 630 | ARKANSAS WESTERN GAS CO | FARMINGTON | WASHINGTON | AR | 72730- |  |  | 815 | 1999-11-17 | 2 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 90000 | 62068.5595 | 135217.8464 | Null | 0 | 30 | 506063 | 19991117 | 250 | 720 | BY TEST | 1080 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1964; NMDIA: 4; THK: 0.156; SPEC: API-5L GRADE; SMYS: 30000; SEAM: ERW; LOCLK: UNDER GROUND; PNAME: JOHN R KEHN, JR; PHONE: 5015215400; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: SIGNS; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | A THIRD PARTY CONTRACTOR WAS CUTTING IN A NEW SUBDIVISION STREET WITH A LARGE EARTH MOVER WHEN IT SEVERED A 4 1/2" STEEL TRANSMISSION LINE. THE GAS IGNITED SEVERELY DAMAGING THE EARTH MOVER.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19990200 | 1999-12-14 | 13750 | NORTHERN NATURAL GAS CO (ENRON) | OELWEIN | FAYETTE | IA | 50662- | 18.00 |  | 1825 | 1999-11-11 | 1 | NO |  |  |  | Null | NO | RUPTURE | 6 | 1 | 1 | 145184 | 100126.2415 | 218127.4201 | Null | 0 | 20 | 505495 | 19991111 | 700 | 960 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1961; NMDIA: 10; THK: 0.203; SPEC: API 5LX; SMYS: 52000; LOCLK: UNDER GROUND; PNAME: PATRICK L VAUGHAN SR, PROJECT ENGINEER; PHONE: 7136467346; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19991108; MARK: NO; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | TILLING CONTRACTOR CHANGED PLANS WITHOUT SUBMITTING NEW LOCATE REQUEST OR NOTIFYING NNG. CONTRACTOR HIT LINE WITH TILLING PLOW.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 19990201 | 1999-12-15 | 14210 | OKLAHOMA NATURAL GAS CO | TALIHINA | LE FLORE | OK | 7 4575 |  |  | 1005 | 1999-11-11 | 3 | NO |  |  |  | Null | NO | OTHER |  | 0 | 1 | 0 | 0 | 0 | Null | 3 | 55 | 505500 | 19991111 | 830 | 960 | BY TEST | 1880 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1973; NMDIA: 8; THK: 0.188; SPEC: API56-X42; SMYS: 42000; SEAM: EW; LOCLK: UNDER GROUND; PNAME: LINDSAY BARNES, ENGINEER I; PHONE: 9188318389; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | Landowner/developer cut the line while excavating. The operator broke his leg by jumping off the dozer and was subsequently hospitalized.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990205 | 1999-12-22 | 15007 | PACIFIC GAS & ELECTRIC CO |  | COLUSA | CA | 95932- | MP 10.94 |  | 1406 | 1999-11-11 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 103000 | 71034.0181 | 154749.3131 | Null | 1 | 27 | 507411 | 19991201 | 676 | 800 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1955; NMDIA: 12; THK: 0.219; SPEC: API 5L GR X-42; SMYS: 42000; SEAM: ERW; LOCLK: UNDER GROUND; PNAME: SHAN BHATTACHARYA; PHONE: 4159736998; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | OUR INVESTIGATION DISCLOSED THAT APPROXIMATELY 1406 HOURS ON NOVEMBER 11, 1999, A RECLAMATION DISTRICT NUMBER 1004 EQUIPMENT OPERATOR HIT A 12-INCH STEEL NATURAL GAS TRANSMISSION PIPELINE NEAR THE INTERSECTION OF GRIDLEY AND BUTLER ROAD, ALLOWING GAS TO ESCAPE. THERE WAS NO REQUEST TO LOCATE AND MARK OUR FACILITIES. WE WERE NOTIFIED OF THIS INCIDENT AT 1415 HOURS BY THE COLUSA COUNTY SHERIFFS DEPARTMENT AND IMMEDIATELY DISPATCHED PERSONNEL TO THE SCENE. COMPANY PERSONNEL ARRIVED ON THE SCENE AT 1515 HOURS. THE FLOW OF GAS WAS CONTROLLED AT 1533 HOURS BY CLOSING VALVES. PERMANANET REPAIRS WERE COMPLETED AT 2010 HOURS ON NOVEMBER 13, 1999. THERE WAS NO INTERRUPTION OF SERVICE TO CUSTOMERS. THERE WERE NO INJURIES OR FATALITIES AS A RESULT OF THIS INCIDENT. DAMAGE TO COMPANY PROPERTY IS ESTIMATED TO BE $103,000; THERE WAS NO THIRD PARTY PROPERTY DAMAGE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 19990206 | 1999-12-13 | 15105 | PANHANDLE EASTERN PIPELINE CO |  | MIAMI | KS | 6 6053 | 2.5/BET STATION & GATE | 130+67 | 245 | 1999-11-09 | 1 | NO |  |  | KS | Null | NO | RUPTURE |  | 0 | 0 | 300000 | 206895.1982 | 450726.1547 | Null | 0 | 50 | 505133 | 19991109 | 788 | 800 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1937 | 24 | 0.281 |  | 48000 | SMLS |  | NATIONAL TUBE | 1937 | UNDER GROUND |  | MARVIN HOVIS, SR ENGINEER | 7139897473 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1957 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | FAILURE IN AREA OF GENERAL CORROSION.
2021-02-26 10:36 | YES | YES |  | 19990207 | 1999-12-13 | 15007 | PACIFIC GAS & ELECTRIC CO | BERKELEY | ALAMEDA | CA | 94704- |  |  | 1423 | 1999-11-24 | 4 | NO |  |  |  | Null | NO | OTHER |  | 1 | 1 | 0 | 0 | 0 | Null | 0 | 10 | 506839 | 19991124 | 0.25 | 0.25 |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTFL: NO DATA; MLKD: NO DATA; SMYS: 0; LOCLK: OTHER; LOCLO: CUSTOMER FACILITY; PNAME: SHAN BHATTACHARYA; PHONE: 4159736998; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000004 | 2000-01-04 | 20230 | KOCH GATEWAY PIPELINE CO | COLLINS | COVINGTON | MS |  | 55.8 | 2946+24 | 1430 | 1999-12-09 | 3 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 120000 | 82758.0793 | 180290.4619 | Null | 0 | 0 | 508490 | 19991209 | 150 | 417 | BY TEST | 468 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1931 | 8 | 0.188 | API5L | 24000 | FURNACE LAP WELD |  | UNKNOWN |  | UNDER PAVEMENT |  | WAYNE F ST GERMAIN | 3189887102 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1942 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | SMALL EXTERNAL CORROSION PIT LEAKING IN CASING UNDER ROAD. RELEASE DID NOT CAUSE A THREAT TO PUBLIC SAFETY BUT WAS REPORTED DUE TO REPAIR COST EXCEEDING $50,000 REPORTING LIMIT.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000007 | 2000-01-10 | 19136 | TEJAS GAS OPERATING LLC | HEBRONVILLE | THOMPSONVILLE | TX | 7 8361 |  | 21+16 | 1345 | 1999-12-18 | 1 | NO |  |  |  | Null | NO | RUPTURE | 0.25 | 0 | 0 | 200000 | 137930.1321 | 300484.1031 | Null | 15 | 0 |  | 19991218 | 890 | 1321 | BY TEST | 1795 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1986; NMDIA: 18; THK: 0.25; SPEC: X-65; SMYS: 65000; SEAM: ERW; MANU: STUPP; MANYR: 1986; LOCLK: UNDER GROUND; PNAME: FRED L DENNIS; PHONE: 7132303175; PROT: Null; CPYR: 0; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | TEXAS ONE CALL LAW PROCEDURES NOT FOLLOWED BY CONTRACTOR. SEE ATTACHEMENT "A"
2021-02-26 10:36 | YES | YES | GG (Gas Gathering) | 20000011 | 2000-01-20 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | WHITEWATER | GRAND TRAVERSE | MI |  |  |  | 2155 | 2000-01-01 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 2 | 2000 | 1351.5385 | 2944.359 | Null | 1 | 55 | 515947 | 20000101 | 6500 | 1440 | BY TEST | 27990 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1973 | 6 | 0.219 | API 5LX GRX46 | 3040 | ERW |  |  |  | UNDER GROUND |  | THOMAS P FUNTSCH | 3135777026 | INTERNALLY | LOCALIZED PITTING |  | OTHER | UNDER DEPOSIT CORROSION | COATED | YES | 1973 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | TWO SNOWMOBILERS IN THE PIPELINE RIGHT OF WAY HAD MECHINCAL PROBLEMS. THEY WERE USING A CIGARETTE LIGHTER TO SEE WITH. WE HAVENT BEEN ABLE TO DETERMINE IF GASOLINE VAPOR OR LEAKING NATURAL GAS FIRST IGNITED CAUSING THE INJURIES. BOTH WERE TREATED AND RELEASED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000012 | 2000-01-20 | 31202 | RELIANT ENERGY - ARKLA | BUFFALO VALLEY | LATIMER | OK |  |  | 636+54 | 1946 | 1999-12-22 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 80000 | 55172.0529 | 120193.6412 | Null | 0 | 0 | 515184 | 19991222 | 870 | 1000 | BY TEST | 1414 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1990; NMDIA: 42; THK: 0.469; SMYS: 65000; SEAM: DSAW; MANYR: 1990; LOCLK: UNDER GROUND; PNAME: TED VANDE KAMP, PIPELINE TECHNICAL LEADER; PHONE: 3184293606; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CAULC: CONSTRUCTION; CTEST: YES; TESTD: 19900924; MED: WATER; TMPS: 8; LKPS: 1414 | PIPE SETTING ON ROCK LEDGE, WHICH CAUSED DENT AND PUNCTURE IN PIPE. NO CORROSION FOUND. SMALL LEAK LOCATED, NO DAMAGE TO PROPERTY EXCEPT PIPELINE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000013 | 2000-01-20 | 15007 | PACIFIC GAS & ELECTRIC CO | AROMAS | SAN BENITO | CA | 9 5004 | 2.20 |  | 830 | 1999-12-20 | 1 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 122000 | 84137.3806 | 183295.3029 | Null | 1 | 41 | 509538 | 19991220 | 380 | 400 | BY TEST | 9000 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1965; NMDIA: 16; THK: 0.25; SPEC: API 5L; SMYS: 35000; SEAM: SSAW; LOCLK: UNDER PAVEMENT; PNAME: SHAN BHATTACHARYA; PHONE: 4159736999; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 19991214; MARK: YES; MRKTP: PIPELINE MARKERS; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20000019 | 2000-02-02 | 19160 | TENNESSEE GAS PIPELINE CO | MARLBOROUGH | MIDDLESEX | MA | 1752 | 269-2+0.00 | 0+00 | 445 | 2000-01-24 | 2 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 0 | 0 | 0 | Null | 0 | 0 | 517700 | 20000125 | 680 | 750 | BY TEST | 1396 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: NO FAILURE; MLKD: STEEL; PRTSY: OTHER; PRTSO: VALVE OPERATOR; PRTYR: 1968; NMDIA: 24; SMYS: 0; VALVE: BALL; MANU: WKM; MANYR: 1967; LOCLK: NO DATA; PNAME: DARON K MOORE,; PHONE: 7134204023; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | MAIN LINE VALVE DID NOT FULLY CLOSE CAUSING OPERATOR TO VENT TO ATMOSPHERE, RESULTING IN LOCAL AUTHORITIES EVACUATING NEARBY VICINITY.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 20000021 | 2000-02-07 | 7605 | HOUSTON PIPELINE CO | GEORGE WEST | LIVE OAK | TX |  |  |  | 930 | 1999-12-10 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 2 | 0 | 0 | 0 | Null | 0 | 1 | 508805 | 19991210 | 0 | 770 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: NO DATA; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1959; NMDIA: 12; THK: 0.312; SPEC: X-42; SMYS: 42000; SEAM: ERW; LOCLK: OTHER; LOCLO: IN EXCAVATION; PNAME: DAVID J. TONSALL; PHONE: 7136466389; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | THE UNKNOWN ACCUMULATION OF LIQUID FUMES IN THE TRENCH AREA. IGNITED BY WELDERS CUTTING TORCH.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000022 | 2000-02-07 | 13750 | NORTHERN NATURAL GAS CO (ENRON) |  |  | TX |  |  |  | 1730 | 1999-12-31 |  | YES | MUSTANG | 762 | TX | Null | NO | LEAK |  | 0 | 0 | 100000 | 68965.0661 | 150242.0516 | Null | 0 | 0 | 515880 | 19991231 | 950 | 1440 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | INTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1984; NMDIA: 12; THK: 0.438; SPEC: API 5L; SMYS: 35000; LOCLK: UNDER WATER; PNAME: MERLIN MOSEMAN; PHONE: 7136467344; LOC: INTERNALLY; COAT: COATED; PROT: YES; CPYR: 1984; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20000023 | 2000-02-08 | 2616 | COLUMBIA GAS TRANSMISSION CORP | BETHLEHEM | HUNTERDON | NJ | 8803 |  | 928+42 | 900 | 2000-01-11 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 70000 | 47303.8462 | 103052.5641 | Null | 0 | 5 | 516665 | 20000111 | 840 | 1200 | BY TEST | 1883 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1990 | 20 | 0.375 | API 5LX | 65000 | ERW |  | STUPP | 1990 | UNDER GROUND |  | STEVEN P BURNLEY | 3043573575 | [6 empty] | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 19991202 | YES | YELLOW FLAGS | YES |  |  | Null |  |  |  | 0 | 0 | WHILE DRIVING A PIECE OF PIPE IN THE GROUND TO ANCHOR A DRILLING MACHINE, A CONTRACTOR PUNCTURED THE PIPELINE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000037 | 2000-02-22 | 19160 | TENNESSEE GAS PIPELINE CO | WEST MONROE | OUACHITA | LA |  | 46-1+0.00 |  | 2230 | 2000-02-01 | 1 | NO |  |  |  | Null | NO | RUPTURE | 5 | 0 | 0 | 190000 | 128396.1538 | 279714.1026 | Null | 1 | 12 | 518468 | 20000201 | 615 | 625 | BY CFR 192.619(A)(3) |  | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; PRTFO: GIRTH; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1944; NMDIA: 24; THK: 0.375; SPEC: API 5LX; SMYS: 45000; MANU: NATIONAL TUBE; MANYR: 1944; LOCLK: UNDER GROUND; PNAME: LOUIS A SALINAS; PHONE: 7134202781; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CAULC: CONSTRUCTION; CTEST: NO; TMPS: 0; LKPS: 0 | APPARENT FAILURE IN A WELD.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20000038 | 2000-02-25 | 31202 | RELIANT ENERGY - ARKLA | BLANCHARD |  | LA |  |  | 398+60 | 755 | 2000-01-27 | 2 | NO |  |  |  | Null | NO | RUPTURE | 2 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 50 | 517943 | 20000127 | 370 | 450 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | EXTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1920; NMDIA: 20; THK: 0.312; SMYS: 24000; LOCLK: UNDER WATER; PNAME: TED VANDE KAMP PIPELINE TECHNICAL LEADER; PHONE: 3184293606; LOC: EXTERNALLY; ADESC: GENERAL CORROSION; CAUCR: OTHER; CAUCO: EROSION/CORROSION; COAT: COATED; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | PIPE FAILED IN BOTTOM OF SMALL CREEK, INITAL EVALUATION APPEARS THAT ERROSION CORR. CAUSED GENERAL THINNING OF THE PIPE WALL ON TOP.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000039 | 2000-02-28 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | GOODRICH | POLK | TX |  | MILE 312 G.C. #2 LINE | 16452+37 | 306 | 2000-02-02 | 1 | NO |  |  |  | Null | NO | RUPTURE | 40 | 0 | 0 | 129000 | 87174.2308 | 189911.1538 | Null | 0 | 30 |  | 20000202 | 842 | 858 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1962 | 30 | 0.298 | 5LX | 60000 |  |  | AO SMITH | 1962 | UNDER GROUND |  | DENNIS JOHNSON (SENIOR STANDARD ENGINEER) | 3039147754 | EXTERNALLY | LOCALIZED PITTING |  | OTHER | UNDEFINED | COATED | YES | 1962 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | INTERACTION OF SOIL ENVIRONMENT PIPE MATERIAL AND OPERATING CONDITIONS
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000044 | 2000-02-29 | 19160 | TENNESSEE GAS PIPELINE CO | MARCELLUS | ONONDAGA | NY | 1 3084 | 240-1+1.87 | 1.87 | 1630 | 2000-02-18 | 2 | NO |  |  |  | Null | NO | LEAK | 5 | 0 | 0 | 100000 | 67576.9231 | 147217.9487 | Null | 0 | 0 | 520444 | 20000218 | 520 | 878 | BY TEST | 1157 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1951 | 24 | 0.281 | API 5L | 52000 | SEAMLESS |  | AO SMITH | 1951 | UNDER GROUND |  | MY LINH LAUD (SENIOR COMPLIANCE ENGINEER) | 7134204523 | [6 empty] | Null | 0 |  |  | Null |  | Null |  | Null | MATERIAL |  | YES | 19680519 | WATER |  | 24 | 1157 | CRACK IN PIPE WALL DUE TO MANUFACTURING DEFECT (DETERMINED AFTER EXCAVATION).
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000045 | 2000-03-10 | 2714 | CNG TRANSMISSION CORP | KINGSVILLE | CLARION | PA |  |  | 120+45 | 1550 | 2000-02-11 | 1 | NO |  |  | PA | Null | NO | LEAK |  | 0 | 0 | 75000 | 50682.6923 | 110413.4615 | Null | 2 | 25 |  | 20000211 | 609 | 713 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1947; NMDIA: 14; THK: 0.375; SPEC: GRADE B; SMYS: 35000; SEAM: SEAMLESS; MANU: J&L STEEL; LOCLK: UNDER GROUND; PNAME: MARTIN C SCHWOEBLE; PHONE: 3046238408; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | ON FRIDAY, FEBRUARY 11, 2000, CNG TRANSMISSION PIPELINE LN-200 WAS STRUCK BY A CONTRACTORS DOZER WORKING FOR TEXAS KEYSTONE, INC WHILE EXCAVATING A DRAINAGE POND/PIT FOR A NEW PRODUCTION WELL. TEXAS KEYSTONE PLACED A ONE-CALL NOTICE AFTER THE INCIDENT BUT NO PRIOR NOTICATION PERTAINING TO THE SUBJECT EXCAVATION SITE WAS MADE ANY TIME IN ADVANCE OF THE PLANNED EXCAVATION AS REQUIRED BY ACT 287.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20000046 | 2000-03-06 | 11680 | TXU LONE STAR PIPELINE | DEW | FREESTONE | TX |  | LINE L8A 3RD | 1189+49 | 730 | 2000-02-05 | 1 | NO |  |  | TX | Null | NO | LEAK |  | 0 | 0 | 50000 | 33788.4615 | 73608.9744 | Null | 2 | 30 | 518851 | 20000205 | 426 | 500 | BY TEST | 550 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1958; NMDIA: 16; THK: 0.281; SPEC: API 5LX; SMYS: 30000; SEAM: LAP WELD; LOCLK: UNDER GROUND; PNAME: ZORA RAOUFPOUR; PHONE: 2148753889; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | FAILED PORTION OF PIPE WAS SENT TO LAB FOR ANALYSIS TO IDENTIFY ROOT CAUSE OF FAILURE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000055 | 2000-03-16 | 11680 | TXU LONE STAR PIPELINE | BOYD | WISE | TX |  | MM4 | 192+87 193+64 | 2330 | 2000-01-27 | 1 | NO |  |  | TX | Null | NO | RUPTURE | 770000 | 0 | 0 | 130000 | 87850 | 191383.3333 | Null | 1 | 10 |  | 20000128 | 6400 | 8000 | BY TEST | 10000 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1960; NMDIA: 20; THK: 0.25; SPEC: API 5L; SMYS: 46000; SEAM: SEAMLESS; LOCLK: UNDER GROUND; PNAME: DAN FOX; PHONE: 2148752227; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | FAILED PORTION OF PIPE SENT TO LAB FOR ANALYSIS TO IDENTIFY ROOT CAUSE OF FAILURE. THIRD PARTY CONTRACTOR WAS WORKING IN PIPELINE RIGHT OF WAY BUT IT IS NOT KNOWN IF THIS IS A CONTRIBUTING FACTOR AT THIS TIME. SUPPLEMENTAL INFORMATION : METALLURGICAL TESTING CONCLUDED THAT FAILURE WAS RESULT OF RECENT MECHANICAL DAMAGE BY OUTSIDE FORCE. SOURCE OF DAMAGE IS UNKNOWN.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000057 | 2000-03-14 | 5304 | FLORIDA GAS TRANSMISSION CO (ENRON) | MELBOURNE | BREVARD | FL |  | 728.586 |  | 1900 | 2000-01-29 | 1 | NO |  |  |  | Null | NO | RUPTURE | 50 | 0 | 0 | 263000 | 177727.3077 | 387183.2051 | Null | 0 | 25 |  | 20000129 | 908 | 936 |  |  | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | WELD |  | STEEL |  | PIPELINE |  | 1959 | 20 | 0.25 | API-5LX | 52000 | ERW |  | YOUNGSTOWN |  | UNDER GROUND |  | MERLIN MOSEMAN | 7136467344 | EXTERNALLY | LOCALIZED PITTING |  | OTHER | MIC | COATED | YES | 1959 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000058 | 2000-03-13 | 405 | ANR PIPELINE CO |  | CLARE | MI |  |  | 20+41 | 530 | 2000-02-23 | 1 | NO |  |  |  | Null | Null | RUPTURE | 12 | 0 | 0 | 297000 | 200703.4615 | 437237.3077 | Null | 1 | 0 |  | 20000223 | 551 | 870 |  | 1362 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | TEMPERATURE | PRTLK: TRANSMISSION SYSTEM; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1951; NMDIA: 12; THK: 0.25; SMYS: 35000; MANU: AO SMITH; MANYR: 1951; LOCLK: UNDER GROUND; PNAME: DON CROSS; PHONE: 3134967115; PROT: Null; CPYR: 0; CAULK: EARTH MOVEMENT: FROST; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | THERE WERE SEVERAL MECHANISMS, COMBINED, THAT CONTRIBUTED TO THE RUPTURE OF THE 12" LINCOLN PIPELINE. THE CONTRIBUTING FACTORS WERE: FROST HEAVE; MISMATCH OF PIPE ENDS DUE TO HIGH-LOW DURING TIE-IN OF A 15-FOOT REPLACEMENT IN 1993 (NOTE: THE HIGH-LOW WAS WITHIN ACCEPTABLE LIMITS IMPOSED BY SECTION 6.3.2 OF API STANDARD 1104 AT THE TIME OF REPLACEMENT).; RESIDUAL FORCES APPLIED DURING CLAMPING OF THE PIPE REPLACEMENT ENDS TO THE EXISTING PIPELINE; UNUSUALLY COLD CLIMATE ON THE DAY OF THE RUPTURE; AND NON-HOMOGENEOUS MATERIAL IN THE WELD METAL AT THE ORIGIN OF THE FRACTURE THAT REDUCED EFFECTIVE WALL THICKNESS (NONFUSION/SLAG), BUT WAS WITHIN API STANDARD 1104 ACCEPTANCE CRITERIA.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000062 | 2000-03-21 | 18532 | SOUTHERN UNION GAS CO | ELPASO | EL PASO | TX | 7 9227 | LOOP 375 VISTA DEL SOL |  | 1054 | 2000-02-18 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 79000 | 53385.7692 | 116302.1795 | Null | 0 | 45 | 520406 | 20000218 | 300 | 363 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1941; NMDIA: 16; THK: 0.219; SPEC: 5LX-42; SMYS: 1152; LOCLK: UNDER GROUND; PNAME: RAYMOMD GONZALEZ; PHONE: 9156808219; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: AERIAL MARKER; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | THIRD PARTY CONTRACTOR EXVACATING FOR DRAINAGE IMPROVEMENTS RELATED TO DEVELOPMENT OF COMMERCIAL PROPERTY FAILED TO CALL FOR UTILITY LOCATIONS PRIOR TO EXCAVATING. EQUIPMENT STRUCK AND DAMAGED 16" WRAPPED STEEL GAS MAIN CAUSING LEAKAGE. ISOLATION OF MAIN BY CLOSING MAIN LINE VALVES MITIGATED LEAKAGE. DAMAGE TEMPORARY REPAIRED WITH A WELD SLEEVE. DAMAGED SECTION OF PIPE WILL BE REMOVED AND REPLACED WITH NEW PIPE AS PERMANENT REPAIR.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000063 | 2000-03-21 | 19160 | TENNESSEE GAS PIPELINE CO | ULYSSES | POTTER | PA |  | 10.2 | 538+56 | 438 | 2000-02-27 | 1 | NO |  |  |  | Null | NO | RUPTURE | 300 | 0 | 0 | 143000 | 96635 | 210521.6667 | Null | 0 | 40 | 521265 | 20000220 | 1150 | 1170 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1955 | 24 | 0.375 | API 5LX | 52000 | SEAMLESS |  | NATIONAL TUBE | 1955 | UNDER GROUND |  | DARON MOORE | 7134204023 | EXTERNALLY | OTHER | STRESS CORROSION CRACKING | OTHER | STRESS CORROSION | COATED | YES | 1955 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | STRESS CORROSION CRACKING AUGMENTED BY A BEND IN THE PIPE.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 20000069 | 2000-03-27 | 30940 | WILLIAMS ENERGY GROUP-FIELD SERVICES | JOHNSON BAYOU | CAMERON | LA | 70631- | 14.2 | 233+14 | 1330 | 2000-02-23 | 1 | NO |  |  | LA | Null | NO | LEAK |  | 0 | 0 | 120000 | 81092.3077 | 176661.5385 | Null | 15 | 5 | 520905 | 20000223 | 870 | 1440 | BY TEST | 1855 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | WELD | GIRTH | STEEL |  | PIPELINE |  | 1977 | 24 | 0.406 | API 5L | 60000 | SEAMLESS |  | NATIONAL TUBE | 1977 | OTHER | MARSH AREA | CHRIS MASON | 7132153022 | INTERNALLY | LOCALIZED PITTING |  | OTHER | BACTERIAL | COATED | YES | 1977 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | LEAK WAS CAUSED BY INTERNAL BACTERIAL CORROSION AT THE 5:30 POSITION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20000072 | 2000-04-06 | 11680 | TXU LONE STAR PIPELINE | SWEETWATER | NOLAN | TX |  | 9885+45 | 9878+10 | 1435 | 2000-02-25 | 1 | NO |  |  | TX | Null | NO | OTHER |  | 0 | 0 | 50000 | 33788.4615 | 73608.9744 | Null | 2 | 0 |  | 20000225 | 556 | 800 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1964; NMDIA: 16; THK: 0.219; SPEC: API5LX; SMYS: 42000; SEAM: SEAMLESS; LOCLK: UNDER GROUND; PNAME: DAN FOX; PHONE: 2148752227; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 20000217; MARK: NO; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000074 | 2000-04-17 | 20230 | KOCH GATEWAY PIPELINE CO | MT OLIVE | COVINGTON | MS |  | 88.5 | 276+96 | 830 | 2000-03-16 | 2 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 110000 | 74334.6154 | 161939.7436 | Null | 0 | 0 | 523107 | 20000316 | 350 | 430 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1930; NMDIA: 16; THK: 0.25; SPEC: API5L; SMYS: 33000; SEAM: ELECTRIC FLASH WELD; MANU: UNKNOWN; LOCLK: UNDER PAVEMENT; PNAME: WAYNE F ST GERMAIN; PHONE: 3379887102; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | VERY SMALL RELEASE WAS DETECTED USING LEAK DETECTION EQUIPMENT. BECAUSE OF THE PROXIMITY OF THE RELEASE TO A ROAD, A NEW CROSSING IS REQUIRED TO MAKE THE REPAIR. RELEASE DID NOT CAUSE A THREAT TO PUBLIC SAFETY BUT WAS REPORTED DUE TO COST EXCEEDING $50,000 REPORTING THRESHOLD.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000075 | 2000-04-14 | 20230 | KOCH GATEWAY PIPELINE CO | VICKSBURG | WARREN | MS | 3 9180 | 82.90 | 4377+13 | 1545 | 2000-03-15 | 2 | NO |  |  |  | Null | NO | LEAK | 0 | 0 | 0 | 130000 | 87850 | 191383.3333 | Null | 0 | 0 | 523063 | 20000315 | 345 | 475 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1939; NMDIA: 18; THK: 0.25; SPEC: API5L; SMYS: 35000; SEAM: ELECTRIC FLASH WELD; MANU: UNKNOWN; LOCLK: UNDER PAVEMENT; PNAME: WAYNE F ST GERMAIN; PHONE: 3379887102; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | VERY SMALL RELEASE WAS DETECTED USING LEAK DETECTION EQUIPMENT. BECAUSE OF THE PROXIMITY OF THE RELEASE TO ROAD, A NEW CROSSING IS REQUIRED TO MAKE THE REPAIR. RELEASE DID NOT CAUSE A THREAT TO PUBLIC SAFETY BUT WAS REPORTED DUE TO REPAIR COST EXCEEDING $50,000 REPORTING THRESHOLD.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000076 | 2000-04-07 | 18536 | SOUTHWEST GAS CORP | HENDERSON | CLARK | NV | 8 9014 | ARROYO GRANDE/PITTMAN WAS |  | 1505 | 2000-03-08 | 3 | NO |  |  | NV | Null | NO | OTHER |  | 0 | 0 | 76170 | 51473.3423 | 112135.9115 | Null | 1 | 28 | 522377 | 20000308 | 300 | 400 | BY TEST | 1180 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1956 | 16 | 0.25 | API5L-X52 | 52000 | ERW |  | LONE STAR | 1956 | UNDER GROUND |  | ANTHONY HILLS | 7023652098 | [6 empty] | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 20000211 | YES | REGULAR LINE LOCATE MARK | YES |  |  | Null |  |  |  | 0 | 0 | WHILE AN OPERATOR WITH M&M CONSTRUCTION WAS GRADING FOR A WALL WITH A D-9 CAT, HE STRUCK AND DAMAGED A 16" STEEL; 300 PSIG GAS MAIN. THE CONTRACTOR DID HAVE A CURRENT USA (ONE CALL) TICKET. THE GAS MAIN LOCATE WAS CORRECT AND PERMANENT LINE MARKERS WERE VISIBLE. THERE WAS NO IGNITION OF GAS OR INJURIES AS A RESULT OF THE INCIDENT. A TOTAL OF 197,141 THERMS OF GAS WAS LOST. THERE WERE 2 CUSTOMER OUTAGES INCLUDING A PARTIAL OUTAGE AT THE SAGUARO POWER PLANT AND PABCO GYSUM PLANT DUE TO THE DAMAGE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000080 | 2000-04-25 | 21031 | PG & E TEXAS PIPELINE, L.P. |  | KARNES | TX | 7 8119 | 48 | 2534+00 | 1415 | 2000-03-22 | 1 | NO |  |  |  | Null | NO | RUPTURE | 200 | 0 | 0 | 360000 | 243276.9231 | 529984.6154 | Null | 0 | 30 | 523850 | 20000322 | 936 | 1045 | BY TEST | 1363 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1962 | 20 | 0.281 |  | 52000 | DSAW |  | MANNESMANN | 1961 | UNDER PAVEMENT |  | KEVIN P SEHY | 2105284206 | EXTERNALLY | LOCALIZED PITTING |  | OTHER | TO BE DETERMINED |  | YES | 1974 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | PG&E TEXAS PIPELINE, LP WAS NOTIFIED THAT A PIPELINE NORTH OF OUR BURNELL COMPRESSOR STATION HAD BLOWN OUT AND WAS ON FIRE. EMPLOYEES VERIFIED THAT THIS WAS OUR EAST SADF 20" (THE SITE OF THE BLOWOUT WAS APPROXIMATELY 8 MILES SOUTH OF KENEDY, TX ON US HWY 181), AND IMMEDIATELY SHUT DOWN COMPRESSOR UNITS AND CLOSED ISOLATION VALVES TO SECURE THE AREA. WORK BEGAN THE SAME DAY, MARCH 22, 2000 TO GET THE ROAD REPAIRS COMPLETED TO US HWY 81 AND THE EAST SADF 20" PIPELINE RETURNED TO SERVICE. THE PIPE FROM THE BLOWOUT IS BEING ANALYZED BY SOUTHWEST RESEARCH TO DETERMINE THE CAUSE OF THE BLOWOUT.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000081 | 2000-04-20 | 20230 | KOCH GATEWAY PIPELINE CO | BASSFIELD | JEFFERSON DAVIS | MS | 3 9421 | MP 14 | 736+26 | 1330 | 2000-03-22 | 2 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 78771 | 53231.0181 | 115965.0504 | Null | 0 | 0 | 523820 | 20000322 | 150 | 430 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1930; NMDIA: 10; THK: 0.25; SPEC: API5L; SMYS: 24000; SEAM: FURNACE LAP WELD; MANU: UNKNOWN; LOCLK: UNDER PAVEMENT; PNAME: RICKY CARLISLE; PHONE: 6015835402; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | MINOR RELEASE UNDER ROAD. RELEASE DID NOT CAUSE A THREAT TO PUBLIC SAFETY BUT WAS REPORTED DUE TO REPAIR COST EXCEEDING $50,000 REPORTING LIMIT.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000082 | 2000-04-28 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | LAKETON | GRAY | OK | 7 9065 | 60 | 15165+18 | 309 | 2000-03-27 | 1 | NO |  |  |  | Null | NO | RUPTURE | 102 | 0 | 0 | 150000 | 101365.3846 | 220826.9231 | Null | 2 | 0 | 524202 | 20000327 | 693 | 720 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | EXTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1972; NMDIA: 26; THK: 0.312; SPEC: X52; SMYS: 1248; LOCLK: UNDER GROUND; PNAME: BERNADETTE M FRIEH; PHONE: 3039147829; LOC: EXTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: OTHER; CAUCO: STRESS CORROSION CRACKING; COAT: COATED; PROT: YES; CPYR: 1972; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | INTERACTION OF SOIL ENVIRONMENT, PIPE MATERIAL AND OPERATING CONDITIONS.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000090 | 2000-05-02 | 15007 | PACIFIC GAS & ELECTRIC CO |  | KERN | CA |  | STATION 3 |  | 1715 | 2000-03-30 | 1 | NO |  |  |  | Null | YES | LEAK |  | 0 | 0 | 200000 | 135153.8462 | 294435.8974 | Null | 2 | 28 | 524643 | 20000330 | 703 | 861 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: VALVE; MLKD: STEEL; PRTSY: REGULATOR/METERING SYSTEM; NMDIA: 0.375; SMYS: 0; LOCLK: ABOVE GROUND; PNAME: SHAN BHATTACHARYA; PHONE: 4159736999; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: SIGN OF FENCE; STAT: NO; CTEST: Null; TMPS: 0; LKPS: 0 | A SEMITRAILER DROVE OFF THE ROAD, KNOCKING DOWN THE CHAIN LINK FENCE SURROUNDING THE STATION. THE TRUCK THEN STRUCK AND DEMOLISHED THE BUILDING THAT HOUSED SCADA CONTROLS FOR PLS 3. A RADIO ANTENNA ON TOP OF THE BUILDING WAS KNOCKED DOWN AND STRUCK THE SENSING LINE TO BLOW OFF VALVE A ON LINE 300-A.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000094 | 2000-05-09 | 405 | ANR PIPELINE CO |  |  | LA |  | X- 1,860,988.96 | Y=-72,751.28 | 913 | 2000-04-24 |  | YES | EUGENE ISLAND BLK | 266F | LA | Null | NO | LEAK |  | 0 | 0 | 79000 | 53385.7692 | 116302.1795 | Null | 0 | 0 | 526947 | 20000424 | 1050 | 1250 | BY TEST | 2690 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1971 | 12 | 0.375 | API5LX | 46000 | ERW |  | A O SMITH | 1971 | UNDER WATER |  | DON CROSS, SR | 3134962460 | INTERNALLY | LOCALIZED PITTING |  | OTHER |  | COATED | YES | 1971 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | SUSPECTED INTERNAL CORROSION - PINHOLE LEAK AT THE 5 OCLOCK POSITION
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000101 | 2000-05-19 | 19160 | TENNESSEE GAS PIPELINE CO |  |  | LA |  | 509A-1201+0.03 | 509A-1200 | 2000 | 2000-04-26 |  | YES | VERMILLION | 261A |  | YES | NO | LEAK |  | 0 | 0 | 150000 | 101365.3846 | 220826.9231 | Null | 0 | 0 | 527237 | 20000426 | 940 | 1728 | BY TEST | 2160 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1979 | 12 | 0.375 | API5LX | 42000 | SEAMLESS |  | US STEEL | 1979 | UNDER WATER |  | MY-LINH LAUD | 7134202496 | INTERNALLY | LOCALIZED PITTING |  | OTHER | INTERNAL | COATED | YES | 1979 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | LEAK UPSTREAM OF CHECK VALVE AT SIX OCLOK POSITION.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 20000106 | 2000-06-06 | 19270 | WILLIAMS GAS PIPELINE - TEXAS GAS | GREENVILLE | WASHINGTON | MS | 3 8701 | MLS,MP 114+0046 |  | 1210 | 2000-05-02 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 6 | 0 | 0 | 0 | Null | 0 | 0 | 527789 | 20000502 |  | 840 |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; MLKD: OTHER; MLKDO: SEE ATTACHMENT; PRTSY: COMPRESSOR STATION; PRTYR: 1949; SMYS: 0; LOCLK: OTHER; PNAME: STEVEN J LAW; PHONE: 2706886954; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | FLASH FIRE ONLY NO FAILURE. ON TUESDAY MAY 2, 2000 AT 12:10 P.M. CENTRAL STANDARD TIME, AN INCIDENT OCCURRED DURING A TURBINE CONSTRUCTION PROJECT AT THE WILLIAMS GAS PIPELINE-SOUTHCENTRAL COMPRESSOR STATION AT GREENVILLE, MS. THE LOCATION OF THE INCIDENT WAS NEAR MILEPOST 114+0046 ON THE COMPANYS MAINLINE SYSTEM PIPELINE IN WASHINGTON COUNTY, MS. A FLASH FIRE OCCURRED WHEN CONTRACTOR EMPLOYEES WERE BEGINNING TO INSTALL AN ISOLATION CAP ON A 26-INCH DIAMETER NATURAL GAS LINE. NO FATALITIES RESULTED FROM THIS EVENT, ALTHOUGH ONE COMPANY EMPLOYEE AND FIVE CONTRACTOR EMPLOYEES WERE INJURED. ALL THE INJURED WERE TRANSPORTED TO DELTA REGIONAL HOSPITAL IN GREENVILLE WHERE THEY WERE LISTED IN STABLE CONDITION AND HAVE CONTINUED TO IMPROVE. THE FIRE OR POLICE DEPARTMENTS WERE NOT DISPATCHED. THE FIRE EXTINGUISHED ITSELF. ALL WILLIAMS GAS PIPELINE-SOUTHCENTRAL FACILITIES WERE IMMEDIATELY SECURE AND THERE WAS NO DANGER TO THE SURROUNDING AREA. THERE WERE NO SERVICE INTERRUPTIONS AS A RESULT OF THE INCIDENT. EVIDENCE AVAILABLE HAS NOT ALLOWED DETERMINATION OF CAUSE AT THIS TIME. THE CAUSE OF THE INCIDENT CONTINUES TO BE INVESTIGATED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000107 | 2000-06-06 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | PITTSBURG | ATOKA | OK | 74560-7002 | LATIMER LINE MILE 42 | BLOCK VALVE:2239+58.8 | 926 | 2000-05-07 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 1950000 | 1317750 | 2870750 | Null | 3 | 0 | 528256 | 20000507 |  |  |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: MOTOR; MLKD: STEEL; PRTSY: OTHER; PRTSO: SERVICE BUILDING; PRTYR: 1991; SMYS: 0; LOCLK: ABOVE GROUND; PNAME: BERNADETTE M FRIEH; PHONE: 3039147829; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | A FIRE OCCURRED IN THE STATIONS SERVICE BUILDING. THE BUILDING WHICH HOUSES THE GENERATORS, AIR COMPRESSORS CONTROL ROOM TECH. SHOP BREAK ROOM OFFICE AND STORAGE AREA WAS HEAVILY DAMAGED. WITH THE EXCEPTION OF THE TWO GENERATORS ALL CONTENTS OF THE BUILDING WERE DESTROYED.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 20000111 | 2000-06-19 | 2616 | COLUMBIA GAS TRANSMISSION CORP | PHELPS | PIKE COUNTY | KY |  |  | 1278+99 | 100 | 2000-05-18 | 1 | NO |  |  | KY | Null | NO | OTHER |  | 1 | 0 | 59800 | 40411 | 88036.3333 | Null | 2 | 0 | 529301 | 20000518 | 275 | 374 | BY TEST | 750 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1999 | 20 | 0.25 | API 5LX | 42000 | ERW |  | U S STEEL | 1999 | OTHER | SURFACE MINING ACTIVITY | PHILLIP ARTHUR | 3043572488 | [6 empty] | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | YES | LINE MARKERS | NO |  |  | Null |  |  |  | 0 | 0 | IN 1999 THIS PIPELINE WAS RELOCATED TO THE CURRENT LOCATION AT THE REQUEST OF THE SURFACE MINING COMPANY. A ROW OF TREES WAS LEFT IN PLACE AS A BUFFER BETWEEN THE MINE AREA AND COLUMBIAS RIGHT-OF-WAY. THE RELOCATION WAS COMPLETED IN NOVEMBER 1999 AND COLUMBIA NOTIFIED THE SURFACE MINING COMPANY THAT THE PIPELINE HAD BEEN RELOCATED, WHERE NEW PIPELINE WAS LOCATED AND WAS IN SERVICE. ON 5/18/00, THERE WAS AN ENROACHMENT ON COLUMBIAS RIGHT-OF WAY BY SURFACE MINING COMPANY. THE SURFACE MINING COMPANY HAD REMOVED THE ROW OF TREES "BUFFER" WITH A LOADER/EXCAVATOR AND STRUCK COLUMBIAS PIPELINE, APPROXIMATELY 50 FEET FROM AN EXISTING PIPELINE MARKER, RESULTING IN THE IGNITION OF NATURAL GAS AND SUBSEQUENT FIRE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000113 | 2000-06-16 | 19235 | TEXAS EASTERN TRANSMISSION CORP (DUKE) |  | PERRY COUNTY | PA | 1 7090 | 138.37 | 7305+93 | 1805 | 2000-05-13 | 1 | NO |  |  | PA | Null | NO | OTHER |  | 0 | 0 | 99000 | 66901.1538 | 145745.7692 | Null | 0 | 0 |  | 20000602 | 996 | 1050 | BY TEST | 2175 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: ESD CONTROLS; MLKD: OTHER; MLKDO: ELECTRONIC COMPONENTS; PRTSY: COMPRESSOR STATION; PRTYR: 1958; SMYS: 0; LOCLK: ABOVE GROUND; PNAME: DWAYNE E TESCHENDORF; PHONE: 7136275573; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | THE EMERGENCY SHUTDOWN DEVICE (ESD) ACTIVATED AT COMPRESSOR STATION BY LIGHTING STRIKE TO COMPRESSOR UNIT GAS MONITOR. ALL EQUIPMENT OPERATED PROPERLY WITH THE EXCEPTION OF A SUCTION VALVE THAT DID NOT CLOSE AUTOMATICALLY. THIS ALLOWED GAS TO CONTINUE VENTING TO ATMOSPHERE IN A CONTROLLED MANNER UNTIL THE VALVE WAS MANUALLY CLOSED (57 MINUTES ELAPSED TIME).
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000117 | 2000-07-05 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) |  |  | TX |  | 26.3 | 1387+76 | 1549 | 2000-06-19 |  | YES |  | 71 |  | YES | NO | LEAK |  | 0 | 0 | 217243 | 146806.135 | 319820.6883 | Null | 0 | 0 | 532694 | 20000619 | 980 | 1200 | BY TEST | 1894 | CORROSION | CORROSION | INTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1973; NMDIA: 16; THK: 0.312; SPEC: API 5LX X52; SMYS: 2028; SEAM: SEAMLESS; MANYR: 1972; LOCLK: UNDER GROUND; PNAME: BERNADETTE M SMITH; PHONE: 3039147829; LOC: INTERNALLY; ADESC: LOCALIZED PITTING; COAT: COATED; PROT: YES; CPYR: 1973; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | A LEAK OCCURRED ON THE ISLAND 16" LATERAL, 18.5 MILES FROM THE BEACH.
2021-02-26 10:36 | NO | NO |  | 20000118 | 2000-07-05 | 21252 | VIKING GAS TRANSMISSION CO | PERHAM | OTTERTAIL | MN | 5 6544 | 2210 | 0+00 | 805 | 2000-06-03 | 1 | NO |  |  | MN | Null | NO | LEAK |  | 0 | 0 | 0 | 0 | 0 | Null | 1 | 0 |  | 20000605 | 800 | 1550 |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTFL: FITTING; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1997; NMDIA: 0.25; SMYS: 0; MANU: SOLAR TURBINES; MANYR: 1997; LOCLK: ABOVE GROUND; PNAME: MARK A MICKELBERG; PHONE: 6512292269; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | ON JUNE 3, 2000 THE WEEKEND DUTY PERSON WAS MAKING ROUNDS PERFORMING ROUTINE INSPECTIONS IN VIKINGS SOLAR CENTAUR GAS TURBINE COMPRESSOR PACKAGE WHEN HE DISCOVERED A 3/8 FITTING ON THE HIGH PRESSURE SEAL OIL LUBE SYSTEM LEAKING. THE STATION DISTRICT FOREMAN AND WEEKEND DUTY PERSON INITIATED A NORMAL SHUTDOWN OF THE UNIT SO REPAIRS COULD BE MADE. AS THE UNIT WAS SHUTTING DOWN THE FITTING BROKE AND OIL SPRAYED ON SOME PART OF THE ENGINE UNIT AND A VAPOR CLOUD STARTED TO APPEAR. THE DISTRICT FOREMAN PUSHED THE FAST STOP ON THE GAS TURBINE UNIT AND EXITED THE BUILDING. THE FIRE IS BELIEVED TO HAVE STARTED WHEN HIGH PRESSURE OIL SPRAY CONTACTED THE TURBINE EXHAUST. THE BUILDING FIRE DETECTION VENTILATION SYSTEM. EMERGENCY RESPONSE AGENCIES WERE IMMEDIATELY NOTIFIED AND THREE FIRE DEPARTMENTS RESPONDED AND THE FIRE WAS EXTINGUISHED WITH FOAM. THE BUILDING WAS SECURED AND DAMAGE ASSESSMENT BEGAN. ALL DAMAGE WAS CONTAINED WITHIN THE TURBINE BUILDING. REPAIRES TO THE TURBINE SKID, ELECTRICAL CONTROL SYSTEM AND BUILDING PANELS ARE CURRENTLY UNDERWAY.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000124 | 2000-07-11 | 19160 | TENNESSEE GAS PIPELINE CO |  |  | LA |  | 507K-1601A+0.00 |  | 640 | 2000-06-17 |  | YES | WC | 177 |  | YES | NO | LEAK |  | 0 | 0 | 600000 | 405461.5385 | 883307.6923 | Null | 6 | 30 | 532481 | 20000617 |  | 1973 | BY TEST | 2175 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: NO DATA; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1975; NMDIA: 4; THK: 0.337; SPEC: 5L; SMYS: 35000; SEAM: SEAMLESS; MANU: US STEEL; MANYR: 1975; LOCLK: UNDER WATER; PNAME: LOUIS A SALIPAS; PHONE: 7134202781; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null; TMPS: 0; LKPS: 0 | A LEAK WAS REPORTED AND DETERMINED TO BE ON A TENNESSEE GAS PIPELINE FACILITY AT 10 A.M. ON 6/17/00 ON THE 507K-100 LINE (26" LINE) IN THE WC 177A.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20000127 | 2000-07-14 | 13702 | NORTHERN GAS CO | RIVERTON | NATRONA | WY | 8 2501 | 39.53 | 2087 +00.2 | 1100 | 2000-06-14 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 53230 | 35971.1962 | 78364.1141 | Null | 1 | 0 | 532311 | 20000616 | 463 | 673 | BY TEST |  | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1964; NMDIA: 16; THK: 0.281; SPEC: X-42; SMYS: 42000; SEAM: ERW; LOCLK: UNDER GROUND; PNAME: BERNADETTE M FRIEH; PHONE: 3039147829; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: LINE MARKERS; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | THIRD PARTY EXCAVATION DAMAGE--A DOZER WITH RIPPER STRUCK A HOLE IN THE MAINLINE DAMAGING A SECTION OF PIPELINE. THIS SECTION WAS REPLACED WITH 14 FEET OF 0.25W X-52 16" PIPE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20000128 | 2000-07-26 | 5304 | FLORIDA GAS TRANSMISSION CO (ENRON) | PLEDGER | BRAZORIA | TX |  | 250.476 |  | 520 | 2000-06-22 | 1 | NO |  |  |  | Null | NO | RUPTURE | 25 | 0 | 0 | 65000 | 43925 | 95691.6667 | Null | 0 | 30 | 533053 | 20000622 | 966 | 975 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1958 | 22 | 0.287 | API5LX | 52000 | SEAMLESS |  | NATIONAL TUBE |  | UNDER GROUND |  | MERLIN H MOSEMAN | 7136467344 | EXTERNALLY | OTHER | SCC |  |  | COATED | YES | 1958 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | PIPELINE FAILURE THE RESULT OF LOCALIZED STRESS CORROSION CRACKING OF PIPE EXTERNAL SURFACE.PIPELINE FAILURE THE RESULT OF LOCALIZED STRESS CORROSION CRACKING OF PIPE EXTERNAL SURFACE.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 20000129 | 2000-07-27 | 18516 | SOUTHERN NATURAL GAS CO | PLAQUEMINES |  | LA |  | ROMERE PASS LINE MP 1.60 | APPROXIMATELY 84+34 | 1934 | 2000-07-05 | 1 | NO |  |  |  | Null | YES | RUPTURE | 22 | 0 | 5 | 500000 | 337884.6154 | 736089.7436 | Null | 2 | 15 |  | 20000705 | 1032 | 1150 | BY TEST | 1805 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1953; NMDIA: 14; THK: 0.312; SPEC: API 5LX; SMYS: 42000; SEAM: SEAMLESS; MANU: NATIONAL TUBE PIPE; MANYR: 1953; LOCLK: UNDER GROUND; PNAME: CHARLIE CHILDS; PHONE: 7134203570; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | A TUGBOAT, OCEAN SCRAMBLER, STRUCK THE MARKED 14" ROMERE PASS TRANSMISSION PIPELINE CAUSING THE RUPTURE. SUBSEQUENTLY, THE M/V LADY MELINDA ARRIVED AND THEN IGNITION OCCURRED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000130 | 2000-07-27 | 19160 | TENNESSEE GAS PIPELINE CO |  |  | LA |  | 507A-3201+0.0 |  | 1210 | 2000-07-05 |  | YES | EC | 33C |  | YES | NO | LEAK |  | 0 | 0 | 100000 | 67576.9231 | 147217.9487 | Null | 2 | 29 |  | 20000705 |  | 2447 | BY TEST | 2165 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | FITTING |  | STEEL |  | PIPELINE |  | 1972 | 12 | 0.5 |  | 52000 |  |  | US STEEL | 1972 | UNDER WATER |  | LOUIS A SALINAS | 7134202781 | INTERNALLY | GENERAL CORROSION |  | OTHER | UNDER INVESTIGATION | COATED | YES | 1972 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | A LEAK WAS REPORTED AND DETERMINED TO BE ON A TENNESSEE GAS PIPELINE FACILITY AT 12:10P.M. ON 7/5/2000 ON THE 507A-3200 LINE IN EC BLOCK 33C.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20000131 | 2000-07-28 | 2620 | COLUMBIA GULF TRANSMISSION CO |  |  | LA |  | VERMILLION 187 | X=1662757.05 Y=64495.59 | 1000 | 2000-06-29 |  | YES | VERMILION | 187 |  | Null | NO | LEAK |  | 0 | 0 | 57000 | 38518.8462 | 83914.2308 | Null | 0 | 0 | 533922 | 20000629 | 1000 | 1250 |  |  | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: VALVE; MLKD: STEEL; PRTSY: OTHER; PRTSO: VALVE; PRTYR: 1989; SMYS: 0; VALVE: 1/2 BLEEDER VALVE; MANYR: 1989; LOCLK: UNDER WATER; PNAME: HENRY WAYNE; PHONE: 7132674371; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null; TMPS: 0; LKPS: 0 | 1/2 BODY BLEED VALVE ON 16" BLOCK VALVE BROKEN OFF BY A TRAWLER.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000132 | 2000-07-31 | 405 | ANR PIPELINE CO | LYNN | RANDOLPH | IN |  | M.P.27.6 | 1457+63 | 2320 | 2000-07-02 | 1 | NO |  |  | IN | Null | Null | LEAK |  | 0 | 0 | 75000 | 50682.6923 | 110413.4615 | Null | 2 | 0 | 534181 | 20000702 | 890 | 944 | BY TEST | 1299 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD |  | STEEL |  | PIPELINE |  | 1990 | 30 | 0.281 | API 5LX | 70000 | DSAW |  | UTM | 1990 | UNDER GROUND |  | DON CROSS SR | 3134962460 | [6 empty] | Null | 0 |  |  | Null |  | Null |  | Null | MATERIAL | 30" GIRTH WELD | YES | 19900709 | WATER |  | 8 | 1299 | A 30" GIRTH WELD WAS LEAKING AT THE 6 OCLOCK (1/8" WIDE X 1-1/4" LONG).
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000134 | 2000-08-03 | 2616 | COLUMBIA GAS TRANSMISSION CORP | ARTEMAS | BEDFORD | PA | 1 7211 | ADJACENT TO WELL#4904 | 1+69 | 507 | 2000-07-02 | 1 | NO |  |  | PA | Null | NO | RUPTURE | 9 | 0 | 0 | 250000 | 168942.3077 | 368044.8718 | Null | 1 | 23 | 534468 | 20000706 | 1730 | 2475 | BY TEST | 3000 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1972 | 6 | 0.219 | API 5LX | 52000 | SEAMLESS |  | US STEEL | 1971 | UNDER GROUND |  | JAMES F SWATZEL | 3043572797 | INTERNALLY | LOCALIZED PITTING |  | OTHER | MICROBIOLOGICAL | COATED | Null | 0 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | THIS FAILURE OCCURRED IN AN ISOLATED AREA WITH NO IGNITION SOURCE OR FIRE. THE RUPTURE WAS CONTAINED WITHIN ONE JOINT OF PIPE ADJACENT TO PIPELINE EQUIPMENT ASSOCIATED WITH A STORAGE WELL. THE FORCE OF THE RUPTURE DESTROYED THE WELL SITE PIPELINE EQUIPMENT. THE PRELIMINARY RESULTS FROM THE ON-GOING INVESTIGATION INDICATE MICROBIOLOGICALLY INFLUENCED CORROSION (MIC).
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000136 | 2000-08-09 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) |  |  | TX |  | 16.7 | 882+36.5 | 330 | 2000-07-07 |  | YES |  | 92 |  | Null | NO | LEAK |  | 0 | 0 | 92823 | 62726.9273 | 136652.1165 | Null | 0 | 0 | 534686 | 20000707 | 1050 | 1200 | BY TEST |  | CORROSION | CORROSION | INTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1980; NMDIA: 16; THK: 0.312; SPEC: 5L X52; SMYS: 2028; SEAM: SEAMLESS; LOCLK: UNDER GROUND; PNAME: BERNADETTE M FRIEH; PHONE: 3039147829; LOC: INTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: OTHER; COAT: COATED; PROT: YES; CPYR: 1980; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | A SMALL PINHOLE LEAK WAS DISCOVERED ON THE HIGH ISLAND 16" LATERAL. PRODUCTION WAS SHUT IN FOR PART OF THE WEEKEND.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000137 | 2000-08-09 | 5304 | FLORIDA GAS TRANSMISSION CO (ENRON) | MOUNT DORA | LAKE | FL |  | 0.016 |  | 1813 | 2000-07-07 | 3 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 208000 | 140560 | 306213.3333 | Null | 0 | 30 | 534705 | 20000707 | 650 | 975 | BY TEST | 1463 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: PRESSURE TRANSMITTER; MLKD: STEEL; PRTYR: 1982; SMYS: 0; LOCLK: ABOVE GROUND; PNAME: MERLIN MOSEMAN; PHONE: 7136467344; PROT: Null; CPYR: 0; CAULK: EARTH MOVEMENT: OTHER; DMGO: LIGHTING OR FIRE; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | A LIGHTNING STRIKE AT OR NEAR THE REGULATOR/METERING STATION RESULTED IN THE FAILURE OF A PRESSURE TRANSMITTER DIAPHRAGM.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20000140 | 2000-08-02 | 21031 | PG & E TEXAS PIPELINE, L.P. | BAY CITY | MATAGORDA | TX | 7 7414 | MP 3.8 | 199+79 | 1620 | 2000-07-03 | 1 | NO |  |  |  | Null | NO | RUPTURE | 36 | 0 | 0 | 47900 | 32369.3462 | 70517.3974 | Null | 0 | 50 |  | 20000703 | 795 | 1003 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | WELD |  | STEEL |  | PIPELINE |  | 1967 | 8 | 0.188 | X46 | 46000 | ERW |  |  |  | UNDER GROUND |  | KEVIN SEHY | 2105284204 | INTERNALLY | LOCALIZED PITTING |  | OTHER | MICROBACTERIAL INDUCED CORROSION | COATED | YES | 1967 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | PIPELINE RUPTURED @ 795 PSIG. METALLURGICAL EXAM REVEALED INTERNAL CORROSION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20000144 | 2000-08-18 | 405 | ANR PIPELINE CO | LENA | OCONTO | WI |  | M.P. 67.85 | 3586+35 | 1230 | 2000-08-02 | 1 | NO |  |  |  | Null | Null | RUPTURE | 3 | 0 | 0 | 50000 | 33788.4615 | 73608.9744 | Null | 0 | 53 | 537404 | 20000802 | 708 | 975 | BY TEST | 1636 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1960; NMDIA: 16; THK: 0.25; SPEC: API 5LX; SMYS: 52000; SEAM: EFW; MANU: A.O. SMITH; MANYR: 1960; LOCLK: UNDER GROUND; PNAME: JOHN P LUCIDO; PHONE: 3134967115; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | CONTRACTOR HIT 16" MARINETTE LATERAL.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20000145 | 2000-08-22 | 13702 | NORTHERN GAS CO | LARAMIE | ALBANY | WY | 82070- | 48.32 | HERRICK LANE MLV | 424 | 2000-07-18 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 0 | 0 | 0 | Null | 0 | 0 |  | 20000718 | 350 | 741 | BY TEST |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: NO FAILURE; MLKD: STEEL; PRTSY: OTHER; PRTSO: VALVE; NMDIA: 12.75; THK: 0.203; SMYS: 1115; SEAM: ERW; VALVE: FIGURE 1889; MANU: ROCKWELL; LOCLK: ABOVE GROUND; PNAME: BERNADETTE M FRIEH; PHONE: 3039147829; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | THE MAINLINE BLOCK VALVE AT HERRICK LANE (UPSTREAM OF LARAMIE TBS) WAS INADVERTENTLY LEFT CLOSED AFTER MAINTENANCE. GAS CONTROL TECHNICIANS(S) DID NOT RESPOND TO THE LOSS OF PRESSURE AND FLOW AT THE TBS. GAS SERVICE WAS LOST TO THE CITY OF LARAMINE. (POPULATION 27000; APPROXIMATELY 10177 METERS) AT APRROXMATELY 1 A.M. SERVICE WAS RESTORED TO THE TBS AT 6 AM. GAS SERVICE WAS RESTORED TO THE MAJORITY OF CUSTOMERS BY 7/21/00.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000146 | 2000-08-22 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) |  |  | TX |  |  | 340+00 | 901 | 2000-07-21 |  | YES |  | 110 |  | YES | NO | LEAK |  | 0 | 0 | 137500 | 92918.2692 | 202424.6795 | Null | 0 | 0 | 536098 | 20000721 | 980 | 1200 | BY TEST |  | CORROSION | CORROSION | INTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1980; NMDIA: 16; THK: 0.312; SPEC: 5LX 52; SMYS: 2028; SEAM: SEAMLESS; LOCLK: UNDER GROUND; PNAME: BERNADETTE M FRIEH; PHONE: 3039147829; LOC: INTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: OTHER; COAT: COATED; PROT: YES; CPYR: 1980; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | A SMALL PINHOLE LEAK WAS DISCOVERED ON THE HIGH ISLAND 16" LATERAL.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 20000151 | 2000-08-22 | 4280 | EL PASO NATURAL GAS CO | PHOENIX | MARICOPA | AZ | 8 5009 | MP 34+4847 |  | 1355 | 2000-07-21 | 1 | NO |  |  |  | Null | NO | OTHER |  | 1 | 1 | 155000 | 104744.2308 | 228187.8205 | Null | 1 | 0 | 536155 | 20000721 | 560 | 650 | BY TEST | 1100 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1950; NMDIA: 16; THK: 0.25; SPEC: GRADE B; SMYS: 35000; SEAM: SMLS; MANU: J & L; MANYR: 1950; LOCLK: UNDER GROUND; PNAME: LARRY J MEYER; PHONE: 5206634243; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PIPELINE MARKES IN PLACE; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | THE BUCKET TEETH ON A FRONT END LOADER EXCAVATING IN THE ROCKLAND MATERIALS YARD PUNCHED TWO HOLES IN THE PIPELINE. THE ESCAPING GAS IGNITED. BURNING THE OPERATOR ON 70% OF HIS BODY. THE OPERATOR WAS ABLE TO GET TO A NEARBY DITCH WITH WATER IN IT. THE VALVES ON BOTH SIDES OF THE INCIDENT SITE WERE CLOSED AND THE FIRE EXTINGUSHED ITSELF BY 3:00PM. THE OPERATOR IS CURRENTLY IN THE PHOENIX BURN CENTER. THE LOADER OPERATOR DIED ON SEPTEMBER 9, 2000
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20000152 | 2000-08-28 | 11820 | LOUISIANA RESOURCES PIPELINE CO, L.P. | HOLLY BEACH | CAMERON | LA | 7 0631 | MP 0/SCRAPER RECEIVER STA | 142+60 | 1500 | 2000-07-15 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 72000 | 48655.3846 | 105996.9231 | Null | 21 | 30 |  | 20000716 | 980 | 1440 | BY TEST | 1959 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | TRANSMISSION SYSTEM | MECHANICAL JOINT |  | STEEL |  | OTHER | SCRAPER RECEIVER STATION | 1977 | 8.625 | 0.219 | API 5LX-42 | 42000 | ERW | BALL (ROCKWELL) | NIPPON STEEL | 1976 | OTHER | ABOVE GROUND IN MARSH | HENRY L LEGER | 3379375958 | [6 empty] | Null | 0 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | MARSH FIRE OF UNKNOWN ORIGIN CONSUMED WOODEN CREOSOTE PLATFORM WHICH SUPPORTED THE SUBJECT PIPELINE VALVE SETTING/SCRAPER RECEIVER STATION
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 20000160 | 2000-09-18 | 4280 | EL PASO NATURAL GAS CO | CARLSBAD | EDDY | NM | 8 8220 | MP 51+ON LINE 1103 |  | 527 | 2000-08-19 | 1 | NO |  |  |  | Null | NO | RUPTURE | 59 | 12 | 0 | 998296 | 674617.72 | 1469670.8933 | Null | 2 | 0 | 539219 | 20000819 | 673 | 837 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1950 | 30 | 0.335 | API 5L | 52000 | DSAW |  | REPUBLIC | 1950 | UNDER GROUND |  | LES WHITE | 9156863277 | INTERNALLY | LOCALIZED PITTING |  | OTHER | SEE #6 | COATED | YES | 1950 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | AT APPROXIMATELY 5:27 A.M. (MST) ON AUGUST 19, 2000 EL PASOS 30-INCH LINE 1103 RUPTURED. GAS CONTROL NOTICED A PRESSURE DROP AND DETERMINED THAT A FAILURE HAD OCCURRED. PECOS RIVER DISTRICT AND JAL DISTRICT PERSONNEL DISPATCHED TO THE SITE. VALVES 6 & 6 3/4 & 6 1/2 WERE SHUT-IN ISOLATING THE SECTION. THE FIRE WAS OUT AT APPROXIMATELY 6:36 A.M. THERE WERE TWELVE FATALITIES ASSOCIATED WITH THIS INCIDENT.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000161 | 2000-09-15 | 15105 | PANHANDLE EASTERN PIPELINE CO | BLUE MOUND | CHRISTIAN | IL |  | MP 26/GATE VALVE 2 | 1334+53 | 1402 | 2000-08-16 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 100000 | 67576.9231 | 147217.9487 | Null | 0 | 33 | 538990 | 20000817 | 546 | 800 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: MECHANICAL JOINT; MLKD: OTHER; MLKDO: COUPLING; PRTSY: PIPELINE; PRTYR: 1954; NMDIA: 10; SMYS: 0; MANU: DRESSER INDUSTRIES; MANYR: 1954; LOCLK: UNDER GROUND; PNAME: MARVIN HOVIS; PHONE: 7139897473; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | MODIFICATIONS WERE MADE TO THE CROSSOVER PIPING BETWEEN TWO LINES TO ACCOMADATE IN-LINE INSPECTIONS. THE MODIFICATIONS DID NOT TAKE INTO ACCOUNT THAT AN UNKNOWN DRESSER COUPLING MIGHT HAVE BEEN INSTALLED ON THE EXISTING UNCOVERED CROSSOVER PIPING. AS THE LINE WAS BEING PRESSURED BACK UP AFTER CONSTRUCTION, THE MODIFIED CROSSOVER PIPE CAME OUT OF THE DRESSER COUPLING. CONTRIBUTING FACTORS TO THE INCIDENT WERE THAT THE MAIN LINE WAS CHECKED FOR DRESSER COUPLINGS, THE CROSSOVER WAS NOT AND THAT THE CONCRETE SUPPORT INSTALLED FOR THE 90 DEGREE ELBOW WAS NOT DESIGNED TO WITHSTAND THE FORCES THAT ARE EXERTED ON ELBOWS IN A LINE WITH COUPLINGS. STANDARD OPERATING PROCEDURES HAVE BEEN MODIFIED TO PREVENT A REOCCURENCE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20000162 | 2000-09-18 | 405 | ANR PIPELINE CO | VERMILION |  | LA |  | MP 7.42 | 480+85 | 1056 | 2000-08-25 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 54000 | 36491.5385 | 79497.6923 | Null | 0 | 0 |  | 20000825 | 848 | 1100 | BY TEST | 1645 | CORROSION | CORROSION | INTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1966; NMDIA: 12; THK: 0.25; SPEC: API-5LX; SMYS: 42000; SEAM: ERW; MANU: STUPP; MANYR: 1966; LOCLK: UNDER WATER; PNAME: DON CROSS SR; PHONE: 3134962460; LOC: INTERNALLY; COAT: COATED; PROT: YES; CPYR: 1966; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | A PINHOLE LEAK WAS DISCOVERED AT THE 6:00 POSITION ON THE BODY OF PIPE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000165 | 2000-09-18 | 20230 | KOCH GATEWAY PIPELINE CO | COLLINS | COVINGTON | MS |  | 51.95 | 2743+19 | 830 | 2000-08-29 | 2 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 80500 | 54399.4231 | 118510.4487 | Null | 0 | 0 | 540327 | 20000829 | 150 | 417 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1931 | 8 | 0.188 | API5L | 24000 | FURNACE LAP WELD |  | UNKNOWN |  | ABOVE GROUND |  | D SCOTT WILLIAMS | 6019580322 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1942 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | SMALL RELEASE WAS DISCOVERED ON KOCHS HATTIESBURG 8" PIPELINE (TPL 387). THE DIFFICULT WORKING TERRAIN SURROUNDING THE RELEASE WILL MAKE THE REPAIR COST EXCEED THE $50,000 REPORTING LIMIT. RELEASE DID NOT CAUSE A THREAT TO PUBLIC SAFETY.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000166 | 2000-09-19 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) |  |  | TX |  | 16 | 844+36.5 | 1408 | 2000-08-16 |  | YES | HIGH ISLAND | 92 |  | YES | NO | LEAK |  | 0 | 0 | 157324 | 106314.7185 | 231609.1656 | Null | 0 | 0 | 538917 | 20000816 | 940 | 1200 | BY TEST |  | CORROSION | CORROSION | INTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1980; NMDIA: 16; THK: 0.312; SPEC: 5LX52; SMYS: 2028; SEAM: SEAMLESS; LOCLK: UNDER GROUND; PNAME: BERNADETTE M FRIEH; PHONE: 3039147829; LOC: INTERNALLY; ADESC: LOCALIZED PITTING; CAUCR: OTHER; COAT: COATED; PROT: YES; CPYR: 1980; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | A SMALL PINHOLE LEAK WAS DISCOVERED ON THE HIGH ISLAND 16"LATERAL.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 20000171 | 2000-09-21 | 31304 | MITCHELL GAS SERVICES LP | COLLEGE STATION | BRAZOS | TX | 7 7845 |  |  | 123 | 2000-08-14 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 50000 | 33788.4615 | 73608.9744 | Null | 2 | 37 | 538593 | 20000814 | 700 | 892 | BY TEST | 1161 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1992 | 12 | 0.188 | X42 | 42000 | SEAMLESS | 600 |  |  | UNDER GROUND |  | KEITH PRESCOTT | 7133777297 | INTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1992 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | 1:23 A.M. OUR 12" PIPELINE LEAKED DUE TO INTERNAL CORROSION. DUE TO THE CLASS I LOCATION, SURROUNDING HOMES WERE EVACUATED AND TRAFFIC WAS REROUTED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000172 | 2000-09-21 | 31451 | KINDER MORGAN TEXAS PIPELINE CO | PAWNEE | BEE | TX | 78145- | 125.33 | 6617+62 | 1230 | 2000-08-04 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 98700 | 66698.4231 | 145304.1154 | Null | 2 | 0 |  | 20000804 | 930 | 1200 | BY TEST |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: NIPPLE AT SIDETAP; MLKD: STEEL; PRTSY: OTHER; PRTSO: NIPPLE; PRTYR: 1981; NMDIA: 30; THK: 0.5; SMYS: 60000; LOCLK: UNDER GROUND; PNAME: BERNADETTE M FRIEH; PHONE: 3039147829; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | A LEAK WAS FOUND ON A 2" SIDETAP ON INDEX 50. THE APPARENT CAUSE WAS THAT THE MAINLINE, OVER TIME, HAD SETTLED WHILE THE BRACE FOR THE 2" VALVE WAS HELD IN POSITION BY A BRACE. THIS EXERTED FORCE ON THE NIPPLE BETWEEN THE VALVE AND THE MAINLINE RESULTING IN A CRACK NEAR THE WELD ON THE 2" NIPPLE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000173 | 2000-09-21 | 405 | ANR PIPELINE CO |  |  | LA |  | X=1,755,695.07 | Y=3,411.86 | 825 | 2000-08-19 |  | YES | SOUTH MARSHALL | 58 | LA | Null | NO | LEAK |  | 0 | 0 | 119000 | 80416.5385 | 175189.359 | Null | 0 | 0 | 539215 | 20000819 | 1170 | 1300 | BY TEST | 2177 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1968 | 20 | 0.438 | API 5LX | 52000 | DSAW |  | USS | 1968 | ABOVE GROUND |  | DON CROSS | 3134962460 | EXTERNALLY | LOCALIZED PITTING |  | OTHER |  | COATED | YES | 1968 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | EXTERNAL CORROSION ON RISER CLAMP ON THE PLATFORM
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20000178 | 2000-10-10 | 4280 | EL PASO NATURAL GAS CO | DENVER CITY | GAINES | TX | 7 9323 | MP 210+4337 ON LINE 1102 |  | 2030 | 2000-08-28 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 50000 | 33788.4615 | 73608.9744 | Null | 2 | 0 | 540289 | 20000828 | 624 |  | BY CFR 192.619(A)(3) |  | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1950; NMDIA: 30; THK: 0.25; SPEC: API 5L; SMYS: 52000; SEAM: DSAW; MANU: CONSOLIDATED; MANYR: 1948; LOCLK: UNDER GROUND; PNAME: RICHARD FAVILA, PRINCIPAL ENGINEER; PHONE: 9155873771; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CAULC: CONSTRUCTION; CTEST: NO; TMPS: 0; LKPS: 0 | LEAK WAS DISCOVERED IN A FARMERS FIELD AFTER EPNG WAS INFORMED OF DARKENED SOIL IN THE VICINITY OF OUR LINE 1102. AN EXPLORATORY HOLE WAS DUG AND OF HAZARDOUS GAS DETECTOR DETERMINED A LEAK EXISTED. THE LINE WAS EXCAVATED AND THE LEAK WAS DETERMINED TO BE A MECHANICAL CLAMP ON AN OLD LEAK. THE LEAK WAS ADJACENT TO THE LONG SEAM OF THE 30" O.D. DSAW PIPE. IN THE INTEREST OF SAFETY IT WAS DECIDED TO REPAIR THE LEAK BY REMOVING A JOINT OF THE 30" PIPE AND REPLACING IT WITH 30" PIPE OF EQUAL OR GREATER STRENGTH. IT WAS NECESSARY TO BLOW DOWN 13 MILES OF PIPELINE IN ORDER TO REPAIR THE PIPELINE. CUSTOMERS WERE SERVICED WITH VOLUME BOTTLES WHILE REPAIRS WERE MADE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000180 | 2000-10-16 | 11680 | TXU LONE STAR PIPELINE | FREESTONE |  | TX |  | LINE L8A | 3054+36 | 1150 | 2000-09-12 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 142000 | 95959.2308 | 209049.4872 | Null | 0 | 30 |  | 20000912 | 401 | 500 | BY TEST | 550 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1934; NMDIA: 12; THK: 0.25; SPEC: API 5LX; SMYS: 30000; SEAM: LAP WELD; LOCLK: UNDER GROUND; PNAME: ZORA RAOUFPOUR; PHONE: 2148753889; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | PIPELINE WAS STRUCK BY A LOCAL CONTRACTOR WITH A BULLDOZER WHILE PREPARING LAND FOR FARMING ACTIVITIES. TXU PIPELINE SERVICES DID NOT RECEIVE PRIOR NOTICE OF THIS ACTIVITY.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000181 | 2000-10-18 | 19160 | TENNESSEE GAS PIPELINE CO | MISSION | HIDALGO | TX |  | 407D-102+3.65 | 192+55 | 212 | 2000-09-26 | 1 | NO |  |  |  | Null | NO | RUPTURE |  | 0 | 0 | 136000 | 91904.6154 | 200216.4103 | Null | 2 | 0 | 543279 | 20000926 | 850 | 1050 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1956 | 12 | 0.25 | 5L | 42000 | FLASH WELD |  | A O SMITH | 1956 | UNDER GROUND |  | LOUIS A SALINAS | 7134202781 | EXTERNALLY | OTHER | STRESS CORROSION CRACKING | OTHER | UNDER INVESTIGATION | COATED | YES | 1956 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | A RUPTURE WAS REPORTED ON THE TGP LINE 407D-100, SULLIVAN CITY LINE, AT 2:12 A.M. ON 9-26-00. THE EXACT CAUSE IS STILL UNDER INVESTIGATION
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20000184 | 2000-10-24 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | SPEARMAN | HANSFORD | TX | 7 0970 | 57 | 2039+23.3 | 830 | 2000-09-27 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 54043 | 36520.5965 | 79560.996 | Null | 0 | 0 | 543441 | 20000927 | 565 | 712 | BY TEST | 935 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; MLKD: STEEL; PRTSY: PIPELINE; NMDIA: 26; THK: 0.25; SPEC: 5L X52; SMYS: 52000; SEAM: ERW; MANU: A O SMITH; MANYR: 1947; LOCLK: UNDER GROUND; PNAME: BERNADETTE M FRIEH, REGULATORY COMPLIANCE; PHONE: 3039147829; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CAULC: CONSTRUCTION; CAULO: WELD WAS DEFECTIVE; CTEST: YES; MED: WATER; TMPS: 8; LKPS: 944 | COMPANY PERSONNEL WERE INFORMED BY ONEOK PERSONNEL OF A POTENTIAL LEAK ON OUR PIPELINE. AFTER INVESTIGATION, IT WAS DETERMINED THAT THERE WAS A LEAK ON THE #2 MAINLINE. NOTIFICATION WERE MADE, THE PIPELINE SECTION WAS SHUT DOWN, DRAWN DOWN, AND BLOWN DOWN FOR EXCAVATION. INSPECTION OF THE PIPE REVEALED A PINHOLE LEAK IN THE BUTT WELD LOCATED AT RECHAIN 2039+26. THE DEFECTIVE WELD WAS CUT OUT AND A 5 5" PUP INSTALLED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000191 | 2000-10-27 | 15105 | PANHANDLE EASTERN PIPELINE CO | MATFIELD GREEN | CHASE | KS |  | 308 GATE | 3529+59.1 | 415 | 2000-10-03 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 209500 | 141573.6538 | 308421.6026 | Null | 4 | 25 | 544293 | 20001005 | 660 | 780 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: VALVE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1963; NMDIA: 2; SPEC: ASA600; SMYS: 0; VALVE: SAF-T-SEAL GATE; MANU: WKM; MANYR: 1963; LOCLK: ABOVE GROUND; PNAME: MARVIN E HOVIS; PHONE: 7139897143; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | BOLTS HOLDING THE VALVE BONNET ON TO THE TOP OF A 2" WKM SAF-T SEAL GATE VALVE FAILED ALLOWING BOTH THE BONNET AND THE GATE SLAB TO BE BLOWN FROM THE VALVE BODY.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000192 | 2000-10-26 | 2620 | COLUMBIA GULF TRANSMISSION CO | MADISON |  | LA | 7 1232 | MP 2.1 | 114+24 | 2003 | 2000-09-29 | 1 | NO |  |  |  | Null | NO | RUPTURE | 83.5 | 0 | 0 | 250000 | 168942.3077 | 368044.8718 | Null | 0 | 57 | 543746 | 20000929 | 1001 | 1008 | BY TEST | 1387 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1958 | 30 | 0.375 | X-56 | 56000 | DSAW |  | NATIONAL TUBE | 1958 | UNDER GROUND |  | HENRY H WANG | 7132674371 | EXTERNALLY | LOCALIZED PITTING |  | OTHER |  | COATED | YES | 1958 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | METAL LOSS NEAR GIRTH WELD
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20000202 | 2000-11-03 | 19160 | TENNESSEE GAS PIPELINE CO | EDNA | JACKSON | TX |  | 12-1 + 6.97 |  | 1615 | 2000-10-12 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 72000 | 48655.3846 | 105996.9231 | Null | 9 | 30 |  | 20001012 | 615 | 750 | BY TEST | 1017 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | WELD | GIRTH WELD | STEEL |  | PIPELINE |  | 1944 | 24 | 0.25 | 5L | 50000 | FLASH WELD |  | NATIONAL TUBE | 1944 | UNDER GROUND |  | LOUIS A SALINAS | 7134202781 | [6 empty] | Null | 0 |  |  | Null |  | Null |  | Null | CONSTRUCTION |  | YES | 20000625 | WATER |  | 8 | 1017 | A LEAK WAS LOCATED BETWEEN MLVS 12 & 13. A SIX INCH LONG CRACK WAS FOUND ON A PRESSURE WELD. THE EXACT CAUSE IS STILL UNDER INVESTIGATION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20000204 | 2000-11-15 | 20230 | KOCH GATEWAY PIPELINE CO | CHENEYVILLE | RAPIDES | LA | 7 1325 | 2.5/#651 | 132+00 | 745 | 2000-10-28 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 50000 | 33788.4615 | 73608.9744 | Null | 9 | 15 | 546637 | 20001028 | 245 | 490 | BY CFR 192.619(A)(3) |  | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: VALVE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1931; SMYS: 0; VALVE: GATE; MANU: WALWORTH; LOCLK: UNDER GROUND; PNAME: RUDY PERCIFUL; PHONE: 3374394893; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | VALVE BODY CRACKED VENTING NATURAL GAS TO ATMOSPHERE. NRC REPORT #546637VALVE BODY CRACKED VENTING NATURAL GAS TO ATMOSPHERE. NRC REPORT #546637
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20000211 | 2000-11-27 | 405 | ANR PIPELINE CO |  |  | LA |  | X=1,921.680.96 | Y=124,783.86 | 1725 | 2000-10-30 |  | YES | EUGENE ISLAND | 305 | LA | Null | NO | LEAK |  | 0 | 0 | 50000 | 33788.4615 | 73608.9744 | Null | 0 | 0 | 546628 | 20001030 | 944 | 1300 | BY TEST | 2306 | CORROSION | CORROSION | INTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1978; NMDIA: 16; THK: 0.375; SPEC: API-5LX; SMYS: 52000; MANU: KAISER; MANYR: 1978; LOCLK: UNDER WATER; PNAME: DON CROSS SR; PHONE: 3134962460; LOC: INTERNALLY; COAT: COATED; PROT: YES; CPYR: 1978; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | POSSIBLE INTERNAL CORROSION @ 6 OCLOCK POSITION 5 FEET WEST OF FIELD JOINT.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20000221 | 2000-12-15 | 17620 | ROCKY MOUNTAIN NATURAL GAS CO INC | TELLURIDE | SAN MIGUEL | CO | 81435- | 15.46 | 816+46 | 600 | 2000-11-13 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 0 | 0 | 0 | Null | 0 | 0 |  | 20001113 | 530 | 1000 | BY TEST |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | TRANSMISSION SYSTEM | OTHER | NO "FAILURE" | STEEL |  | PIPELINE |  | 1987 | 6.625 | 0.156 | X-42 | 0 | ERW | N/A | N/A | 1987 | OTHER | TOWNS OF TELLURIDE, MOUNTAIN VILLAGE, AND NEARBY A | BERNADETTE M. FRIEH | 3039147829 | [6 empty] | Null | 0 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | HYDROCARBON FREEZE-OFF IN ABOVE-GROUND LINE CAUSED PRESSURE LOSS IN LINE, CAUSING LOSS OF GAS SUPPLY TO THE TOWNS OF TELLURIDE, MOUNTAIN VILLAGE, AND NEARBY AREAS.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 20000223 | 2000-12-18 | 30940 | WILLIAMS ENERGY GROUP-FIELD SERVICES |  |  | TX |  | 22.31 | N/A | 1345 | 2000-11-16 |  | YES | GALVESTON | 237 |  | YES | NO | LEAK |  | 0 | 0 | 730000 | 493311.5385 | 1074691.0256 | Null | 1 | 35 | 548441 | 20001116 | 800 | 1440 | BY TEST | 2218 | CORROSION | CORROSION | UNSPECIFIED CORROSION | PRTLK: GATHERING SYSTEM; PRTFL: MECHANICAL JOINT; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1977; NMDIA: 12; THK: 0.5; SPEC: API 5LX; SMYS: 42000; SEAM: SEAMLESS; MANU: US STEEL; LOCLK: UNDER WATER; PNAME: JAMES C. MASON; PHONE: 9185748016; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | ON 11-16-00 A PRODUCER FLYING TO A PLATFORM NOTICED THE APPARENT SIGN OF A SUBSEA GAS LEAK. HE CALLED THE WFS AREA MANAGER TO REPORT THE LEAK. THE AREA MANAGER CALLED THE NRC AND REPORTED THE INCIDENT. THE LINE SEGMENT WAS THEN SHUT-IN AT THE PLATFORM DOWNSTREAM OF THE LEAK, AFTER WHICH THE UPSTREAM PLATFORMS WERE SHUT-IN TO ISOLATE THE LEAK. DIVERS WERE DISPATCHED TO LOCATE THE EXACT LOCATION AND NATURE OF THE LEAK. THE LEAK WAS VERIFIED AS A CRACKED FORGED-ON END CONNECTOR (BIG INCH MARINE BRAND). THE END CONNECTOR WAS FROM A PREVIOUS REPAIR THAT WAS COMPLETED IN 1994. REPAIRS WERE MADE BY REMOVING A 39 SEGMENT AND REPLACING WITH A NEW SEGMENT. THE PIPELINE SEGMENT WAS BACK IN SERVICE ON 12-8-00. THE FAILED CONNECTOR WAS SENT TO A BATON ROUGE COMPANY TO PERFORM A METALLURGICAL ANALYSIS.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000224 | 2000-12-19 | 19730 | TRUNKLINE GAS CO | POLLOCK | GRANT | LA | 7 1467 | POLLOCK COMPRESSOR | 0+00 | 130 | 2000-11-23 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 900000 | 608192.3077 | 1324961.5385 | Null | 1 | 0 | 549015 | 20001123 |  |  |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: UPS SYSTEM; MLKD: OTHER; MLKDO: BATTERIES ON UPS; PRTSY: COMPRESSOR STATION; PRTYR: 1970; SMYS: 0; MANU: GENERAL ELECTRIC GAS TURBINE; MANYR: 1970; LOCLK: ABOVE GROUND; PNAME: MARVIN HOVIS; PHONE: 7139897473; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | COMPRESSOR STATION COMMERCIAL POWER FAILED. UNINTERRUPTED POWER SYSTEM TO THE CONTROLS OF THE AUXILIARY GENERATOR FAILED, SO AC POWER WAS NOT AVAILABLE TO PUMPS OR ELECTRICALLY OPERATED LOADING VALVES. GAS TURBINE CONTINUED TO RUN UNTIL LUBRICATING OIL HIGH TEMPERATURE SAFETY SHUT IT DOWN. THE CENTRIFUGAL COMPRESSOR REMAINED PRESSURIZED AFTER SHUT DOWN, SINCE AC POWER WAS NOT AVAILABLE TO OPERATE THE ISOLATION AND BLOW DOWN VALVES. ABOUT 15 MINUTES AFTER SHUT DOWN, THE GRAVITY FED CENTRIFUGAL COMPRESSOR SEAL OIL TANKS EMPTIED ALLOWING GAS PRESSURE TO BACK INTO THE OIL DRAIN SYSTEM, FORCING OIL & GAS THROUGHOUT THE SYSTEM. GAS PRESSURE ALSO CAUSED A DRESSER COUPLING ON THE SHAFT BEARING DRAIN LINE BETWEEN THE CENTRIFUGAL COMPRESSOR & TURBINE TO SEPARATE. OIL VAPOR & NATURAL GAS BEING FORCED OUT OF THE OIL SUMP VENT & FROM THE SEPARATED DRESSER COUPLING WAS IGNITED. PROBABLE SOURCE OF THE IGNITION WAS EXPOSED HOT METAL ON THE TURBINE EXHAUST. THE MAJORITY OF PROPERTY LOSS IS DUE TO DISMANTLING AND INSPECTION OF THE GAS TURBINE TO CHECK FOR DAMAGE, BEFORE PUTTING IT BACK IN SERVICE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000225 | 2000-12-26 | 30950 | EL PASO FIELD SERVICES | BAYTOWN | CHAMBERS | TX | 7 7520 | 800-1LINE/4.74MP/VALVE815 | 250+19.2(EAST END OF RUPT | 2048 | 2000-12-04 | 2 | NO |  |  |  | Null | Null | RUPTURE | 26.25 | 0 | 0 | 2200000 | 1486692.3077 | 3238794.8718 | Null | 4 | 42 | 549947 | 20001204 | 618 | 715 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1955; NMDIA: 30; THK: 0.344; SPEC: API5LX; SMYS: 52000; SEAM: FLASH WELD; MANU: AO SMITH; MANYR: 1955; LOCLK: UNDER GROUND; PNAME: JOHN S STERRETT; PHONE: 7134202398; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | 8:48-OCC RECEIVED TELEPHONE CALL FROM ART MANGUS IN BAYTOWN, TX CONCERNING A LINE RUPTURE AND GAS BLOWING TO THE ATMOSPHERE. HIS TELEPHONE NUMBER IS 281-383-7453. 8:50PM OCC CONTROLLERS BEGAN NOTIFYING OPERATIONS PERSONNEL FOLLOWED BY OTHER KEY COMPANY PERSONNEL, HPL GAS CONTROL, TGP GAS CONTROL, AND DOW GAS CONTROL. ADVISED HPL TO BEGIN SHUTTING RECEIPTS AND DELIVERIES IN THE SHIP CHANNEL AREA AS NEEDED. 9:01PM OCC CONTROLLERS BEGAN NOTIFYING CUSTOMERS IN THE SHIP CHANNEL AREA OF THE SITUATION AND ADVISED THEM TO SWITCH TO ALTERNATE FUEL SOURCES IF NEEDED. BEGAN SHUTTING IN RECEIPTS AND DELIVERIES IN THE SHIP CHANNEL AREA THAT WERE REMOTE CONTROLLED FROM THE OCC. 9:15PM OCC ISSUED STATION 809 UNITS A REMOTE STOP COMMAND, REMOTE FAILED AND GERRY TREVINO AND FRANK REEVES WERE NOTIFIED TO SHUT DOWN THE UNITS.9:40PM STATION 812-1A REMOTELY PINCHED DOWN ATTEMPTING TO REDUCE VOLUME INTO THE SHIP CHANNEL AREA. 9:45PM STATION 809 UNITS SHUT DOWN PER GERRY TREVINO. 9:45PM RECEIVED CALL FROM BEACH CITY FIRE DEPARTMENT REPORTING 40 FLUME OF NATURAL GAS BUT NO FIRE AT HIGHWAY 565 AND NEEDLEPOINT ROAD (FM2354). THEY REPORTED THAT THE AREA HAD BEEN PARTIALLY EVACUATED AT THIS TIME.10:07 PM MAINLINE VALVE 816 CLOSED. 10:15 PM RECEIVED UPDATE FROM JOHN D CARTER THAT RUPTURE APPEARS TO BE ON THE 30"A/S LINE BETWEEN BLOCK VALVES.10:20 PM MAINLINE VALVE 815 CLOSED. SEGMENT IS ISOLATED AND BEING DEPRESSURIZED. VERIFIED BY JOHN D CARTER.10:25PM JOHN STERRETT NOTIFIED THE OCC THAT THE DOT NATIONAL RESPONSE CENTER HAD BEEN NOTIFIED. 10:38PM JOHN STERRETT NOTIFIED THE OCC THAT THE TEXAS RAILROAD COMMISSION HAD BEEN NOTIFIED. 11:38PM BEGAN WITHDRAWAL FROM MOSS BLUFF TO BRING THE LINEPACK ON THE EAST END BACK TO NORMAL.11:41PM 812-1A REGULATOR OPENED BACK UP TO 100%. 11:45PM BEGAN BRINGING CUSTOMERS BACK ON-LINE IN THE SHIP CHANNEL AREA.12:00AM STATION 809 #1B UNIT BACK LINE. 12:05AM BEGAN RECEIVING GAS FROM TGP SABINE TO HELP BRING EAST END LINE PACK BACK UP.1:30AM OCC NOTIFIED THAT M/L VALVE HAS BEEN TAKEN OUT OF SERVICE TO INSTALL AN AIR MOVER. 4:45 AM SYSTEM BACK TO NORMAL OPERATING PRESSURES AND CUSTOMERS ARE BACK ON-LINE WITH THE EXCEPTION OF THE CUSTOMERS WITHIN THE SEGMENT THAT IS ISOLATED. DURING THIS INCIDENT THERE WAS NUMEROUS AND CONSTANT COMMUNICATIONS WITH EPFS PERSONNEL, HPL PERSONNEL, AND CUSTOMERS CONCERNING THE ON-GOING SITUATION.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 20000226 | 2000-12-26 | 19160 | TENNESSEE GAS PIPELINE CO | PORTLAND | SUMNER | TN |  | 87-1+0.00 |  | 1100 | 2000-11-28 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 3 | 0 | 0 | 0 | Null | 0 | 15 |  | 20001128 |  |  | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: ENGINE; MLKD: OTHER; MLKDO: COMPRESSOR ENGINE; PRTSY: COMPRESSOR STATION; PRTYR: 1950; SMYS: 0; LOCLK: ABOVE GROUND; PNAME: LOUIS A. SALINAS; PHONE: 7134202781; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | A MAINTENANCE CREW WAS PERFORMING WORK IN COMPRESSOR BUILDING "D", WHEN AN EXPLOSION/FLASH FIRE OCCURRED. APPARENTLY, GAS FROM THE COMPRESSOR MIGRATED INTO A CRANKCASE AND WAS IGNITED BY A SPARK, CAUSING THE EXPLOSION/FLASH FIRE. A POSSIBLE SOURCE OF IGNITION, THAT HAS BEEN IDENTIFIED, IS A WELDING MAINTENANCE ACTIVITY ON AN OIL LUBRICATION LINE, CONNECTED TO THE CRANKCASE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20000227 | 2000-12-21 | 18516 | SOUTHERN NATURAL GAS CO | KOSCIUSKO | ATTALA | MS |  | 137.3 |  | 1144 | 2000-11-25 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 0 | 0 | 0 | Null | 2 | 0 | 549118 | 20001125 | 413 | 500 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1942 | 22 | 0.281 | 5L | 35000 | SEAMLESS |  | NATIONAL TUBE | 1942 | UNDER GROUND |  | LOUIS A SALINAS | 7134202781 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1970 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | A LEAK WAS LOCATED ON THE NORTH MAIN LOOP, AT MP 137.3 EXTERNAL CORROSION IS THE APPARENT CAUSE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20000228 | 2000-12-22 | 13750 | NORTHERN NATURAL GAS CO (ENRON) | OSAKIS | DOUGLAS | MN | 5 6360 |  | 93+00 | 1500 | 2000-11-18 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 129000 | 87174.2308 | 189911.1538 | Null | 1 | 0 | 548619 | 20001118 | 50 | 50 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | INTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: CONTROL TUBING; MLKD: STEEL; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1961; SMYS: 0; LOCLK: ABOVE GROUND; PNAME: PAT VAUGHAN; PHONE: 7136467346; LOC: INTERNALLY; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | APPARENT CAUSE OF INCIDENT WAS A CORROSION LEAK WHICH DEVELOPED IN THE FIRE TUBE OF THE INDIRECT GAS HEATER. THE ETHYLENE GLYCOL/WATER MIXTURE CAUGHT FIRE INSIDE THE HEATER. HEAT FROM THE BURNING GLYCOL MIXTURE CAUSED THE CONTROL TUBING ON THE PRESSURE CONTROLLER TO FAIL. GAS AT APPROX 15 PSIG WAS RELEASED FROM THE CONTROL TUBING AND CONTROLLER BODIES. NO OTHER PRESSURE CONTAINING PIPING FAILED. THE FIRE CAUSED RELIEF VALVE TO FAIL OPEN BUT THE VENTED GAS DID NOT IGNITE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010001 | 2000-12-29 | 19580 | TRANS - COLORADO PIPELINE CO | MONTROSE | MONTROSE | CO | 81401- | 132.8 | 7016+74 | 700 | 2000-11-20 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 92000 | 62170.7692 | 135440.5128 | Null | 5 | 0 |  | 20001120 |  | 1285 | BY TEST |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: CONTROL SYSTEM; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1998; SMYS: 0; LOCLK: ABOVE GROUND; PNAME: BERNADETTE M. FRIEH; PHONE: 3039147829; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | THERE WAS A FALSE EMERGENCY SHUTDOWN AT THE OLATHE COMPRESSOR STATION DUE TO FAILURE OF THE CONTROL PANEL. IN ADDITION, THE CONTROL PANEL ONLY SENT A PARTIAL ESD SIGNAL, LEAVING THE COMPRESSOR INLET VALVE OPEN, UNDETECTED, FOR ABOUT 5 HOURS. THIS ALLOWED VENTING OF PIPELINE GAS TO ATMOSPHERE. NOTICE OF SITUATION WAS RECEIVED FROM A PRIVATE PARTY AND SUBSEQUENTLY CORRECTED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20010006 | 2001-01-08 | 11680 | TXU LONE STAR PIPELINE | KNOX | KNOX | TX |  |  | 328+80 | 1615 | 2000-11-27 | 3 | NO |  |  | TX | Null | NO | LEAK |  | 0 | 0 | 58900 | 39802.8077 | 86711.3718 | Null | 5 | 45 |  | 20001127 | 297 | 500 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1964; NMDIA: 4; THK: 0.164; SPEC: API 5L; SMYS: 30000; SEAM: LAB WELD; LOCLK: UNDER GROUND; PNAME: JOHN C. KNOLL; PHONE: 2148753028; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: COMPANY PIPELINE MARKER; STAT: NO; CTEST: Null; TMPS: 0; LKPS: 0 | KNOX COUNTY MAINTAINER WAS GRADING WHEN MAINTAINER HIT LINE U10. LINE U10 WAS APPROXIMATELY 16" DEEP.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 20010007 | 2001-01-08 | 21031 | PG & E TEXAS PIPELINE, L.P. | BRUNI | WEBB | TX | 7 8344 | 68.5 | 3616+80 | 945 | 2000-11-30 | 1 | NO |  |  |  | Null | NO | RUPTURE | 28 | 1 | 1 | 133000 | 89877.3077 | 195799.8718 | Null | 1 | 15 | 549612 | 20001130 | 880 | 1010 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1960; NMDIA: 20; THK: 0.281; SPEC: API X52; SMYS: 52000; LOCLK: UNDER GROUND; PNAME: KEVIN SEHY; PHONE: 2105284206; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | A THIRD-PARTY TELEPHONE COMPANY WAS PLANNING TO LAY FIBER-OPTIC CABLE IN THE VICINITY OF A PG&E NGL MARKETING, L.P. 6" PRODUCT LINE AND A PG & E TEXAS PIPELINE, L.P. 20" NATURAL GAS LINE WHICH PARALLEL EACH OTHER. THE TELEPHONE COMPANY CONTACTED PGE TEXAS PIPELINE COMPANY PERSONNEL ON NOVEMBER 29TH REGARDING THE PLANNED EXCAVATION. PGE TEXAS PIPELINE COMPANY PERSONNEL MET WITH TELEPHONE COMPANY PERSONNEL THE FOLLOWING MORNING AND PROCEEDED TO THE JOB SITE TO LOCATE THE TWO PIPELINES. UPON ARRIVING AT THE SITE AT APPROXIMATELY 9:30 A.M. EXCAVATION EQUIPMENT WAS IDLE. IT WAS DETERMINED BY PGE TEXAS PIPELINE COMPANY PERSONNEL THAT EXCAVATION WORK HAD BEGUN PRIOR TO THE MORNING OF NOVEMBER 30TH AND THAT THE 6" PRODUCT LINE HAD BEEN CROSSED. PGE TEXAS PIPELINE COMPANY PERSONNEL BEGAN REMOVING LINE-FINDING EQUIPMENT FROM THEIR VEHICLES TO VERIFY THE CROSSING DEPTH OF THE 6" LINE AND TO LOCATE AND DETERMINE THE DEPTH OF COVER ON THE 20" LINE. TELEPHONE COMPANY PERSONNEL INSTRUCTED THE OPERATOR OF A ROCK-SAW TRACTOR TO MOVE HIS EQUIPMENT OUT OF THE WAY IN ORDER TO FACILITATE LINE SPOTTING. AT APPROXIMATELY 9:45 A.M. AN EXPLOSION WITH NO IGNITION OCCURRED ON THE 20" GAS LINE. PRELIMINARY INVESTIGATION INDICATES THAT THE ROCK- SAW GOUGED THE PIPELINE THUS CAUSING THE ENSUING EXPLOSION. THE OPERATOR OF THE TRACTOR WAS BLOWN OFF THE EQUIPMENT AND DIED ONSITE. ANOTHER TELEPHONE COMPANY EMPLOYEE RECEIVED HEAD AND EYE INJURIES.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010008 | 2001-01-05 | 405 | ANR PIPELINE CO |  | LAPORTE | IN |  | 888.38 | 1727+10 | 1500 | 2000-12-06 | 1 | NO |  |  | IN | Null | Null | LEAK |  | 0 | 0 | 95061 | 64239.2988 | 139946.8542 | Null | 0 | 0 | 550268 | 20001207 | 709 | 850 | BY TEST | 1080 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | TEMPERATURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: VALVE BODY BLEED; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1960; NMDIA: 30; SMYS: 0; VALVE: GATE; MANU: GROVE; MANYR: 1960; LOCLK: UNDER GROUND; PNAME: DON CROSS SR; PHONE: 3134967115; PROT: Null; CPYR: 0; CAULK: EARTH MOVEMENT: FROST; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | A CRACKED THREAD ON A 1/2" X 11-1/2" LONG PIPE NIPPLE THAT WAS PART OF A BELOW GRADE BODY BLEED SYSTEM WAS LEAKING.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010009 | 2001-01-09 | 15105 | PANHANDLE EASTERN PIPELINE CO | HAVEN | RENO | KS | 6 7543 | 7/0 | 312+31 | 1836 | 2000-12-09 | 1 | NO |  |  |  | Null | NO | RUPTURE | 76 | 0 | 0 | 750000 | 506826.9231 | 1104134.6154 | Null | 1 | 9 | 550498 | 20001209 | 898 | 900 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | WELD | LONGITUDINAL | STEEL |  | PIPELINE |  | 1962 | 30 | 0.3125 | API 5LX X60 | 600000 | EFW |  | AO SMITH | 1962 | UNDER GROUND |  | MARVIN HOVIS | 7139897473 | EXTERNALLY | GENERAL CORROSION |  |  |  | COATED | YES | 1962 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | SELECTIVE SEAM CORROSION IN AN EFW WELD SEAM. ACCELERATED CORROSION RATE EXPERIENCED IN THE SEAM DUE TO VARYING CHEMISTRY BETWEEN THE SEAM WELD METAL AND THE PIPE PARENT METAL. CORROSION IN THE PIPE BODY WAS LIGHT, BUT VERY DEEP AT THE WELD SEAM.
2021-02-26 10:36 | YES | NO |  | 20010016 | 2001-01-22 | 8040 | ILLINOIS POWER CO | IRVING | MONTGOMERY | IL | 6 2051 | NATURAL GAS STORAGE FIELD |  | 2350 | 2000-12-16 |  | NO |  |  |  | Null | Null | RUPTURE |  | 0 | 0 | 1000000 | 675769.2308 | 1472179.4872 | Null | 0 | 1 |  | 20001216 |  |  |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTFL: NO DATA; MLKD: STEEL; PRTSY: COMPRESSOR STATION; SMYS: 0; MANU: KENNEDY; MANYR: 1992; LOCLK: ABOVE GROUND; PNAME: DON R. JOHNSON; PHONE: 2174247001; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | WHILE CONDUCTING A ROUTINE INSPECTION OF THE PLANT FACILITIES AT THE HILLSBORO STORAGE FIELD ON SATURDAY, DECEMBER 16, 2000, THE PLANT OPERATOR ON DUTY OBSERVED THE SIGHT GAUGE ON THE WATER SEPARATOR TANK AND DETERMINED THAT WATER SHOULD BE TRANSFERRED TO THE PRODUCED WATER HOLDING TANK. THE OPERATOR PROCEEDED TO MANUALLY OPERATE THE CONTROLLER ON A PNEUMATIC VALVE TO TRANSFER THE WATER. WHEN THE OPERATOR NO LONGER HEARD WATER FLOWING THROUGH TRANSFER LINE, HE MANUALLY OPERATED THE CONTROLLER TO CLOSE THE VALVE. AT THIS TIME, THE OPERATOR HEARD ABNORMAL SOUNDS COMING FROM THE AREA OF THE PRODUCED WATER HOLDING TANK. SECONDS LATER, THE OPERATOR HEARD A VIOLENT ROAR NEAR THE PLANT REGULATOR BUILDING. IMMEDIATELY THEREAFTER, THE PLANT LIGHTING WAS DISRUPTED. REALIZING THE POSSIBILITY A SERIOUS EVENT HAD OCCURED, THE OPERATOR SCANNED THE IMMEDIATE AREA WITH A FLASHLIGHT AND NOTICED LARGE PIECES OF METALLIC DEBRIS NEAR THE PLANT REGULATOR BUILDING. THE EMERGENCY SHUTDOWN SYSTEM (ESD) WAS ENGAGED AT APPROXIMATELY 11:50PM. THE OPERATOR NOTIFIED GAS DISPATCH THAT THE ESD HAD BEEN ENGAGED AND REQUESTED ASSISTANCE. UPON ARRIVAL, PLANT PERSONNEL OBSERVED THE PRODUCED WATER HOLDING TANK HAD BEEN DISLODGED. THE 50,000 GALLON WATER HOLDING TANK WAS DISLODGED FROM ITS FOUNDATION AND MOVED APPROXIMATELY 300 FEET CAUSING DAMAGE TO THE FIELDS REGULATOR STATION, 2 GAS DEHYDRATION TOWERS, AND NEARBY CABLE TRAYS. A NEARBY PRIMARY ELECTRIC LINE WAS ALSO DAMAGED. IN ACCORDANCE WITH COMPANY PROCEDURES, APPROPRIATE STATE AND FEDERAL AGENCIES WERE NOTIFIED BY TELEPHONE WITHIN THE REQUIRED TIME. THE FOLLOWING DAY, ILLINOIS POWERS CLAIMS PERSONNEL WERE NOTIFIED OF THE INCIDENT DESCRIBED ABOVE. SUBSEQUENTLY A DAMAGE ASSESSMENT WAS REQUESTED. ON MONDAY, DECEMBER 18, CLAIMS, GAS SUPPLY, AND ICC PIPELINE SAFETY PERSONNEL ARRIVED ON SITE TO CONDUCT AN ASSESSMENT OF THE DAMAGE AND DETERMINE POSSIBLE CAUSE. THE TEAM DECIDED TO RETAIN THE SERVICES OF AN INDEPENDENT DAMAGE ASSESSMENT SPECIALIST. ON TUESDAY, DECEMBER 19, PACKER ENGINEERING, INC. REPRESENTATIVES ARRIVED TO BEGIN THEIR INVESTIGATION. RESULTS OF THEIR INVESTIGATION ARE PENDING. CONDITIONS AT THE TIME OF THE INCIDENT WERE AS FOLLOWS: TEMPERATURE 5 DEGREES F.WIND VELOCITY 35 MPH GUSTING TO 40-45 MPH. WIND DIRECTION NORTHWEST. WIND CHILL FACTOR APPROXIMATELY MINUS 35 TO 45 DEGREES F.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010023 | 2001-01-29 | 30682 | AIM PIPELINE CO | PRENTISS | JEFFERSON DAVIS | MS | 39474- | T7N,R18W, SECTION 29/30 |  | 1747 | 2000-06-28 | 1 | NO |  |  |  | Null | NO | RUPTURE | 6 | 0 | 0 | 107500 | 72645.1923 | 158259.2949 | Null | 2 | 37 | 533867 | 20000629 | 800 | 960 | BY CFR 192.619(A)(3) | 1440 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1975; NMDIA: 8; THK: 0.188; SPEC: API 5LX X42; SMYS: 0; SEAM: ERW; LOCLK: UNDER GROUND; PNAME: KEN DUNCAN; PHONE: 4092962155; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | ON 06-28-00 SHORTLY BEFORE 5:47 P.M. THE FRM PIPELINE, AN 8 INCH HIGH PRESSURE GAS PIPELINE THAT RUNS EAST AND WEST FROM TRANSCO TO THE GEORGIA PACIFIC PAPER MILL, RUPTURED RELEASING NATURAL GAS TO THE ATMOSPHERE. AT 5:47P.M. JAMES DICKENS, A LOCAL LANDOWNER AND RESIDENT, NOTIFIED THE PRENTISS VOLUNTEER FIRE DEPARTMENT AND DEFS GAS CONTROL OF THE PIPELINE RUPTURE. AT 5:50 P.M. GAS CONTROL NOTIFIED JIM BERTELMAN, DEFS MEASUREMENT SUPERVISOR OF THE RUPTURE WHO IN TURN NOTIFIED MICHAEL SMALL, DEFS FIELD OPERATOR AND BUTCH HEMPHILL. DEFS SYSTEM SUPERVISOR AT 6:15 P.M. THE LINE IGNITED. THE PRENTISS VFD WAS ONSITE; HOWEVER, NO EFFORTS WERE MADE TO EXTINGUISH THE FIRE AS THE FIRE WAS ALLOWED TO BURN UNDER CONTROL. AT 6:55 P.M. THE LINE WAS SHUT-IN AND ISOLATED BY CLOSING THE MAIN PIPELINE BLOCK VALVES. AT 8:27 P.M. THE FUEL HAD BEEN CONSUMED AND THE FIRE WAS CONTAINED WITHIN THE BELLHOLE. DEFS PERSONNEL REMAINED ONSITE UNTIL THE LINE WAS REPAIRED THE FOLLOWING DAY, 06-29-00. AS A PRECAUTIONARY MEASURE, THE PRENTISS VFD EVACUATED THREE NEARBY RESIDENCES. ALL THREE WERE ALLOWED TO RETURN TO THEIR HOMES BEFORE 7:45 P.M. (NOTE: THERE WERE NO INJURIES AND NO MAJOR PROPERTY DAMAGE ASSOCIATED WITH THIS INCIDENT.) THE RUPTURE IN THE PIPE MEASURED SIX INCHES BY THREE INCHES. THE RUPTURE POINT IN THE LINE WAS IN A LOW-LYING AREA ON THE BOTTOM OF THE LINE APPROXIMATELY TWO INCHES FROM A JOINT WELD. AN EXTERNAL INSPECTION OF THE LINE DID NOT REVEAL FURTHER DAMAGE. A 53 FOOT SECTION OF LINE WAS REPLACED AND THE LINE WAS READY TO BE PUT BACK INTO SERVICE ON THE P.M. OF 6-29-00. THE LINE WAS PURGED, SLOWLY PRESSURIZED AND RETURNED TO SERVICE ON 6-30-00.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010024 | 2001-01-29 | 15105 | PANHANDLE EASTERN PIPELINE CO | NEBO | PIKE | IL | 6 2363 | 7.6/0 | 425+67 | 2332 | 2000-12-29 | 1 | NO |  |  |  | Null | NO | RUPTURE | 40 | 0 | 0 | 1030000 | 696042.3077 | 1516344.8718 | Null | 1 | 33 | 552219 | 20001230 | 867 | 900 | BY TEST | 1248 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1948 | 26 | 0.312 | API 5LX X52 | 520000 | SMLS |  | NATIONAL TUBE | 1948 | UNDER GROUND |  | MARVIN HOVIS | 7139897473 | EXTERNALLY | GENERAL CORROSION |  |  |  | COATED | YES | 1948 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | GENERAL CORROSION IN THE PIPE BODY AT THE LOCATION OF AN OVERBEND. COMPARISON OF COATING AT THE OVERBEND TO COATING ON THE ADJACENT PIPE INDICATES THAT THE COATING AT THE OVERBEND WAS DISBONDED. CONJECTURE IS THAT COATING WAS MANUALLY APPLIED AFTER INSTALLATION OF THE OVERBEND.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010025 | 2001-01-29 | 15007 | PACIFIC GAS & ELECTRIC CO | CORDELIA | SOLANO | CA | 9 4533 | 18.53 |  | 815 | 2000-12-26 | 1 | NO |  |  |  | Null | NO | NO DATA |  | 0 | 0 | 150000 | 101365.3846 | 220826.9231 | Null | 8 | 15 | 551911 | 20001226 | 1297 |  | BY TEST | 1297 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1965; NMDIA: 32; THK: 0.36; SPEC: API 5L X60; SMYS: 60000; SEAM: ARC; LOCLK: UNDER GROUND; PNAME: SHAN BHATTACHARYA; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | DESILVA CONSTRUCTION HIT 32" STEEL TRANSMISSION LINE 2010 WITH D6 GRADER WHILE GRADING FOR ROAD.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010031 | 2001-02-07 | 13580 | NORTH CAROLINA NATURAL GAS CORP | LILESVILLE | ANSON | NC | 2 8091 | MP 64 | 3519+27 | 1005 | 2001-01-03 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 2159963 | 1425997.6169 | 3106570.0312 | Null | 38 | 0 |  | 20010103 | 600 | 800 | BY TEST | 880 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; NMDIA: 16; THK: 0.219; SPEC: API-5L; SMYS: 42000; SEAM: ERW; MANU: UNKNOWN; MANYR: 1959; LOCLK: UNDER GROUND; PNAME: THEODORE R HODGES; PHONE: 9195466369; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 20010101; MARK: NO; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | CONTRACTOR WAS EXCAVATING, IN VIOLATION OF PROCEDURES, WHEN HE STRUCK 2-INCH LATERAL OFF OF 16 INCH TRANSMISSION LINE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010032 | 2001-02-10 | 19270 | WILLIAMS GAS PIPELINE - TEXAS GAS | SHELBY | BOLIVAR | MS | 38774- | MP 121+3000 |  | 800 | 2001-01-04 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 106000 | 69980.7114 | 152454.6593 | Null | 2 | 18 | 552669 | 20010105 | 450 | 700 | BY TEST | 840 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1940; NMDIA: 18; THK: 0.25; SPEC: API 5L; SMYS: 35000; MANU: YOUNGSTOWN; MANYR: 1940; LOCLK: UNDER GROUND; PNAME: STEVEN J LAW; PHONE: 2706886954; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | ON THURSDAY, JANUARY 4, 2001, AT APPROXIMATELY 8:00 AM CENTRAL STANDARD TIME, WILLIAMS GAS PIPELINE -- SOUTHCENTRAL (TEXAS GAS TRANSMISSION) WAS NOTIFIED THAT GAS WAS HEARD BLOWING IN A FIELD APPROXIMATELY 5 MILES WEST OF SHELBY, MS, AND 1 MILE SOUTH OF US HIGHWAY 32. THE COMPANY PROMPTLY DETERMINED THAT THE GAS WAS LEAKING FROM THE COMPANYS EIGHTEEN-INCH SYSTEM (EIS) #2 PIPELINE, NEAR MILEPOST 121+2948 IN BOLIVAR COUNTY , MS (SECTION 18, TOWNSHIP 19 NORTH, RANGE 7 WEST). THERE WAS NO DEATHS OR INJURIES RESULTING FROM THIS INCIDENT. ALSO, THERE WAS NO FIRE AT OR NEAR THE PIPELINE FACILITY. THERE WERE NO SERVICE INTERRUPTIONS AS A RESULT OF THIS INCIDENT. EVIDENCE AVAILABLE HAS NOT ALLOWED DETERMINATION OF CAUSE AT THIS TIME. THE CAUSE OF THE INCIDENT CONTINUES TO BE UNDER INVESTIGATION. PROPERTY DAMAGE WAS CONFINED TO COMPANY FACILITIES. THE INCIDENT OCCURRED IN A CROP FIELD WHERE THERE WERE NO DWELLINGS WITH THE PIPELINE CORRIDOR. THE COST OF REPAIR AND GAS LOSS ARE ESTIMATED AS FOLLOWS: GAS LOSS 106,000, MATERIAL 1,000, LABOR 3,000, EQUIPMENT 750, X-RAY 1,500, TOTAL COST 112,250EST. ADDITIONAL COMMENTS: COMPANY PERSONNEL FOUND THE DAMAGED PIPE SECTION TO HAVE A 40-INCH BURIAL DEPTH. ONCE UNCOVERED, A FRACTURE (APPROXIMATELY 30 INCHES LONG CIRCUMFERENTIALLY) WAS OBSERVED IN A WRINKLE BEND SITUATED ON THE TOP OF THE PIPE. ON FRIDAY, JANUARY 5, 2001, COMPANY PERSONNEL RETURNED THE EIS #2 TO SERVICE AFTER CUTTING OUT AND REPLACING THE DAMAGED PIPE SECTION WITH APPROXIMATELY 12 FEET OF 18-INCH PRETESTED PIPE FROM STOCK.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010036 | 2001-02-06 | 15105 | PANHANDLE EASTERN PIPELINE CO | HARRISONVILLE | CASS | MO | 64701- | 14.5 / 1 | 766+09 | 1822 | 2001-01-04 | 1 | NO |  |  |  | Null | NO | RUPTURE | 120 | 0 | 0 | 365000 | 240971.3176 | 524961.7986 | Null | 0 | 53 |  | 20010104 | 490 | 625 | BY CFR 192.619(A)(3) |  | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1931 | 22 | 0.31 | API 5L | 30700 | LAP WELD |  | NATIONAL TUBE | 1931 | UNDER GROUND |  | MARVIN HOVIS SR | 7139897473 | [6 empty] | Null | 0 |  |  | Null |  | Null |  | Null | CONSTRUCTION |  | YES | 19640718 | WATER |  | 24 | 750 | CIRCUMFERENTIAL SPLIT IN A SHARP WRINKLE BEND.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010037 | 2001-02-14 | 18516 | SOUTHERN NATURAL GAS CO | HOLT | TUSCALOOSA | AL |  | 157.2 |  | 1200 | 2001-01-16 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 217850 | 143823.5659 | 313323.0899 | Null | 0 | 0 |  | 20010116 | 500 | 750 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1952 | 24 | 0.25 | 5L | 52000 | DSAW |  | REPUBLIC PIPE | 1952 | UNDER GROUND |  | LOUIS A. SALINAS | 7134202781 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1972 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | A LEAK WAS LOCATED ON THE NORTH MAIN SYSTEM, AT MP 157.2, AFTER DEAD VEGETATION WAS FOUND. FURTHER INVESTIGATION WITH GAS DETECTION INSTRUMENTS AND EXCAVATION REVEALED A SMALL LEAK ON THE 2ND NORTH MAIN PIPELINE. A LOCALIZED EXTERNAL CORROSION HOLE IS THE APPARENT CAUSE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010038 | 2001-02-14 | 12876 | QUESTAR GAS COMPANY | LEHI | UTAH | UT |  |  | 724+37 | 625 | 2001-01-15 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 300838 | 198611.861 | 432680.7057 | Null | 3 | 50 | 553588 | 20010115 | 300 | 370 | BY TEST | 892 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1942; NMDIA: 20; THK: 0.281; SPEC: APL 5L; SMYS: 42000; LOCLK: ABOVE GROUND; PNAME: JEFFREY D. HANSEN; PHONE: 8013243645; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PIPELINE MARKER SIGNS; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | ON JANUARY 15, 2001, AT APPROXIMATELY 0625 A QUESTAR GAS COMPANY PHONE OPERATOR RECEIVED NOTIFICATION THAT A QUESTAR LINE WAS BLOWING. A QUESTAR EMPLOYEE ARRIVED ON-SCENE AND VERIFIED THAT THE BLOWING LINE WAS A 20 INCH HIGH PRESSURE (300 PSI) STEEL PIPELINE AND IT HAD BEEN HIT BY A FRONT END LOADER (1997 CATERPILLAR 980 G CAT). THE SECTION OF LINE THAT WAS DAMAGED WAS AN ABOVEGROUND SPAN THAT WENT ACROSS A RAVINE (APPROXIMATELY 20 ACROSS). INVESTIGATION REVEALED THAT SOME TIME DURING THE PREVIOUS NIGHT, A FRONT END LOADER HAD BEEN STOLEN FROM A NEARBY SAND AND GRAVEL PIT. IT IS BELIEVED THAT THE FRONT END LOADER WAS HOT WIRED AND USED TO PULL TWO TRUCKS FROM THE MUD IN THE HILLS ABOVE THE SCENE OF THE INCIDENT. THE FRONT END LOADER WAS THEN ROLLED DOWN THE HILL WHERE IT STRUCK THE PIPELINE WHERE IT CROSSED THE RAVINE. THIS RESULTED IN AN APPROXIMATE 9 INCH BY 3 INCH TEAR IN THE PIPELINE. THE TOTAL PROPERTY DAMAGE INCLUDING COST OF LOST GAS IS $300,838.00, OF WHICH $277,838.00 IS THE MARKET VALUE OF THE LOST GAS, AND $23,000.00 WAS THE COST OF THE REPAIR.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20010039 | 2001-02-16 | 31129 | BASIN EXPLORATION INC | HOLLY BEACH | CAMERON | LA |  |  |  | 740 | 2001-01-25 | 1 | NO |  |  | LA | Null | NO | LEAK |  | 0 | 0 | 0 | 0 | 0 | Null | 0 | 15 | 554695 | 20010125 | 350 | 1440 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1958; NMDIA: 16; THK: 0.432; SMYS: 0; MANU: TRANSCONTINENTAL GAS PIPELINE COMPANY; MANYR: 1958; LOCLK: UNDER GROUND; PNAME: K.W. PRITCHETT; PHONE: 2815783388; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 20010040 | 2001-02-16 | 13845 | NORTHWEST PIPELINE CORP (WGP) | BEAR LAKE | MONTPELIER | ID | 8 3254 | MP 495.53, | 5469+64.7 | 1830 | 2001-01-16 | 1 | NO |  |  | ID | Null | NO | OTHER |  | 1 | 2 | 0 | 0 | 0 | Null | 0 | 5 | 553780 | 20010116 | 30 | 850 | BY TEST | 1275 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: UNINTENTIONAL VENTING OF NATURAL GAS IN A BUILDING; MLKD: OTHER; MLKDO: N/A; PRTSY: COMPRESSOR STATION; PRTYR: 1979; SMYS: 0; LOCLK: ABOVE GROUND; PNAME: JOSEPH P. ROBERTSON; PHONE: 8015846776; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | A TEAM OF NORTHWEST PIPELINE CORPORATION EMPLOYEES WERE IN THE PROCESS OF PURGING AND PACKING THE PEGRAM COMPRESSOR STATION PIPING AFTER THE COMPLETION OF A CONSTRUCTION PROJECT. DURING THE PURGE PROCESS THREE EMPLOYEES WERE FOUND INSIDE THE UNIT #1 VALVE BUILDING. THE PURGING PROCESS WAS QUICKLY TERMINATED AND THE THREE MEN WERE REMOVED FROM THE BUILDING. TWO HAD VITAL SIGNS AND THE THIRD HAD NO VITAL SIGNS.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20010046 | 2001-02-23 | 22617 | WILLIAMS GAS PIPELINE CENTRAL, INC. | LOUISBURG | MIAMI | KS | 6 6053 | MAP 30 | 1480+65 | 830 | 2001-01-29 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 50000 | 33009.7695 | 71912.5752 | Null | 1 | 30 | 555048 | 20010129 | 530 | 550 | BY CFR 192.619(A)(3) |  | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1930; NMDIA: 12.75; THK: 0.284; SPEC: API 5L; SMYS: 35000; SEAM: SMLS; MANU: NATIONAL STEEL; MANYR: 1930; LOCLK: UNDER GROUND; PNAME: JOE FREISBERG; PHONE: 2706886961; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | CRACKED WELD. INCOMPLETE PENETRATION IN ACETYLENE TYPE WELD.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010059 | 2001-03-13 | 12690 | MONTANA POWER CO | HELENA | JEFFERSON | MT |  | MP 1.96 | 103+21 | 1400 | 2001-02-04 | 1 | NO |  |  |  | Null | NO | RUPTURE | 1 | 0 | 0 | 150000 | 99029.3086 | 215737.7255 | Null | 1 | 10 | 555725 | 20010204 | 376 | 500 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1962; NMDIA: 8; THK: 0.188; SPEC: API 5L B; SMYS: 42000; SEAM: ERW; MANU: LONE STAR STEEL; MANYR: 1962; LOCLK: UNDER GROUND; PNAME: JAY WATERMAN; PHONE: 4064972441; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: WARNING SIGNS; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | A CONTRACTOR DIGGING WITH AN LARGE TRACK MOUNTED EXCAVATOR HIT THE MPC EAST HELENA TO BOULDER 8" NATURAL GAS TRANSMISSION LINE AT MP 1.96. THE IMPACT OF THE EXCAVATOR TOOTH PUNCTURED THE LINE AND IMMEDIATELY NATURAL GAS BEGAN BLOWING. HIGH PRESSURE GAS BLEW BUT DID NOT IGNITE. TWO FARM TAP CUSTOMERS WERE LOST AS A RESULT. NO INJURIES OCURRED.A CONTRACTOR DIGGING WITH AN LARGE TRACK MOUNTED EXCAVATOR HIT THE MPC EAST HELENA TO BOULDER 8" NATURAL GAS TRANSMISSION LINE AT MP 1.96. THE IMPACT OF THE EXCAVATOR TOOTH PUNCTURED THE LINE AND IMMEDIATELY NATURAL GAS BEGAN BLOWING. HIGH PRESSURE GAS BLEW BUT DID NOT IGNITE. TWO FARM TAP CUSTOMERS WERE LOST AS A RESULT. NO INJURIES OCCURRED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20010060 | 2001-03-06 | 11680 | TXU LONE STAR PIPELINE | TRAVIS |  | TX |  |  | 2232+50 ON LINE P (SOUTH) | 1545 | 2001-02-08 | 1 | NO |  |  | TX | Null | NO | LEAK |  | 0 | 0 | 55000 | 36310.7465 | 79103.8327 | Null | 0 | 25 |  | 20010209 | 669 | 779 | BY TEST | 1200 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1995; NMDIA: 20; THK: 0.5; SPEC: API 5LX; SMYS: 42000; LOCLK: UNDER GROUND; PNAME: ZORA RAOUFPOUR; PHONE: 2148753889; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CAULC: CONSTRUCTION; CTEST: YES; TESTD: 19950713; MED: WATER; TMPS: 8; LKPS: 1200 | DURING INSTALLATION OF A HOT TAP CONNECTION FOR CITY OF AUSTINS SAND HILL POWER PLANT, THE CONTRACTOR GOUGED A HOLE IN THE PIPE.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 20010061 | 2001-03-21 | 31365 | SEACREST CO LLC |  |  | TX |  | LAT 28 34' 23.77 |  | 1846 | 2001-03-10 |  | YES | BRAZOS | 412 |  | YES | NO | LEAK |  | 0 | 0 | 75000 | 49514.6543 | 107868.8627 | Null | 1 | 30 | 559149 | 20010310 | 1000 | 1440 | BY CFR 192.619(A)(3) | 2700 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; NMDIA: 12; THK: 0.312; SPEC: API 5LX 60; SMYS: 2114; SEAM: ERW; LOCLK: UNDER WATER; PNAME: FRED WHITTED; PHONE: 7138212200; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | APPARENTLY A SUBSEA OBJECT DRUM OVER THE GATHERING LINE CAUSING A LEAK ON A COATED PIPE IN THE 3 OCLOCK POSITION.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 20010062 | 2001-03-28 | 30950 | EL PASO FIELD SERVICES |  |  | LA |  | WC 181 PRODUCTION PLATFOR |  | 330 | 2001-02-28 |  | YES | WC | 181 |  | YES | NO | OTHER |  | 0 | 0 | 7550600 | 4984871.3176 | 10859661.7986 | Null | 15 | 35 | 558117 | 20010228 | 1000 | 1300 | BY TEST | 3000 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1971; NMDIA: 16; THK: 0.625; SPEC: API 5LX; SMYS: 52000; MANU: USS; LOCLK: OTHER; LOCLO: PLATFORM RISER SEVERED ABOVE WATER LEVEL; PNAME: JOHN S STERRETT; PHONE: 7134202398; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: Null; MARK: Null; STAT: NO; CTEST: Null; TMPS: 0; LKPS: 0 | DETERMINED TO BE A PROBABLE PIPELINE INCIDENT AT 1015 CST WHEN NOTIFIED THAT THE PIPELINE PRESSURE WAS ZERO. AT ABOUT 0330 CST, A BOAT HIT A PRODUCTION PLATFORM AND SEVERED THE PIPELINE RISER, WHICH WAS ATTACHED TO THE PLATFORM. THE ABOVE COST ESTIMATE INCLUDES LOSS OF GAS, REPAIR OF PIPELINE, REPLACEMENT OF A COMMUNICATION HUB, AND PRODUCERS ESTIMATE OF PLATFORM AND EQUIPMENT DAMAGE, INCLUDING THE LOSS OF A PARKED HELICOPTER. THE INCIDENT WAS CONSIDERED SAFE WHEN SUBSEA BLOCK VALVE WAS CLOSED. ALSO, SEE ATTACHED RECORDS OF EVENTS.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 20010070 | 2001-04-17 | 30950 | EL PASO FIELD SERVICES | OFFSHORE | GULF OF MEXICO | TX |  |  |  | 1800 | 2001-02-03 |  | YES | BRAZOS | 368 | TX | Null | NO | LEAK |  | 0 | 0 | 97336 | 64260.7786 | 139993.6483 | Null | 0 | 0 |  | 20010206 | 318 | 1440 | BY TEST | 2400 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1974; NMDIA: 8.6; THK: 0.322; SPEC: 35000; SMYS: 261333; SEAM: SEAMLESS; VALVE: ANSI 600; LOCLK: UNDER WATER; PNAME: RONDA LOUDERMAN; PHONE: 3615780267; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CAULC: MATERIAL; CTEST: YES; TESTD: 19741205; MED: WATER; TMPS: 24; LKPS: 2400 | EPFS TELEPHONED THE RAILROAD COMMISSION OF TEXAS WITHIN 2 HOURS OF THE DETERMINATION THAT THE LEAK WAS ON AN EPFS LINE. IN REGARDS TO THE ABOVE MENTIONED LEAK, THE FOLLOWING IS A SUMMARY OF EVENTS THAT OCCURRED: ON FEBRUARY 4, 2001, A HELICOPTER PILOT WITH THE TNRCC HELICOPTER PATROL NOTICED BUBBLES IN THE WATER AROUND AN UNMANNED PLATFORM. THE PIPELINE ASSOCIATED WITH THIS PLATFORM IS AN 8" NATURAL GAS TRANSMISSION LINE WITH AN OPERATING PRESSURE OF 300 PSIG THAT WAS RECENTLY ACQUIRED BY EL PASO FIELD SERVICES FROM COASTAL. CODY MILBURN, AN EL PASO FIELD SERVICES REPRESENTATIVE WAS NOTIFIED AND MR. MILBURN THEN SET UP A DIVE BOAT TO BE DISPATCHED IN ORDER TO INVESTIGATE THE BUBBLES. THE PLATFORM WAS IN 30 FEET OF WATER AND IS LOCATED APPROXIMATELY SIX (6) MILES OFFSHORE. AT THE TIME THAT THE BUBBLES WERE SEEN, THERE WAS NO SHEEN ON THE WATER. THE 8" LINE WAS SUBSEQUENTLY BLOCKED IN ON FEBRUARY 4 UNTIL THE POSSIBLE LEAK COULD BE LOCATED AND VERIFIED THAT IT BELONGED TO EL PASO FIELD SERVICES. WHEN THIS DETERMINATION WAS MADE, THE LINE WAS RE-PRESSURIZED ON FEBRUARY 6 IN ORDER TO ASCERTAIN OF THE CORRECT LINE AND LOCATION AND THEN BLOCKED IN AGAIN SO THAT REPAIRS COULD BE MADE. REPAIRS WERE COMPLETED ON FEBRUARY 7 AND THE LINE PUT BACK INTO SERVICE ON FEBRUARY 8, 2001. ELI GUZMANN OF THE TEXAS RAILROAD COMMISSION WAS NOTIFIED BY THE AREA MANAGER OVER THESE ASSETS, J.R. LOGAN, ABOUT THE EVENTS LEADING UP TO THE ACTIONS. WE ARE CURRENTLY IN THE PROCESS OF FILLING OUT FORM RSPA F7100.2 IN ORDER TO MEET REQUIREMENTS OF THE RAILROAD COMMISSION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20010071 | 2001-04-10 | 12462 | MID LOUISIANA GAS CO | PLAQUEMINES |  | LA |  |  | 123+93.49 | 1600 | 2001-03-05 | 1 | NO |  |  | LA | Null | YES | LEAK |  | 0 | 0 | 30000 | 19805.8617 | 43147.5451 | Null | 2 | 0 |  |  | 900 | 1320 | BY TEST | 2140 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1975; NMDIA: 6; THK: 0.188; SPEC: X-42; SMYS: 42000; SEAM: ERW; MANU: J&L; MANYR: 1975; LOCLK: UNDER WATER; PNAME: GARY GILBERT; PHONE: 3186654426; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | SOMETHING (3RD PARTY) STRUCK PIPELINE MAKING A PIN SIZE HOLE AT 3 OCLOCK POSITION. DO NOT KNOW WHO OR WHAT HIT PIPE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010072 | 2001-04-11 | 15350 | PEOPLES NATURAL GAS CO | PALMER LAKE | EL PASO | CO |  |  |  | 1215 | 2001-03-28 | 3 | NO |  |  |  | Null | NO | RUPTURE | 0.66 | 0 | 0 | 140000 | 92427.3547 | 201355.2104 | Null | 1 | 0 | 561008 | 20010328 | 450 | 820 | BY TEST | 1230 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1990; NMDIA: 6; THK: 0.188; SMYS: 0; LOCLK: UNDER GROUND; PNAME: GEORGE PETERSON; PHONE: 7192263225; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: CARSONITE LINE MARKERS; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | DEVELOPER WAS LEVELING SITE FOR CONSTRUCTION OF TOWNHOMES. TRANSMISSION LINE WAS STRUCK BY EARTHMOVER.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 20010073 | 2001-04-06 | 31130 | DUKE ENERGY FIELD SERVICES INC | YUKON | CANADIAN | OK | 7 3099 | W YUKON BOOSTER | NE/4 SEC.1 12N 6W | 915 | 2001-03-19 | 1 | NO |  |  | OK | Null | NO | OTHER |  | 0 | 0 | 15000 | 9902.9309 | 21573.7725 | Null | 0 | 45 | 559987 | 20010319 |  |  | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: GATHERING SYSTEM; PRTFL: OTHER; PRTFO: DEHYDRATOR; MLKD: NO DATA; PRTSY: COMPRESSOR STATION; PRTYR: 1984; SMYS: 0; LOCLK: ABOVE GROUND; PNAME: CHAD MASHBURN; PHONE: 4052634688; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | A FIELD OPERATOR ARRIVED AT WEST YUKON BOOSTER THE MORNING OF MARCH 19TH, 2001. THE OPERATOR WAS CHECKING THE EQUIPMENT AT THE BOOSTER WHEN HE FOUND THE TEMPERATURE OF THE GLYCOL IN THE DEHYDRATOR WAS AT 50 F, WELL BELOW NORMAL OPERATING TEMPERATURE. AFTER A CLOSER INSPECTION OF UNIT, LEVELS, AND ALARMS, HE DETERMINED THE BURNER TUBE WAS NOT OPERATING. AT APPROXIMATELY 8:50 A.M., HE RESTARTED THE UNIT BY RE-IGNITING THE BURNER TUBE AND THEN PROCEEDED WITH HIS ROUNDS. APPROXIMATELY 5 MINUTES LATER HE HEARD A GURGLING NOISE FROM THE DEHYDRATOR AND SAW LIQUID BEING RELEASED FROM THE 2" VENT. AT THAT INSTANT, THE LIQUID/VAPOR IGNITED AND BEGAN TO BURN. THE FEILD OPERATOR IMMEDIATELY SHUT DOWN THE UNIT. AFTER SEVERAL MINUTES, THE LIQUID AND VAPOR RELEASE FROM THE 2" VENT STOPPED. A RESIDUAL FIRE STILL BURNED ON THE EXTERIOR OF THE UNIT AND ON THE LIQUID TRAPPED INSIDE THE UNITS DIKED AREA. ANOTHER OPERATOR HAD ARRIVED TO ASSIST AND TOGETHER THEY EXTINGUISHED THE RESIDUAL FIRE USING TWO 30# PORTABLE FIRE EXTINGUISHERS. THE YUKON FIRE DEPARTMENT WAS CALLED AND ARRIVED AT APPROXIMATELY 9:20 A.M. THE FIRE DEPARTMENT APPLIED WATER TO THE DEHYDRATOR UNIT TO ASSIST COOLING AND PREVENT RE-IGNITION. NO INJURIES OCCURRED. DAMAGE COST IS ESTIMATED AT $15,000. PRELIMINARY INVESTIGATION REVEALED THE FLAME IN THE BURNER TUBE WAS SOMEHOW EXTINGUISHED AND THE FLAME SENSOR FAILED TO DETECT IT. THE SENSOR IS CONFIGURED TO SHUT DOWN THE UNIT IN THE EVENT OF A "FLAME OUT" AND SIGNAL AN OPERATIONAL UPSET ALARM. THE GLYCOL PUMPS CONTINUED TO CIRCULATE GLYCOL THROUGH THE CONTACT TOWER AND BACK TO THE DEHYDRATOR UNIT. WITH THE BURNER TUBE NOT HEATING THE GLYCOL, IT COOLED TO THE POINT WHERE NATURAL GAS CONDENSATE WAS NOT SEPARATING FROM THE GLYCOL IN THE CONTACT TOWER. NATURAL GAS CONDENSATE THEN BEGAN TO ENTER THE DEHYDRATOR UNIT WITH THE GLYCOL. THE CONDENSATE ACCUMULATED ON TOP OF THE GLYCOL DUE TO ITS LOWER SPECIFIC GRAVITY. WHEN THE OPERATOR RE-STARTED BURNER TUBE IT HEATED THE GLYCOL/CONDENSATE MIXTURE CAUSING THE CONDENSATE TO RAPIDLY EVAPORATE INSIDE THE DEHYDRATOR UNTIL ENOUGH PRESSURE BUILT UP TO "BURP" LIQUID FROM THE 2" VENT. SOME OF THE CONDENSATE CONTACTED THE BURNER TUBE EXHAUST STACK AND IGNITED. AN INVESTIGATION TEAM HAS BEEN ASSEMBLED AND IS CURRENTLY CONDUCTING A THROUGH INVESTIGATION OF THIS INCIDENT.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010074 | 2001-04-16 | 5304 | FLORIDA GAS TRANSMISSION CO (ENRON) | EUSTIS | LAKE | FL | 3 2776 | M.P. 643.7 | 1889+94 | 800 | 2001-03-22 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 105000 | 69320.516 | 151016.4078 | Null | 0 | 40 | 560330 | 20010322 | 740 | 812 | BY TEST | 1600 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: NO DATA; MLKD: NO DATA; PRTSY: COMPRESSOR STATION; SMYS: 0; LOCLK: ABOVE GROUND; PNAME: DAVID PARHAM; PHONE: 4078387119; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | ON MARCH 22, 2001 AT APPROXIMATELY 0800, GAS VENTING FROM A BLOWDOWN SILENCER ADJACENT TO THE FGT 24" MAINLINE IGNITED DURING A PLANNED PIPELINE BLOWDOWN. THE FIRE WAS EXTINGUISHED BY CLOSURE OF THE BLOWDOWN VALVE APPROXIMATELY 40 MINUTES AFTER THE GAS IGNITION. DAMAGE FROM THE FIRE WAS LIMITED TO THE SILENCER, A BACKHOE, AND SEVERAL ADJACENT POWER LINES. THE CAUSE OF THE GAS IGNITION IS NOT KNOWN.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20010075 | 2001-04-20 | 31286 | ONEOK GAS TRANSPORTATION, LLC | SEMINOLE | GAINES | TX |  | SEC 168 BLK G |  | 1417 | 2001-03-29 | 1 | NO |  |  |  | Null | Null | RUPTURE |  | 0 | 0 | 42000 | 27728.2064 | 60406.5631 | Null | 1 | 30 |  | 20010329 | 430 | 610 | BY TEST | 1585 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1955; NMDIA: 6; THK: 250; SPEC: GRADE B; SMYS: 2642; SEAM: SEAMLESS; VALVE: 600 ANSI; MANU: UNKNOWN; LOCLK: UNDER GROUND; PNAME: STEVE BUSTOS; PHONE: 8067473037; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | COUNTY MAINTAINE STRUCK AND RUPTURED PIPELINE WHILE GRADING BAR DITCH.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010076 | 2001-04-17 | 4280 | EL PASO NATURAL GAS CO | ASHFORK | YAVAPAI | AZ |  | SALIGMAN STATION |  | 730 | 2001-03-17 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 534000 | 352544.3387 | 768026.3026 | Null | 22 | 0 | 559926 | 20010318 | 750 | 845 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: LIMIT SWITCH; PRTSY: COMPRESSOR STATION; PRTYR: 1959; SMYS: 0; VALVE: PLUG; LOCLK: ABOVE GROUND; PNAME: RICHARD FAVILA; PHONE: 9155873771; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | A MALFUNCTION OF A LIMIT SWITCH FAILED TO CLOSE THE #2 ELECTRIC UNIT SUCTION VALVE. THIS CAUSED THE #2 UNIT VENT TO REMAIN OPEN AFTER THE UNIT WAS DROPPED OF LINE ON SATURDAY, MARCH 17; HOWEVER, THE SIGNAL WAS PASSED ON TO THE DISCHARGE VALVE TO CLOSE. THE CLOSED DISCHARGE VALVE CAUSED THE VENT TO OPEN AND VENT GAS TO THE ATMOSPHERE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20010077 | 2001-04-17 | 7605 | HOUSTON PIPELINE CO | FREER | MCMULLEN | TX | 7 8022 |  | 599+80 DRAWING HC-3034-38 | 1500 | 2001-03-29 | 1 | NO |  |  |  | Null | Null | LEAK |  | 0 | 0 | 40000 | 26407.8156 | 57530.0601 | Null | 0 | 0 |  | 20010329 | 725 | 770 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1959 | 12 | 0.25 | API 5LX | 42000 | ERW |  | BETHLEHEM STEEL | 1959 | UNDER GROUND |  | DANNY COSBY | 7138536045 | EXTERNALLY | LOCALIZED PITTING |  | OTHER | COATING HOLIDAY | COATED | YES | 1959 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 20010080 | 2001-04-30 | 22175 | DYNEGY MIDSTREAM SERVICES, L.P. | WEST CAMERON 72 |  | LA |  |  |  | 930 | 2001-04-06 |  | YES | WC | 72 |  | Null | NO | LEAK |  | 0 | 0 | 0 | 0 | 0 | Null | 1 | 30 | 562056 | 20010426 | 1000 | 1235 | BY TEST | 1875 | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1997 | 12 | 0.375 | API 5LX X42 | 42000 | ERW |  | USS TUBULAR PRODUCTS | 1996 | UNDER WATER |  | TIM HUFFER | 3375834642 | INTERNALLY | LOCALIZED PITTING |  | OTHER | BIOLOGICAL | COATED | YES | 1997 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | PIN HOLE LEAK AT THE 3 OCLOCK POSITION.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010083 | 2001-05-01 | 7605 | HOUSTON PIPELINE CO | MORGAN'S POINT | HARRIS | TX | 7 7571 |  | 220+74 | 1500 | 2001-03-13 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 117500 | 77572.9584 | 168994.5516 | Null | 0 | 0 |  | 20010313 | 500 | 650 | BY CFR 192.619(A)(3) |  | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; PRTFO: WELDOLET; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1968; NMDIA: 4.5; THK: 0.337; SMYS: 0; LOCLK: UNDER GROUND; PNAME: DANNY COSBY; PHONE: 7138536045; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CAULC: CONSTRUCTION; CAULO: WELDOLET, 24" RUN X 4.5" BRANCH; CTEST: YES; MED: WATER; TMPS: 8; LKPS: 1350 | WHILE BOLTING UP A FLANGE TO CONNECT A LINE TO THE 4" TAP VALVE, A LEAK WAS DISCOVERED IN THE WELDOLET ON THE TAP VALVE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010084 | 2001-05-01 | 2616 | COLUMBIA GAS TRANSMISSION CORP | LIONSVILLE | CHESTER | PA | 1 9335 |  | 46+54 | 2000 | 2001-03-30 | 3 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 88000 | 58097.1944 | 126566.1323 | Null | 0 | 50 | 561310 | 20010331 | 1100 | 1200 |  |  | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1965 | 20 | 0.312 | AP15 LX65 | 65000 | FLASH WELD |  | AO SMITH | 1965 | UNDER PAVEMENT |  | CHRIS LEGG | 3043573227 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | NO | 0 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | A LEAK AT A ROAD CROSSING (PA 401/CONESTOGA ROAD) WAS DISCOVERED BY A MOTORIST AND REPORTED TO COLUMBIA. A PRELIMINARY FAILURE INVESTIGATION SUGGESTS THE LEAK OCCURRED IN AN AREA OF LOCALIZED EXTERNAL CORROSION WHICH WAS ATMOSPHERICALLY EXPOSED IN THE ROAD CASING.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20010085 | 2001-05-01 | 11808 | LOUISIANA INTRASTATE GAS CO, L.L.C. | BROUSSARD | ST MARTIN | LA |  |  |  | 1450 | 2001-04-04 | 1 | NO |  |  |  | Null | Null | OTHER |  | 0 | 0 | 0 | 0 | 0 | Null | 1 | 50 | 561808 | 20010404 | 530 | 1000 | BY TEST | 1500 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1950; NMDIA: 10; THK: 0.279; SPEC: API SL; SMYS: 35000; SEAM: ERW; LOCLK: UNDER GROUND; PNAME: MICHAEL LEGAR; PHONE: 3372338945; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: Null; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | CONTRACTOR WAS USING A DOZER TO PERFORM EARTHWORK AND LAND LEVELING OVER THE PIPELINE. THE CARTHERN COVER OVER THE PIPELINE WAS EVENTUALLY REMOVED. THE DOZER BLADE PUNCTURED A HOLE IN THE 10" PIPELINE. CONTRACTOR DID NOT MAKE THE PROPER ONE CALL NOTIFICATION, FOR THE STATE OF LA.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010086 | 2001-05-04 | 15105 | PANHANDLE EASTERN PIPELINE CO | TUSCOLA | DOUGLAS | IL | 6 1953 | 69 | 3653+45 | 247 | 2001-04-07 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 109620 | 72370.6187 | 157661.1298 | Null | 1 | 0 | 562463 | 20010410 | 730 | 708 | BY TEST | 1000 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | TRANSMISSION SYSTEM | OTHER | CONTROL SYSTEM | OTHER | SHORTED WIRE | OTHER | RELIEF VALVE | 1966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1966 | ABOVE GROUND |  | MARVIN HOVIS | 7139897473 | [6 empty] | Null | 0 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | A CONTROL SYSTEM FAILURE SHUT ALL OF THE UNITS COMPRESSING THIS LINE DOWN. PRESSURE INCREASED UNTIL RELIEF VALVE OPERATED. RELIEF VALVE OPERATED NORMALLY TO PREVENT PRESSURE FROM EXCEEDING MAOP+10%. INCIDENT REPORT IS BEING SUBMITTED BECAUSE GAS LOSS EXCEEDED $50,000. MODIFICATIONS ARE BEING MADE TO PREVENT REOCCURRENCE.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 20010087 | 2001-05-07 | 30940 | WILLIAMS ENERGY GROUP-FIELD SERVICES | MOSQUITO BAY MARSH | TERREBONNE | LA |  | 130.82 | 6907+28 | 1000 | 2001-04-05 | 1 | NO |  |  | LA | Null | NO | LEAK |  | 0 | 0 | 1250000 | 825244.2385 | 1797814.3788 | Null | 1 | 0 | 561893 | 20010405 | 730 | 1170 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1959 | 20 | 0.312 | API 5LX | 52000 | FLASH WELD |  | AO SMITH | 1959 | OTHER | TIDAL MARSH | CHRIS MASON | 9185748016 | INTERNALLY | LOCALIZED PITTING |  |  |  | COATED | YES | 1959 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | CORROSION TECH NOTICED A SHEEN IN THE MARSH WHILE WORKING AT THE MOSQUITO BAY PIPELINE MANIFOLD PLATFORM. STATE AND FEDERAL AGENCIES WERE NOTIFIED. A UNIFIED INCIDENT COMMAND STRUCTURE WAS ACTIVATED. BOOMS WERE DEPLOYED TO ISOLATE AND CONTAIN THE CONDENSATE PRODUCT. FOLLOWING THE CLEAN UP, THE LEAK WAS LOCATED. THE AREA OF PIPE IN THE VICINITY OF THE LEAK WAS RADIOGRAPHICALLY AND ULTRASONICALLY INSPECTED WITH NO FURTHER EVIDENCE OF CORROSION FOUND. THE CIRCUMFERENCE OF THE LINE NEAR THE LEAK WAS CLEANED AND CLAMPED. SAFETY AND ENVIRONMENTAL MEASURES WERE MONITORED THROUGHOUT THE PROCESS. THE LINE WAS RETURNED TO SERVICE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010089 | 2001-05-08 | 22617 | WILLIAMS GAS PIPELINE CENTRAL, INC. | ROSE HILL | BUTLER | KS | 6 7133 | 409+92 |  | 150 | 2001-04-04 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 100000 | 66019.5391 | 143825.1503 | Null | 17 | 30 | 561798 | 20010404 | 190 | 270 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1976; NMDIA: 8.62; THK: 0.188; SPEC: UNKNOWN; SMYS: 24000; SEAM: ERW; MANU: UNKNOWN; LOCLK: UNDER GROUND; PNAME: JOHN M HAMLIN; PHONE: 2706886965; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 20010319; MARK: YES; MRKTP: TEMPORARY STAKES; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | WHILE INSTALLING AN ELECTRIC LINE, AN OUTSIDE CONTRACTOR PUNCTURED THE LINE WITH A TRENCHER.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 20010090 | 2001-05-08 | 22617 | WILLIAMS GAS PIPELINE CENTRAL, INC. | BUFFALO | HARPER | OK | 7 3834 | NW 1/4, SEC 4, R27N |  | 1030 | 2001-04-05 | 1 | NO |  |  |  | Null | NO | OTHER |  | 1 | 0 | 0 | 0 | 0 | Null | 0 | 0 | 561915 | 20010405 |  |  |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: NO DATA; MLKD: NO DATA; SMYS: 0; LOCLK: NO DATA; PNAME: JOE FREISBERY; PHONE: 2706886961; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | BACKHOE TRACTOR FELL INTO EXCAVATION DURING THE RECLAIM OF A SETTING RESULTING IN THE FATALITY OF AN CENTRL EMPLOYEE
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010091 | 2001-05-08 | 18532 | SOUTHERN UNION GAS CO | EL PASO | EL PASO | TX | 7 9904 | 8600 RAILROAD DRIVE |  | 325 | 2001-04-04 | 1 | NO |  |  |  | Null | YES | OTHER |  | 0 | 0 | 120000 | 79223.4469 | 172590.1804 | Null | 5 | 33 | 561742 | 20010404 | 340 | 325 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: VALVE; MLKD: STEEL; PRTSY: OTHER; PRTSO: RELIEF; NMDIA: 6; SMYS: 0; VALVE: PILOT OPERATED RELIEF; MANU: ANDERSON/GREENWOOD; LOCLK: ABOVE GROUND; PNAME: JESSE WALLIS; PHONE: 5123708212; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | COMPANY PERSONNEL RESPONDED TO A BLOWING GAS SITUATION AT 2:25 AM MST ON APRIL 4, 2001. CONFLICTING REPORTS OF UNDERGROUND LEAKS, POSSIBLE EXPLOSIONS, AND NUMEROUS GAS ODOR REPORTS NECESSITATED A THOROUGH AND CAUTIOUS INVESTIGATION IN CONJUCTION WITH LOCAL PUBLIC SAFETY OFFICIALS TO PROTECT EMERGENCY RESPONDERS AND THE PUBLIC. PERSONNEL TOOK NUMEROUS SURFACE AND SUBSURFACE GAS READINGS AT LOCATIONS THROUGHOUT THE AREA. NO NATURAL GAS WAS FOUND EXCEPT THAT BEING RELEASED FROM THE RELIEF VALVE INTO THE ATMOSPHERE IN THE IMMEDIATE AREA. DUE TO THE REMOTE LOCATION OF THE INCIDENT, THE PROPERTIES OF NATURAL GAS, AND ATMOSPHERIC CONDITIONS THERE WAS NO THREAT TO THE PUBLIC. IT WAS DETERMINED THAT THE RELEASE OF GAS WAS SOLELY DUE TO A BLOWING RELIEF VALVE. THERE WERE NO LEAKS, EXPLOSIONS, OR GAS IN THE SURROUNDING AREAS. THE INVESTIGATION SHOWED THAT THE RELIEF VALVE WAS BLOWING DUE TO AN INCREASE IN DELIVERY PRESSURE ABOVE THE NORMAL OPERATING PRESSURE. DUE TO THE LARGE PRESSURE DROP THE TEMPERATURE AT THE VALVE DROPPED SIGNIFICANTLY AND MAY HAVE THE RELIEF VALVE TO FREEZE IN THE OPEN POSITION. THREE SUBSEQUENT TESTS OF THE RELIEF VALVE HAVE SHOWN THAT IT IS FUCTIONING PROPERLY.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010096 | 2001-05-21 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | GLASCO | CLOUD | KS | 6 7445 | 367 | 17526+78 | 940 | 2001-04-16 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 81000 | 53475.8267 | 116498.3717 | Null | 7 | 10 | 563110 | 20010416 | 657 | 712 | BY CFR 192.619(A)(3) |  | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1960; NMDIA: 36; THK: 0.344; SPEC: X-52; SMYS: 52000; MANU: AO SMITH; MANYR: 1960; LOCLK: UNDER GROUND; PNAME: BERNADETTE M. FRIEH; PHONE: 3039147829; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CAULC: MATERIAL; CTEST: YES; TESTD: 20011124; MED: WATER; TMPS: 8; LKPS: 1023 | DEAD VEGETATION DISCOVERED 04/13/01 ON FLYOVER. USED LEL DETECTOR ON 04/16/01 TO CONFIRM LEAK. LINE WAS ISOLATED AND PRESSURE WAS DRAWN DOWN TO 319 PSIG. A 1/2-INCH PENETRATOR WAS FOUND IN A LONG SEAM, ABOUT 1/8 INCH FROM THE GIRTH WELD. A FULL CIRCUMFERENCE SLEEVE WAS INSTALLED, AND THE LINE WAS RETURNED TO SERVICE ON 04/19/01.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20010097 | 2001-05-25 | 602 | RELIANT ENERGY GAS TRANSMISSION | HAUGHTON | BOSSIER | LA | 7 1037 |  | 1578+81 | 1813 | 2001-04-25 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 50000 | 33009.7695 | 71912.5752 | Null | 2 | 0 |  | 20010425 | 645 | 1000 | BY TEST | 1616 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1969; NMDIA: 12; THK: 0.203; SPEC: API 5L; SMYS: 46000; SEAM: ERW; MANU: STUPP; MANYR: 1969; LOCLK: UNDER GROUND; PNAME: TED VANDE KAMP; PHONE: 3184293606; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 20010418; MARK: YES; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | CONTRACTOR INSTALLING GATHERING LINE STRUCK LINE ST-10 WITH BACKHOE BUCKET PUNCTURING PIPELINE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010102 | 2001-05-29 | 30826 | WILLIAMS FIELD SERVICES | EUNICE | ACADIA | LA |  | 10.02 | 529+29 | 1000 | 2001-04-27 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 450000 | 297087.9259 | 647213.1764 | Null | 6 | 30 | 564274 | 20010427 | 630 | 1012 | BY TEST | 1369 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | WELD |  | STEEL |  | PIPELINE |  | 1967 | 24 | 0.281 | X60 | 60000 |  |  | AO SMITH |  | OTHER | CREEK CROSSING | KEN LYBARGER | 9185748029 | INTERNALLY | LOCALIZED PITTING |  | OTHER | WET UNDER DEPOSIT | COATED | YES | 1967 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | AIR PATROL NOTICED BUBBLES IN A FLOWING CREEK. STATE & FEDERAL AGENCIES WERE NOTIFIED. A AFFECTED SEGMENT OF PIPELINE WAS ISOLATED AND BLOWN DOWN. REPAIRS OR OTHER MEASURES WILL OCCUR IN THE NEAR FUTURE. A SUPPLEMENTAL FF7100.2 REPORT WILL BE SUBMITTED WHEN FUTURE ACTIONS ARE COMPLETED. 406.5 FEET OF PIPE WAS REPLACED, COMPLETE 8/31/01
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010107 | 2001-06-06 | 4280 | EL PASO NATURAL GAS CO | ELDORADO | SUTTON | TX |  | LINE 3137 / VALVE 0 & 1 | 140+3100 | 1908 | 2001-05-04 | 1 | NO |  |  |  | Null | NO | RUPTURE | 18 | 0 | 0 | 252176 | 166485.4329 | 362692.511 | Null | 2 | 45 | 565631 | 20010504 | 704 | 815 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; NMDIA: 20; THK: 0.25; SPEC: API 5LX X52; SMYS: 52000; SEAM: ERW; MANU: YOUNGSTOWN; MANYR: 1958; LOCLK: UNDER GROUND; PNAME: PAUL A. LOPEZ; PHONE: 7195204339; PROT: Null; CPYR: 0; CAULK: EARTH MOVEMENT: SUBSIDENCE; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | GROUND SETTLEMENT AT 6"X 20" TIE-IN RESULTED IN REDUCTION IN UNDERLYING STRUCTURAL SUPPORT FOR TIE-IN.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20010108 | 2001-06-06 | 19160 | TENNESSEE GAS PIPELINE CO | NEW IBERIA | IBERIA | LA |  | 507G-501+1.63 | 86+30 | 1612 | 2001-05-11 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 52000 | 34330.1603 | 74789.0782 | Null | 2 | 0 | 565794 | 20010511 | 900 | 1042 | BY TEST | 1302 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1951; NMDIA: 12; THK: 0.281; SPEC: 5L; SMYS: 42000; SEAM: SEAMLESS WELD; MANU: REPUBLIC; MANYR: 1951; LOCLK: UNDER GROUND; PNAME: LOUIS A SALINAS; PHONE: 8326764169; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | A LEAK WAS LOCATED AFTER A FARMER HIT THE PIPELINE WITH A DITCHING MACHINE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010114 | 2001-06-19 | 18152 | SEA ROBIN PIPELINE CO |  |  | LA |  | 0.00 | 0+20 | 1130 | 2001-05-13 |  | YES | EL | 295 |  | Null | NO | LEAK |  | 0 | 0 | 630000 | 415923.0962 | 906098.4469 | Null | 88 | 25 | 565922 | 20010513 | 934 | 1306 | BY TEST | 2400 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: SWIVEL FLANGE; MLKD: OTHER; PRTSY: PIPELINE; PRTYR: 1977; SMYS: 0; VALVE: SWIVEL FLANGE; MANU: CAMERON; MANYR: 1977; LOCLK: UNDER WATER; PNAME: MARVIN HOVIS SR.; PHONE: 7139897473; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null; TMPS: 0; LKPS: 0 | FISHING NET BROKE A GREASE FILLING OFF FROM A SWIVEL FLANGE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010118 | 2001-06-21 | 2616 | COLUMBIA GAS TRANSMISSION CORP | PETERSBURG | GRANT | WV |  |  | 300+59 | 1600 | 2001-05-21 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 149200 | 98501.1523 | 214587.1242 | Null | 4 | 0 | 567330 | 20010525 | 713 | 1000 | BY TEST | 1137 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1967; NMDIA: 36; THK: 0.438; SPEC: API 5LX; SMYS: 60000; SEAM: DSAW; MANU: USX; MANYR: 1967; LOCLK: UNDER GROUND; PNAME: MARY S FRIEND; PHONE: 3043572475; PROT: Null; CPYR: 0; CAULK: OPERATOR ACTION; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | DURING CIS SURVEY, CREW SMELLED GAS. FURTHER INVESTIGATION INDICATED A LEAK IN THE LINE. LINE PRESSURE WAS LOWERED UNTIL PIPE COULD BE UNCOVERED AND EXAMINED. EXAMINATION OF PIPE INDICATED A LEAK CAUSED BY DENT FROM THE LINE SITTING ON A ROCK.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 20010119 | 2001-06-21 | 22175 | DYNEGY MIDSTREAM SERVICES, L.P. |  |  | LA |  |  |  | 1050 | 2001-05-24 |  | YES | WC | 72 |  | YES | NO | LEAK |  | 0 | 0 | 130000 | 85825.4008 | 186972.6954 | Null | 0 | 25 | 567182 | 20010524 | 1000 | 1235 | BY TEST | 1875 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: GATHERING SYSTEM; PRTFL: FITTING; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1997; NMDIA: 12; THK: 0.218; SPEC: ANSI 900; SMYS: 53000; MANU: HACKNEY; MANYR: 1997; LOCLK: UNDER WATER; PNAME: KEVIN JOUBERT, PIPELINE TECH; PHONE: 3377742995; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: NO; CTEST: Null; TMPS: 0; LKPS: 0 | UNKNOWN OUTSIDE FORCE
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20010120 | 2001-06-21 | 30918 | KINDER MORGAN GP, INC. | PHILLIPSBURG | PHILLIPS | KS | 6 7661 |  | 1719+02 | 930 | 2001-05-24 | 1 | NO |  |  |  | Null | NO | RUPTURE |  | 0 | 0 | 69000 | 45553.482 | 99239.3537 | Null | 1 | 30 | 567198 | 20010524 | 657 | 795 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1946; NMDIA: 12; THK: 0.25; SPEC: X-42; SMYS: 42000; SEAM: WELDED; MANU: YOUNGSTOWN; MANYR: 1946; LOCLK: UNDER GROUND; PNAME: BERNADETTE M FRIEH; PHONE: 3039147829; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; STAT: NO; CTEST: Null; TMPS: 0; LKPS: 0 | A COUNTY MAINTAINER WAS GRADING THE ROAD AND CUT INTO THE PIPELINE, WHICH CROSSED UNDER THE ROAD.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010129 | 2001-07-16 | 6900 | GULF SOUTH PIPELINE CO | CARTHAGE | PANOLA | TX | 75633- |  |  | 2310 | 2001-06-16 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 125000 | 82524.4238 | 179781.4379 | Null | 0 | 30 |  | 20010616 | 650 | 1200 |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: COMPRESSOR; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1980; SMYS: 0; LOCLK: OTHER; LOCLO: INSIDE COMPRESSOR BUILDING; PNAME: JAMES H HILL; PHONE: 9036935172; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | THE COMPRESSOR FRAME EXPERIENCED MECHANICAL FAILURE IN THE CROSSHEAD AREA WHICH LOOSENED THE COMPRESSOR ROD PACKING GLAND. GAS PRESSURE ESCAPED BY THE PACKING GLAND AND IGNITED BEFORE THE UNIT SHUT DOWN. THE UNIT SHUTDOWN ON VIBRATION AND THE STATION FIRE AND GAS DETECTION "EMERGENCY SHUTDOWN SYSTEM" ACTIVATED AND SHUTDOWN THE STATION. FAILURE OCCURRED DUE TO LIQUID GETTING INTO THE UNIT.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010130 | 2001-07-13 | 6900 | GULF SOUTH PIPELINE CO | PENSACOLA | ESCAMBIA | FL | 3 2506 |  | 120+66.5 | 1020 | 2001-06-13 | 3 | NO |  |  |  | Null | NO | RUPTURE |  | 0 | 0 | 518140 | 342073.6398 | 745215.6338 | Null | 0 | 15 | 569368 | 20010613 | 300 | 375 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCE | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1943; NMDIA: 8; THK: 0.203; SMYS: 24000; SEAM: FURNACE LAP WELD; LOCLK: UNDER PAVEMENT; PNAME: JACK L ADAMS; PHONE: 7135443624; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | METALLURGICAL STUDY IS CURRENTLY BEING PERFORMED. A CAUSE WILL BE DETERMINED ONCE THE ANALYSIS IS COMPLETED. SEE ATTACHED INCIDENT SKETCH 6/13/2001 FOR DETAILS OF THE INCIDENT AREA. ADDITIONAL SUPPLEMENTAL REPORT(S) WILL BE FILED AS INFORMATION BECOMES AVAILABLE. SUPPLEMENTAL 12-13-2002- AS WAS STATED IN OUR INITIAL INCIDENT RESPONSE TO THE FAILURE THAT OCCURRED ON JUNE 13, 2001 ON OUR 8" LINE FEEDING THE TWO NAVAL BASES IN PENSACALA, WE SHIPPED OFF THE SECTION OF PIPE TO A THIRD PARTY FOR A METALLURGICAL EVALUATION OF THE FAILURE. THE PIPE WS EVALUATED BY KIEFNER AND ASSOCIATES, INC IN WORTHINGTON - OHIO. THE FAILURE OCCURRED WHILE A READY-MIX TRUCK WAS UNLOADING CONCRETE FOR A CONCRETE SLAB. THE REAR AXLES OF THE READY-MIX TRUCK WERE POSITIONED APPROXIMATELY ALMOST PARALLEL TO AND OVER THE PIPELINE. THE LINE WAS OPERATING AT APPROXIMATELY 300 PSIG AT THE TIME OF THE FAILURE. AN 8.2 FOOT SEGMENT OF FAILED PIPE WAS ANALYZED TO DETERMINE MATERIAL PROPERTIES, CHEMICAL PROPERTIES, AND TO CHARACTERIZE THE FRACTURE AREA. TWO ADDITIONAL 1-FOOT SEGMENTS WERE REMOVED FROM THE PIPELINE ADJACENT TO THE FAILURE TO PROVIDE MATERIAL FOR MECHANICAL TESTING. THE PIPE WAS 8.625 INCH OD, 0.203 INCH WT FURNACE LAP WELDED PIPE. THE CONSLUSIONS FROM THE TESTING PROVIDED BY KIEFNER AND ASSOCIATES INC, STATED THAT THE LAP-WELD SEAM WAS NOT CONTRIBUTING FACTOR TO THE FAILURE OF THE IRON PIPE. AN AREA OF MECHANICAL DAMAGE WAS LOCATED IN THE CENTER OF THE FRACTURE. THE MECHANICAL DAMAGE WAS PRESENT PRIOR TO THE FRACTURE, AS INDICATED BY THE MATCHING SMEARED METAL PATTERN APPEARING ON BOTH SIDES OF THE FRACTURE. THE PREEXISTING MECHANICAL DAMAGE LOCATED AT THE CENTER OF THE PIPELINE FRACTURE IS CONSIDERED TO BE A CONTRIBUTING FACTOR TO THE FAILURE. THE FINAL REPAIR CONSISTED OF REPLACING 3,200 FT OF 8" LINE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20010131 | 2001-07-10 | 13750 | NORTHERN NATURAL GAS CO (ENRON) | POYNETTE | COLUMBIA | WI |  | 21.491 |  | 1730 | 2001-06-14 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 42000 | 27728.2064 | 60406.5631 | Null | 0 | 30 | 569577 | 20010614 | 809 | 960 | BY TEST | 1332 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | UNSPECIFIED EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1966; NMDIA: 4.5; THK: 0.156; SPEC: API 5L A; SMYS: 35000; MANU: LONE STAR STEEL; LOCLK: UNDER GROUND; PNAME: MERLIN MOSEMAN; PHONE: 7136467344; PROT: Null; CPYR: 0; CAULK: NO DATA; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | LEAK RESULTED FROM SUSPECTED LIGHTING STRIKING PIPELINE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010132 | 2001-07-10 | 602 | RELIANT ENERGY GAS TRANSMISSION | CARBON CITY | LOGAN | AR | 7 2855 |  | 355+77 | 1500 | 2001-06-19 | 1 | NO |  |  |  | Null | YES | LEAK |  | 0 | 0 | 89000 | 58757.3898 | 128004.3838 | Null | 0 | 55 | 570128 | 20010619 | 640 | 1000 | BY TEST | 1345 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1968; NMDIA: 20; THK: 0.25; SPEC: API 5LX X60; SMYS: 60000; MANU: KAISER STEEL CO.; MANYR: 1967; LOCLK: UNDER GROUND; PNAME: TED VANDE KAMP; PHONE: 3184293606; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | THIRD PARTY CONTRACTOR CALLED IN LOCATE REQUEST. COMPANYS PIPELINE IN AREA IDENTIFIED ON LOCATE WAS MARKED. CONTRACTOR STRUCK ANOTHER ONE OF COMPANYS PIPELINES WHILE WORKING OUTSIDE THE AREA IDENTIFIED ON THE LOCATE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010138 | 2001-07-20 | 405 | ANR PIPELINE CO | DAYTON | MONTGOMERY | OH |  | 6.1 |  | 1755 | 2001-06-20 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 506539 | 334414.7131 | 728530.4781 | Null | 1 | 0 | 570250 | 20010620 | 650 | 1000 | BY TEST | 1554 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1991; NMDIA: 20; THK: 0.278; SPEC: 5L; SMYS: 60000; SEAM: ERW; MANU: AMERICAN; MANYR: 1991; LOCLK: UNDER GROUND; PNAME: LOUIS A. SALINAS; PHONE: 8326764169; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | THIRD PARTY/LANDOWNER HIT THE PIPELINE AS HE WAS EXCAVATING IN THE AREA FOR THE PURPOSE OF BURYING ANIMAL CARCASSES. A LEAK WAS LOCATED AND REPAIRED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20010142 | 2001-08-06 | 2616 | COLUMBIA GAS TRANSMISSION CORP | CORRINE | WYOMING | WV | 2 5826 |  | 43+30 | 2000 | 2001-07-08 | 1 | NO |  |  | WV | Null | NO | OTHER |  | 0 | 0 | 53800 | 35518.512 | 77377.9309 | Null | 5 | 0 | 572288 | 20010708 | 121 | 395 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | EARTH MOVEMENT | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1965 | 3.5 | 0.156 | UNKNOWN | 24000 | UNKNOWN | N/A | UNKNOWN | 1965 | OTHER | ABOVE GROUND PIPING UNDER FLOODING | ALYSIA M. DESKINS | 3043572511 | [6 empty] | Null | 0 | EARTH MOVEMENT: OTHER |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | LINE KA-14 WAS A SUSPENDED CROSSING OF THE GUYANDOTTE RIVER. THE CATACLYSMIC FLOODING OF THE GUYANDOTTE RIVER COMPLETELY WASHED OUT THE PIPELINE. THE FAILURE RESULTED FROM THE EXTREME EXTERNAL FORCES ASSOCIATED WITH THE FLOODING. ABOUT 200 FEET OF PIPELINE WAS WASHED OUT. A CREW WAS DISPATCHED TO THE AREA. HOWEVER, DUE TO MANY WASHED OUT ROADS AND BRIDGES AND DANGEROUS FLOODING CONDITIONS, IT TOOK 5 HOURS FOR THE CREW TO REACH SHUT OFF VALVES ON BOTH SIDES OF THE PIPELINE WASHOUT.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20010146 | 2001-08-15 | 13750 | NORTHERN NATURAL GAS CO (ENRON) | SATANTA | HASKELL | KS | 6 7870 | 0+65 |  | 2310 | 2001-08-15 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 0 | 0 | 0 | Null | 60 | 0 | 573077 | 20010715 | 140 | 430 | BY TEST | 540 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | OTHER | FLAN. GASKET | STEEL |  | REGULATOR/METERING SYSTEM |  | 1970 | 4 | 0.237 | API 5L A | 35000 | SEAMLESS | PLUG | ROCKWELL | 1970 | ABOVE GROUND |  | WILL BURKS | 7136467966 | [6 empty] | Null | 0 |  |  | Null |  | Null |  | Null |  | METALLIC FLANGE GASKET. | YES | 19720601 | WATER |  | 8 | 540 | GAS WAS IGNITED INSIDE A METER BUILDING. THE EXACT CAUSE CANNOT BE DETERMINE SUSPECTED TO BE GAS LEAKING FROM A FLANGE THAT WAS IGNITED BY LIGHTING.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010147 | 2001-08-20 | 19160 | TENNESSEE GAS PIPELINE CO | FALFURRIAS | BROOKS | TX |  | 403-2+9.26 | 488+93 | 1615 | 2001-07-23 | 1 | NO |  |  | TX | Null | NO | LEAK |  | 0 | 0 | 194560 | 128447.6152 | 279826.2124 | Null | 10 | 0 | 574018 | 20010723 | 669 | 860 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1951; NMDIA: 26; THK: 0.281; SPEC: API 5L A; SMYS: 52000; SEAM: ELECTRIC RESIST; MANU: NATIONAL TUBE; MANYR: 1950; LOCLK: UNDER GROUND; PNAME: LOUIS A. SALINAS; PHONE: 8326764169; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | AT APPROXIMATELY 3:20 PM ON 7/23/01, HAAS ANDERSON CONTRACTOR WAS DIGGING A HOLE WITH A 950 FRONT END LOADER/EXCAVATOR TO BURY A DEBRIS. THEY STRUCK THE TGP 26" 400-2 SAN SALVADOR LINE AND PUNCTURED A HOLE AT APPROXIMATE MP 403-2+9.26.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010148 | 2001-08-21 | 19235 | TEXAS EASTERN TRANSMISSION CORP (DUKE) | RACELAND | LAFOURCHE | LA |  | 84.30(LINE 40) | 4451+00 | 1015 | 2001-07-25 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 200000 | 132039.0782 | 287650.3006 | Null | 3 | 55 |  | 20010725 | 825 | 1100 | BY TEST | 2175 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: VALVE; MLKD: STEEL; PRTSY: PIPELINE; SMYS: 0; VALVE: GATE 2-INCH; MANU: WKM; MANYR: 1964; LOCLK: UNDER GROUND; PNAME: DWAYNE E TESCHENDORF; PHONE: 7136275573; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CAULC: MATERIAL; CAULO: 2-INCH WKM GATE VALVE; CTEST: YES; TESTD: 19690401; MED: WATER; TMPS: 24; LKPS: 2175 | A TAP VALVE, A 2-INCH WKM GATE VALVE, WAS BEING CLOSED TO INITIATE THE ABANDONMENT OF A LATERAL WHEN THE VALVE BONNET SEPARATED FROM THE BODY OF THE VALVE DUE TO A GASKET FAILURE RESULTING IN GAS RELEASE TO ATMOSPHERE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010150 | 2001-08-27 | 1541 | BP PIPELINES (ALASKA), INC | NORTH SLOPE |  | AK |  | 479+96.6 |  | 1200 | 2001-08-14 | 1 | NO |  |  | AK | Null | NO | LEAK |  | 0 | 0 | 100000 | 66019.5391 | 143825.1503 | Null | 0 | 11 | 576520 | 20010814 | 255 | 3440 | BY TEST | 4300 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1998; NMDIA: 6; THK: 0.375; SPEC: API 5L A; SMYS: 65000; SEAM: SEAMLESS; MANU: NIPPON STEEL; MANYR: 1997; LOCLK: ABOVE GROUND; PNAME: GREG SWANK; PHONE: 9075645586; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | WIND-INDUCED VIBRATION OF THE ELEVATED PIPELINE CREATING HIGH CYCLIC STRESSES MAY HAVE CAUSED A FATIGUE FAILURE OF A GIRTH WELD. A COMPLETE FAILURE ANALYSIS WILL BE CONDUCTED.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 20010151 | 2001-09-05 | 31547 | VOYAGEUR PIPELINE LLP | LONGVIEW | GREGG | TX |  | 4.3 | 277+04 | 1530 | 2001-07-25 | 3 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 6600 | 4357.2896 | 9492.4599 | Null | 0 | 45 |  | 20010725 | 220 | 1456 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: GATHERING SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1956; NMDIA: 8; THK: 0.25; SPEC: API 5LX X42; SMYS: 42000; MANU: NATIONAL TUBE; MANYR: 1956; LOCLK: UNDER GROUND; PNAME: GREG GEE; PHONE: 9036632477; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 20010724; MARK: YES; MRKTP: PERMANENT PLASTIC POST; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | BUILDING CONTRACTOR CONSTRUCTING A DRIVEWAY ENTRANCE TO NEW RETAIL STORE DUG TOO DEEP WITH ROTO MIXER, LINE WAS MARKED PREVIOUS DAY.
2021-02-26 10:36 | NO | NO | GG (Gas Gathering) | 20010154 | 2001-09-05 | 18508 | SOUTHERN INDIANA GAS & ELECTRIC CO | MIDWAY | SPENCER | IN | 4 7611 |  | SEC 13-6S-7W | 1430 | 2001-07-29 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 5000 | 3300.977 | 7191.2575 | Null | 1 | 0 |  | 20010730 | 600 | 600 | BY TEST | 906 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: GATHERING SYSTEM; PRTFL: OTHER; PRTFO: REGULATOR; MLKD: OTHER; MLKDO: SOFT GOODS; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1966; NMDIA: 1; SMYS: 0; MANU: FISHER; MANYR: 1966; LOCLK: ABOVE GROUND; PNAME: RICK L. SLAGLE; PHONE: 8124914611; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | AN ELECTRICAL STORM APPEARS TO HAVE CAUSED DAMAGE TO A REGULATOR FEEDING A 1-INCH PIPELINE NEAR A GAS WELLHEAD. LEAKING NATURAL GAS (FROM THE REGULATOR) IGNITED FROM AN UNKNOWN SOURCE. FLAMES FROM THE FIRE THEN ENGULFED TWO -(2) NEARBY 3" VALVES, DESTROYING THE FLANGE GASKET MATERIAL THUS ALLOWING GAS LEAKING FROM THESE AREAS TO FEED THE EXISTING FIRE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010155 | 2001-09-05 | 2620 | COLUMBIA GULF TRANSMISSION CO | ST LANDRY |  | LA | 7 0578 | M.P. 13.2 | 698+95 | 1100 | 2001-08-03 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 78000 | 51495.2405 | 112183.6172 | Null | 3 | 0 | 575297 | 20010803 | 879 | 935 | BY TEST | 1428 | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1954 | 3 | 0.5 | API 5LX X52 | 52000 | DOUBLE SUBMERGED ARC |  | NATIONAL TUBE | 1953 | UNDER GROUND |  | HENRY H. WANG | 7132674371 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | NO | 0 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | GAS DETECTOR INDICATED GAS LEAK DURING CASING VENT LEAKAGE SURVEY. PIN HOLE LEAK FOUND NEXT TO CASING SPACER DUE TO ATMOSPHERIC CORROSION.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010160 | 2001-09-06 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | BOKCHITO | BRYAN | OK | 7 4726 | 89 | 4696+14.2 | 1145 | 2001-08-09 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 135600 | 89522.495 | 195026.9038 | Null | 16 | 0 | 575940 | 20010809 | 805 | 1050 | BY TEST |  | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1989; NMDIA: 30; THK: 0.312; SPEC: API 5LX X70; SMYS: 70000; MANU: NAPA; MANYR: 1989; LOCLK: UNDER GROUND; PNAME: BERNADETTE M. FRIEH; PHONE: 3039147829; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CAULC: CONSTRUCTION; CTEST: YES; TESTD: 19891221; MED: WATER; TMPS: 8; LKPS: 1400 | DEAD VEGETATION DISCOVERED AND CONFIRMED TO BE GAS LEAKAGE-FOUND LEAK ON WELD.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20010161 | 2001-09-13 | 31451 | KINDER MORGAN TEXAS PIPELINE CO | REFUGIO | REFUGIO | TX | 78377- | 7.64 | 403+87 | 1045 | 2001-08-20 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 16680 | 11012.0591 | 23990.0351 | Null | 0 | 45 |  | 20010820 | 669 | 795 | BY TEST |  | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1956; NMDIA: 10.75; THK: 0.25; SPEC: API 5LX X42; SMYS: 1953; SEAM: SEAMLESS; MANU: UNKNOWN; MANYR: 1956; LOCLK: UNDER GROUND; PNAME: BERNADETTE M. FRIEH; PHONE: 3039147829; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | THIRD PARTY GOUGED INDEX 153 WHILE LAYING 3" FIBERGLASS PIPELINE AND DID NOT NOTIFY KMTP, CAUSING LINE TO LEAK.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010162 | 2001-09-13 | 4280 | EL PASO NATURAL GAS CO | WILLIAMS | COCONINO | AZ |  | MP 286+5040.00 |  | 500 | 2001-08-11 | 1 | NO |  |  |  | Null | YES | RUPTURE | 19 | 0 | 0 | 737500 | 486894.1007 | 1060710.4835 | Null | 1 | 27 | 576119 | 20010811 | 798.6 | 845 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1951 | 24 | 0.271 | API 5L A | 52000 | DSAW |  | REPUBLIC STEEL | 1951 | UNDER GROUND |  | LOUIS A. SALINAS | 8326764169 | EXTERNALLY | OTHER | STRESS CORROSION CRACKING | OTHER | UNDER INVESTIGATION | COATED | YES | 1951 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | EPNG LINE L1200 RUPTURED AT MP 286+5040, AT APPROXIMATELY 5:00 A.M. (MST) ON 8/11/01. THE EXACT CAUSE IS STILL UNDER INVESTIGATION. HOWEVER, STRESS CORROSION CRACKING (SCC) IS SUSPECTED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20010165 | 2001-09-19 | 5304 | FLORIDA GAS TRANSMISSION CO (ENRON) | ORLANDO | ORANGE | FL |  | 679.227 | 549+88 | 2250 | 2001-08-14 | 3 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 0 | 0 | 0 | Null | 0 | 0 | 576787 | 20010816 | 762 | 974 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1968 | 26 | 0.353 | API 5LX | 60000 |  |  | KAISER | 1968 | UNDER GROUND |  | MERLIN MOSEMAN | 7136467344 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1968 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | ELECTRICAL INTERFERENCE FROM ADJACENT TELEPHONE CABLE CAUSED LOCALIZED LOSS OF EFFECTIVE PIPELINE CATHODIC PROTECTION.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20010166 | 2001-09-21 | 6900 | GULF SOUTH PIPELINE CO | FRANKLIN | ST MARY | LA | 7 0538 | MP 45.856 | 2421+21 | 830 | 2001-08-21 |  | YES |  |  |  | Null | NO | RUPTURE |  | 0 | 0 | 50832 | 33559.0521 | 73109.2004 | Null | 0 | 30 | 577245 | 20010821 | 900 | 1015 | BY TEST | 1582 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1952; NMDIA: 20; THK: 0.5; SPEC: 5LX; SMYS: 42000; SEAM: SEAMLESS; MANU: AO SMITH; LOCLK: UNDER GROUND; PNAME: MIKE MARTIN; PHONE: 3379887103; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; STAT: NO; CTEST: Null; TMPS: 0; LKPS: 0 | CONTRACTOR USING A TREE GRINDER ON AMPHIBIOUS EXCAVATOR WAS CLEANING RIGHT OF WAY FOR WILLIAMS FIELD SERVICES AND INADVERTENTLY SET GRINDER DOWN ON 20" PIPELINE AND PUNCTURED THE PIPELINE. THE PIPELINE WAS BURIED ONLY 6" BELOW SOIL BY DESIGN FOR ARMY CORP OF ENGINEERS LEAVE CROSSING.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20010167 | 2001-09-20 | 12690 | MONTANA POWER CO | BEAVERHEAD |  | MT |  | MP 55.7 | 2941+04 | 1150 | 2001-09-07 | 1 | NO |  |  |  | Null | NO | RUPTURE | 1 | 0 | 0 | 50000 | 33009.7695 | 71912.5752 | Null | 0 | 30 | 579144 | 20010907 | 365 | 590 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1964; NMDIA: 3; THK: 0.156; SPEC: API 5LX X42; SMYS: 42000; SEAM: ERW; MANU: SOUTHWESTERN PIPE INC; MANYR: 1964; LOCLK: UNDER GROUND; PNAME: JAY WATERMAN; PHONE: 4064982441; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | A CONTRACTOR DIGGING WITH AN LARGE TRACK MOUNTED EXCAVATOR HIT THE MPC 3" DILLION TO BARRETTS NATURAL GAS TRANSMISSION LINE AT MP 55.7. THE IMPACT OF THE EXCAVATOR TOOTH PUNCTURED THE LINE AND NATURAL GAS BEGAN BLOWING IMMEDIATELY. HIGH PRESSURE GAS ESCAPED BUT DID NOT IGNITE. APPROXIMATELY 90 FARM TAP CUSTOMERS AS WELL AS ONE LARGE INDUSTRIAL CUSTOMER LOST NATURAL GAS SERVICE. NO INJURIES OCCURRED.A CONTRACTOR DIGGING WITH AN LARGE TRACK MOUNTED EXCAVATOR HIT THE MPC 3" DILLION TO BARRETTS NATURAL GAS TRANSMISSION LINE AT MP 55.7. THE IMPACT OF THE EXCAVATOR TOOTH PUNCTURED THE LINE AND NATURAL GAS BEGAN BLOWING IMMEDIATELY. HIGH PRESSURE GAS ESCAPED BUT DID NOT IGNITE. APPROXIMATELY 90 FARM TAP CUSTOMERS AS WELL AS ONE LARGE INDUSTRIAL CUSTOMER LOST NATURAL GAS SERVICE. NO INJURIES OCCURRED.A CONTRACTOR DIGGING WITH AN LARGE TRACK MOUNTED EXCAVATOR HIT THE MPC 3" DILLION TO BARRETTS NATURAL GAS TRANSMISSION LINE AT MP 55.7. THE IMPACT OF THE EXCAVATOR TOOTH PUNCTURED THE LINE AND NATURAL GAS BEGAN BLOWING IMMEDIATELY. HIGH PRESSURE GAS ESCAPED BUT DID NOT IGNITE. APPROXIMATELY 90 FARM TAP CUSTOMERS AS WELL AS ONE LARGE INDUSTRIAL CUSTOMER LOST NATURAL GAS SERVICE. NO INJURIES OCCURRED.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20010169 | 2001-09-25 | 405 | ANR PIPELINE CO |  |  | LA |  | 750-32 MP00 |  | 750 | 2001-08-26 |  | YES | E.I. | 266 |  | Null | NO | LEAK |  | 0 | 0 | 75000 | 49514.6543 | 107868.8627 | Null | 0 | 0 | 577758 | 20010826 | 1050 | 1300 | BY TEST | 2690 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1970; NMDIA: 12; THK: 0.375; SPEC: API 5L A; SMYS: 46000; SEAM: ERW WELD; MANU: AMERICAN STEEL YEAR.; MANYR: 1970; LOCLK: UNDER WATER; PNAME: LOUIS A. SALINAS; PHONE: 8326764169; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | A LEAK WAS LOACTAED AFTER GAS BUBBLES WERE REPORTED IN EI 266 IN AREA OF PLIDCO REPAIR CLAMP INSTALLED IN 1987.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20010170 | 2001-09-25 | 19160 | TENNESSEE GAS PIPELINE CO | GULF OF MEXICO |  | LA |  | 523M-102+17.98 |  | 1600 | 2001-08-26 |  | YES | SHIP SHOAL | 198G |  | Null | NO | LEAK |  | 0 | 0 | 70000 | 46213.6774 | 100677.6052 | Null | 4 | 0 | 577808 | 20010826 | 950 | 1250 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: VALVE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1969; SMYS: 0; VALVE: 16" WHEATLEY CHECK VALVE; MANU: WHEATLEY; MANYR: 1969; LOCLK: UNDER WATER; PNAME: LOUIS A. SALINAS; PHONE: 8326764169; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; NOTDT: 20010930; MARK: NO; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | A SHRIMPERS NET, APPARENTLY SNAGGED A SUBSEA ASSEMBLY, UNDER THE VALVE GUARD AT SIDE VALVE 523M-102, IN SHIP SHOAL BLOCK 198G.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010171 | 2001-09-28 | 18516 | SOUTHERN NATURAL GAS CO |  |  | LA |  | 13.90 |  | 1700 | 2001-08-31 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 90000 | 59417.5852 | 129442.6353 | Null | 0 | 0 |  | 20010831 | 970 | 1100 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1958; NMDIA: 12; THK: 0.312; SPEC: API 5L A; SMYS: 46000; SEAM: ERW; MANU: LONE STAR PIPE; MANYR: 1957; LOCLK: UNDER GROUND; PNAME: LOUIS A. SALINAS; PHONE: 8326764169; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | A LEAK WAS LOCATED ON THE 12" WEST DELTA BLOCK 30 LINE, AT MP 13.90, AFTER BUBBLES WERE SPOTTED IN THE PIPE DITCH. PIPE IS IN THE MARSH UNDER SEVERAL FEET OF MUD. LINE WILL BE ISOLATED AND THE REPAIR MADE BY INSTALLING A LEAK CLAMP. THE REPAIR IS PENDING, AFTER APPROVAL FOR A CORPS OF ENGINEERS PERMIT IS GRANTED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010174 | 2001-10-01 | 12462 | MID LOUISIANA GAS CO | FAIRBANKS | OUACHITA | LA |  | MILEPOST 3 |  | 1220 | 2001-09-03 | 1 | NO |  |  | LA | Null | NO | RUPTURE | 10 | 0 | 0 | 450000 | 297087.9259 | 647213.1764 | Null | 0 | 15 | 578944 | 20010905 | 213 | 245 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1926 | 22 | 0.406 | GRADE B | 24000 | OTHER |  |  | 1926 | UNDER GROUND |  | BLAINE BROWN | 7136508900 | INTERNALLY |  |  | OTHER | WATER COLLECTING IN LOW SPOT | COATED | YES | 1960 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | FAILURE UNDER INVESTIGATION. PIPE SENT TO LAB FOR ANALYSIS. HISTORICAL RECORDS AND PIPELINE OPERATIONS BEING REVIEWED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010177 | 2001-10-15 | 20010 | U G I CORP | EAST COCALICO | LANCASTER | PA | 1 7517 | NORTHEAST OF HILL ROAD |  | 1442 | 2001-09-17 | 3 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 80000 | 52815.6313 | 115060.1202 | Null | 2 | 52 | 580005 | 20010917 | 355 | 400 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: FITTING; MLKD: STEEL; PRTSY: PIPELINE; NMDIA: 8; THK: 0.25; SPEC: API 5L A; SMYS: 30000; SEAM: LAP WELDED; LOCLK: UNDER GROUND; PNAME: JAMES R. HEINTZ; PHONE: 6107963528; PROT: Null; CPYR: 0; CAULK: OPERATOR ACTION; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | WHILE EXCAVATING A PROPERLY MARKED PIPELINE TO EXPOSE A CONTROL FITTING, UGIS CONTRACTOR HIT AN ADJACENT SERVICE PUNCH TEE THAT THE CONTRACTOR HAD PREVIOUSLY INSTALLED. THE SERVICE PUNCH TEE WAS TORN PARTIALLY FROM THE MAIN PIPELINE. GAS SUBSEQUENTLY ESCAPED. FINDINGS INDICATE THE CONTRACTOR WAS USING POWERED EXCAVATING EQUIPMENT TOO CLOSE TO THE PIPELINE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010178 | 2001-10-22 | 2899 | CROSSTEX PIPELINE CO | CORPUS CHRISTI | NUCES | TX | 7 8408 | 196+89 |  | 1620 | 2001-07-24 | 3 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 124000 | 81864.2285 | 178343.1864 | Null | 0 | 30 |  | 20010724 | 580 | 1019 | BY TEST | 1529 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1987; NMDIA: 12.75; THK: 0.25; SPEC: API 5LX X52; SMYS: 0; LOCLK: ABOVE GROUND; PNAME: LEONARD STROMAN; PHONE: 3612994000; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: YES; MRKTP: PIPELINE MARKERS SIGNS; STAT: NO; CTEST: Null; TMPS: 0; LKPS: 0 | TRAIN DERAILED OFF TRACK WHICH CAUSED ONE TRAIN CAR TO LAND ON PIPELINE CROSSING A DRAINAGE DITCH.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20010179 | 2001-10-22 | 13845 | NORTHWEST PIPELINE CORP (WGP) | POST FALLS | KOOTENAI | ID | 8 3854 | 182.5733 | 9639+87 | 945 | 2001-09-21 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 64215 | 42394.447 | 92357.3203 | Null | 59 | 50 | 580493 | 20010921 | 657 | 811 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: VALVE; MLKD: STEEL; PRTSY: REGULATOR/METERING SYSTEM; PRTYR: 1957; SMYS: 0; VALVE: GATE; MANU: COOPER INDUSTRIES; MANYR: 1957; LOCLK: UNDER GROUND; PNAME: ERIC CARLSON; PHONE: 8015846321; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | WHILE ATTEMPTING TO REPAIR A 2" WKM GATE VALVE AT THE MCGUIRE METER STATION, THE TOP OF THE VALVE CAME APART DUE TO A BROKEN STEM IN THE INTERIOR OF THE VALVE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010182 | 2001-10-22 | 6900 | GULF SOUTH PIPELINE CO | RINGGOLD | BEINVILLE | LA | 7 1068 | INDEX 903-04 | 12+50 | 400 | 2001-09-25 | 1 | NO |  |  |  | Null | NO | RUPTURE | 9 | 0 | 0 | 115850 | 76483.636 | 166621.4366 | Null | 1 | 0 | 580834 | 20010925 | 1900 | 2160 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | INTERNAL | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; NMDIA: 8; THK: 0.312; SPEC: API 5LX; SMYS: 52000; SEAM: SEAMLESS; MANU: U S STEEL; LOCLK: UNDER GROUND; PNAME: JERRY GULLETTE; PHONE: 3188948223; LOC: INTERNALLY; ADESC: LOCALIZED PITTING; COAT: COATED; PROT: YES; CPYR: 1966; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | THE PIPE WILL BE TAKEN TO A METALLURGIST TO DETERMINE THE CAUSE OF THE INCIDENT. 11-19-2001 - BASED ON THE ANALYSIS FROM METALLURGICAL CONSULTANTS, INC. THE FAILURE WAS CAUSED BY INTERNAL CORROSION. THE INTERNAL CORROSION APPEARS TO BE THE RESULTS OF (MIC) MICROBIOLOGICALLY INDUCED CORROSION.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010194 | 2001-11-07 | 2616 | COLUMBIA GAS TRANSMISSION CORP | LEESBURG | LOUDOUN | VA | 2 0176 |  | 530+03 | 1905 | 2001-10-09 | 3 | NO |  |  | VA | Null | NO | LEAK |  | 0 | 0 | 100000 | 66019.5391 | 143825.1503 | Null | 3 | 25 | 582452 | 20011009 | 764 | 899 | BY TEST | 1935 | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: WELD; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 2001; NMDIA: 30; THK: 0.417; SPEC: API 5L A; SMYS: 65000; SEAM: DSAW; MANU: BERG; LOCLK: UNDER GROUND; PNAME: ALYSIA M. DESKINS; PHONE: 3043572511; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CAULC: CONSTRUCTION; CAULO: THE FAILURE OCCURRED IN A GIRTH WELD.; CTEST: NO; TMPS: 0; LKPS: 0 | THE PIPELINE LEAK WAS CAUSED BY A GIRTH WELD FAILURE OF A RECENTLY CONSTRUCTED PIPELINE SECTION. THE FORMAL FAILURE INVESTIGATION HAS NOT BEEN COMPLETED. HOWEVER, PRELIMINARY RESULTS INDICATE THAT THIS FAILURE WAS CAUSED BY A COMBINATION OF CONSTRUCTION AND PRESSURIZATION STRESS ACTING UPON A HYDROGEN CRACK.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010195 | 2001-11-16 | 19160 | TENNESSEE GAS PIPELINE CO | GULF OF MEXICO |  | LA |  | 526A+2401+3.84 |  | 1440 | 2001-10-18 |  | YES |  |  |  | Null | NO | LEAK |  | 0 | 0 | 275000 | 181553.7325 | 395519.1633 | Null | 26 | 0 | 583615 | 20011018 | 951 | 1440 | BY TEST | 2032 | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1972; NMDIA: 12; THK: 0.5; SMYS: 42000; MANU: U S STEEL; MANYR: 1972; LOCLK: UNDER WATER; PNAME: LOUIS A. SALINAS; PHONE: 8326764169; PROT: Null; CPYR: 0; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | BUBBLES REPORTED BY WORK BOAT IN SP. BLK. 39 AREA, APPROXIMATELY 300 FEET WEST OF 526A-2400 LINE. POSSIBLE STRESS CRACK DUE TO MUD SLIDE ACTIVITY IN THE AREA.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010196 | 2001-11-16 | 19160 | TENNESSEE GAS PIPELINE CO | OFFSHORE |  | LA |  | 526A-101+8.75 |  | 1230 | 2001-10-16 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 570000 | 376311.3727 | 819803.3567 | Null | 6 | 0 | 583347 | 20011016 | 862 | 1133 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCE | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1956; NMDIA: 20; THK: 0.375; SPEC: API 5L A; SMYS: 52000; MANU: AO SMITH; MANYR: 1956; LOCLK: UNDER WATER; PNAME: LOUIS A. SALINAS; PHONE: 8326764169; PROT: Null; CPYR: 0; CAULK: EARTH MOVEMENT: LANDSLIDE/WASHOUT; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | A LEAK WAS LOCATED AFTER GAS BUBBLES WERE REPORTED APPROXIMATELY 20 FEET WEST OF THE EMPIRE WATERWAY CROSSING. AFTER FURTHER INVESTIGATION, IT WAS DETERMINED THAT THE AREA HAD BEEN SCOURED DUE TO EROSION, AND THE PIPE HAD BECOME EXPOSED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010197 | 2001-11-21 | 19160 | TENNESSEE GAS PIPELINE CO | OFFSHORE |  | LA |  | 821E-104+11.31 |  | 1030 | 2001-10-24 |  | YES | W.C. | 53 |  | Null | NO | LEAK |  | 0 | 0 | 123000 | 81204.0331 | 176904.9349 | Null | 0 | 0 |  | 20011024 | 1059 | 1440 | BY TEST | 2162 | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | FITTING |  | STEEL |  | PIPELINE |  | 1981 | 2 | 0.318 | API 5L A | 35000 |  |  | U S STEEL | 1981 | UNDER WATER |  | LOUIS A. SALINA | 8326764169 | INTERNALLY | LOCALIZED PITTING |  | OTHER | EROSION/CORROSION | COATED | YES | 1981 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | A LEAK WAS LOCATED AFTER GAS BUBBLES WERE REPORTED IN WC 53, 1/2 MILE NORTHEST OF THE WC BLK. 53 PLATFORM. INVESTIGATIVE DIVE REVEALED A 2" ELL ON THE BYPASS LINE AROUND SV 821E-114A WAS LEAKING. INTERNAL CORROSION IS THE APPARENT CAUSE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20010198 | 2001-12-17 | 2588 | COLUMBIA GAS OF MARYLAND INC | WESTERNPORT | ALLEGHANY | MD | 2 1562 | 3546 |  | 1630 | 2001-11-07 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 0 | 0 | 0 | Null | 3 | 0 | 585408 | 20011107 | 40 | 43 |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: NO DATA; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1907; SMYS: 0; LOCLK: OTHER; LOCLO: PIPELINE DUG BY HAND INTO ROCK OF MOUNTAINSIDE; PNAME: TRACEY L FAULK; PHONE: 7245273960; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | WILDFIRE BURNING ON THE MOUNTAINSIDE CROSSED OVER THE AREA OF THE PIPELINE AND IGNITED SMALL LEAKS THAT WERE ON A REGULAR MONITORING SCHEDULE. SERVICE WAS INTERRUPTED TO 70 CUSTOMERS WHILE AREA WAS SECURED AND 21 SECTION OF PIPE WAS REPLACED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20010199 | 2001-12-27 | 19590 | TRANSOK INC | HUGHES |  | OK |  | 12.5 |  | 105 | 2001-10-12 | 1 | NO |  |  |  | Null | NO | RUPTURE | 4 | 0 | 0 | 107500 | 70971.0045 | 154612.0366 | Null | 2 | 0 |  | 20011012 | 735 | 100 | BY TEST | 1464 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: NEAR A WELD; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1995; NMDIA: 24; THK: 0.281; SPEC: API 5LX X65; SMYS: 0; MANU: STUPP CORPORATION; MANYR: 1995; LOCLK: UNDER GROUND; PNAME: ERIC R SPERLING; PHONE: 4055575235; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | AT 0105 HRS A DROP IN PRESSURE WAS EXPERIENCED ON TRANSOK LINE #31. THE DROP IN PRESSURE WAS THE RESULT OF A RUPTURE. THE ESCAPING GAS IGNITED AND A FIRE RESULTED. THE INCIDENT IS UNDER INVESTIGATION TO IDENTIFY CAUSE. AFTER DETERMINATION A SUPPLEMENTAL REPORT WILL FOLLOW. 1-17-02 AFTER FURTHER INVESTIGATION, IT WAS CONCLUDED THA THE CAUSE OF THE TRANSOK LINE #31 RUPTURE AND SUBSEQUENT FIRE WAS DUE TO A WELD FAILURE RESULTING FROM TENSILE OVERLOAD. THE ULTIMATE FAILURE OCCURRED AS A RESULT OF A COMBINATION OF THE FOLLOWING CAUSAL FACTORS: EXCESSIVE LOADING ON THE PIPE DUE TO PIPE MISALIGNMENT, RESIDUAL MAGNETIC FIELDS, AND EXTERNAL LOADING CAUSED BY SETTLING OF BACKFILL AND SIGNIFICANT RAINFALL.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20020004 | 2002-01-08 | 6900 | GULF SOUTH PIPELINE CO | CALVIN | WINN | LA | 71031- | 381.93 | 20165+90 | 2010 | 2001-12-07 | 1 | NO |  |  |  | Null | YES | LEAK |  | 0 | 0 | 89634 | 59175.9537 | 128916.2352 | Null | 0 | 0 | 588102 | 20011207 | 850 | 936 | BY CFR 192.619(A)(3) |  | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1952; NMDIA: 30; THK: 0.375; SPEC: API 5LX; SMYS: 52000; SEAM: ELECTRIC FLASH WELD; MANU: AOS; MANYR: 1952; LOCLK: NO DATA; PNAME: JIMMY HUCKABY; PHONE: 3183523215; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | HAIRLINE FRACTURE DEVELOPED IN THE PIPE WALL DUE TO ELEVATED HARDNESS. THE LOCATION ALREADY HAD A REINFORCING SLEEVE OVER THE PIPE. THE PIPE STOPPED LEAKING WHEN THE PRESSURE WAS REDUCED. THE LOCATION WAS REMOTE AND WAS NEVER CONSIDERED UNSAFE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20020005 | 2002-01-08 | 30826 | WILLIAMS FIELD SERVICES |  |  |  |  | LONGITUDE 28" 33' 34" |  | 1700 | 2001-09-20 |  | YES | GALVESTON | 419 |  | Null | NO | LEAK |  | 0 | 0 | 250000 | 165048.8477 | 359562.8758 | Null | 4 | 0 |  | 20010921 | 915 | 1440 | BY TEST | 2163 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: VALVE; MLKD: STEEL; PRTSY: PIPELINE; NMDIA: 12; THK: 0.687; SPEC: ANSI 900; SMYS: 2220; VALVE: BALL VALVE; MANU: GROVE OR CAMERON; MANYR: 1990; LOCLK: UNDER WATER; PNAME: KENNETH L LYBARGER; PHONE: 9185748029; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | BUBBLES WERE REPORTED ON GALVESTON BLOCK 419. INVESTIGATION DETERMINED A 12" VALVE WAS LEAKING. THE VALVE AND ASSOCIATED PIPE WERE REMOVED AND REPLACED WITH A SPOOL OF NEW, PRE-TESTED PIPE OF SAME GRADE, AND THE LINE RETURNED TO SERVICE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20020006 | 2002-01-07 | 2616 | COLUMBIA GAS TRANSMISSION CORP | HENRY CLAY | FAYETTE | PA | 1 5459 |  | 2247+47 | 1325 | 2001-12-07 | 1 | NO |  |  |  | Null | NO | RUPTURE | 10 | 0 | 0 | 348000 | 229747.996 | 500511.523 | Null | 2 | 0 | 588053 | 20011207 | 825 | 936 | BY CFR 192.619(A)(3) |  | CONSTRUCTION/MATERIAL DEFECT | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1960 | 20 | 0.25 | API 5LX | 52000 | ELECTRIC RESISTANCE WELD |  | YOUNGSTOWN SHEET | 1960 | NO DATA |  | DAVID D ANDERSON | 7242232766 | [6 empty] | Null | 0 |  |  | Null |  | Null |  | Null | CONSTRUCTION |  | YES | 19601010 | WATER |  | 24 | 1023 | ON 12/7/2001 LINE 1804 RUPTURED IN THE VICINITY OF A SIDE CONNECTION. THERE WERE NO INJURIES.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20020007 | 2002-01-10 | 2600 | COLUMBIA GAS OF PENNSYLVANIA | PITTSBURGH | ALLEGHENY | PA |  | 4-63 |  | 1229 | 2001-12-10 | 3 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 100000 | 66019.5391 | 143825.1503 | Null | 26 | 0 | 585285 | 20011210 | 65 | 80 |  |  | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1957; NMDIA: 16; SMYS: 0; LOCLK: UNDER GROUND; PNAME: TRACEY L FAULK; PHONE: 7245273960; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; MARK: NO; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | SEWER CONTRACTOR PERFORMING EMERGENCY REPAIR HIT 16 STEEL LINE. LINE WAS HIT WITH TOOTH OF EXCAVATION EQUIPMENT CAUSING 2X3 GASH IN PIPE.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20020012 | 2002-01-18 | 22617 | WILLIAMS GAS PIPELINE CENTRAL, INC. | WAVERLY | LAFAYETTE | KS |  |  | 1800+44 | 100 | 2001-11-13 | 1 | NO |  |  | KS | Null | NO | LEAK |  | 0 | 0 | 800000 | 528156.3126 | 1150601.2024 | Null | 4 | 30 | 585912 | 20011113 | 470 | 500 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | EXTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1978 | 8.625 | 0.322 | API 5L A | 35000 | ERW |  | LONESTAR | 1977 | ABOVE GROUND |  | JOHN M. HAMLIN | 2706886965 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | COATED | NO | 0 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | ROAD SALT SPILLED ON TO LINE CAUSING CORROSION. THE CORROSION OCCURRED WHERE ROAD ALS AND GRIME SPILLED DOWN ON THE LINE. THIS BRIDGE CROSSING WAS SCHEDULED TO BE REPLACED WITH A ROAD BORE IN 2002. HOWEVER, BECAUSE OF THE LEAK, THIS PROJECT WILL BEGIN IN DECEMBER 2001. THE COST OF THIS PROJECT WILL BE BETWEEN $800,000 AND $1,000,000.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 20020013 | 2002-01-18 | 602 | RELIANT ENERGY GAS TRANSMISSION | BLUE SPRING | GARLAND | AR | 7 1909 | 38 | 1587+76 | 1000 | 2001-11-05 | 1 | NO |  |  |  | Null | NO | OTHER |  | 0 | 1 | 0 | 0 | 0 | Null | 1 | 30 |  | 20011105 | 25 | 1000 | BY TEST | 1294 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: PIG LAUNCHER; MLKD: STEEL; PRTSY: OTHER; PRTSO: PIG LAUNCHER; PRTYR: 1959; NMDIA: 16; THK: 0.25; SPEC: API 5LX X46; SMYS: 46000; SEAM: ERW; VALVE: GATE; MANU: GROVE; LOCLK: ABOVE GROUND; PNAME: TED VANDE KAMP; PHONE: 3184293606; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | COMPANY EMPLOYEE AND TWO CONTRACT EMPLOYEES WERE AT THE JESSIEVILLE SCRAPER TRAP YARD TO INSERT AND RUN A 16" CLEANING PIG IN COMPANYS 16" PIPELINE, BT-1-AS, LOCATED IN RURAL GARLAND COUNTY, ARKANSAS ON NOVEMBER 5, 2001. COMPANYS EMPLOYEE REMOVED THE 16" LAUNCHER FROM SERVICE BY CLOSING ALL ASSOCIATED VALVES AND BLOWING DOWN THE LAUNCHER. AFTER THE BLOWDOWN WAS COMPLETED COMPANY EMPLOYEE NOTICED UNRELATED LEAKAGE FROM A 4" KICKER LINE VALVE, AND USING A HIGH-PRESSURE GREASE GUN, GREASED THE 4" VALVE. COMPANYS EMPLOYEE AND THE TWO CONTRACT EMPLOYEES OPENED THE SCRAPER TRAP DOOR AND INSERTED THE PIG. BEFORE THE LAUNCHER DOOR COULD BE SHUT THE PIG WAS EJECTED FROM THE OPEN END OF THE LAUNCHER STRIKING BOTH CONTRACT EMPLOYEES. BOTH CONTRACT EMPLOYEES WERE TAKEN TO ST. JOSEPH HOSPITAL IN HOT SPRINGS, ARKANSAS. ONE BEING TREATED IN THE EMERGENCY ROOM AND RELEASED AND THE OTHER ADMITTED WITH A BROKEN LEG.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20020019 | 2002-01-23 | 14210 | OKLAHOMA NATURAL GAS CO | TULSA | TULSA | OK | 7 4145 |  |  | 700 | 2001-10-23 | 3 | NO |  |  | OK | Null | NO | OTHER |  | 0 | 0 | 55000 | 36310.7465 | 79103.8327 | Null | 3 | 50 | 584230 | 20011023 | 252 | 300 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION LINE OF DISTRIBUTION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1961; NMDIA: 18; THK: 0.25; SMYS: 42000; SEAM: EW; MANYR: 1960; LOCLK: UNDER GROUND; PNAME: RICKY D. MEAD; PHONE: 9188318204; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: YES; NOTDT: 20010927; MARK: YES; MRKTP: FLAG AND PAINT; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | EXCAVATOR USING A TRACKHOE DAMAGED ONGS 18-INCH PIPELINE.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20020020 | 2002-01-23 | 22617 | WILLIAMS GAS PIPELINE CENTRAL, INC. | SOLOMON RAPIDS | MITCHELL | KS |  | 77.4 | 4091+24 | 900 | 2001-12-12 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 50000 | 33009.7695 | 71912.5752 | Null | 1 | 0 | 588431 | 20011212 | 500 | 550 | BY TEST | 605 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: UNKNOWN; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1929; NMDIA: 8.625; THK: 0.203; SPEC: UNKNOWN; SMYS: 24000; SEAM: SEAMLESS; MANU: NATIONAL TUBE; LOCLK: OTHER; LOCLO: UNDER RAILROAD; PNAME: JOHN M. HAMLIN; PHONE: 2706886965; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | LEAK IS INSIDE CASING. UNKNOWN CAUSE. NEW XING WILL EXCEED $50,000. LEAK WILL BE INVESTIGATED AFTER REPAIRS.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20020021 | 2002-01-23 | 22617 | WILLIAMS GAS PIPELINE CENTRAL, INC. | LEBANON | SMITH | KS |  | 20.6 | 1090+78 | 400 | 2001-12-06 | 1 | NO |  |  | KS | Null | NO | LEAK |  | 0 | 0 | 50000 | 33009.7695 | 71912.5752 | Null | 1 | 0 | 587965 | 20011206 | 350 | 400 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: UNKNOWN; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1957; NMDIA: 6.625; THK: 0.156; SPEC: API; SMYS: 35000; SEAM: ERW; MANU: NEWPORT; MANYR: 1955; LOCLK: UNDER PAVEMENT; PNAME: JOHN M. HAMLIN; PHONE: 2706886965; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | LEAK IS DETECTED INSIDE CASING. UNKNOWN CAUSE. NEW ROAD XING WILL EXCEED 50,000.00. LEAK WILL BE INVESTIGATED AFTER REPAIRS.
2021-02-26 10:36 | NO | NO | GT (Gas Transmission) | 20020024 | 2002-01-25 | 15007 | PACIFIC GAS & ELECTRIC CO | GERBER | TEHAMA | CA |  | 149.18 |  | 535 | 2001-11-06 | 2 | NO |  |  |  | Null | NO | OTHER |  | 0 | 0 | 0 | 0 | 0 | Null | 1 | 10 | 585264 | 20011106 | 800 | 1000 | BY TEST | 1500 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: FITTING; MLKD: STEEL; PRTSY: COMPRESSOR STATION; PRTYR: 1971; NMDIA: 25; SPEC: TBD; SMYS: 0; LOCLK: ABOVE GROUND; PNAME: SHAN BHATTACHARYA; PHONE: 4159736999; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | LUBE OIL MIST RELEASED FROM A CRACKED 1/4- IN PIPE NIPPLE FLASHED WHEN THE TURBINE UNIT REACHED OPERATING TEMP. COMPRESSOR STATION SHUT DOWN SAFETY- NO RELEASE OF GAS. TURBINE SKID, COMPRESSOR AND COMPRESSOR BUILDING SEVERELY DAMAGED.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 20020025 | 2002-01-30 | 30940 | WILLIAMS ENERGY GROUP-FIELD SERVICES | MOSQUITO BAY MARSH | TERREBONNE | LA |  | 128.16 | 6819+98 | 1000 | 2001-12-06 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 450000 | 297087.9259 | 647213.1764 | Null | 3 | 0 | 587925 | 20011206 | 800 | 1170 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  |  | 20 | 0.312 | API 5LX | 52000 | FLASH WELD |  | AO SMITH | 1959 | OTHER | TIDAL MARSH | JOE FREISBERG | 9185730810 | INTERNALLY | LOCALIZED PITTING |  |  |  | COATED | YES | 1959 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | A TEMPORARY LEAK CLAMP WAS INSTALLED; LINE HAS BEEN SHUT-IN AND WILL NOT BE BROUGHT BACK INTO SERVICE UNTIL AN ASSESSMENT OF THE LINES CONDITION IS DETERMINED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20020037 | 2002-02-20 | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) |  |  | TX |  | 1310+16.1 |  | 1550 | 2001-11-21 |  | YES | HIGH LAND | 72 |  | Null | NO | LEAK |  | 0 | 0 | 162350 | 107182.7217 | 233500.1315 | Null | 0 | 0 | 586663 | 20011121 | 1040 | 1200 | BY TEST |  | CORROSION | CORROSION | INTERNAL | TRANSMISSION SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  | 1980 | 16 | 0.312 | API 5LX X52 | 2028 | SEAMLESS |  | UNKNOWN |  | UNDER GROUND |  | BERNADETTE M. FRIEH | 3039147829 | INTERNALLY | LOCALIZED PITTING |  | OTHER |  | COATED | YES | 1980 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | A SMALL PINHOLE LEAK WAS DISCOVERED ON THE BOTTOM OF THE PIPE NEAR THE 6 OCLOCK POSITION. A LEAK CLAMP WAS INSTALLED.
2021-02-26 10:36 | YES | NO | GT (Gas Transmission) | 20020042 | 2002-03-08 | 15007 | PACIFIC GAS & ELECTRIC CO | WINDSOR | SONOMA | CA | 9 5492 | 58.04 |  | 42 | 2001-12-16 | 3 | NO |  |  |  | Null | NO | RUPTURE | 610 | 0 | 0 | 120000 | 79223.4469 | 172590.1804 | Null | 1 | 28 | 588825 | 20011216 | 415 | 720 | BY TEST | 1600 | DAMAGE BY OUTSIDE FORCE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | PRTLK: TRANSMISSION SYSTEM; PRTFL: BODY OF PIPE; MLKD: STEEL; PRTSY: PIPELINE; PRTYR: 1967; NMDIA: 12; THK: 0.25; SPEC: API 5LX X52; SMYS: 0; SEAM: ERW; MANU: UNKNOWN; LOCLK: OTHER; LOCLO: EXPOSED BY 3RD PARTY; PNAME: SHAN BHATTACHARYA; PHONE: 4159736999; PROT: Null; CPYR: 0; CAULK: OUTSIDE/THIRD PARTY; NOTIF: NO; MARK: NO; STAT: YES; CTEST: Null; TMPS: 0; LKPS: 0 | IT IS SUSPECTED THAT A CONTRACTOR EXCAVATING OVER THE LINE DAMAGED THE LINE ENOUGH TO SIGNIFICANTLY WEAKEN IT TO THE EXTENT THAT IT RUPTURED DAYS AFTER THE DAMAGE.
2021-02-26 10:36 | YES | NO | GG (Gas Gathering) | 20020067 | 2002-05-14 | 30940 | WILLIAMS ENERGY GROUP-FIELD SERVICES | MOSQUITO BAY | TERREBONNE | LA |  | 128.99 | 6810+98 | 1000 | 2001-06-30 | 1 | NO |  |  |  | Null | NO | LEAK |  | 0 | 0 | 300000 | 198058.6172 | 431475.4509 | Null | 1 | 0 |  | 20011206 | 800 | 1170 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | INTERNAL | GATHERING SYSTEM | BODY OF PIPE |  | STEEL |  | PIPELINE |  |  | 20 | 0.312 | API 5LX | 52000 | FLASH WELD |  | A O SMITH | 1959 | OTHER | TIDAL MARSH | JOE FREISBERG | 9185730810 | INTERNALLY | LOCALIZED PITTING |  |  |  | COATED | YES | 1959 |  |  | Null |  | Null |  | Null |  |  | Null |  |  |  | 0 | 0 | AERIAL PATROL NOTICED SHEEN IN MARSH. STATE AND FEDERAL AGENCIES WERE NOTIFIED. BOOMS WERE DEPLOYED TO ISOLATE AND CONTAIN PRODUCT. ALL RELEASED PRODUCT WAS RECOVERED. LINE THEN WAS BLOWN DOWN AND REPAIRED.
2021-02-26 10:36 | YES | YES | GT (Gas Transmission) | 20020105 | 2002-09-16 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | FARMINGTON |  | MI |  |  |  | 1412 | 2001-12-12 | 1 | NO |  |  |  | Null | NO | RUPTURE |  | 0 | 2 | 0 | 0 | 0 | Null | 0 | 0 | 588473 | 20011212 | 590 |  |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | PRTLK: TRANSMISSION SYSTEM; PRTFL: OTHER; PRTFO: STOPPLE; MLKD: OTHER; MLKDO: RUBBER; PRTSY: OTHER; PRTSO: SEALING ELEMENT; PRTYR: 2001; SMYS: 0; LOCLK: OTHER; LOCLO: OPEN EXCAVATION; PNAME: LARRY CROWDER; PHONE: 3135777024; PROT: Null; CPYR: 0; NOTIF: Null; MARK: Null; STAT: Null; CTEST: Null; TMPS: 0; LKPS: 0 | FAILURE OF SEALING ELEMENT OF STOPPLE.