2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190016 | 31668 | 2019-02-18 12:04 | ORIGINAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2019-01-20 20:00 | 2019 |  |  | 40.4288 | -96.2181 | 1235664 | 2019-01-20 23:17 |  | NATURAL GAS |  | 5316 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-01-20 23:03 | 2019-01-26 12:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-20 20:00 | 2019-01-20 20:03 | ONSHORE | NE | 68450 | TECUMSEH | JOHNSON | MILEPOST | 18.45 | AUBURN BRANCH LINE | NEB46001 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | YES |  |  |  |  | YES | UNCASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6.625 |  | 0.25 | 24000 | UNKNOWN | LONGITUDINAL ERW - LOW FREQUENCY |  | UNKNOWN | NONE | [28 empty] | 1932 | 1931 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 113 | 2 |  | CLASS 1 LOCATION | NO |  | 102 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 13000 | 13000 | 15000 | 15305.2248089568 | 20000 | 20406.9664119424 | 0 | 0 |  |  | 48000 | 29870.5283907221 | 48712.1912208992 | [8 empty] | 536 |  | 500 | 192.619(C) |  |  |  | PRESSURE EXCEEDED MAOP, BUT DID NOT EXCEED THE APPLICABLE ALLOWANCE IN 192.201 | NO |  |  |  |  | MANUAL | MANUAL | 50500 | NO |  |  |  | YES |  | YES | DRESSER COUPLINGS. | YES |  | YES |  |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER IDENTIFIED THE INCIDENT AND NOTIFIED THE CORRECT PERSONNEL TO RESPOND. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | YES | [14 empty] | YES | HIGH PHOSPHORUS WAS DETECTED IN THE METAL EXAMINATION. | [13 empty] | YES | THERE WAS NOT PHYSICAL DAMAGE TO THE PIPE THAT FAILED. INITIALLY, IT APPEARS TO BE STEEL CHEMISTRY. | [55 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | JOHN A GORMLEY | SR CORROSION SPECIALIST - PIPELINE SAFETY | john.gormley@nngco.com | 4023987494 |  |  |  |  | JOHN A GORMLEY | SR CORROSION SPECIALIST - PIPELINE SAFETY | 4023987494 | john.gormley@nngco.com | AT APPROXIMATELY, 20:00 ON 1/20/19 A RUPTURE OCCURRED ON THE AUBURN (NEB46001) BRANCH LINE. AT 20:48, THE RUPTURE AT MILEPOST 18.45 WAS REPORTED BY FIRST RESPONDERS TO THE OPERATIONS COMMUNICATION CENTER (OCC). THE RUPTURE IS LOCATED ON THE WEST SIDE OF 619TH AVENUE, NORTH OF HIGHWAY 41 IN SECTION 6, TOWNSHIP 5N, AND RANGE 11E IN JOHNSON COUNTY, NEBRASKA. AT THE INCIDENT LOCATION, INVESTIGATORS OBSERVED A HOLE 15 FEET IN LENGTH AND 10 FEET IN WIDTH EXPOSING THE PIPELINE RUPTURE AT A DEPTH 48" BELOW GRADE. A FAILURE MEASURING 113" IN LENGTH ALONG THE 5 O'CLOCK POSITION OF THE PIPELINE OCCURRED ON THE 6-INCH-DIAMETER SEGMENT OF PIPELINE WITH A WALL THICKNESS OF 0.250". THE PIPELINE IS VINTAGE 1932 DRESSER COUPLED PIPE WITH A SPECIFIED MINIMUM YIELD STRENGTH (SMYS) OF 24,000 PSI. THE PRESSURE AT THE POINT OF THE FAILURE WAS ESTIMATED 535 PSIG, PRODUCING A HOOP STRESS OF 29% SMYS. A DRESSER COUPLING WAS PRESENT, BUT REMAINED INTACT. NO EXTERNAL STRESSES WERE PRESENT THAT WOULD BE INDICATIVE OF THIRD PARTY DAMAGE. CALIPER MEASUREMENT OF THE PIPELINE WALL THICKNESS MEASURED CONSISTENTLY THROUGHOUT THE LENGTH OF THE FAILURE SO CORROSION IS NOT A FACTOR. THERE IS EVIDENCE OF A SEAM FOUND INTACT AT THE 10 O'CLOCK POSITION INDICATING THAT COMPOSITION OF CARBON, MAGNESIUM AND SULFUR ARE NOT EXCESSIVE AS CRACKING ALONG THE SEAM IS MORE COMMON WHEN COMPOSITION ISSUES EXIST. INITIAL INVESTIGATION REVEALED THAT A QUICK-CONNECT ON THE VALVE VRG CONTROLLER AT THE AUBURN TAKE-OFF SETTING SENSE LINE WAS LEAKING GAS. THIS SMALL LEAK CAUSED THE AUBURN TAKEOFF REGULATOR TO MALFUNCTION, RESULTING IN THE AUBURN BRANCH LINE REACHING A PRESSURE OF 535 PSIG PRIOR TO RUPTURE, WHEREAS THE TYPICAL OBSERVED LINE PRESSURE IS APPROXIMATELY 425 PSIG. LOCAL OPERATIONS EMPLOYEES WERE WORKING ON THE CONTROLLER WHEN THE RUPTURE OCCURRED ALLOWING A QUICK RESPONSE. THIS INCREASED PRESSURE IS CERTAINLY A CONTRIBUTING FACTOR TO THE PIPELINE FAILURE, BUT THE PIPELINE SHOULD NOT HAVE FAILED AT 525 PSIG, AS THIS IS LESS THAN THE MAOP PLUS ALLOWABLE BUILDUP. LABORATORY ANALYSIS OF THE PIPELINE WILL BE REQUIRED TO DETERMINE THE ROOT CAUSE OF THE PIPELINE FAILURE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190017 | 32014 | 2019-02-20 12:38 | SUPPLEMENTAL FINAL | 31604 | EQUITRANS MIDSTREAM CORPORATION | 2200 ENERGY DRIVE | CANONSBURG | PA | 15317 | 2019-01-29 11:30 | 2019 |  |  | 39.39 | -80.3545 | 1236276 | 2019-01-29 16:25 |  | NATURAL GAS |  | 17812 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-01-29 13:49 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-29 14:51 | 2019-01-29 13:49 | ONSHORE | WV | 26366 | LUMBERPORT | HARRISON | SURVEY STATION NO. | 460+77 | H312 | H312 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 108 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 12 |  | 0.312 | 52000 | API 5L PSL 2 | LONGITUDINAL ERW - HIGH FREQUENCY |  | MAVERICK TUBE CORPORATION | EPOXY | [9 empty] | PIPE GIRTH WELD | [18 empty] | 2015 | 2014 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 12 | 3.6 |  | CLASS 1 LOCATION | NO |  | 287 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 71248 | 71248 | 15000 | 15305.2248089568 | 140 | 142.848764883597 | 0 | 0 |  |  | 86388 | 80957.1101415326 | 86696.0735738404 | [8 empty] | 701 |  | 1200 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 12904 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  | YES | CONTROLLER WAS NOT NOTIFIED BY SCADA THAT AN INCIDENT WAS HAPPENING DUE TO ALERT/ALARM SETTINGS. FATIGUE DID NOT PLAY A PART IN THIS FAILURE. | YES | YES | [7 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [52 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | LANDSLIDE |  |  |  |  | NO | [306 empty] | JACOB LYONS | MANAGER PIPELINE COMPLIANCE | jlyons@equitransmidstream.com | 4125537870 |  |  |  |  | GREGG WEST | VP ENVIRONMENTAL SAFETY AND COMPLIANCE | 4123952971 | gwest@equitransmidstream.com | ON 1/29/19 A RUPTURE OCCURRED ON THE MAINLINE OF H312 PIPELINE. THE FAILURE WAS LOCATED AT A GIRTHWELD OF AN ELBOW AND MAINLINE PIPE. THE PIPE AND COATING INFORMATION IS IN PART C OF THIS REPORT. THE FITTING INFORMATION IS 12.75", 0.375 WT, Y52. THE COATING FOR THE WELD WAS DENSO 7200. THE ROOT CAUSE INVESTIGATION FOUND THAT A LANDSLIDE ABOUT 150 YARDS FROM THE RUPTURE MOVED THE PIPELINE FROM IT'S ORIGINAL LOCATION APPROXIMATELY 10 FEET AND PLACED STRESSED ON THE WELD AT THE ELBOW. THE WELD WAS SENT OUT FOR ANALYSIS. THE NDT READER SHEET SHOWS THE X-RAY FOR THE WELD PASSED. THE HYDROTEST PERFORMED DURING CONSTRUCTION WAS SUCCESSFUL. TIMELINE DATE: 1/29/2019 1:03 PM CYBERTEL (ANSWERING SERVICE FOR EMERGENCY NUMBER) CALLED OPERATION FIELD TECH ABOUT POTENTIAL LEAK 1:36 PM XTO CALLED INTO EQUITRANS GAS CONTROL ABOUT POTENTIAL LEAK ON H312 1:49 PM H312 PIPELINE ISOLATED 2:30 PM EQUITRANS MIDSTREAM COMPLIANCE DEPARTMENT NOTIFIED OF POTENTIAL LINE RUPTURE 2:51 PM EQUITRANS OPERATIONS FIELD PERSONNEL PERFORMED A VISUAL CONFIRMATION OF INCIDENT 4:25 PM NATIONAL RESPONSE CENTER NOTIFIED OF INCIDENT METALLURGICAL ANALYSIS SHOWED HIGH APPLIED AXIAL STRESS (LAND/SOIL MOVEMENT) ACTING ON A GIRTHWELD. THE GIRTHWELD SHOWED SOME PRE-EXISTING HYDROGEN ASSISTED COLD CRACKS OR HYDROGEN EMBRITTLEMENT, WHICH FORMED OVER TIME AS A RESULT OF HYDROGEN IN THE WELD OR A COMBINATION OF THESE TWO PROCESSES. WITH CONSULTATION, THESE CRACKS WERE STABLE UNDER HOOP STRESS BUT BECAME UNSTABLE WITH THE ADDED AXIAL STRESS. A LANDSLIDE WAS OBSERVED APPROXIMATELY 100 YARDS FROM THE FAILURE LOCATION PERPENDICULAR TO THE PIPE ON A SIDE HILL.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190018 | 31880 | 2019-02-20 15:50 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2019-01-21 02:43 | 2019 |  |  | 42.2069 | -83.9693 | 1235668 | 2019-01-21 04:30 |  | NATURAL GAS |  | 32564 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-01-21 04:31 | 2019-01-21 09:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-21 02:43 | 2019-01-21 02:43 | ONSHORE | MI | 48158 | MANCHESTER | WASHTENAW | MILEPOST | PLANT II | PLANT II | FREEDOM COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | CATALYTIC HEATER | 2016 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL | OTHER | [8 empty] | CATALYTIC HEATER FAILURE PREVENTED THE PILOT GAS REGULATOR FROM OPERATING RAPIDLY ENOUGH TO MAINTAIN PRESSURE FOR THE PILOT GAS SYSTEM. | CLASS 1 LOCATION | NO |  | 390 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 100623 | 100623 | 1405 | 1433.58939043896 | 1209 | 1233.60111960192 | 0 | 0 |  |  | 103237 | 105544.743893685 | 103290.190510041 | [8 empty] | 668 |  | 800 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | APPROPRIATE RESPONSE BY CONTROLLERS WAS PERFORMED | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | YES |  |  |  | YES |  |  |  |  | YES | [25 empty] | YES | CATALYTIC HEATER FAILURE | [161 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  |  |  |  | JASON PIONK | GAS COMPLIANCE LEAD | 989-791-5749 | jason.pionk@cmsenergy.com | ON JANUARY 21, 2019 AT APPROXIMATELY 02:43 HOURS, AN OPERATOR --ALREADY ONSITE RESPONDING TO A LOW PILOT PRESSURE ALARM AT CONSUMERS ENERGY'S FREEDOM COMPRESSOR STATION --OBSERVED GAS BLOWING AT OR NEAR THE PLANT II FIREGATE BLOW DOWN VALVES. DURING HIS INVESTIGATION THE OPERATOR DETERMINE THAT THREE (3) OF THE PLANT 2 FIREGATE BLOW DOWN VALVES WERE IN THE OPEN POSITION. THE OPERATOR WAS SUCCESSFUL AT CLOSING TWO OF THE THREE BLOW DOWN VALVES BUT UNABLE TO CLOSE THE THIRD VALVE (VALVE 614). THE OPERATOR PERFORMED A MANUAL EMERGENCY SHUT DOWN (ESD) OF PLANT 2 BY OPENING A PILOT GAS VENT VALVE TO STOP THE GAS FROM BLOWING. THE PLANT 2 ESD ISOLATION VALVE (VALVE 609) STUCK OPEN AND GAS CONTINUED TO ESCAPE. THE OPERATOR ATTEMPTED TO HAND PUMP VALVE 609 TO THE CLOSE POSITION WITH NO SUCCESS. THE OPERATOR WITH THE ASSISTANCE OF 2 STATION MECHANICS CLOSED VALVES 267 AND 268, WHICH ARE DOWNSTREAM OF VALVE 609. THIS OPERATION SUCCESSFULLY STOPPED THE GAS FROM BLOWING. AN INCIDENT INVESTIGATION IDENTIFIED A CATALYTIC HEATER FAILURE PREVENTED THE PILOT GAS REGULATOR FROM OPERATING RAPIDLY ENOUGH TO MAINTAIN PRESSURE FOR THE PILOT GAS SYSTEM CAUSING THE BLOW DOWN VALVES TO OPEN AND GAS TO BLOW. OPERATIONS PERSONNEL ARE EVALUATING ACTIONS TO IMPLEMENT THAT WILL MINIMIZE FUTURE OCCURRENCE.
2021-02-26 10:37 | YES | YES | GT (Gas Transmission) | 20190019 | 33216 | 2019-02-20 17:59 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2019-01-21 10:37 | 2019 |  |  | 39.7659 | -81.346 | 1235682 | 2019-01-21 11:59 |  | NATURAL GAS |  | 74768 | 22051 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 |  | YES |  | 2019-01-21 10:48 | 2019-04-02 09:00 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 4 | 2019-01-21 10:43 | 2019-01-21 11:10 | ONSHORE | OH | 43788 | SUMMERFIELD | NOBLE | MILEPOST | 678.8 | LINE 10 | ATHE-BERN | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 |  | 0.375 | 52000 | API-5L | DSAW |  | CLAYMONT STEEL | COAL TAR | [28 empty] | 1952 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 624 | 30 |  | CLASS 1 LOCATION | NO |  | 634 |  | YES | NO | NO |  | 4000000 | 4081393.28238848 | 66153 | 67499.1024524614 | 224304 | 224304 | 14000000 | 14284876.4883597 | 1500000 | 1530522.48089568 | 1500000 | 1530522.48089568 | OTHER RESTORATION AND SETTLEMENTS |  | 21290457 | 10099232.8720504 | 21719117.834992 | [8 empty] | 803 |  | 936 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 57300 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE DID NOT EXCEED MAOP PRIOR TO THE FAILURE, AND THUS CONTROLLER ERROR WAS NOT THE CAUSE OF THE FAILURE. WHEN THE PRESSURE LOSS WAS OBSERVED, THE CONTROLLER PROMPTLY NOTIFIED APPROPRIATE COMPANY PERSONNEL TO RESPOND TO THE FAILURE. | [12 empty] | YES | 11 | 0 | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [52 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | LANDSLIDE |  |  |  |  | NO | [306 empty] | MAYRA SALINAS |  | marya.salinas@enbridge.com | [5 empty] | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 7136275008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: 48 HR NRC REPORT 1235825 AT APPROXIMATELY 10:37 A.M. EST ON JANUARY 21, 2019, TETLP'S 30-INCH DIAMETER LINE 10 TRANSPORTING NATURAL GAS FROM BERNE COMPRESSOR STATION TO ATHENS COMPRESSOR STATION IN NOBLE COUNTY, OHIO FAILED AT MP 678.8, APPROXIMATELY 2.8 MILES SOUTH OF THE BERNE COMPRESSOR STATION. TETLP CONFIRMED THE RUPTURE AT 10:43 A.M. EST. THE FAILURE RESULTED IN AN EXPLOSION AND FIRE. THERE WERE TWO INJURIES AND NO FATALITIES. ONE INJURY REQUIRED INPATIENT HOSPITALIZATION. APPROXIMATELY 4 RESIDENTS WERE EVACUATED. THE ESD AT THE BERNE COMPRESSOR STATION WAS ACTIVATED AT 10:48 AM EST. THE MAINLINE VALVE AT M.P. 670.55 WAS CLOSED AT 11:00 AM EST AND THE BERNE COMPRESSOR STATION BY-PASS VALVE WAS CLOSED AT 11:14 AM EST, COMPLETING THE ISOLATION OF THE FAILURE SITE. TETLP PERSONNEL ARRIVED AT THE FAILURE SITE AT APPROXIMATELY 11:14 AM EST. A THIRD PARTY METALLURGICAL INVESTIGATION IS ONGOING. THE ROOT CAUSE IS PENDING. THE COST OF THE DAMAGE HAS NOT YET BEEN DETERMINED. THE PIPELINE REMAINS OUT OF SERVICE AT THIS TIME. SUPPLEMENTAL REPORT (10/04/2019) UPDATED PART D.7 TO INCLUDE COST OF DAMAGE SUPPLEMENTAL REPORT (10/24/2019) THE METALLURGICAL ROOT CAUSE OF THE INCIDENT WAS A RESULT OF DUCTILE OVERLOAD FROM A LONGITUDINAL TENSILE OR BENDING FORCE, LIKELY FROM LAND MOVEMENT THAT EXCEEDED THE LOAD CARRYING CAPACITY OF THE WELD. SUPPLEMENTAL REPORT (01/21/2020) THE METALLURGICAL ROOT CAUSE OF THE INCIDENT WAS A RESULT OF DUCTILE OVERLOAD FROM A LONGITUDINAL TENSILE OR BENDING FORCE FROM LAND MOVEMENT THAT EXCEEDED THE LOAD CARRYING CAPACITY OF THE WELD. - UPDATED RESTART TIME TO 04/02/2019 AT 9:00 AM CST - UPDATED NUMBER OF INJURIES FROM 1 TO 2 IN PART A AND UPDATED NARRATIVE TO REFLECT 1 INPATIENT HOSPITALIZATION - UPDATED APPARENT CAUSE IN PART G FROM LAND MOVEMENT TO LANDSLIDE
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190020 | 32068 | 2019-03-01 11:03 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-01-31 14:45 | 2019 |  |  | 30.5438 | -94.868 | 1236458 | 2019-01-31 15:40 |  | NATURAL GAS |  | 1269 | 4594 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-01-31 15:00 | 2019-02-11 13:23 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-31 13:52 | 2019-01-31 14:10 | ONSHORE | TX | 77371 | SHEPHERD | SAN JACINTO | SURVEY STATION NO. | 374 + 34.1 | TGP 100-1 | 100-1 25-1D TO 32-1S | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 40 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 24 |  | 0.25 | 50000 | API 5L | FLASH WELDED |  | AO SMITH | COAL TAR | [9 empty] | PIPE GIRTH WELD | [18 empty] | 1944 | 1944 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 454 |  | NO | NO | NO |  | 10000 | 10203.4832059712 | 12311 | 12561.5081748712 | 3400 | 3400 | 87867 | 89654.9458859072 | 2000 | 2040.69664119424 | 0 | 0 |  |  | 115578 | 56065.385600547 | 117860.633907944 | [8 empty] | 716 |  | 750 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 37065 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WAS NO INDICATION THAT ANY ACTIONS ON THE PART OF THE CONTROLLER CONTRIBUTED TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | YES | [7 empty] | YES | LACK OF FUSION DUE TO MISALIGNMENT | [12 empty] | YES | YES |  |  |  | YES | [58 empty] | YES | YES |  |  | YES |  |  |  | 2014 | [31 empty] | 2014 | [23 empty] | YES | 1984 | 1581 | NO | [13 empty] | NO | [63 empty] | SHELLEY DIETZ | PIPELINE ENGINEER | shelley_dietz@kindermorgan.com | 713-420-4417 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | AT 1:52PM ON JANUARY 31, 2019, A LOCAL PUMPER NOTIFIED TENNESSEE GAS PIPELINE (TGP) OPERATIONS ABOUT A POTENTIAL LEAK SOUTH OF THE TRINITY RIVER IN SAN JACINTO COUNTY, TEXAS. TGP DISPATCHED OPERATIONS TO THE SITE TO INVESTIGATE. THEY ARRIVED AT 2:10PM AND AT 2:45PM CONFIRMED THAT THE 100-1 LINE WAS LEAKING. THE LINE WAS ISOLATED BY CLOSING MAINLINE VALVES MLV 27-1A AND MLV 27-1 AT 3:00PM. THE LINE WAS THEN BLOWN DOWN TO 0PSIG BY 8:00PM ON JANUARY 31, 2019. DUE TO WET GROUND CONDITIONS AND LOGISTICS, EXCAVATION OF THE LINE BEGAN ON FEBRUARY 2, 2019. THE LEAK WAS DETERMINED TO BE COMING FROM A CRACK IN THE PIPE GIRTH WELD. TO REPAIR THE CRACKED SECTION, THE LINE WAS CUT OUT AND REPLACED. REPAIRS WERE COMPLETED AND THE LINE WAS RETURNED TO SERVICE ON 1:23PM ON FEBRUARY 11, 2019. METALLURGICAL ANALYSIS DETERMINED THAT THE CAUSE OF THE CRACK WAS LACK OF FUSION IN THE PIPE GIRTH WELD DUE TO PIPE MISALIGNMENT DURING WELDING. A 48-HOUR PHONE UPDATE WAS PROVIDED TO THE NRC. THE 48-HOUR NRC REPORT NUMBER IS 1236609.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190021 | 33564 | 2019-03-01 13:47 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2019-01-30 10:25 | 2019 | EASTERN | NO | 42.8095 | -82.8675 | 1236339 | 2019-01-30 11:29 | 1236476 | NATURAL GAS |  | 2766 | 508 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-01-30 10:28 | 2019-12-30 15:30 |  | YES | OPERATOR | 2019-01-30 10:29 | YES | 2019-01-30 10:26 | ALLOWED TO BURN OUT |  | 2212 | NO | [6 empty] | 0 | 2019-01-30 10:25 | 2019-01-30 10:25 | ONSHORE | MI | 48005 | ARMADA | MACOMB | NOT APPLICABLE |  | RAY COMPRESSOR STATION | PLANT 3 THROUGHPUT PIPING | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2012 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | PLANT 3 EMERGENCY SHUT DOWN (ESD) ACTIVATION RESULTING IN A RELEASE OF GAS THROUGH THE BLOW DOWN SILENCERS DUE TO WIND CONDITIONS AND LOCATION OF THE BLOW DOWN SILENCERS, A GAS PLUME MADE CONTACT WITH THE PLANT 2 THERMAL OXIDIZER EXHAUST CAUSING GAS TO IGNITE AND SUBSEQUENT FIRE. | CLASS 1 LOCATION | NO |  | 702 |  | NO | NO |  |  | 0 | 0 | 2261 | 2307.00755287009 | 12309 | 12309 | 17500000 | 17856095.6104496 | 2582 | 2634.53936378177 | 0 | 0 |  | 4.45 | 17517152 | 8211448.6506432 | 17873346.1573663 | 0 | 0 | 0 | 0 | NO |  |  |  | 1170 | 800 | 1800 | 192.619(A)(2) |  | 2011-06-10 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 500 | NO | YES |  |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM REPRESENTATIVE RESPONDED APPROPRIATELY | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  | YES | [6 empty] | YES | [24 empty] | YES | VOLTAGE SPIKE IN THE GROUNDING SYSTEM OF THE DET-TRONIC PANEL | [161 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON PIONK | GAS COMPLIANCE MANAGER | 989-791-5749 | jason.pionk@cmsenergy.com | ON JANUARY 30, 2019 AT APPROXIMATELY 10:23 A.M., CONSUMERS ENERGY'S (CE) RAY COMPRESSOR STATION PLANT 3 DETECTED AN ABNORMAL OPERATING CONDITION IN THE DET-TRONICS CONTROL SYSTEM. AS PART OF THE EMERGENCY SAFETY FIRE-GATE PROCESS, THE PLANT RELEASED NATURAL GAS INTO THE ATMOSPHERE THROUGH PLANT 3 BLOWDOWN SILENCERS. THE NATURAL GAS RELEASED FROM THE FIRE-GATE EVENT MIGRATED IN A NORTHEAST DIRECTION OVER THE PLANT 2 PROCESSING EQUIPMENT AS A RESULT OF THE WIND CONDITIONS OCCURRING AT THE TIME OF THE EVENT. AT APPROXIMATELY 10:25 A.M., A GAS PLUME IGNITED FROM THE PLANT 3 BLOWDOWN SILENCERS (SUCTION AND DISCHARGE). THE PLANT 2 THERMAL OXIDIZER'S 1506 DEGREES F EXHAUST STREAM AUTO-IGNITED THE PLANT 3 FIRE-GATE GAS PLUME. PERSONNEL AT THE RAY PLANT MANUALLY FIRE-GATED PLANT 1 AND PLANT 2, AS PART OF OUR STANDARD SAFETY PROTOCOLS, AT 10:27:58 A.M. AND 10:28:22 A.M., RESPECTIVELY. AT 10:28:48 A.M., THERE WAS A SECOND IGNITION AT THE PLANT 2 VENT STACK, WHICH IS LOCATED NEXT TO PLANT 3'S BLOWDOWN SILENCERS AND IS THE LOCATION WHERE THE NATURAL GAS IS RELEASED FOR PLANT 2. THE ARMANDA TOWNSHIP FIRE DEPARTMENT WAS NOTIFIED AT 10:29 A.M. AND ARRIVED ONSITE AT 10:38. THE EMERGENCY RESPONDERS REMAINED AT THE SITE UNTIL ALL THE NATURAL GAS WAS VENTED FROM THE PIPING TO ADDRESS REMAINING FIRE AND HOTSPOTS. A ROOT CAUSE ANALYSIS (RCA) TEAM WAS ASSEMBLED AND MET ON SITE FEBRUARY 2, 2019 TO IDENTIFY THE IGNITION SOURCE INITIATING THE FIRE AT THE RAY COMPRESSOR STATION PLANT 3 BLOW DOWN SILENCERS AND DEFINE HOW TO CONTROL AND PREVENT RE-OCCURRENCE. (REFER TO MPSC STAFF' INVESTIGATION REPORT APPENDIX A) FURTHER INVESTIGATION INTO THE DET-TRONICS FAILURE LEADING TO THE FIREGATE ACTIVATION REVEALED THAT A GROUNDING FAULT WAS THE UNDERLYING CAUSE OF THE INITIAL FIREGATE EVENT. WHEN THE STATION'S [DOMESTIC WATER] WELL PUMP STARTED UP, ITS VARIABLE FREQUENCY DRIVE CAUSED A VOLTAGE SPIKE IN THE GROUNDING SYSTEM OF THE DET-TRONICS PANEL LOCATED IN THE HEADQUARTERS BUILDING. THESE HIGH VOLTAGES CAUSED ENHANCED DISCRETE INPUT/OUTPUT (EDIO) AND ANALOG INPUT MODULE (AIM) TO LOSE COMMUNICATION WITH THE DET-TRONICS PILOT AIR SYSTEM, A FAULT WHICH TRIGGERED THE INITIAL FIREGATE. TO ELIMINATE THE GROUNDING VOLTAGE INTO THE DET-TRONICS SYSTEM, THE WELL PUMP PRESSURE SWITCH AND PRESSURE TRANSMITTER WERE RELOCATED TO THE EAST SIDE OF THE PLANT 3 AUXILIARY BUILDING. THE RISK OF A COMMUNICATIONS BREAK-DOWN BETWEEN THE PILOT AIR SYSTEM AND ITS MODULES HAS BEEN MITIGATED BY RELOCATING THE MODULES FROM THE HEADQUARTERS BUILDING TO THE PLANT 3 AUXILIARY BUILDING. RESTORATION AND RECOVERY ACTIVITIES HAVE BEEN OUTLINED THE CONSUMERS ENERGY COMPANY'S RAY NATURAL GAS COMPRESSOR STATION STORAGE FIELD INJECTION TIMELINE AND FACILITY REPAIR UPDATE TIMELINE & FACILITY REPAIR UPDATE (REFER TO MPSC STAFF INVESTIGATION REPORT APPENDIX M) FOLLOWING RESTORATION ACTIONS, NORMAL OPERATIONS TO THE CONSUMERS ENERGY RAY COMPRESSOR STATION WAS RESUMED ON DECEMBER 30, 2019.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190022 | 31750 | 2019-03-01 15:32 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-01-31 02:08 | 2019 |  |  | 39.9386 | -81.6847 | 1236402 | 2019-01-31 03:01 |  | NATURAL GAS |  | 55924 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-01-31 02:45 | 2019-01-31 10:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-31 02:08 | 2019-01-31 02:08 | ONSHORE | OH | 43732 | CUMBERLAND | GUERNSEY | MILEPOST | 12 | COMPRESSOR STATION 209 | 200 SYSTEM | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1950 |  | CARBON STEEL |  | LEAK |  |  | OTHER | RELEASE THROUGH OPEN VALVE | [5 empty] | CLASS 1 LOCATION | NO |  | 698 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 150000 | 150000 | 300 | 306.104496179136 | 500 | 510.17416029856 | 0 | 0 |  |  | 150800 | 155886.504465954 | 150816.278656478 | [8 empty] | 669 |  | 790 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WAS NO INDICATION THAT ANY ACTIONS ON THE PART OF THE CONTROLLER CONTRIBUTED TO THE INCIDENT. | [12 empty] | YES | 1 | 0 | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | NO | [306 empty] | SHELLEY BROMAN | PIPELINE ENGINEER CODES AND STANDARDS | shelley_broman@kindermorgan.com | 7134204417 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | ON JANUARY 31, 2019 AT 2:08AM, TENNESSEE GAS PIPELINE COMPRESSOR STATION 209 IN CUMBERLAND, OHIO EXPERIENCED AN EMERGENCY SHUTDOWN (ESD). THE ON DUTY OPERATOR NOTICED THAT THE STATION CONTINUED TO BLOW DOWN BEYOND DURATION OF A NORMAL SHUTDOWN AND CALLED THE OPERATIONS SUPERVISOR AND STATION PERSONNEL FOR ASSISTANCE IN LOCATING THE SOURCE OF THE CONTINUAL GAS RELEASE. THE OPERATIONS SUPERVISOR ARRIVED ON SITE AND TOGETHER WITH THE OPERATOR AND STATION PERSONNEL IDENTIFIED THAT THE STATION HEADER SUCTION VALVE, AS-1, AND DISCHARGE VALVE, AD-3, HAD NOT CLOSED AS DESIGNED. THE OPERATOR AND THE OPERATIONS PERSONNEL (OPERATIONS SPECIALIST) MANUALLY CLOSED THE SUCTION AND DISCHARGE VALVES AND STOPPED THE GAS RELEASE AT 2:45AM ON JANUARY 31, 2019. THE STATION VENTED FOR A TOTAL OF 37 MINUTES AND THE TOTAL GAS RELEASE WAS 55,924 MCF. THE INVESTIGATION REVEALED THAT ESD PUSH BUTTON 5 HAD HAD MOISTURE ENTER THE CASING AND CAUSED CORROSION ON THE BUTTON. ON THE DAY OF THIS EVENT, THE EXTREMELY COLD TEMPERATURES (-4 DEGREES FAHRENHEIT) CAUSED THE MOISTURE IN THE CASING TO FREEZE THEREFORE OPENING THE CIRCUIT ON THE BUTTON AND INITIATING THE ESD. IN ADDITION, MOISTURE HAD GOTTEN IN TO THE AS-1 SUCTION VALVE ACTUATOR AND AD-3 DISCHARGE VALVE ACTUATOR AND THE EXTREMELY COLD WEATHER CAUSED THE VALVE O-RINGS TO FREEZE, PREVENTING THEM FROM CLOSING. IN ORDER TO PREVENT A REOCCURRENCE OF THESE EVENTS THE PUSH BUTTON WAS REPLACED AND FRYQUEL 300 WAS ADDED TO THE VALVE ACTUATORS ON AS-1 AND AD-3 TO ENSURE THEY ARE SEALING TIGHTLY AND WATERTIGHT. A 48-HOUR PHONE CALL UPDATE WAS MADE TO THE NRC. THE 48-HOUR REPORT NUMBER IS 1236569. THE "ORIGINAL" REPORT WAS INTENDED TO BE MARKED AS "ORIGINAL/FINAL" BUT THE "FINAL" DESIGNATION WAS INADVERTENTLY NOT MARKED. NO NEW INFORMATION HAS BEEN ADDED TO THIS "SUPPLEMENTAL/FINAL" REPORT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190023 | 31812 | 2019-03-04 11:03 | SUPPLEMENTAL FINAL | 12498 | MIDWESTERN GAS TRANSMISSION CO | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2019-02-08 23:05 | 2019 |  |  | 36.6199 | -86.5633 | 1237270 | 2019-02-09 11:00 |  | NATURAL GAS |  | 4650 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE COMPRESSOR VENT PERFORMED AS DESIGNED. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-02-09 09:00 | 2019-02-09 09:00 | ONSHORE | TN | 37148-9737 | Not Within a Municipality | SUMNER | MILEPOST | 2101 | PORTLAND | COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | VALVE ACTUATOR | 2018 |  | CARBON STEEL |  | OTHER | [8 empty] | GAS RELIEVED THROUGH A VENT VALVE AS DESIGNED UPON SHUTDOWN OF THE COMPRESSOR STATION. | CLASS 1 LOCATION | NO |  | 633 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 12431 | 12431 | 200 | 204.069664119424 | 0 | 0 | 0 | 0 |  |  | 12631 | 12981.4555128139 | 12635.0696641194 | [8 empty] | 590 |  | 936 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A FAILURE OF A VALVE ACTUATOR. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | [204 empty] | EQUIPMENT NOT INSTALLED PROPERLY | [5 empty] | YES |  |  | OTHER MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | TERI ANDERSON | MANAGER REGULATORY COMPLIANCE | teri.anderson@oneok.com | 918-382-2073 |  |  |  |  | WESLEY DUNBAR | VP NATURAL GAS PIPELINE OPERATIONS | 918-588-7424 | wesley.dunbar@oneok.com | ON 02/08/2019 AT 23:05 HOURS, THE MGT-PORTLAND COMPRESSOR STATION EXPERIENCED A SHUTDOWN ON THE #1 COMPRESSOR. THE FIELD MECHANIC RESPONDED TO A CALLOUT AND STARTED THE #5 COMPRESSOR TO CONTINUE WITH THE GAS PROCESSING. UPON MAKING REPAIRS TO THE #1 COMPRESSOR AND STARTING THE UNIT BACK UP, THE FIELD MECHANIC ISSUED A SHUTDOWN COMMAND TO THE #5 COMPRESSOR. AS PER NORMAL OPERATIONS, WHEN A COMPRESSOR SHUTS DOWN, TELEMETRY CLOSES THE SUCTION VALVE AND BLOWS DOWN THE COMPRESSOR. UNKNOWN TO THE FIELD MECHANIC, THE VALVE ACTUATOR WHICH CLOSES THE #5 COMPRESSOR SUCTION VALVE WAS UNABLE TO PERFORM THE CLOSE FUNCTION. THE #5 COMPRESSOR SUCTION VALVE REMAINED OPEN. THE COMPRESSOR BEGAN TO BLOW DOWN AS PROGRAMMED, BUT WITH THE SUCTION VALVE REMAINING OPEN, NATURAL GAS CONTINUED TO RELIEVE OUT THE BLOW DOWN VENT. THE FIELD MECHANIC DID NOT SEE THE SUCTION VALVE HAD REMAINED OPEN AND THE CONTROLLER HAD A CLOSED VALVE INDICATOR ON HIS SCADA DISPLAY AS THE DISCONNECTED ACTUATOR HAD ACTIVATED THE LIMIT SWITCH DISPLAYING THE VALVE AS CLOSED IN SCADA. THE FIELD MECHANIC DID NOT HEAR THE GAS RELIEVING THROUGH THE VENT LINE AS THE BLOW DOWN HAS A SILENCER INSTALLED. DURING STATION ROUNDS ON 02/09/2019 AT 09:00, THE FIELD OPERATOR FOUND THE GAS RELIEVING THROUGH THE COMPRESSOR VENT LINE. THE GAS LOSS WAS CALCULATED AT 4.65 MMCF AND WAS REPORTED TO THE NRC ON 02/09/2019 AT 1100 HRS. THE ORIGINAL NRC REPORT NUMBER IS 1237270. THE 48 HOUR NRC REPORT NUMBER IS 1237760. ACTION TAKEN: AN LEL TRANSMITTER TO ALERT THE CONTROL CENTER OF VENTING GAS FROM THE BLOW DOWN HAS BEEN INSTALLED TO ASSIST THEM IN DETERMINING IF GAS IS VENTING TO ATMOSPHERE. THE SUCTION VALVE ACTUATOR WAS REPAIRED AND THE REMAINING STATION ACTUATORS WERE INSPECTED WITH NO ISSUES FOUND. SUPPLEMENTAL REPORT WAS CREATED DUE TO THE NRC REPORTING DATE IN PART A WAS INCORRECT IN THE FIRST REPORT. 3/18/2019 - SUPPLEMENTAL CREATED TO CORRECT NRC ORIGINAL REPORT NUMBER AND DESCRIPTION OF CONTROL VALVE BECOMING DISENGAGED FROM VALVE. THE MOUNTING NUTS HAD VIBRATED LOOSE ON THE MOUNTING STUDS OF THE VALVE ACTUATOR. WHEN THE NUTS VIBRATED LOOSE, THE ACTUATOR SLID OFF OF THE SHAFT WHICH DISENGAGED THE KEY ON THE SHAFT. WHEN A CLOSED COMMAND WAS SENT TO THE VALVE, THE ELECTRIC OPERATOR CLOSED AS IT SHOULD, BUT DID NOT MOVE THE VALVE. IT MADE THE CLOSED LIMIT SWITCH ON THE ELECTRIC OPERATOR, BUT BECAUSE IT WAS DISENGAGED FROM THE GEAR BOX SHAFT IT DID NOT OPERATE THE SUCTION VALVE. THE CONTROLS SAW THE CLOSED LIMIT ON THE SUCTION VALVE AND ALSO ON THE DISCHARGE VALVE AND IT THEN OPERATED AS IT SHOULD ALLOWING THE VENT VALVE TO OPEN TO BLOW DOWN THE COMPRESSORS. THE REPAIR WAS MADE BY INSTALLING THE ELECTRIC OPERATOR BACK ON THE SHAFT AND REPLACING THE NUTS. THE OPEN AND CLOSED LIMITS WERE THEN RESET AND TESTED AS PER PROCEDURE. INSTALLATION OF THE ACTUATOR WAS CONDUCTED BY A CONTRACTOR AND THE ACTUATOR HAD PERFORMED CORRECTLY POST INSTALLATION. MAINTENANCE HAD BEEN PERFORMED ON THE VALVE AND THERE WERE NO ISSUES FOUND DURING THE MAINTENANCE ACTIVITY. ALL ACTUATORS HAVE BEEN INSPECTED AT THE COMPRESSOR STATION TO VERIFY NUTS WERE TIGHT. 3/19/2019 SUPPLEMENTAL: UPDATED ROOT CAUSE TO INCORRECT OPERATION DURING INSTALLATION. THE BOLTS, IF TORQUED, SHOULD NOT HAVE VIBRATED LOOSE. THERE WAS NOT A FAILURE OF THE ACTUATOR, AS IT PERFORMED AS DESIGNED. THERE WERE NO BROKEN PARTS TO THE ACTUATOR.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190024 | 31734 | 2019-03-04 17:01 | ORIGINAL FINAL | 26330 | ENABLE OKLAHOMA INTRASTATE TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2019-02-07 05:00 | 2019 |  |  | 35.2978 | -98.8337 | 1237058 | 2019-02-07 10:29 |  | NATURAL GAS |  | 8884 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE FACILITY WAS ALREADY SHUT DOWN. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-02-07 08:30 | 2019-02-07 08:30 | ONSHORE | OK | 73632 | CORDELL | WASHITA | MILEPOST | CORDELL | CORDELL COMPRESSOR STATION | CORDELL COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ABOVEGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | FAILURE DUE TO ICING. | CLASS 1 LOCATION | NO |  | 50 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 28182 | 28182 | 500 | 510.17416029856 | 500 | 510.17416029856 | 0 | 0 |  |  | 29182 | 29685.9258580326 | 29202.3483205971 | [8 empty] | 0 |  | 1200 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | VALVE WAS ICED OVER AND DID NOT CLOSE PROPERLY WHEN THE STATION WAS SHUT DOWN AT 01:00. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | SURGE VALVE | [22 empty] | YES | ICING | [161 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | AT 2/7/19 AT 01:00 THE CORDELL COMPRESSOR STATION WAS SHUT DOWN BY SYSTEM CONTROL. WHEN THE STATION SHUT DOWN, A SURGE VALVE FOR THE FUEL GAS LINE HUNG OPEN DUE TO SEVERE ICING. DUE TO THE VALVE NOT CLOSING, NATURAL GAS WAS ALLOWED TO FLOW BY AND SINCE THE STATION WAS SHUT DOWN THIS GAS ESCAPED THROUGH A 2" VENT FOR 7.5 HOURS UNTIL IT WAS DISCOVERED BY AN OPERATOR EMPLOYEE AT 08:30 THE SAME DAY. THE VALVE WAS ISOLATED, DE-ICED, AND PUT BACK INTO SERVICE IMMEDIATELY. GAS LOSS FOR THE EVENT WAS CONFIRMED AT 09:30 AND A CALL WAS PLACED WITH THE NRC AT 10:28 (#1237058). A 48 HOUR FOLLOW UP CALL WAS PROVIDED ON 2/8/19 AT 07:34 (#1237159).
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190025 | 31736 | 2019-03-04 21:22 | ORIGINAL FINAL | 14210 | OKLAHOMA NATURAL GAS COMPANY, A DIVISION OF ONE GAS, INC. | 401 N. HARVEY AVE | OKLAHOMA CITY | OK | 73102 | 2019-01-31 15:02 | 2019 |  |  | 36.1335 | -95.8868 | 1236467 | 2019-01-31 17:27 |  | NATURAL GAS |  | 16800 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-01-31 17:50 | 2019-02-03 11:28 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-31 15:05 | 2019-01-31 15:20 | ONSHORE | OK | 74129 | TULSA | TULSA | SURVEY STATION NO. | N/A | LINE C NORTH | LINE C NORTH | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | BOLT-TYPE MECHANICAL COUPLING | 1959 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | BOLT-TYPE MECHANICAL COUPLING | OTHER | [8 empty] | MECHANICAL COUPLING SEPARATION | CLASS 3 LOCATION | YES | METHOD2 | 200 |  | NO | NO | NO |  | 25000 | 25508.708014928 | 0 | 0 | 53978 | 53978 | 265000 | 270392.304958237 | 25000 | 25508.708014928 | 0 | 0 |  |  | 368978 | 203496.986487627 | 375387.720988093 | [8 empty] | 230 |  | 300 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 26400 | NO | YES | YES |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) | [5 empty] | YES | [7 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | PROJECT ENGINEERING DID NOT REFER TO THE CORRECT WORK ORDER OR MAP IN DESIGNING THE PROJECT AND FAILED TO IDENTIFY THE NEARBY COUPLING. |  |  |  | YES | PROJECT ENGINEERING DID NOT REFER TO THE CORRECT WORK ORDER OR MAP IN DESIGNING THE PROJECT AND FAILED TO IDENTIFY THE NEARBY COUPLING. | NORMAL OPERATING CONDITIONS | NO | [150 empty] | SETH SLIFER | SR. COMPLIANCE SPECIALIST | seth.slifer@onegas.com | 405-248-7018 |  |  |  |  | MEGHAN BOOKER | DIRECTOR OF ENGINEERING | 405-2390573 | meghan.booker@onegas.com | A RECENT PIPELINE CONSTRUCTION PROJECT REPLACED PART OF AN ORIGINALLY ALL-WELDED 16-INCH PIPELINE INSTALLED IN 1955. ALTHOUGH OPERATOR RECORDS EXISTED, THE PROJECT DESIGNERS AND REVIEWERS FAILED TO IDENTIFY THAT TWO COUPLINGS HAD LATER BEEN INSTALLED IN 1959. THE CURRENT REPLACEMENT PROJECT CREATED A 90-DEGREE OFFSET IN THE ORIGINAL PIPELINE ROUTE NEAR THE MOST PROXIMATE BURIED COUPLING, AND THE NEW PIPE CONFIGURATION INCREASED THE COUPLING'S AXIAL STRESS. BECAUSE THE EXISTENCE OF THE COUPLINGS WAS NOT NOTED, THE OPERATOR'S PRACTICE TO IMPROVE THE COUPLING'S RESTRAINT SYSTEM, NEAR THE NEWLY INSTALLED 90-DEGREE ELBOW, WERE NOT FOLLOWED AND THE BURIED COUPLING SEPARATED AT NORMAL OPERATING PRESSURE INTO THE PROXIMATE CONSTRUCTION TIE-IN POINT EXCAVATION WHICH WAS STILL OPEN. CORRECTIVE ACTIONS INCLUDE COMPLETING ADDITIONAL ENGINEERING REVIEW OF ACTIVE PROJECTS AND ADDITIONAL TRAINING.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190026 | 31772 | 2019-03-04 22:34 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2019-01-31 11:00 | 2019 |  |  | 40.0639 | -76.5762 | 1236976 | 2019-02-06 14:04 |  | NATURAL GAS |  | 1782 | 2417.6 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-01-31 11:00 | 2019-01-31 21:12 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-31 11:00 | 2019-01-31 11:00 | ONSHORE | PA | 17547 | MARIETTA | LANCASTER | MILEPOST | 169.92 | MARIETTA | HEID-MARI | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | TUBING FITTING | UNKNOWN |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STELL | LEAK |  |  | OTHER | TUBING FITTING | [5 empty] | CLASS 3 LOCATION | YES | METHOD2 | 829 |  | NO | NO | NO |  | 0 | 0 | 6914 | 7054.6882886085 | 5096 | 5096 | 200 | 204.069664119424 | 0 | 0 | 0 | 0 |  |  | 12210 | 8615.21602910974 | 12354.7579527279 | [8 empty] | 709 |  | 1000 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | MARIETTA COMPRESSOR STATION IS LOCALLY MANNED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | DEFECTIVE OR LOOSE TUBING OR FITTING | MATERIAL/WELD/EQUIP FAILURE | DEFECTIVE OR LOOSE TUBING/FITTING | [166 empty] | DEFECTIVE OR LOOSE TUBING OR FITTING | [20 empty] | YES | [177 empty] | MAYRA SALINAS | ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: 48 HR NRC 1237186 AT APPROXIMATELY 11:00 AM EST ON JANUARY 31, 2019, A NATURAL GAS RELEASE WAS DISCOVERED FROM A RELIEF VALVE AT MARIETTA COMPRESSOR STATION ON THE TEXAS EASTERN TRANSMISSION (TETLP) SYSTEM IN LANCASTER COUNTY, PA. THE INITIAL GAS LOSS WAS DETERMINED TO BE LESS THAN THE REPORTING THRESHOLD. THE APPARENT CAUSE WAS A TUBING FITTING UNDER A RELIEF VALVE SNAPPING OFF DUE TO VIBRATION, WHICH CAUSED THE RELIEF VALVE 305-10 TO ACTIVATE AND VENT GAS TO ATMOSPHERE. THE GAS LOSS WAS LATER REVISED ON FEBRUARY 6, 2019 AFTER IT WAS DETERMINED THAT DURING STATION ESD, THE MARIETTA STATION 36"X30" SUCTION VALVE #2-6290 DID NOT CLOSE AS INTENDED DUE TO FREEZING IN THE VALVE CONTROLS. THE REVISED GAS LOSS EXCEEDED THE REPORTING THRESHOLD. AFTER CONSULTATION WITH PHMSA ON FEBRUARY 6, 2019, PHMSA RECOMMENDED THAT ENBRIDGE MAKE THE NRC NOTIFICATION. THE AFFECTED PART OF MARIETTA STATION WAS RETURNED TO SERVICE BY 9:12 PM EST ON JANUARY 31, 2019. SUPPLEMENTAL REPORT: AT APPROXIMATELY 11:00 AM EST ON JANUARY 31, 2019, A NATURAL GAS RELEASE WAS DISCOVERED FROM A RELIEF VALVE AT MARIETTA COMPRESSOR STATION ON THE TEXAS EASTERN TRANSMISSION (TETLP) SYSTEM IN LANCASTER COUNTY, PA. THE ESD SYSTEM WAS ACTIVATED TO ISOLATE THE LEAK IMMEDIATELY AFTER THE LEAK WAS IDENTIFIED. THE INITIAL GAS LOSS WAS DETERMINED TO BE APPROXIMATELY 1,782 MCF, LESS THAN THE REPORTING THRESHOLD. THE APPARENT CAUSE WAS THE FAILURE OF A TUBING FITTING UNDER A RELIEF VALVE DUE TO VIBRATION, WHICH CAUSED THE RELIEF VALVE 305-10 TO ACTIVATE AND VENT GAS TO ATMOSPHERE. ON FEBRUARY 5, DURING THE INVESTIGATION OF THIS EVENT, IT WAS DETERMINED THE MARIETTA STATION 36"X30" SUCTION VALVE #2-6290 DID NOT CLOSE AS INTENDED DUE TO FREEZING IN THE VALVE CONTROLS, RESULTING IN A GAS LOSS VOLUME GREATER THAN ORIGINALLY ESTIMATED. THE GAS LOSS WAS REVISED TO APPROXIMATELY 4,200 MCF ON FEBRUARY 5, 2019. THE REVISED GAS LOSS EXCEEDED THE REPORTING THRESHOLD. AFTER CONSULTATION WITH PHMSA ON FEBRUARY 6, 2019, PHMSA RECOMMENDED THAT ENBRIDGE MAKE THE NRC NOTIFICATION. THE NRC NOTIFICATION WAS MADE ON FEB. 6, AS RECOMMENDED BY PHMSA. THE AFFECTED PART OF MARIETTA STATION WAS RETURNED TO SERVICE BY 9:12 PM EST ON JANUARY 31, 2019.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190027 | 31777 | 2019-03-12 14:54 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2019-02-14 15:26 | 2019 |  |  | 38.2286 | -122.5949 | 1237755 | 2019-02-15 08:12 |  | NATURAL GAS |  | 0.24 | 0.003 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-02-16 03:50 | 2019-02-16 03:50 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-02-14 15:26 | 2019-02-14 15:26 | ONSHORE | CA | 94954 | PETALUMA | SONOMA | MILEPOST | MP 1.9 | L21G | 34717 (ROUTE ID) | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | WETLAND | 18 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | THREADED PLUG- LEAK FROM THREADS | 1961 |  | CARBON STEEL |  | LEAK |  |  | OTHER | THREADED PLUG- LEAK FROM THREA | [5 empty] | CLASS 3 LOCATION | NO |  | 116 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 1 | 1 | 132987 | 135693.062111249 | 0 | 0 | 0 | 0 |  |  | 132988 | 62287.7327646 | 135694.062111249 | [8 empty] | 308 |  | 450 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 4 | NO | [5 empty] | YES | SMALL DIAMETER- 3/4" | YES |  |  |  |  | YES | SMALL DIAMETER- 3/4" | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THESE LEAKS ARE UNIDENTIFIABLE ON SCADA. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | THREADED FITTING | [19 empty] | YES | LEAK FROM THREADED PLUG | [161 empty] | ENZA BARBATO | REGULATORY COMPLIANCE | e1bo@pge.com | [5 empty] | SUSIE RICHMOND | MANAGER REGULATORY COMPLIANCE | 925-328-5776 | gsr8@pge.com | ON THURSDAY, FEBRUARY 14, 2019 AT 1526 HOURS, PG&E WAS NOTIFIED OF A GRADE 1 LEAK AT 2100 S. MCDOWELL BLVD AT THE LOCATION WHERE THE PIPELINE ENTERS SHOLLENBERGER PARK (WETLAND) (L21G MP 1.9). PG&E LEAK SURVEYOR WAS ON SITE APPROXIMATELY AT 1526 HOURS. THE AREA WAS MADE SAFE AND A LEAK SURVEY STAYED ONSITE THROUGHOUT THE NIGHT TO MONITOR AND ENSURE SITE SAFETY. ON 2/15 PG&E CREWS ARRIVED ON-SITE AT APPROXIMATELY 800 HOURS. THE LEAK WAS REPAIRED BY 3:50 HOURS ON 2/16/19. THE GRADE 1 LEAK WAS IDENTIFIED ON A THREADED PLUG DOWNSTREAM OF A 3/4" VALVE. A VISUAL SOAP TEST CONFIRMED THAT THE LEAK WAS CAUSED BY IMPROPER SEALING OF THE THREADS. TOTAL GAS LOSS ESTIMATED AT 0.24 MCF. THERE WAS NO CUSTOMER IMPACT. THERE WERE NO INJURIES OR FATALITIES. THERE WAS NO MEDIA, POLICE, FIRE DEPARTMENT REPORTED . THERE WERE NO INJURIES OR FATALITIES. THERE WAS NO MEDIA, POLICE, FIRE DEPARTMENT REPORTED. THIS INCIDENT WAS REPORTED TO THE DOT (1237755) AND CPUC (190215-9105) DUE TO THE EXPECTED REPAIR COSTS BEING ESTIMATED AT OVER $50K ON 2/15/19 AT 0800 HOURS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190028 | 32542 | 2019-03-15 16:21 | SUPPLEMENTAL FINAL | 8070 | INDIANA GAS CO INC | 211 NW RIVERSIDE DRIVE | EVANSVILLE | IN | 47708 | 2019-01-20 00:01 | 2019 |  |  | 39.8898 | -86.3837 | 1235638 | 2019-01-20 13:43 |  | NATURAL GAS |  | 15900 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | BLOCKING VALVES AHEAD OF RELIEF VALVES WERE CLOSED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-20 00:01 | 2019-01-20 00:55 | ONSHORE | IN | 46112 | BROWNSBURG | HENDRICKS | MILEPOST | HCJ STATION | HENDRICKS COUNTY JUNCTION | RELIEF VALVES ON SOUTH AND EAST LINES | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2014 |  | CARBON STEEL |  | OTHER | [8 empty] | NATURAL GAS RELEASED TO THE ATMOSPHERE AS A RESULT OF EQUIPMENT FAILURE | CLASS 1 LOCATION | NO |  | 541 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 51474 | 51474 | 100 | 102.034832059712 | 500 | 510.17416029856 | 0 | 0 |  |  | 52074 | 53646.4531526149 | 52086.2089923583 | [8 empty] | 518 |  | 600 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ON SITE INVESTIGATION CONFIRMED CONTROLLERS ACTIONS | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | CONTROL LINE TO PILOT REGULATORS FOR RELIEF VALVES OBSTRUCTED WITH ICE | [161 empty] | JERRY KNECHT | GAS COMPLIANCE SPECIALIST | jerry.knecht@centerpointenergy.com | 7653669496 |  |  |  |  | ADAM GILLES | REGIONAL OPERATIONS DIRECTOR | 8125688554 | adam.gilles@centerpointenergy.com | VECTREN'S HENDRICKS COUNTY JUNCTION (HCJ) IS A NATURAL GAS TRANSMISSION PIPELINE WITH A COMPRESSOR STATION. HCJ IS A CENTRAL STATION THAT DIRECTS THE FLOW OF GAS INTO VECTREN'S NORTH, SOUTH & EAST SYSTEMS. DURING THIS GAS RELEASE INCIDENT, VECTREN'S SCADA DATA SHOWS THAT NONE OF THE PIPELINES WERE OVER-PRESSURIZED. THE PRESSURES AT THE TIME OF THE INCIDENT WERE WELL WITHIN NORMAL OPERATING PRESSURE RANGES. THIS GAS RELEASE INCIDENT WAS CAUSED BY MOISTURE FREEZING IN THE CONTROL LINE TO THE RELIEF VALVES CAUSING THEM TO OPEN AND VENT NATURAL GAS TO ATMOSPHERE. LOW PRESSURE LIMITS ON SCADA SYSTEM ALERTED GAS CONTROLLERS TO POTENTIAL ISSUE, WHO IN TURN NOTIFIED SUPERVISION, WHICH DISPATCHED 1ST RESPONDER PERSONNEL, WHO ARRIVED AND INVESTIGATED AND RECTIFIED THE SITUATION. TEMPORARY HEAT TAPE, INSULATION AND COVERING OVER THE SECTIONS OF THE CONTROL LINES AND SYSTEM COMPONENTS THAT WERE INVOLVED IN THE FREEZE-OFF WERE PERFORMED THAT WEEK. VECTREN WILL BE MAKING THESE MORE PERMANENT SOLUTIONS LATER THIS SPRING/SUMMER. NOTE: THIS IS INTENDED TO REPLACE REPORT NUMBER 20190015 - 31671 WHICH WAS MISTAKENLY SUBMITTED VIA THE FORM PHMSA F 7100.1.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190029 | 31804 | 2019-03-18 13:56 | ORIGINAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2019-02-18 18:09 | 2019 |  |  | 38.9563 | -77.3397 | 1238646 | 2019-02-26 10:26 |  | NATURAL GAS |  | 7.235 | 36591 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-02-18 18:42 | 2019-02-23 18:49 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-02-18 18:09 | 2019-02-18 18:09 | ONSHORE | VA | 20190 | RESTON | FAIRFAX | MILEPOST | 1597.19 | MAINLINE D / MLV 185D14 | MLV 185D0 (STATION 185) TO MLV R9 (POTOMAC RIVER) | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 57 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | MAINLINE | BALL |  | TIV |  |  |  | 2019 | 2016 | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | CARBON STEEL WITH ASTM A182 F316 | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | YES | METHOD2 | 809 |  | NO | NO | NO |  | 0 | 0 | 104559 | 106686.600053314 | 21 | 21 | 100041 | 102076.666340857 | 13335 | 13606.3448551626 | 70337 | 71768.2398258397 | NDT, INSPECTION, AND DOWN TIME COSTS |  | 288293 | 135038.806663318 | 294158.851075173 | [8 empty] | 485 |  | 780 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | AUTOMATIC | 107765 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS A MATERIAL DEFECT, NOT ASSOCIATED WITH A CONTROLLER PERFORMANCE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | OTHER | WELD CONNECTION BETWEEN THE GREASE FITTING EXTENSION AND THE MAIN VALVE BODY. CRACKED WELD. |  |  |  |  | YES | [174 empty] | TIMOTHY HUGGINS | PRINCIPAL ENGINEER | timothy.n.huggins@williams.com | 7132152889 |  |  |  |  | CLINT RATKE | MANAGER PIPELINE SAFETY | 9185736724 | clint.ratke@williams.com | ON 2/18/2019, DURING PURGE AND PACK OPERATIONS ON THE MAINLINE D VALVE SETTING OUTAGE FROM MLV 185D0 (STATION 185) TO R9 AT THE POTOMAC RIVER VALVE SITE (APPROX. 20.41 MILES OF 42" ML D), OPERATIONS PERSONNEL DETECTED A LEAK AT THE NEWLY INSTALLED MLV 185D14 VALVE SETTING AT 6:09 PM ET. THE SOURCE WAS THEN IDENTIFIED AS THE BACK WELD ON THE GREASE EXTENSION FITTING ON THE NEW 42" BALL VALVE. THE PACK STOPPED AT 6:42 PM ET AND PIPELINE SECTION WAS ISOLATED. THIS IS CONSIDERED AS THE SHUTDOWN TIME. IMMEDIATELY PERSONNEL BEGAN TO BLOWDOWN THE SECTION OF MAIN LINE D, AT ~7:00 PM. THE LINE WAS THEN ISOLATED, AND DRAWN DOWN THE NEXT DAY BY WASHINGTON GAS, AND BLOWDOWN RESUMED AGAIN AT 2:06 PM ON 2/19/2019. THE BLOWDOWN WAS COMPLETED TO 0 PSIG AT 8:40 PM ON 2/20/2019. THE LINE WAS THEN SWEPT WITH AIR AND THE CRACKED WELD CONNECTION BETWEEN THE GREASE FITTING EXTENSION AND THE MAIN VALVE BODY WAS POSITIVELY IDENTIFIED AS THE SOURCE OF THE LEAK. THE WELD WAS SAND BLASTED AND INSPECTED, AND REPAIRED USING TIG WELDING. THE CAUSE OF THE EQUIPMENT FAILURE WAS A CRACKED WELD CONNECTION AT THE FITTING. WELD REPAIR, INSPECTION, AND RE-COATING WAS COMPLETED BY 12:16 PM ON 2/23/2019 AND THE PIPELINE SECTION WAS RETURNED TO SERVICE (PURGE AND PACK) BY 6:49 PM ON 2/23/2019. NO FURTHER REVIEW OR ROOT CAUSE ANALYSIS (RCA) HAS BEEN PERFORMED. THE INITIAL TOTAL REPAIR COSTS WERE COLLECTED, REVIEWED, AND WERE DETERMINED TO EXCEED THE $50,000 LIMIT AT 10:15 AM ET ON 2/26/2019 DURING A PROJECT MEETING. THEREFORE, THIS LEAK EVENT IS A DOT REPORTABLE INCIDENT DUE TO THE REPAIR COSTS. THE NRC WAS CONTACTED AT 10:26 AM ET ON 2/26/2019 - INITIAL NRC# 1238646. A 48-HOUR UPDATE WAS SUBMITTED ON 2/28/2019 - NRC# 1238845, AND CORRECTED TO "WELD" CONNECTION, NOT "WELL" CONNECTION. A 30-DAY INCIDENT REPORT (F 7100.2) IS REQUIRED TO BE SUBMITTED TO PHMSA. FINAL REPAIR COSTS ARE INCLUDED IN THIS REPORT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190030 | 32951 | 2019-03-19 21:32 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2019-02-19 02:20 | 2019 |  |  | 42.8103 | -82.868 | 1238054 | 2019-02-19 10:23 |  | NATURAL GAS |  | 8367 | 1520 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-02-19 06:30 | 2019-10-15 11:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-02-19 02:43 | 2019-02-19 03:26 | ONSHORE | MI | 48005 | ARMADA | MACOMB | SURVEY STATION NO. | RELIEF VALVE | SLUG CATCHER VESSEL 3 - RELIEF VALVE PSV-00103 | SLUG CATCHER VESSEL 3 - RELIEF VALVE PSV-00103 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | SLUG CATCHER RELIEF VALVE PSV-00103 | 2018 |  | CARBON STEEL |  | OTHER | [8 empty] | VENTING GAS - SLUG CATCHER SAFETY RELIEF VALVE | CLASS 1 LOCATION | NO |  | 702 |  | NO | NO | NO |  | 0 | 0 | 4560 | 4652.78834192287 | 25268 | 25268 | 7700 | 7856.68206859783 | 1000 | 1020.34832059712 | 0 | 0 |  |  | 38528 | 32407.0267462791 | 38797.8187311178 | [8 empty] | 1194.79 |  | 1800 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [18 empty] | YES | [172 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  |  |  |  | JASON PIONK | GAS COMPLIANCE LEAD | 989-791-5749 | jason.pionk@cmsenergy.com | ON FEBRUARY 19, 2019 AT APPROXIMATELY 02:43 HOURS CONSUMERS ENERGY GAS CONTROL WAS NOTIFIED OF VENTING GAS AT RAY COMPRESSOR STATION. RAY COMPRESSOR STATION IS LOCATED IN ARMADA, MICHIGAN (MACOMB COUNTY). THE ON-CALL STATION MECHANIC WAS DISPATCHED AT 02:47 HOURS AND ARRIVED AT THE SITE AT APPROXIMATELY 03:26 HOURS AND GAS WAS NO LONGER VENTING. SECURITY CAMERAS AT THE STATION WERE USED TO DETERMINE THE APPROXIMATE LOCATION OF THE BLOWING GAS. UPON FURTHER INVESTIGATION THE SOURCE OF THE BLOWING GAS WAS DETERMINE TO BE THE PRESSURE RELIEF VALVE (PSV-00103) ON THE SLUG CATCHER. SUBSEQUENT REVIEW OF PRESSURE DATA INDICATES GAS BEGAN VENTING AT APPROXIMATELY 02:20 HOURS AND BLEW FOR APPROXIMATELY 37 MINUTES BEFORE PRESSURE READINGS NORMALIZED. AT APPROXIMATELY 06:30 HOURS THE SLUG CATCHER WAS ISOLATED TO FURTHER INVESTIGATE THE POTENTIAL CAUSE OF THE GAS RELEASE. DURING THE VISUAL INSPECTION, ICE IN THE PILOT SENSING LINE WAS IDENTIFIED AS A POTENTIAL CAUSE. AFTER CONSULTING WITH ENGINEERING THE DECISION WAS MADE TO ISOLATE THE SLUG CATCHER PRESSURE RELIEF VALVE AND RESUME NORMAL OPERATION OF THE SLUG CATCHER. ON FEBRUARY 20, 2019 AFTER CONTINUED INVESTIGATION AND ADDITIONAL ENGINEERING CONSULTATION, THE SLUG CATCHER WAS BLOWN DOWN AND REMOVED FROM SERVICE PENDING A ROOT CAUSE REVIEW. A ROOT CAUSE ANALYSIS (RCA) WAS CONDUCTED BY THE EXPERITEC, THE PRESSURE RELIEF VALVE MANUFACTURE, ON FEBRUARY 25, 2019. A SUMMARY OF THE INVESTIGATION RESULTS ARE AS FOLLOWS: BASED ON THE MULTIPLE CONFERENCE CALLS HELD WITH TAYLOR FORGE (VESSEL MANUFACTURER), CONSUMER ENERGY, EXPERITEC AND EMERSON IT IS OUR OPINION THAT THE EXTERNAL LOW AMBIENT TEMPERATURES AND INTERNAL WET CONDITIONS OF THE NATURAL GAS CAUSED THE SUBJECT RELIEF VALVE TO FREEZE AT VARIOUS POINTS WITHIN THE VALVE. THE FREEZING CAUSED THE VALVE TO OPEN BELOW IT DESIGNATED SET PRESSURE. THE MANUFACTURER RECOMMENDED THAT ALL FOUR (4) RELIEF VALVES BE HEAT TRACED AND INSULATED TO PREVENT THE POTENTIAL OF POSSIBLE FREEZING IN THE FUTURE. CONSUMERS ENERGY'S OPERATIONS HAVE BEEN PERFORMING THE RECOMMENDED REQUIREMENTS TO RETURN THE VESSEL TO SERVICE. THE ANTICIPATED RETURN TO SERVICE DATE IS MARCH 20, 2019. THE FOUR (4) RELIEF VALVES WERE HEAT TRACED AND INSULATED PER MANUFACTURER'S RECOMMENDATION ON MARCH 18, 2019. THE EQUIPMENT WILL RESUME NORMAL OPERATION AS NEEDED DURING THE 2019-2020 WITHDRAWAL SEASON.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190031 | 32447 | 2019-03-21 17:05 | SUPPLEMENTAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2019-02-21 15:45 | 2019 |  |  | 34.4746 | -84.9743 | 1238276 | 2019-02-21 16:08 |  | NATURAL GAS |  | 600.3 | 2138 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-02-21 18:39 | 2019-02-24 22:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 1 | 2019-02-21 14:19 | 2019-02-21 15:20 | ONSHORE | GA | 30701 | CALHOUN | GORDON | MILEPOST | VALVE 10 | CHATTANOOGA ROME CALHOUN CROSSOVER | CHATTANOOGA ROME CALHOUN CROSSOVER VALVE 10 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1986 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | NO |  | 107 |  | NO | NO | NO |  | 0 | 0 | 5644 | 5758.84592145015 | 1585 | 1585 | 128000 | 130604.585036431 | 2000 | 2040.69664119424 | 1712 | 1746.83632486227 | METALLURGICAL FAILURE ANALYSIS LAB COST |  | 138941 | 65976.2320509429 | 141735.963923938 | [8 empty] | 1030 |  | 1190 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 33137 | NO | [5 empty] | YES | SECTION IS NOT PIGGABLE BECAUSE IT DOES NOT HAVE LAUNCHERS OR RECEIVERS. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATING NORMALLY AT THE TIME DUE TO THE DEMAND OF THE SYSTEM. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | OTHER | FAILURE OF THE VALVE BOLTS WAS ATTRIBUTED TO HYDROGEN EMBRITTLEMENT, IN THE FORM OF HYDROGEN-STRESS CRACKING. | [16 empty] | YES | BOLTS DID NOT MEET THE ASTM A193 B7 HARDNESS SPECIFICATION. | [161 empty] | DANIEL GRANT | PIPELINE ENGINEER | daniel_grant@kindermorgan.com | 7134204409 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR OF COMPLIANCE CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | AT 14:19 EST ON 02/21/2019 SOUTHERN NATURAL GAS COMPANY (SNG) WAS NOTIFIED BY THE FIRE DEPARTMENT THAT THERE WAS AN ODOR AND PLUME OF GAS ABOVE A PIPELINE OPERATED BY SNG. AT 15:20 EST SNG PERSONNEL ARRIVED ON SITE. AT 18:39 EST THE SEGMENT WAS ISOLATED. AS A PRECAUTION THE HOME NEAR THE INCIDENT WAS EVACUATED AND THE OWNER STAYED WITH A RELATIVE FOR ONE NIGHT. THE FIRST VISUAL OBSERVATION OF THE RELEASE POINT IDENTIFIED THAT FOUR FACTORY INSTALLED BOLTS USED TO HOLD THE LOWER TRUNNION TO THE BALL VALVE WERE FOUND BROKEN OFF. THE UNINTENTIONAL AMOUNT OF GAS RELEASED WAS 600.3 MCF. TO REPAIR THE ISSUE THE DAMAGED VALVE WAS REMOVED AND BLIND FLANGES WERE INSTALLED ON BOTH ENDS OF THE PIPELINE. ON 02/24/2019 THE LINE WAS PURGED AND PUT BACK INTO SERVICE. THE ABNORMALLY HIGH REPAIR COSTS WERE DUE TO SNG CHOOSING TO MOBILIZE ITS CONTRACTOR AND WORK THROUGH THE WEEKEND TO MAKE THE REPAIRS SO THAT THE PIPELINE SYSTEM COULD BE RESTORED TO FULL CAPACITY AS SOON AS POSSIBLE, THUS MINIMIZING THE IMPACT TO DOWNSTREAM CUSTOMERS. THE ESTIMATED COST FOR REPAIRING THIS ISSUE UNDER NORMAL CIRCUMSTANCES IS $40,000. AFTER A METALLURGICAL ANALYSIS, THE FAILURE OF THE BOLTS WAS DETERMINED TO BE ATTRIBUTED TO HYDROGEN EMBRITTLEMENT, IN THE FORM OF HYDROGEN-STRESS CRACKING. THE TENSILE STRENGTH AND CHEMICAL COMPOSITION OF THE BOLTS CONFORM TO THE REQUIREMENTS OF ASTM A193 GRADE B7 MATERIAL. HOWEVER, THE BOLTS DID NOT MEET THE ASTM A193 B7 HARDNESS SPECIFICATION. THE BOLTS HAD A HARDNESS OF 40 HRC, WHICH EXCEEDS THE MAXIMUM ASTM A193 B7 HARDNESS REQUIREMENTS OF 35 HRC. THE HARDNESS CONDITION INCREASED THE MICROSTRUCTURE'S SUSCEPTIBILITY TO HYDROGEN CRACKING. NO EVIDENCE OF OVER-TORQUING, STRESS CORROSION CRACKING, OR OTHER METALLURGICAL IRREGULARITIES WAS FOUND. 48-HR NRC REPORT UPDATE NUMBER IS 1238409.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190033 | 32599 | 2019-03-27 16:34 | SUPPLEMENTAL FINAL | 13845 | NORTHWEST PIPELINE LLC | 295 CHIPETA WAY | SALT LAKE CITY | UT | 84108 | 2019-02-28 14:47 | 2019 |  |  | 43.5285 | -116.3431 | 1238916 | 2019-02-28 19:17 |  | NATURAL GAS |  | 934.65 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-03-03 11:16 | 2019-03-03 19:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-02-28 14:47 | 2019-02-28 14:47 | ONSHORE | ID | 83642 | MERIDIAN | ADA | MILEPOST | 823.3 | ALBERTSON'S METER STATION | 1400 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | FLANGE ASSEMBLY | [38 empty] | UNKNOWN |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 507 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 1020 | 1020 | 50000 | 51017.4160298561 | 2000 | 2040.69664119424 | 0 | 0 |  |  | 53020 | 25412.5540665156 | 54078.1126710503 | [8 empty] | 700 |  | 809 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SMALL UNDERGROUND LEAK NOT RELATED TO CONTROL ROOM ACTIVITY | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | GASKET | [7 empty] | YES | [172 empty] | SHANE FRASIER | PIPELINE SAFETY ENGINEER | shane.frasier@williams.com | 8015846844 |  |  |  |  | SHANE FRASIER | PIPELINE SAFETY ENGINEER | 8015846844 | shane.frasier@williams.com | THURSDAY MARCH 28TH TWO WILLIAMS INTEGRITY SPECIALISTS DISCOVERED A GAS LEAK AROUND THE ALBERTSONS METER STATION LOOP LINE TAP VALVE. THIS OCCURRED JUST BEFORE 1400 MOUNTAIN TIME. DURING THIS CONVERSATION IT WAS COMMUNICATED THAT LEVELS GREATER THAN 10% LEL WERE BEING MEASURED ON THE COUNTY ROAD ADJACENT TO THE FACILITY. THE EMPLOYEES WERE DIRECTED TO SECURE THE ROAD AT A SAFE DISTANCE AND CONTINUE TO MONITOR LEL LEVELS. AT 1404 FROM THAT INITIAL PHONE CALL THE DISTRICT LEADERSHIP MADE NOTIFICATION TO GAS CONTROL AND INTERMOUNTAIN GAS (IMG) OUR LOCAL LDC. GAS CONTROL ALSO TOOK THE LEAD TO INTERFACE WITH THE SOC. DISTRICT LEADERSHIP DISPATCHED TO THE SITE TO ESTABLISH AN INCIDENT COMMAND IF NEEDED. SITE ASSESSMENTS DETERMINED THE LOOP LINE TAP VALVE WAS THE PROBABLE CAUSE. THIS IS A 4' WELD BY FLANGE VALVE BURIED BELOW GRADE AT OR ABOUT 6 FEET. WITH CLOSE COORDINATION AND COMMUNICATION WITH INTERMOUNTAIN GAS ON SITE, IT WAS DETERMINED NEITHER NWP NOR IMG COULD ISOLATE THE FACILITY WITH CURRENT SYSTEM DEMAND. THIS DECISION POINT OCCURRED LATE IN THE DAY WHICH DROVE FURTHER STEPS TO SECURE THE ROAD LONG TERM AND COMMUNICATE THE ACTIVITY TO LOCAL PROPERTY OWNERS. A 24 HOUR SCHEDULE WAS STAFFED FOR CONTINUES MONITORING AND ON SITE RESPONSE IF NEEDED, ALONG WITH DIRECT LINES OF COMMUNICATION WITH GAS CONTROL. FRIDAY MARCH 1ST WITH WORK PLANS AND SSMP'S IN PLACE EXCAVATION AND CONSTRUCTION COMMENCED WITH THE INSTALLATION OF A THREAD-O-RING FITTING TO FACILITATE A TEMPORARY BYPASS TO MAINTAIN SYSTEM THROUGHPUT FOR IMG. SATURDAY MARCH 2ND WITH THE SUPPORT OF POCATELLO DISTRICT, GAS CONTROL, OTS, AND MATERIALS MANAGEMENT A TEMPORARY BYPASS WAS FABRICATED AND TESTED. SUNDAY MARCH 3RD AT 1116 THE BYPASS WAS PLACED IN SERVICE WITH CONTINUOUS MONITORING BY BOTH NWP AND IMG OPERATIONS PERSONNEL. EXCAVATION THEN BEGAN ON THE LOOP LINE TO EXPOSE THE SUSPECTED LEAKING FITTING. IT WAS CONFIRMED THAT A BLOWN INSULATING GASKET WAS THE CAUSE. THE GASKET WAS REPLACED WITH A FLEXITALLIC GASKET IN PLACE OF THE INSULATING FLANGE GASKET. THE LINE WAS THEN CHECKED FOR LEAKS. AT 1930 ALBERTSONS METER STATION WAS RETURNED TO SERVICE, BYPASS LINE BLOWN DOWN AND SECURED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190034 | 32184 | 2019-03-28 09:44 | SUPPLEMENTAL FINAL | 4070 | EAST TENNESSEE NATURAL GAS, LLC (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2019-03-01 15:16 | 2019 |  |  | 35.822 | -83.9791 | 1239000 | 2019-03-01 16:29 |  | NATURAL GAS |  | 190 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-03-01 16:00 | 2019-03-01 16:10 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-03-01 15:16 | 2019-03-01 15:53 | ONSHORE | TN | 37701 | ALCOA | BLOUNT | MILEPOST | 0.713 | M&R 59048 | MARY-TOPS | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | 1/2" NIPPLE AND ISOLATION VALVE | UNKNOWN |  | CARBON STEEL |  | LEAK |  |  | OTHER | DAMAGE DURING MAINTENANCE | [5 empty] | CLASS 1 LOCATION | NO |  | 112 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 544 | 544 | 50 | 51.0174160298561 | 0 | 0 | 0 | 0 |  |  | 594 | 587.407841458062 | 595.017416029856 | [8 empty] | 554 |  | 610 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE VOLUME OF THE LEAK WAS MINIMAL TO BE DETERMINED BY CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [260 empty] | MAYRA SALINAS | SENIOR ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: 48 HR NRC REPORT 1239112 AT APPROXIMATELY 3:16 PM EST ON MARCH 1, 2019, EAST TENNESSEE NATURAL GAS (ETNG) RECEIVED NOTIFICATION FROM A THIRD PARTY CONTRACTOR ABOUT DAMAGE TO ETNG'S PIPELINE FACILITIES (M&R 59048) IN BLOUNT COUNTY, TENNESSEE. EMERGENCY RESPONDERS ARRIVED ONSITE AND IMPLEMENTED A PARTIAL CLOSURE OF AN ADJACENT HIGHWAY UNTIL THE LEAK WAS ISOLATED. ETNG PERSONNEL ARRIVED ON SITE AT APPROXIMATELY, 3:53 PM EST ON MARCH 1, 2019 AND DETERMINED THAT A 1/2-INCH NIPPLE AND AN ISOLATION VALVE WAS DAMAGED CAUSING A RELEASE OF GAS. ETNG PERSONNEL SUBSEQUENTLY ISOLATED THE METER RUN AT APPROXIMATELY 4:00 PM EST AND REPLACED THE NIPPLE AND ISOLATION VALVE. THE METER RUN WAS RETURNED BACK TO SERVICE AT 4:10 PM EST. THE APPARENT CAUSE OF THE INCIDENT WAS A THIRD PARTY CONTRACTOR DAMAGING ETNG'S PIPELINE FACILITY WITH A FORKLIFT WHILE PREFORMING MAINTENANCE WORK FOR A THIRD PARTY PIPELINE UTILITY COMPANY. WHILE THIS INCIDENT DOES NOT MEET THE GAS LOSS OR COST CRITERIA OF A REPORTABLE INCIDENT, ETNG CLASSIFIED IT AS AN INCIDENT DUE TO THE PARTIAL CLOSURE OF THE HIGHWAY.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190035 | 32003 | 2019-03-28 18:45 | SUPPLEMENTAL FINAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-01-25 01:28 | 2019 |  |  | 41.2353 | -91.35 | 1239835 | 2019-03-11 17:46 |  | NATURAL GAS |  | 5679 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | ONLY UNIT 9 AND UNIT 10 FOR 80 MINUTES | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-25 00:45 | 2019-01-24 18:00 | ONSHORE | IA | 52738 | Not Within a Municipality | LOUISA | MILEPOST | 9.7 | COMPRESSOR STATION 204 (CIARO COLUMBUS LATERAL) | COMPRESSOR STATION 204 UNIT 9 DISCHARGE PIPING | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2007 |  | CARBON STEEL |  | OTHER | [8 empty] | SUSPECTED LIQUIDS IN THE RELIEF VALVE SENSING LINE AND RELIEF VALVE PILOT FROZE CAUSING THE RELIEF VALVE TO PREMATURELY OPEN. | CLASS 1 LOCATION | NO |  | 510 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 13630 | 13630 | 0 | 0 | 110 | 112.238315265683 | 0 | 0 |  |  | 13740 | 14182.3602433337 | 13742.2383152657 | [8 empty] | 210 |  | 712 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SEVERE COLD AND WIND CHILL EVENT; | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | NO | [306 empty] | WILLIAM MARTIN MULLER | SPECIALIST-PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205-325-3863 | 205-325-3592 |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | WITH EXTREME COLD TEMPERATURE OF APPROXIMATELY -6 DEGREES F AND WIND CHILL OF APPROXIMATELY -21 DEGREE F, SUSPECTED LIQUIDS IN THE RELIEF VALVE SENSING LINE AND RELIEF VALVE PILOT FROZE CAUSING THE RELIEF VALVE TO PREMATURELY OPEN. SAID RELIEF VALVE IS LOCATED OUTSIDE THE COMPRESSOR BUILDING ON THE UNIT 9 DISCHARGE PIPE. LOCAL SOFTWARE RECOGNIZED THE RELIEF VALVE EVENT AND IMMEDIATELY SHUT DOWN UNIT 9 HOWEVER THE RELIEF VALVE CONTINUED TO RELEASE GAS. NIGHT SHIFT STAFF WERE ON SITE WORKING THE COLD WEATHER SHIFT AND INVESTIGATED THE GAS RELEASE WITH IMMEDIATE ATTEMPT TO RESET THE RELIEF VALVE. THE STAFF APPLIED HEAT TO THE RELIEF VALVE TO THAW ANY SUSPECTED ICE AND MANUALLY CLOSED THE LINE VALVE TO ISOLATE THE RELIEF VALVE; THE RELIEF VALVE THEN RESET. STAFF RETURNED THE ISOLATION VALVE TO THE OPEN POSITION AND RETURNED UNIT 9 TO SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190036 | 32539 | 2019-03-29 10:44 | SUPPLEMENTAL FINAL | 32005 | ENLINK LBU-GAS&LIQUIDS | 1722 ROUTH STREET SUITE 1300 | DALLAS | TX | 75201 | 2019-03-04 15:20 | 2019 |  |  | 32.0077 | -93.7267 | 1239229 | 2019-03-04 16:16 |  | NATURAL GAS |  | 1 | 149 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-03-15 07:15 | 2019-03-17 15:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-03-04 15:20 | 2019-03-04 15:20 | ONSHORE | LA | 71052 | Not Within a Municipality | DESOTO | MILEPOST | MP16.43 | P1323-BAYOU PIERRE TO LOGANSPORT 6" | P1323-BAYOU PIERRE TO LOGANSPORT 6" | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | YES |  |  | YES | CASED | [18 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 |  | 0.195 | 35000 | GRADE B | LONGITUDINAL ERW - LOW FREQUENCY |  | UNKNOWN | OTHER | TGF | [27 empty] | 1940 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 93 |  | NO | NO | NO |  | 0 | 0 | 425 | 433.648036253776 | 3 | 3 | 131536 | 134212.536698063 | 0 | 0 | 0 | 0 |  |  | 131964 | 61809.2619156233 | 134649.184734317 | [8 empty] | 410 |  | 500 | OTHER | 192.557 |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 33528 | NO | YES | [6 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | DURING THE ANNUAL CP SURVEY |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A VERY SMALL LEAK INSIDE A CASING FOUND BY OPERATOR PERSONNEL DURING THE ANNUAL CP SURVEY. THE LEAK WAS NOT LARGE ENOUGH TO BE ABLE TO DISCOVER THE LEAK ON SCADA. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  |  | YES | [7 empty] | YES |  |  |  | YES | NO |  | YES | YES | YES |  |  |  | 2019 |  |  |  | YES | [190 empty] | NO | [63 empty] | YES | 2003 | 500 | NO | [13 empty] | NO | [63 empty] | CORDELL THERIOT | SR. DOT COMPLIANCE SPECIALIST | cordell.theriot@enlink.com | 3373226682 | 3379378524 |  |  |  | CORDELL THERIOT | SR. DOT COMPLIANCE SPECIALIST | 3373226682 | cordell.theriot@enlink.com | DURING THE ANNUAL CP SURVEY, OPERATIONS PERSONNEL FOUND AN APPARENT SMALL LEAK INSIDE A CASING AT A RAILROAD CROSSING. THE LEL ON THE VENT PIPE WAS FOUND TO BE 15%. IF THE REPAIR COST DID NOT EXCEED THE $50,000 THRESHOLD, THIS INCIDENT WOULD NOT HAVE BEEN REPORTABLE. THE ACTUAL LEAK WAS A MINOR PIN HOLE INSIDE THE CASING. IT APPEARS THE COATING WAS DAMAGED DURING THE INITIAL INSTALLATION OF THE CROSSING. THE CASING WAS NOT SHORTED. THE ESTIMATED GAS LOSS IS <1MCF.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190037 | 31886 | 2019-04-01 14:51 | ORIGINAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2019-03-06 06:50 | 2019 |  |  | 33.0919 | -93.3964 | 1239400 | 2019-03-06 14:47 |  | NATURAL GAS |  | 8600 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE FACILITY WAS SHUT DOWN | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-03-06 06:50 | 2019-03-06 08:55 | ONSHORE | AR | 71861 | TAYLOR | COLUMBIA | MILEPOST | 3146+22 | TAYLOR STATION | LINE S | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | MAUAL VALVE HAND PUMP | 2016 |  | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 421 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 24000 | 24000 | 2500 | 2550.8708014928 | 2500 | 2550.8708014928 | 0 | 0 |  |  | 29000 | 27223.7237783521 | 29101.7416029856 | [8 empty] | 723 |  | 880 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | CONTROLLER |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | FAILURE OF EQUIPMENT BODY (EXCEPT COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL | MATERIAL/WELD/EQUIP FAILURE | FAILURE OF EQUIPMENT BODY | [166 empty] | FAILURE OF EQUIPMENT BODY (EXCEPT COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL | [23 empty] | YES | [174 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | ON 3/6/2019 AT 06:50 ENABLE GAS TRANSMISSION SYSTEM CONTROL NOTICED A DECREASE IN FLOW FOR LINE S AND DISPATCHED THE LOCAL OPERATIONS GROUP TO INVESTIGATE. UPON ARRIVING AT THE TAYLOR COMPRESSOR STATION, OPERATIONS DISCOVERED GAS BLOWING THROUGH THE UNIT 4 BLOWDOWN STACK. AFTER FURTHER INVESTIGATION, OPERATIONS DISCOVERED A DISCHARGE VALVE HAD OPENED CAUSING GAS FROM LINE S TO FILL THE STATION AND GAS WAS VENTING TO ATMOSPHERE THROUGH AN OPEN BLOWDOWN. USING GAS PRESSURE TO SHUT THE DISCHARGE VALVE, THE STATION WAS ISOLATED FROM LINE S. OPERATIONS WORKED WITH SYSTEM CONTROL TO CONFIRM THAT PRESSURE ON LINE S HAD INDEED STARTED TO BUILD. FURTHER INVESTIGATION DETERMINED THE DISCHARGE VALVE OPENED DUE TO HYDRAULIC PRESSURE LEAKING BACK THROUGH TO THE MANUAL HAND PUMP BY WAY OF A CUT O-RING. THIS ALLOWED GAS TO FLOW INTO THE STATION AND SINCE THE STATION BLOWDOWNS WERE OPEN (TO ELIMINATE ANY BUILDUP OF STATION GAS THAT MIGHT LEAK BY CLOSED VALVES WHILE THE STATION IS OFFLINE) GAS WAS ALLOWED TO VENT TO ATMOSPHERE. A PUMP OVERHAUL KIT WAS PURCHASED AND INSTALLED ON THE FAULTY MANUAL HAND PUMP. AFTER THE OVERHAUL KIT WAS INSTALLED AND TESTED IT WAS NOTICED THAT THE MACHINING INSIDE THE MANUAL HAND PUMP HAD AN ILL-MACHINED PORT THAT WAS CUTTING THE NEW O-RING SIMILAR TO THE FIRST O-RING. A NEW PUMP WAS INSTALLED. THE GAS LOSS WAS DETERMINED TO BE 8.6 MMCF AT 14:17 AND A CALL WAS PLACED TO THE NRC (#1239400) AT 14:28. A 48-HOUR FOLLOW UP WAS PROVIDED TO THE NRC (#1239553) ON 3/8/19 AT 07:47
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190038 | 32815 | 2019-04-01 23:10 | SUPPLEMENTAL FINAL | 39167 | SABAL TRAIL TRANSMISSION, LLC (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2019-03-06 02:05 | 2019 |  |  | 28.2614 | -81.5563 | 1239356 | 2019-03-06 09:24 |  | NATURAL GAS |  | 21700 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-03-06 02:05 | 2019-03-06 20:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-03-06 02:05 | 2019-03-06 03:00 | ONSHORE | FL | 33869 | DAVENPORT | OSCEOLA | MILEPOST | 482.37 | COMPRESSOR STATION | DUMM-REUN | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2016 |  | CARBON STEEL |  | OTHER | [8 empty] | SUCTION BLOCK VALVE | CLASS 1 LOCATION | NO |  | 948 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 59458 | 59458 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 59458 | 61642.8083989501 | 59458 | [8 empty] | 1200 |  | 1456 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER'S ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. THE MALFUNCTION OF THE ISOLATION VALVE COULD NOT BE ASSOCIATED WITH THE ROLES AND RESPONSIBILITIES OF A CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | SUCTION VALVE | [22 empty] | YES | FAULTY LIMIT SWITCH | [161 empty] | NATHAN ATANU | SUPERVISOR | nathan.atanu@enbridge.com | 713-627-5008 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: 48 HR NRC REPORT 1239356 AT APPROXIMATELY 5:00 AM EST ON MARCH 6, 2019, AN ENBRIDGE TECHNICIAN DISCOVERED A NATURAL GAS RELEASE THROUGH A VENT VALVE ON UNIT 1 AT THE REUNION COMPRESSOR STATION ON THE SABAL TRAIL TRANSMISSION (STT) SYSTEM IN OSCEOLA COUNTY, FL. THE NATURAL GAS RELEASED OCCURRED DURING COMPRESSOR STATION UNIT OPERATIONS SWITCHOVER FROM UNIT 1 TO UNIT 2. AT APPROXIMATELY 2:05 AM EST, ENBRIDGE GAS CONTROL ISSUED A CALL ATTENDANT AND DISPATCHED AN ENBRIDGE TECHNICIAN HAVING DIFFICULTIES SWITCHING FROM UNIT 1 TO UNIT 2. AN ENBRIDGE TECHNICIAN ARRIVED ON SITE AT APPROXIMATELY 3:00 AM EST AND CLEARED ALARM ON UNIT 1. AT APPROXIMATELY, 5:00 AM EST THE ENBRIDGE TECHNICIAN DETERMINED THAT A SUCTION VALVE ON UNIT 1 HAD MALFUNCTIONED AND DID NOT COMPLETELY CLOSE RESULTING IN NATURAL GAS BEING VENTED TO THE STATION SOURCE CONTROL. THE ENBRIDGE TECHNICIAN SUBSEQUENTLY ISOLATED A MANUAL BLOCK VALVE DOWNSTREAM OF VENT VALVE TO STOP THE RELEASE OF NATURAL GAS TO ATMOSPHERE BAT 5:30AM EST. ENBRIDGE WAS UNABLE TO DETERMINE THE ESTIMATED GAS LOSS UNTIL APPROXIMATELY 9:00 AM EST. THE APPARENT CAUSE OF THE NATURAL GAS RELEASE IS STILL UNDER INVESTIGATION. SUPPLEMENTAL REPORT: THE CAUSE OF THE NATURAL GAS RELEASE WAS A MALFUNCTION OF THE UNIT 1 SUCTION VALVE DUE TO A FAULTY LIMIT SWITCH.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190039 | 32446 | 2019-04-02 15:18 | SUPPLEMENTAL FINAL | 15105 | PANHANDLE EASTERN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2019-03-03 03:23 | 2019 |  |  | 39.1923 | -91.891 | 1239100 | 2019-03-03 04:47 |  | NATURAL GAS |  | 90006 | 1713 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-03-03 04:25 | 2019-04-16 19:03 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 2 | 2019-03-03 03:23 | 2019-03-03 03:45 | ONSHORE | MO | 65265 | MEXICO | AUDRAIN | SURVEY STATION NO. | 739+83 | CENTRALIA DISCHARGE | 400 LINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 |  | 0.312 | 60000 | API-5LX | DSAW |  | KAISER | OTHER | PITTSBURGH ENAMEL | [27 empty] | 1962 | 1962 | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | 6 O'CLOCK POSITION | 864 | 94 |  | CLASS 1 LOCATION | NO |  | 621 |  | YES | NO | NO |  | 993000 | 1013205.88235294 | 5436 | 5546.61347076595 | 285616 | 285616 | 206000 | 210191.754043007 | 12000 | 12244.1798471655 | 0 | 0 |  |  | 1502052 | 865849.316385611 | 1526804.42971388 | [8 empty] | 888 |  | 900 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 84069 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 4 | 0 | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED |  | YES | [15 empty] | STRESS CORROSION CRACKING | [5 empty] | YES | [63 empty] | YES | YES |  |  | YES |  |  | YES | 2008 | [31 empty] | 2008 | [17 empty] | COMBINATION TOOL | 2015 |  |  |  |  | YES | 2019 | 1145 | NO | [13 empty] | NO | [63 empty] | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | (713)857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | (713)857-5479 | nathan.hlavaty@energytransfer.com | 3/3/19 3:28 CST COMPANY EMPLOYEE NOTIFIED GAS CONTROL OF LARGE FIRE NORTH OF MEXICO, MO NEAR 2 GATE. 3/3/19 3:36 CST EMPLOYEES DISPATCHED TO CENTRALIA STATION, 1 GATE AND 3 GATE. 3/3/19 3:45 CST EMPLOYEE ARRIVED ONSITE AND SPOKE TO MO STATE PATROL ONSITE. 3/3/19 4:17 CST DISCHARGE FIRE GATE CLOSED AT CENTRALIA STATION. 3/3/19 4:25 CST 403 GATE CLOSED. 3/3/19 4:35 CST 401 GATE CLOSED. 3/3/19 4:47 CST NRC TELEPHONIC NOTIFICATION MADE NRC#1239100. 3/3/19 4:54 CST FIRE DIMINISHED. 3/3/19 5:13 CST PHMSA AID NOTIFIED. 3/3/19 17:00 CST POWER RESTORED TO ELECTRIC CUSTOMERS. 3/4/19 22:11 CST 48-HOUR NRC NOTIFICATION MADE NRC#1239251. 3/4/19 22:43 CST PHMSA AID UPDATED. THE INITIAL SUPPLEMENTAL REPORT SUBMITTED ON 5/2/19 UPDATED THE FOLLOWING SECTIONS: PART A, QUESTION 15.B LOCAL TIME PIPELINE/FACILITY RESTARTED: 4/16/19 19:03 CST PART D, QUESTION 7.B ESTIMATED COST OF OPERATOR'S PROPERTY DAMAGE & REPAIRS: $206,000 THE SUPPLEMENTAL/FINAL DATED 7/19/19 UPDATED THE FOLLOWING SECTIONS: PART G, CONFIRMED CAUSE AS G5 ENVIRONMENTAL CRACKING RELATED BASED ON METALLURGICAL LAB ANALYSIS. PART G5, QUESTION 6, STRENGTH AND SPIKE PRESSURE TESTS WERE COMPLETED IN 2019, POST INCIDENT AND PRIOR TO RESTARTING THE LINE. STRENGTH TEST PRESSURE WAS 1145 PSIG. SPIKE TEST PRESSURE WAS 1264 PSIG.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20190040 | 33848 | 2019-04-02 17:36 | SUPPLEMENTAL FINAL | 32595 | HIGH POINT GAS GATHERING, LLC | THIRD COAST MIDSTREAM, LLC PO BOX 1227 | HOUSTON | TX | 77251 | 2019-01-14 13:15 | 2019 | CENTRAL | NO | 29.3875 | -89.4431 | 1235206 | 2019-01-14 14:47 |  | NATURAL GAS |  | 9094.533 | 10069 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-01-16 09:00 | 2019-12-03 08:00 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-01-14 14:00 | VALVE CLOSURE |  | 2019-01-15 15:00 | 0 | 2019-01-16 09:00 | 2019-01-15 07:00 | OFFSHORE | [28 empty] | 15 | IN STATE WATERS | LA | MARDI GRAS PASS | UNKNOWN | PLAQUEMINES |  |  |  | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 20 | NO | 0.344 | 60 | 52000 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | OTHER | ENAMEL WRAP WITH 2" CONCRETE | UNKNOWN | [26 empty] | 1953 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 20 | 0.5 |  | CLASS 1 LOCATION | NO |  | 400 |  | NO | NO |  |  | 0 | 0 | 33832 | 34520.4243824418 | 30558 | 30558 | 700000 | 714243.824417985 | 25000 | 25508.708014928 | 12000 | 12244.1798471655 | METALLURGICAL ANALYSIS | 3.36 | 801390 | 392712.985565937 | 817075.13666252 | 0 | 0 | 0 | 0 | NO |  |  |  | 800 | 20000 | 1072 | 192.619(A)(1) |  | 1953-12-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | AUTOMATIC | MANUAL | 79200 | YES | [7 empty] | NO | [6 empty] | OFFSHORE GATHERING | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS DISCOVERED BY A PUBLIC FISHERMAN, AND WAS A CAUSE OF WHAT APPEARS TO BE WELD FAILURE. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES |  |  |  | YES | MECHANICAL VIBRATION | [14 empty] | YES | [10 empty] | 800 | [54 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KEVIN STANLEY | SR. MANAGER EHS | kstanley@3cmidstream.com | 346-241-3585 |  |  |  |  | KEVIN STANLEY | SR. MANAGER EHS | 346-241-3585 | kstanley@3cmidstream.com | A FISHERMAN IN THE AREA SAW THE BUBBLING WATER AND REPORTED TO THE NRC AND THE LOCAL PARISH SHERIFF'S OFFICE. AMID OPERATIONS CONTROL CENTER WAS NOTIFIED BY THE US COAST GUARD. AFTER FLY-OVERS TO VIEW THE AREA, IT WAS CONFIRMED TO BE AN AMID 20" NATURAL GAS GATHERING PIPELINE. THE LINE WAS SHUT IN. UPON FURTHER INVESTIGATION BY A THIRD-PARTY CONTRACTOR, THE LINE HAD FAILED AT A WELD, WITH THE ENTIRE GIRTH COMING APART. THIRD PARTLY ANALYSIS ON THE PIPE DETERMINED THE ROOT CAUSE WAS FATIGUE FRACTURE IN GIRTH WELDMENT DUE TO MECHANICAL VIBRATION (OSCILLATION). INSTALLED MECHANICAL FLANGES AT EACH CUT WHERE THE DAMAGED SECTION OF THE PIPELINE WAS REMOVED. INSTALLED PRE-HYDROTESTED PIPE SECTION WITH 9 PALLETS OF 3:1 CEMENT/SAND BAGS FOR SUPPORT. LINE WAS LEAK TESTED AT OPERATING PRESSURE, DIVERS OBSERVED FOR 2 HOURS AND VERIFIED NO LEAKS AT THE FLANGES.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190041 | 31960 | 2019-04-03 09:18 | SUPPLEMENTAL FINAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-03-05 17:13 | 2019 |  |  | 29.7943 | -93.7481 | 1239330 | 2019-03-05 18:04 |  | NATURAL GAS |  | 66216.8 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-03-05 17:12 | 2019-03-06 07:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-03-05 17:13 | 2019-03-05 17:55 | ONSHORE | LA | 70631 | CAMERON | CAMERON | SURVEY STATION NO. | R-14-W,T-14-S | COMPRESSOR STATION 342 | VALVE #1342-5 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2006 |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENTIONAL GAS LOSS THROUGH A SIDE GATE VALVE. VALVE FAILED TO CLOSE ALL THE WAY DURING THE STATION ESD. | CLASS 1 LOCATION | NO |  | 589 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 203286 | 203286 | 15750 | 16070.4860494047 | 0 | 0 | 16532 | 16868.3984361116 | COST TO MAN THE STATION UNTIL IT WAS BROUGHT BACK INTO SERVICE |  | 235568 | 225875.64390334 | 236224.884485516 | [8 empty] | 955 |  | 1100 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO ACTIONS WERE BEING PERFORMED BY GAS CONTROL AT THE STATION AND THERE WERE NO INDICATIONS OF AN ABNORMAL OPERATION EVENT BEFORE THE ALARM. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | YES | [9 empty] | YES | [24 empty] | YES | DISCH. SIDE GATE VALVE PNEUMATIC INTERLOCKING DEVICES DIDN'T FUNCTION PROPERLY | [161 empty] | KRISTIN VAN DER LAAN | MANAGER-ENGINEERING-COMPLIANCE CODES AND STNDS | kristin_vanderlaan@kindermorgan.com | [5 empty] | JAIME HERNANDEZ | DIRECTOR-ENGINEERING-COMPLIANCE CODES AND STNDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | AT 17:12 CST, THE STATION EMERGENCY SHUTDOWN (ESD) SYSTEM AT THE NATURAL GAS PIPELINE COMPANY OF AMERICA, LLC (NGPL) STATION 342 IN JOHNSON BAYOU, LA (CAMERON PARISH) WAS ACTIVATED. NGPL GAS CONTROL IN HOUSTON, TX RECEIVED AN ABNORMAL SHUTDOWN ALARM AROUND 17:13. THE CONTROLLER DISPATCHED A TECHNICIAN TO THE SITE. PERSONNEL ARRIVED AT THE STATION AT 17:55. UPON ARRIVAL, THE TECHNICIAN ASSESSED THE SITUATION RECOGNIZING THAT THE DISCHARGE BLOWDOWN VALVE WAS VENTING GAS; THEREFORE, THE DISCHARGE SIDE GATE VALVE (1342-5) DID NOT CLOSE PROPERLY WHEN THE ESD WAS ACTIVATED. THE TECHNICIAN CLOSED THE VALVE STOPPING THE RELEASE OF GAS AT 17:58. NOTE THAT LOCAL EMERGENCY RESPONDERS HAD TEMPORARILY BLOCKED THE ACCESS ROAD TO THE STATION (DEEP BAYOU ROAD) UNTIL THE GAS RELEASE STOPPED. STATION PERSONNEL BEGAN INVESTIGATING THE CAUSE OF THE ESD AND IT WAS INITIALLY DETERMINED THAT THE PNEUMATIC FIRE PROTECTION PANEL TRIPPED INITIATING THE ESD. RETURN TO SERVICE WAS DELAYED DUE TO DETERMINING THE CAUSE OF THE ESD AS WELL AS OBTAINING REPLACEMENT COMPONENTS IN THE FIRE PROTECTION PANEL. ADDITIONALLY, LINE BREAK/PIPELINE RUPTURE DETECTION DEVICES HAD CLOSED THE UPSTREAM AND DOWNSTREAM MAINLINE BLOCK VALVES ADDING TO THE DELAY. THE DELAY IMPACTED ONE NGPL CUSTOMER, THE CHENIERE LNG FACILITY. THE INVESTIGATION DETERMINED THAT THE ESD WAS CAUSED BY COMPONENT FAILURE OF THE PNEUMATIC ESD RESET PALM BUTTON IN THE FIRE PROTECTION CONTROL PANEL. ADDITIONALLY, THE ESD DID NOT FUNCTION AS DESIGNED DUE TO THE DISCHARGE SIDE GATE VALVE NOT CLOSING FULLY DUE TO THE PNEUMATIC INTERLOCKING DEVICES NOT FUNCTIONING PROPERLY. NOTE: 48-HOUR NRC UPDATE #1239500
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190042 | 32017 | 2019-04-12 10:26 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2019-03-20 12:00 | 2019 |  |  | 42.3487 | -94.0408 | 1240413 | 2019-03-20 16:30 |  | NATURAL GAS |  | 62000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | SERVICE TO THE TOWN OF LEHIGH, IA COULD BE MAINTAINED WITH THE LEAK. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-03-20 12:00 | 2019-03-20 13:00 | ONSHORE | IA | 50557 | Not Within a Municipality | WEBSTER | MILEPOST | 20.88 | OGDEN TO VENTURA | M520A | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION | [19 empty] | OTHER BUTT WELD | [18 empty] | 1956 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 70 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 142600 | 142600 | 100000 | 102034.832059712 | 10000 | 10203.4832059712 | 0 | 0 |  |  | 252600 | 199360.24333372 | 254838.315265683 | [8 empty] | 360 |  | 380 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 10600 | NO | [5 empty] | YES | 2-INCH PIPELINE | YES |  |  |  |  | YES | 2-INCH PIPELINE | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK IS SO SMALL THAT SCADA DID NOT REGISTER A PRESSURE DROP AND THERE WAS NO LOSS OF SERVICE. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [52 empty] | HEAVY RAINS/FLOODS |  | OTHER |  |  | FLOATING DEBRIS (WOOD OR ICE) STRUCK ABOVE GROUND APPURTENANCE THAT WAS SUBMERGED IN FLOOD WATERS AND CAUSED LEAKAGE. | NO | [306 empty] | JOHN A GORMLEY | SR CORROSION SPECIALIST - PIPELINE SAFETY | john.gormley@nngco.com | 402-398-7494 |  |  |  |  | TOM CORRELL | VP PIPELINE SAFETY AND RISK | 402-398-7715 | thomas.correll@nngco.com | ON MARCH 20, 2019, THE OGDEN (IOWA) FIELD OPERATIONS TEAM WAS NOTIFIED BY THE COUNTY SHERIFF OF GAS BLOWING UNDER THE FLOOD WATERS OF THE DES MOINES RIVER NEAR THE TOWN OF LEHIGH, IOWA. THE LEHIGH TAKE-OFF VALVE SETTING IS LOCATED IN THIS AREA AND WAS COMPLETELY SUBMERGED BY THE FLOOD WATERS OF THE DES MOINES, RIVER. THE LEAK WAS SMALL ENOUGH THAT NO LOSS OF SERVICE OCCURRED. THE FIELD OPERATIONS TEAM INSPECTED THE SITE DAILY TO MONITOR THE LEAK AND CHECK ON FLOOD WATER LEVELS. THE SITE WAS STILL UNDER WATER AS OF APRIL 12, 2019 BUT THE LEAK WAS VISIBLE FROM SHORE. THE BUTT WELD BELOW THE BLOW OFF VALVE BETWEEN THE WELD NECK FLANGE AND TEE IS CRACKED PROBABLY DUE TO BEING STRUCK BY FLOATING ICE. THE WELD QUALITY IS NOT SUSPECTED SO IT WON'T BE SENT TO A LABORATORY FOR ANY FURTHER ANALYSIS. THE TAKE-OFF SETTING WAS TOTALLY BYPASSED TO ELIMINATE THE LEAK. THE SECTION OF A-LINE WAS ISOLATED, BLOWN DOWN AND CAPPED. THE TOWN OF LEHIGH, IA IS BEING FED FROM THE B-LINE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190043 | 32171 | 2019-04-12 11:53 | SUPPLEMENTAL FINAL | 4900 | KINDER MORGAN TEJAS PIPELINE | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2019-03-17 06:41 | 2019 |  |  | 29.9884 | -93.9327 | 1240289 | 2019-03-17 08:19 |  | NATURAL GAS |  | 5302 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-03-17 07:35 | 2019-03-17 14:37 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-03-17 05:44 | 2019-03-17 07:20 | ONSHORE | TX | 77651 | PORT NECHES | JEFFERSON | SURVEY STATION NO. | STATION 3+46 | SABINE COMPRESSOR STATION | TEXACO - SABINE CS TIE-IN | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1996 |  | CARBON STEEL |  | OTHER | [8 empty] | AS DESIGNED, STATION ESD ACTIVATED FOLLOWING LOSS OF COMMERCIAL POWER AND LATER LOSS OF UPS POWER AND ESD ISOLATION VALVE FG-3 DID NOT CLOSE ALLOWING A NATURAL GAS TO CONTINUE FLOW INTO ESD SYSTEM; | CLASS 1 LOCATION | NO |  | 246 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 14845 | 14845 | 7000 | 7142.43824417985 | 500 | 510.17416029856 | 0 | 0 |  |  | 22345 | 18903.2365861634 | 22497.6124044784 | [8 empty] | 756 |  | 1100 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | NO | NO | NO | OTHER | ADJACENT COMPANY MOTIVA CALLED GAS CONTROL; CUSTOMER ENLINK CALLED GAS CONTROL; |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | AS DESIGNED, STATION ESD ACTIVATED FOLLOWING LOSS OF COMMERCIAL POWER AND LATER LOSS OF UPS POWER AND ESD ISOLATION VALVE FG-3 DID NOT CLOSE ALLOWING A NATURAL GAS TO CONTINUE FLOW INTO ESD SYSTEM; UPON THE COMPLETE LOSS OF POWER, THE COMPRESSOR STATION PLC SENT MISCELLANEOUS, INADVERTENT, AND INACCURATE STATUS AND SIGNALS THROUGH THE SCADA SYSTEM TO KM TEJAS GAS CONTROL. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | ESD ISOLATION VALVE FG-3 DID NOT CLOSE ALLOWING A NATURAL GAS TO CONTINUE FLOW INTO ESD SYSTEM; | [11 empty] | YES | [173 empty] | WILLIAM MARTIN MULLER | SPECIALIST-PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205-325-3863 | 205-325-3592 |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | POST INCIDENT INVESTIGATION DETERMINED KM TEJAS SABINE COMPRESSOR STATION LOST COMMERCIAL AC POWER, 3/15/2019, AT 18:00 HOURS. FOLLOWING THE COMMERCIAL AC POWER FAILURE, THE COMPRESSOR STATION WAS PROVIDED ELECTRICAL POWER BY THE COMPRESSOR STATION UPS BATTERY SYSTEM. ONCE THE UPS BATTERY SYSTEM WAS DEPLETED, THE COMPRESSOR STATION WENT INTO ESD MODE AS COMPRESSOR STATION LOGIC IS PROGRAMMED FOR A COMPLETE POWER LOSS OCCURRENCE. 3/17/2019, 05:44-HOURS MOTIVA EMPLOYEE CALLED KM TEJAS GAS CONTROL CONCERNING A POSSIBLE EVENT AT THE COMPRESSOR STATION SITE. 05:45-HOURS, ENLINK EMPLOYEE CALLED KM TEJAS GAS CONTROL BELIEVING KM TEJAS WAS TAKING NATURAL GAS FROM ENLINK. UPON THE COMPLETE LOSS OF POWER, THE COMPRESSOR STATION PLC SENT MISCELLANEOUS, INADVERTENT, AND INACCURATE STATUS AND SIGNALS THROUGH THE SCADA SYSTEM TO KM TEJAS GAS CONTROL. BECAUSE THE PLC WAS BLACKED-OUT, ALL COMPRESSOR STATION ALARMS AND COMPRESSOR STATION VALVE STATUS SEEN THROUGH SCADA DID NOT REFLECT ACTUAL COMPRESSOR STATION VALVE CONFIGURATIONS. ALSO UPON THE COMPLETE LOSS OF POWER, A VALVE IDENTIFIED AS FIREGATE 3 (FG-3), ONE OF THE COMPRESSOR STATION ESD ISOLATION VALVES, DID NOT CLOSE. THE OPEN VALVE FG-3 ALLOWED NATURAL GAS TO FLOW FROM CUSTOMER ENLINK THROUGH KM TEJAS METERS AND INTO THE COMPRESSOR STATION ESD SYSTEM THEREBY RELEASING ADDITIONAL NATURAL GAS TO ATMOSPHERE. NATURAL GAS VENTED UNTIL THE KM TEJAS EMPLOYEE ACCESSED THE COMPRESSOR STATION SITE BY ENTRY THROUGH MOTIVA PROPERTY SECURITY AND ARRIVED AT THE COMPRESSOR STATION SITE AT 07:20-HOURS AND CONFIRMED NATURAL GAS WAS VENTING AND MANUALLY CLOSED TWO (2) UPSTREAM VALVES ON THE METER RUNS TO TERMINATE THE NATURAL GAS RELEASE AT 07:35-HOURS. COMMERCIAL AC POWER WAS RESTORED TO THE COMPRESSOR STATION AND THE COMPRESSOR STATION RETURNED TO SERVICE AT 14:37-HOURS ON 3/17/2019. FOLLOWING THIS INCIDENT, KM TEJAS REPLACED VALVE FG-3 TO ENSURE VALVE OPERATION RELIABILITY. ALSO BY ELECTIVE CHOICE, KM TEJAS HAS INSTALLED LOSS OF AC POWER INDICATOR ALARMS IN THE COMPRESSOR STATION PLC SYSTEM. THE TEXAS RAILROAD COMMISSION INCIDENT REPORT NUMBER FOR THIS INCIDENT IS #1958. THE NRC 48-HOUR UPDATE INCIDENT REPORT NUMBER FOR THIS INCIDENT IS #1240384. SUBMITTING AS FINAL WITH NO CHANGES.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190044 | 33451 | 2019-04-12 12:16 | SUPPLEMENTAL FINAL | 31286 | ONEOK GAS TRANSPORTATION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2019-02-07 03:00 | 2019 | CENTRAL | NO | 35.7474 | -97.6388 | 1237104 | 2019-03-07 15:56 |  | NATURAL GAS |  | 6736 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | RELIEF VALVE |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2019-02-07 03:00 | 2019-02-07 03:00 | ONSHORE | OK | 73003 | EDMOND | LOGAN | MILEPOST | EDMONDSTORAGE | EDMOND STORAGE | A-4002 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2008 | 2008 | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE RELEASED PRIOR TO SET POINT. | CLASS 1 LOCATION | NO |  | 500 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 19537 | 19537 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2.9004 | 19537 | 20254.8950131234 | 19537 | 0 | 0 | 0 | 0 | NO |  |  |  | 729 | 97 | 740 | 192.619(A)(1) |  | 1979-05-15 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  |  | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLS HAVE NO CONTROL OF THE MANUAL RELIEF VALVES | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | RELIEF VALVE RELEASED PRIOR TO SET POINT. | [161 empty] | JACK CROW | COMPLIANCE SPECIALIST | jcrow@oneok.com | 4053232492 |  |  |  |  | JACK CROW | COMPLIANCE SPECIALIST | 4053232492 | jcrow@oneok.com | THURSDAY FEBRUARY 7TH AT 3:00 AM THE 8' RELIEF VALVE PROTECTING A-4002 FROM A-1129 WENT OFF AT 729 PSI WITH A 740 PSI SET POINT. MERCER VALVE HAD TESTED THE RELIEF VALVE WEDNESDAY FEBRUARY 4TH. THE EVENT LASTED FOR 15 MINUTES AT 729 PSI THROUGH A 8' RELIEF WITH AN APPROX. 6MMCF GAS LOSS. MERCER HAS RETESTED THE RELIEF VALVE AND FOUND TO BE SET AT 740 PSI SET POINT. THE FREEZING COLD TEMPERATURES AND PRESSURES WITHIN 11 PSI OF MAOP MAY HAVE BEEN THE LEADING CAUSE OF EVENT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190045 | 34165 | 2019-04-12 16:05 | SUPPLEMENTAL FINAL | 31286 | ONEOK GAS TRANSPORTATION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2019-02-22 15:00 | 2019 | CENTRAL | NO | 35.6828 | -97.1163 | 1238392 | 2019-02-22 17:06 |  | NATURAL GAS |  | 491 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-02-22 18:45 | 2019-02-23 15:15 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-02-22 18:45 | VALVE CLOSURE |  | 2019-02-22 18:45 | 0 | 2019-02-22 15:15 | 2019-02-22 15:15 | ONSHORE | OK | 74881 | WELLSTON | LINCOLN | MILEPOST | A-26 | A-26 | A-26 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PULSATION BOTTLE OR DRIP/DRIP COLLECTION DEVICE | [38 empty] | 1951 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 500 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 1188 | 1188 | 50000 | 51017.4160298561 | 5000 | 5101.74160298561 | 5000 | 5101.74160298561 | INSPECTION COST | 2.42 | 61188 | 29333.6617181782 | 62408.8992358273 | 0 | 0 | 0 | 0 | NO |  |  |  | 542 | 194 | 600 | 192.619(A)(1) |  | 1970-01-01 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 41184 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [10 empty] | YES |  |  |  |  | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES |  |  | UTILITY OWNER | YES | YES | YES | 22 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO SUPPORT EXPOSED FACILITIES | [263 empty] | JACK CROW |  | jcrow@oneok.com | 4053232492 |  |  |  |  | JACK CROW |  | 4053232492 | jcrow@oneok.com | EXCAVATOR WORKING FOR OPERATOR FAILED TO PROTECT THE PIPE FROM EXCAVATION DAMAGE. DIRT SLOUGHED OFF BANK STRIKING A 1-INCH DRIP LINE AND BROKE A 1-INCH NIPPLE JUST ABOVE THE VALVE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190046 | 32035 | 2019-04-15 15:35 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2019-03-25 03:13 | 2019 |  |  | 38.1459 | -97.4542 | 1240963 | 2019-03-25 07:46 |  | NATURAL GAS |  | 9300 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-03-25 03:13 | 2019-03-25 07:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-03-25 03:46 | 2019-03-25 03:46 | ONSHORE | KS | 67062 | Not Within a Municipality | HARVEY | MILEPOST | GATE 42 | HESSTON COMPRESSOR STATION | 171-01-001 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1954 |  | CARBON STEEL |  | OTHER | [8 empty] | DURING ESD OF THE HESSTON COMPRESSOR STATION, THE STATION ISOLATION GATE VALVE #42 FAILED TO CLOSE ALLOWING MAINLINE GAS TO VENT DURING THE STATION BLOW-DOWN | CLASS 1 LOCATION | NO |  | 414 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 21155 | 21155 | 1200 | 1224.41798471655 | 0 | 0 | 0 | 0 |  |  | 22355 | 22494.3892448623 | 22379.4179847165 | [8 empty] | 580 |  | 900 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE AUTOMATIC ESD WAS TRIGGERED AND THE UNINTENTIONAL GAS RELEASE BECAUSE THE ISOLATION VALVE FAILED TO CLOSE, THE CONTROLLER WAS NOT AT FAULT | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | ISOLATION VALVE FAILED TO AUTOMATICALLY CLOSE DURING ESD. | [161 empty] | ERIC GLAHN | PIPELINE COMPLIANCE ENGINEER | eric.glahn@southernstar.com | 270-852-4414 | 270-852-5016 |  |  |  | SHAWN PATTERSON | VP AND CHIEF OPERATIONS OFFICER | 270-852-4670 | shawn.patterson@southernstar.com | ON 3/25/2019 AT 3:13 AM LOCAL TIME, SOUTHERN STAR CENTRAL GAS PIPELINE (SSCGP) GAS CONTROL RECEIVED AN ALARM THAT AN AUTOMATIC EMERGENCY SHUTDOWN (ESD) WAS UNDERWAY AT THE HESSTON COMPRESSOR STATION IN HARVEY COUNTY, KANSAS. OPERATIONS PERSONNEL WERE DISPATCHED TO THE STATION ARRIVING AT 3:46 AM. UPON ARRIVAL IT WAS NOTICED THAT GAS WAS STILL VENTING OUT OF THE STATION BLOW-OFF STACK. IT WAS DETERMINED THAT VALVE #42 FAILED TO CLOSE AUTOMATICALLY AND IT WAS CLOSED MANUALLY USING GAS POWER AT 3:56 AM AND THE GAS RELEASE STOPPED. SINCE THE GAS RELEASE WAS PART OF AN ESD IT WAS NOT IMMEDIATELY DETERMINED THAT THIS WAS A REPORTABLE EVENT. A SOLENOID VALVE IN THE BASEMENT FOR THE ESD SYSTEM WAS REPLACED AND THE STATION WAS BROUGHT BACK INTO OPERATION AT 7:15 AM. THE INITIAL GAS LOSS ESTIMATE WAS MADE AT 7:30 AM AND IT WAS DETERMINED THAT THIS WOULD BE A REPORTABLE EVENT AND THE NRC WAS CALLED AT 7:46 AM (NRC#1240963). AFTER INVESTIGATING THE ISOLATION VALVE, THE CAUSE OF THE FAILURE OF THE VALVE TO CLOSE WAS BECAUSE SOME MATERIAL HAD BUILT UP IN THE OPERATOR OF THE VALVE. ALL COMPONENTS OF THE VALVE WERE CLEANED OUT. ALL OF THE ESD LINES WERE ISOLATED AND BLOWN OUT TO REMOVE ANY DEBRIS THAT MAY HAVE BEEN REMAINING IN THE LINE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190047 | 32549 | 2019-04-17 14:22 | SUPPLEMENTAL FINAL | 5304 | FLORIDA GAS TRANSMISSION CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2019-03-21 16:38 | 2019 |  |  | 25.6667 | -80.3185 | 1240712 | 2019-03-21 19:55 |  | NATURAL GAS |  | 5017 | 773 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-03-21 17:51 | 2019-03-23 20:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 1 | 2019-03-21 16:38 | 2019-03-21 17:21 | ONSHORE | FL | 33156 | PINECREST | MIAMI DADE | SURVEY STATION NO. | 7235+24 | FGT | FLMEA-22 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 60 |  | YES |  |  |  |  | YES | UNCASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 18 |  | 0.25 | 52000 | API 5LX | LONGITUDINAL ERW - HIGH FREQUENCY |  | YOUNGSTOWN SHEET AND TUBE | POLYOLEFIN | [28 empty] | 1959 | 1959 | CARBON STEEL |  | MECHANICAL PUNCTURE | 3 | 3 | [7 empty] | CLASS 3 LOCATION | YES | METHOD2 | 211 |  | NO | NO | NO |  | 15500 | 15815.3989692554 | 4191 | 4276.27981162253 | 15923 | 15923 | 226912 | 231529.278123334 | 0 | 0 | 0 | 0 |  |  | 262526 | 132008.75581199 | 267543.956904212 | [8 empty] | 269 |  | 288 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 24288 | NO | [5 empty] | YES | THIS LINE DOES NOT HAVE A LAUNCHER OR RECEIVER INSTALLED. THE MAOP HAS BEEN REDUCED TO 288 PSI IN RECENT YEARS. MAOP 288 IS OPERATING AT 20% OF SMYS. | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INVESTIGATION WAS NOT NECESSARY DUE TO PIPELINE OPERATING NORMALLY BEFORE BEING HIT BY 3RD PARTY DIGGING IN THE AREA. | [12 empty] | YES | 3 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | NO | YES | CITY STREET | [9 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 72915175 | N/A | UTILITY OWNER | YES | YES | YES | 50 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NOTIFICATION TO ONE-CALL CENTER MADE, BUT NOT SUFFICIENT | [265 empty] | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | (713)857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | (713)857-5479 | nathan.hlavaty@energytransfer.com | 3/21/19 17:41 EST OPERATIONS ARRIVED ON SITE AND CONFIRMED LINE HIT. 3/21/19 17:48 EST LINE SHUT IN AND ISOLATED. 3/21/19 19:55 EST NRC TELEPHONIC NOTIFICATION MADE NRC#1240712. 3/21/19 20:20 EST PHMSA AID NOTIFIED. 3/21/19 21:00 EST FPL POWER RESTORED TO CUSTOMERS AND EVACUEE RETURNED HOME. 3/23/19 16:09 EST REPLACEMENT COMPLETED AND LINE PUT BACK IN SERVICE. 3/23/19 17:54 EST 48-HOUR NRC NOTIFICATION MADE NRC#1240870. 3/23/19 18:23 EST PHMSA AID UPDATED. THE SUPPLEMENTAL REPORT SUBMITTED 8/13/19, CORRECTED PART A: 5 - LATITUDE/LONGITUDE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190048 | 32425 | 2019-04-19 10:14 | SUPPLEMENTAL FINAL | 11032 | SPIRE MISSOURI INC. EAST | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2019-03-19 08:00 | 2019 |  |  | 38.6613 | -90.2896 | 1240527 | 2019-03-20 08:31 |  | NATURAL GAS |  | 4.56 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | LEAK WAS ON DRIP RISER, NOT ON THE LINE PIPE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-03-19 08:30 | 2019-03-19 08:43 | ONSHORE | MO | 63112 | ST. LOUIS | Not Within a County or Parish | SURVEY STATION NO. | STA 302+27 | LANSDOWNE TO STATION N | C-2 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 120 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PULSATION BOTTLE OR DRIP/DRIP COLLECTION DEVICE | [38 empty] | 1951 |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | YES | METHOD2 | 287 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 14 | 14 | 61272 | 62518.7822996268 | 1500 | 1530.52248089568 | 0 | 0 |  |  | 62786 | 29414.8353882457 | 64063.3047805225 | [8 empty] | 185 |  | 300 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 20 | NO |  | YES | YES | YES |  |  |  | YES |  | YES |  |  |  |  | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATIONAL PARAMETERS WERE NOT EXCEEDED. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [103 empty] | OTHER OUTSIDE FORCE DAMAGE | [9 empty] | WHILE LIFTING A STREET COVER PLATE, THE PLATE STRUCK THE DRIP BOX AND CRACKED THE 2" DRIP RISER INSIDE THE BOX RESULTING IN A LEAK. | [251 empty] | LAURA KLECKLEY | MANAGER TIM CORROSION CONTROL PUBLIC AWARENESS | laura.kleckley@spireenergy.com | 205-326-2680 |  |  |  |  | CRAIG R. HOEFERLIN | VP OPERATIONS SERVICES | 314-349-2972 | craig.hoeferlin@spireenergy.com | ON MARCH 19, 2019 AT 8:00 AM CST, A SPIRE STREET REPAIR CREW DAMAGED A DRIP BOX WHILE LIFTING A STREET COVER PLATE. THE 2" DRIP RISER ATTACHED TO THE TRANSMISSION PIPELINE WAS CRACKED INSIDE THE DRIP BOX AND RESULTED IN A LEAK. THE TRANSMISSION PIPELINE WAS NOT DAMAGED. SPIRE INSTALLED A 2" STOPPER FITTING AND CAPPED THE RISER TO REPAIR THE LEAK, WHICH WAS COMPLETED AT APPROXIMATELY 12:00 AM CST ON MARCH 21, 2019. A 48 HR. UPDATE WAS CALLED INTO THE NRC AT 9:18 AM CST ON MARCH 22, 2019 THAT THE LEAK HAD BEEN PERMANENTLY REPAIRED AND THERE WAS NO MORE RELEASE OF GAS TO THE ENVIRONMENT; NRC REPORT NUMBER 1240741.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20190049 | 32882 | 2019-04-23 16:15 | SUPPLEMENTAL FINAL | 31130 | DCP MIDSTREAM | 370 17TH STREET SUITE 2500 | DENVER | CO | 80202 | 2019-04-02 10:00 | 2019 |  |  | 40.2921 | -104.9418 | 1242220 | 2019-04-08 16:22 |  | NATURAL GAS |  | 533 | 32 | 1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-04-02 10:30 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 2 | 2019-04-02 10:00 | 2019-04-02 10:15 | ONSHORE | CO | 80534 | Not Within a Municipality | WELD | SURVEY STATION NO. | 6+176 | SOCO GATHERING SYSTEM | BZ-7-1-2-EXT | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 |  | 0.125 |  | UNKNOWN | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 2 LOCATION | NO |  | 83 |  | NO | YES | NO |  | 59951 | 61170.902168118 | 71 | 72.4447307623956 | 1359 | 1359 | 1000 | 1020.34832059712 | 159525 | 162771.065843256 | 159525 | 162771.065843256 | INVESTIGATION, ENVIRONMENTAL RESPONSE, ENVIRONMENTAL INVESTIGATION |  | 381431 | 179422.044525201 | 389164.826905989 | [8 empty] | 200 |  | 400 | 192.619(A)(4) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 12153 | YES | [7 empty] | YES |  | YES | YES |  |  |  | TYPE A GATHERING | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [103 empty] | OTHER OUTSIDE FORCE DAMAGE | [9 empty] | THE CAUSE WAS CYCLIC STRESS RESULTING FROM INSTALLATION OF CONCRETE ROAD DRAINAGE STRUCTURES OVER THE PIPELINE. PLEASE SEE ADDITIONAL NARRATIVE IN SECTION H. | [251 empty] | MIKE PAVLAK | SR. COMPLIANCE SPECIALIST | mpavlak@dcpmidstream.com | 970-378-8241 |  |  |  |  | JOHN PONTIOUS | MANAGER PIPELINE COMPLIANCE | 405-605-3859 | jdpontious@dcpmidstream.com | DCP GAS CONTROL RECEIVED A CALL FROM A PROPERTY OWNER ON APRIL 2, 2019 AT APPROXIMATELY 10:00 AM MST REPORTING A SUSPECTED GAS RELEASE. DCP PERSONNEL ARRIVED ON SITE AT APPROXIMATELY 10:15 AM MST AND CONFIRMED A GAS RELEASE AND ISOLATED THE LINE. DCP PERSONNEL BLEW DOWN REMAINING PRESSURE IN THE LINE. INITIAL INVESTIGATION INDICATED A CRACK IN THE PIPE AT APPROXIMATELY THE 6-O'CLOCK POSITION IMMEDIATELY ADJACENT TO A GIRTH WELD TO BE THE SOURCE OF THE RELEASE. BASED ON INVESTIGATION AND METALLURGICAL ANALYSIS, DCP HAS DETERMINED THAT THE BZ-7-1-2-EXT CLASS 2 GAS GATHERING PIPELINE FAILED DUE TO CYCLIC FATIGUE CAUSED BY EXTERNAL LOADING. THE BZ-7-1-2-EXT PIPELINE RUNS PARALLEL TO A COUNTY ROAD AND UNDERNEATH AN INTERSECTION WITH A SECOND COUNTY ROAD. AS PART OF A COUNTY ROAD EXPANSION PROJECT IN AUGUST 2015, A HEAVY CONCRETE PRE-FABRICATED DRAINAGE CULVERT AND SUPPORT BRACE WERE INSTALLED DIRECTLY OVER AND WITHIN A FEW INCHES OF THE TOP OF THE PIPELINE AT THE INTERSECTION. DCP HAD LOCATED AND MARKED THE PIPELINE IN JULY 2015 IN RESPONSE TO AN 811 NOTIFICATION FOR THE ROAD PROJECT, BUT DCP WAS NOT PROVIDED WITH THE COUNTY'S CONSTRUCTION PLANS PRIOR TO THE WORK BEING DONE, AND WAS NOT AWARE NOR MADE AWARE OF THE CONFLICT BETWEEN THE CULVERT INSTALLATION AND THE PIPELINE. FREQUENT HEAVY VEHICLE TRAFFIC AT THE INTERSECTION SUBSEQUENTLY APPLIED REGULAR CYCLIC LOADING TO THE CONCRETE CULVERT AND CONCRETE SUPPORT BRACE UNDER THE ROADWAY, WHICH CYCLIC LOADING CAUSED A BENDING FRACTURE AND THEN FINAL DUCTILE OVERLOAD TEAR OF THE GATHERING PIPELINE IMMEDIATELY BELOW, RESULTING IN THE FAILURE OF THE BZ-7-1-2-EXT PIPELINE ON OR IMMEDIATELY BEFORE APRIL 2, 2019. THE AFFECTED PIPELINE SEGMENT HAS BEEN PURGED OF ALL HYDROCARBONS, PHYSICALLY DISCONNECTED FROM ALL SOURCES OF GAS, AND CAPPED. DCP HAS FURTHER RESPONDED TO THE FAILURE BY CONDUCTING AN EXTENSIVE SOIL AND GROUNDWATER INVESTIGATION ON THE SURROUNDING PROPERTIES, AND IS PURSUING REMEDIATION OPTIONS WITH THE PROPERTY OWNERS UNDER THE OVERSIGHT OF THE COLORADO OIL AND GAS CONSERVATION COMMISSION.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20190050 | 32432 | 2019-04-23 21:42 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2019-03-24 10:30 | 2019 |  |  | 28.4313 | -91.0844 | 1240916 | 2019-03-24 11:44 |  | NATURAL GAS |  | 336 | 13500 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-03-24 11:44 | 2019-03-26 09:35 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-03-24 10:30 | 2019-03-25 11:15 | OFFSHORE | [28 empty] | 150 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SHIP SHOAL | 242 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 20 |  | 0.5 | 52000 | AP5L | SEAMLESS |  | UNITED SATES STEEL CORPORATION | OTHER | CONCRETE | [27 empty] | 1972 | 1972 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 1 |  | NO | NO | NO |  | 0 | 0 | 34641 | 35345.8861738049 | 862 | 862 | 36000 | 36732.5395414964 | 281000 | 286717.878087791 | 0 | 0 | CLAMP |  | 352503 | 165590.645484347 | 359658.303803092 | [8 empty] | 660 |  | 1440 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | AUTOMATIC | 197322 | NO | [5 empty] | YES | UPSTREAM END OF PIPELINE IS SUB-SEA WITH NO PIGGING FACILITIES | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | YES | YES | YES | NO | NO | OTHER | PRODUCER SAW BUBBLES |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | STEPHANIE ROSS | PIPEINE SAFETY ENGINEER | stephanie.ross@williams.com | 713-215-4163 |  |  |  |  | CINT RATKE | MANAGER PIPELINE SAFETY | 918-573-6724 | clint.ratke@williams.com | WILLIAMS OPERATIONS RECEIVED A CALL ABOUT A SHEEN AND BUBBLES ONE MILE FROM THE SHIP SHOAL 229 PLATFORM. BOTH WILLIAMS AND ANCHOR SHUT-IN PRODUCTION AT SHIP SHOAL 229 & 243. WILLIAMS OPERATIONS SUPERVISOR AND TECHNICIAN FLEW OFFSHORE AND PLOTTED THE COORDINATES OF THE SHEEN TO BE LESS THAN 100 FT FROM OUR LINE. O'BRIENS WAS NOTIFIED AND PRODUCERS WERE SHUT IN ON 3/24/3019. WILLIAMS CONTACTED CHET MORRISON DIVERS TO REQUEST THEIR SERVICE FOR THE LEAK INVESTIGATION AND PETROQUIP TO INQUIRE ABOUT A 20" REPAIR CLAMP. DIVERS CONFIRMED THE LEAK ON 3/25/19 COMING FROM THE WILLIAMS 20" PIPELINE SEGMENT #1636 AND WAS FOUND AT THE 4 O CLOCK POSITION. ADDITIONAL NOTIFICATIONS OF THE CONFIRMED LEAK WERE MADE BY WITT O' BRIEN'S. WORK BEGAN TO REMOVE CONCRETE AND CLEARING AREA FOR REPAIR WORK. ON 3/26/2019, DIVERS REPORTED ALL CONCRETE REMOVED AND COMPLETED THE REPAIR CLAMP INSTALLATION ON 3/27/2019. LINE PRESSURE WAS RETURNED ON 3/28/19 AND NO LEAKS WERE DISCOVERED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190051 | 32191 | 2019-04-25 10:21 | SUPPLEMENTAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2019-03-27 12:03 | 2019 |  |  | 27.4681 | -98.0503 | 1241224 | 2019-03-27 15:32 |  | NATURAL GAS |  | 8490 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-03-27 12:03 | 2019-03-29 01:31 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-03-27 12:03 | 2019-03-27 12:03 | ONSHORE | TX | 78363 | KINGSVILLE | KLEBERG | MILEPOST | 0.02 | LOBO 30" RESIDUE | #20150125 KR04 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2016 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE MALFUNCTION | CLASS 1 LOCATION | NO |  | 687 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 15000 | 15000 | 5000 | 5101.74160298561 | 0 | 0 | 0 | 0 |  |  | 20000 | 17893.0151169348 | 20101.7416029856 | [8 empty] | 847 |  | 915 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | MANUAL | 144500 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INVESTIGATION IDENTIFIED NO CONTROLLER ISSUES. CONTROLLER ACTIONS WERE CONSISTENT WITH COMPANY PROTOCOL. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | RELIEF VALVE RELEASED PREMATURELY . SYSTEM DID NOT EXCEED MAOP | [161 empty] | TIMOTHY BUNAG | ENGINEER | timothy.bunag@energytransfer.com | 832-294-5324 |  |  |  |  | CHRIS KRESTA | MANAGER- REGULATORY COMPLIANCE | 713-989-7077 | christopher.kresta@energytransfer.com | ON MARCH 27, 2019 AT APPROXIMATELY 12:03 PM, ENERGY TRANSFER HAD A RELIEF VALVE MALFUNCTION ON THE LOBO 30" RESIDUE PIPELINE. THIS PIPELINE SYSTEM IS A CLASS 1 TRANSMISSION LINE AND IS LOCATED ON THE KING RANCH IN KLEBERG COUNTY IN KINGSVILLE, TX. THE EVENT WAS REPORTABLE DUE TO THE UNINTENTIONAL RELEASE OF GAS AMOUNTED AT 8.49 MMCF. THE RELIEF VALVE MALFUNCTIONED AND RELEASED PREMATURELY. THE PRESSURE ON THIS SYSTEM DID NOT EXCEED MAOP. THE PIPELINE WAS SHUT IN FOR RELIEF VALVE REPAIR. THE RELIEF VALVE WAS REBUILT AND REPLACED AND THE LINE WAS RETURNED TO SERVICE AT 1:31 AM ON MARCH 29, 2019. THIS PIPELINE IS UNDER THE JURISDICTION OF THE TX RRC AS INTRASTATE (SYSTEM ID #730067). THIS LEAK WAS TELEPHONICALLY REPORTED TO THE TX RRC ON MARCH 27, 2019. A 48 HR. NRC UPDATE WAS MADE ON MARCH 29, 2019 AT 08:51 AM. INCIDENT REPORT #1241355 5/24/19 TO PREVENT REOCCURRENCE OF THIS ISSUE, ENERGY TRANSFER WILL CONTINUE TO ENSURE OUR RELIEF VALVES ARE BEING TESTED AND INSPECTED ANNUALLY BY OUR QUALIFIED INDIVIDUALS IN ACCORDANCE WITH OUR SOP.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190052 | 34171 | 2019-04-26 10:49 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2019-03-25 14:35 | 2019 | EASTERN | NO | 37.5181 | -77.5396 | 1241015 | 2019-03-25 14:35 | 1241186 | NATURAL GAS |  | 33.49 | 492.74 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-03-30 12:53 | 2019-04-10 16:20 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-03-23 13:57 | VALVE CLOSURE |  | 2019-03-23 13:57 | 0 | 2019-03-22 16:30 | 2019-03-22 17:30 | ONSHORE | VA | 23225 | RICHMOND | RICHMOND | SURVEY STATION NO. | 3876+89 | VM-107 | VS-12017 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | ROAD CROSSING |  | NO | YES |  |  |  |  | YES | CASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 18 | NO | 0.25 | 46000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | YOUNGSTOWN | COAL TAR |  | UNKNOWN | [26 empty] | 1951 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | NO |  | 314 |  | NO | NO |  |  | 0 | 0 | 1306 | 1332.57490669984 | 89 | 89 | 828825 | 845690.196818909 | 0 | 0 | 0 | 0 |  | 2.65 | 830220 | 388898.07281144 | 847111.771725609 | 0 | 0 | 0 | 0 | NO |  |  |  | 380 | 105000 | 639 | 192.619(A)(1) |  | 1988-08-24 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 11540 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATIONAL PERSONNEL DISCOVERED LEAK DURING ROUTINE LEAKAGE SURVEY. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | OTHER | LIGHTNING OR AC FAULT DAMAGE | [5 empty] | YES | LIGHTNING OR AC FAULT DAMAGE |  |  | YES | YES | YES | KNOWN HVAC CORRIDOR | YES | YES | 1952 | NO | YES | YES | YES | YES | 2006 ' AC MODELING PRIOR TO THE INSTALLATION OF THE AC MITIGATION THAT WAS INSTALLED IN 2007. | 2019 | 2010 | 2006 |  | YES | [190 empty] | YES | YES |  |  | YES |  |  |  | 2014 | FREE SWIMMING | METAL LOSS |  | STANDARD RESOLUTION |  | 2007 | FREE SWIMMING | METAL LOSS |  | STANDARD RESOLUTION | [21 empty] | 2014 | FREE SWIMMING | STANDARD RESOLUTION |  | INSIDE ILI CUPS | 2007 | FREE SWIMMING | STANDARD RESOLUTION |  | NO CUPS | [14 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | MARK NEWMAN | US REGULATORY COMPLIANCE SPECIALIST | mark_newman@transcanada.com | 304-722-8475 | 304-722-8420 |  |  |  | GEORGE HAMATY | MANGER TC EAST | 304-357-3728 | george_hamaty@transcanada.com | ON MARCH 22, 2019 AT 07:38 AM WHILE CONDUCTING A LEAK SURVEY AT A CASING VENT A POSITIVE INDICATION OF THE PRESENCE OF NATURAL GAS WAS DISCOVERED AND REPORTED TO THE MONITORING CENTER. THE LEAK WAS DISCOVERED AT A VENT FROM A ROAD CASING AND A SAMPLE SENT TO DETERMINE THE GAS SOURCE. ON MARCH 25, 2019 AFTER THE DETERMINATION THAT THE GAS SOURCE WAS PIPELINE AND THE ESTIMATED COSTS TO REPAIR THE LEAK WOULD EXCEED $50,000 AT REPORT WAS FILED WITH THE NRC. THIS INCIDENT WAS NOT REPORTED DUE TO THE ESTIMATED AMOUNT OF GAS RELEASED EXCEEDING 3,000 MCF, BUT AN UNINTENDED RELEASE OF GAS WITH COSTS FOR REPAIRS EXCEEDING $50,000. THE AREA WAS ISOLATED, THE TRANSMISSION PIPELINE PRESSURE WAS REDUCED TO 185 PSIG (FROM 380 PSIG). CONSTRUCTION CREWS PULLED THE EXISTING PIPELINE SECTION FROM THE CURRENT ROAD CROSSING (CASED) AND REPLACE WITH NEW PRETESTED PIPE. WORK WAS COMPLETED ON 4/8/2019 AND LINE FULLY RESTORED TO SERVICE ON 4/10/2019. DNV CONCLUSION THAT IT WAS LIKELY A NEARBY LIGHTNING STRIKE THAT CAUSED THE LEAK. THE END SEAL EXHIBITED SIGNS THAT ITS CONFIGURATION AND COMPOSITION MAY HAVE FACILITATED THE ARCING BETWEEN THE PIPELINE AND CASING. CP ANNUAL SURVEY WAS CONDUCTED POST INCIDENT TESTING AND DURING THE PIPE INSPECTION. IF UPGRADE TO THE AC MITIGATION OCCURS, TC ENERGY MAY BE ABLE TO PROVIDE SUPPORTING DATA / MODELING TO BETTER DEFINE THE EXACT CAUSE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190053 | 32856 | 2019-05-02 09:21 | SUPPLEMENTAL FINAL | 31023 | CITGO REFINING & CHEMICAL CO. L.P. | 1293 ELDRIDGE PARKWAY | HOUSTON | TX | 77077 | 2018-11-12 03:00 | 2018 |  |  | 27.805 | -97.4784 | 1242400 | 2019-04-10 16:23 |  | HYDROGEN GAS |  | 1700 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-11-13 06:48 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-11-13 00:55 | 2018-11-13 00:55 | ONSHORE | TX | 78407 | CORPUS CHRISTI | NUECES | MILEPOST | VS-C | N02 HYDROGEN PIPELINE | VS-C TO VS-E | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 216 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10 |  | 0.25 | 42000 | API 5L X42 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | EPOXY | [28 empty] | 1983 | 1983 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | YES | METHOD1 | 93 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 4000 | 3602.83687943262 | 1600000 | 1665711.69537625 | 150000 | 156160.471441523 | 350000 | 364374.433363554 | UT ILI SMART PIGGING COSTS |  | 2104000 | 1007280.10219282 | 2189849.43706076 | [8 empty] | 260 |  | 390 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 17233 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | NOTIFICATION FROM OTHER THIRD PARTY OPERATOR PERSONNEL |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK OCCURRED WITHIN NORMAL OPERATING CONDITIONS. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | ILI EXAMINATION IDENTIFIED INTERNAL CORROSION AS THE CAUSE OF FAILURE |  |  |  |  | YES | SATURATED LIQUID HYDROCARBON DROP-OUT |  |  | YES | UT ILI SMART PIGGING RESULTS | YES |  | YES |  |  |  | NO | NO | NO | YES | [168 empty] | YES | YES |  | YES |  |  |  |  | 2012 | [19 empty] | 2018 | [35 empty] | YES | 2016 | 663 | NO | [13 empty] | NO | [63 empty] | DAVID R. GARCIA | PROCESS SAFETY MANAGEMENT ADVISOR | dgarci2@citgo.com | 361-844-5479 |  |  |  |  | DAVID R. GARCIA | PROCESS SAFETY MANAGEMENT ADVISOR | 361-844-5479 | dgarci2@citgo.com | AT 3:00 AM ON NOVEMBER 12, 2018, LYONDELL PERSONNEL REPORTED A POTENTIAL PIPELINE LEAK JUST SOUTH OF LYONDELL VALVE STATION CLOSE TO CITGO VALVE STATION C (LATITUDE:27.80514; LONGITUDE: 097.47093). THE POTENTIAL LEAK WAS DISCOVERED DUE TO BUBBLING WATER IN THE DITCH. NO VISIBLE HYDROCARBON SHEEN WAS NOTED, INDICATING A PROBABLE NON-HYDROCARBON GAS LEAK. THE MORNING OF NOVEMBER 12TH, LYONDELL TESTED THEIR AREA GAS PIPELINES AND DETERMINED THAT LYONDELL WAS NOT THE SOURCE OF THE LEAK. LATER THAT DAY, CITGO TESTED THE N11 (PURCHASED H2) PIPELINE, NB7 (AIR LIQUIDE) PIPELINE, AND FINALLY THE N02 (#5 PLAT H2) PIPELINE. THE N02 PIPELINE WAS DETERMINED TO BE THE SOURCE OF THE LEAK. WHEN THE N02 LINE WAS DE-PRESSURED, THE BUBBLING IN THE DITCH SUBSIDED. THE SCADA SYSTEM WAS FUNCTIONAL AND OPERATING UNDER NORMAL CONDITIONS AT THE TIME OF THE INCIDENT. THE PIPELINE PRESSURE DROP DUE TO THE FAILURE WAS SO SMALL THAT IT DID NOT INDICATE ON THE CONTROL ROOM SCADA SCREEN AT THE PRESSURE POINT ADJACENT TO THE LEAK AREA. THE TEXAS RAILROAD COMMISSION WAS CALLED AND NOTIFIED OF THE LEAK AT 12:55 AM ON NOVEMBER 13, 2018. THE N02 LINE WAS DE-PRESSURED TO THE POINT WHERE THE BUBBLING STOPPED (NOON ON NOVEMBER 13TH) AND A PLAN WAS DEVELOPED TO ISOLATE THE LINE WHILE MINIMIZING EMISSIONS FROM THE WEST PLANT DUE TO H2 CONTAINMENT FROM THE #5 REFORMER. AN ADDITIONAL ISOLATION VALVE ON THE N02 LINE AT CITGO VALVE STATION C WAS INSTALLED IN ORDER TO ISOLATE THE N02 LINE FROM THE N11 LINE. HYDRO-EXCAVATION WAS ATTEMPTED TO UNCOVER THE LEAK LOCATION BUT, DUE TO SOIL INSTABILITY, THE DEPTH OF THE EXCAVATION (OVER 25 FOOT), AND ITS PROXIMITY TO I-37, THE DECISION WAS MADE TO ABANDON THIS ACTIVITY AND BACKFILL THE EXCAVATION. QUEST INTEGRITY WAS CONTRACTED TO SMART PIG THE N02 LINE. RESULTS FROM THE UT ILI SMART PIG IDENTIFIED 5 AREAS OF CONCERN. ALL LOCATIONS WERE AT THE BOTTOM OF THE PIPE AND AT LOW LYING AREAS. NO PROPERTY DAMAGE OCCURRED DUE TO THE INCIDENT, EITHER CITGO OR PROPERTY OF OTHERS. THE LEAK RESULTED IN 1.7 MMSCF OF GAS RELEASED TO ATMOSPHERE AN NRC CALL (REPORT #1242400) WAS MADE ON 4/10/19 AT 16:23 AN NCR 48-HOUR UPDATE (RENEWED REPORT #1242587) WAS MADE ON 4/12/19 AT 13:38 THE RE-ROUTE OF A PORTION OF THE N02 LINE IS NOW ALMOST COMPLETE. MAINTENANCE COSTS INCURRED DUE TO THE PARTIAL REPLACEMENT OF THE LINE ARE YET TO BE FINALIZED BUT COST ESTIMATES HAVE BEEN REPORTED HEREIN AS REQUESTED. ESTIMATED COMPLETION OF THE N02 PIPELINE REPAIR IS EXPECTED BY THE END OF NOVEMBER 2019; THE LINE CONTINUES TO BE ISOLATED AND DEPRESSURED AT THIS TIME.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190054 | 32063 | 2019-05-03 08:57 | ORIGINAL FINAL | 4070 | EAST TENNESSEE NATURAL GAS, LLC (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2019-04-04 21:17 | 2019 |  |  | 35.9798 | -84.2287 | 1241906 | 2019-04-04 22:31 |  | NATURAL GAS |  | 3138 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE NATURAL GAS RELEASE WAS ISOLATED TO THE RELEIF VALVE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-04-04 21:58 | 2019-04-04 21:58 | ONSHORE | TN | 37830 | OAK RIDGE | ANDERSON | MILEPOST | 9.377 | MR 59021 | WART -TOPS | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ABOVEGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 2016 |  | CARBON STEEL |  | OTHER | [8 empty] | RELEASE OF NATURAL GAS FROM RELIEF VALVE. | CLASS 3 LOCATION | NO |  | 236 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 7720 | 7720 | 1000 | 1020.34832059712 | 0 | 0 | 0 | 0 |  |  | 8720 | 8472.04134359693 | 8740.34832059712 | [8 empty] | 130 |  | 720 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE VOLUME OF LEAK WAS TOO SMALL TO BE IDENTIFIED BY THE CONTROLLER VIA SCADA | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [25 empty] | YES | FILTER ELEMENT IN REGULATOR GAS SUPPLY WAS DISTORTED | [161 empty] | MAYRA SALINAS | SENIOR ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: 48 HR NRC REPORT 1242022 AT APPROXIMATELY 9:17 PM EST ON APRIL 4, 2019, EAST TENNESSEE NATURAL GAS (ETNG) WAS NOTIFIED BY A UTILITY COMPANY EMPLOYEE ABOUT A NATURAL GAS RELEASE AT ETNG'S METER AND REGULATOR STATION (M&R 59021) IN ANDERSON COUNTY, TN. ETNG PERSONNEL ARRIVED AT M&R 59021 AT APPROXIMATELY 9:58 PM EST AND DISCOVERED NATURAL GAS RELEASE FROM A RELIEF VALVE. ETNG PERSONNEL SUBSEQUENTLY ISOLATED THE RELIEF VALVE. THE APPARENT CAUSE WAS A COLLAPSED SUPPLY GAS FILTER ON THE UPSTREAM REGULATOR THAT STOPPED THE SUPPLY GAS TO THE BOOT AND RESULTING IN THE REGULATOR TO FAIL OPEN.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190055 | 34303 | 2019-05-03 11:11 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2019-04-03 15:48 | 2019 | PACIFIC | NO | 38.4958 | -121.4295 | 1241929 | 2019-04-05 08:50 |  | NATURAL GAS |  | 25.2 | 23 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | POST-MAINTENANCE/REPAIR | [5 empty] | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-04-05 00:20 | VALVE CLOSURE |  | 2019-04-05 00:20 | 0 | 2019-04-03 15:48 | 2019-04-03 15:48 | ONSHORE | CA | 95823 | SACRAMENTO | SACRAMENTO | MILEPOST | 2.45 | DFM 0609-02 | 35151 (ROUTE ID) | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 48 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 6 |  | 0.188 | 30000 | API 5L X-42 | LONGITUDINAL ERW - LOW FREQUENCY |  | UNKNOWN | ASPHALT |  | YES | [7 empty] | PIPE GIRTH WELD |  | NO | [16 empty] | 1962 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | CONSTRUCTION RELATED DEFECT | [5 empty] | CLASS 3 LOCATION | NO |  | 56 |  | NO | NO |  |  | 0 | 0 | 69 | 70.4040341212013 | 76 | 76 | 201636 | 205738.953971921 | 0 | 0 | 0 | 0 |  | 3 | 201781 | 94550.7186327917 | 205885.358006042 | 0 | 0 | 0 | 0 | NO |  |  |  | 130 | 130 | 150 | 192.619(A)(2) |  | 1962-12-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 300 | NO | [5 empty] | YES | PIPELINE IS NOT CURRENTLY CONFIGURED TO ACCOMMODATE TRADITIONAL ILI TOOLS DUE TO THE LOW PRESSURE OF THE PIPELINE (150 MAOP). IT IS CATEGORIZED FOR A FUTURE NON-TRADITIONAL INSPECTION AND WILL BE EVALUATED AT THAT TIME FOR ANY TOOL PASSAGE CONSTRAINTS. | YES |  | YES |  |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO SYSTEM IMPACT OR ALARMS DETECTED ON SCADA | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) |  | YES | [13 empty] | YES | MATERIAL/WELD FAILURE | [13 empty] | YES | MATERIAL/WELD FAILURE | UNKNOWN | [54 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | ENZA BARBATO | REGULATORY COMPLIANCE | e1bo@pge.com | [5 empty] | SUSIE RICHMOND | MANAGER - REGULATORY COMPLIANCE | 925-328-5776 | susie.richmond@pge.com | ON APRIL 3, 2019 AT 1548 HOURS, PG&E IDENTIFIED A GRADE 1 LEAK ALONG DFM 0609-02 AT 6434 FLORIN RD, SACRAMENTO. PG&E CREWS WERE ONSITE AND FINISHED MAKING REPAIRS TO THE LEAKS DISCOVERED ON A SAVE-A-VALVE AND PCF ON APRIL 4, 2019 AT 0414 HOURS. A LEAK SURVEY WAS CONDUCTED FOLLOWING THE REPAIRS AND FOUND AN ADDITIONAL LEAK ON THE WELD OF DFM 0609-02. ON APRIL 6, 2019, PG&E CUT OUT THE FOLLOWING: LEAKING MITER ELBOW, PCF, SAVE-A-VALVE, 6IN ELBOW AND INSTALLED A NEW 6IN PCF AND MAIN. THE APPARENT CAUSE WAS DETERMINED AS METALLURGICAL FAILURE OF THE MITER WELD, LIKELY DUE A CONSTRUCTION-RELATED DEFECT. THERE ARE NO KNOWN INJURIES OR FATALITIES. CUSTOMER IMPACT IS UNKNOWN. NO POLICE OR FIRE DEPARTMENT REPORTED. ON APRIL 5, 2019, THIS INCIDENT WAS REPORTED TO DOT (1241929) AND CPUC (190405-9141) DUE TO MEDIA PRESENCE (FOX NEWS) AND THE EXPECTED REPAIR COSTS BEING ESTIMATED AT OVER $50K.
2021-02-26 10:37 | YES | NO | UNGS (Underground Natural Gas Storage) | 20190056 | 34113 | 2019-05-06 16:15 | SUPPLEMENTAL FINAL | 17620 | ROCKY MOUNTAIN NATURAL GAS LLC | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2019-04-07 09:00 | 2019 | MOUNTAIN | NO | 39.3092 | -107.3962 | 1242079 | 2019-04-07 09:31 | 1242266 | NATURAL GAS |  | 800 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-04-06 22:34 | 2019-10-21 08:00 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2019-04-07 00:30 | YES | 2019-04-06 22:30 | ALLOWED TO BURN OUT |  | 800 | YES | [6 empty] | 0 | 2019-04-06 22:34 | 2019-04-07 01:00 | ONSHORE | CO | 81623 | Not Within a Municipality | PITKIN | MILEPOST | WC71 PROCESS | GAS STORAGE WELL #71- PROCESSING BUILDING | WC71 PROCESSING BUILDING | YES | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTRASTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | DEHYDRATOR/DRIER/TREATER/SCRUBBER | [38 empty] | 2012 | 2012 | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | A 1-INCH THREADED NOZZLE RUPTURED. EXTRA HEAVY WALL THICKNESS 0.179. APPROXIMATE ID OF RUPTURED 0.957. | 1 | 1 |  | CLASS 1 LOCATION | NO |  | 179 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 842480 | 859623.053136662 | 2500 | 2550.8708014928 | 0 | 0 |  | 0 | 844980 | 395760.58112671 | 862173.923938155 | 0 | 0 | 0 | 0 | NO |  |  |  | 930 | 0 | 1318 | 192.619(A)(1) |  | 2013-10-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | THREADED FITTING |  |  |  |  | YES |  | YES |  |  | YES | [6 empty] | YES |  |  | YES | GLYCOL CONTRIBUTED TO INTERNAL CORROSION | [161 empty] | JASON PRICE | PROGRAM MANAGER SIMP | jason.price@blackhillscorp.com | 3073157860 |  | THOM WARNES | thomas.warnes@blackhillscorp.com | 9709897053 | BILL STEPHENS | MANAGER CODES AND STANDARDS | 3039816474 | bill.stephens@blackhillscorp.com | 4/6/19 AT 10:30PM MT- DENVER GAS CONTOL RECEIVED A CHAIN OF ALARMS RESULTING IN AN EMEGENCY SHUT DOWN AND ISOLATION OF THE WOLF CREEK WELL #71. ON-CALL OPERATIONS PERSONNEL WERE NOTIFIED AND DISPATCHED TO THE SITE. GAS CONTROL UTILIZED AUTOMATIC ISOLATION VALVES AND SHUT IN THE ENTIRE STORAGE FIELD. COMPANY PERSONNEL SHUT MANUAL ISOLATION VALVES ALONG 3-INCH PIPELINE WHILE TRAVELING TO THE WELL LOCATION. UPON ARRIVAL (1:00 AM MT ON 4-7-19) TO WELL LOCATION COMPANY PERSONNEL OBSERVED A SMALL FIRE BURING FROM 1-INCH GLYCOL PIPING OFF OF THE GAS/GLYCOL HEAT EXCHANGER ON THE DEHYDRATION UNIT HOUSE WITHIN THE PROCESS BUILDING. A SMALL FIRE WAS OBSERVED FROM RESIDUAL GAS BURNING OFF FROM PROCESS PLUMBING. PERSONNEL ALSO WITNESSED EVIDENCE OF SMALL SECONDARY FIRES INSIDE THE PROCESS BUILDING THAT WERE STILL SMOLDERING. ALL TRIETHYLENE GLYCOL WAS CONTAINED WITHIN THE SECONDARY CONTAINMENT OF THE PROCESS BUILDING OR WAS CONSUMED DURING THE FIRE. PERSONNEL LEFT THE WELL SITE AND EVALUATED ALL OTHER WELL LOCATIONS WITHIN THE STORAGE FIELD. NO ISSUES WERE OBSERVED AT ANY OTHER LOCATIONS. PERSONNEL RETURNED BACK TO WELL #71 LOCATION TO EVALUATE OVERALL SITE CONDITIONS. THEY VERIFIED SLAM VALVES, VENT VALVE AND SUB-SURFACE SAFETY VALVE WERE IN THE CORRECT EMERGENCY SHUT POSITION AND ISOLATED MANUAL BLOCK VALVES ON THE FLOW LINE AND PIPELINE. PERSONNEL EVALUATED WELLHEAD HOUSED IN WELLHEAD BUILDING; NO ISSUES WERE OBSERVED, SHUT MASTER AND WING VALVES ON TREE ALL OK. COMPANY PERSONNEL LEFT SITE TO COMMUNICATE FINDINGS WITH MANAGEMENT. MANGEMENT WAS NOTIFIED AT 6:30 AM MT (4-7-19) OF SITE FINDINGS. NO INJURIES OCCURED DURING INCIDENT. NO BREACH OF SECONDARY CONTAINMENT OF ANY STORED OR RELEASED LIGUIDS (TRIETHYLENE GLYCOL). FOLLOW-UP 48 HOUR NRC #1242266. THROUGH INTERNAL AND EXTERNAL INVESTIGATION THE ROOT CAUSE WAS CAUSED BY A FAILED 1-INCH NIPPLE ON GLYCOL GAS HEAT EXCHANGER ON THE DEHYDRATION UNIT. IGNITION SOURCE WAS DETERMINED TO BE UNKNOWN AT THE TIME OF THE INCIDENT. IT IS KNOWN THAT THE PROCESS BUILDING CONTAINED AN ATOMIZED GLYCOL AND GAS MIXTURE RESULTING IN A EXPLOSION AND FIRE. LESSONS LEARNED: OPERATOR IS USING INTERNAL AND EXTERNAL ENGINEERING TO REVIEW THE USE OF HIGH PRESSURE THREADED CONNECTIONS ON AUXILIARY LINES ON DEHYDRATION UNITS.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190057 | 32365 | 2019-05-14 13:03 | SUPPLEMENTAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2019-04-23 08:10 | 2019 |  |  | 32.9787 | -91.8147 | 1243855 | 2019-04-26 14:40 |  | NATURAL GAS |  | 0.1 | 5006 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-04-23 16:29 | 2019-04-29 11:47 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-04-23 08:10 | 2019-04-23 08:10 | ONSHORE | LA | 71220 | BASTROP | MOREHOUSE | MILEPOST | 58+1674 | MAIN LINE SYSTEM | MLS 26-2 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 42 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 26 |  | 0.281 | 52000 | API 5L | DSAW |  | NATIONAL TUBE | COAL TAR | [28 empty] | 1952 | 1952 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 560 |  | NO | NO | NO |  | 0 | 0 | 13566 | 13842.0453172205 | 0 | 0 | 61898 | 63157.5203483206 | 0 | 0 | 0 | 0 |  |  | 75464 | 35344.8324151413 | 76999.5656655411 | [8 empty] | 660 |  | 840 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 43178 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | MINOR LEAK NOT DETECTABLE BY SCADA. INCIDENT REPORTABLE ONLY BECAUSE REPAIR COSTS MAY MEET THE REPORTING THRESHOLD OF $50,000. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | YES | YES | [13 empty] | YES | PINHOLE LEAK IN LONGITUDINAL SEAM | [7 empty] | YES | [62 empty] | YES | YES | [6 empty] | 2013 | [55 empty] | YES | 1963 | 1161 | NO | [13 empty] | NO | [63 empty] | SHANNON MATTINGLY | OQ PA AND EVENT PROGRAM LEADER | shannon.mattingly@bwpmlp.com | 2706886357 |  |  |  |  | DARRAL WARD | MANAGER PIPELINE SAFETY | 2706886356 | darral.ward@bwpmlp.com | ON APRIL 21, 2019 AT APPROXIMATELY 4:00 PM, TEXAS GAS TRANSMISSION RECEIVED NOTIFICATION FROM AN INDIVIDUAL WHO WAS RIDING A FOUR WHEELER NEAR THE RIGHT-OF-WAY THAT HE OBSERVED SMALL BUBBLES IN A MUD HOLE. ON APRIL 22, METHANE WAS DETECTED IN THE AREA USING MULTIPLE LEAK DETECTORS BUT BECAUSE OF RECENT FLOODING, IT COULD NOT BE ASSUMED THAT THIS REPRESENTED A NATURAL GAS LEAK. ON APRIL 23 AT APPROXIMATELY 8:10, OPERATIONS PERSONNEL CONFIRMED A POSSIBLE LEAK WITH LEAK DETECTOR. OPERATIONS NOTIFIED PIPELINE SERVICES , THE LINE WAS ISOLATED AND PRESSURE WAS REDUCED FROM 660 PSIG TO 300 PSIG. ON APRIL 23, 2019 AT APPROXIMATELY 11:00 AM, PIPELINE SERVICES BEGAN AN INVESTIGATIVE DIG WHICH CONFIRMED A PINHOLE LEAK IN AN EXISTING WELD ON THE MLS 26-2. THE LINE WAS BLOWN DOWN TO 0 PSIG AT 4:29 PM ON APRIL 23. AFTER EVALUATION, IT WAS DETERMINED THAT ESTIMATED REPAIR COSTS MAY EXCEED $50,000, THUS, MEETING THE PHMSA INCIDENT DEFINITION AND THE NRC WAS CONTACTED. A SECTION OF PIPE WAS CUT OUT, THE LINE WAS PURGED AND PACKED AND PLACED BACK INTO SERVICE ON APRIL 29, 2019 AT 11:00. 6-28-19 UPDATE TO SUBMIT FINAL REPORT. UPDATED PART C TO INDICATE INCIDENT OCCURRED ON PIPE INSTEAD OF WELD AND SUB-CAUSE BASIS TO INCLUDE METALLURGICAL ANALYSIS AS REQUESTED BY PHMSA. ACTUAL COSTS ARE NOW REPRESENTED AND PIR WAS CONFIRMED AS REQUESTED BY PHMSA.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190058 | 32469 | 2019-05-16 18:53 | SUPPLEMENTAL FINAL | 4900 | KINDER MORGAN TEJAS PIPELINE | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2019-04-19 05:31 | 2019 |  |  | 27.7595 | -97.7982 | 1243158 | 2019-04-19 06:09 |  | NATURAL GAS |  | 8802 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-04-19 05:18 | 2019-04-19 06:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-04-19 04:40 | 2019-04-19 05:23 | ONSHORE | TX | 78339 | BANQUETE | NUECES | MILEPOST | BANQUETE C/S | BANQUETE COMPRESSOR STATION | TRAILSTONE UNIT 5010 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2018 |  | CARBON STEEL |  | LEAK |  |  | OTHER | RELIEF VALVE RELEASE | [5 empty] | CLASS 1 LOCATION | NO |  | 358 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 20114 | 20114 | 9000 | 9183.13488537409 | 250 | 255.08708014928 | 0 | 0 |  |  | 29364 | 25185.4900398202 | 29552.2219655234 | [8 empty] | 846 |  | 1050 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE EVENT WAS DETERMINED INDEPENDENT FROM CONTROLLER ACTION. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [13 empty] | YES | [177 empty] | DANIEL GRANT | PIPELINE ENGINEER | daniel_grant@kindermorgan.com | 7134204409 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR - ENGINEERING | 7133699443 | jaime_hernandez@kindermorgan.com | AT 4:40 AM ON APRIL 19TH, 2019 NATURAL GAS PIPELINE CO. OF AMERICA, LLC (NGPL) RECEIVED A CALL FROM FIRST RESPONDERS IN BANQUETE, TX REPORTING A LOUD NOISE. NGPL NOTIFIED KINDER MORGAN TEJAS PIPELINE, LLC (TEJAS) WHO SHUT DOWN THE BANQUETE COMPRESSOR STATION AT 5:18 AM. A TEJAS OPERATOR ARRIVED ON SITE AT 5:23 AM. AT 5:31 AM IT HAD BEEN DETERMINED THAT THE 4" RELIEF VALVE CONNECTED TO TRAILSTONE UNIT 5010 HAD BEEN RELIEVING PRESSURE CAUSING THE LOUD NOISE. THE UNIT WHICH WAS RUNNING AT THE TIME OF THE EVENT WAS LOCKED OUT AND THE STATION WAS BROUGHT BACK ONLINE AT 6:45 AM. A UNIT DISCHARGE RELIEF VALVE WAS FOUND TO HAVE DRIFTED FROM ITS LAST KNOWN SET PRESSURE, OPENING PREMATURELY AT 846 PSIG RELEASING 8,802 MCF. THE INVESTIGATION FOUND THAT THE RELIEF VALVE'S DESIGNED SET POINT IS 1050 PSIG HOWEVER, THE INVESTIGATION ALSO FOUND THAT THE RELIEF VALVE WAS LAST SET AT 970 PSIG. IT IS BELIEVED THAT THE CAUSE FOR THE RELIEF VALVE DRIFT WAS DUE TO VIBRATION AND PRESSURE PULSATIONS FROM THE UNIT. ADDITIONAL CONTRIBUTING FACTORS TO THE AMOUNT OF UNINTENTIONAL RELEASED GAS WAS THAT THE RELIEF VALVE'S VENT LINE CONNECTING PIPE NIPPLE FOR THE PRESSURE SWITCH WAS FOUND TO HAVE BEEN BROKEN AT THE CONNECTING THREADS TO THE PRESSURE SWITCH. BY VISUAL EXAMINATION THE PIPE NIPPLE WAS DETERMINED NOT TO MEET TEJAS SCHEDULE 160 REQUIREMENTS. POST-INCIDENT IT WAS DISCOVERED THAT THE LADDER LOGIC ASSOCIATED WITH THE PRESSURE SWITCH HAD NOT BEEN ENABLED. HAD THE LADDER LOGIC BEEN ENABLED, WITH THE ACTIVATION OF THE PRESSURE SWITCH, IT WOULD HAVE STOPPED THE UNIT THEREFORE REDUCING THE AMOUNT OF UNINTENTIONAL RELEASED GAS. UPON RESTARTING THE UNIT AFTER THE EVENT, THE TECHNICIAN NOTICED THERE WAS BACKFLOW INTO THE UNIT COMING FROM THE DISCHARGE PIPING DOWNSTREAM OF THE CHECK VALVE. FURTHER INVESTIGATION OF THE CHECK VALVE DETERMINED THAT THE CHECK VALVE'S FLAPPER ON THE DISCHARGE PIPELINE FAILED DURING THIS EVENT. HOWEVER, IT IS NOT BELIEVED THAT THIS FAILURE WAS A CONTRIBUTING FACTOR TO THE AMOUNT OF GAS RELEASED RATHER IT WAS A RESULT OF THE DISCHARGE PULSATING EVENTS ASSOCIATED WITH THE CONTINUED COMPRESSOR OPERATIONS AND THE PRESSURE FLUCTUATIONS ASSOCIATED WITH THE ON/OFF ACTIVATION OF THE DISCHARGE RELIEF VALVE. THE 48-HR NRC INCIDENT REPORT NUMBER IS 1243256.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190059 | 32813 | 2019-05-22 10:06 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2019-04-23 13:04 | 2019 |  |  | 39.6392 | -79.3394 | 1243531 | 2019-04-23 16:23 |  | NATURAL GAS |  | 3136 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-04-23 13:04 | 2019-04-23 14:43 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-04-23 13:04 | 2019-04-23 13:04 | ONSHORE | MD | 21520 | KAESE MILL | GARRETT | MILEPOST | 0 | ACCIDENT COMPRESSOR STATION | ACCI-UNIO | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | ESD SYSTEM | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | EMERGENCY SHUTDOWN OF COMPRESSOR STATION | CLASS 1 LOCATION | NO |  | 987 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 8374 | 8374 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 8374 | 8681.70603674541 | 8374 | [8 empty] | 2368 |  | 3550 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS DETERMINED THE CONTROLLERS ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. THE ESD WAS TRIGGERED BY A FIRE DETECTOR AND THIS EVENT COULD NOT BE ASSOCIATED WITH THE ROLES AND RESPONSIBILITIES OF A CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | ESD WAS TRIGGERED AS A RESULT OF THE FIRE DETECTOR DETECTING A FLAME SIGNATURE NEAR THE SALT BATH HEATER. | YES |  |  |  |  | NORMAL OPERATING CONDITIONS | NO | [150 empty] | MAYRA SALINAS | SENIOR ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: 48 HR NRC REPORT 1243693 AT APPROXIMATELY 1:04 PM EDT ON APRIL 23, 2019, AN EMERGENCY SHUTDOWN (ESD) SYSTEM WAS ACTIVATED AT ACCIDENT COMPRESSOR STATION ON THE TEXAS EASTERN TRANSMISSION (TETLP) SYSTEM IN GARRETT COUNTY, MARYLAND. TETLP COMPLETED THE REPORT TO THE NATIONAL RESPONSE CENTER AT APPROXIMATELY 4:23 EDT ONCE IT WAS DETERMINED THE GAS LOSS VOLUME EXCEEDED 3 MMSCF. THE ESD OCCURRED WHILE RETURNING A SALT BATH HEATER (SBH) BACK TO NORMAL OPERATIONS. THIS PROCESS INVOLVES USING GAS FIRED AUXILIARY BURNERS TO HEAT THE SALT TO A LIQUID STATE AND USING THE MAIN BURNERS TO KEEP THE SALT AT A LIQUID STATE AFTER THE GAS FIRED AUXILIARY BURNER IS DEACTIVATED. THIS PROCESS WAS BEING PERFORMED IN ACCORDANCE WITH THE MANUFACTURER'S RECOMMENDED PROCEDURE. THE ESD WAS TRIGGERED BY THE FIRE DETECTOR NEAR THE GAS FIRED AUXILIARY HEATER THAT DETECTED THE FLAME SIGNATURE. TETLP'S INVESTIGATION DETERMINED THAT BOTH THE AUXILIARY HEATER AND THE FIRE DETECTOR WERE FUNCTIONING AS DESIGNED AT THE TIME OF THE ESD. AS PART OF THE MITIGATIVE PLAN, THE TEMPERATURE OF THE GAS POWERED AUXILIARY BURNER WAS LOWERED DURING STARTUP. SUPPLEMENTAL REPORT 10/14/19: CAUSE HAS BEEN UPDATED TO INCORRECT OPERATION.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190060 | 32814 | 2019-05-22 14:38 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2019-04-27 07:03 | 2019 |  |  | 39.6392 | -79.3394 | 1243893 | 2019-04-27 08:02 |  | NATURAL GAS |  | 3324 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-04-27 07:03 | 2019-04-27 13:38 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-04-27 07:03 | 2019-04-27 07:03 | ONSHORE | MD | 21520 | KAESE MILL | GARRETT | MILEPOST | 0 | ACCIDENT COMPRESSOR STATION | ACCI-UNIO | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | ESD SYSTEM | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | EMERGENCY SHUTDOWN OF COMPRESSOR STATION | CLASS 1 LOCATION | NO |  | 987 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 8876 | 8876 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 8876 | 9202.15223097113 | 8876 | [8 empty] | 2477 |  | 3550 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS DETERMINED THE CONTROLLERS ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. THE ESD WAS TRIGGERED BY A FIRE DETECTOR AND THIS EVENT COULD NOT BE ASSOCIATED WITH THE ROLES AND RESPONSIBILITIES OF A CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | ESD WAS TRIGGERED AS RESULT OF THE FIRE DETECTOR DETECTING A FLAME SIGNATURE NEAR THE SALT BATH HEATER. | YES |  |  |  |  | NORMAL OPERATING CONDITIONS | NO | [150 empty] | MAYRA SALINAS | SENIOR ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: 48 HR NRC REPORT 1244152 AT APPROXIMATELY 7:03 AM EDT ON APRIL 27, 2019, AN EMERGENCY SHUTDOWN (ESD) SYSTEM WAS ACTIVATED AT ACCIDENT COMPRESSOR STATION ON THE TEXAS EASTERN TRANSMISSION (TETLP) SYSTEM IN GARRETT COUNTY, MARYLAND. THE ESD OCCURRED WHILE RETURNING A SALT BATH HEATER (SBH) BACK TO NORMAL OPERATIONS. THIS PROCESS INVOLVES USING GAS FIRED AUXILIARY BURNERS TO HEAT THE SALT TO A LIQUID STATE AND USING THE MAIN BURNERS TO KEEP THE SALT AT A LIQUID STATE AFTER THE GAS FIRED AUXILIARY BURNER IS DEACTIVATED. THIS PROCESS WAS BEING PERFORMED IN ACCORDANCE WITH THE MANUFACTURER'S RECOMMENDED PROCEDURE. THE ESD WAS TRIGGERED BY THE FIRE DETECTOR NEAR THE GAS FIRED AUXILIARY BURNER THAT DETECTED THE FLAME SIGNATURE. TETLP'S INVESTIGATION DETERMINED THAT BOTH THE AUXILIARY BURNER AND THE FIRE DETECTOR WERE FUNCTIONING AS DESIGNED AT THE TIME OF THE ESD. AS PART OF THE MITIGATIVE PLAN, THE TEMPERATURE OF THE GAS POWERED AUXILIARY BURNER WAS LOWERED DURING STARTUP. FOLLOWING THIS ESD AT THE STATION, REVISIONS WERE MADE TO THE MITIGATIVE PLAN THAT NOW REQUIRES THE FIRE DETECTOR TO BE DISABLED WHEN RETURNING THE SBH TO OPERATIONS AND THE STATION MANNED LOCALLY UNTIL THE FIRE DETECTOR IS ACTIVATED. SUPPLEMENTAL REPORT 10/14/19: CAUSE HAS BEEN UPDATED TO INCORRECT OPERATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190061 | 32178 | 2019-05-22 16:12 | ORIGINAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2019-04-22 14:36 | 2019 |  |  | 33.2328 | -97.6756 | 1243544 | 2019-04-23 17:11 |  | NATURAL GAS |  | 62.4 | 73.5 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-04-22 19:50 | 2019-04-24 18:50 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-04-22 14:37 | 2019-04-22 15:08 | ONSHORE | TX | 76234 | DECATUR | WISE | SURVEY STATION NO. | 16972 | W 12-1 | DECATUR TO BRIDGEPORT | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 198 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 4 |  | 0.156 | 42000 | X42 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | EPOXY | [28 empty] | 1991 | 1991 | CARBON STEEL |  | MECHANICAL PUNCTURE | 0.2 | 0.7 | [7 empty] | CLASS 1 LOCATION | NO |  | 54 |  | NO | NO | NO |  | 183000 | 186723.742669273 | 236 | 240.802203660921 | 200 | 200 | 165000 | 168357.472898525 | 0 | 0 | 676 | 689.755464723654 | MEALS |  | 349112 | 163626.147019875 | 356211.773236183 | [8 empty] | 240 |  | 300 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 19008 | NO |  |  | YES | YES |  |  |  | NO | [6 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [7 empty] | CONTRACTOR | AUGER | POLE | YES | 1960726723 | TEXAS811 | CONTRACT LOCATOR | NO | NO | YES | 47 | LOCATING PRACTICES NOT SUFFICIENT |  | FACILITY WAS NOT LOCATED OR MARKED | [264 empty] | RON WHITSON | FIELD SUPERVISOR | ronald.whitson@atmosenergy.com | 940-872-6151 |  |  |  |  | MARLO SUTTON | VICE PRESIDENT TECHNICAL SERVICES | 214-206-2033 | marlo.sutton@atmosenergy.com | ADDITIONAL NRC REPORT NUMBER 1243764 ON APRIL 22, 2019 AT 14:36, A THIRD-PARTY CONTRACTOR HIT ATMOS ENERGY'S LINE W 12-1 WHILE DRILLING TO INSTALL A BILLBOARD POLE, PUNCTURING THE LINE AND CAUSING A LEAK. THE LINE SEGMENT WAS ISOLATED AT 19:50 AND A CONTROLLED GAS RELEASE WAS PERFORMED UNTIL THE PRESSURE WAS ELIMINATED. CNG RESOURCES WERE UTILIZED TO SERVE 5 CUSTOMERS DURING THE SHUTDOWN. ON APRIL 23, 2019 AT 19:02, THE DAMAGED SECTION OF PIPE WAS REMOVED AND REPAIRS COMMENCED. SERVICE WAS RESTORED AT 18:50 ON APRIL 24, 2019. AFTER INVESTIGATION OF THE INCIDENT, IT WAS DETERMINED THAT THE CONTRACT LOCATOR DID NOT APPROPRIATELY MARK THE LINE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190062 | 32965 | 2019-05-24 17:24 | SUPPLEMENTAL FINAL | 32645 | HILCORP ALASKA, LLC | 3800 CENTERPOINT DR. SUITE 1400 | ANCHORAGE | AK | 99503 | 2019-04-27 19:30 | 2019 |  |  | 60.7764 | -151.4333 | 1243956 | 2019-04-27 22:27 |  | NATURAL GAS |  | 1.6 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-04-27 20:00 | 2019-05-27 14:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-04-27 19:30 | 2019-04-27 19:30 | ONSHORE | AK | 99635 | Not Within a Municipality | KENAI PENINSULA BOROUGH | MILEPOST | MILE 4.48 | MIDDLE GROUND SHOALS | MGS A PIPELINE | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | OTHER | SUBMERGED, ON SEAFLOOR |  |  | YES | [6 empty] | YES | UNCASED | COOK INLET | 60 | BELOW WATER, PIPE ON OR ABOVE BOTTOM | [11 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 8 |  | 0.594 | 35000 | API 5L | SEAMLESS |  | UNKNOWN | COAL TAR | [9 empty] | PIPE GIRTH WELD | [18 empty] | 1965 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | CORROSION / WELD DISCONTINUITY | [5 empty] | CLASS 1 LOCATION | NO |  | 123 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 50 | 50 | 1500000 | 1530522.48089568 | 0 | 0 | 0 | 0 |  |  | 1500050 | 702602.04164212 | 1530572.48089568 | [8 empty] | 195 |  | 499 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 37193 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | DIVERS NOTICED THE LEAK DURING SUBSEA INSPECTIONS |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | NO | [11 empty] | YES | YES | [190 empty] | YES |  |  | YES | [24 empty] | 2017 | [35 empty] | YES | 2017 | 750 | NO | [13 empty] | NO | [63 empty] | JUSTIN SELVIK | REGULATORY COMPLIANCE SPECIALIST | jselvik@hilcorp.com | (907) 777-8538 |  |  |  |  | BEN WASSON | INTEGRITY ENGINEER | (907) 777-8447 | bwasson@hilcorp.com | DIVERS WERE CONDUCTING TACTILE INSPECTIONS OF A METAL LOSS ANOMALY IDENTIFIED BY A 2017 ILI WHEN THE DIVE BOAT NOTICED SMALL BUBBLES AT THE WATER SURFACE. UPON INVESTIGATION, DIVERS FOUND BUBBLES EMANATING FROM THE TOP OF THE PIPELINE NEAR A GIRTH WELD, LOCATED APPROXIMATELY FIVE FEET AWAY FROM THE ILI ANOMALY. PRODUCTION ON THE PLATFORM WAS SHUT-IN AND PIPELINE PRESSURE WAS REDUCED TO LIMIT THE LEAK TO THE FULLEST EXTENT WHILE MAINTAINING POSITIVE PRESSURE INSIDE THE PIPELINE. DIVERS BEGAN REPAIR ACTIVITIES, AND COMPLETED INSTALLATION OF A TEMPORARY CLAMP TO STOP THE LEAK WITHIN 24 HOURS OF DISCOVERY. THE INSTALLATION OF THE PERMANENT CLAMP TO REPAIR THE PIPELINE WAS COMPLETED ON MAY 24. HILCORP ALASKA SELECTED THE ONSHORE PIPELINE CLASSIFICATION IN PART B OF THIS REPORT. HOWEVER, HILCORP ALASKA AND PHMSA ARE CURRENTLY IN DISCUSSIONS REGARDING THE APPROPRIATE STATUS OF THE PIPELINE (ONSHORE VERSUS OFFSHORE).
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190063 | 33239 | 2019-05-28 11:19 | SUPPLEMENTAL FINAL | 20044 | LINDE | 10 RIVERVIEW DR. | DANBURY | CT | 06810 | 2019-05-05 17:30 | 2019 |  |  | 29.8269 | -94.9946 | 1244769 | 2019-05-06 09:22 |  | HYDROGEN GAS |  | 65.4 | 759 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-05-06 12:30 | 2019-05-12 09:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-05-05 17:30 | 2019-05-05 18:30 | ONSHORE | TX | 77521 | BAYTOWN | HARRIS | MILEPOST | 105+72.74 | GCPO | 232 - H2 BAYTOWN SEG 2 10IN | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 84 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10 |  | 0.228 | 52000 | API 5LX52 | LONGITUDINAL ERW - HIGH FREQUENCY |  | AMERICAN STEEL PIPE | EPOXY | [28 empty] | 1992 | 1992 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 156 |  | NO | NO | NO |  | 0 | 0 | 873 | 890.764083881287 | 75 | 75 | 400000 | 408139.328238848 | 100000 | 102034.832059712 | 0 | 0 |  |  | 500948 | 234670.041581716 | 511139.924382442 | [8 empty] | 800 |  | 1100 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 35646 | NO |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK INDICATIONS WERE NOT VISIBLE FROM THE SCADA. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [52 empty] | LIGHTNING |  |  | SECONDARY IMPACT SUCH AS RESULTING NEARBY FIRES |  |  | NO | [306 empty] | SEAN BINGHAM | PIPELINE REGULATORY SPECIALIST | sean_bingham@praxair.com | 6302079543 |  |  |  |  | SEAN BINGHAM | PIPELINE REGULATORY SPECIALIST | 6302079543 | sean_bingham@praxair.com | AT 1730 ON 5 MAY 2019, PRAXAIR WAS NOTIFIED BY A THIRD PARTY THAT THERE WAS A POSSIBLE LEAK ON ITS HYDROGEN PIPELINE, AS IDENTIFIED BY SOUND. PRAXAIR PERSONNEL ARRIVED ON THE SITE AT 1830 AND CONFIRMED THAT HYDROGEN WAS PRESENT IN THE AREA. THE LOCATION WAS IN AN ISOLATED AREA. MANUAL ISOLATION VALVES WERE SHUT TO CLOSE IN THE SEGMENT AND IT WAS MANUALLY BLOWN DOWN. AT 0852 ON 6 MAY 2019, PRAXAIR DETERMINED THAT THE INCIDENT MET REPORTABLE CRITERIA AND CALLED THE NATIONAL RESPONSE CENTER AT 0922. BLOWDOWN OF THE ISOLATED SEGMENT WAS COMPLETED AT 1230 ON 6 MAY 2019. THERE WAS NO IMMEDIATELY RECOGNIZABLE CAUSE OF THE INCIDENT. NO EXCAVATORS WERE OPERATING IN THE AREA, AND CP TESTING SHOWED NO ABNORMALITIES. THE SUSPECTED AREA OF THE LEAK WAS EXCAVATED, BUT THE PIPE WAS SHOWN TO BE IN EXCELLENT CONDITION. UPON FURTHER INVESTIGATION, IT WAS DETERMINED THAT THE LEAK WAS MOST LIKELY LOCATED UNDERNEATH A SMALL NON-NAVIGABLE DRAINAGE CANAL. UNABLE TO EXCAVATE UNDER THE WATER, A NEW SEGMENT OF PIPE WAS INSTALLED, REROUTING AROUND THE LEAK. THE PIPELINE WAS PUT BACK INTO SERVICE ON 12 MAY 2019 AT 0930. IN JUNE 2019, THE INACTIVE SEGMENT OF PIPE WAS FURTHER INVESTIGATED WITH A TETHERED INLINE INSPECTION (ILI) TOOL IN ORDER TO FURTHER INVESTIGATE THE CAUSE OF THE LEAK. RESULTS SHOWED AN ANOMALY IN THE VICINITY OF A GROUNDING ROD FOR A NEARBY ELECTRICAL TRANSMISSION TOWER. AN ADDITIONAL DCVG INSPECTION SHOWED A SIMILAR ANOMALY, CORRELATING THE RESULTS OF THE ILI. IT IS THEREFORE SUSPECTED THAT LIGHTNING STRUCK THE TOWER DURING A STORM, CREATING A SURGE OF ENERGY THAT RELEASED INTO THE GROUND THROUGH THE GROUNDING ROD. THIS ELECTRICAL ENERGY CREATED THE ANOMALY ON THE PIPE WHICH EVENTUALLY LED TO THE SMALL LEAK. THE NEWLY INSTALLED SEGMENT OF PIPE IS NOT LOCATED IN THE VICINITY OF THE GROUNDING ROD. AN EXTERNAL INSPECTION COMPANY WAS HIRED TO REVIEW PIPELINE LOCATIONS WITH SIMILAR ENVIRONMENTS THROUGHOUT THE PIPELINE SYSTEM. NO OTHER ANOMALIES WERE DISCOVERED AND A SIMILAR INCIDENT IS NOT SUSPECTED TO OCCUR AGAIN.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190064 | 33419 | 2019-05-31 08:41 | SUPPLEMENTAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2019-05-02 22:39 | 2019 | CENTRAL | YES | 34.6253 | -93.0407 | 1244490 | 2019-05-03 02:03 | 1244649 | NATURAL GAS |  | 51886 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-05-03 01:20 | 2020-02-02 09:30 |  | YES | OPERATOR | 2019-05-02 | NO | [5 empty] | VALVE CLOSURE |  | 2019-05-03 01:00 | VALVE CLOSURE |  | 2019-05-03 01:00 | 350 | 2019-05-02 22:50 | 2019-05-03 01:00 | ONSHORE | AR | 71909 | HOT SPRINGS VILLAGE | GARLAND | MILEPOST | 4131+28 | BT-1 | BT-1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 42 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 | NO | 0.328 | 65000 | API 5LX | SINGLE SAW |  | REPUBLIC | ASPHALT |  | YES | [26 empty] | 1973 | 1973 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 120 | 60 |  | CLASS 1 LOCATION | NO |  | 655 |  | NO | NO |  |  | 86421 | 88179.5222143238 | 0 | 0 | 136979 | 136979 | 4746798 | 4843387.36751377 | 25000 | 25508.708014928 | 0 | 0 |  | 2.64 | 4995198 | 2417440.84996994 | 5094054.59774303 | 0 | 0 | 10 | 0 | NO |  |  |  | 962 | 160000 | 1000 | 192.619(A)(1) |  | 2012-03-30 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 88338 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED |  | YES | [15 empty] | STRESS CORROSION CRACKING | [12 empty] | YES | NEAR NEUTRAL PH SCC ACTING WITHIN AREA OF EXTERNAL CORROSION. | 1426 | [54 empty] | YES | YES | [6 empty] | 2018 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2011 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [45 empty] | NO |  |  | NO | [13 empty] | NO | [45 empty] | YES | [17 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  | CASEY ROBERTS | casey.roberts@enablemidstream.com | 4055584647 | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | ON 5/2/2019 AT 22:39 ENABLE GAS TRANSMISSION LINE BT-1 EXPERIENCED A FAILURE NEAR HOT SPRINGS VILLAGE IN GARLAND COUNTY, ARKANSAS. THE FAILED SECTION OF BT-1 WAS SENT TO STRESS ENGINEERING SERVICES (SES) FOR METALLURGICAL ANALYSES. AS OF THE DUE DATE FOR THIS REPORT, THE LINE IS CURRENTLY OUT OF SERVICE AND THE RESULTS OF THE ANALYSIS HAVE NOT BEEN RECEIVED. PRELIMINARY FINDINGS FOR THE FAILURE ARE NEAR NEUTRAL STRESS CORROSION CRACKING ACTING WITHIN AREA OF EXTERNAL CORROSION. THE NRC WAS NOTIFIED ON 5/3/2019 AT 02:03 (NRC#1244490). A 48 HOUR FOLLOW UP CALL WAS PROVIDED TO THE NRC ON 5/4/2019 AT 14:54 (NRC# 1244649). THE FAILURE INVESTIGATION IS ON-GOING. ------UPDATE------ BASED ON EXAMINATIONS AND ANALYSIS BY STRESS ENGINEERING, IT WAS DETERMINED THE PIPE FAILED AS A RESULT OF NEAR-NEUTRAL PH STRESS CORROSION CRACKING (SCC) IN CONCERT WITH GENERAL EXTERNAL CORROSION THAT REDUCED THE WALL THICKNESS NEAR THE 6 O'CLOCK ORIENTATION OF THE PIPE. THE PIPELINE CONTINUES TO BE OUT OF SERVICE UNTIL ALL OF THE 30" IS HYDROTESTED. ------UPDATE------ THE LINE HAS BEEN FULLY HYDROTESTED AND WAS PLACED BACK INTO SERVICE ON FEBRUARY 2, 2020. 09/25/2019 SUPPLEMENTAL A.10 GAS LOSS VOLUME UPDATED. D.7 UPDATED CONSTRUCTION COSTS D.7.F GAS LOSS TOTAL UPDATED G.1 UPDATED TO DETERMINED BY METALLURGICAL ANALYSIS H. NARRATIVE UPDATED 2/3/2020 SUPPLEMENTAL A.15.B UPDATED TO 2/2/2020 AND 09:30 C.3.D UPDATED TO API-5L C.3.E UPDATED TO SUBMERGED ARC WELDING D.7 COSTS UPDATED E.5.C ENTERED 88,338 H. NARRATIVE UPDATED
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190065 | 32545 | 2019-05-31 11:38 | SUPPLEMENTAL FINAL | 2564 | COLORADO INTERSTATE GAS CO | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2019-05-02 23:54 | 2019 |  |  | 40.2277 | -103.8131 | 1244489 | 2019-05-03 00:57 |  | NATURAL GAS |  | 12626 | 166 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-05-08 19:00 | 2019-05-15 19:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-05-02 23:20 | 2019-05-02 23:54 | ONSHORE | CO | 80701 | FORT MORGAN | MORGAN | SURVEY STATION NO. | 11+2414 | FORT MORGAN LOOP | 4B | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | OTHER | VALVE STEM/OPERATOR |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | MAINLINE | BALL |  | GROVE |  |  |  | 1959 | 1959 | CARBON STEEL |  | OTHER | [8 empty] | VALVE FLANGE PULLED APART JUST ENOUGH TO ALLOW GAS RELEASE | CLASS 1 LOCATION | NO |  | 130 |  | NO | NO | NO |  | 0 | 0 | 332 | 338.755642438244 | 25252 | 25252 | 80000 | 81627.8656477697 | 2500 | 2550.8708014928 | 0 | 0 |  |  | 108084 | 64975.6540321388 | 109769.492091701 | [8 empty] | 630 |  | 800 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 29357 | YES | [7 empty] | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLERS COULD NOT HAVE CONTRIBUTED TO AN INCIDENT FROM 3RD PARTY DAMAGE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [260 empty] | KENNETH PETERS | SENIOR PIPELINE ENGINEER | ken_peters@kindermorgan.com | 2053257554 | 2053253592 |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | LATE NIGHT MAY 2, 2019, A FARMER WAS RUNNING A TRACTOR PLANTER IN A CIRCULAR PATTERN, PLANTING A FIELD OF CORN. THE TRACTOR PLANTER RAN THROUGH A STEEL BARRICADE AND OVER COLORADO INTERSTATE GAS (CIG) TRANSMISSION'S LINE 4B ABOVEGROUND VALVE STEM/OPERATOR. THIS CAUSED THE VALVE FLANGE TO PULL APART BELOWGROUND AND RELEASE NATURAL GAS. THE FARMER SHUT DOWN THE TRACTOR AND REMOVED HIMSELF FROM THE SCENE. CIG OPERATIONS PERSONNEL SECURED THE SITE AND DETERMINED THAT THERE WAS NO THREAT TO THE GENERAL PUBLIC SINCE THE OCCURRENCE WAS IN THE MIDDLE OF A FIELD, AWAY FROM ANY POPULATED AREAS. THE NEED TO MAINTAIN SERVICE TO CUSTOMERS RESULTED IN ALLOWING THE GAS TO CONTINUE TO RELEASE UNTIL A BYPASS COULD BE CONSTRUCTED AND INSTALLED. FOLLOWING THIS, ISOLATION VALVES WERE CLOSED AND THE PIPELINE WAS BLOWN DOWN TO ALLOW REMOVAL OF THE TRACTOR PLANTER AND REPAIR OF THE FACILITY. THE FACILITY WAS RESTORED TO SERVICE MAY 15, 2019. THE NECESSARY 48-HOUR UPDATE WAS PROVIDED TO THE NRC MAY 4, 2019 AT 13:06 MDT AND WAS ASSIGNED REPORT NUMBER 1244639.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190066 | 32600 | 2019-06-05 11:21 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2019-05-15 15:50 | 2019 |  |  | 30.6397 | -93.9097 | 1246205 | 2019-05-20 10:45 |  | NATURAL GAS |  | 0.1 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | MINOR LEAK ONLY REPORTED BECAUSE REPAIR COST MAY EXCEED $50,000 | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-05-15 15:50 | 2019-05-15 15:50 | ONSHORE | TX | 75956 | KIRBYVILLE | JASPER | MILEPOST | 120.33 | BEAUMONT-LATEX LINE | INDEX 64 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | IN OR SPANNING AN OPEN DITCH |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.25 | 30000 | API 5L | LAP WELDED |  | UNKNOWN | ASPHALT | [28 empty] | 1924 | 1924 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 196 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 55000 | 56119.1576328417 | 0 | 0 | 0 | 0 |  |  | 55000 | 25760.1741602985 | 56119.1576328417 | [8 empty] | 155 |  | 292 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 116160 | NO | YES |  | YES |  |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | MINOR LEAK NOT DETECTABLE BY SCADA | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  |  | YES | [7 empty] | YES |  |  |  | NO | [11 empty] | YES | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpmlp.com | 2706886357 |  |  |  |  | DARRAL WARD | MANAGER PIPELINE SAFETY | 2706886356 | darral.ward@bwpmlp.com | GULF SOUTH'S PIPELINE TECH FOUND A MINOR LEAK DURING LINE PATROL OF ITS INDEX 64. THE LINE IS IN A CREEK EXPOSURE. INDEX 64 IS OPERATING AT 155 PSIG AND HAS A MAOP OF 292 PSIG. THE LEAK IS SMALL AND 700 FT. FROM THE NEAREST STRUCTURE AND HIGHWAY. THE AREA WAS FLAGGED OFF AND CONTACT AT THE NEAREST PROPERTY WAS MADE. GULF SOUTH WILL INVESTIGATE THE LEAK TO DETERMINE WHAT REPAIR METHOD IS NEEDED. A PIPE REPLACEMENT IS THE LIKELY THE BEST REPAIR WHICH WOULD CAUSE THE COST TO EXCEED $50,000, MEETING THE PHMSA DEFINITION FOR INCIDENT. FOR THIS REASON, THE NRC WAS CALLED. THE GAS LOSS REMAINS UNKNOWN, BUT MINIMAL, AT THIS TIME AND THEREFORE, A GAS LOSS COST IS NOT DOCUMENTED IN THIS REPORT. THE RESPONSES TO PART E QUESTIONS 5A, 5B, AND 5C REPRESENT THE ANSWERS THAT WILL BE TRUE WHEN THE SECTION IS ISOLATED AND BLOWN DOWN; THAT HAS NOT YET HAPPENED BUT THE ANSWERS ARE POPULATED BECAUSE THE PORTAL WILL NOT ALLOW SUBMISSION OF THIS REPORT WITHOUT POPULATING THESE FIELDS. 8-21-19 UPDATE TO SUBMIT FINAL REPORT. A PLIDCO BOLT-ON CLAMP WAS INSTALLED. UPDATED REPAIR COSTS ACCORDINGLY. IN RESPONSE TO PHMSA EMAIL DATED 6-18-19, THE DATE SHOWN IN PART A, ITEM 4 (5-15-2019) IS CORRECT. THIS WAS THE DATE THE "POTENTIAL" LEAK WAS FIRST DISCOVERED ALTHOUGH IT WAS NOT A CONFIRMED LEAK NOR YET CONFIRMED WHAT THE REPAIR WOULD BE, THEREFORE, REPAIR COSTS COULD NOT YET BE ESTIMATED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190067 | 32584 | 2019-06-05 11:24 | SUPPLEMENTAL FINAL | 15105 | PANHANDLE EASTERN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2019-05-10 18:45 | 2019 |  |  | 39.7902 | -88.3589 | 1245594 | 2019-05-14 10:53 |  | NATURAL GAS |  | 3121.014 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | ISOLATED UNIT 1215 | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-05-10 18:47 | 2019-05-10 19:03 | ONSHORE | IL | 61953 | TUSCOLA | DOUGLAS | MILEPOST | 0+00 | TUSCOLA COMPRESSOR STATION | UNIT 1215 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1963 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE SETPOINT WAS SET TOO LOW | CLASS 1 LOCATION | NO |  | 331 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 8239 | 8239 | 0 | 0 | 0 | 0 | 157 | 160.194686333748 | 4 MAN HOURS FOR CALL-OUT |  | 8396 | 8615.27899488173 | 8399.19468633375 | [8 empty] | 843 |  | 900 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DID NOT EXCEED MAOP. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | TEST STAND WORN CAUSING RELIEF VALVE ACTUAL SET PRESSURE TO BE LOW | [15 empty] | YES | TEST STAND WORN CAUSING RELIEF VALVE ACTUAL SET PRESSURE TO BE LOW | [161 empty] | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | 5/10/19 18:47 CST PROPERTY OWNER NOTIFIED OPERATIONS OF GAS BLOWING AT STATION. 5/10/19 18:49 CST YARD NOISE ALARM TO GAS CONTROL. 5/10/19 19:03 CST UNIT 1215 SHUTDOWN AND TAKEN OUT OF SERVICE. 5/14/19 10:53 CST NRC TELEPHONIC NOTIFICATION MADE NRC#1245594. 5/14/19 11:11 CST PHMSA AID UPDATED. 5/16/19 10:16 CST 48-HOUR NRC NOTIFICATION MADE NRC#1245848. 5/16/19 10:47 CST PHMSA AID UPDATED. THE SUPPLEMENTAL REPORT SUBMITTED 8/20/19, IS MADE TO UPDATE PART D: 7D AND TO FURTHER CLARIFY THE EVENT. - THERE WERE NO REPAIRS REQUIRED TO THE RELIEF VALVE AS IT FUNCTIONED PROPERLY. IT WAS A FAULTY TEST STAND USED DURING THE TEST AND INSPECT OF THE RELIEF VALVE THAT LED TO THE SET-POINT BEING SET BELOW WHERE IT SHOULD HAVE BEEN SET, RESULTING IN THE RELEASE OF GAS. - THE TEST STAND WAS COMPLETELY REBUILT AND THE ACCURACY CONFIRMED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190068 | 32512 | 2019-06-07 11:14 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2019-05-08 20:02 | 2019 |  |  | 37.5801 | -84.7499 | 1245076 | 2019-05-08 22:12 |  | NATURAL GAS |  | 19350 | 226 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-05-08 20:43 | 2019-05-10 17:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-05-08 20:02 | 2019-05-08 20:35 | ONSHORE | KY | 40422 | DANVILLE | LINCOLN | MILEPOST | 427.273 | DANVILLE COMPRESSOR STATION | DANV-OWSV | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1948 |  | CARBON STEEL |  | OTHER | [8 empty] | EMERGENCY SHUTDOWN OF COMPRESSOR STATION | CLASS 1 LOCATION | NO |  | 634 |  | NO | NO | NO |  | 0 | 0 | 590 | 602.005509152301 | 50504 | 50504 | 0 | 0 | 3000 | 3061.04496179136 | 0 | 0 |  |  | 54094 | 54041.2268487098 | 54167.0504709437 | [8 empty] | 800 |  | 936 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS DETERMINED THE CONTROLLERS ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. AN ESD ISOLATION VALVE DID NOT CLOSE PROPERLY AND THE THIS EVENT COULD NOT BE ASSOCIATED WITH THE ROLES AND RESPONSIBILITIES OF THE CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [204 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | [5 empty] | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | MAYRA SALINAS | SENIOR ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: 48 HR NRC REPORT 1245382 AT APPROXIMATELY 8:02 PM EDT ON MAY 8, 2019, A NATURAL GAS RELEASE FROM THE EMERGENCY SHUTDOWN (ESD) SYSTEM OCCURRED AT THE DANVILLE COMPRESSOR STATION ON THE TEXAS EASTERN TRANSMISSION (TETLP) IN LINCOLN COUNTY, KENTUCKY. TETLP PERSONNEL ARRIVED ON SITE AT APPROXIMATELY 8:35 PM EDT AND DETERMINED THAT A VALVE (LINE 10 ESD ISOLATION VALVE) DID NOT CLOSE PROPERLY CAUSING THE GAS RELEASE AFTER THE ESD SYSTEM WAS ACTIVATED. THE TETLP PERSONNEL SUBSEQUENTLY ISOLATED THE ESD SYSTEM AT APPROXIMATELY 8:43 PM EDT, STOPPING THE GAS RELEASE. THE STATION WAS RETURNED TO NORMAL OPERATIONS ON MAY 10, 2019. THE APPARENT CAUSE IS STILL UNDER INVESTIGATION. SUPPLEMENTAL REPORT: TETLP HAS COMPLETED ITS INVESTIGATION OF THE MAY 8, 2019 ESD EVENT AT DANVILLE COMPRESSOR STATION. THE EMERGENCY SHUTDOWN (ESD) SYSTEM ACTIVATION WAS CAUSED BY A TRIP IN THE BREAKER SUPPLYING ELECTRICITY TO THE ESD PANEL RESULTING FROM A SHORT IN THE WIRING THAT RUNS FROM THE ESD PANEL TO AN ESD PULL-BUTTON. THE ESD SYSTEM ACTIVATED, BUT ONE OF THE ESD BLOCK VALVES, VALVE# 10-296, DID NOT CLOSE AS INTENDED. THE BLOCK VALVE HAD BEEN DEACTIVATED DURING THE ROUTINE TESTING AND INSPECTION OF THE ESD AS REQUIRED BY COMPANY PROCEDURES, HOWEVER, THE BLOCK VALVE WAS NOT REACTIVATED AFTER THE ROUTINE TESTING AND INSPECTION HAD BEEN COMPLETED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190069 | 32353 | 2019-06-10 12:26 | SUPPLEMENTAL FINAL | 31531 | ONEOK WESTEX TRANSMISSION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2019-05-23 | 2019 |  |  | 31.989 | -102.484 | 1247712 | 2019-06-03 14:33 |  | NATURAL GAS |  | 5232 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | #3 COMPRESSOR SHUT DOWN, STATION CONTINUED TO OPERATE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-05-23 20:30 | 2019-05-24 07:00 | ONSHORE | TX | 79741 | Not Within a Municipality | ECTOR | MILEPOST | COMPRESSOR ST | ONEOK WESTEX TRANSMISSION ECTOR CO. COMPRESSOR STA | ONEOK INDEX NUMBER 4056-000 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2016 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | SUCTION VALVE | OTHER | [8 empty] | RELIEF OPENED WHEN SUCTION VALVE FAILED TO CLOSE | CLASS 1 LOCATION | NO |  | 671 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 14269 | 14269 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 14269 | 14793.3202099738 | 14269 | [8 empty] | 957 |  | 1188 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | COMPRESSOR SUCTION ISOLATION VALVE | [22 empty] | YES | STATION PROGRAMING DID NOT INITIATE SUCTION VALVE CLOSURE DURING ENGINE SHUTDOWN | [161 empty] | BRACKEN HILL | COMPLIANCE SPECIALIST | bracken.hill@oneok.com | 806-324-9702 |  |  |  |  | BRACKEN HILL | COMPLIANCE SPECIALIST | 806-324-9702 | bracken.hill@oneok.com | AT APPROXIMATELY 20:30 ON 5/23/2019, THE HIGH TURBO TEMPERATURE ALARM INITIATED AN ENGINE SHUTDOWN FOR THE NUMBER 3 COMPRESSOR AT THE ONEOK WESTEX TRANSMISSION, ECTOR COUNTY COMPRESSOR STATION. AS THE COMPRESSOR SHUT DOWN THE STATION ALARM CONTROL LOGIC FAILED TO AUTOMATICALLY CLOSE THE SUCTION VALVE TO THE COMPRESSOR. FAILURE TO CLOSE THE SUCTION VALVE CAUSED 5232 MCF OF NATURAL GAS TO BE RELEASED THROUGH THE VENT VALVE.THE RELEASE WAS IDENTIFIED BY ONEOK OPERATIONS TEAM MEMBERS WHEN THEY ARRIVED ON SITE AT 07:00 ON 5/24 AND REVIEWED THE STATION CONTROL LOG. ONEOK TECHNICIANS REVIEWED THE PROGRAMMING LOGIC FOR THE CONTROLS OF THE COMPRESSOR. CORRECTIONS WERE MADE TO THE UNITS PROGRAMMING TO INSURE THE SUCTION VALVE CLOSES WHENEVER SHUT DOWN BY AN ALARM; TO PROHIBIT THIS EVENT FROM REOCCURRING.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190071 | 32325 | 2019-06-24 14:03 | ORIGINAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2019-05-25 02:00 | 2019 |  |  | 39.9307 | -78.5767 | 1246785 | 2019-05-25 10:02 |  | NATURAL GAS |  | 5900 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELIEF VALVE WAS ISOLATED AND HAD NO IMPACT ON PIPELINE OPERATIONS. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-05-25 06:30 | 2019-05-25 07:00 | ONSHORE | PA | 15522 | BEDFORD | BEDFORD | MILEPOST | 59.617 | M&R 71144 | BEDF-CHAM | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | UNKNOWN |  | CARBON STEEL |  | LEAK |  |  | OTHER | RELIEF VALVE RELEASE | [5 empty] | CLASS 1 LOCATION | NO |  | 103 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 15342 | 15342 | 0 | 0 | 1000 | 1020.34832059712 | 0 | 0 |  |  | 16342 | 16374.1148344106 | 16362.3483205971 | [8 empty] | 300 |  | 1389 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS DETERMINED THE CONTROLLERS ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. THE ACTIVATION OF THE RELIEF VALVE RELEASE COULD NOT BE ASSOCIATED WITH THE ROLES AND RESPONSIBILITIES OF THE A CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [25 empty] | YES | PRESSURE REGULATOR LEAKAGE DUE TO CUSTOMER DEMAND DROPPING TO ZERO FLOW | [161 empty] | MAYRA SALINAS | SENIOR ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: 48 HR NRC REPORT 1246924 AT APPROXIMATELY 6:30 AM EDT ON MAY 25, 2019, TEXAS EASTERN TRANSMISSION (TETLP) RECEIVED NOTIFICATION FROM A LAND OWNER ABOUT A RELEASE OF NATURAL GAS AT TETLP'S METER AND REGULATOR STATION (M&R 71144) IN BEDFORD COUNTY, PA. TETLP'S EMPLOYEE ARRIVED AT M&R 71144 AT APPROXIMATELY 7:00 AM EDT AND DISCOVERED A NATURAL GAS RELEASE THROUGH A RELIEF VALVE. THE EMPLOYEE STOPPED THE RELEASE BY CLOSING AN ISOLATION VALVE. THE RELIEF VALVE ACTIVATED BECAUSE THE CUSTOMER DEMAND HAD DROPPED TO ZERO FLOW (NOT UNUSUAL WITH WARM WEATHER) AND THE PRIMARY PRESSURE REGULATOR (SET AT 285 PSIG) SHUT OFF (AS INTENDED) THOUGH IT LEAKED A SMALL QUANTITY OF GAS THROUGH IT. THE SMALL LEAKAGE CAUSED THE PRESSURE TO BUILD UP UNTIL THE RELIEF VALVE ACTIVATED AT 300 PSIG. TETLP'S EMPLOYEE SUBSEQUENTLY INSPECTED THE RELIEF VALVE AND PRESSURE REGULATOR AND DETERMINED THAT THERE WERE NO MECHANICAL FAILURES (OTHER THAN THE SMALL LEAKAGE THROUGH THE REGULATOR WHEN THE CUSTOMER DEMAND WAS ZERO). THERE WAS NO OTHER IMPACT DUE TO THE RELEASE. THE PRESSURE REGULATOR SETTING AND RELIEF VALVE SETTINGS WERE ADJUSTED TO ACCOMMODATE FOR LOW DEMAND SUMMER CONDITIONS. TETLP REVIEWED THE SCADA DATA AT APPROXIMATELY 9:45 AM EDT ON MAY 25, 2019 AND DETERMINED THAT THE RELIEF VALVE BEGAN VENTING AT APPROXIMATELY 2 AM EDT ON MAY 25, 2019. TETLP WAS ABLE TO CALCULATE THE GAS LOSS BY CALCULATING THE RELIEF VALVE CAPACITY FLOW RATE AND OVER A 5-HOUR DURATION. TETLP SUBSEQUENTLY NOTIFIED THE NRC AT APPROXIMATELY 10:02 EDT.
2021-02-26 10:37 | YES | YES | GG (Gas Gathering) | 20190072 | 33829 | 2019-06-27 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2019-05-28 22:55 | 2019 | EASTERN | NO | 41.072 | -79.241 | 1247157 | 2019-05-29 14:04 | 1247379 | NATURAL GAS |  | 2400 | 7.78 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-05-29 13:55 | 2019-09-20 13:00 |  | NO |  |  | YES | 2019-05-29 13:55 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 2400 | YES | VALVE CLOSURE |  | 2019-05-29 12:15 | VALVE CLOSURE |  | 2019-05-29 12:17 | 2 | 2019-05-29 13:55 | 2019-05-28 23:55 | ONSHORE | PA | 16240 | MAYPORT | CLARION | MILEPOST | 682+07 | LINE 4010 | 4010-015 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 36 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 | NO | 0.156 | 42000 | X42 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | EXTRUDED POLYEHYLENE |  | NO | [26 empty] | 1982 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 2 LOCATION | NO |  | 93 |  | YES | YES | NO |  | 1000000 | 1020348.32059712 | 18 | 18.3662697707482 | 5520 | 5520 | 250000 | 255087.08014928 | 250000 | 255087.08014928 | 300000 | 306104.496179136 | ROOT CAUSE FAILURE ANALYSIS AND OTHER ENGINEERING COSTS | 2.3 | 1805538 | 848791.510494256 | 1842165.34334459 | 0 | 1 | 2 | 2 | NO |  |  |  | 32 | 1000 | 50 | 192.619(A)(2) |  | 1982-08-20 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 1076 | NO | YES | YES | [5 empty] | YES |  | YES |  |  |  |  | TYPE B GATHERING | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LINE 4010 IS NOT COVERED UNDER THE SCADA SYSTEM. NO ACTIVITIES BY THE GAS CONTROLLER | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES |  | YES |  |  |  |  | DIRECT CURRENT | CATHODIC PROTECTION CURRENT FROM NEARBY PROTECTED PIPELINE | YES | YES |  |  | YES | NO |  | YES | NO | [8 empty] | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | WILLIAM YOUSE | COMPLIANCE SPECIALIST | william_youse@tcenergy.com | (304)357-3596 |  |  |  |  | PAUL SHAFFER | US REGULATORY COMPLIANCE EAST MANAGER | (304)357-2245 | paul_shaffer@tcenergy.com | ON MAY 28, 2019, AT APPROXIMATELY 10:55 P.M., COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA) RECEIVED NOTICE OF A POTENTIAL INCIDENT AT 2464 PINE RUN ROAD NEAR MAYPORT, PENNSYLVANIA. THE INCIDENT LOCATION WAS ADJACENT TO A COLUMBIA PIPELINE, LINE 4010, WHICH IS PART OF A 13.88-MILE GATHERING SYSTEM THAT TRANSPORTS GAS FROM PRODUCTION FACILITIES IN JEFFERSON AND CLARION COUNTIES, PENNSYLVANIA, TO A COMPRESSOR STATION IN RIMERSBURG, PENNSYLVANIA. THE FEDERAL POWER COMMISSION ORIGINALLY APPROVED COLUMBIA'S ACQUISITION OF LINE 4010 IN 1971, AND THE PIPELINE REMAINS SUBJECT TO THE JURISDICTION OF THE FEDERAL ENERGY REGULATORY COMMISSION UNDER THE NATURAL GAS ACT. COLUMBIA'S RECORDS INDICATE THAT THE SECTION ADJACENT TO THE INCIDENT LOCATION WAS REPLACED IN 1982 USING 0.156-INCH WALL THICKNESS, 6-INCH NPS CARBON STEEL PIPE WITH AN EXTRUDED POLYETHYLENE COATING. COLUMBIA'S RECORDS ALSO INDICATE THAT AT THE TIME OF THE INCIDENT THE MAXIMUM ALLOWABLE OPERATING PRESSURE OF LINE 4010 WAS 50 PSIG, PRODUCING A HOOP STRESS THAT IS LESS THAN 20 PERCENT OF SPECIFIED MINIMUM YIELD STRENGTH OF THE LINE PIPE, AND THAT THE OPERATING PRESSURE WAS 32 PSIG. COLUMBIA'S RECORDS FURTHER INDICATE THAT THE SECTION ADJACENT TO THE INCIDENT LOCATION WAS NOT PART OF A REGULATED GATHERING LINE, ALTHOUGH PHMSA AND COLUMBIA ARE CURRENTLY REVIEWING THAT DETERMINATION. COLUMBIA OPERATIONS PERSONNEL ARRIVED AT THE INCIDENT LOCATION AT APPROXIMATELY 11:10 P.M. A RESIDENCE AT THE LOCATION SUSTAINED FIRE-RELATED DAMAGE, AND AN OCCUPANT SUSTAINED INJURIES NECESSITATING IN-PATIENT HOSPITALIZATION. ANOTHER SINGLE-FAMILY DWELLING IN THE VICINITY WAS EVACUATED AS A PRECAUTIONARY MEASURE. AS PART OF ITS INITIAL RESPONSE TO THE INCIDENT, COLUMBIA SURVEYED THE AREA TO IDENTIFY POTENTIAL LEAK SOURCES, ISOLATED THE AFFECTED SECTION, AND TOOK OTHER REMEDIAL ACTIONS IN COOPERATION WITH STATE AND LOCAL AUTHORITIES. COLUMBIA ALSO SUBMITTED INCIDENT REPORTS TO THE NATIONAL RESPONSE CENTER (NRC) ON MAY 29, 2019 (NRC REPORT NO. 1247157), AND MAY 31, 2019 (NRC. REPORT NO. 1247379). A THIRD PARTY, ECHELON- APPLIED GEOSCIENCES CONSULTING, CONDUCTED A STRAY GAS ORIGIN STUDY AS PART OF COLUMBIA'S INCIDENT INVESTIGATION. THE STUDY REVEALED THAT THE STRAY GAS IN THE SOILS IN THE VICINITY OF THE INCIDENT LOCATION WAS OF THE SAME GENETIC ORIGIN AS THE GAS IN LINE 4010, AND THAT THERE WAS A FEASIBLE PATHWAY FOR LEAKING GAS TO MIGRATE FROM LINE 4010 TO THE RESIDENCE. HOWEVER, THE STUDY ALSO INDICATED THAT STRAY GAS DETECTED IN THE SOILS WAS OF THE SAME GENETIC ORIGIN AS GAS FROM A NEARBY WELL (API # 37-031-00978), WHICH IS THE SUBJECT OF AN ONGOING INVESTIGATION BY THE PENNSYLVANIA DEPARTMENT OF ENVIRONMENTAL PROTECTION (PADEP). ANOTHER THIRD PARTY, KIEFNER AND ASSOCIATES (KIEFNER), PREPARED A ROOT CAUSE FAILURE ANALYSIS (RFCA) FOR COLUMBIA. IN THE RCFA, KIEFNER CONCLUDED THAT A LEAK IN LINE 4010 BENEATH PINE RUN ROAD WAS THE SIGNIFICANT CONTRIBUTOR OF FUEL TO THE FIRE AT THE RESIDENCE, AND THAT THE LEAK WAS CAUSED BY EXTERNAL CORROSION. HOWEVER, KIEFNER ALSO NOTED THAT TWO OTHER POTENTIAL COMBUSTIBLE GAS SOURCES WERE PRESENT IN THE AREA: (1) A THIRD-PARTY METER STATION LOCATED TO THE SOUTH OF THE RESIDENCE, WHICH WAS LEAKING AT THE TIME OF THE INCIDENT, AND (2) A THIRD-PARTY WELL LOCATED ON A NEIGHBORING PROPERTY WITH GAS GEOCHEMISTRY THAT WAS INDISTINGUISHABLE FROM THE GAS IN LINE 4010. KIEFNER COULD NOT OFFER A CONCLUSIVE DETERMINATION ABOUT THE POSSIBLE INFLUENCE OF THESE OTHER GAS SOURCES ON THE INCIDENT. COLUMBIA IS IN THE PROCESS OF IMPLEMENTING THE RECOMMENDATIONS THAT KIEFNER INCLUDED IN THE RCFA TO PREVENT THE POTENTIAL RECURRENCE OF A SIMILAR INCIDENT. COLUMBIA HAS COOPERATED WITH THE VARIOUS AUTHORITIES INVOLVED IN THE INCIDENT INVESTIGATION AND WILL UPDATE THE INFORMATION PROVIDED IN THIS REPORT IF ADDITIONAL RELEVANT MATERIAL BECOMES AVAILABLE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190073 | 32346 | 2019-06-27 15:08 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-05-30 09:45 | 2019 |  |  | 35.8487 | -87.4505 | 1247267 | 2019-05-30 10:54 |  | NATURAL GAS |  | 48698 | 1956 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE INCIDENT OCURRED WHEN THE STATION WAS ALREADY OFF-LINE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-05-30 09:45 | 2019-05-30 09:45 | ONSHORE | TN | 37137 | NUNNELLY | HICKMAN | MILEPOST | CS 860 | COMPRESSOR STATION 860 | 500 LINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1962 |  | CARBON STEEL |  | LEAK |  |  | OTHER | RELEASE THROUGH BLOWDOWN STACK | [5 empty] | CLASS 3 LOCATION | NO |  | 633 |  | NO | NO | NO |  | 0 | 0 | 5086 | 5189.49155855696 | 126615 | 126615 | 4400 | 4489.53261062733 | 1280 | 1306.04585036431 | 0 | 0 |  |  | 137381 | 136309.956685217 | 137600.070019549 | [8 empty] | 702 |  | 936 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WAS NO INDICATION THAT ANY ACTIONS ON THE PART OF THE CONTROLLER CONTRIBUTED TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | YES | ISOLATION VALVE | [22 empty] | YES | INTERNAL WORN VANES IN VALVE ACTUATOR MOTOR | [161 empty] | SHELLEY DIETZ | PIPELINE ENGINEER | shelley_dietz@kindermorgan.com | 713-420-4417 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | AT 9:42AM ON MAY 30, 2019, THE ESD SYSTEM AT TENNESSEE GAS PIPELINE COMPANY (TGP) STATION 860 WAS ACTIVATED FOR A SCHEDULED ESD TEST. AFTER 3 MINUTES, AT 9:45AM, STATION PERSONNEL NOTICED THAT THE SUCTION SIDE OF THE STATION WAS EVACUATED AS DESIGNED; HOWEVER, THE DISCHARGE SIDE CONTINUED TO BLOW DOWN. AT THIS POINT, STATION PERSONNEL BEGAN TO LOCATE THE SOURCE OF THE RELEASE. STATION PERSONNEL DETERMINED THAT BD 500-1, A 30" ISOLATION VALVE, DID NOT CLOSE AS INTENDED DURING THE ESD. THIS ALLOWED GAS TO BLOW THROUGH FOUR 8" AND ONE 10" BLOWDOWN STACKS. STATION PERSONNEL CLOSED THE BLOWDOWN VALVES TO STOP THE RELEASE. THE TOTAL VENT TIME WAS 16 MINUTES AND THE TOTAL UNINTENTIONAL GAS LOSS WAS 48,698 MCF. INCIDENT INVESTIGATION REVEALED THAT VALVE BD 500-1 FAILED TO CLOSE AS THE VALVE ACTUATOR MOTOR DID NOT OPERATE. A 3RD PARTY CONTRACTOR EXAMINED THE MOTOR AND DETERMINED THAT INTERNAL WORN VANES CAUSED THE FAILURE TO OPERATE. TO PREVENT A REOCCURRENCE, THE VALVE ACTUATOR MOTOR WAS REPLACED. A 48-HR UPDATE CALL WAS MADE TO THE NRC. THE NRC REPORT NUMBER FOR THIS CALL IS #1247459.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190074 | 33883 | 2019-06-28 16:53 | SUPPLEMENTAL FINAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-06-01 10:12 | 2019 | CENTRAL | NO | 34.4636 | -97.5309 | 1247500 | 2019-06-01 11:02 | 1247648 | NATURAL GAS |  | 150 | 250 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | IDLE | [5 empty] | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2019-06-01 10:30 | YES | 2019-06-01 10:12 | ALLOWED TO BURN OUT |  | 150 | NO | [6 empty] | 0 | 2019-06-01 10:12 | 2019-06-01 10:12 | ONSHORE | OK | 73481 | RATLIFF CITY | CARTER | SURVEY STATION NO. | CS 801 | RATLIFF CITY COMPRESSOR STATION 801 | AG TEXOMA SYSTEM | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | FILTER/STRAINER/SEPARATOR | [38 empty] | 1999 | 1999 | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 671 |  | NO | NO |  |  | 0 | 0 | 650 | 663.226408388129 | 390 | 390 | 450588 | 459756.709081216 | 3500 | 3571.21912208992 | 156097 | 159273.311800249 | MATERIALS FOR TEMPORARY SETUP | 2.6 | 611225 | 286499.166766952 | 623654.466411942 | 0 | 0 | 0 | 0 | NO |  |  |  | 652 | 0 | 1050 | 192.619(A)(1) |  | 1989-12-16 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WAS NO INDICATION THAT ANY ACTIONS ON THE PART OF THE CONTROLLER CONTRIBUTED TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | INADEQUATE PROCEDURE. FURTHER EXPLANATION PROVIDED IN PART H: NARRATIVE. | YES |  |  |  |  | OTHER MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [146 empty] | YES | YES |  | SHELLEY DIETZ | PIPELINE ENGINEER | shelley_dietz@kindermorgan.com | 713-420-4417 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | AT 10:12AM ON JUNE 1, 2019, OPERATIONS PERSONNEL WORKING AT THE NATURAL GAS PIPELINE COMPANY OF AMERICA (NGPL) RATLIFF CITY COMPRESSOR STATION 801 HEARD A LOUD NOISE FROM THE OTHER SIDE OF THE YARD. EMPLOYEES SAW FLAMES ORIGINATE FROM AND ENGULF FILTER/SEPARATOR #3. OPERATIONS PERSONNEL IMMEDIATELY CALLED THEIR SUPERVISOR AND MUSTERED AT THE FRONT GATE. THERE WERE NO INJURIES. THE RATLIFF CITY FIRE DEPARTMENT ARRIVED ON SITE AFTER RECEIVING A CALL FROM A CONCERNED CITIZEN. HOWEVER, THEY DID NOT APPROACH OR FIGHT THE FIRE. AT THE TIME OF THE NRC CALL, 11:02AM, THE FIRE HAD DIED OUT. PRIOR TO THE EVENT, THE STATION WAS OFF-LINE AND ISOLATED FOR MAINTENANCE. THIS THEREFORE MINIMIZED THE AMOUNT OF GAS LOSS. THE INVESTIGATION IN TO THE INCIDENT WAS INCONCLUSIVE ON THE EXACT CAUSE OF THE INCIDENT. CONTRIBUTING FACTORS TO THE INCIDENT WERE DETERMINED TO INCLUDE THE PRESENCE OF A FLAMMABLE ATMOSPHERE AND IRON SULFIDE IN THE FILTER SEPARATOR AND INADEQUATE PROCEDURES. THE INVESTIGATION REVEALED THAT THERE WAS NEITHER A MANUFACTURERS NOR A SITE-SPECIFIC PROCEDURE FOR PURGING AND PACKING THE FILTER SEPARATOR UNITS. IN ADDITION, THERE WAS NOT A MAINTENANCE PROCEDURE FOR CLEANING OUT OF THE ACCESSIBLE SECTIONS OF THE FILTER SEPARATORS, LEADING TO AN EXCESSIVE AMOUNT OF SOLID BUILD UP, INCLUDING IRON SULFIDE. IN ORDER TO PREVENT A REOCCURRENCE, A PURGE VALVE WAS ADDED TO THE DOWNSTREAM SECTION OF FILTER SEPARATORS #1 AND #3 (ONE ALREADY EXISTED ON #2) TO MAKE THE PURGING SEQUENCE REQUIRED ON EACH SEPARATOR SIMILAR. THE EMPLOYEES HAVE BEEN RETRAINED ON PURGING AND PACKING, AND A SITE-SPECIFIC PROCEDURE TO ENSURE AN EFFECTIVE PURGE THROUGH THE ENTIRE FILTER SEPARATOR VESSEL WAS CREATED. IN ADDITION, NGPL EMPLOYEES ALSO REVISED THE SITE-SPECIFIC MAINTENANCE PROCEDURE TO INCREASE THE FREQUENCY OF FILTER ELEMENT REPLACEMENT AND CLEANING PARTICULATES OUT OF THE SUMP VESSEL.
2021-02-26 10:37 | YES | NO | UNGS (Underground Natural Gas Storage) | 20190075 | 32926 | 2019-06-28 17:24 | SUPPLEMENTAL FINAL | 4060 | DOMINION ENERGY OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2019-05-30 06:09 | 2019 |  |  | 40.886 | -81.5428 | 1247272 | 2019-05-30 12:08 |  | NATURAL GAS |  | 1.2 | 4.5 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-05-30 06:48 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-05-30 06:09 | 2019-05-30 06:45 | ONSHORE | OH | 44614 | Not Within a Municipality | STARK | MILEPOST | WELL # 1944 | WELL # 1944 MORELLI REALTY #1 | WELL # 1944 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | OTHER | [37 empty] | RING GASKET | UNKNOWN |  | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 47 |  | NO | NO | NO |  | 0 | 0 | 9 | 9.18313488537409 | 2 | 2 | 250000 | 255087.08014928 | 1000 | 1020.34832059712 | 0 | 0 |  |  | 251011 | 117566.356323584 | 256118.611604763 | [8 empty] | 315 |  | 2000 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION IN STORAGE FIELD | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [260 empty] | JEFFERY BURDETTE | ENGINEERING TECHNICAL CONSULTANT | jeffery.l.burdette@dominionenergy.com | 3307545524 |  |  |  |  | TERRY GLIDDEN | MANAGER GAS OPERATIONS OHIO PIPELINE SAFETY | 3303514326 | terry.l.glidden@dominionenergy.com | AT APPROXIMATELY 6:00 AM ON MAY 30, 2019, STORAGE WELL #1944 WAS STRUCK WITH A TRACTOR AND MANURE SPREADER. THE CONTRACTED MANURE SPREADER WAS NOT THE NORMAL FARMER DOING THE WORK, AND NOT FAMILIAR WITH THE PROPERTY. THE WORK WAS PERFORMED DURING EARLY HOURS WITH LESS DAY LIGHT FOR VISIBILITY. DOMINION ENERGY OHIO FIELD PERSONNEL WERE NOTIFIED BY THE FARMER AND ARRIVED ON LOCATION AT 06:45 AM. THE GAS LEAK WAS FOUND TO BE COMING FROM BELOW THE MASTERVALVE (GATE VALVE), ON THE FLANGE BETWEEN THE MASTERVALVE AND THE WELLHEAD ADAPTER FLANGE (INTERNAL WELLHEAD SEALS). WELLHEAD CASING PRESSURE (3.50" OD CASING) WAS MEASURED AT 315 PSIG. ANNULAR PRESSURE WAS MEASURED AT 0.5 PSIG. AT 06:48 HRS, THE WELL WAS BLOWN TO THE STOCK TANK AND BLEW DOWN COMPLETELY IN 5 MINUTES. THE WELL IS STILL BLOWN DOWN AND REPAIR COSTS ARE ESTIMATED. ADDITIONAL PROTECTION AROUND THE WELL IS BEING CONSIDERED TO MINIMIZE THE POSSIBILITY OF A RECURRENCE. ALSO, ADDITIONAL ENHANCEMENTS TO PUBLIC AWARENESS IS BEING CONSIDERED TO INCLUDE MANURE SPREADER CONTRACTORS. THE WELL IS STILL SHUT IN AND IS ANTICIPATED TO BE REPAIRED/REPLACED SOMETIME IN NOVEMBER 2019. UPDATES WILL CONTINUE TO BE PROVIDED VIA EMAIL TO THE LEAD PHMSA STORAGE INSPECTOR. THE OCTOBER 2019 UPDATE REQUEST AND GUIDANCE PROVIDED BY PHMSA FOR UPDATES ALSO SUGGESTED THAT NO FURTHER SUPPLEMENTAL REPORTING WAS REQUIRED FOR THIS INCIDENT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190076 | 32742 | 2019-07-02 16:47 | SUPPLEMENTAL FINAL | 4060 | DOMINION ENERGY OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2018-04-16 08:00 | 2018 |  |  | 41.8105 | -81.0946 | NRC NOTIFICATION REQUIRED BUT NOT MADE |  |  | NATURAL GAS |  | 2119 | 215 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-03-29 17:43 | 2018-03-31 18:10 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-03-29 13:01 | 2018-03-29 13:32 | ONSHORE | OH | 44057 | MADISON | LAKE | MILEPOST | L#298 | LAKESHORE LINE | L#298 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.25 | 35000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1969 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 2.5 | 0.6 | [7 empty] | CLASS 3 LOCATION | NO |  | 223 |  | NO | NO | NO |  | 0 | 0 | 426 | 443.495738893926 | 4195 | 3778.47517730496 | 56130 | 58435.2484134179 | 4974 | 5178.28123300091 | 0 | 0 |  |  | 65725 | 33321.1816987413 | 67835.5005626177 | [8 empty] | 144 |  | 260 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 27984 | YES | [7 empty] | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | YES |  |  |  |  | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 807200681 | OHIO ONE-CALL (OUPS) | CONTRACT LOCATOR | YES | YES | YES | 48 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO MAINTAIN CLEARANCE | [263 empty] | JEFFERY BURDETTE | TECHNICAL CONSULTANT | jeffery.l.burdette@dominionenergy.com | 3307545524 |  |  |  |  | TERRY GLIDDEN | MANAGER GAS OPERATIONS OHIO PIPELINE SAFETY | 3303514326 | terry.l.glidden@dominionenergy.com | A CONTRACTOR INSTALLING A WATER MAIN DROVE A TRENCH BOX INTO A DOMINION ENERGY OHIO TRANSMISSION LINE L#298. THE CONTRACTOR WAS INFORMED OF THE SAFE DIGGING REQUIREMENTS, BUT FAILED TO CONTACT THE COMPANY OR CONTRACTED LOCATING SERVICE WHEN EXCAVATING WITHIN 10 FEET OF THE TRANSMISSION LINE. AN RCA WAS CONDUCTED AND FOUND THE ROOT CAUSE TO BE A FAILURE TO MAINTAIN CLEARANCE BETWEEN POWERED EQUIPMENT AND UNDERGROUND FACILITIES. THIS INCIDENT WAS FOUND UNREPORTED DURING A PUCO PIPELINE SAFETY INSPECTION. THE REASON WAS DUE TO THE $50,000 THRESHOLD EXCEEDANCE FROM CONTRACTOR REPAIR COSTS INCURRED AFTER THE EVENT, BUT NOT CORRECTLY TRACKED FOR REPORTING REQUIREMENTS. DOMINION ENERGY OHIO HELD AN INTERNAL MEETING TO ADDRESS THIS ISSUE AND IMPLEMENTED MEASURES TO ENSURE FUTURE REPORTING IS NOT MISSED AGAIN.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190077 | 33514 | 2019-07-03 11:22 | SUPPLEMENTAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2019-06-18 15:18 | 2019 | CENTRAL | YES | 34.4532 | -90.5873 | 1249387 | 2019-06-19 10:20 | 1249482 | NATURAL GAS |  | 19105 | 601 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-06-19 11:33 |  | YES | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | FLOW CONTROL UPSTREAM FED PARALLEL LINE. |  | OPERATIONAL CONTROL | FLOW CONTROL UPSTREAM FED PARALLEL LINE. |  | 0 | 2019-06-18 15:18 | 2019-06-19 09:10 | ONSHORE | AR | 72342 | HELENA | PHILLIPS | MILEPOST | 9+1382 | HELENA 12" LINE #1 | HEL 12-1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | UNDERWATER IN MS RIVER | 240 | NO | YES | [6 empty] | YES | UNCASED | MISSISSIPPI RIVER | 192 | BELOW WATER, PIPE BURIED BELOW BOTTOM (NOT IN BORED/DRILLED CROSSING) | YES | [10 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 | NO | 0.5 | 42000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | YOUNGSTOWN | COAL TAR |  | UNKNOWN | [26 empty] | 1950 | 1950 | CARBON STEEL |  | LEAK |  |  | OTHER | UNKNOWN; UNSAFE FOR DIVING OPS | [5 empty] | CLASS 1 LOCATION | NO |  | 290 |  | NO | NO |  |  | 0 | 0 | 1581 | 1613.17069486405 | 50246 | 50246 | 1400000 | 1428487.64883597 | 1500 | 1530.52248089568 | 0 | 0 |  | 2.63 | 1453327 | 709248.871911392 | 1481877.34201173 | 0 | 0 | 0 | 0 | NO |  |  |  | 683 | 40000 | 914 | 192.619(A)(1) |  | 1949-12-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 15097 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | LINE HAS BEEN ABANDONED; FINAL DETERMINATION WILL NOT BE COMPLETED. | [145 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 270-688-6357 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 270-688-6497 | tina.baker@bwpipelines.com | ON JUNE 18, 2019, TEXAS GAS TRANSMISSION'S GAS CONTROL RECEIVED A CALL ABOUT A POSSIBLE UNDERWATER PIPELINE LEAK IN THE MISSISSIPPI RIVER. AREA PERSONNEL ARRANGED FOR HELICOPTER, FLEW OVER AREA, AND CONFIRMED BUBBLES ON JUNE 19 AT APPROXIMATELY 09:10. NRC NOTIFICATION WAS MADE AND LINE WAS ISOLATED AND PRESSURED DOWN TO 0 PSIG. ON JUNE 21, A SONAR INSPECTION WAS DONE BUT WATER WAS AT A HIGH LEVEL WITH THE EAST BANK RIGHT-OF-WAY FLOODED AND INACCESSIBLE. DUE TO THE WATER MOVEMENT AND FLOODING IT WAS UNSAFE FOR DIVING OPERATIONS; INCIDENT SITE IS APPROXIMATELY 80 FEET BELOW WATER. MULTIPLE SONAR PASSES WERE RECORDED FROM APPROXIMATELY THE MIDDLE OF THE RIVER TOWARD THE WEST BANK WHERE THE SUSPECTED LEAK IS LOCATED. SONAR INDICATES THERE MAY BE A POSSIBLE EXPOSURE ON THE HELENA 12" #1 LINE (HEL 12-1). IT IS LIKELY THAT THIS SECTION OF THIS LINE WILL BE ABANDONED. 9-6-19 EMAIL RECEIVED FROM PHMSA INDICATED THAT THE LATITUDE AND LONGITUDE INDICATED ON THIS REPORT DOES NOT FALL ON THE REFERENCED MAPPED PIPELINE. THIS PIPELINE IS UNDER THE MISSISSIPPI RIVER AND THE LOCATION PROVIDED IS WHERE BUBBLES WERE FOUND IN THE WATER; THIS IS THE MOST ACCURATE LATITUDE AND LONGITUDE AVAILABLE AT THIS TIME. THE LINE IS STILL SHUT IN. ALTHOUGH IT IS NOT KNOWN WHETHER THE INCIDENT OCCURRED ON THE PIPE OR A WELD, TO ACCOMMODATE PHMSA'S REQUEST FOR PIPE DATA, THE ANSWERS PROVIDED IN PART C HAVE CHANGED FROM "ITEM INVOLVED IN INCIDENT = UNKNOWN," TO "ITEM INVOLVED IN INCIDENT = PIPE." REGARDING THE COSTS AND ABANDONMENT, COST HAS BEEN REDUCED FROM $5,000,000 TO $1,400,000 BECAUSE TEXAS GAS ORIGINALLY EXPECTED TO REPAIR THE LINE BUT INSTEAD WILL CHECK THE INTEGRITY OF THE HEL 12-2 (PARALLEL LINE) AND CONSIDER ABANDONING THE HEL 12-1; IF THIS APPROACH IS USED, PIG TRAPS MAY ALSO BE INSTALLED. CAUSE HAS NOT BEEN DETERMINED. THIS LINE IS OUT OF SERVICE AND THE LOCATION IS UNDER THE MISSISSIPPI RIVER. NO ADDITIONAL INVESTIGATION INTO CAUSE IS PLANNED. 11-14-19 UPDATE: TEXAS GAS WILL INVESTIGATE USING A DIVING TEAM. AT THIS TIME, THE CAUSE REMAINS UNKNOWN. ADDITIONALLY, TEXAS GAS PLANS TO PERFORM AN INLINE INSPECTION ON THE PARALLEL LINE. 3-25-2020 DIVERS WERE UNABLE TO IDENTIFY THE CAUSE OF THIS INCIDENT. THE PIPELINE INVOLVED IN THIS INCIDENT HAS NOW BEEN ABANDONED IN PLACE. A SECOND REDUNDANT PIPELINE IN THE SAME RIGHT-OF-WAY WAS MODIFIED AND INLINE INSPECTED TO ENSURE ITS INTEGRITY. INLINE INSPECTION SHOWED THIS PIPELINE IS FIT FOR SERVICE. SUBSEQUENTLY, GAS WAS RE-ROUTED TO THIS PIPELINE TO PROVIDE SERVICE. TO FURTHER INVESTIGATE THE CAUSE OF THIS INCIDENT WOULD REQUIRE PHYSICAL INSPECTION OF THE ABANDONED PIPELINE. DOING SO WOULD REQUIRE DIVERS TO JET OUT APPROXIMATELY 20 FEET OF SILT FROM THE RIVER BOTTOM. THIS ACTION WOULD NOT ONLY POSE SIGNIFICANT RISK TO PERSONNEL BUT COULD POSSIBLY JEOPARDIZE THE INTEGRITY OF THE SECOND PIPELINE NOW IN SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190078 | 32463 | 2019-07-05 10:25 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2019-06-07 04:14 | 2019 |  |  | 32.4671 | -91.5975 | 1248110 | 2019-06-07 06:35 |  | NATURAL GAS |  | 28400 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-06-07 05:38 | 2019-06-07 13:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-06-07 04:14 | 2019-06-07 05:30 | ONSHORE | LA | 71232 | DELHI | RICHLAND | MILEPOST | MLV 13 | DELHI COMPRESSOR STATION | 8012501 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1956 |  | CARBON STEEL |  | OTHER | [8 empty] | MALFUNCTION OF THE EMERGENCY SHUTDOWN SYSTEM (ISOLATION VALVE FAILED TO CLOSE) | CLASS 1 LOCATION | NO |  | 788 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 69000 | 69000 | 0 | 0 | 0 | 0 | 350 | 357.121912208992 | LABOR COSTS |  | 69350 | 71699.3614518862 | 69357.121912209 | [8 empty] | 670 |  | 858 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER IDENTIFIED THE ISSUE VIA SCADA ALARMS AND INITIATED A CALL-OUT OF FIELD OPERATIONAL PERSONNEL, WHO IDENTIFIED THE INCIDENT AND TOOK CORRECTIVE ACTIONS. GAS CONTROL DOES NOT HAVE THE CAPABILITY TO REMOTELY CLOSE VALVES AND THEREFORE COULD PREVENT THE INCIDENT THROUGH THEIR ACTIONS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [5 empty] | YES | [12 empty] | YES | [11 empty] | YES | VALVE FAILED TO CLOSE COMPLETELY | [161 empty] | ROGER STREET | COMPLIANCE SPECIALIST | roger_street@transcanada.com | 615-465-5123 |  |  |  |  | ERIK HUGHES | US REGUALTORY COMPLIANCE MANAGER - WEST | 402-492-7447 | erik_hughes@transcanada.com | ON JUNE 7 AT 04:14 CT, ANR PIPELINE GAS CONTROL RECEIVED AN EMERGENCY SHUTDOWN SYSTEM (ESD) ALARM AT DELHI COMPRESSOR STATION LOCATED AT 1984 HWY 80 W, DELHI, LA 71232 (32.46620, -91.59704). WHEN THE ALARM WAS DETECTED, A TECHNICIAN WAS DISPATCHED TO THE COMPRESSOR STATION TO INVESTIGATE. UPON ARRIVAL AT THE SITE AT 05:30 CT, THE TECHNICIAN DISCOVERED NATURAL GAS BEING RELEASED THROUGH THE STATION BLOWDOWN STACKS. IMMEDIATE ACTION WAS TAKEN BY CLOSING THE VALVES OPEN TO ATMOSPHERE, WHICH ENDED THE RELEASE AT 05:38 CT. UNINTENTIONAL GAS LOSS WAS CALCULATED TO 28.4 MILLION CUBIC FEET (MMCF). NO PROPERTY DAMAGE OR INJURIES WERE DOCUMENTED AND NO EVACUATIONS WERE REQUIRED. INVESTIGATION INTO THE CAUSE OF THE UNINTENTIONAL RELEASE WAS ATTRIBUTED TO A FIRE DETECTION EQUIPMENT (FIRE EYE) FAULT THAT INITIATED THE ACTIVATION OF THE ESD SYSTEM. WHEN THE SYSTEM ACTIVATED, A STATION ISOLATION VALVE FAILED TO FULLY CLOSE RESULTING IN THE RELEASE GAS ABOVE 3 MILLION CUBIC FEET THROUGH THE STATION'S BLOWDOWN PIPING. NO EVIDENCE OF FIRE WAS DISCOVERED WITHIN THE COMPRESSOR STATION BUILDING. THUNDERSTORMS WITH LIGHTNING MAY HAVE ALSO CONTRIBUTED TO THE ACTIVATION OF THE FIRE DETECTION EQUIPMENT. PRIOR TO PLACING THE STATION BACK INTO SERVICE, THE FIRE DETECTOR WAS TESTED AND FOUND TO OPERATE CORRECTLY. ADDITIONALLY, THE ISOLATION VALVE WAS INSPECTED AND MAINTENANCE PERFORMED, WHICH INCLUDED GREASING, TESTING, CHECKING HYDRAULIC FLUIDS, A SIMULATED ACTIVATION, FOLLOWING PROCEDURES FOR INSPECTION, AND ENSURING COMPLETE OPERATION OF VALVE. ON JUNE 7, 2019 AT 11:45 CT, DELHI COMPRESSOR STATION WAS RETURNED TO SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190079 | 32461 | 2019-07-10 13:01 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2019-06-07 13:00 | 2019 |  |  | 39.9854 | -83.9189 | 1248488 | 2019-06-11 08:22 |  | NATURAL GAS |  | 361 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-06-11 16:45 | 2019-06-19 10:22 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-06-07 13:00 | 2019-06-07 13:00 | ONSHORE | OH | 45502 | SPRINGFIELD | CLARK | SURVEY STATION NO. | 00+50 | LINE Z-228 | Z-228-001 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | YES |  |  |  |  | YES | CASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 2.375 |  | 0.154 | 24000 | UNKNOWN | OTHER | UNKNOWN | UNKNOWN | NONE | [28 empty] | 1955 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 72 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 840 | 840 | 300000 | 306104.496179136 | 0 | 0 | 0 | 0 |  |  | 300840 | 141380.907016088 | 306944.496179136 | [8 empty] | 167 |  | 175 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 164 | NO | [5 empty] | YES | LINE Z-228 IS A 2.375- INCH DIAMETER PIPELINE. | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1959 | YES | YES | YES |  |  |  | 2019 |  |  |  | NO | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KAMRAN ROSTAMI ASRABADI | COMPLIANCE SPECIALIST | kamran_rostami@transcanada.com | (304)357-2351 |  |  |  |  | GEORGE HAMATY | US REGULATORY COMPLIANCE MANAGER EAST | (304) 357-3728 | george_hamaty@transcanada.com | ON JUNE 7, 2019, AT APPROXIMATELY 13:00 EASTERN STANDARD TIME (EST), A COLUMBIA GAS TRANSMISSION, LLC. (COLUMBIA) OPERATIONS PERSONNEL WAS PERFORMING NORMAL ROUTINE MAINTENANCE TASKS ON LINE Z-215 AND ASSOCIATED SIDE LINES. AT THE LAWRENCEVILLE MEASURING STATION, THE OPERATIONS PERSONNEL NOTICED A WEAK SMELL OF ODOR OF GAS. BASED ON THE LOCATION AND THE AMOUNT OF GAS, THE LEAK WAS GRADED AS A GRADE 2 LEAK. ON JUNE 10, 2019, OPERATIONS PERSONNEL CONDUCTED ADDITIONAL SURVEYS FOR FURTHER INVESTIGATIONS. AFTER EXPOSING THE PIPE, IT WAS DISCOVERED THAT NATURAL GAS WAS LEAKING FROM AN UNMAPPED CASING ON LINE Z-228 UNDER SHRINE ROAD. AT APPROXIMATELY 14:00 EST OPERATIONS TEAM DECIDED TO UPGRADE THE LEAK TO A GRADE 1 AND CONTINUED MONITORING THE LEAK THROUGH THE NIGHT. ON JUNE 11, 2019 AT APPROXIMATELY 08:00 EST AFTER ESTIMATING THE COST OF THE PIPELINE REPAIR, IT WAS DECIDED TO REPORT THIS EVENT TO THE NATIONAL RESPONSE CENTER AS AN INCIDENT DUE TO COST OF THE REPAIRS. PIPELINE Z-228 IS A 2.375-INCH IN DIAMETER WITH0.154-INCH WALL THICKNESS. IT IS 164-FEET LATERAL PIPELINE FROM LINE Z-215 LOCATED IN CLARK COUNTY ON 3735 SHRINE RD, SPRINGFIELD, OHIO. ON JUNE 11, 2019, AT 16:35 EST A COMPRESSED NATURAL GAS TANKER WAS CONNECTED AND STARTED FEEDING THROUGH LAWRENCEVILLE POINT OF DELIVERY TO CONTINUE DELIVERABILITY TO THE DOWNSTREAM TOWN. AT 16:45 LINE Z-228 WAS BLOWN DOWN. ON JUNE 13, 2019, THE CONSTRUCTION CREW WAS DISPATCHED TO THE SITE AND ON JUNE 14, 2019 THE CASING AND PIPE WERE REMOVED AND SENT TO A COLUMBIA STORAGE FACILITY. AFTER INVESTIGATION, IT WAS IDENTIFIED THE INCIDENT WAS CAUSED DUE TO EXTERNAL CORROSION PITTING. THE INITIAL NRC REPORT NO.1248488 AND THE NRC 48-HOUR REPORT NO. 1248650 HAVE BEEN CALLED-IN ON JUNE 11TH AND JUNE 12TH RESPECTIVELY.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190080 | 33002 | 2019-07-10 17:41 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2019-06-10 12:29 | 2019 |  |  | 32.4671 | -91.5975 | 1248420 | 2019-06-10 13:44 |  | NATURAL GAS |  | 5700 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-06-10 12:45 | 2019-06-14 15:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-06-10 12:29 | 2019-06-10 12:40 | ONSHORE | LA | 71232 | DELHI | RICHLAND | MILEPOST | MLV 13 | DELHI COMPRESSOR STATION | 8012501 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1956 |  | CARBON STEEL |  | OTHER | [8 empty] | MALFUNCTION OF EMERGENCY SHUTDOWN SYSTEM (ISOLATION VALVE FAILED TO CLOSE) | CLASS 1 LOCATION | NO |  | 788 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 13800 | 13800 | 2500 | 2550.8708014928 | 0 | 0 | 0 | 0 | NONE |  | 16300 | 15478.0036214595 | 16350.8708014928 | [8 empty] | 835 |  | 858 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER IDENTIFIED THE ISSUE VIA SCADA ALARMS AND INITIATED A CALL-OUT OF FIELD OPERATIONAL PERSONNEL, WHO IDENTIFIED THE INCIDENT AND TOOK CORRECTIVE ACTIONS. GAS CONTROL DOES NOT HAVE THE CAPABILITY TO REMOTELY CLOSE VALVES AND THEREFORE COULD NOT PREVENT THE INCIDENT THROUGH THEIR ACTIONS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [5 empty] | YES | [14 empty] | YES | [9 empty] | YES | VALVE FAILED TO CLOSE COMPLETELY | [161 empty] | ROGER STREET | COMPLIANCE SPECIALIST | roger_street@transcanada.com | 615-465-5123 |  |  |  |  | ERIK HUGHES | US REGUALTORY COMPLIANCE MANAGER - WEST | 402-492-7447 | erik_hughes@transcanada.com | ON JUNE 10 AT 12:29 CT, ANR PIPELINE'S GAS CONTROL RECEIVED AN EMERGENCY SHUTDOWN SYSTEM (ESD) ALARM AT DELHI COMPRESSOR STATION LOCATED AT 1984 HWY 80 W, DELHI, LA 71232 (32.46707, -91.59751). WHEN THE ALARM WAS DETECTED, A TECHNICIAN WAS DISPATCHED TO THE COMPRESSOR STATION TO INVESTIGATE. UPON ARRIVAL AT THE SITE AT 12:40 CT, THE TECHNICIAN DISCOVERED NATURAL GAS BEING RELEASED THROUGH THE STATION'S BLOWDOWN STACKS. IMMEDIATE ACTION WAS TAKEN BY VERIFYING NO EMERGENCY EXISTED AND CLOSING THE VALVES, WHICH ENDED THE RELEASE AT 12:45 CT. UNINTENTIONAL GAS LOSS WAS CALCULATED TO 5.7 MILLION CUBIC FEET (MMCF). NO PROPERTY DAMAGE OR INJURIES WERE DOCUMENTED AND NO EVACUATIONS WERE REQUIRED. THE CAUSE OF THE UNINTENTIONAL RELEASE WAS ATTRIBUTED TO A FLAME DETECTION EQUIPMENT (FIRE EYE) THAT INITIATED THE ACTIVATION OF THE ESD SYSTEM. WHEN THE SYSTEM ACTIVATED, STATION ISOLATION VALVE 501-14-16 FAILED TO FULLY CLOSE RESULTING IN THE RELEASE GAS. FOLLOWING THE INCIDENT, DELHI COMPRESSOR STATION WAS TAKEN OUT OF SERVICE DURING THE INVESTIGATION. VALVE 501-14-16 WAS LOCKED OUT OF SERVICE AND BY-PASSED TO ANOTHER ESD VALVE CAPABLE OF ISOLATING THE STATION. THE FLAME DETECTION EQUIPMENT WAS REMOVED FROM THE BUILDING AND REPLACED. DELHI COMPRESSOR STATION WAS PLACED BACK INTO SERVICE ON JUNE 10, 2019. THE COMPRESSOR ENGINE BUILDING WHERE THE SHUTDOWN WAS INITIATED REMAINED OUT OF SERVICE UNTIL JUNE 14 AT 15:45 CT. DURING THE SHUTDOWN PERIOD, NO ADDITIONAL FLAME DETECTION ACTIVATIONS WERE DETECTED. THE FLAME DETECTOR UNIT WAS SENT TO THE ORIGINAL MANUFACTURER FOR EVALUATION. THE MANUFACTURER REPORTED THAT THE UNIT MET ALL MANUFACTURING SPECIFICATIONS AND OPERATED AS INTENDED. THE MANUFACTURER RECOMMENDED THAT THE UNIT'S SENSITIVITY BE REDUCED FROM "HIGH" TO "MEDIUM". THIS RECOMMENDED CHANGE IS DUE TO THE OPERATIONAL AND ENVIRONMENTAL CONDITION IN THE RECIPROCATING ENGINE COMPRESSOR BUILDING. THE CHANGE IN SENSITIVITY DOES NOT AFFECT THE SAFETY OF THE PIPELINE FACILITY AND THE SYSTEM HAS BEEN TESTED ACCORDING TO PROCEDURES. THIS ACTION WAS COMPLETED ON JULY 26, 2019. ON 19 NOVEMBER 2019 INVESTIGATION AND REMEDIAL ACTION WAS TAKEN TO REPAIR VALVE 501-14-16, WHICH FAILED TO OPERATE FULLY CLOSED DURING A STATION ESD. THE 3-WAY PILOT VALVE, WHICH SENDS POWER GAS TO OPERATE THE VALVE WHEN PILOT PRESSURE DROPS OUT, WAS REPLACED. AN EXTRA POWER GAS BOTTLE WAS ALSO INSTALLED IN LINE WITH THE POWER GAS SUPPLY LINE TO ENSURE WE HAVE AN AMPLE AMOUNT OF POWER GAS TO FULLY STROKE THE VALVE. AN FULL EMERGENCY SHUTDOWN SYSTEM WAS CONDUCTED ON 11/19/2019 TO TEST REPAIRS ON VALVE 501-14-16. DURING THIS TEST, IT WAS DISCOVERED THAT PRESSURE TO THE POWER GAS SUPPLY ON THE ACTUATOR DROPPED OUT CAUSING THE VALVE TO NOT OPERATE. FURTHER INVESTIGATION REVEALED THAT THE PILOT GAS SUPPLY WAS INSTALLED INTO THE POWER GAS PORT AND THE POWER GAS SUPPLY WAS INSTALLED INTO THE PILOT GAS PORT ON THE OPERATOR. THE SWITCHING OF THESE SUPPLIES CAUSED AN INCOMPLETE OPERATION OF THE VALVE DUE TO RELIEVING PRESSURE OF THE PILOT GAS DURING AN ESD INITIATION. THESE LINES WERE SWITCHED TO THE CORRECT PORTS ON THE ACTUATOR AND PROPER OPERATION FOR VALVE CLOSURE WAS DOCUMENTED. VALVE 501-14-16 WAS PLACED BACK INTO SERVICE ON 22 NOVEMBER 2019.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190081 | 32413 | 2019-07-11 14:20 | ORIGINAL FINAL | 31978 | ATMOS PIPELINE - TEXAS | 5420 LBJ FREEWAY, SUITE 1500 | DALLAS | TX | 75240 | 2019-06-14 03:00 | 2019 |  |  | 32.27 | -95.2413 | 1248878 | 2019-06-14 09:50 |  | NATURAL GAS |  | 49 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-06-14 07:40 | 2019-06-19 21:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-06-14 07:20 | 2019-06-14 07:20 | ONSHORE | TX | 75791 | WHITEHOUSE | SMITH | MILEPOST | MLR-38 | S2-3-1 | MLR-38 BARBEE RD. | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | YES |  |  |  |  | YES | UNCASED | [16 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2009 |  | CARBON STEEL |  | OTHER | [8 empty] | VEHICLE RAN OVER 2-INCH VALVE CAUSING FLANGE LEAK | CLASS 2 LOCATION | NO |  | 29 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 161 | 161 | 90000 | 91831.3488537409 | 2000 | 2040.69664119424 | 3500 | 3571.21912208992 | CNG |  | 95661 | 44895.9456888353 | 97604.264617025 | [8 empty] | 240 |  | 300 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [260 empty] | BRUCE CAUGHRON | OPERATIONS SUPERVISOR | bruce.caughron@atmosenergy.com | 903-738-8122 | 903-242-4826 |  |  |  | MARLO SUTTON | VICE PRESIDENT TECHNICAL SERVICES | 214-206-2033 | marlo.sutton@atmosenergy.com | ADDITIONAL NRC REPORT # 1249008 A VEHICLE WAS TRAVELING SOUTHBOUND ON HWY 110 TOWARD WHITEHOUSE, TEXAS. THE DRIVER LEFT THE ROADWAY ONTO THE EAST SIDE OF HWY 110 WHILE STILL TRAVELING SOUTH. THE VEHICLE THEN TRAVELED THROUGH THE STATION FENCE DAMAGING A 2-INCH ABOVEGROUND VALVE. THE INCIDENT OCCURRED ON 6/14/19 AT APPROXIMATELY 03:00. ATMOS ENERGY WAS FIRST NOTIFIED BY THE FIRE DEPARTMENT AT 06:18. THE FIRE DEPARTMENT INITIALLY NOTIFIED CENTERPOINT ENERGY, WHO DETERMINED THAT THEY DID NOT OPERATE THE FACILITY. AN ATMOS ENERGY TECHNICIAN WAS THE FIRST RESPONDER AND ARRIVED AT APPROXIMATELY 07:20. THE EMERGENCY VALVE AT THE STATION WAS TURNED OFF AT APPROXIMATELY 07:40. AT APPROXIMATELY 09:30 ON 6/14/19, IT WAS DETERMINED THAT REPAIRS WOULD LIKELY EXCEED THE $50,000 THRESHOLD, AND THE TELEPHONIC REPORT TO THE NRC WAS MADE AT 09:50. CNG WAS UTILIZED TO MAINTAIN SERVICE UNTIL NECESSARY REPAIRS COULD BE MADE. THE LINE WAS PLACED BACK IN SERVICE AT 21:15 ON 06/19/19. POLICE ADVISED THERE WERE NO INJURIES.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190082 | 32430 | 2019-07-16 14:57 | SUPPLEMENTAL FINAL | 31613 | MIDCOAST PIPELINES (EAST TEXAS), L.P. | 1501 MCKINNEY SUITE 600 | HOUSTON | TX | 77010 | 2019-06-20 20:30 | 2019 |  |  | 30.6062 | -94.9401 | 1249587 | 2019-06-20 22:45 |  | NATURAL GAS |  | 17468 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-06-20 20:30 | 2019-06-21 18:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-06-20 20:30 | 2019-06-20 20:30 | ONSHORE | TX | 77335 | GOODRICH | POLK | MILEPOST | GOODRICH STA. | GOODRICH COMPRESSOR STATION | TXCG-36 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2007 |  | CARBON STEEL |  | LEAK |  |  | OTHER | COMPRESSOR BLOW DOWN | [5 empty] | CLASS 1 LOCATION | NO |  | 830 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 42500 | 42500 | 1795 | 1831.52523547183 | 682 | 695.877554647236 | 0 | 0 |  |  | 44977 | 45221.8243608455 | 45027.4027901191 | [8 empty] | 867 |  | 1050 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT DUE TO MECHANICAL MALFUNCTION. NO CONTROLLER INVOLVEMENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [7 empty] | YES |  |  | YES | [13 empty] | YES | [5 empty] | YES | [167 empty] | BENITA KALKA | GIS ANALYST | benita.kalka@midcoastenergy.com | 713-627-5723 |  |  |  |  | BENITA KALKA | GIS ANALYST | 713-627-5723 | benita.kalka@midcoastenergy.com | * INADEQUATE WARNING SYSTEM * TEMPERATURE EXTREMES AIR CONDITIONING FAILED WHICH CAUSED ELEVATED TEMPERATURES IN THE MCC. THE ELEVATED TEMPERATURES LEAD THE SHUTDOWN OF THE UPS. THE SHUTDOWN OF THE UPS (LOSS OF POWER) TRIGGERED THE ESD OF THE FACILITY. THE ELEVATED TEMPERATURES DID TRIGGER AN ALARM, BUT THIS ALARM WAS INACCURATELY LABELED IN THE MOST PROMINENT LOCATION. THE ALARM TAG WAS CORRECT BUT THE DESCRIPTION OF ALARM WAS WRONG. THIS GAVE OPERATIONS THE FALSE IMPRESSION OF A GENERATOR ISSUE WHICH WAS FOLLOWED UP ON AN NO ISSUES WERE FOUND. * INADEQUATE ENGINEERING * INADEQUATE OR IMPROPER CONTROLS DUE THE ESD VALVE SEQUENCE DESIGN, THE INLET AND STATION VALVES ACTUATED CLOSED AND THE BLOWDOWN VALVES ACTUATED OPEN. HOWEVER, THE OUTLET OUTLET VALVE (0201) FAILED TO SEAL CLOSED ALLOWING THE BLOWDOWN VALVES TO NOT ONLY DE-PRESSURE THE STATION BUT CONTINUE TO BLOWDOWN THE PIPELINE SYSTEM THAT SHOULD HAVE BEEN ISOLATED BY DESIGN. ACTIONS TAKEN TO DATE: 1) VALVE CONTRACTOR CHANGED OUT HYDRAULIC FLUID, ADJUSTED PRESSURES IN VALVE CHAMBERS, 2) CHANGED DESCRIPTION ON THE ALARM TAG IN SOFTWARE, 3) AS MENTION ABOVE THE ESD VALVE CLOSURE SEQUENCE HAS BEEN MODIFIED TO PRESENT BLOW DOWN VALVE FROM OPENING UNTIL INLET AND OUTLET VALVES ARE COMPLETELY CLOSED ON STATION. THIS SETUP WAS TESTED AND DOCUMENTED AS WORKING PROPERLY.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190083 | 32434 | 2019-07-18 10:51 | ORIGINAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2019-06-29 22:31 | 2019 |  |  | 39.6392 | -79.3394 | 1250551 | 2019-06-29 23:29 |  | NATURAL GAS |  | 3642 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-06-29 22:31 | 2019-06-30 07:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-06-29 22:31 | 2019-06-29 23:31 | ONSHORE | MD | 21520 | KAESE MILL | GARRETT | MILEPOST | 0 | ACCIDENT COMPRESSOR STATION | ACCI-UNIO | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | ESD SYSTEM | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | EMERGENCY SHUTDOWN OF COMPRESSOR STATION | CLASS 1 LOCATION | NO |  | 987 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 8413 | 8413 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 8413 | 8722.13910761155 | 8413 | [8 empty] | 2657 |  | 3550 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS DETERMINED THE CONTROLLERS ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. THE ESD WAS TRIGGERED BY A FIRE DETECTOR AND THIS EVENT COULD NOT BE ASSOCIATED WITH THE ROLES AND RESPONSIBILITIES OF A CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [52 empty] | LIGHTNING |  |  | DIRECT HIT |  |  | YES |  |  |  | YES | YES, THERE WAS A SEVERE STORM WITH AN EXTREME AMOUNT OF LIGHTNING ACTIVITY. | [301 empty] | MAYRA SALINAS | SENIOR ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: 48 HR NRC REPORT 1250679 AT APPROXIMATELY 10:31 PM EDT ON JUNE 29, 2019, AN EMERGENCY SHUTDOWN (ESD) WAS INADVERTENTLY ACTIVATED AT ACCIDENT COMPRESSOR STATION ON THE TEXAS EASTERN TRANSMISSION (TETLP) SYSTEM IN GARRETT COUNTY, MARYLAND. THE ESD OCCURRED DURING A SEVERE LIGHTENING STORM IN THE AREA. THE ESD WAS TRIGGERED BY A FIRE DETECTOR THAT DETECTED A FLAME SIGNATURE AS A RESULT OF THE SEVERE LIGHTING STORM. TETLP'S INVESTIGATION DETERMINED THAT THE ESD SYSTEM AND FIRE DETECTOR WERE FUNCTIONING AS DESIGNED AT THE TIME OF THE ESD. THE COMPRESSOR STATION WAS RETURNED TO NORMAL OPERATIONS AT APPROXIMATELY 7:30 AM EDT ON JUNE 30, 2019.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190084 | 33154 | 2019-07-19 12:53 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2019-06-21 09:28 | 2019 |  |  | 35.5553 | -109.7275 | 1249637 | 2019-06-21 11:22 |  | NATURAL GAS |  | 11628.6 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RESPONDING OPERATIONS PERSONNEL WERE ABLE TO MANUALLY CLOSE THE ESD VALVE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-06-21 09:28 | 2019-06-21 10:30 | ONSHORE | AZ | 86505 | Not Within a Municipality | APACHE | MILEPOST | C DISCHARGE | NAVAJO C/S DISCHARGE PIPING, C PLANT TO 1201 LINE | POWER GAS VALVE TO 1201 DISCHARGE VALVE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1993 |  | CARBON STEEL |  | OTHER | [8 empty] | GAS RELEASE THROUGH VENT VALVE | CLASS 1 LOCATION | NO |  | 602 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 18839 | 18839 | 0 | 0 | 180 | 183.662697707482 | 0 | 0 |  |  | 19019 | 19615.5527436847 | 19022.6626977075 | [8 empty] | 758 |  | 845 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS DEEMED THE INCIDENT WAS INDEPENDENT OF CONTROLLER ACTION. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [204 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE |  |  |  | YES |  | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | DANIEL GRANT | PIPELINE ENGINEER | daniel_grant@kindermorgan.com | 7134204409 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR OF COMPLIANCE CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | AT 9:28 AM (MST) EL PASO NATURAL GAS COMPANY, LLC (EPNG) NAVAJO COMPRESSOR STATION C PLANT EXPERIENCED AN EMERGENCY SHUTDOWN (ESD). EPNG GAS CONTROL DISPATCHED A TECHNICIAN TO THE NAVAJO COMPRESSOR STATION WHO ARRIVED AT 10:30 AM (MST). UPON ARRIVAL THE TECHNICIAN DISCOVERED GAS VENTING THROUGH A VENT VALVE. AT 10:32 AM (MST) THE TECHNICIAN PROCEEDED TO MANUALLY CLOSE THE DISCHARGE VALVE WHICH STOPPED THE UNINTENTIONAL RELEASE OF GAS. THE ACTIVATION OF THE ESD WAS DUE TO A FIRE EYE MALFUNCTION. UPON ACTIVATION OF THE ESD THE INLET AND DISCHARGE VALVES ARE DESIGNED TO TURN TO THE CLOSED POSITION AND THE GAS REMAINING IN THE PLANT IS VENTED TO ATMOSPHERE, HOWEVER IN THIS EVENT THE DISCHARGE VALVE DID NOT CLOSE. THE DISCHARGE VALVE IN THIS SYSTEM HAD UNDERGONE AN ESD MAINTENANCE TEST ON MARCH 6TH, 2019 AND THE VALVE HAD CLOSED AS DESIGNED. THE DISCHARGE VALVE IS ACTUATED WITH POWER GAS BUT DURING THE INVESTIGATION IT WAS FOUND THAT THE ASSOCIATED POWER GAS SUPPLY VALVE WAS IN THE CLOSED POSITION. CONSEQUENTLY, WHEN THE ESD SYSTEM WAS ACTIVATED THERE WAS NO POWER GAS FEEDING THE DISCHARGE VALVE ENABLING IT TO TURN TO THE CLOSED POSITION. THIS RESULTED IN THE DISCHARGE VALVE REMAINING OPEN ALLOWING GAS FROM THE DISCHARGE SIDE OF THE PLANT TO CONTINUE TO VENT. THE DISCHARGE VALVE REMAINED OPEN UNTIL IT WAS MANUALLY SHUT BY THE TECHNICIAN. THE 48-HR NRC INCIDENT REPORT NUMBER IS 1249752. THE CONFIRMED DISCOVERY TIME OF THE INCIDENT WAS 10:30 AM (MST).
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190085 | 32977 | 2019-07-25 10:29 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | ONE ENERGY PLAZA | DETROIT | MI | 48226 | 2019-06-30 10:20 | 2019 |  |  | 43.9578 | -86.1865 | 1250615 | 2019-07-01 12:28 |  | NATURAL GAS |  | 2186 | 2227 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-07-01 12:18 | 2019-07-04 12:25 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-06-30 10:20 | 2019-06-30 10:20 | ONSHORE | MI | 49405 | CUSTER | MASON | MILEPOST | MLV 4-5 | LOREED-LUDINGTON PIPELINE (16 INCH) | LOREED-LUDINGTON PIPELINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 72 |  | YES |  |  |  |  | YES | UNCASED | YES | UNCASED | HATTING CREEK | 6 | SHORELINE/BANK/MARSH CROSSING | [11 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.25 | 1625 | X52 | LONGITUDINAL ERW - HIGH FREQUENCY |  | STUPP | OTHER | TRENTON WAX COATING | [27 empty] | 1968 | 1968 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 334 |  | NO | NO | NO |  | 0 | 0 | 13362 | 13633.8942598187 | 13116 | 13116 | 97218 | 99196.2230318109 | 37985 | 38757.9309578816 | 27914 | 28482.003021148 | SEE PART H FOR DESCRIPTION |  | 189595 | 96254.8577674569 | 193186.051270659 | [8 empty] | 495 |  | 913 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | YES | NO | NOT MANDATED |  |  | REMOTELY CONTROLLED | REMOTELY CONTROLLED | 13 | NO | [5 empty] | YES | PIG TRAPS WERE NOT USABLE AS CONFIGURED. | YES |  |  |  |  | YES | DESIGN OF PIG TRAPS | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE VOLUME WAS NOT SIGNIFICANT ENOUGH TO SHOW ANY NOTICEABLE PRESSURE DECREASES OR FLOW INCREASES IN GAS CONTROL. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING | [6 empty] | YES | KIEFNER PERFORMED AN INVESTIGATION OF THE CAUSE OF THE LEAK. SEE PART H FOR THE SUMMARY AND CONCLUSIONS. |  |  | YES | YES |  |  | YES | YES | 1968 | YES | YES | YES |  |  |  | 2018 |  |  |  | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | CORRIE J. TOWNS | SUPERVISOR OF CODES AND STANDARDS | corrie.towns@dteenergy.com | 313-346-2896 |  |  |  |  | CORRIE TOWNS | SUPERVISOR OF CODES AND STANDARDS | 313-346-2896 | corrie.towns@dtenergy.com | A VERBAL NOTIFICATION REGARDING A LEAK ON THE 16' LOREED-LUDINGTON TRANSMISSION LINE FOR DTE GAS WAS MADE TO THE MPSC AND NRC. THE LEAK WAS FOUND BY A LANDOWNER AND THE DTE CREW WAS DISPATCHED AT 10:20 PM ON 6/30/2019. DTE GAS LOWERED THE PRESSURE OF THE LINE AS OF 12:18 AM ON 7/1/2019 AND PRESSURE CONTROL PROCEDURE AND A REPAIR PLAN ARE BEING DEVELOPED. APPROXIMATELY 5.5 FEET SECTION WAS REPLACED AND THE PIPE SECTION IS UNDERGOING A FAILURE INVESTIGATION BY A THIRD PARTY LABORATORY. MPSC, JIM JOHNSON, WAS NOTIFIED AT 12:30 AM AND WE HAD A FOLLOW-UP DISCUSSION AT APPROXIMATELY 12:53 AM. THE NRC WAS NOTIFIED AT 12:28 AM AND THE INCIDENT NUMBER IS 1250615. THE LINE WAS RETURNED TO SERVICE ON 7/4/2019. KIEFNER PERFORMED AN INVESTIGATION OF THE CAUSE OF THE LEAK. THE REPORT WAS DATED AUGUST 29, 2019. THE SUMMARY AND CONCLUSION OF THE REPORT STATED "THE LEAK THAT OCCURRED ON THE LOREED-LUDINGTON PIPELINE IN THE MLV 4-5 VALVE SECTION ON JUNE 30, 2019 WAS LIKELY CAUSED BY CORROSION WHICH THINNED THE PIPE WALL THICKNESS TO THE POINT THAT THE REMAINING LIGAMENT WAS UNABLE TO SUPPORT THE STRESS INDUCED BY THE INTERNAL PRESSURE. THE FAILURE OF THE PIPE WALL WAS BY DUCTILE TEARING AND THE APPEARANCE OF A CRACK-LIKE FEATURE WAS CAUSED BY THE LOCALIZED NECKING OF THE MATERIAL JUST PRIOR TO TEARING. AN AREA OF COATING DAMAGE AND DISBONDMENT, WHICH CAUSED CATHODIC SHIELDING OF THE PIPE MATERIAL, LIKELY ENABLED THE CORROSION TO OCCUR. THE PRESENCE OF A TWO PART FULL-ENCIRCLEMENT SWAMP WEIGHT OVER THE LEAK LOCATION LIKELY CONTRIBUTED TO THE CONDITIONS WHICH WOULD BE NECESSARY FOR DISBANDED COATING TO SHIELD THE PIPE MATERIAL. THE TYPE OF CORROSION THAT OCCURRED AT THIS LOCATION CAN BE DESCRIBED AS 'UNDER DEPOSIT ACID ATTACK.' HOWEVER, THE EXACT CAUSE OF THE CORROSION WAS NOT IDENTIFIED. AN ANALYSIS OF THE CORROSION PRODUCTS FOR THE PRESENCE OF BACTERIA FOUND A LOW PRESENCE OF COMMON BACTERIA ASSOCIATED WITH PIPELINE CORROSION. PART D7.D ESTIMATED OTHER COSTS DESCIPTION: LUMPED COST OF FLEET, FACILITY, TRAVEL/MILEAGE, AND HOTEL COSTS FOR EVERYONE THAT WAS DEPLOYED ON SITE FOR THE WEEK OF THE INCIDENT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190086 | 32476 | 2019-07-26 11:33 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-06-28 00:22 | 2019 |  |  | 30.3202 | -95.1591 | 1250361 | 2019-06-28 01:25 |  | NATURAL GAS |  | 137143 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-06-28 00:49 | 2019-06-28 03:35 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-06-28 00:49 | 2019-06-28 00:49 | ONSHORE | TX | 77328 | Not Within a Municipality | MONTGOMERY | SURVEY STATION NO. | 485 | LINE 100-1 | VALVE SEGMENT 100-25-1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2016 |  | CARBON STEEL |  | OTHER | [8 empty] | DURING STATION ESD, VALVE BS-2 DID NOT CLOSE PROPERLY BECAUSE OF MALFUNCTION OF REGULATOR ON POWER GAS SUPPLY TO THE VALVE OPERATOR; | CLASS 1 LOCATION | NO |  | 496 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 338524 | 338524 | 1000 | 1020.34832059712 | 2800 | 2856.97529767194 | 5050 | 5152.75901901546 | INVESTIGATION; |  | 347374 | 355108.248305531 | 347554.082637285 | [8 empty] | 735 |  | 750 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DURING STATION ESD, VALVE BS-2 DID NOT CLOSE PROPERLY BECAUSE OF MALFUNCTION OF REGULATOR ON POWER GAS SUPPLY TO THE VALVE OPERATOR; | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [25 empty] | YES | TRASH IN REGULATOR OF POWER SUPPLY GAS TO VALVE OPERATOR; | [161 empty] | WILLIAM MARTIN MULLER | SPECIALIST-PIPELINE TECHNICAL | martiin_muller@kindermorgan.com | 205-325-3863 | 205-325-3508 |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | AT 00:22-HOUR AN EMERGENCY SHUTDOWN (ESD) OCCURRED AT STATION 25. PROPER NOTIFICATIONS WERE MADE AND ON-CALL EMPLOYEES ARRIVED ON SITE AT 00:49-HOUR AND FOUND GAS VENTING THEREBY CONFIRMING THE EVENT. EMPLOYEES CLOSED THE NECESSARY VALVES TERMINATING THE RELEASE OF NATURAL GAS. AN INVESTIGATION OF THE EVENT PROMPTLY BEGAN. A FAULTY MODULE IN THE PLC WAS DISCOVERED WHICH INITIATED THE ESD. THE MODULE WAS REPLACED POST-INCIDENT. ALSO IT WAS ALSO DETERMINED THE POWER GAS REGULATOR TO THE OPERATOR OF VALVE BS-2 HAD MALFUNCTIONED CAUSING THE VALVE TO REMAIN OPEN INSTEAD OF CLOSING PROPERLY FOR THE ESD. TRASH WAS FOUND IN THE POWER GAS REGULATOR CAUSING IT TO MALFUNCTION. THE POWER GAS REGULATOR WAS REPLACED POST-INCIDENT. ALL REGULATORS INVOLVING POWER GAS TO VALVE OPERATORS IN THE ESD SYSTEM AND THE ESD VALVES WERE INSPECTED POST-INCIDENT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190087 | 32863 | 2019-07-29 12:54 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-06-29 11:40 | 2019 |  |  | 36.3459 | -86.8682 | 1250516 | 2019-06-29 13:34 |  | NATURAL GAS |  | 3588 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-07-05 14:40 | 2019-07-10 11:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-06-29 11:40 | 2019-06-29 12:20 | ONSHORE | TN | 37080 | Not Within a Municipality | DAVIDSON | SURVEY STATION NO. | 1322 | LINE 500-1 | VALVE SEGMENT 563-1-1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | ESD SYSTEM; | 2018 |  | CARBON STEEL |  | OTHER | [8 empty] | ESD ACTIVATION; | CLASS 2 LOCATION | NO |  | 760 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 8857 | 8857 | 21320 | 21753.8261951306 | 3000 | 3061.04496179136 | 5000 | 5101.74160298561 | INVESTIGATION; |  | 38177 | 22914.9687296952 | 38773.6127599076 | [8 empty] | 814 |  | 936 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ALL CONTROL ROOM MANAGEMENT PROCESSES WERE FOLLOWED; | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [7 empty] | YES | [16 empty] | YES | [10 empty] | YES | UPS SYSTEM BATTERIES; | [161 empty] | WILLIAM MARTIN MULLER | SPECIALIST-PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205-325-3863 | 205-325-3592 |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | ON 06/29/2019 AT 11:40-HOURS, THE TGP ON-CALL EMPLOYEE RESPONDED TO A GAS CONTROL CALL OUT CONCERNING A POSSIBLE ESD AT TGP STATION #563, JOELTON, TN. THE EMPLOYEE ARRIVED ON SITE AT APPROXIMATELY 12:20-HOURS AND PROCEEDED TO VERIFY SYSTEM STATUS. AT 12:45-HOURS, THE EMPLOYEE DISCUSSED WITH SUPERVISION AND CONFIRMED THE FACILITY ESD HAD OCCURRED WITH ALL VALVES WORKING AS DESIGNED. AT 13:00 HOURS, OPERATIONS ESTIMATED THE GAS LOSS FOR THE EVENT TO BE 4,005 MCF AND WAS REPORTED AS NRC #1250516 ON 06/29/2019 AT 13:34-HOURS. ENGINEERING PROVIDED REVISED ESTIMATED GAS LOSS ON 07/12/2019 AS 3,588 MCF. INVESTIGATION FOUND THERE WAS A MOMENTARY LOSS OF COMMERCIAL POWER AND THE STATION UPS SYSTEM DID NOT HOLD THE REQUIRED COMPRESSOR STATION VOLTAGE (120 VDC) IN THE INTERIM WHILE THE EMERGENCY GENERATOR WAS RAMPING UP TO COME ON-LINE. THIS INTERIM LACK OF VOLTAGE TRIGGERED THE COMPRESSOR STATION ESD. THE INVESTIGATION IDENTIFIED TWO BATTERIES IN THE UPS SYSTEM HAD IMPROPERLY DRAINED POWER. FURTHER INVESTIGATION FOUND SAID BATTERIES HAD NOT BEEN STORED AND MAINTAINED CORRECTLY DURING COMPRESSOR STATION CONSTRUCTION PRIOR TO OCTOBER, 2018. THE FAULTY BATTERIES WERE REPLACED. THE REPAIRS ALSO INCLUDED REPLACING SOME WIRING, FUSES, BREAKERS AND BATTERY CHARGERS. THE INVESTIGATION ALSO FOUND PREVIOUS AUTOMATION PROGRAMMING IN MAY, 2019 HAD INADVERTENTLY DISABLED AN ALARM CONCERNING ELECTRICAL POWER STATUS; SAID ALARM HAS BEEN REESTABLISHED. DURING THE INVESTIGATION AND REPAIR TIME PERIOD, THE STATION WAS IN MANNED OPERATION WITH THE EXCEPTION OF JULY 5, 2019, 14:40-HOURS TO JULY 10, 2019, 11:00-HOURS. JULY 5, 2019, INCLEMENT WEATHER IN THE AREA CAUSED ANOTHER LOSS OF COMMERCIAL POWER AND STATION ESD INCIDENT. (REFERENCE DOT REPORT #2019092) OPERATIONS KEPT THE STATION OFF LINE FOLLOWING THE JULY 5, 2019 INCIDENT UNTIL JULY 10, 2019 FOR CERTAIN TASKS RELATED TO BOTH INCIDENTS TO OCCUR. THE STATION THEN RESUMED MANNED OPERATION UNTIL OCTOBER 3, 2019, AT APPROXIMATELY 18:00-HOURS WHEN ALL REPAIRS FOR THE JUNE 29, 2019 INCIDENT WERE COMPLETED AND THE STATION RETURNED TO AUTOMATED OPERATION. THE 48-HOUR UPDATE IS NRC REPORT #1250639.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190088 | 32480 | 2019-07-30 10:25 | ORIGINAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2019-07-10 07:00 | 2019 |  |  | 35.7699 | -91.6 | 1251484 | 2019-07-10 07:12 |  | NATURAL GAS |  | 3667 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | STOPPLES WERE INSTALLED. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-07-04 10:30 | 2019-07-04 07:00 | ONSHORE | AR | 72501 | BATESVILLE | INDEPENDENCE | MILEPOST | 1408+92 | JM-7 | JM-7 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION | [19 empty] | FILLET WELD | [18 empty] | 1977 |  | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | NO |  | 148 |  | NO | NO | NO |  | 2000 | 2040.69664119424 | 0 | 0 | 9000 | 9000 | 137200 | 139991.789585925 | 0 | 0 | 14000 | 14284.8764883597 | MISCELLANEOUS, FUEL, OVERHEAD |  | 162200 | 81084.5028679216 | 165317.362715479 | [8 empty] | 606 |  | 720 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL |  | NO | YES | YES |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS DISCOVERED DURING A DIRECT ASSESSMENT DIG. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [8 empty] | YES | LEAKING WELD | [13 empty] | YES | [62 empty] | NO | [63 empty] | NO |  |  | Yes, and an investigative dig was cunducted at the point of the Accident | 2019 | [12 empty] | NO | [63 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | DURING AN IM ECDA DIG ON 7/4/2019, TWO SMALL PIN HOLE LEAKS WERE FOUND IN A FILLET WELD ON LINE JM-7 AT THE BATESVILLE TB #2 TAP. A 20% PRESSURE REDUCTION WAS IMPLEMENTED, AND THIS LEAK WAS TREATED AS A SAFETY RELATED CONDITION. THE MAOP OF JM-7 IS 720 PSIG AND THE DISCOVERY PRESSURE WAS 606 PSIG. THE LINE WAS RESTRICTED IN THIS AREA TO 485 PSIG UNTIL REPAIRS WERE COMPLETED. JM-7 IS A PREDOMINANTLY 8" PIPELINE AND OPERATES AT 40% SMYS AT THIS LOCATION. THIS IS A CLASS 3 SEGMENT, AND THE LEAK WAS LOCATED ON COMPANY PROPERTY IN INDEPENDENCE COUNTY, AR. THE LEAKS WERE TREATED AS AN SRC UNTIL THE MORNING OF 7/10/2019 WHEN IT WAS DETERMINED THE PLAN OF REPAIR WOULD EXCEED $50,000. A CALL WAS PLACED TO THE NRC (NRC# 1251484) ON 7/10/2019 @ 07:12. A 48 HR. FOLLOW UP TO THE NRC (NRC# 1251686) WAS PLACED ON 7/12/2019 @ 06:52. THE LINE WAS REPAIRED WITHOUT INTERRUPTING SERVICE BY INSTALLING TWO STOPPLES AND A BYPASS. IN BETWEEN THE STOPPLES, AROUND 20 FEET OF PIPE WAS REPLACED ELIMINATING THE LEAK. THE REPAIR JOB WAS COMPLETED ON 7/18/19 AND THE LINE WAS RETURNED TO REGULAR SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190089 | 32762 | 2019-07-30 17:20 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2019-06-30 08:58 | 2019 |  |  | 30.466 | -92.5223 | 1250564 | 2019-06-30 10:31 |  | NATURAL GAS |  | 99000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-06-30 09:43 | 2019-06-30 11:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-06-30 08:58 | 2019-06-30 09:35 | ONSHORE | LA | 70535 | EUNICE | ACADIA | MILEPOST | 501 MP 0 | EUNICE COMPRESSOR STATION | 8001501 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | EMERGENCY SHUTDOWN SYSTEM | 1973 |  | CARBON STEEL |  | OTHER | [8 empty] | EMERGENCY SHUTDOWN SYSTEM MALFUNCTION | CLASS 1 LOCATION | NO |  | 788 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 230000 | 230000 | 75000 | 76526.1240447841 | 1000 | 1020.34832059712 | 0 | 0 | NONE |  | 306000 | 274047.320591057 | 307546.472365381 | [8 empty] | 602 |  | 975 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE OPERATOR IDENTIFIED THE ALARM AND FOLLOWED THE PROCEDURES TO INITIATE AN INVESTIGATION. FIELD PERSONNEL WAS DISPATCHED TO THE SITE AND RESPONDED TO THE LOCATION OF THE ALARM. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | YES |  |  | YES | [5 empty] | YES | [19 empty] | YES | [167 empty] | ROGER STREET | COMPLIANCE SPECIALIST | roger_street@transcanada.com | 615-465-5123 |  |  |  |  | ERIK HUGHES | US REGUALTORY COMPLIANCE MANAGER - WEST | 402-492-7447 | erik_hughes@transcanada.com | ON JUNE 30 AT 08:58 CDT, ANR PIPELINE'S GAS CONTROL RECEIVED AN EMERGENCY SHUTDOWN SYSTEM (ESD) FIRE ALARM AT EUNICE COMPRESSOR STATION LOCATED AT 4202 FOURNERAT ROAD, EUNICE, LA 70535 (30.465980, - 92.522270). WHEN THE ALARM WAS DETECTED, A TECHNICIAN WAS DISPATCHED TO THE COMPRESSOR STATION TO INVESTIGATE. UPON ARRIVAL AT THE SITE AT 09:35 CDT, THE TECHNICIAN DISCOVERED NATURAL GAS BEING RELEASED TO THE ATMOSPHERE THROUGH THE VENT STACKS. IMMEDIATE ACTION WAS TAKEN BY VERIFYING NO FIRE EXISTED AND CLOSING THE VALVES OPEN TO ATMOSPHERE, WHICH ENDED THE RELEASE AT 09:43 CDT. UNINTENTIONAL GAS LOSS WAS CALCULATED TO 99 MILLION CUBIC FEET (MMCF). NO PROPERTY DAMAGE OR INJURIES WERE DOCUMENTED, AND NO MANDATORY EVACUATIONS WERE REQUIRED. THE CAUSE OF THE UNINTENTIONAL RELEASE HAS BEEN ATTRIBUTED TO A FLAME DETECTION EQUIPMENT (FIRE EYE) ACTIVATION THAT INITIATED THE EMERGENCY SHUTDOWN (ESD) SYSTEM. WHEN THE SYSTEM INITIATED, SEVEN ESD VALVES DID NOT FULLY OPERATE ALLOWING GAS TO CONTINUE TO VENT UNTIL PERSONNEL ARRIVED ON SITE AND ISOLATED THE SYSTEM. NO INDICATION OF FIRE WAS OBSERVED IN THE COMPRESSOR BUILDING. THE FLAME DETECTOR UNIT WAS SENT TO THE ORIGINAL MANUFACTURER FOR EVALUATION. THE MANUFACTURER REPORTED THAT THE DETECTION UNIT MET ALL MANUFACTURING SPECIFICATIONS AND OPERATED AS INTENDED. THE MANUFACTURER ALSO RECOMMENDED THAT THE UNIT'S SENSITIVITY BE REDUCED FROM "HIGH" TO "MEDIUM" AND INCREASE THE ACTIVATION DELAY FROM 8 SECONDS TO 10 SECONDS. THESE RECOMMENDED CHANGES ARE DUE TO THE OPERATIONAL AND ENVIRONMENTAL CONDITION IN THE RECIPROCATING ENGINE COMPRESSOR BUILDING. THE CHANGE IN SENSITIVITY AND TIMING DOES NOT AFFECT THE SAFETY OF THE PIPELINE FACILITY AND THE SYSTEM HAS BEEN TESTED ACCORDING TO PROCEDURES. THE CHANGES TO THE FLAME DETECTION EQUIPMENT WAS COMPLETED ON 26 JULY 2019. INVESTIGATION INTO ESD VALVES DETERMINED THAT PILOT GAS WAS NOT VENTED COMPLETELY UPON AUTOMATIC ACTIVATION. EVEN THOUGH THE ESD SYSTEM HAD ACTIVATED AND STARTED TO VENT PILOT GAS, PRESSURES THROUGH THE SUPPLY LINE MAINTAINED ENOUGH PRESSURE TO PREVENT THE VALVES FROM FULLY MOVING TO THE CLOSED POSITION. TO REDUCE THE PILOT GAS SUPPLY, A SMALLER 1/32" ORIFICE PLATE WAS INSTALLED INTO THE SUPPLY LINE ON AUGUST 14, 2019, REDUCING THE FLOW OF GAS AND RECHARGE TIME INTO THE SUPPLY SYSTEM. THE PURPOSE OF THE ORIFICE IS TO MAINTAIN PILOT GAS PRESSURE IN THE EVENT OF A MINOR LEAK TO PREVENT AN UNINTENDED ESD. THE ESD SYSTEM HAS BEEN INSPECTED AND TESTED ACCORDING TO PROCEDURES SINCE THE ORIFICE REPLACEMENT AND OPERATED CORRECTLY. THE SYSTEM HAS BEEN PLACED BACK INTO FULL SERVICE. IN ADDITION TO THE ORIFICE CHANGE, FIVE EMERGENCY VALVES WILL BE UPGRADED WITH NEW THREE-WAY PILOT VALVE ASSEMBLIES AND THE END-OF-STROKE VALVE ON TWO OTHER VALVES WILL BE REPLACED, WHICH WILL ENSURE PROPER OPERATION OF THE VALVES. THE ADDITIONAL UPGRADES TO THE VALVES ARE ANTICIPATED TO BE COMPLETED WITHIN 120 DAYS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190090 | 33322 | 2019-07-31 13:50 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2019-07-09 12:43 | 2019 | EASTERN | NO | 38.5762 | -83.4674 | 1251442 | 2019-07-09 16:23 | 1251614 | NATURAL GAS |  | 10969.5 | 59 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | COMPRESSED NATURAL GAS WAS USED TO MAINTAIN SERVICE TO CUSTOMERS |  |  |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-07-11 15:30 | VALVE CLOSURE |  | 2019-07-11 19:15 | 0 | 2019-07-09 12:42 | 2019-07-09 15:58 | ONSHORE | KY | 41179 | VANCEBURG | LEWIS | SURVEY STATION NO. | 3876+89 | EM122 | FLOC NUMBER 026298 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 30 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 | NO | 0.188 | 42000 | X42 | OTHER | UNKNOWN | UNKNOWN | EXTRUDED POLYEHYLENE |  | NO | [26 empty] | 1995 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 2 | 0.5 | [7 empty] | CLASS 1 LOCATION | NO |  | 123 |  | NO | NO |  |  | 0 | 0 | 137 | 139.787719921806 | 25449 | 25449 | 286740 | 292574.677448018 | 1000 | 1020.34832059712 | 0 | 0 |  | 2.32 | 313326 | 161216.163980891 | 319183.813488537 | 0 | 0 | 0 | 0 | NO |  |  |  | 450 | 336 | 720 | 192.619(A)(1) |  | 1986-05-16 | NO | PRESSURE DID NOT EXCEED MAOP | YES | NO | NOT MANDATED | NO | YES | MANUAL | MANUAL | 64200 | NO | YES |  |  | YES |  |  |  | YES |  |  | YES |  | YES | SINGLE GAS SUPPLY | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | OTHER | OUR OPERATING PERSONNEL WAS FIRST NOTIFIED BY LOCAL DISTRIBUTION PERSONEL |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO THE INCIDENT DID NOT OCCUR DUE TO CONTROL ROOM OR SUPERVISORY PERSONNEL ACTIONS. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | STORM DRAIN/CULVERT | NO | [7 empty] | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | MARK NEWMAN | REGIONAL COMPLIANCE SPECIALIST | mark_newman@transcanada.com | 304-722-8475 | 304-722-8420 |  |  |  | GEORGE HAMATY | MANAGER EAST US REGULATORY COMPLIANCE | 304-357-3782 | george_hamaty@transcanada.com | ON 7/9/2019 A CONTRACTOR WAS WORKING FOR THE LANDOWNER TO INSTALL A NEW CULVERT AT THE SAME LOCATION AS AN EXISTING CULVERT. DURING THE EXCAVATION THE CONTRACTOR CAME IN CONTACT WITH PIPELINE OPERATOR COLUMBIA GAS TRANSMISSION, LLC (OPID 2616), COLUMBIA, PIPELINE EM-122. PRESSURE ON EM-122 WAS REDUCED FROM 450 PSIG TO ABOUT 100 PSIG IN ORDER TO MAINTAIN MARKET REQUIREMENTS UNTIL COMPRESSED NATURAL GAS (CNG) TRUCKS COULD BE USED AS AN ALTERNATE SUPPLY WHILE REPAIRS WERE MADE. APPROXIMATELY 9 COMPRESSED TANKERS MAINTAINED THE VANCEBURG MARKET THROUGHOUT THE PIPELINE REPAIR. THE CONTRACTOR WAS USING AN EXCAVATOR (KOBELCO 135SR) TO INSTALL THE NEW CULVERT. THE LANDOWNER ACKNOWLEDGE THAT A CALL WAS NOT MADE TO KY811. COLUMBIA HAS VERIFIED THAT A LOCATE REQUEST FOR THIS LOCATION WAS NOT MADE FOR THE DATE OF THIS INCIDENT. ON 7/9/2019 COLUMBIA LOWERED THE PIPELINE PRESSURE TO 100 PSIG, AND PROVIDE ONSITE MONITORING A CONTROLLED LEAK 24/7 UNTIL MATERIALS AND EQUIPMENT WERE AVAILABLE TO MAKE REPAIRS. LINE EM-122 IS LOCATED IN A CLASS 1 LOCATION. THE CLOSEST HABITABLE RESIDENTS ARE APPROXIMATELY 500 FEET AWAY AND WERE MADE AWARE OF THE INCIDENT AND MAINTAINED COMMUNICATION DURING REPAIR OPERATIONS. ON 7/11/2019 CNG WAS PLACED INTO SERVICE TO VANCEBURG MARKET. LINE EM-122 WAS SHUT IN AND BLOWDOWN. NO MARKET CUSTOMERS WERE AFFECTED, BUT APPROXIMATELY 14 FARM TAPS WERE SHUT IN DURING PIPELINE REPAIRS. ON 7/13/2019, FINAL REPAIRS WERE MADE USING PRETESTED 6.625' OD, 0.188 WALL, MAOP OF 720 PSIG PIPE. CNG HAS DISCONNECTED FROM THE VANCEBURG MARKET. THE PIPELINE WAS PURGED AND PLACE INTO SERVICE ON 7/11/2019. COLUMBIA DID INVESTIGATE PUBLIC AWARENESS RECORDS AND DETERMINED THAT THE LANDOWNER HAS RECEIVED PAST INFORMATION FROM ITS MAILING PROGRAM THAT INCLUDED A REMINDER TO CALL BEFORE YOU DIG.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20190091 | 32652 | 2019-08-01 22:30 | SUPPLEMENTAL FINAL | 39352 | GENESIS OFFSHORE HOLDINGS, LLC | 919 MILAM STREET SUITE 2100 | HOUSTON | TX | 77002 | 2019-07-05 15:30 | 2019 |  |  | 27.9428 | -94.3892 | 1251095 | 2019-07-05 17:55 |  | NATURAL GAS |  | 5225 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-07-05 18:00 | 2019-08-22 12:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-07-05 17:13 | 2019-07-05 18:00 | OFFSHORE | [28 empty] | 350 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | HIA | 582 | BELOW WATER, PIPE ON OR ABOVE SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 30 |  | 0.5 | 60000 | 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | ITALSIDER | ASPHALT | [28 empty] | 1977 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 143 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 12018 | 12018 | 750000 | 765261.240447841 | 250000 | 255087.08014928 | 0 | 0 |  |  | 1012018 | 480826.409213732 | 1032366.32059712 | [8 empty] | 745 |  | 1440 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 24 | NO | YES | [6 empty] | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS SUB-SEA AND NO CONTROLLER'S ACTIONS WERE RELATED. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | NO | [11 empty] | YES | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | JORGE MORICE | PIPELINE COMPLIANCE SPECIALIST | jorge.morice@genlp.com | 7137251663 |  |  |  |  | JOHN JEWETT | DOT COMPLIANCE AND FACILITY SECURITY MANAGER | 7138602605 | john.jewett@genlp.com | ON 7/5/19, A GENESIS EMPLOYEE RECEIVED A CALL AT 15:30 HOURS OF A SUSPECTED LEAK IN THE HIA 582 AREA. DURING A HELICOPTER OVERFLIGHT, THE GENESIS EMPLOYEE OBSERVED SOME BUBBLING IN THE WATER AND A BARELY VISIBLE SHEEN (500 FT. BY 20FT.) AT THE REPORTED COORDINATES. THE LEGS OF THE PIPELINE WERE SHUT IN AS GENESIS CONTINUED TO MONITOR. A DIVE BOAT AND CREW WAS CALLED IN TO INVESTIGATE. WHEN THE DIVE CREW ARRIVED TO INSPECT THE PIPELINE, THEY NOTICED HOLE WITH AN APPROXIMATE DIAMETER OF 1/8 IN.. AT THE TIME, HOWEVER, VISIBILITY ON THE SEA FLOOR WAS VERY POOR MAKING ANY FURTHER DETERMINATION OF THE EXACT CAUSE DIFFICULT TO COMPLETE. THE PIPELINE WILL CONTINUE TO BE SHUT IN UNTIL A SEPARATE DIVE BOAT ARRIVES MID TO LATE AUGUST TO FURTHER ASSESS THE CAUSE OF THE LEAK AND THEN REPAIR THE PIPELINE. SUPPLEMENTAL REPORT (9/03/2019): ON 8/22/19 A DIVE TEAM REPAIRED PIPE WITH 30" PLEDCO CLAMP. THE PIPELINE WAS PRESSURED TO 1000 PSI WITH NO LEAKAGE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190092 | 32862 | 2019-08-02 12:25 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-07-05 14:40 | 2019 |  |  | 36.3459 | -86.8682 | 1251077 | 2019-07-05 15:25 |  | NATURAL GAS |  | 3506 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-07-05 14:40 | 2019-07-10 11:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-07-05 14:40 | 2019-07-05 14:40 | ONSHORE | TN | 37080 | Not Within a Municipality | DAVIDSON | SURVEY STATION NO. | 1322 | LINE 500-1 | VALVE SEGMENT 563-1-1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | ESD SYSTEM; | 2018 |  | CARBON STEEL |  | OTHER | [8 empty] | ESD ACTIVATION; | CLASS 2 LOCATION | NO |  | 760 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 8655 | 8655 | 0 | 0 | 600 | 612.208992358273 | 0 | 0 |  |  | 9255 | 9254.0515778117 | 9267.20899235827 | [8 empty] | 848 |  | 936 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ALL CONTROL ROOM MANAGEMENT PROCESSES WERE FOLLOWED; | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [7 empty] | YES | [16 empty] | YES | [10 empty] | YES | UPS SYSTEM BATTERIES; | [161 empty] | WILLIAM MARTIN MULLER | SPECIALIST-PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205-325-3863 | 205-325-3592 |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | THE STATION WAS IN MANNED OPERATION AS INVESTIGATION CONTINUED FROM AN ESD EVENT ON JUNE 29, 2019. (REFERENCE DOT REPORT #2019087) INCLEMENT WEATHER INCLUDING LIGHTNING ACTIVITY IN THE AREA CAUSED A MOMENTARY LOSS OF COMMERCIAL POWER. A COMPRESSOR STATION EMERGENCY SHUTDOWN (ESD) WAS INITIATED. THE INTERLOCKING COMPRESSOR STATION ESD FUNCTIONED AS DESIGNED RESULTING IN A PHMSA REPORTABLE GAS LOSS OF 3,506 MCF. OPERATIONS PERSONNEL WERE ON SITE DURING THE EVENT AND CONFIRMED A LOUD POP DUE TO LIGHTNING ACTIVITY. INVESTIGATION RESOURCES INCLUDING DIVISION CONTROLS SUPPORT, HOUSTON AUTOMATION AND OPERATIONS CONFIRMED LOCAL INCLEMENT WEATHER CAUSED THE LOSS OF COMMERCIAL POWER, AND THE STATION UPS SYSTEM DID NOT HOLD THE REQUIRED COMPRESSOR STATION VOLTAGE (120 VDC) IN THE INTERIM WHILE THE EMERGENCY GENERATOR WAS RAMPING UP TO COME ON-LINE. THIS INTERIM LACK OF VOLTAGE TRIGGERED THE COMPRESSOR STATION ESD. INVESTIGATION OF THIS EVENT AND INVESTIGATION AND REPAIRS CONCERNING THE JUNE 29, 2019 INCIDENT CONTINUED WITH THE STATION HELD OFF LINE BY OPERATIONS TO ALLOW CERTAIN TASKS TO OCCUR UNTIL JULY 10, 2019 AT 11:00-HOURS WHEN THE STATION RESUMED MANNED OPERATION. ON-SITE PERSONNEL WERE UNABLE TO LOCATE ANY DIRECT LIGHTNING STRIKE TO THE FACILITIES. NO DAMAGE BY THIS LIGHTNING EVENT AND INCLEMENT WEATHER WAS IDENTIFIED. THE STATION REMAINED IN MANNED OPERATION UNTIL OCTOBER 3, 2019, AT APPROXIMATELY 18:00-HOURS WHEN ALL REPAIRS FOR THE JUNE 29, 2019 INCIDENT WERE COMPLETED AND THE STATION RETURNED TO AUTOMATED OPERATION. NRC 48-HOUR UPDATE IS REPORT #1251213.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190093 | 32525 | 2019-08-07 16:34 | ORIGINAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2019-07-08 15:35 | 2019 |  |  | 28.3781 | -92.7564 | 1251360 | 2019-07-08 19:24 |  | NATURAL GAS |  | 571 | 22638 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-07-08 19:00 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-07-20 19:10 | 2019-07-20 19:10 | OFFSHORE | [28 empty] | 180 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EAST CAMERON | 286 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 |  | 0.375 | 52000 | API-5LX | SEAMLESS |  | U.S. STEEL | OTHER | CONCRETE AND SOMASTIC | [27 empty] | 1975 | 1975 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 419 |  | NO | NO | NO |  | 0 | 0 | 55690 | 56823.1979740537 | 1405 | 1405 | 468000 | 477523.014039453 | 0 | 0 | 0 | 0 |  |  | 525095 | 246735.638314892 | 535751.212013506 | [8 empty] | 670 |  | 1440 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 48734 | NO |  |  |  | YES |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS DETERMINED THE CONTROLLERS ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. THE LEAK WAS TOO SMALL TO BE IDENTIFIED BY THE CONTROL ROOM PERSONNEL. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NOT APPLICABLE - NOT MAINLINE PIPE | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | MAYRA SALINAS | SENIOR ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: 48 HR NRC REPORT 1251483 AT APPROXIMATELY 3:35 PM CDT ON JULY 8, 2019, SURFACE BUBBLES WERE DISCOVERED BY A THIRD PARTY FLYING OVER LINE ON THE TEXAS EASTERN TRANSMISSION (TETLP) IN EAST CAMERON BLOCK 286. TETLP TOOK PROACTIVE MEASURES AND SHUT DOWN TETLP'S 16-INCH, LINE 41-A-5 NATURAL GAS PIPELINE ON JULY 8, 2019 AT APPROXIMATELY 7:00 PM CDT. DUE TO HURRICANE ACTIVITIES, TETLP WAS UNABLE TO INVESTIGATE AND DETERMINE THE SOURCE OF THE LEAK UNTIL JULY 20, 2019. THE LINE REMAINS SHUT DOWN AND HAS NOT BEEN RETURNED TO SERVICE. THIS LINE IS SCHEDULED FOR ABANDONMENT IN 2019. THE FERC APPROVAL FOR ABANDONMENT WAS RECEIVED ON JULY 18, 2019. THE APPARENT CAUSE IS INTERNAL CORROSION.
2021-02-26 10:37 | NO | NO | GG (Gas Gathering) | 20190094 | 32985 | 2019-08-13 12:39 | SUPPLEMENTAL FINAL | 31943 | MIDCOAST GATHERING (NORTH TEXAS) L.P. | 55 WAUGH DRIVE SUITE 601 A | HOUSTON | TX | 77007 | 2019-07-19 03:30 | 2019 |  |  | 32.9857 | -97.6849 | 1252461 | 2019-07-19 05:40 |  | NATURAL GAS |  | 5135 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-07-19 03:30 | 2019-07-19 04:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-07-19 03:15 | 2019-07-19 04:23 | ONSHORE | TX | 76082 | SPRINGTOWN | PARKER | MILEPOST | SPRINGTOWN YA | SPRINGTOWN PIPE YARD | CAG 2ND | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2011 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE | CLASS 3 LOCATION | NO |  | 1 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 15706 | 15706 | 0 | 0 | 405 | 413.241069841834 | 0 | 0 |  |  | 16111 | 16472.8119147604 | 16119.2410698418 | [8 empty] | 490 |  | 500 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 1500 | NO | [5 empty] | YES | GATHERING LINE | YES |  |  |  |  | YES | GATHERING LINE | TYPE A GATHERING | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | CONTROL ROOM OPERATOR FAILED TO NOTIFY FIELD PERSONNEL OF LOSS IF COMMUNICATIONS |  |  | YES |  |  | NON-ROUTINE OPERATING CONDITIONS (ABNORMAL OPERATIONS OR EMERGENCIES) | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | BENITA KALKA | GIS ANALYST | benita.kalka@midcoastenergy.com | 7138212072 |  |  |  |  | MELANIE HOSEY | DIRECTOR OF INTEGRITY | 7138212063 | melanie.hosey@midcoastenergy.com | THE COMPRESSION AT THE MIDCOAST SPRINGTOWN PLANT SHUT DOWN DUE TO A POWER FAILURE. THE PLANT IS APPROXIMATELY 350 YARDS FROM THE SPRINGTOWN PIPE YARD WHERE THE RELIEF VALVE ON 2ND CAG WENT OFF AT SET PRESSURE (490 PSIG). GAS CONTROL RECEIVED AN ALARM THAT THE DECATUR COMPRESSOR SHUT IN AND WEATHERFORD PLANT CALLED GAS CONTROL THAT THEY WERE LOSING INLET VOLUME. GAS CONTROL CALLED PLANT OPERATOR TO GO TO SPRINGTOWN PLANT TO CHECK ON COMPRESSION AT 3:00 AM. AT 3:15 AM POLICE CALLED GAS CONTROL THAT THERE WAS GAS RELIEVING AT THE SPRINGTOWN PIPE YARD. MIDCOAST EMPLOYEE ARRIVED AT THE SPRINGTOWN PLANT AND HEARD RELIEF VALVE GOING OFF AT 3:30 AM (CONFIRMATION BY THE OPERATOR). MIDCOAST OPERATIONS TECH WAS CALLED TO INVESTIGATE THE RELIEF VALVE AND VERIFIED THE RELIEF VALVE ON 2ND CAG WAS RELIEVING AT 4:23 AM. OPERATION TECH OPEN BLOCK VALVE TO SWITCH 2ND CAG GAS INTO SM-12 PIPELINE AND THE RELIEF VALVE CLOSED AT 4:45 AM. THE RELIEF VALVE HAD RELIEVED AT 490 PSIG AT SET PRESSURE. RELIEF VALVE INFORMATION: MAKE: CONSOLIDATED, MODEL # 3910R-4-CC-V-65 SIZE 6' X 8' X8' MIDCOAST PERSONNEL (OPERATIONS, GAS CONTROL, IT,) PERFORMED A IN HOUSE INVESTIGATION AND HAS IDENTIFIED THAT WE WILL INSTALL A LOW LOW ALARM AT THE 4TH CAG TO SM-12 PIPELINE TO GIVE AN ALARM AT 30,000N MCF TO INFORM GAS CONTROL TO CALL OUT PERSONNEL TO THE SPRINGTOWN PLANT (ONLY MANNED DAYLIGHT HOURS) TO CALL SOMEONE OUT. THIS SHOULD PREVENT TISE FROM OCCURRING AGAIN. PREVENTION OF RECURRENCE TO PREVENT THIS FROM HAPPENING AGAIN A COMMITTEE REVIEWED THE INCIDENT AND DETERMINED THE FOLLOWING WILL BE IMPLEMENTED. AUTOMATE THE BYPASS VALVE TO OPEN AND COMMON UP THE SUCTION AND DISCHARGE HEADERS. SETTING PRESSURE TO OPERATE BELOW RELIEF VALVE SETTING. INSTALL A CHECK VALVE DOWNSTREAM OF THE PSV TO PREVENT ANY BACKFLOW IN THE EVENT SPRINGTOWN'S DISCHARGE LINE PRESSURE IS HIGHER THAN SPRINGTOWN'S SUCTION LINE PRESSURE. CHANGE THE METER RUN COMMUNICATION TO ALLOW GAS CONTROL THROUGH SCADA TO SEE NO FLOW ON THE SUCTION LINE TO SPRING TOWN. AFE HAS BEEN APPROVED, ENGINEERING HAS ORDERED PARTS AND SET UP A WORK ORDER. GAS CONTROL'S INCIDENT REVIEW CONTROLLER DIDN'T RECOGNIZE COMPRESSOR UNITS WERE DOWN DUE TO THE COMMUNICATIONS OUTAGE. REVIEWED THE GAS CONTROL AND OPERATIONS MEETING MINUTES AND SCADA CHANGES MADE. REVIEWED GAS CONTROL'S COMMUNICATION OUTAGE PROCEDURE. REVIEWED CORRECTIVE ACTIONS: GAS CONTROL WILL NOTIFY ON-CALL OPERATOR IF COMMUNICATION OUTAGE OCCURS AT SPRINGTOWN PLANT. CORRECTIVE ACTIONS 11/13/2019 GAS CONTROL CHANGE THE COMMUNICATION OUTAGE SETPOINT TO 30 MINUTES FROM 60 MINUTES. MOVE THE 4TH CAG OUTLET METER TO A SEPARATE COMMUNICATIONS PATH SO EITHER INLET OR OUTLET OF COMPRESSOR STATION CAN BE SEEN IF FUTURE COMMUNICATION OUTAGE OCCURS. CONTROLLER WILL NOTIFY FIELD PERSONAL IF COMMUNICATION OUTAGE OCCURS. FIELD INSTALLED A PRESSURE CONTROL VALVE TO SHUT GAS IN AT A PRESSURE SET POINT. INSTALLED A CONTROL VALVE TO RE-ROUTE GAS TO A DIFFERENT PIPELINE AT A PRESSURE SET POINT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190095 | 33137 | 2019-08-16 08:59 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2019-07-18 13:53 | 2019 |  |  | 34.7475 | -87.8178 | 1252409 | 2019-07-18 14:57 |  | NATURAL GAS |  | 15.5 | 27097 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-07-18 14:00 | 2019-07-24 20:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-07-18 13:53 | 2019-07-18 13:53 | ONSHORE | AL | 35633 | FLORENCE | LAUDERDALE | MILEPOST | 160.05 | LINE 10 | BART-MTPL | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | TAP FITTING(STOPPLE, THREAD-O-RING, WELD-O-LET, ETC.) | [20 empty] | WELD SADDLE | [17 empty] | UNKNOWN |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 633 |  | NO | NO | NO |  | 0 | 0 | 62595 | 63868.7031277768 | 36 | 36 | 484915 | 494782.205882353 | 0 | 0 | 0 | 0 |  |  | 547546 | 256472.831098374 | 558686.90901013 | [8 empty] | 810 |  | 936 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | REMOTELY CONTROLLED | 87490 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS DETERMINED THE CONTROLLERS ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. THE LEAK WAS TOO SMALL TO BE IDENTIFIED BY THE CONTROL ROOM PERSONNEL. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | YES | [6 empty] | YES | YES | HYDROGEN INDUCED CRACKING AT ORGINAL CONSTRUCTION WELD REPAIR | [12 empty] | YES | [63 empty] | YES | YES | [6 empty] | 2019 | [55 empty] | YES | 1996 | 1310 | NO | [13 empty] | NO | [63 empty] | MAYRA SALINAS | SENIOR ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: 48 HR NRC REPORT 1252608 AT APPROXIMATELY 1:53 PM CDT ON JULY 18, 2019, AN ENBRIDGE EMPLOYEE DISCOVERED A NATURAL GAS RELEASE DURING A HYDO-VAC EXCAVATION ACTIVITIES ON TEXAS EASTERN TRANSMISSION'S (TETLP) LINE 10 PIPELINE SYSTEM IN LAUDERDALE COUNTY, AL. THE LEAK LOCATION WAS SUBSEQUENTLY ISOLATED AT APPROXIMATELY 2:35 PM CDT, STOPPING THE GAS RELEASE. THE LEAK WAS ON THE WELD SADDLE CONNECTING LINE 10 TO A 16 INCH PIPE. THE AFFECTED PIPE WAS REPLACED AND RETURNED TO SERVICE AT APPROXIMATELY 8:30 PM CDT ON JULY 24, 2019. THE APPARENT CAUSE IS STILL UNDER INVESTIGATION. SUPPLEMENTAL-FINAL REPORT 01/02/2020 METALLURGICAL ANALYSIS REPORT DETERMINED CAUSE OF THE LEAK WAS BENDING LOAD AND HYDROGEN INDUCED CRACKING AT ORIGINAL CONSTRUCTION WELD REPAIR.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190097 | 33434 | 2019-08-22 17:22 | SUPPLEMENTAL FINAL | 1217 | BEAR CREEK STORAGE CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-07-25 08:18 | 2019 | CENTRAL | YES | 32.3886 | -92.9297 | 1253115 | 2019-07-25 09:07 | 1253288 | NATURAL GAS |  | 154.08 | 98.29 | 0.3 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-07-25 08:35 | 2019-12-13 17:30 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-07-25 08:23 | VALVE CLOSURE |  | 2019-07-25 08:30 | 0 | 2019-07-25 07:50 | 2019-07-25 08:18 | ONSHORE | LA | 71008 | Not Within a Municipality | BIENVILLE | SURVEY STATION NO. | 959 | BCS-5.7-4 LINE | BCS-5.7-4 LINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 | NO | 0.375 | 52000 | API 5L | SEAMLESS |  | ARMCO STEEL | COAL TAR |  | YES | [26 empty] | 1981 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 331 |  | NO | NO |  |  | 0 | 0 | 208 | 212.232450684201 | 327 | 327 | 43172 | 44050.4776968189 | 50 | 51.0174160298561 | 48108 | 49086.9170072863 | LAB COST & FREIGHT - $2,000; ENVIRONMENTAL TESTING & SOIL REMEDIATION - $46, 108 | 2.12 | 91865 | 43212.3761532207 | 93727.6445708193 | 0 | 0 | 0 | 0 | NO |  |  |  | 2267 | 1815 | 3100 | 192.619(A)(1) |  | 1981-11-13 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 1712 | YES | [7 empty] | YES |  |  |  |  | YES | PIG TRAPS ARE NOT INSTALLED | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS DEEMED INDEPENDENT OF CONTROLLER ACTION. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  | YES | [5 empty] | YES |  |  | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [20 empty] | YES | [42 empty] | DANIEL GRANT | PIPELINE ENGINEER | daniel_grant@kindermorgan.com | 7134204409 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR - ENGINEERING | 7133699443 | jaime_hernandez@kindermorgan.com | ON JULY 25TH, 2019 AT 7:50 AM A BIENVILLE SHERIFF NOTICED A POTENTIAL LEAK COMING FROM THE BEAR CREEK STORAGE COMPANY, LLC (BCSC) 5.7-4 LINE. THE SHERIFF'S DEPARTMENT THEN NOTIFIED BCSC GAS CONTROL. AT 8:18 AM BCSC PERSONNEL ARRIVED ON SITE TO CONFIRM THE LEAK. AT 8:30 AM THE LINE WAS ISOLATED, AND AT 8:35 AM THE BLOWDOWN PROCESS COMMENCED. THE UNINTENTIONAL GAS LOSS WAS ESTIMATED TO BE 154.08 MCF. THE SECTION OF PIPE THAT HAD A LEAK WAS CUTOUT AND SENT IN FOR METALLURGICAL ANALYSIS. AFTER A NEW SECTION OF PIPE WAS INSTALLED, THE PIPELINE WAS RESTARTED ON DECEMBER 13TH, 2019. BCSC HAS DETERMINED THAT THE CAUSE OF THE LEAK WAS INTERNAL PITTING CORROSION. BCSC BELIEVES THE CAUSE MAY BE MIC, BUT THE METALLURGICAL REPORT IS NOT DEFINITIVE. AFTER THE INCIDENT, BCSC BATCH TREATED ALL LINES WITH BIOCIDE. BCSC WILL EVALUATE THE CURRENT INTERNAL CORROSION MITIGATION PROGRAM AND MAKE CHANGES TO THE PROGRAM BASED ON FINDINGS FROM THE EVALUATION. BECAUSE LIQUIDS HAD BEEN RELEASED DURING THE INCIDENT, BCSC COMPLETED ENVIRONMENTAL TESTING AND REMOVED, DISPOSED OF, AND REPLACED, THE CONTAMINATED SOIL AT THE LEAK SITE. THE ACTIONS TAKEN TO REMEDIATE THE SITE LED TO THE ABNORMALLY HIGH COSTS ASSOCIATED WITH THE INCIDENT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190098 | 32770 | 2019-08-23 09:18 | SUPPLEMENTAL FINAL | 26330 | ENABLE OKLAHOMA INTRASTATE TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2019-07-26 06:10 | 2019 |  |  | 36.4408 | -96.4953 | 1253231 | 2019-07-26 07:47 |  | NATURAL GAS |  | 23516 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-07-26 07:57 | 2019-08-01 17:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-07-26 06:10 | 2019-07-26 07:30 | ONSHORE | OK | 74035 | HOMINY | OSAGE | MILEPOST | 5239+72 | LINE 7 | LINE 7 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.25 | 52000 | API 5LX | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | US STEEL | COAL TAR | [28 empty] | 1970 | 1970 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 81 | 20 |  | CLASS 1 LOCATION | NO |  | 388 |  | NO | NO | NO |  | 5000 | 5101.74160298561 | 0 | 0 | 55750 | 55750 | 250000 | 255087.08014928 | 10000 | 10203.4832059712 | 6000 | 6122.08992358273 | MISCELLANEOUS |  | 326750 | 184725.960020281 | 332264.39488182 | [8 empty] | 750 |  | 780 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 101100 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | YES | 1 | 0 | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED |  | YES | [15 empty] | STRESS CORROSION CRACKING | [5 empty] | YES | [63 empty] | YES | YES | [6 empty] | 2015 | [55 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | ON 7/26/2019 AT 06:10 RATE OF CHANGE ALARMS ALERTED THE SYSTEM CONTROLLER OF A POSSIBLE SITUATION WITH LINE 7. THE CONTROLLER STARTED TO DISPATCH O&M TECHS TO INVESTIGATE THE CAUSE OF THE ALARMS. AT 6:20 A LANDOWNER CALLED SYSTEM CONTROL TO NOTIFY OF A JET ENGINE NOISE ON HIS PROPERTY. O&M TECHNICIANS DISCOVERED THE RUPTURE SITE TO BE ON A LARGE RANCH NEAR HOMINY, OKLAHOMA. THE AREA IS A CLASS 1 LOCATION AND THERE WERE NO INJURIES, EVACUATIONS, FIRES, OR FATALITIES. VALVES WERE SHUT AND THE LINE WAS ISOLATED AT 07:57. THE NRC WAS NOTIFIED ON 7/26/19 AT 07:47 (NRC# 1253231). A 48 HOUR FOLLOW UP CALL WAS PROVIDED TO THE NRC ON 7/27/19 AT 15:57 (NRC# 1253370). THE FAILED SECTION OF PIPE WAS REMOVED AND SENT TO A LAB FOR METALLURGICAL ANALYSIS. THE RESULTS OF THE METALLURGICAL FAILURE EXAMINATION INDICATED: -THE PIPE FAILED DUE TO NEAR NEUTRAL STRESS CORROSION CRACKING FROM A BREAK IN THE OD SURFACE COATING THAT ALLOWED THE PIPE TO BE EXPOSED TO THE ELEMENTS. -STRAIGHT, WIDE CRACKS WERE OBSERVED WITH VERY LITTLE BRANCHING. THESE ARE A HALLMARK FEATURE OF NEAR-NEUTRAL STRESS CORROSION CRACKING. -EXPOSURE TO THE ELEMENTS CAUSED PITTING CORROSION, WHICH ACTED AS NUCLEATION SITES FOR STRESS CORROSION CRACKING. -THE FAILURE INITIATION REGION EXHIBITED A PRE-EXISTING CRACK THAT HAD PROPAGATED APPROXIMATELY 80% OF THE PIPE WALL THICKNESS AT THE TIME OF FAILURE. -IN ADDITION, THE OD SURFACE OF THE PIPE EXHIBITED A COLONY OF CRACKS PROPAGATING PARALLEL TO THE FRACTURE SURFACE. THE REGIONS OF THE PIPE IMMEDIATELY ADJACENT TO THE FAILURE INITIATION REGION DID NOT EXHIBIT PITTING CORROSION, INDICATING THAT THE INITIAL REGION OF COATING DAMAGE WAS SMALL AND LOCALIZED. 10/1/2019 SUPPLEMENTAL REPORT PART G.5.1 UPDATED TO DETERMINED BY METALLURGICAL ANALYSIS PART G.5.3 UPDATED TO STRESS CORROSION CRACKING PART H NARRATIVE UPDATED TO INCLUDE METALLURGICAL RESULTS
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190099 | 32606 | 2019-08-23 10:19 | ORIGINAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2019-08-20 08:44 | 2019 |  |  | 33.1525 | -85.5113 | 1255737 | 2019-08-20 09:03 |  | NATURAL GAS |  | 23800 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-08-20 05:20 | 2019-08-20 09:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-08-20 05:20 | 2019-08-20 05:15 | ONSHORE | AL | 36276 | WADLEY | RANDOLPH | MILEPOST | MP 969.48 | COMPRESSOR STATION 110 - MAIN UNIT (MU) #04 | MU 04 RELIEF VALVE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | OTHER | 3/8" PILOT TUBING TO THE RELIEF VALVE |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | TUBING | [38 empty] | 2018 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL (SS) TUBING | OTHER | [8 empty] | SS TUBING CONNECTION FAILURE | CLASS 1 LOCATION | NO |  | 7 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 52836 | 52836 | 400 | 408.139328238848 | 100 | 102.034832059712 | 0 | 0 |  |  | 53336 | 55011.6637164179 | 53346.1741602986 | [8 empty] | 753 |  | 800 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | OTHER | LOCAL LANDOWNER CALLED THE SHERIFF ABOUT NOISE. DEPUTY CALLED, SEE PART H. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA AND ESD SYSTEMS WERE OPERATING NORMALLY. PIPELINE CONTROL DISPATCHED THE OPERATION TECHNICIAN AFTER NOTIFICATION CALL RECEIVED FROM THE SHERIFF DEPUTY. THE RESPONSE PROCESSES AND PROCEDURES WERE EFFECTIVE TO IDENTIFY THE TUBING CONNECTION FAILURE AND SHUT-DOWN THE COMPRESSOR UNIT TO STOP THE GAS RELEASE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES |  |  |  |  | YES | 3/8" PILOT TUBING CONNECTION FAILED AT THE PRESSURE RELIEF VALVE PILOT CAUSING THE RELIEF VALVE TO VENT OPEN (LOSS OF PILOT PRESSURE). | [7 empty] | YES | [177 empty] | TIM HUGGINS | PRINCIPAL ENGINEER | timothy.n.huggins@williams.com | 7132152889 |  |  |  |  | TYSON GREEN | MANAGER PIPELINE SAFETY | 7132152535 | tyson.green@williams.com | COMPRESSOR STATION 110 MAIN UNIT 04 RELIEF VALVE RELEASE TUBING CONNECTION FAILURE EVENT TIMELINE 08/20/2019 4:47 AM PIPELINE CONTROL (HOUSTON) CONTACTED LOCAL OPERATION TECHNICIAN. CONTROLLER HAD RECEIVED A CALL FROM THE LOCAL DEPUTY THAT WAS ON-SITE OUTSIDE AT THE STATION GATE. LOCAL LANDOWNER NEAR STATION HAD CALLED THE SHERIFF ABOUT THE STATION NOISE AND DEPUTY WAS DISPATCHED TO THE SITE. 5:15 AM OPERATION TECHNICIAN ARRIVED AND HEARD GAS RELEASE, ACCESS WAS HELD-UP BY THE DEPUTY UNTIL IDENTIFIED. 5:20 AM OP TECH MANUALLY SHUT-DOWN THE UNIT AND IDENTIFIED THE PILOT TUBING CONNECTION FAILURE AT THE PRESSURE RELIEF VALVE. THE 3/8-INCH STAINLESS STEEL TUBING CONNECTION FAILED AT THE PRESSURE RELIEF VALVE PILOT AND CAUSED THE RELIEF VALVE TO VENT OPEN (LOSS OF PILOT PRESSURE TO THE RELIEF VALVE). NO OTHER OPERATING ISSUES WERE IDENTIFIED. 6:15 AM OPERATIONS PERSONNEL REVIEWED THE STATION HMI AND TRENDED THE OPERATION DATA BACK TO APPROXIMATELY 2:40 AM FOR NORMAL OPERATION. A 9 PSIG PRESSURE DROP WAS NOTED ON MU04 WITH NO CHANGES IN HORSEPOWER COMMANDS. THERE WERE NO SHUT-DOWN ALARMS. MU04 WAS RUNNING UNTIL MANUALLY SHUT-DOWN AT 5:20 AM. THE REASONABLE GAS RELEASE DURATION IS APPROXIMATELY 2-HOURS AND 40-MINUTES. 7:33 AM OPERATIONS NOTIFIED DIVISION ENGINEER TO DETERMINE THE APPROXIMATE GAS RELEASE VOLUME ASSOCIATED WITH THIS DURATION. 8:41 AM ENGINEER CALCULATED 23,800 MSCF FOR THE GAS RELEASE DURATION. 8:44 AM SECURITY OPERATIONS CENTER WAS CONTACTED AND THE GAS RELEASE VOLUME WAS CONFIRMED WITH PIPELINE SAFETY. THIS GAS RELEASE EVENT WAS DETERMINED TO BE A REPORTABLE INCIDENT DUE TO EQUIPMENT FAILURE AND THE RELEASE VOLUME EXCEEDING 3 MMSCF. 9:00 AM THE PILOT TUBING WAS REPLACED, PILOT RE-SET, CHECKED, AND COMPRESSOR UNIT AND RELIEF VALVE WERE RETURNED BACK TO SERVICE. THE TUBING CONNECTION FAILURE WAS LIKELY DUE TO VIBRATION (RECIPROCATING COMPRESSOR UNIT) AND FATIGUE ON THE MOUNTED TUBING. THE NEW PILOT TUBING INSTALLATION WAS MODIFIED. 9:03 AM/10:03 AM NRC REPORT TIME SOC CONTACTED THE NRC, INCIDENT REPORT # 1255737. 9:17 AM PHMSA AID CONTACTED PIPELINE SAFETY TO DISCUSS THE INCIDENT. THE GENERAL LOCATION AND RELEASE INFORMATION, WAS AN INCIDENT DUE TO EQUIPMENT FAILURE (TUBING) AND THE GAS RELEASE VOLUME EXCEEDING 3 MMSCF, AND WAS NOT AN EMERGENCY. NO SPECIFIC EVENT DETAILS WERE KNOWN AT THIS TIME, OTHER THAN A TUBING FAILURE HAD OCCURRED CAUSING THE MAIN UNIT RELIEF VALVE TO VENT OPEN. 10:00 AM OPERATIONS DISCUSS THE RELEASE EVENT SUMMARY AND TIMELINE WITH PIPELINE SAFETY, GATHERED SITE INFORMATION, AND THE INCIDENT REVIEW PROCESS BEGINS. 08/22/2019 7:57 AM NRC CONTACTED FOR PHMSA 48-HOUR UPDATE, NRC INCIDENT REPORT # 1256000 AND PROVIDED UPDATED INFORMATION. PLEASE NOTE, THE NRC CONTACT REVISED THE INCIDENT DISCOVER DATE AND TIME TO 22-AUG-2019 AT 08:00 LOCAL INCIDENT TIME, WHICH WAS THE APPROXIMATE TIME FOR THE 48-HOUR UPDATE? THE NRC CONTACT MAY HAVE MISUNDERSTOOD THE COMMUNICATION. THE ORIGINAL INCIDENT DATE AND TIME IS STILL 20-AUG-2019 AT 08:44 LOCAL INCIDENT TIME AS NOTED ON NRC INCIDENT REPORT # 1255737. 08/23/2019 THE INCIDENT REVIEW AND CAUSE WERE COMPLETED. INCIDENT REPORT SUBMITTED. ROOT CAUSE ANALYSIS AND REMEDIATION THE NEW PRESSURE RELIEF/SAFETY VALVE (PSV) WAS INSTALLED ON 10/25/2018 WITH THE ORIGINAL VENDOR PILOT FILTER AND TUBING ATTACHED TO THE PSV. THE VENDORS PSV DESIGN HAD THE PILOT FILTER SUPPORTED SOLELY BY THE TUBING CONNECTING THE FILTER TO THE RELIEF VALVE PILOT. THE TUBING FAILED AT THE CONNECTION TO THE PSV PILOT. THIS FAILURE APPEARS TO BE DUE TO VIBRATION INDUCED FATIGUE FROM THE UNSUPPORTED WEIGHT OF THE PILOT FILTER AND THE FAILURE EVENT WAS REVIEWED WITH THE VENDOR. WILLIAMS-TRANSCO HAS REPLACED THE PILOT TUBING AND REMOTE MOUNTED THE PILOT FILTER FOR BETTER SUPPORT WHICH SHOULD PREVENT ANY FUTURE FAILURE FROM OCCURRING. THE TUBING AND PILOT FILTER INSTALLATION WILL BE MONITORED FOR NORMAL OPERATION AND VIBRATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190100 | 33138 | 2019-08-26 12:57 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2019-07-29 20:28 | 2019 |  |  | 39.6108 | -81.6289 | 1253581 | 2019-07-29 23:41 |  | NATURAL GAS |  | 45 | 26520.63 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-07-29 22:33 | 2019-08-19 18:35 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-07-29 21:59 | 2019-07-30 21:59 | ONSHORE | OH | 45715 | BEVERELY | MORGAN | MILEPOST | 658.85 | LINE 10 | ATHE-BERN | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 |  | 0.375 | 52000 | API-5L X-52 | DSAW |  | NATIONAL TUBE | COAL TAR | [28 empty] | 1952 | 1952 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 633 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 59406 | 59406 | 454762 | 464015.642971388 | 0 | 0 | 0 | 0 |  |  | 514168 | 274584.321664808 | 523421.642971388 | [8 empty] | 806 |  | 936 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 79728 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS DETERMINED THE CONTROLLER'S ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. THE VOLUME OF THE LEAK WAS TOO SMALL TO BE DETECTED BY THE CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | YES | [7 empty] | YES | PIPE DURING ORIGINAL CONSTRUCTION INSTALLED ON SHARP ROCK | [8 empty] | YES |  |  |  | YES | [63 empty] | YES | YES |  |  | YES |  |  |  | 2019 | [31 empty] | 2019 | [23 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | MAYRA SALINAS | SENIOR ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: 48 HR NRC REPORT # 1253798 AT APPROXIMATELY 8:28 PM EDT ON JULY 29, 2019, ENBRIDGE'S GAS CONTROL RECEIVED A NOTIFICATION OF A NATURAL GAS RELEASE FROM THE PUBLIC ON TEXAS EASTERN TRANSMISSION'S (TETLP) LINE 10 PIPELINE SYSTEM AT MP 658.85 IN LAUDERDALE COUNTY, OH. TETLP DISPATCHED EMPLOYEES TO THE LOCATION AND DISCOVERED A LEAK AT APPROXIMATELY 9:59 PM EDT. TETLP MADE THE NRC NOTIFICATION AT 11:41 PM EDT FOLLOWING CONFIRMED DISCOVERY OF THE LEAK. THE PIPELINE WAS SUBSEQUENTLY ISOLATED AT 10:33 PM EDT, STOPPING THE RELEASE OF GAS. THE AFFECTED PIPE WAS REPLACED AND RETURNED TO SERVICE AT APPROXIMATELY 6:35 PM EDT ON AUGUST 19, 2019. THE APPARENT CAUSE IS STILL UNDER INVESTIGATION. SUPPLEMENTAL REPORT: 01/02/2020 THE APPARENT CAUSE IS A CRACK ASSOCIATED WITH PIPE LAID ON SHARP ROCK DURING ORIGINAL CONSTRUCTION.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190101 | 32621 | 2019-08-28 13:59 | ORIGINAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2019-07-29 09:15 | 2019 |  |  | 27.6982 | -97.9708 | 1253535 | 2019-07-29 13:55 |  | NATURAL GAS |  | 340 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-07-29 09:15 | 2019-07-30 05:39 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-07-29 09:15 | 2019-07-29 09:45 | ONSHORE | TX | 78332 | ALICE | JIM WELLS | MILEPOST | 327+31 | ALICE TO DRISCOLL 8" | 3054 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 12 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8.625 |  | 0.25 |  | UNKNOWN | SEAMLESS |  | UNKNOWN | COLD APPLIED TAPE | [28 empty] | 1964 | 1964 | CARBON STEEL |  | MECHANICAL PUNCTURE | 9 | 5 | [7 empty] | CLASS 1 LOCATION | NO |  | 134 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 800 | 800 | 45000 | 45915.6744268704 | 1500 | 1530.52248089568 | 0 | 0 |  |  | 47300 | 22608.4526609845 | 48246.1969077661 | [8 empty] | 260 |  | 300 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 24148 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | OTHER | ENTERPRISE EMPLOYEE WORKING NEARBY NOTIFIED GAS CONTROL |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLERS ACTIONS WERE CONSISTENT WITH EXPECTATIONS AND FOLLOWED ESTABLISHED OPERATING PROCEDURES. INVESTIGATION WAS NOT WARRANTED. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  |  |  | YES | [6 empty] | FARMER | FARM EQUIPMENT | AGRICULTURE | NO | [5 empty] | YES | 9 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | CHRISTOPHER KRESTA | REGULATORY MANAGER | chris.kresta@energytransfer.com | 713-989-7077 |  |  |  |  | CHRISTOPHER KRESTA | REGULATORY MANAGER | 713-989-7077 | chris.kresta@energytransfer.com | AT APPROXIMATELY 09:15 HOURS ON JULY 29, 2019, ENERGY TRANSFER SUSTAINED A PIPELINE STRIKE FROM A FARMER PLOWING ACROSS IT'S EASEMENT ON ITS ALICE TO DRISCOL 8" TRANSMISSION LINE, ACCOUNT #3054. (RRC SYSTEM ID: 962481). THIS EVENT OCCURRED IN A RURAL CLASS 1 LOCATION IN SOUTH TEXAS OUTSIDE THE CITY OF ALICE IN JIM WELLS COUNTY. THERE WERE NO FIRES, INJURIES, OR EVACUATIONS. NOTIFICATIONS WERE MADE TO THE NRC AT 13:55 HOURS ON JULY 29, 2019 (NRC INCIDENT # 1253535) AND TX RRC (INCIDENT # 2036) AT APPROXIMATELY 14:07 HOURS. THE LINE WAS MECHANICALLY PUNCTURED BY THE LINE STRIKE. IT WAS ISOLATED, BLOWN DOWN, AND THE DAMAGED SECTION WAS REMOVED AND REPLACED. THE LINE WAS RETURNED TO SERVICE ON JULY 30, 2019 AT APPROXIMATELY 05:39 HOURS. THIS REPORT IS BEING SUBMITTED AS A "SIGNIFICANT EVENT" UNDER CFR 191.3 (3) AND DOES NOT MEET OTHER REPORTING CRITERIA. THIS EVENT OCCURRED ON AN INTRASTATE GAS TRANSMISSION PIPELINE UNDER JURISDICTION OF THE TEXAS RAILROAD COMMISSION. TO PREVENT REOCCURRENCE, ENERGY TRANSFER MET WITH THE EXCAVATOR AND EXPLAINED ONE CALL PROCEDURES AND SPECIFICS OF OUR PIPELINE THROUGH THE PROPERTY. ENERGY TRANSFER ALSO LOWERED A PORTION THE AFFECTED PIPELINE IN THE AREA OF THE INCIDENT. ** PHMSA 48 HR. NRC UPDATE MADE ON JULY 30, 2019 AT 16:03 HOURS. ( #1253688)
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190102 | 32795 | 2019-08-29 20:19 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2019-07-30 20:55 | 2019 |  |  | 31.9497 | -103.1073 | 1253714 | 2019-07-30 21:52 |  | NATURAL GAS |  | 5628 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE FACILITY WAS DOWN BEFORE THE INCIDENT OCCURED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-07-30 20:29 | 2019-07-30 20:30 | ONSHORE | TX | 79745 | KERMIT | WINKLER | MILEPOST | KEYSTONE CS | KEYSTONE CS | B-PLANT SUCTION PIPING | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | UNKNOWN |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | URETHANE SEAT | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 85 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 6529 | 6529 | 3565 | 3637.54176292874 | 100 | 102.034832059712 | 0 | 0 |  |  | 10194 | 8485.47509383657 | 10268.5765949884 | [8 empty] | 581 |  | 585 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | BECAUSE THE INCIDENT OCCURRED DUE TO A POWER FAILURE WHICH CAUSE THE COMPRESSOR STATION TO STOP WORKING WHICH CAUSED BACK PRESSURE AND THUS GAS RELEASE THROUGH RELIEF VALVE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | DUE TO PARTIAL SEAT FAILURE. | [161 empty] | KRITI BHAYANI | PIPELINE ENGINEER - CODES AND STANDARDS | kriti_bhayani@kindermorgan.com | 7134206633 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR - CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | ON JULY 30, 2019, KEYSTONE COMPRESSOR STATION IN KERMIT CITY, WINKLER COUNTY, TEXAS LOST POWER AT 7:50 PM (CST). THE COMPRESSOR STATION SHUTDOWN DUE TO LOSS OF COMMERCIAL POWER. APPROXIMATELY 39 MINUTES AFTER THE LOSS OF POWER, THE PLANT B INLET SUCTION PIPING RELIEF VALVE, SET AT 585 PSIG, BEGAN RELIEVING PRESSURE INTERMITTENTLY UNTIL 8:55 PM DUE TO PRESSURE BUILD UP FROM UPSTREAM NATURAL GAS FLOW. GAS CONTROL NOTIFIED LOCAL OPERATIONS ABOUT THE RELIEF VALVE RELEASE AT 8:29 PM AND AT 8:30 PM PERSONNEL STARTED TO INVESTIGATE THE CAUSE OF THE RELIEF VALVE'S INTERMITTENT ACTIVATION. AT APPROXIMATELY 8:55 PM THE RELIEF VALVE SEAT MATERIAL PARTIALLY FAILED DUE TO THE INTERMITTENT ACTIVITY, ALLOWING THE VALVE TO LEAK GAS UNTIL 10:12 PM. DURING THIS EVENT FIELD PERSONNEL WERE IN CONTACT WITH THE CONTROL CENTER AND BOTH WERE TRYING TO DETERMINE IF THE RELIEF VALVE WAS TRULY ACTIVATING DUE TO AN OVERPRESSURE EVENT AND WERE TRYING TO DETERMINE HOW TO ELIMINATE OR DIVERT THE PRESSURE SOURCE. ONCE THEY DETERMINED WE DID NOT HAVE AN OVERPRESSURE EVENT LOCAL PERSONNEL OPENED A BYPASS VALVE AT 10:00 PM BETWEEN PLANT-B SUCTION AND DISCHARGE PIPING. THIS ACTION DIVERTED THE INCOMING FLOW OF GAS. ONCE THIS WAS ACCOMPLISHED FIELD PERSONNEL THEN ISOLATED THE RELIEF VALVE BY CLOSING ITS ISOLATION VALVE AT APPROXIMATELY 10:12 PM. THE POST INCIDENT INVESTIGATION DETERMINED THAT THE RELIEF VALVE SEAT WAS WEATHERED AND PARTIALLY TORN. THE RELIEF VALVE'S SEAT MATERIAL WAS REPLACED AND TESTED BEFORE B-PLANT WAS PUT BACK IN SERVICE.
2021-02-26 10:37 | YES | YES | GT (Gas Transmission) | 20190103 | 34056 | 2019-08-30 10:24 | SUPPLEMENTAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2019-08-01 01:23 | 2019 | CENTRAL | YES | 37.5445 | -84.8078 | 1253844 | 2019-08-01 03:14 | 1254075 | NATURAL GAS |  | 101485 | 25918 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 6 | 6 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-08-01 02:20 |  | YES | NO |  |  | YES | 2019-08-01 01:25 | ALLOWED TO BURN OUT |  | 101485 | YES | VALVE CLOSURE |  | 2019-08-01 01:35 | VALVE CLOSURE |  | 2019-08-01 02:20 | 75 | 2019-08-01 01:25 | 2019-08-01 02:20 | ONSHORE | KY | 40484 | STANFORD | LINCOLN | MILEPOST | MP 423.4 | LINE 15 | DANV - TOMP | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 43 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 | NO | 0.375 | 52000 | API-5L | FLASH WELDED |  | A. O. SMITH | COAL TAR |  | YES | [26 empty] | 1958 | 1957 | CARBON STEEL |  | OTHER | [8 empty] | UNDER INVESTIGATION BY THE NTSB. WILL SUPPLEMENT WHEN AVAILABLE. | CLASS 2 LOCATION | NO |  | 633 |  | YES | YES | YES | SOME PERSONS HAVE COMPLAINED OF RESPIRATORY DISTRESS AND EMOTIONAL DISTRESS. | 4200000 | 4285462.94650791 | 58056 | 59237.3421005865 | 227326 | 227326 | 9700000 | 9897378.70979207 | 1800000 | 1836626.97707482 | 3500000 | 3571219.12208992 | ENVIRONMENTAL MITIGATION -INCIDENT INVESTIGATION -MISCELLANEOUS COSTS | 2.24 | 19485382 | 9255513.30542048 | 19877251.0975653 | 5 | 0 | 19 | 0 | NO |  |  |  | 925 | 452751 | 936 | 192.619(A)(1) |  | 2014-10-17 | YES | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 100742 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, BUT THE INVESTIGATION OF THE CONTROL ROOM AND/OR CONTROLLER ACTIONS HAS NOT YET BEEN COMPLETED BY THE OPERATOR (SUPPLEMENTAL REPORT REQUIRED) | [13 empty] | YES | 7 | 0 | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [146 empty] | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | nathan.atanu@enbridge.com | [5 empty] | RICK KIVELA | SR SPECIALIST OPERATIONAL COMPLIANCE | 713-627-6388 | rick.kivela@enbridge.com | ORIGINAL REPORT: ORIGINAL NRC # 1253844 48 HOUR REPORT NRC # 1254075 AT APPROXIMATELY 1:23 A.M. EDT ON AUGUST 1, 2019, TETLP'S 30-INCH DIAMETER LINE 15 TRANSPORTING NATURAL GAS FROM DANVILLE COMPRESSOR STATION TO TOMPKINSVILLE COMPRESSOR STATION IN KENTUCKY FAILED AT MP 423.4. THE FAILURE RESULTED IN AN EXPLOSION AND FIRE. TETLP GAS CONTROL RECEIVED A RATE OF CHANGE ALARM ON LINE 15 ON THE SOUTH SIDE OF DANVILLE COMPRESSOR STATION AT APPROXIMATELY 1:25 AM EDT. DURING THE ENSUING MINUTES, TETLP BEGAN RECEIVING REPORTS FROM THE PUBLIC AND A TETLP OPERATOR OF A FIRE SOUTH OF THE DANVILLE COMPRESSOR STATION. TETLP PERSONNEL WERE IMMEDIATELY DISPATCHED TO CLOSE MAINLINE BLOCK VALVES, MLV 15-382 AT MP 408.48 AND MLV 15-393 AT THE DANVILLE COMPRESSOR STATION, THUS ISOLATING THE FAILED SEGMENT. FIRST RESPONDERS EVACUATED APPROXIMATELY 75 MEMBERS OF THE PUBLIC. THE INCIDENT RESULTED IN 1 FATALITY AND 6 KNOWN INJURIES. THE APPARENT CAUSE OF THE INCIDENT IS UNDER INVESTIGATION BY THE NTSB. THE INCIDENT CAUSE IS BEING REPORTED AS OTHER INCIDENT CAUSE UNTIL THE NTSB RELEASES INFORMATION ABOUT THE INCIDENT CAUSE. THE APPARENT CAUSE WILL BE UPDATED WHEN IT BECOMES AVAILABLE FROM THE NTSB. ALSO NOTE THE PIPE INVOLVED IN THE INCIDENT WAS MANUFACTURED IN 1957 AND INSTALLED IN 1958, AS REFLECTED IN PART C, ITEM 3G OF THIS REPORT. THE PHMSA CORRECTIVE ACTION ORDER INCORRECTLY STATED THE PIPE WAS INSTALLED IN 1942. SUPPLEMENTAL REPORT - 7/21/2020 UPDATED PART A.7 ESTIMATED VOLUME OF GAS RELEASED UNINTENTIONALLY TO 101,485 MCF UPDATED PART A.8 ESTIMATED VOLUME OF INTENTIONAL AND CONTROLLED RELEASE/BLOWDOWN TO 25,918 MCF UPDATED ADDITIONAL PARTS AS A RESULT OF CHANGES TO THE PHMSA PORTAL
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190104 | 32722 | 2019-08-30 11:56 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2019-08-03 16:25 | 2019 |  |  | 34.5372 | -106.679 | 1254143 | 2019-08-03 18:02 |  | NATURAL GAS |  | 9268 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-08-03 16:10 | 2019-08-03 19:16 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-08-03 17:10 | 2019-08-03 17:10 | ONSHORE | NM | 87002 | BODEGA | VALENCIA | SURVEY STATION NO. | COMPRESSOR ST | BELEN COMPRESSOR STATION | WEST FLOW VENT VALVE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1956 |  | CARBON STEEL |  | OTHER | [8 empty] | EQUIPMENT MALFUNCTION: SUCTION VALVE'S ACTUATOR PILOT MALFUNCTIONED. | CLASS 1 LOCATION | NO |  | 120 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 21099 | 21099 | 50 | 51.0174160298561 | 150 | 153.052248089568 | 0 | 0 |  |  | 21299 | 21967.9646991656 | 21303.0696641194 | [8 empty] | 689 |  | 836 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | NO | YES | YES | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | BECAUSE THE INCIDENT WAS CAUSED DUE TO EQUIPMENT FAILURE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | YES | [33 empty] | YES | DEBRIS FOUND IN THE PILOT VALVE OF THE ACTUATOR VALVE CAUSED MALFUNCTION | [161 empty] | KRITI BHAYANI | PIPELINE ENGINEER - CODES AND STANDARDS | kriti_bhayani@kindermorgan.com | 7134206633 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR - CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | ON 8/3/2019, BELEN COMPRESSOR STATION, VALENCIA COUNTY, NEW MEXICO EXPERIENCED A FIRE EYE DETECTION EVENT WHICH RESULTED IN AN ESD AT 4:10PM (MST). THE MAINLINE 1300 WEST FLOW SUCTION VALVE'S ACTUATOR PILOT MALFUNCTIONED RESULTING IN THE SUCTION VALVE NOT CLOSING UPON INITIATION OF THE ESD. THIS MALFUNCTION KEPT THE STATION PIPING FROM BEING ISOLATED WHICH RESULTED IN A CONTINUOUS RELEASE OF GAS THROUGH 6" ESD VENT VALVE. UPON RECEIPT OF THE ORIGINAL FIRE DETECTION SYSTEM ALARM GAS CONTROL DISPATCHED AN EPNG TECHNICIAN TO THE COMPRESSOR STATION AND UPON ARRIVAL AT 5:10 PM THE TECHNICIAN DISCOVERED AND CONFIRMED THE ESD VENT VALVE WAS VENTING GAS. THE EMPLOYEE PROCEEDED TO MANUALLY CLOSE THE SUCTION VALVE AND COMPLETED THE TASK BY 5:14 PM. HE IMMEDIATELY NOTIFIED HIS SUPERVISOR AT 5:15 PM. AN ERL CALL WAS INITIATED AT WHICH TIME WE CONFIRMED DISCOVERY AND AN NRC REPORT WAS MADE AT 6:02 PM. THE NATURAL GAS LOSS WAS ESTIMATED TO BE 9,268 MCF. THE ACTUATOR PILOT VALVE WAS REPAIRED AND TESTED THEN PLACED BACK IN SERVICE. THE ORIGINAL FIRE DETECTION EVENT WAS DETERMINED TO HAVE BEEN A FALSE EVENT INITIATED BY LIGHTING IN CLOSE PROXIMITY TO THE STATION AS THERE WERE LIGHTING STORMS IN THE AREA AND THERE WAS NO EVIDENCE OF FIRE AT THE STATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190105 | 32818 | 2019-09-08 15:12 | SUPPLEMENTAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2019-08-12 15:33 | 2019 |  |  | 40.9135 | -90.9504 | 1254968 | 2019-08-12 20:25 |  | NATURAL GAS |  | 8125 | 435 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-08-12 22:00 | 2019-08-14 09:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 1 | 2019-08-12 15:49 | 2019-08-12 16:00 | ONSHORE | IL | 61469 | OQUAWKA | HENDERSON | SURVEY STATION NO. | 1852+19 | CARTHAGE LINE - STATION 323 TO STA. 950 | N/A | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 39 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10.75 |  | 0.203 | 35000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | AMERICAN STEEL PIPE (ACIPCO) | COAL TAR | [28 empty] | 1966 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 8 | 6 | [7 empty] | CLASS 2 LOCATION | NO |  | 263 |  | NO | NO | NO |  | 0 | 0 | 1464 | 1493.78994135419 | 27349 | 27349 | 389521 | 397447.098187311 | 2300 | 2346.80113737338 | 28800 | 29386.0316331971 | FOOD AND LODGING. |  | 449434 | 226044.552139408 | 458022.720899236 | [8 empty] | 375 |  | 600 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 45900 | NO |  |  |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS INCIDENT WAS CAUSED BY THIRD PARTY EXCAVATION DAMAGE. THE STATION FEEDING THE SYSTEM FROM ABOUT 60 MILES TO THE NORTH IS MONITORED BY GAS CONTROL BUT THEY DO NOT HAVE REMOTE CONTROL CAPABILITIES FOR THE STATION. THE CONTROLLER DID OBSERVE A LOW-LOW ALARM AND NOTIFIED THE OPERATING DEPARTMENT, WHO WAS ALREADY AWARE OF THE EXCAVATION DAMAGE AND TOOK OVER MANUAL CONTROL OF VALVES TO ISOLATE THE SYSTEM. | [12 empty] | YES | 2 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | NO | YES | STATE HIGHWAY | [9 empty] | CONTRACTOR | TRENCHER | TELECOMMUNICATIONS | YES | 2170416 | J.U.L.I.E. | UTILITY OWNER | NO | NO | YES | 36 | LOCATING PRACTICES NOT SUFFICIENT |  | FACILITY WAS NOT LOCATED OR MARKED | [264 empty] | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QA | lquezad@southernco.com | 6303882316 |  |  |  |  | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QA | 6303882316 | lquezad@southernco.com | SUPPLEMENTAL REPORT WAS CREATED AND FILED AT PHMSA STAFF REQUEST. CHANGED LOCAL TIME OF INCIDENT FROM 15:49 TO 15:33. ++++++++++++++++++++++++++++++++++++++++++++++++++++++++++++++++++++++++ THIRD PARTY EXCAVATOR WAS PERFORMING INSTALLATION OF TELECOMMUNICATIONS FACILITIES VIA TRENCHING WHEN THEY STRUCK AN UNMARKED 10" NATURAL GAS TRANSMISSION LINE THAT IS OPERATED AS PART OF A DISTRIBUTION SYSTEM. THE TRANSMISSION LINE WAS PURGED INTO SERVICE ON 8/14/19 AT 09:15. THE TRANSMISSION LINE FEEDS A 60-PSIG DISTRIBUTION SYSTEM WITH 788 MOSTLY RESIDENTIAL CUSTOMERS THAT WERE INTERRUPTED. THE 60-PSIG SYSTEM WAS ENERGIZED IN MULTIPLE PHASES, WITH THE MAINS IN THE LAST PHASE ENERGIZED AT 17:00 ON 8/15/19. THE COST OF DAMAGE AND REPAIRS INCLUDES THE REACTIVATION OF THE 60-PSIG DISTRIBUTION SYSTEM AND TURN-ON/RELIGHTS FOR THE CUSTOMERS INTERRUPTED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190106 | 34095 | 2019-09-18 16:41 | SUPPLEMENTAL FINAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-08-21 17:50 | 2019 | MOUNTAIN | YES | 32.7896 | -104.2383 | 1255973 | 2019-08-21 18:55 | 1255979, 1256183 | NATURAL GAS |  | 30663 | 66.5 | 70 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-08-21 19:16 | 2020-02-17 08:00 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2019-08-21 19:17 | NO | [5 empty] | VALVE CLOSURE |  | 2019-08-21 19:16 | VALVE CLOSURE |  | 2019-08-21 17:41 | 0 | 2019-08-21 19:35 | 2019-08-21 19:35 | ONSHORE | NM | 88210 | Not Within a Municipality | EDDY | MILEPOST | MP 37 | INDIAN BASIN | LAUNCHER SITE TO CS 167 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 20 |  | 0.235 | 60000 | API 5L GRADE X60 | LONGITUDINAL ERW - LOW FREQUENCY |  | YOUNGSTOWN SHEET AND TUBE | ASPHALT |  | YES | [26 empty] | 1965 | 1965 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 687.6 | 60 |  | CLASS 1 LOCATION | NO |  | 436 |  | NO | NO |  |  | 25279 | 25793.3851963746 | 133 | 135.706326639417 | 61203 | 61203 | 166800 | 170194.0998756 | 608 | 620.371778923049 | 36493 | 37235.5712635507 | REPL. PIPE XPORT, MET. RPT, CONTAINMENT SOAKERS (RAIN-PREV. MEAS), M. PHONE CHGS | 1.996 | 290516 | 170854.525810595 | 295182.134441088 | 0 | 0 | 0 | 0 | NO |  |  |  | 879 | 6000 | 1000 | 192.619(A)(1) |  | 1965-12-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | AUTOMATIC | AUTOMATIC | 89760 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE WAS OPERATING UNDER MAOP AND CONTROLLERS WERE NOT MAKING ANY CHANGES TO PIPELINE CONDITIONS. NO CHANGES WERE MADE TO EITHER SETPOINT OR HORSEPOWER. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | OTHER | LOCALIZED PITTING AND GENERAL CORROSION |  |  |  |  | YES | YES | ELECTROCHEMICAL |  |  |  | YES |  |  | YES | YES | 1966 |  | YES | YES | YES |  |  | 2019 | 2016 |  |  | NO | [190 empty] | YES | YES |  |  | YES |  |  |  | 2017 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2002 | FREE SWIMMING | METAL LOSS |  | STANDARD RESOLUTION | [21 empty] | 2017 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | 2017 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | [14 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KRISTIN VAN DER LAAN | ENGINEERING MANAGER - CODES AND COMPLIANCE | kristin_vanderlaan@kindermorgan.com | 303-914-7753 |  |  |  |  | JAIME HERNANDEZ | ENGINEERING DIRECTOR - CODES AND COMPLIANCE | 713-369-9443 | jaime_hernandez@kindermorgan.com | ON AUGUST 21, 2019 THE NATURAL GAS PIPELINE COMPANY OF AMERICA, LLC (NGPL) 20-INCH INDIAN BASIN PIPELINE EXPERIENCED AN IN-SERVICE FAILURE RESULTING IN A PIPELINE RUPTURE AND LIQUID SPRAY (A MIXTURE OF CONDENSATE AND USED OIL), BUT NO FIRE. AUGUST 21, 2019: 17:41 - RIVERSIDE FIRE DEPARTMENT (NM) DISPATCHED 17:51 - A MEMBER OF THE PUBLIC WORKING IN THE LOCO HILLS NEW MEXICO AREA CONTACTED NGPL GAS CONTROL AND REPORTED AN EVENT IN THE AREA OF THE PIPELINE. 17:55 - RIVERSIDE FIRE DEPARTMENT (NM) ARRIVES ON SCENE. ON ARRIVAL, UNITS STAGED UPWIND AND SECURED ALL ROADS GOING TOWARDS THE PIPELINE. 17:57 TO 18:04 - CALLS MADE TO DEPLOY NGPL PERSONNEL TO THE REPORTED EVENT LOCATION (NGPL TECHNICIAN 3) AND TO CLOSE THE UPSTREAM AND DOWNSTREAM VALVES (NGPL TECHNICIANS 1 AND 2). 18:32 - INTERNAL EMERGENCY RESPONSE LINE (ERL+) CALL NOTIFICATIONS INITIATED PER COMPANY PROCEDURES TO DISCUSS THE INCIDENT. DURING THE CALL, IT WAS COMMUNICATED THAT THE LOCAL FIRE DEPARTMENT ON-SITE HAD CLOSED HILLTOP ROAD AND HIGHWAY 82. 18:51 - CALL TO NRC INITIATED (#1255973) 19:15 - NGPL TECHNICIAN 1 ARRIVES AT MLV IB-3, AUTOMATIC VALVE FOUND FULLY OPEN. 19:16 - NGPL TECHNICIAN 1 CLOSES MLV IB-3 AND IN ROUTE TO MLV IB-4. 19:20 - NGPL TECHNICIAN 2 ARRIVES AT MLV IB-2 AND VERIFIES THAT THE VALVE IS CLOSED AND IN ROUTE TO MLV IB-1. MLV IB-2 TO MLV IB-3 ISOLATED. 19:29 - NGPL TECHNICIAN 3 ARRIVES AT THE GENERAL INCIDENT LOCATION. 19:35 - NGPL TECHNICIAN 3 ON THE FAILURE SITE, VERIFIES FAILURE, REPORTED NO GAS BLOWING. 19:45 - NGPL TECHNICIAN 1 VERIFIES MLV IB-4 CLOSED AND STANDING BY AT SITE. 20:05 - NGPL TECHNICIAN 2 ARRIVES AT MLV IB-1 AND CLOSES THE VALVE. 20:20 - RIVERSIDE FIRE DEPARTMENT (NM) LEAVES THE SCENE. AUGUST 29, 2019: 12:00 - PIPE REPLACED AND COVERED. METALLURGICAL REPORT COMPLETED NOVEMBER 13, 2019. THE RESULTS OF THE METALLURGICAL ANALYSIS INDICATE THAT THE FAILURE OCCURRED AT AN AREA OF WALL THINNING IN THE LONGITUDINAL SEAM WELD DUE TO EXTERNAL CORROSION. THE WALL THINNING LED TO A BRITTLE FRACTURE INDUCED BY THE OPERATING PRESSURE. THE BRITTLE RUPTURE BEHAVIOR OF THE LONGITUDINAL SEAM WAS DUE IN PART TO THE LOW TOUGHNESS AND ALSO THE STRAIN RATE OF THE RUPTURE EVENT. MULTIPLE CORROSION MECHANISMS WERE OBSERVED AT THE RUPTURE INITIATION SITE, INCLUDING LOCALIZED CORROSION IN THE FORM OF SELECTIVE SEAM WELD CORROSION (SSWC), PITTING CORROSION AND GENERAL CORROSION. UPDATE NRC REPORT 1255979 AND 48-HOUR NRC REPORT 1256183. NOTE THAT FORM PHMSA F 7100.2 (REV 09-2019) PART J, Q1 WHEN A POSITIVE RESPONSE IS ENTERED FOR AN INTERNAL INSPECTION TOOL THEN BOTH A MOST RECENT AND A PREVIOUS ENTRY IS REQUIRED. NGPL RAN A GEOMETRY/DEFORMATION TOOL IN 2017 BUT DID NOT HAVE A PRIOR TOOL RUN OF THIS TYPE. IN ORDER TO SUBMIT THIS FORM THE 2017 RUN HAS BEEN ENTERED TWICE IN THAT SECTION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190107 | 33229 | 2019-09-19 18:31 | SUPPLEMENTAL FINAL | 32005 | ENLINK LBU-GAS&LIQUIDS | 1722 ROUTH STREET SUITE 1300 | DALLAS | TX | 75201 | 2019-08-20 20:25 | 2019 |  |  | 29.7706 | -91.717 | 1255844 | 2019-08-20 20:53 |  | NATURAL GAS |  | 4688 | 3060 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-08-20 | 2019-10-10 12:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-08-20 | 2019-08-20 19:30 | ONSHORE | LA | 70538 | Not Within a Municipality | ST. MARY | MILEPOST | WEST OF BV-2 | P1566 - WEEKS ISLAND TO ST. JAMES 36" | P1566 - WEEKS ISLAND TO ST. JAMES 36" | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | UNDER WATER | 77 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 36 |  | 0.438 | 60000 | 5LX60 | DSAW |  | ARMCO | OTHER | THIN FILM EPOXY (TFE) | [27 empty] | 1979 | 1979 | CARBON STEEL |  | LEAK |  |  | OTHER | INTERNAL CORROSION | [5 empty] | CLASS 1 LOCATION | NO |  | 786 |  | NO | NO | NO |  | 0 | 0 | 7650 | 7805.66465256798 | 11720 | 11720 | 360000 | 367325.395414964 | 0 | 0 | 0 | 0 |  |  | 379370 | 184345.711259502 | 386851.060067532 | [8 empty] | 811 |  | 1001 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 38016 | NO | [5 empty] | YES | SEGMENT IS CAPPED ON ONE END. | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CAUSE OF THE LEAK WAS INTERNAL CORROSION. THE LEAK WAS NOT LARGE ENOUGH FOR PIPELINE CONTROL TO DETECT A LEAK. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | GENERAL CORROSION | [14 empty] | NO |  |  |  | NO | [9 empty] | GENERAL CORROSION |  |  |  | YES |  |  |  | YES | YES |  |  | YES | [5 empty] | NO | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | CORDELL THERIOT | SR. DOT SPECIALIST | cordell.theriot@enlink.com | 3373226682 |  |  |  |  | CORDELL THERIOT | SR. DOT SPECIALIST | 3373226682 | cordell.theriot@enlink.com | ON 8/20/2019 ENLINK WAS NOTIFIED BY A LOCAL FISHERMAN OF A POSSIBLE LEAK. OPERATIONS IMMEDIATELY BEGAN TO DETERMINE IF THE LEAK WAS ON OUR ENLINK PIPELINE. AFTER CONFIRMING THE LEAK WAS ON AN ENLINK PIPELINE, OPERATIONS SHUT DOWN THE PIPELINE AND ALLOWED THE LINE TO CONTINUE LEAKING UNTIL THE PRESSURE WAS AT A SAFE ENOUGH LEVEL TO MAKE THE NECESSARY REPAIRS. THE LEAK WAS IN AN AREA COMPLETELY UNDERWATER. REPAIR WAS MADE BY CUTTING OUT A SECTION OF PIPE AND REPLACING WITH NEW PIPE. THE CUTOUT WAS SENT TO A METALLURGICAL LAB AND THE CONCLUSIONS ARE THAT BACTERIA WAS FOUND IN THE CORROSION DEPOSITS BUT WAS NOT THE MAIN CAUSE OF THE CORROSION, RATHER TUBERCLE FORMATIONS WERE THE MAIN CAUSE. THE 48-HOUR NOTIFICATION TO THE NRC WAS MADE ON 8/22/2019 @ 23:02, INCIDENT # 1256107.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190108 | 34607 | 2019-09-20 08:18 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2019-08-21 02:25 | 2019 | EASTERN | YES | 41.0258 | -79.6328 | 1255871 | 2019-08-21 09:05 | 1256125 | NATURAL GAS |  | 29311 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | POST-MAINTENANCE/REPAIR | [5 empty] | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-08-21 07:58 | VALVE CLOSURE |  | 2019-08-21 07:58 | 0 | 2019-08-21 02:09 | 2019-08-21 07:31 | ONSHORE | PA | 16028 | Not Within a Municipality | ARMSTRONG | MILEPOST | VS-5016 | PIPELINE 134 | VS-5016 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 24 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | MECHANICAL PIPE COUPLER | 1929 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | ONE JOINT OF PIPE BECAME DISCONNECTED FROM THE PIPELINE AT MECHANICAL PIPE COUPLER. | CLASS 1 LOCATION | NO |  | 109 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 54812 | 54812 | 314517 | 320916.892749245 | 3000 | 3061.04496179136 | 0 | 0 |  | 1.87 | 372329 | 205540.511399854 | 378789.937711036 | 0 | 0 | 0 | 0 | NO |  |  |  | 229 | 7000 | 250 | 192.619(A)(3) |  | 1929-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 10824 | NO |  | YES |  | YES |  |  |  | YES |  | YES |  |  | YES | MECHANICALLY COUPLED PIPE | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | CONTROLLER |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 1 | 0 | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | OTHER | MECHANICAL COUPLING -DRESSER STYLE |  |  |  | YES | [12 empty] | YES | CONSTRUCTION ACTIVITIES ON THE PIPELINE | [161 empty] | WILLIAM YOUSE | COMPLIANCE SPECIALIST | william_youse@tcenergy.com | 304-357-3596 | 304-357-3522 |  |  |  | PAUL SHAFFER | US REGULATORY COMPLIANCE EAST MANAGER | 304-357-2245 | paul_shaffer@tcenergy.com | PIPELINE 134 IS A 10-INCH BARE CARBON-STEEL PIPELINE OWNED AND OPERATED BY COLUMBIA GAS TRANSMISSION, LLC (OPID 2616), A TC ENERGY ENTITY. THIS SEGMENT OF LINE 134 IS MECHANICALLY COUPLED, PLACED INTO SERVICE IN 1929 WITH A MAXIMUM ALLOWABLE OPERATING PRESSURE OF 250 PSIG. ON AUGUST 21, 2019 LINE 134 WAS SUBJECT TO A MECHANICAL COUPLING FAILURE OCCURRING IN ARMSTRONG COUNTY, PENNSYLVANIA. THE MORNING OF AUGUST 21ST, GAS CONTROL RECEIVED AN ALARM FROM THE IOWA COMPRESSOR STATION INDICATING THAT UNIT 1 HAD HIGH DISCHARGE PRESSURE. STATION PERSONNEL WERE DISPATCHED AND RESPONDED TO THIS CALL. LATER THAT HOUR GAS CONTROL RECEIVED A SECOND ALARM FROM THE IOWA COMPRESSOR STATION INDICATING THAT UNIT 2 HAD LOW SUCTION PRESSURE. THIS CALL WAS ALSO RESPONDED TO AND EVALUATED. PIPELINE PRESSURE CONTINUED TO DROP. OPERATIONS MANAGERS WERE NOTIFIED, AND ADDITIONAL SUPPORTING COMPANY PERSONNEL WERE DISPATCHED. THE PIPELINE LEAK WAS LOCATED AND ISOLATED BY 7:58 AM. THE PIPELINE IN THIS AREA IS PART OF A MODERNIZATION PROJECT. AT THE TIME OF THE INCIDENT, THE EFFECTED SEGMENT OF LINE 134 IN THIS PROJECT HAD BEEN EXPOSED, STOPPLES INSTALLED, PIPELINE SECTIONS REMOVED, AND END CAPS WERE INSTALLED. THE CONSTRUCTION ACTIVITIES DURING THIS CONSTRUCTION WORK APPEAR TO HAVE CONTRIBUTED TO THE DISCONNECTION OF THIS SECTION OF PIPE. INITIAL NRC REPORT NUMBER IS 1255871 REPORTED AUGUST 21, 2019 AND THE 48-HOUR NRC REPORT NUMBER IS 1256125 REPORTED ON AUGUST 23, 2019. THE INTERNAL INVESTIGATION INTO THIS INCIDENT HAS DETERMINED THE FOLLOWING CAUSAL FACTORS: -GUIDELINES FOR THE USE OF MECHANICAL COUPLINGS RESIDED WITHIN CPG INTEGRATED DOCUMENTS LISTING BUT NOT WITHIN THE TC ENERGY CONTROLLED DOCUMENT LIBRARY; THE SINGLE REFERENCE SOURCE FOR US NATURAL GAS PIPELINES PROJECTS. -DURING PROJECT PLANNING THE RISKS OF EXCAVATION ON 1929 VINTAGE PIPELINE SYSTEM WITH PROBABILITY FOR MECHANICAL COUPLINGS WAS NOT DOCUMENTED AS A POTENTIAL HAZARD FOR EXCAVATION/CONSTRUCTION ACTIVITIES. -WHEN A MECHANICAL COUPLING WAS EXPOSED DURING EXCAVATION, THE RISK WAS NOT ADEQUATELY ESCALATED BY THE CONTRACTOR TO THE PROJECT MANAGER. ADDITIONALLY, THE DECISION TO MOVE THE STOPPLE INSTALLATION POINT DUE TO MECHANICAL COUPLING DISCOVERY AT THAT POINT DID NOT GENERATE DISCUSSION ON THE RISK OF THE EXPOSED MECHANICAL COUPLING OR THE POTENTIAL OF ADDITIONAL MECHANICAL COUPLINGS NEAR THE EXCAVATION SITE. CORRECTIVE ACTIONS COMPLETED TO DATE INCLUDE: -ESTABLISHED US NATURAL GAS PROJECTS INITIATIVE TO IDENTIFY GAPS IN EXISTING ENGINEERING DESIGN STANDARDS -REQUIRE ALL PROJECTS TO DEVELOP A PRE-JOB SAFETY MANAGEMENT PLAN -THE DISTRIBUTION OF THE "MECHANICAL PIPELINE REPAIR TAPPING AND JOINING" PROCEDURE TO US NATURAL GAS PROJECT, US CONSTRUCTION SERVICES STAFF, US GAS OPERATIONS FIELD OPERATIONS MANAGERS AND TEAM LEADERS -PUBLICATION OF THE "MECHANICAL PIPELINE REPAIR TAPPING AND JOINING" PROCEDURE TO THE CONTROLLED DOCUMENT LIBRARY -ESTABLISHED REQUIRED TRAINING FOR US NATURAL GAS PROJECT CONSTRUCTION MANAGERS AND US GAS OPERATIONS FIELD OPERATIONS STAFF ON "MECHANICAL PIPELINE REPAIR TAPPING AND JOINING" PROCEDURES. -DISTRIBUTED LESSONS LEARNED SAFETY SHARE TO US NATURAL GAS PIPELINES PROJECTS, CONSTRUCTION SERVICES AND US GAS OPERATIONS FIELD OPERATIONS. -ADDITIONAL TRAINING PLANNED IN 2021
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190109 | 32765 | 2019-09-27 17:16 | ORIGINAL FINAL | 13845 | NORTHWEST PIPELINE LLC | 295 CHIPETA WAY | SALT LAKE CITY | UT | 84108 | 2019-09-04 04:16 | 2019 |  |  | 47.6374 | -117.6689 | 1257199 | 2019-09-04 09:31 |  | NATURAL GAS |  | 4623 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE STATION CONTINUED TO OPERATE SAFELY DURING THE CONTROLLED REALEASE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-09-04 04:04 | 2019-09-04 04:55 | ONSHORE | WA | 99022 | AIRWAY HEIGHTS | SPOKANE | MILEPOST | MP 146.1 | 2435 SPOKANE LINE | 2435 SPOKANE LINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 2019 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | REGULATOR PILOR FILTERS, REGULATOR PILOT | OTHER | [8 empty] | REGULATOR VALVE EQUIPMENT FAILURE | CLASS 1 LOCATION | NO |  | 138 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 9492 | 9492 | 300 | 306.104496179136 | 400 | 408.139328238848 | 0 | 0 |  |  | 10192 | 10168.644163615 | 10206.243824418 | [8 empty] | 372 |  | 625 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE WILLIAMS CONTROLLER PROMPTLY NOTIFIED AND DISPATCHED THE WILLIAMS ON-CALL TECHNICIAN TO INVESTIGATE THE ISSUE AT THE FACILITY. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [19 empty] | YES | [168 empty] | JASON LAMBERT | MGR. PIPELINE SAFETY - WEST | jason.lambert@williams.com | 801-584-6657 |  |  |  |  | JASON LAMBERT | MGR. PIPELINE SAFETY - WEST | 801-584-6657 | jason.lambert@williams.com | ON 9/4/19, WILLIAMS NORTHWEST PIPELINE (NWP) CUSTOMER (AVISTA) GAS CONTROL REPORTED HIGH PRESSURE ALARM TO THE NWP CONTROL ROOM AT 04:04 PT. THE NWP PIPELINE CONTROLLER CONTACTED THE ON-CALL TECHNICIAN AND DISPATCHED HIM TO THE SITE AT 04:14 PT TO INVESTIGATE. THE TECHNICIAN ARRIVED ONSITE AT 04:55 PT TO FIND THE NWP RELIEF VALVE VENTING. THE TECHNICIAN MOVED FLOW FROM PRIMARY RUN TO SECONDARY RUN. THIS LOWERED PRESSURE TO 340 PSIG AND THE RELIEF VALVE RE-SEATED AND STOPPED BLOWING. THE TECHNICIAN ISOLATED, LOCKED OUT AND DEPRESSURIZED THE PRIMARY METER RUN AT 05:10 PT. THE TECHNICIAN DISASSEMBLED THE MOONEY REGULATOR PILOT AND BOOT TO INVESTIGATE. THE TECHNICIAN FOUND A LARGE AMOUNT OF ICE BUILT UP ON PILOT STEM. THE RESULTS OF THE INVESTIGATION WERE: THE REGULATOR PILOT FAILURED DUE TO ICE IN PILOT, CAUSING RISE IN PRESSURE AND THE RELIEF VALVE TO OPERATE. THE ICE IN THE PILOT WAS DETERMINED TO BE CASUED BY DITHIAZINE BUILD UP IN PILOT FILTER AND FILTERS FAILURE TO CONTAIN THE HYDRATES CREATED BY THE THE REACTION OF THE FILTER MEDIA REMOVING THE DITHIAZINE. PROPER REPAIRS WERE MADE ON 9/4/19 INCLUDING: 1) A NEW SULFUR FILTER WAS INSTALLED; AND 2) AN ADDITIONAL DESICANT FILTER IN SERIES AFTER THE SULFUR FILTER TO CAPTURE HYDRATES. NRC REPORTING: AT 08:45, WILLIAMS ENGINEERING PERSONNEL DISCOVERED THE ESTIMATED VOLUME OF GAS RELEASED EXCEEDED THE 3,000 MCF REPORTING THRESHOLD. AS A RESULT, THE WILLIAMS SECURITY OPERATION CENTER NOTIFIED THE NRC AT 09:31 (INCIDENT REPORT # 1257199). A 48-HOUR UPDATE REPORT (INCIDENT REPORT # 1257382) WAS MADE TO THE NRC ON 9/5/19 AT 16:06. AT THE TIME OF THE INCIDENT, THE NWP SCADA MONITORING WAS TEMPORARILY DISABLED DUE TO SCHEDULED MAINTENANCE. PREARRANGED PLANS WERE CONFIRMED BEFORE BEING DISABLED THAT AVISTA WOULD MONITOR AND NOTIFY NWP CONTROL ROOM AS APPROPRIATE. AFTER SCHEDULED MAINTENANCE CONCLUDED, THE NWP SCADA RETURNED TO FULL SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190110 | 32872 | 2019-10-04 11:35 | SUPPLEMENTAL FINAL | 31286 | ONEOK GAS TRANSPORTATION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2019-09-05 12:30 | 2019 |  |  | 34.3043 | -97.4476 | 1257346 | 2019-09-05 13:05 |  | NATURAL GAS |  | 11683 | 1130 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-09-05 14:30 | 2019-09-06 02:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-09-05 12:30 | 2019-09-05 13:00 | ONSHORE | OK | 73438 | HEALDTON | CARTER | MILEPOST | LINE Q | LINE Q | Q | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 24 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 |  | 0.203 | 42000 | CARBON STEEL | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | LONE STAR STEEL COMPANY | COAL TAR | [28 empty] | 1961 | 1961 | CARBON STEEL |  | MECHANICAL PUNCTURE | 8 | 8 | [7 empty] | CLASS 1 LOCATION | NO |  | 330 |  | NO | NO | NO |  | 0 | 0 | 1673 | 1707.04274035898 | 29209 | 29209 | 57000 | 58159.8542740359 | 8000 | 8162.78656477697 | 0 | 0 |  |  | 95882 | 61509.7164386462 | 97238.6835791719 | [8 empty] | 535 |  | 565 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 36960 | NO |  |  |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS A THIRD PARTY DAMAGE AND NOT A DIRECT RESULT OF A CONTROLLERS ACTIONS. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  |  |  | YES | [6 empty] | FARMER | FARM EQUIPMENT | GRADING | NO | [5 empty] | YES | 14 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | JACK CROW | COMPLIANCE SPECIALIST | jcrow@oneok.com | 4053232492 |  |  |  |  | JACK CROW | COMPLIANCE SPECIALIST | 4053232492 | jcrow@oneok.com | AT APPROXIMATELY 12:30 PM ON 9/5/2019 A LANDOWNER'S EMPLOYEE OPERATING A DOZER WITHOUT A ONE CALL TICKET STRUCK A 12 INCH NATURAL GAS PIPELINE NEAR THE TOWN OF HEALDTON IN CARTER COUNTY. ONEOK WAS NOTIFIED BY A THIRD PARTY CALL TO OUR CONTROL CENTER AT APPROXIMATELY 12:15 PM WHICH MATCHED WHAT THEY WERE SEEING IN SCADA. ONEOK PIPELINE CONTROL CENTER DISPATCHED LOCAL FIELD OPERATORS TO THE LOCATION AND SET UP AN EMERGENCY BRIDGE CALL FOR THE INCIDENT. FIELD OPERATIONS PERSONNEL ARRIVE ON LOCATION AT APPROXIMATELY 13:00 HOURS AND CONFIRMED THE RELEASE WAS ON THE ONEOK PIPELINE. FIELD PERSONNEL BEGAN TO ISOLATED THE DAMAGED AREA AND WORKED TO REROUTE GAS TO MAINTAIN SERVICE TO LOCAL COMMUNITIES. AT APPROXIMATELY 14:30 HOURS THE DAMAGE SECTION OF THE ONEOK Q PIPELINE WAS ISOLATED. ONCE GAS WAS REMOVED FROM THE PIPELINE FIELD PERSONNEL REMOVED THE DAMAGED SECTION OF PIPE AND NEW PRE-TESTED PIPE WAS INSTALLED. THE PIPELINE WAS RETURNED TO NORMAL OPERATIONS AT APPROXIMATELY 02:00 ON 9/06/2019. LOCAL ONEOK OPERATIONS MANAGEMENT MET WITH THE LANDOWNER'S EMPLOYEE TO DISCUSS THE IMPORTANCE OF CALLING OKLAHOMA ONE-CALL WHENEVER CONDUCTING ANY EXCAVATIONS. ONEOK ALSO VERIFIED THE LANDOWNER IS IN THE CURRENT ONEOK PUBLIC AWARENESS DATABASE. ONEOK HAS ALSO VERIFIED THE PIPELINE IS CLEARLY IDENTIFIED WITH PIPELINE MARKER SIGNS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190111 | 32799 | 2019-10-10 16:30 | ORIGINAL FINAL | 12576 | ENABLE MISSISSIPPI RIVER TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2019-09-13 16:05 | 2019 |  |  | 38.2619 | -90.4097 | 1258179 | 2019-09-13 18:02 |  | NATURAL GAS |  | 0 | 1 | 3 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE PIPELINE REMIANED IN SERVICE DURING CLEANUP. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-09-13 16:05 | 2019-09-13 15:00 | ONSHORE | MO | 63048 | HERCULANEUM | JEFFERSON | MILEPOST | NA | ML1 | ML1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | SCRAPER/PIG TRAP | [38 empty] | 2019 |  | CARBON STEEL |  | OTHER | [8 empty] | WHILE BLOWING DOWN A PIG TRAP, A SLUG OF HYDROCARBON LIQUID ATOMIZED AND BLEW INTO THE AIR. | CLASS 3 LOCATION | NO |  | 371 |  | NO | YES | NO |  | 400000 | 408139.328238848 | 5 | 5.10174160298561 | 0 | 0 | 0 | 0 | 60000 | 61220.8992358273 | 40000 | 40813.9328238848 | MISCELLANEOUS, VEHICLE, OVERHEAD |  | 500005 | 234185.743291274 | 510179.262040164 | [8 empty] | 450 |  | 595 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 546 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL ROOM DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | UNEXPECCTED LIQUID IN TRANSMISSION LINE. | [147 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | IN PREPARATION FOR AN ILI RUN, TEMPORARY PIG TRAPS WERE INSTALLED ON ML1 AT VARIOUS LOCATIONS THROUGHOUT THE LINE. AFTER INSTALLATION OF PIG TRAPS, THE LOCAL OPERATION TEAMS BEGAN PIGGING THE LINE IN PREPARATION FOR THE ILI RUN. AFTER RECEIVING THE "DRY" PIGS IN JEFFERSON COUNTY, MISSOURI THE OPERATIONS GROUP BLEW DOWN THE JOACHIM CREEK RECEIVER BARREL. LIQUIDS WERE NOT ANTICIPATED TO BE IN THE LINE. GAS FOLLOWED BY A BROWN MIST WAS RELEASED FROM A 3" BLOWDOWN ON THE PIG TRAP. THE MIST WAS BLOWN HIGH IN THE AIR INTO TREES, A NEARBY TRIBUTARY, AND SPREAD ACROSS 2.5 ACRES INTO A HOUSING DEVELOPMENT. THE AFFECTED AREA WAS REMEDIATED, AND THE RECOVERED HYDROCARBON LIQUID WILL BE RECYCLED AS USED OIL. A CALL WAS PLACED TO THE NRC(#1258179) ON 9/13/2019 AT 18:02 AND A 48 HR. FOLLOW UP (#1258293) WAS PLACED ON 9/15/2019 AT 12:36.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190112 | 32833 | 2019-10-16 15:00 | ORIGINAL FINAL | 18152 | SEA ROBIN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2019-09-19 16:24 | 2019 |  |  | 28.701 | -91.6775 | 1258724 | 2019-09-19 16:32 |  | NATURAL GAS |  | 0 | 48609 | 3 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-09-19 16:27 | 2019-09-29 18:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-09-19 16:24 | 2019-09-23 16:30 | OFFSHORE | [28 empty] | 100 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EUGENE ISLAND | 197 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 24 |  | 0.5 | 60000 | UNKNOWN | DSAW |  | UNKNOWN | OTHER | MASTIC AND CONCRETE | [27 empty] | 1970 | 1970 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 585 |  | NO | NO | NO |  | 0 | 0 | 108000 | 110197.618624489 | 0 | 0 | 360000 | 367325.395414964 | 0 | 0 | 0 | 0 |  |  | 468000 | 219195.663763995 | 477523.014039453 | [8 empty] | 850 |  | 1250 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 247653 | NO |  | YES | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | AIR PATROL |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS TOO SMALL FOR SCADA TO DETECT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  | YES | [7 empty] | YES | SAMPLE ANALYSIS WAS UTILIZED | YES | [5 empty] | YES | NO | YES | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | 9/19/19 RECEIVED NOTIFICATION OF A POSSIBLE LEAK. NRC TELEPHONIC NOTIFICATION MADE AT 16:32 NRC#1258724. 9/20/19 PHMSA AID NOTIFIED 07:53 9/21/19 48-HOUR UPDATE NRC NOTIFICATION MADE AT 13:38 NRC# 1258902. PHMSA AID UPDATED AT 15:10 9/23/19 PHMSA AID UPDATED AT 9:47. 9/29/19 REPAIR COMPLETED. 9/30/19 LINE WAS RETURNED TO SERVICE. PART A, QUESTION 10: THE ESTIMATED VOLUME OF UNINTENTIONAL GAS RELEASED WAS 0. THE LEAK WAS INTERMITTENT FROM A PINHOLE AND THERE WERE NO BUBBLES, ONLY SHEEN FROM THE CONDENSATE.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20190113 | 33008 | 2019-10-18 22:43 | SUPPLEMENTAL FINAL | 39352 | GENESIS OFFSHORE HOLDINGS, LLC | 919 MILAM STREET SUITE 2100 | HOUSTON | TX | 77002 | 2019-09-20 11:30 | 2019 |  |  | 27.9432 | -94.3886 | 1258971 | 2019-09-20 12:00 |  | NATURAL GAS |  | 5500 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-09-20 12:00 | 2019-10-10 16:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-09-20 11:30 | 2019-10-02 23:15 | OFFSHORE | [28 empty] | 350 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | HIA | 582 | BELOW WATER, PIPE ON OR ABOVE SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 30 |  | 0.5 | 60000 | 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | ITALSIDER | ASPHALT | [28 empty] | 1977 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 143 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 12000 | 12000 | 700000 | 714243.824417985 | 0 | 0 | 0 | 0 |  |  | 712000 | 340297.706922053 | 726243.824417985 | [8 empty] | 840 |  | 1440 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 77088 | NO | YES | [6 empty] | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK OCCURRED SUB-SEA AND NO CONTROLLER'S ACTIONS WERE RELATED. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN | [5 empty] | YES | THE CAUSE IS LIKELY INTERNAL CORROSION HOWEVER FURTHER CAUSE-ANALYSIS CANNOT BE PERFORMED DUE TO THE LOCATION OF THE PIPE. |  |  | YES | THE CAUSE IS LIKELY INTERNAL CORROSION HOWEVER FURTHER CAUSE-ANALYSIS CANNOT BE PERFORMED DUE TO THE LOCATION OF THE PIPE. |  |  |  |  | YES | STRAIGHT PIPE NOT ON A LOW POINT. | NO | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | JORGE MORICE | PIPELINE COMPLIANCE SPECIALIST | jorge.morice@genlp.com | 7137251663 |  |  |  |  | JOHN JEWETT | DOT COMPLIANCE MANAGER | 7138602605 | john.jewett@genlp.com | WHILE PERFORMING A ROUTINE VISIT TO HIA 582 MANIFOLD PLATFORM, GENESIS PERSONNEL NOTICED AN AREA OF DISTURBED WATER TO THE SOUTH OF THE FACILITY. PERSONNEL INVESTIGATED THE AREA WITH A HELICOPTER AND FOUND THAT THERE WERE GAS BUBBLES COMING TO THE SURFACE OVER GENESIS 30" GAS PIPELINE. PERSONNEL MADE NOTIFICATIONS AND ISOLATED THE PIPELINE SEGMENT. THERE WAS NO SHEEN ASSOCIATED WITH THIS EVENT. DIVE CREW ARRIVED ON THE SCENE FOR REPAIRS WITH A CLAMP. THE DIVERS DESCRIBED THE ENVIRONMENT AS HAVING POOR VISIBILITY BUT DESCRIBED RELEASE POINT AS A THIN "SPLIT." UT MEASUREMENTS TAKEN NEAR THE RELEASE SITE INDICATED LITTLE TO NO METAL LOSS ON THE PIPE EXCEPT IMMEDIATELY ADJACENT TO THE SPLIT. AFTER THE TEST, THE PIPE WAS PRESSURED UP AGAIN WITHOUT ANY LEAKAGE. PART E, QUESTION 5C - THIS SEGMENT IS ISOLATED BY CLOSING 3 UPSTREAM VALVES AND ONE DOWNSTREAM VALVE. THE DISTANCE REPORTED IN THIS QUESTION IS THE LONGEST DISTANCE BETWEEN VALVES USED. PART G: EARLY ANALYSIS APPEARS TO POTENTIALLY POINT TO SOME TYPE OF CORROSION EVENT HOWEVER, DUE TO THE DEPTH OF THE PIPE AND THE POOR VISIBILITY ON THE SEA FLOOR, THE DATA AVAILABLE MAKES IT DIFFICULT TO DETERMINE WITH HIGH CONFIDENCE WHETHER IT IS INTERNAL OR EXTERNAL AT THIS TIME. GENESIS WILL COLLABORATE WITH A THIRD PARTY SME TO AID IN THE DETERMINATION. SUPPLEMENTAL (11/18/2020) - AFTER CONSULTING WITH A THIRD PARTY CORROSION EXPERT, GENESIS BELIEVES THE LEAK WAS PROBABLY CAUSED BY INTERNAL CORROSION, HOWEVER IT IS NOT POSSIBLE TO DETERMINE WHAT TYPE OF INTERNAL CORROSION IS RESPONSIBLE WITH A HIGH DEGREE OF CONFIDENCE. PRIOR TO REPAIRING THE LEAK SITE, DIVERS CONDUCTED SEVERAL UT SCANS OF THE RELEASE AREA, BOTH CIRCUMFERENTIALLY AND UPSTREAM/DOWNSTREAM FROM THE RELEASE SPOT. THE TESTS SHOWED METAL LOSS ONLY AT THE SPOT OF THE SPLIT BUT NOWHERE ELSE THAT WAS SCANNED. FURTHER ASSESSMENT IS NOT POSSIBLE SINCE VISIBILITY ON THE SEA FLOOR IS VERY POOR AT THIS SIGHT AND ALSO, THE SEGMENT IS NOT ILI PIGGABLE DUE TO THE DIFFERING PIPE DIAMETERS OF THE CONNECTING UPSTREAM PIPELINES. SINCE AT THIS TIME IT IS DIFFICULT TO DEFINITIVELY DETERMINE WHETHER THE EVENT WAS CAUSED BY INTERNAL OR EXTERNAL CORROSION, GENESIS HAS COMPLETED SEVERAL MITIGATING TECHNIQUES TO ENHANCE THE CATHODIC PROTECTION OF THIS SEGMENT. FIRST, GENESIS HAS INSTALLED AN ADDITIONAL SACRIFICIAL ANODE ON THIS SECTION OF PIPE. SECOND, AN ADDITIONAL WATER TRAP AND CORROSION COUPON HAVE BEEN INSTALLED ON HIA 582. FINALLY, GENESIS INTENDS TO RECOMMEND TREATMENT MEASURES FOR THE UPSTREAM OPERATOR TO FURTHER PROTECT THE DOWNSTREAM SEGMENTS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190114 | 33487 | 2019-10-21 14:19 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-10-04 15:45 | 2019 | EASTERN | YES | 39.9246 | -81.6915 | 1260273 | 2019-10-04 16:37 | 1260341 | NATURAL GAS |  | 897 | 23595 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-10-04 17:15 | 2019-10-08 05:40 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-10-04 17:15 | VALVE CLOSURE |  | 2019-10-04 17:15 | 0 | 2019-10-04 15:57 | 2019-10-04 15:57 | ONSHORE | OH | 43732 | Not Within a Municipality | MUSKINGUM | MILEPOST | 208-4+11.53 | LINE 200-4 | 204-4 TO 209-4 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 45 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION | [19 empty] | FILLET WELD | [18 empty] | 2009 | 2008 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 698 |  | NO | NO |  |  | 0 | 0 | 56628 | 57780.2846987738 | 2153 | 2153 | 105000 | 107136.573662698 | 1300 | 1326.45281677626 | 5825 | 5943.52896747823 | LAB ANALYSIS; | 2.4 | 170906 | 81270.4159531262 | 174339.840145726 | 0 | 0 | 0 | 0 | NO |  |  |  | 730 | 746000 | 790 | 192.619(A)(1) |  | 1968-11-16 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 68957 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IMMEDIATE EXCAVATION AT SITE FOUND CRACK IN THE NECK OF THE HOT TAP FITTING; NOT CONTROL ROOM DETECTABLE LEAK; | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES |  |  |  | YES | MECHANICAL VIBRATION |  | YES | [14 empty] | YES | [8 empty] | 2220 | [54 empty] | YES | YES | [6 empty] | 2018 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2011 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [45 empty] | NO |  |  | NO | [13 empty] | YES | 2009 | [6 empty] | YES | [55 empty] | WM. MARTIN MULLER | SPECIALIST-PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205-325-3863 | 205-325-3592 | CARL BAYER | carl_bayer@kindermorgan.com | 740-638-2101 | JAIME HERNANDEZ | DIRECTOR ENGINEERING CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | NRC #1260273; NRC #1260341 (48-HOUR); 36-INCH TENNESSEE GAS PIPELINE COMPANY, L.L.C. (TGP); LINE 200-4 WITH HOT TAP RECEIVING NATURAL GAS FROM TALLGRASS BIG MUSKINGUM METER STATION: AT 15:45-HOURS, THE LANDOWNER OBSERVED DIRT BLOWING AT THE HOT TAP RISER AND NOTIFIED A GRANDSON WHO NOTIFIED HIS BROTHER, A TGP COMPANY EMPLOYEE. AT 15:57-HOURS, EMPLOYEE ARRIVED ON SITE AND CONFIRMED A LEAK AT THE HOT TAP RISER. AT 16:15-HOURS, ALTHOUGH THE LANDOWNER'S HOME WAS OUTSIDE OF THE PIR (MORE THAN 1,900 FEET FROM THE LEAK SITE) THE LANDOWNER'S GRANDSON CHOSE TO RELOCATE THE LANDOWNER TO A RELATIVE'S HOME. THE DOWNSTREAM AND THE UPSTREAM PIPELINE MAIN LINE VALVES WERE CLOSED AT 17:15-HOURS. FOLLOWING NOTIFICATION TO APPLICABLE EMERGENCY RESPONDERS, AT 19:22-HOURS, BLOW-DOWN OF THE PIPELINE VALVE SECTION BEGAN. ON OCTOBER 5, 2019, AT 00:05-HOUR, BLOW-DOWN OF THE VALVE SECTION WAS COMPLETE. EXCAVATION AT THE HOT TAP SITE FOUND THE NECK OF THE HOT TAP FITTING CONTAINED A CRACK. THE HOT TAP WAS CUT OUT OF THE PIPELINE AND THE PIPELINE WAS REPAIRED WITH REPLACEMENT PIPE. DUE TO CHANGES IN BUSINESS NEEDS, THE HOT TAP CONNECTION WILL NOT BE REPLACED. THE HOT TAP FITTING WENT THROUGH LABORATORY ANALYSIS FOR CAUSE OF THE NECK FILLET WELD CRACK. THE JANUARY 17, 2020 METALLURGICAL REPORT CONCLUDES THE HOT TAP NECK FILLET WELD CRACK OCCURRED FROM FATIGUE. SAID REPORT FINDS FATIGUE CAUSE WAS STRESS AND / OR VIBRATION FROM PULSATION OF THE COMPONENT AND INSUFFICIENT SUPPORT OF A NEARBY BLOW OFF VALVE ASSEMBLY. NO MATERIAL DEFICIENCIES WERE FOUND WHICH WOULD HAVE CONTRIBUTED TO THE COMPONENT FAILURE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190115 | 33452 | 2019-10-25 16:04 | SUPPLEMENTAL FINAL | 1217 | BEAR CREEK STORAGE CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-09-26 18:50 | 2019 | CENTRAL | YES | 32.3894 | -92.939 | 1259488 | 2019-09-26 21:01 | 1259665 | NATURAL GAS |  | 28779 | 2225 | 0.9 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-09-26 20:10 | 2020-02-04 11:00 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-09-26 19:09 | VALVE CLOSURE |  | 2019-09-26 18:50 | 0 | 2019-09-26 19:03 | 2019-09-26 19:31 | ONSHORE | LA | 71008 | BIENVILLE | BIENVILLE | MILEPOST | WELLHEAD 12-3 | LINE #4 | LATERAL 12-3 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 3 | NO | 0.3 | 52000 | X52 | SEAMLESS |  | UNKNOWN | PAINT |  | YES | [26 empty] | 1979 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | THE FAILURE OCCURRED IN AN ELBOW. THE ORIENTATION OF THE RUPTURE WAS AT THE EXTRADOS OF THE ELBOW. THE ELBOW CHANGES DIRECTION 90-DEGREES. | 9 | 4.5 |  | CLASS 1 LOCATION | NO |  | 115 |  | NO | NO |  |  | 0 | 0 | 5514 | 5626.20063977253 | 71323 | 71323 | 128048 | 130653.56175582 | 1688 | 1722.34796516794 | 14396 | 14688.9344233162 | $12,090 - ENVIRONMENTAL REMEDIATION $2,306 - METALLURGICAL EVALUATION/REPORT | 2.4783 | 220969 | 144033.011239865 | 224014.044784077 | 0 | 0 | 0 | 0 | NO |  |  |  | 2449 | 4968.7 | 3100 | 192.619(A)(1) |  | 1981-11-13 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | REMOTELY CONTROLLED | AUTOMATIC | 12338 | NO | [5 empty] | YES | THE PIPE DIAMETER FOR THIS SEGMENT IS 3-INCHES AND GOES FROM THE WELL VALVE TO THE METER RUN, APPROXIMATELY 22FT. OF PIPE. | YES |  |  |  |  | YES | DIAMETER, BENDS, AND SEGMENT LENGTH | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | EROSION |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES | NO | NOT APPLICABLE - NOT MAINLINE PIPE | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | YES |  |  | 2004 | [6 empty] | YES | [53 empty] | KRISTIN VAN DER LAAN | ENGINEERING MANAGER - CODES AND COMPLIANCE | kristin_vanderlaan@kindermorgan.com | 303-914-7753 |  |  |  |  | JAIME HERNANDEZ | ENGINEERING DIRECTOR - CODES AND COMPLIANCE | 713-369-9443 | jaime_hernandez@kindermorgan.com | ON SEPTEMBER 26, 2019 THE BEAR CREEK STORAGE COMPANY (BCSC) LINE 4 LATERAL 12-3 RUPTURED RELEASING NATURAL GAS TO ATMOSPHERE. THE LEAK WAS DETERMINED TO BE ON BCSC LINE 4 FROM AN ABOVEGROUND 3-INCH PIPELINE CONNECTING A METER STATION IN THE AREA TO STORAGE WELL 12-3 (OFTEN REFERRED TO AS A "WELL LEAD"). FOLLOWING AN INVESTIGATION, PRELIMINARY FINDINGS POINTED TO LOSS OF INTERNAL PIPE WALL THICKNESS IN THE 3-INCH PIPE CAUSED THE PIPE TO RUPTURE AND BREAK APART. SAMPLES OF THE PIPE WERE SUBMITTED FOR METALLURGICAL TESTING AND IT WAS DETERMINED THAT THE RUPTURE WAS DUE TO EROSION (AS INDICATED IN PART G1). DURING THE NATURAL GAS RELEASE BETWEEN 0.7 AND 0.9 BARRELS OF LIQUIDS, CONSISTING OF A MIXTURE OF WATER AND DISTILLATE, WERE ALSO RELEASED UNDER HIGH PRESSURE. DUE TO THE HIGH PRESSURE OF THE RELEASE, THE LIQUIDS WERE RELEASED IN A BROAD AREA ADJACENT TO THE WELL SITE. THE SURFACE OF THIS ENTIRE AREA WAS TREATED WITH BIO-AMENDMENTS. THE FOLLOWING TIMELINE IS BASED ON BEAR CREEK STORAGE COMPANY (BCSC) INVESTIGATION: SEPTEMBER 26, 2019 (ALL TIMES CST) 18:50 (APPROX.) - DURING INJECTION LINE 4 PIPELINE RUPTURES RELEASING NATURAL GAS TO ATMOSPHERE. STORAGE WELL 12-3 SURFACE SAFETY VALVE SHUTS IN AUTOMATICALLY. 19:03 - BCSC PERSONNEL (EMPLOYEE A) NOTIFIED OF NATURAL GAS RELEASE NEAR STORAGE WELL 12-3 BY MOWING CONTRACTORS. 19:09 - EMPLOYEE A NOTIFIED THE BCSC OPERATOR TO SHUT-IN (CLOSE) UPSTREAM VALVE, LINE 4 FIELD HEADER ISOLATION VALVE. 19:31 - EMPLOYEE A ARRIVED ON-SITE, CONFIRMED GAS VENTING WAS AT WELL 12-3 AND ITS ASSOCIATED METER STATION BUT DID NOT HAVE ENOUGH INFORMATION TO QUANTIFY THE EXTENT OF THE RELEASE DUE TO LOW VISIBILITY AT DUSK AND BECAUSE HE STAYED AT A SAFE DISTANCE BASED ON COMPANY'S PROCEDURES. SUBSEQUENTLY, HE CONTINUED WITH HIS EMERGENCY RESPONSE ACTIONS, PROCEEDING TO SHUT-IN THE REMAINING WELLS ON LINE 4. 19:45 - INTERNAL EMERGENCY RESPONSE LINE (ERL) CALL NOTIFICATIONS INITIATED PER COMPANY PROCEDURES TO DISCUSS THE INCIDENT. INITIAL ASSESSMENT OF THE INCIDENT GAVE NO INDICATIONS OF NRC REPORTABLITY. NOTE THAT EMPLOYEE A WAS UNABLE TO ATTEND THE CALL DUE TO EMERGENCY RESPONSE ACTIVITIES. 20:10 - LEAK SITE ISOLATED AND EMPLOYEE A WAS ALLOWING THE PIPE SEGMENT TO BLOWDOWN. 20:40 (APPROX.) - ONCE THE SEGMENT WAS BLOWN DOWN TO A SAFE LEVEL, EMPLOYEE A WAS ABLE TO ACCESS THE LOCATION AND ASSESS THE INCIDENT. 20:43 - DETERMINED THAT THE INCIDENT WOULD LIKELY MEET THE NRC REPORTABLE CRITERIA. 20:57 - CALL TO NRC INITIATED (#1259488). BY 21:00 - THE GAS RELEASE HAD COMPLETELY STOPPED. ADDITIONAL NOTES: 48-HOUR NRC UPDATE = 1259665, REPORT TAKEN AT 14:20C ON SEPTEMBER 28, 2019.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20190116 | 32923 | 2019-11-05 14:51 | SUPPLEMENTAL FINAL | 18152 | SEA ROBIN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2019-10-06 13:13 | 2019 |  |  | 28.3858 | -90.1448 | 1260388 | 2019-10-06 14:51 |  | NATURAL GAS |  | 1000 | 1661 | 4.8 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-10-06 14:51 | 2019-10-13 06:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-10-06 13:13 | 2019-10-07 14:30 | OFFSHORE | [28 empty] | 236 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SOUTH TIMBALIER | 229 | BELOW WATER, PIPE ON OR ABOVE SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 10 |  | 0.5 | 42000 | API 5L | SEAMLESS |  | US STEEL | EPOXY | [28 empty] | 1996 | 1995 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 239 |  | NO | NO | NO |  | 0 | 0 | 3577 | 3649.7859427759 | 2149 | 2149 | 236954 | 241775.61595877 | 0 | 0 | 0 | 0 |  |  | 242680 | 114884.701351097 | 247574.401901546 | [8 empty] | 939 |  | 1200 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 59664 | NO | YES | YES | YES |  |  |  |  | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT DUE TO A SMALL PINHOLE LEAK | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | PINHOLE LEAK |  |  |  |  | YES | LOW FLOW | YES | [7 empty] | YES | PINHOLE AT THE 6:00 OCLOCK POSITION | YES | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | 10/6/19 RECEIVED NOTIFICATION OF A POSSIBLE LEAK. NRC TELEPHONIC NOTIFICATION MADE AT 14:51 NRC#1260388. PHMSA AID NOTIFIED 15:29. 10/8/19 48-HOUR UPDATE NRC NOTIFICATION MADE AT 9:24 NRC#1260544. PHMSA AID UPDATED AT 13:51. CLAMP INSTALLED AT 18:00. 10/11/19 PHMSA AID UPDATED AT 11:25. 10/13/2019 LINE PRESSURED UP TO OPERATING PRESSURE AT 06:00. 10/14/19 PHMSA AID UPDATED AT 08:38. REPAIR COMPLETED. FLY OVER CONFIRMED NO BUBBLES OR SHEEN PRESENT. 11/12/19 SUPPLEMENTAL-FINAL SUBMITTED TO CORRECT NOMINAL DIAMETER (PART C - 3A) TO 10" AND PART G QUESTION #8 TO "FIELD EXAMINATION."
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190117 | 34868 | 2019-11-12 19:08 | SUPPLEMENTAL | 31531 | ONEOK WESTEX TRANSMISSION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2019-10-20 04:05 | 2019 | CENTRAL | NO | 32.7206 | -102.1715 | 1261647 | 2019-10-20 04:50 |  | NATURAL GAS |  | 0 | 122 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | STATION WAS SHUTDOWN AND ISOLATED, PIPELINE CONTINUED TO FLOW. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2019-10-20 04:05 | 2019-10-20 04:07 | ONSHORE | TX | 79331 | Not Within a Municipality | DAWSON | MILEPOST | COMPRESSOR | LAMESA COMPRESSOR STATION | 500 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 1982 | 1982 | CARBON STEEL |  | OTHER | [8 empty] | COMPRESSOR FIRE. | CLASS 2 LOCATION | NO |  | 476 |  | NO | NO |  |  | 0 | 0 | 361 | 368.345743735561 | 0 | 0 | 10401206 | 10612853.0742847 | 1500 | 1530.52248089568 | 2500 | 2550.8708014928 | 0 | 2.96 | 10405567 | 4873622.14830282 | 10617302.8133108 | 0 | 0 | 0 | 0 | NO |  |  |  | 1134.75 | 180 | 1188 | 192.619(A)(1) |  | 1982-09-29 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO CONTROLLER ACTIONS HAVE TAKEN PLACE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | OTHER | MECHANICAL FAILURE | [20 empty] | YES | STILL UNDER INVESTIGATION | [161 empty] | BRACKEN HILL | COMPLIANCE SPECIALIST | bracken.hill@oneok.com | 806-324-9702 |  |  |  |  | BRACKEN HILL | COMPLIANCE SPECIALIST | 806-324-9702 | bracken.hill@oneok.com | ON OCTOBER 20, 2019 AT 2:27 A.M. A CONTROL ROOM EMPLOYEE RECEIVED AN ACTIVE LOW OIL ALARM AND COMPRESSOR MALFUNCTION ALARM ON UNIT 6307 AT THE LAMESA STATION. A FIELD EMPLOYEE WAS DISPATCHED TO VERIFY THE PROBLEM. AT 4:05 A.M. THE FIELD EMPLOYEE DISCOVERED THE UNIT TO BE ON FIRE. EMERGENCY SERVICES WAS NOTIFIED AND DISPATCHED TO THE STATION. AT 4:07 A.M. A STATION ESD WAS ACTIVATED BY THE FIELD EMPLOYEE, AT 4:46 A.M. THE FIRE WAS CONTAINED, AND NOTIFICATIONS WERE MADE. THE INITIAL CAUSE IS STILL UNDER INVESTIGATION. ONEOK HAS CONTRACTED WITH BAKER RISK OUT OF SAN ANTONIO, TX TO FURTHER INVESTIGATE AS TO THE ROOT CAUSE OF THE INCIDENT. MORE INFORMATION WILL BE UPDATED AS IT BECOMES KNOWN. UPDATE - APRIL 22, 2020 - UPDATED D7B - ESTIMATED COST OF OPERATORS PROPERTY DAMAGE AND REPAIR. COMPLETION OF REPAIRS EXPECTED TO BE COMPLETE EARLY 4TH QUARTER 2020. INVESTIGATION OF FAILURE IS CURRENTLY ON HOLD DUE TO COVID-19 RESTRICTIONS. INVESTIGATION IS EXPECTED TO RESUME LATE MAY 2020. UPDATE - FEBRUARY 17, 2021 - INVESTIGATION IS ONGOING SEVERAL POSSIBLE SCENARIOS ARE BEING LOOKED AT THIS TIME. NOTHING CONCLUSIVE HAS BEEN FOUND THAT WOULD HAVE INITIATED OR FUELED THE FIRE. ADDITIONAL TESTING AND INVESTIGATION IS CONTINUING PENDING COVID-19 RESTRICTIONS AND GUIDELINES. SUBMITTED BY BH.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190118 | 33061 | 2019-11-14 11:18 | SUPPLEMENTAL FINAL | 19730 | TRUNKLINE GAS CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2019-10-17 18:16 | 2019 |  |  | 32.6211 | -91.5767 | 1261451 | 2019-10-17 19:58 |  | NATURAL GAS |  | 41238 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE ESD SYSTEM TRIPPED THE STATION SHUTDOWN TEMPORARILY | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-10-17 18:16 | 2019-10-17 18:35 | ONSHORE | LA | 71237 | EPPS | WEST CARROLL | MILEPOST | VALVE SITE 66 | EPPS COMPRESSOR STATION | EPPS COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | MAINLINE | BALL |  | CAMERON |  |  |  | 1960 | 1960 | CARBON STEEL |  | OTHER | [8 empty] | POWER BREAKER THAT SUPPLIES THE TURBINE CONTROL BUILDING WAS TRIPPED. WHEN THIS BREAKER TRIPPED THE UPS BATTERIES RAN DOWN WHICH ACTIVATED THE ESD SYSTEM. | CLASS 1 LOCATION | NO |  | 745 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 83095 | 83095 | 0 | 0 | 3000 | 3061.04496179136 | 0 | 0 |  |  | 86095 | 87553.459988796 | 86156.0449617914 | [8 empty] | 785 |  | 900 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) | [5 empty] | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [13 empty] | YES | [173 empty] | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | 10/17/19 NRC TELEPHONIC NOTIFICATION MADE AT 19:58 NRC#1261451. PHMSA AID NOTIFIED 20:13. 10/18/19 PHMSA AID UPDATED AT 14:00. 10/19/19 48-HOUR UPDATE NRC NOTIFICATION MADE AT 15:19 NRC#1261620. PHMSA AID UPDATED AT 15:39. THE SUPPLEMENTAL/FINAL REPORT DATED 12/11/19, PROVIDES FURTHER CLARIFICATION/CORRECTIONS FOR THE FOLLOWING SECTIONS: PART A, QUESTION 10. THE ESD SYSTEMS OPERATED AS DESIGNED. THERE WAS A STATION YARD BLOCK VALVE OUTSIDE THE ESD SYSTEM THAT WAS INADVERTENTLY OPEN THAT CONTRIBUTED TO THE AMOUNT RELEASED. PART E, QUESTION 7. RECEIVED AN ESD SAFETY STATUS ALARM FOR THE FUEL METER AT EPPS STATION THAT THE CONTROLLER ACKNOWLEDGED IMMEDIATELY. THE COMMUNICATIONS AT EPPS STATION WENT DOWN THE SAME TIME AS THE ESD TRIPPED. GAS CONTROL COULD NOT SEE A PROBLEM UNTIL THERE WAS A PRESSURE DROP AT THE UPSTREAM AND DOWNSTREAM LOCATIONS. COMMUNICATIONS WERE OUT AT THE STATION SO THE CONTROLLERS WERE NOT ABLE TO CONFIRM AN ACTUAL ESD. CONTROLLERS REVIEWED UPSTREAM AND DOWNSTREAM PRESSURES AND THERE WERE NO NEGATIVE RATE OF CHANGE ALARMS PRESENT. UPSTREAM PRESSURE STARTED TO SHOW A SLOW DECLINE IN PRESSURE. LOCAL SHERIFF'S DEPT CALLED IN A FEW MINUTES LATER AND REPORTED THERE WAS GAS BLOWING AT THE STATION. THE CONTROLLERS IMMEDIATELY DISPATCHED FIELD PERSONNEL TO THE SCENE AND STARTED AN EVERBRIDGE CONFERENCE BRIDGE TO ALERT MANAGEMENT AND FIELD PERSONNEL IN THE AREA. PART E, QUESTION 8. UPDATED YES, BASED ON THE INVESTIGATION NO CONTROLLER ISSUES WERE IDENTIFIED. PART H, THE UPS FOR THE ESD SYSTEM AND COMMUNICATION EQUIPMENT IS SIZED TO MAINTAIN POWER FOR A MINIMUM OF 4 HOURS AND WE HAVE A BACK-UP GENERATOR THAT WILL COME ON-LINE WHEN THERE IS A LOSS OF COMMERCIAL POWER ACROSS THE WHOLE STATION. THE BREAKER THAT TRIPPED WAS SUPPLING POWER TO THE CONTROL BUILDING ONLY, WHERE THE ESD CONTROLS AND COMMUNICATION EQUIPMENT IS LOCATED. IF THERE WOULD HAVE BEEN A LOSS OF COMMERCIAL POWER OF THE WHOLE STATION THE GENERATOR WOULD HAVE STARTED AUTOMATICALLY AND GAS CONTROL WOULD HAVE RECEIVED AN ALARM. THE UPS BATTERIES WOULD NOT HAVE RUN DOWN. THE STATION YARD BLOCK VALVE WAS IDENTIFIED AND LOCKED CLOSED. AN ALARM HAS BEEN INSTALLED TO NOTIFY GAS CONTROL IF THERE IS A FUTURE POWER LOSS AT THIS CONTROL BUILDING TO PREVENT RECURRENCE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190119 | 32938 | 2019-11-14 15:19 | ORIGINAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2019-11-05 06:00 | 2019 |  |  | 29.9338 | -91.7436 | 1263095 | 2019-11-05 06:41 |  | NATURAL GAS |  | 15 | 97 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-11-10 14:30 | 2019-11-11 21:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-11-02 10:35 | 2019-11-02 11:25 | ONSHORE | LA | 70544 | JEANERETTE | IBERIA | MILEPOST | 7407+97 | INDEX 205 | IOWA CS TO FRANKLIN, LA | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 58 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | MECHANICAL COUPLING | 1931 |  | CARBON STEEL |  | LEAK |  |  | OTHER | LEAKING MECHANICAL COUPLING | [5 empty] | CLASS 1 LOCATION | NO |  | 128 |  | NO | NO | NO |  | 0 | 0 | 271 | 276.51439488182 | 42 | 42 | 132000 | 134685.97831882 | 500 | 510.17416029856 | 0 | 0 |  |  | 132813 | 62229.0720968502 | 135514.666874 | [8 empty] | 267 |  | 480 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 18469 | NO | [5 empty] | YES | MECHANICAL COUPLINGS AND ACETYLENE WELDS PREVENT INLINE INSPECTION | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | MINOR LEAK NOT DETECTABLE ON SCADA SYSTEM. NRC WAS CALLED ONLY BECAUSE THE REPAIR COSTS ARE EXPECTED TO EXCEED $50,000. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | YES | [29 empty] | YES | MECHANICAL COUPLING LEAK | [200 empty] | SHANNON MATTINGLY | OQ PA AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipeline.com | 270-6886357 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 2706886497 | tina.baker@bwpipelines.com | ON 11-2-19 AT APPROXIMATELY 10:35 AM, GULF SOUTH RECEIVED A CALL FROM AN ATMOS TECHNICIAN ABOUT A POTENTIAL LEAK ON A GULF SOUTH PIPELINE. GULF SOUTH INVESTIGATED AND DETERMINED THERE WAS A MECHANICAL COUPLING LEAK ON ITS INDEX 205 (8" LINE) IN IBERIA PARISH, LOUISIANA. AFTER LOWERING THE PRESSURE BY 20% (270 PSI TO 215 PSI) AND MONITORING THE AREA NEAR THE LEAK WITH LEL EQUIPMENT, IT WAS DETERMINED THAT THE LEAK COULD BE MONITORED UNTIL A REPAIR PLAN WAS FORMULATED. BECAUSE IT WAS A COUPLING, A PRESSURIZED WELD OVER SLEEVE WOULD HAVE TO BE INSTALLED TO CORRECT THE LEAK. FOR BUSINESS REASONS, THE LINE WOULD NEED TO BE ISOLATED WITH STOPPLE FITTINGS AND DE-PRESSURED AND THE CUSTOMERS LOCATED WITHIN THE AFFECTED AREA SERVED BY A TEMPORARY BYPASS INSTALLED ON AN ADJACENT GULF SOUTH PIPELINE. ONCE THE LINE WAS DE-PRESSURED, THE WELD OVER SLEEVE COULD BE SAFELY INSTALLED. ON 11-5-19, WHEN THAT DECISION WAS MADE, THE REPAIR COSTS WERE THEN EXPECTED TO EXCEED THE $50,000 INCIDENT REPORTING CRITERIA AND THE NRC WAS CALLED. THE NRC NOTIFICATION FOR THIS INCIDENT WAS ONLY MADE BECAUSE OF ESTIMATED REPAIR COSTS. THE RESPONSES TO PART E QUESTIONS 5A AND 5B STATE THAT MANUAL VALVES UPSTREAM AND DOWNSTREAM WERE USED TO ISOLATE THE SEGMENT. ALTHOUGH THE NEAREST UPSTREAM AND DOWNSTREAM VALVES ARE MANUAL, STOPPLES WERE USED TO ISOLATE THE SECTION. THAT IS NOT AN OPTION IN THE SELECTIONS FOR THIS REPORT. ON 11-11-19 REPAIRS WERE COMPLETED AND LINE WAS RETURNED TO SERVICE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190120 | 33888 | 2019-11-22 10:13 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2019-10-23 13:00 | 2019 | EASTERN | NO | 39.8734 | -75.7419 | 1261975 | 2019-10-23 14:40 |  | NATURAL GAS |  | 730 | 730 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | POST-MAINTENANCE/REPAIR | [5 empty] | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-10-23 13:00 | VALVE CLOSURE |  | 2019-10-23 13:00 | 0 | 2019-10-23 12:30 | 2019-10-23 13:30 | ONSHORE | PA | 19348 | KENNETT SQUARE | CHESTER | MILEPOST | 9.78/516+26 | DELAWARE POWER & LIGHT LATERAL | DELAWARE POWER & LIGHT LATERAL | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 16 |  | 0.25 | 52000 | APL 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | YOUNGSTOWN STEEL | COAL TAR |  | YES | [26 empty] | 1964 | 1964 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 1300 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 65000 | 66322.6408388129 | 150 | 153.052248089568 | 0 | 0 |  | 0 | 65150 | 30514.0972098809 | 66475.6930869024 | 0 | 0 | 0 | 0 | NO |  |  |  | 600 | 0 | 780 | 192.619(A)(4) |  | 1990-06-15 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | REMOTELY CONTROLLED | REMOTELY CONTROLLED | 81312 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PINHOLE LEAK WAS DISCOVERED DURING A DIG | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | YES | YES | [13 empty] | YES | PIN-HOLE LEAK ON LONG SEAM. | [7 empty] | YES | [7 empty] | 1257 | [54 empty] | YES | YES | YES |  | YES | YES |  |  | 2017 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2010 | FREE SWIMMING | METAL LOSS |  | STANDARD RESOLUTION |  | 2018 | FREE SWIMMING | STANDARD RESOLUTION | [17 empty] | 2017 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | 2010 | FREE SWIMMING | STANDARD RESOLUTION |  | NO CUPS | 2018 | FREE SWIMMING | [12 empty] | YES | 1990 | 1257.35 | NO | [13 empty] | YES |  |  | 2019 | 2019 | [5 empty] | YES | YES | [52 empty] | MARK CLARKE | SENIOR ENGINEER | mark.clarke@williams.com | 7132153051 |  |  |  |  | TYSON GREEN | MANAGER PIPELINE SAFETY | 7132152535 | tyson.green@williams.com | DURING ANOMALY INVESTIGATION OF FEATURE ID 1160 (DPLL A-4I_156_2019) THE FINDING REVEALED POSSIBLE LACK OF FUSION IN THE LONG SEAM CREATING A SMALL THROUGH WALL DEFECT LOCATED AT 11:30 POSITION ON THE DP&L LATERAL LOCATED AT APPROXIMATE MP 9.78. THE DEFECT PRODUCED A LOSS OF CONTAINMENT (GAS LEAK). THE REPAIRS WERE COMPLETED ON OCTOBER 26, 2019 DURING THE INSPECTION OF THE PIPE, (6) ID CONNECTED LACK OF FUSION INDICATIONS WERE FOUND IN THE INSPECTION AREA WITH A MAXIMUM DEPTH OF 0.192'-75.6% WALL LOSS. ALSO, IN THE INSPECTION AREA, (4) MID-WALL INCLUSIONS WERE FOUND WITH A MAXIMUM HEIGHT OF 0.168'-66.1% WALL LOSS. IN THE AREA OF MID-WALL INCLUSION #4 (FID #1160), A PINHOLE LEAK WAS FOUND WITH A SOAPY SOLUTION AFTER GAS WAS DETECTED DURING THE INSPECTION. A MAGNETIC PARTICLE INSPECTION WAS PERFORMED REVEALING NO RELEVANT INDICATIONS. PREDICTED ILI TOOL DATA AND ACTUAL LOCATION OF ANOMALY WERE FOUND TO BE IN THE SAME LOCATION. PER WILLIAMS PROCEDURES, A PIPE REPLACEMENT WAS PERFORMED TO COMPLETE THE MITIGATION FOR THIS DIG SITE. MAGNETIC PARTICLE, PAUT AND STRAIGHT BEAM ULTRASOUND INSPECTIONS WERE PERFORMED AT THE UPSTREAM AND DOWNSTREAM TIE-IN LOCATIONS FINDING NO RELEVANT INDICATIONS.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190121 | 33716 | 2019-11-26 13:46 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2019-11-01 14:00 | 2019 | EASTERN | NO | 39.9887 | -75.7666 | 1262859 | 2019-11-01 15:57 |  | NATURAL GAS |  | 50 | 1047 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | ROUTINE SHUTDOWN | [5 empty] | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-11-01 14:50 | VALVE CLOSURE |  | 2019-11-01 14:50 | 0 | 2019-11-01 14:00 | 2019-11-01 14:30 | ONSHORE | PA | 19335 | DOWNINGTOWN | CHESTER | SURVEY STATION NO. | 81+84 | DELAWARE POWER & LIGHT LATERAL | DELAWARE POWER & LIGHT LATERAL | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 | NO | 0.25 | 52000 | APL 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | YOUNGSTOWN STEEL | COAL TAR |  | YES | [26 empty] | 1964 | 1964 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | NO |  | 1300 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 65000 | 66322.6408388129 | 150 | 153.052248089568 | 0 | 0 |  | 0 | 65150 | 30514.0972098809 | 66475.6930869024 | 0 | 0 | 0 | 0 | NO |  |  |  | 600 | 0 | 780 | 192.619(A)(3) |  | 1990-06-15 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | REMOTELY CONTROLLED | REMOTELY CONTROLLED | 81312 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LINE WAS EXPOSED | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | YES | YES | [13 empty] | YES | PINHOLE LEAK IN LONGSEAM | [7 empty] | YES | [7 empty] | 1257 | [54 empty] | YES | YES | YES |  | YES | YES |  |  | 2017 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2010 | FREE SWIMMING | METAL LOSS |  | STANDARD RESOLUTION |  | 2018 | FREE SWIMMING | STANDARD RESOLUTION | [17 empty] | 2017 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | [5 empty] | 2018 | FREE SWIMMING | [12 empty] | YES | 1990 | 1257.35 | NO | [13 empty] | YES |  |  | 2019 | 2019 | [5 empty] | YES | YES | [52 empty] | MARK CLARKE | SENIOR ENGINEER | mark.clarke@williams.com | 7132153051 |  |  |  |  | TYSON GREEN | MANAGER PIPELINE SAFETY | 7132152535 | tyson.green@williams.com | DURING ANOMALY INSPECTION OF THE PIPE, ONE ID CONNECTED LACK OF FUSION AND TWO ID PLANAR DEFECTS WERE FOUND IN THE ILI CALL AREAS. PLANAR DEFECT #1 WAS FOUND TO BE 100.0% THRU-WALL AND WAS LEAKING AFTER ABRASIVE SANDBLASTING OPERATIONS WERE COMPLETED. PREDICTED ILI TOOL DATA AND ACTUAL LOCATION OF ANOMALY WERE FOUND TO BE IN THE SAME LOCATION. PER WILLIAMS PROCEDURES, A PIPE REPLACEMENT WAS PERFORMED TO COMPLETE THE MITIGATION FOR THIS DIG SITE. MAGNETIC PARTICLE, PAUT AND STRAIGHT BEAM ULTRASOUND INSPECTIONS WERE PERFORMED AT THE UPSTREAM AND DOWNSTREAM TIE-IN LOCATIONS FINDING NO RELEVANT INDICATIONS. LABORATORY FINDINGS: SCANNING ELECTRON MICROSCOPIC (SEM) EXAMINATIONS ITEM - A PORTION OF THE CRACK SURFACE, DETECTED DURING ULTRASONIC EXAMINATIONS REVEALED AFTER SECTIONING. FINDINGS - RUST COLORED DEPOSITS ORIGINATING ON THE INTERNAL SURFACE COVERED A PORTION OF THE FRACTURE SURFACE IN THE AREAS IDENTIFIED IN UT EXAMINATION. THESE AREAS WERE CONFIRMED TO BE CORRODED AND PITTED UNFUSED WELD METAL. METALLOGRAPHIC EXAMINATIONS SPECIMEN - A TRANSVERSE SECTION ACROSS THE REVEALED CRACKS. FINDINGS - THE CRACKS WERE CONFIRMED TO BE LONGITUDINAL, FOLLOWING A VIRTUALLY STRAIGHT PATH ALONG WHAT APPEARS TO BE THE ORIGINAL WELD LINE OF FUSION WITH A REPAIR WELD PRESENT ON THE EXTERNAL SURFACE OF THE SAMPLE. COMMENTS THE CRACK INDICATIONS WERE FOUND TO BE CORRODED AND PITTED AREAS OF THE UNFUSED WELD METAL ORIGINATING ON THE INTERNAL SURFACE OF THE PIPE FOLLOWING THE WELD LINE OF FUSION WITH A REPAIR WELD PRESENT ON THE EXTERNAL SURFACE OF THE PIPE. THE CRACKS APPEAR TO HAVE BEEN INTRODUCED DURING MANUFACTURING
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190122 | 33474 | 2019-11-26 17:19 | SUPPLEMENTAL FINAL | 15033 | PAIUTE PIPELINE CO | P.O. BOX 94197 | LAS VEGAS | NV | 89193 | 2019-10-29 07:34 | 2019 | PACIFIC | NO | 39.2914 | -118.5236 | 1262507 | 2019-10-29 09:23 | 1262689 | NATURAL GAS |  | 169 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-10-29 09:44 | 2019-11-02 11:53 |  | NO |  |  | YES | 2019-10-29 07:34 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 169 | NO | [6 empty] | 0 | 2019-10-29 08:19 | 2019-10-29 08:19 | ONSHORE | NV | 89406 | FALLON | CHURCHILL | MILEPOST | GA-19.73 | GABBS LATERAL | FALLON CITY GATE #3 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 2 | NO | 0.154 | 35000 | API 5L | SEAMLESS |  | UNKNOWN | PAINT |  | YES | [26 empty] | 1992 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | OTHER OUTSIDE FORCE STRUCK FACILITY | 2 | 2 |  | CLASS 3 LOCATION | NO |  | 64 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 1390 | 1390 | 69102 | 70508.1096499023 | 31115 | 31748.1379953794 | 0 | 0 |  | 8.2249 | 101607 | 48379.3920031699 | 103646.247645282 | 0 | 0 | 0 | 0 | NO |  |  |  | 358 | 909.31 | 531 | 192.619(A)(2) |  | 2005-10-20 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES |  |  | 90 | NO | [5 empty] | YES | THIS WAS A CITY GATE. | YES |  |  |  |  | YES | CITY GATE | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | COMPANY SCADA NETWORK TRENDS ALERTED GAS CONTROL PERSONNEL TO A POTENTIAL ISSUE AT THE FACILITY. COMPANY EMPLOYEES WERE DISPATCHED TO THE FACILITY TO INVESTIGATE AND CONFIRMED THE SCADA INFORMATION. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [9 empty] | UNKNOWN | [5 empty] | UNKNOWN |  | YES | LARGE TRUCK | ROADWAY | 50 | YES | YES | YES | [236 empty] | WILLIAM PARRY | MANAGER - ENGINEERING STAFF | william.parry@swgas.com | 702-218-9781 | 702-876-4238 | CHRIS ANDERSON | chris.anderson@swgas.com | 775-887-2805 | CHRIS ANDERSON | DIRECTOR OF OPERATIONS PAIUTE PIPELINE | 775-887-2805 | chris.anderson@swgas.com | ON OCTOBER 29, 2019, A SEMI-TRUCK INVOLVED IN A THREE-VEHICLE COLLISION, VEERED OFF THE ROADWAY STRIKING A PAIUTE PIPELINE ABOVE GROUND METER AND PRESSURE REGULATION FACILITY, (FALLON CITY GATE #3) LOCATED AT THE INTERSECTION OF US HIGHWAY 50 AND SHECKLER ROAD IN FALLON, NV. THE DAMAGE TO THE FACILITY RESULTED IN AN UNINTENTIONAL RELEASE OF NATURAL GAS AND IGNITION. SUBSEQUENT TO STRIKING THE PAIUTE FACILITY THE SEMI-TRUCK IMPACTED AN EARTHEN BERM. THE DRIVER WAS EJECTED FROM THE VEHICLE AND PRONOUNCED DEAD AT THE SCENE. THE OCCUPANT OF ANOTHER VEHICLE WHICH COLLIDED WITH THE SEMI-TRUCK IN THE ROADWAY SUSTAINED INJURIES REQUIRING INPATIENT HOSPITALIZATION. COMPANY SCADA NETWORK TRENDS ALERTED GAS CONTROL PERSONNEL TO A POTENTIAL ISSUE AT THE FACILITY. COMPANY EMPLOYEES WERE DISPATCHED TO THE FACILITY TO INVESTIGATE AND CONFIRMED THE SCADA INFORMATION. THE INLET VALVE TO FALLON CITY GATE #3 WAS OPERATED TO CONTROL THE FLOW OF GAS AND DOWNSTREAM SERVICE WAS MAINTAINED THROUGH ADJACENT FACILITIES. SERVICE WAS TEMPORARILY RESTORED THROUGH THE EXISTING FACILITIES ON THE SAME DATE. NEW PERMANENT FACILITIES WERE PLACED IN SERVICE ON 11/02/2019. SUPPLEMENTAL: AN INVESTIGATION, LED BY LOCAL AUTHORITIES, DETERMINED THAT THE NATURAL GAS OF PAIUTE PIPELINE COMPANY'S FACILITIES WAS NOT RELATED TO THE CAUSE OF DEATH OR HOSPITALIZATION OF THOSE INVOLVED IN THIS INCIDENT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190123 | 34314 | 2019-11-27 16:51 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2019-10-28 13:15 | 2019 | EASTERN | NO | 31.5828 | -89.4962 | 1262447 | 2019-10-28 16:58 |  | NATURAL GAS |  | 125 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | CROSSOVER HEADER WAS SHUT IN. MAINLINE WAS LEFT IN SERVICE |  |  |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-10-28 14:15 | VALVE CLOSURE |  | 2019-10-28 14:15 | 0 | 2019-10-28 13:15 | 2019-10-28 14:15 | ONSHORE | MS | 39401 | SEMINARY | COVINGTON | MILEPOST | 70-30VALVE YD | MAINLINE A | 70-30 VALVE YARD | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  |  | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | FLANGE ASSEMBLY | [38 empty] | 2017 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 304 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 500 | 500 | 80000 | 81627.8656477697 | 1000 | 1020.34832059712 | 0 | 0 |  | 4 | 81500 | 38456.0837394881 | 83148.2139683668 | 0 | 0 | 0 | 0 | NO |  |  |  | 645 | 48000 | 760 | 192.619(A)(2) |  | 2017-11-28 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 50 | NO | [5 empty] | YES | DOWNSTREAM CROSSOVER HEADER. MULTIPLE BENDS BETWEEN PIPELINE SEGMENTS. NO LAUNCHER/RECEIVERS INSTALLED. | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | GASKET | [17 empty] | YES | N/A | [161 empty] | STEPHANIE ROSS | PIPELINE SAFETY ENGINEER | stephanie.ross@williams.com | 832-215-4163 |  |  |  |  | TYSON GREEN | MANAGER PIPELINE SAFETY | 713-215-2535 | tyson.green@williams.com | ON 10/28/2019 AT APPROXIMATELY 1:15 PM, GAS WAS HEARD RELEASING FROM THE 70-30 VALVE YARD. THE RELEASE WAS DETERMINED TO BE IN THE VICINITY OF THE MAINLINE A BLOCK VALVE IN THE 70-30 VALVE YARD. THE AREA NEAR THE CO2 CROSSOVER VALVE WAS HAND EXCAVATED AND BUBBLING WAS OBSERVED IN RAIN/WATER PUDDLE NEAR THE CO2 CROSSOVER VALVE AND 16 INCH INSULATING FLANGE. THE WILLIAMS' SECURITY OPERATIONS CENTER WAS CONTACTED AND NRC NOTIFICATION 1262447 WAS MADE AS IT WAS DETERMINED REPAIR COSTS WOULD BE EXPECTED EXCEED $50,000. THE DOWNSTREAM CROSSOVER HEADER WAS ISOLATED, BLOWN DOWN, AND LEAKING CEASED. THE AREA NEAR THE CO2 CROSSOVER VALVE AND 16 INCH INSULATING FLANGE WAS EXCAVATED. THE GASKET WAS REPLACED AND THE 16 INCH FLANGE WAS TIGHTENED TO SPECIFICATIONS. THE DOWNSTREAM CROSSOVER HEADER WAS PRESSURED UP AND LEAK TESTED. NO FURTHER RELEASE OF GAS WAS IDENTIFIED. THE EXCAVATED AREA WAS PROPERLY BACK-FILLED AND DOWNSTREAM CROSSOVER HEADER WAS BROUGHT BACK ON LINE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190124 | 34387 | 2019-12-03 12:01 | SUPPLEMENTAL FINAL | 14435 | OZARK GAS TRANSMISSION, L.L.C. (SPECTRA ENERGY PARTNERS, LP) | 1501 MCKINNEY SUITE 800 | HOUSTON | TX | 77010 | 2019-11-05 17:36 | 2019 | CENTRAL | NO | 36.2305 | -90.2749 | 1263191 | 2019-11-05 20:28 |  | NATURAL GAS |  | 10792 | 714 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-11-05 17:46 | 2019-12-19 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-11-05 17:46 | VALVE CLOSURE |  | 2019-11-05 20:07 | 0 | 2019-11-05 17:36 | 2019-11-05 19:15 | ONSHORE | AR | 72461 | RECTOR | CLAY | MILEPOST | 251.402 | LINE 2 | SROC-EOLN | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 6 | NO | YES | [6 empty] | YES | UNCASED | UNKNOWN | 5 | BELOW WATER, PIPE BURIED BELOW BOTTOM (NOT IN BORED/DRILLED CROSSING) | NO | [10 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10 | NO | 0.188 | 60000 | API-5LX | LONGITUDINAL ERW - HIGH FREQUENCY |  | US STEEL | EPOXY |  | NO | [26 empty] | 1993 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  |  |  |  | CLASS 1 LOCATION | NO |  | 285 |  | NO | NO |  |  | 0 | 0 | 2756 | 2812.07997156567 | 41657 | 41657 | 3800000 | 3877323.61826906 | 60000 | 61220.8992358273 | 0 | 0 |  | 3.86 | 3904413 | 1852374.38157095 | 3983013.59747645 | 0 | 0 | 0 | 0 | NO |  |  |  | 1164 | 3650 | 1480 | 192.619(A)(1) |  | 1993-12-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | REMOTELY CONTROLLED | REMOTELY CONTROLLED | 52483 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE DID NOT EXCEED MAOP, BUT RATHER A PRESSURE LOSS WAS OBSERVED BY THE CONTROLLER. WHEN THE PRESSURE LOSS WAS OBSERVED, THE CONTROLLER PROMPTLY NOTIFIED APPROPRIATE COMPANY PERSONNEL TO RESPOND TO THE FAILURE. | [12 empty] | YES | 7 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  | YES | PRIVATE LANDOWNER | [7 empty] | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO | [5 empty] | NO |  | PREVIOUS DAMAGE | [266 empty] | MAYRA SALINAS |  | mayra.salinas@enbridge.com | [5 empty] | RONDA LOUDERMAN | DIRECTOR EHSR | 361-960-5671 | rlouderman@blackbearllc.com | ORIGINAL REPORT: 48 HR NRC REPORT 1263227 AT APPROXIMATELY 5:36 P.M. CST ON NOVEMBER 5, 2019, OZARK GAS TRANSMISSION'S (OGT) 10-INCH DIAMETER LINE 2 TRANSPORTING NATURAL GAS FROM STANDING ROCK COMPRESSOR STATION TO THE END OF LINE IN CLAY COUNTY ARKANSAS FAILED AT MP 251.402. THE FAILURE RESULTED IN A RUPTURE WITHOUT FIRE. THERE WERE NO INJURIES OR FATALITIES OR EVACUATIONS. OGT'S GAS CONTROL RECEIVED A LOW LOW ALARM AT 5:36 PM CST AND SUBSEQUENTLY DISPATCHED OGT PERSONNEL TO THE FAILURE SITE. OGT'S GAS CONTROL REMOTELY CLOSED UPSTREAM AND DOWNSTREAM VALVES AT 5:48 PM CST, AND FURTHER ISOLATED THE RUPTURED SECTION OF PIPELINE BY MANUALLY CLOSING A VALVE NEARER TO THE RUPTURE SITE AT 8:07 PM CST. OGT PERSONNEL ARRIVED AT THE FAILURE SITE AT 7:15 PM CST AND BELIEVED THAT THE PIPELINE WAS LEAKING BUT NOT RUPTURED. THE NRC WAS NOTIFIED AT 8:28 PM CST OF AN APPARENT LEAK, AS SOON AS LOCATION INFORMATION FOR THE SITE WAS AVAILABLE. THE NRC WAS UPDATED THE FOLLOWING MORNING WITH INFORMATION CONFIRMING THERE HAD BEEN A RUPTURE WITH NO FIRE, CONFIRMED IN THE FIELD AFTER DAYLIGHT. THE SECTION OF THE LINE IS STILL ISOLATED AND SHUTDOWN. A 3RD PARTY METALLURGICAL INVESTIGATION IS ONGOING. THE APPARENT CAUSE IS PENDING. SUPPLEMENTAL REPORT 05/04/2020 THE CAUSE OF THIS INCIDENT IS THIRD PARTY DAMAGE. NOTE THAT THE PIPE ENDS DOWNSTREAM OF THE INCIDENT SITE AND DOES NOT HAVE A SOURCE OF GAS TO CONTINUOUSLY FEED FROM THAT SIDE. AS SUCH, THE LOCAL TIME OF FINAL UPSTREAM AND DOWNSTREAM IS UPDATED ON PART A.22.C AND PART A.22.F
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190125 | 33088 | 2019-12-04 12:53 | SUPPLEMENTAL FINAL | 207 | ALASKA PIPELINE CO | 3000 SPENARD ROAD P.O. BOX 190288 | ANCHORAGE | AK | 99519 | 2019-11-09 08:52 | 2019 |  |  | 61.1393 | -149.8729 | 1263538 | 2019-11-09 10:36 |  | NATURAL GAS |  | 348 | 172 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-11-09 11:03 | 2019-11-11 17:20 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-11-09 08:52 | 2019-11-09 09:09 | ONSHORE | AK | 99515 | ANCHORAGE | ANCHORAGE | MILEPOST | MILE POST 7 | WEST SIDE FEEDER | A8 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 72 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 |  | 0.188 | 42000 | 5L-X42 | SEAMLESS |  | UNDETERMINED | COLD APPLIED TAPE | [28 empty] | 1976 | 1975 | CARBON STEEL |  | MECHANICAL PUNCTURE | 11 | 1 | [7 empty] | CLASS 3 LOCATION | NO |  | 159 |  | NO | NO | NO |  | 0 | 0 | 17204 | 17554.0725075529 | 34807 | 34807 | 894 | 912.191398613826 | 50280 | 51303.1135596232 | 0 | 0 |  |  | 103185 | 68111.9826250171 | 104576.37746579 | [8 empty] | 582 |  | 685 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 10853 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  |  |  | YES | YES | YES |  |  |  |  | CONTRACTOR | UNKNOWN/OTHER | POLE | NO | [5 empty] | NO |  | OTHER |  |  |  | CONTRACTOR WAS WORKING OUTSIDE OF THEIR LOCATE REQUEST SCOPE. | [262 empty] | RUSTY ALLEN | COMPLIANCE ENGINEER | rusty.allen@enstarnaturalgas.com | 907-334-7765 |  |  |  |  | STEVE COOPER | DIRECTOR OF OPERATIONS | 907-334-7730 | steve.cooper@enstarnaturalgas.com | ON NOVEMBER 9, 2019 A THIRD PARTY CONTRACTOR RUPTURED THE PIPELINE WHILE DRIVING PILE INTO THE GROUND. THE CONTRACTOR HAD BEEN NOTIFIED OF THE 8 INCH TRANSMISSION PIPELINE IN THE EASEMENT AND IGNORED THE OPERATORS REQUEST FOR A SAFETY WATCH. THE CONTRACTOR WAS PERFORMING WORK OUTSIDE OF THEIR LOCATE TICKET REQUEST AT THE TIME OF THE DAMAGE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190126 | 33025 | 2019-12-05 13:46 | ORIGINAL FINAL | 5304 | FLORIDA GAS TRANSMISSION CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2019-11-07 21:48 | 2019 |  |  | 28.521 | -81.4889 | 1263440 | 2019-11-08 10:25 |  | NATURAL GAS |  | 3900 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE ESD SYSTEM TRIPPED THE STATION SHUTDOWN TEMPORARILY | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-11-07 21:48 | 2019-11-07 22:43 | ONSHORE | FL | 32835 | ORLANDO | ORANGE | MILEPOST | 668.8 | ORLANDO COMPRESSOR STATION 18 | STATION YARD | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2003 |  | CARBON STEEL |  | OTHER | [8 empty] | COMPRESSOR STATION ESD SYSTEM WAS INITIATED AS A RESULT OF A FAILED FIBER OPTICS COMMUNICATION CABLE. THE ESD SEQUENCE PROCESS FAILED, THE FIRE GATE VALVE DID NOT CLOSE COMPLETELY DUE TO A FAILED PILOT. AS A RESULT OF THE OPEN VALVE A REPORTABLE VOLUME OF GAS WAS RELEASED. | CLASS 3 LOCATION | YES | METHOD2 | 646 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 12051 | 12051 | 550 | 561.191576328417 | 1200 | 1224.41798471655 | 0 | 0 |  |  | 13801 | 13313.4608027382 | 13836.609561045 | [8 empty] | 867 |  | 973 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EQUIPMENT FAILURE IN THE FIELD. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | YES | COMPRESSOR STATION ESD SYSTEM WAS INITIATED AS A RESULT OF A FAILED FIBER OPTICS COMMUNICATION CABLE. THE ESD SEQUENCE PROCESS FAILED, THE FIRE GATE VALVE DID NOT CLOSE COMPLETELY DUE TO A FAILED PILOT. AS A RESULT OF THE OPEN VALVE A REPORTABLE VOLUME OF GAS WAS RELEASED. | [22 empty] | YES | SOFT GOODS INSIDE THE PILOT REGULATOR FAILED | [161 empty] | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | 11/7/19 COMPRESSOR STATION ESD SYSTEM WAS INITIATED AS A RESULT OF A FAILED FIBER OPTICS COMMUNICATION CABLE AT 21:48. 11/8/19 NRC TELEPHONIC NOTIFICATION MADE AT 10:25 NRC#1263440. PHMSA AID NOTIFIED 10:39. 11/9/19 48-HOUR UPDATE NRC NOTIFICATION MADE AT 18:42 NRC#1263560. PHMSA AID UPDATED AT 19:25. 11/11/19 PHMSA AID UPDATED AT 11:34. THE COMPRESSOR STATION ESD SYSTEM WAS INITIATED AS A RESULT OF A FAILED FIBER OPTICS COMMUNICATION CABLE. THE ESD SEQUENCE PROCESS FAILED, THE FIRE GATE VALVE DID NOT CLOSE COMPLETELY DUE TO A FAILED PILOT. SOFT GOODS INSIDE THE PILOT REGULATOR FAILED. AS A RESULT OF THE OPEN VALVE A REPORTABLE VOLUME OF GAS WAS RELEASED. THE SOFT GOODS INSIDE THE PILOT REGULATOR WERE REPLACED TO PREVENT RECURRENCE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190127 | 34462 | 2019-12-08 22:54 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2019-11-08 14:05 | 2019 | EASTERN | NO | 35.1707 | -81.4091 | 1263466 | 2019-11-08 14:38 |  | NATURAL GAS |  | 1226 | 263 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-11-06 15:00 | 2019-12-30 08:13 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-11-06 15:00 | VALVE CLOSURE |  | 2019-11-06 15:00 | 0 | 2019-11-08 14:05 | 2019-11-06 15:00 | ONSHORE | NC | 28073 | GROVER | CLEVELAND | MILEPOST | STATION 145 | MAINLINE D, STA. 145 | 145D0 TO 145D1 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 42 |  | 0.625 | 60200 | API 5L, X60 | LONGITUDINAL ERW - LOW FREQUENCY |  | NA | EPOXY |  | YES | [26 empty] | 2017 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 809 |  | NO | NO |  |  | 0 | 0 | 6838 | 6977.14181624311 | 31876 | 31876 | 475000 | 484665.452283632 | 45000 | 45915.6744268704 | 0 | 0 |  | 26 | 558714 | 279800.726301806 | 569434.268526746 | 0 | 0 | 0 | 0 | NO |  |  |  | 635 | 0 | 780 | 192.619(A)(2) |  | 2017-07-09 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | REMOTELY CONTROLLED | AUTOMATIC | 490 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | AIR PATROL |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DOES NOT PERTAIN TO CONTROL ROOM OPERATORS | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES | [7 empty] | YES | CONSTRUCTION INSTALLATION | [12 empty] | YES | [8 empty] | 1351 | [54 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | YES | 2019 | [6 empty] | YES | [55 empty] | STEPHANIE ROSS | PIPELINE SAFETY ENGINEER | stephanie.ross@williams.com | 713-215-4163 |  |  |  |  | TYSON GREEN | MANAGER PIPELINE SAFETY | 713-215-2535 | tyson.green@williams.com | DURING THE SEMI-ANNUAL LEAK SURVEY FLIGHT, AN ELEVATED CH4 LEVEL WAS INDICATED. A LOCAL OPERATIONS TECH USED HANDHELD RMLD TO VERIFY THE PRESENCE OF NATURAL GAS. IT WAS INITIALLY BELIEVED A BURIED THREADED CONNECTION IN THE BODY VENT PIPING OF VALVE WAS LEAKING. POTHOLING, VACUUM EXCAVATION, AND PROBING WERE USED TO DETERMINE THE LEAK LOCATION UPSTREAM OF MAINLINE BLOCK VALVE 145D1 WHERE INCREASED LEVELS OF NATURAL GAS WERE NOTED ONCE THE PROBE BAR WAS REMOVED. THE PIPELINE SEGMENT WAS ISOLATED AND BLOWN DOWN TO ALLOW FOR FURTHER EXCAVATION. ONCE PIPELINE WAS EXCAVATED, THE SOURCE OF LEAK WAS IDENTIFIED USING LEAK DETECTION LIQUID AT A WELD FITTING. X-RAYS OF THE SUBJECT WELD WERE TAKEN. A PLAN HAS BEEN FORMULATED AND APPROVED TO CUT OUT THE WELD THAT WAS LEAKING AND ALSO THE FITTING JUST DOWNSTREAM OF THE SUSPECT WELD. NEW PIPE AND FITTING WILL BE INSTALLED. ONCE THE SUSPECT WELD AND FITTING ARE REMOVED, IT WILL BE SENT TO LAB FOR A FULL METALLURGICAL ANALYSIS. THE WORK IS SET TO BEGIN THE WEEK OF 12/9/2019. UPDATE: CRACKING CONFINED TO WELD METAL. CRACKING MOST LIKELY OCCURRED BY A HYDROGEN ASSISTED CRACKING (HAC) MECHANISM. THE HAC CRACKING WAS MOST LIKELY FACILITATED BY THE HI-LOW OF THE JOINT FIT-UP, AND QUALITY OF APPLICATION OF THE ROOT PASS DURING CONSTRUCTION INSTALLATION. ANY UNDUE STRESSES ASSOCIATED WITH THE FINAL TIE IN WELD MAY HAVE CONTRIBUTED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190128 | 34078 | 2019-12-11 10:59 | SUPPLEMENTAL FINAL | 12576 | ENABLE MISSISSIPPI RIVER TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2019-11-14 13:00 | 2019 | CENTRAL | NO | 32.6784 | -92.3239 | 1263945 | 2019-11-14 14:23 | 1264007 | NATURAL GAS |  | 22213 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | POST-MAINTENANCE/REPAIR | [5 empty] | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-11-14 13:45 | VALVE CLOSURE |  | 2019-11-14 14:00 | 0 | 2019-11-14 13:12 | 2019-11-14 13:30 | ONSHORE | LA | 71234 | Not Within a Municipality | UNION | MILEPOST | 1052+39 | WESTLINE | WESTLINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 18 |  | 0.281 | 52000 | API 5LX | OTHER | SMITH WELD | AO SMITH | COAL TAR |  | NO | [7 empty] | PIPE GIRTH WELD |  | YES | 0.375 | 52000 | API 5LX | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | SEAH STEEL COMPANY | FUSION BONDED EPOXY(FBE) |  | NO | [7 empty] | 1950 | 1950 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 9 | 2 |  | CLASS 1 LOCATION | NO |  | 363 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 58864 | 58864 | 75000 | 76526.1240447841 | 1000 | 1020.34832059712 | 0 | 0 |  | 2.65 | 134864 | 96622.8586488 | 136410.472365381 | 0 | 0 | 0 | 0 | NO |  |  |  | 649 | 12000 | 855 | 192.619(A)(2) |  | 2012-03-30 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 96901 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES | [7 empty] | YES | WELDER PERFORMANCE | [13 empty] | YES | [7 empty] | UNKNOWN | [54 empty] | YES | YES | YES |  | YES |  |  |  | 2012 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2005 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2019 | FREE SWIMMING | HIGH RESOLUTION |  | 2019 | FREE SWIMMING | HIGH RESOLUTION | [13 empty] | 2019 | FREE SWIMMING | HIGH RESOLUTION |  | INSIDE ILI CUPS | 2012 | FREE SWIMMING | HIGH RESOLUTION |  | INSIDE ILI CUPS | [14 empty] | NO |  |  | NO | [13 empty] | NO | [41 empty] | YES | [21 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  | CASEY ROBERTS | casey.roberts@enablemidstream.com | 4055584647 | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | 11/14/19, 13:00 EMRT'S WESTLINE EXPERIENCED A FAILURE IN UNION PARISH LOUISIANA. THE FAILURE OCCURRED NEAR THE GIRTH WELD AREA OF A REPAIRED SECTION OF PIPE. THE PIPE WAS INSTALLED THE PREVIOUS DAY TO REMOVE AN ANOMALY DISCOVERED BY AN ILI TOOL RUN. THE FAILED SECTION WAS REMOVED AND SENT TO PRECISION ENGINEERING FOR ANALYSIS. NRC INITIAL 11/14/2019 (NRC # 1263945). 48 HR FOLLOW UP 1/15/2019 (NRC# 1264007). 07.10.2020 SUPPLEMENTAL. PRECISION ENGINEERING SOLUTIONS, LLC WAS CONTRACTED TO PERFORM A FAILURE INVESTIGATION FOR ENABLE ON CRACKING AND LEAKING ASSOCIATED WITH A GIRTH WELD IN THE WESTLINE SYSTEM THAT JOINED TWO PIPE MATERIALS: 18" .281" (OLD PIPE) AND 18" .375" (NEW PIPE). THE OLD PIPE WAS INSTALLED IN 1950, WHILE THE NEW PIPE WAS INSTALLED IN 2019. THE DIMENSIONAL EXAMINATION SHOWED THAT THE PIPE ON EITHER SIDE OF THE GIRTH WELD MET THE DIMENSIONAL REQUIREMENTS OF THE APPLICABLE API 5L AND 5LX SPECIFICATIONS FOR THEIR RESPECTIVE DATES OF MANUFACTURE AND SIZES. THE CHEMICAL ANALYSIS SHOWED THAT THE NEW PIPE MET THE CHEMICAL COMPOSITION REQUIREMENTS API 5L, BUT THAT THE OLD PIPE DID NOT, DUE TO HIGH CARBON, PHOSPHOROUS, AND CARBON EQUIVALENCY. IT IS TO BE NOTED THAT THERE WERE NO CHEMICAL COMPOSITION REQUIREMENTS FOR X52 LINE PIPE AT THE TIME OF THE MANUFACTURE OF THE OLD PIPE (1950). THE HARDNESS TESTING CONDUCTED DID NOT SHOW ANY ABNORMALITIES IN THE HARDNESS OF THE PIPES, HEAT AFFECTED ZONES, OR WELD METAL. THE MAGNETIC PARTICLE INSPECTION OF THE I.D. SURFACE SHOWED CRACK INDICATIONS ON THE OLD PIPE SIDE OF THE GIRTH WELD AROUND THE ENTIRE CIRCUMFERENCE. THE MICROSCOPIC EXAMINATION SHOWED LACK OF FUSION ORIGINATING AT THE I.D. BETWEEN THE OLD PIPE AND THE ROOT PASS WELD METAL. DUCTILE OVERLOAD FRACTURE WAS FOUND NEAR THE O.D. AND THROUGH-WALL IN SOME REGIONS. A VISUAL EXAMINATION OF THE FRACTURE SURFACE OF THE THROUGH WALL CRACK SHOWED LACK OF FUSION PRESENT AROUND MOST OF THE I.D. SURFACE WITH THE REMAINDER OF THE FRACTURE SURFACE BEING DUCTILE OVERLOAD. THE LACK OF FUSION IS THOUGHT TO BE ASSOCIATED WITH WELDING PARAMETERS AND WELDING TECHNIQUE. ALTHOUGH THE CARBON CONTENT AND CARBON EQUIVALENCE OF THE OLD PIPE WAS HIGH AND IN EXCESS OF CURRENT API 5L REQUIREMENTS, IT IS NOT THOUGHT TO BE THE PRIMARY CAUSE OF THE FAILURE. ADDITIONALLY, THE PRESENCE OF ELEVATED STRESSES GENERATED DURING THE TIE-IN PROCESS CANNOT BE DISCOUNTED, ALTHOUGH IT IS DIFFICULT TO QUANTIFY WHAT MAGNITUDE OF STRESS MIGHT HAVE EXISTED AT THE TIME OF CONSTRUCTION. ALL TIE IN WELDS ON THE WESTLINE REMEDIATION PROJECT WERE NON-DESTRUCTIVELY TESTED WHEN COMPLETED. WELDS TI-9 AND TI-10 (NEW PIPE) WERE TESTED AND PASSED BY A LEVEL II TECHNICIAN. THE TECHNICIAN'S PAPERWORK STATED THEY WERE FOLLOWING THE MINIMUM GUIDELINES SET FORTH IN API 1104. AFTER THE INCIDENT, THE X-RAY FILM FOR TI-9 AND TI-10 WAS SENT TO A 3RD PARTY X-RAY COMPANY FOR A QUALITY CONTROL CHECK. THE 3RD PARTY FOUND THE FILM DENSITY TO BE LESS THAN THE REQUIRED RANGE OF 1.8 - 4.0 THAT API 1104 AND ENABLE MIDSTREAM CONSTRUCTION SPEC CS-095 REQUIRE. FIVE OF THE SIX X-RAY SHOTS FOR TI-9 AND TI-10 WERE BELOW THE MINIMUM DENSITY REQUIREMENT OF 1.8. DENSITY BELOW 1.8 COULD POSSIBLY CAMOUFLAGE A FEATURE, IF PRESENT. DUE TO FILM DENSITY BEING OUT OF SPEC, ENABLE DISQUALIFIED THE X-RAY TECH. 7/30/20 SUPPLEMENTAL. BOTH WELDERS THAT PERFORMED THE WELDS WERE QUALIFIED AT THE TIME OF THE TIE-IN. BOTH HAD BEEN OBSERVED FOLLOWING THE WELDING PROCEDURE PRIOR TO THE FAILURE. AFTER THE FAILURE, A WELDER REVIEW WAS CONDUCTED AND THEY WERE NOT DISQUALIFIED. OF THE THREE X-RAY REVIEWS AFTER THE INCIDENT, ONLY ONE WELD WAS FOUND TO BE OUT OF SPEC (TI-10) FOR WHICH IT WAS REPAIRED IMMEDIATELY, X-RAYED, AND FOUND PASSING. WELD TESTING WAS PERFORMED AND CONFIRMED THE WELDING PROC. USED WAS ADEQUATE. ALONG WITH WELD TESTING, AND LEVEL III TECH REVIEWS, ENABLE WILL PERFORM AN ASSESSMENT APPROPRIATE FOR CRACK-LIKE DEFECTS ON THE WESTLINE HCAS, MCAS AND CLASS 3 LOCATIONS DURING THE NEXT REASSESSMENT CYCLE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190129 | 33944 | 2019-12-12 16:14 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2019-11-13 11:04 | 2019 | CENTRAL | NO | 31.949 | -103.1069 | 1263831 | 2019-11-13 12:00 | 1263966 | NATURAL GAS |  | 11048 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | PIGGING OPERATIONS CONTINUED AS SCHEDULED AFTER RELEASE WAS STOPPED |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2019-11-13 11:04 | 2019-11-13 11:04 | ONSHORE | TX | 79745 | KERMIT | WINKLER | SURVEY STATION NO. | 10 +52 | LINE 3026 | 0010- MILEPOST 10 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1952 | 1952 | CARBON STEEL |  | LEAK |  |  | OTHER | RELEASE THROUGH RELIEF VALVE | [5 empty] | CLASS 1 LOCATION | NO |  | 528 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 30272 | 30272 | 0 | 0 | 250 | 255.08708014928 | 0 | 0 |  | 2.74 | 30522 | 31501.4486561092 | 30527.0870801493 | 0 | 0 | 0 | 0 | NO |  |  |  | 605 | 140 | 651 | 192.619(C) |  | 1952-06-30 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS INDEPENDENT OF CONTROLLER ACTION. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | PSSR NOT EFFECTIVELY COMPLETED. |  |  | YES |  |  | COMMISSIONING | NO | [150 empty] | SHELLEY DIETZ | PIPELINE ENGINEER | shelley_dietz@kindermorgan.com | 713-420-4417 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | ON NOVEMBER 13, 2019 AT 11:04AM, KINDER MORGAN EMPLOYEES AT THE EL PASO NATURAL GAS (EPNG) KEYSTONE COMPRESSOR STATION HEARD GAS VENTING IN THE STATION YARD AND NOTICED TWO RELIEF VALVES ON LINE 3026 WERE RELIEVING. SMART-PIGGING ACTIVITIES WERE BEING PERFORMED AND OPERATIONS DETERMINED THAT THE PIG WAS STUCK RESULTING IN AN INCREASE IN PRESSURE ON THE LINE. OPERATIONS DETERMINED THAT THE PIG WAS STOPPED AT BLOCK VALVE 1, WHICH WAS CLOSED. THEY OPENED THE VALVE MANUALLY WHICH ALLOWED THE PIG TO RESUME ITS RUN AND THE GAS RELEASE WAS STOPPED. A TOTAL OF 11,048 MCF OF GAS WAS RELEASED. THE INVESTIGATION REVEALED THAT BLOCK VALVE 1 WAS INCORRECTLY LEFT IN THE CLOSED POSITION FOR THIS PIG RUN DUE TO A MISUNDERSTANDING OF ITS FUNCTIONALITY. A RECENT PROJECT HAD REPLACED THE VALVE ACTUATOR TO MAKE THE VALVE CAPABLE OF REMOTE OPERATION. THIS VALVE IS ON THE BOUNDARY OF THE HOBBS AND ODESSA OPERATIONS AREA. THE PSSR FOR THE PROJECT HAD ONLY BEEN PERFORMED WITH THE HOBBS AREA, BUT THE ODESSA AREA WAS USING THE VALVE IN THEIR PIGGING OPERATIONS. THE PSSR HAD NOT SUCCESSFULLY COMMUNICATED HOW THIS VALVE FUNCTIONS TO THE ODESSA AREA AT THE COMPLETION OF THE PROJECT. THIS RESULTED IN THE ODESSA AREA INCORRECTLY BELIEVING THIS VALVE WOULD OPEN AS THE PIG APPROACHED AND ULTIMATELY CAUSING THE OVERPRESSURE AND RELEASE OF GAS. IN ORDER TO PREVENT A REOCCURRENCE, BOTH HOBBS AND ODESSA AREA OPERATIONS PERSONNEL HAVE BEEN RETRAINED ON THE CORRECT OPERATION OF THIS VALVE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190130 | 34391 | 2019-12-16 14:19 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2019-11-17 08:23 | 2019 | EASTERN | NO | 41.173 | -82.2132 | 1264138 | 2019-11-17 10:27 |  | NATURAL GAS |  | 1467 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-11-17 09:26 | 2019-11-17 17:15 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-11-17 09:26 | VALVE CLOSURE |  | 2019-11-17 09:26 | 12 | 2019-11-17 08:23 | 2019-11-17 09:01 | ONSHORE | OH | 44090 | WELLINGTON | LORAIN | SURVEY STATION NO. | 260+73 | L-722 | L722-055 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | COUPLING | 2014 | UNKNOWN | PLASTIC |  | OTHER | [8 empty] | SEPARATION | CLASS 3 LOCATION | YES | METHOD2 | 92 |  | NO | NO |  |  | 257000 | 262229.51839346 | 0 | 0 | 3257 | 3257 | 10000 | 10203.4832059712 | 0 | 0 | 0 | 0 | 0 | 2.22 | 270257 | 128430.616168203 | 275690.001599431 | 0 | 0 | 1740 | 236 | NO |  |  |  | 76 | 1224 | 100 | 192.619(A)(1) |  | 2016-11-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 5300 | NO | YES | [6 empty] | YES |  | YES |  |  |  |  | TRANSMISSION SYSTEM | NO |  |  |  |  | OTHER | DOWNSTREAM CUSTOMER- COLUMBLIA GAS OF OHIO |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | OTHER | COUPLING- DRESSER STYLE |  |  |  | YES | [175 empty] | KAMRANROSTAMI ASRABADI | COMPLIANCE SPECIALIST | kamran_rostami@tcenergy.com | (304)357-2351 |  |  |  |  | PAUL SHAFFER | PAUL SHAFFER | 304-550-4866 | paul_shaffer@tcenergy.com | OPERATIONS TEAM LEADER RECEIVED A CALL FROM COLUMBIA GAS OF OHIO (COH), THE LOCAL DISTRIBUTION COMPANY REGARDING LOW PRESSURE ALARMS AT WELLINGTON MEASURING STATION 706948 . COLUMBIA OPERATIONS PERSONNEL WERE ON THE SITE AT 09:00 EST AND CONFIRMED THAT THE LOW-PRESSURE ALARM WAS DUE TO A PLASTIC COUPLING SEPARATION ON LINE L-722. LINE L-722, IS CLASSIFIED AS TRANSMISSION THAT IS OPERATED AND MAINTAINED BY COLUMBIA. AT 09:36 EST, THE LEAK WAS ISOLATED, AND THE PIPELINE WAS REMOVED FROM SERVICE. PIPELINE L-722 IS A 4-INCH IN DIAMETER PLASTIC PIPELINE AT THE SITE OF THE INCIDENT WITH A MAXIMUM ALLOWABLE OPERATING PRESSURE OF XXX PSIG, LOCATED IN LORAIN COUNTY, VILLAGE OF WELLINGTON, OHIO. THE REPAIR WAS COMPLETED BY REPLACING THE FAILED COUPLING AND LINE L-722 WAS RETURNED INTO SERVICE ON NOVEMBER 17, 2019 AT 15:15 EST. APPROXIMATELY 2,000 COH CUSTOMERS LOST NATURAL GAS SERVICE IN LIEU OF THIS INCIDENT AND DURING THE REPAIR INTERVAL OF THE AFFECTED SEGMENT OF LINE L-722. THE FAILED COUPLING WAS PRESERVED AND PROTECTED AS EVIDENCE, THEN SENT TO A LOCAL COLUMBIA OFFICE FOR FURTHER INVESTIGATION. THE INITIAL NATIONAL RESPONSE CENTER (NRC) REPORT NO. 1264138 AND THE NRC 48-HOUR REPORT NO. 1264285 HAVE BEEN CALLED-IN ON NOVEMBER 17TH AND NOVEMBER 19TH RESPECTIVELY. AFTER COMPLETION OF ROOT CAUSE ANALYSIS, IT WAS DETERMINED THAT THE CAUSAL AND ROOT CAUSE FACTORS OF PIPELINE SEPARATION INDICATE FIRST A LACK OF AWARENESS BY PROJECT TEAM AND FIELD OPERATIONS PERSONNEL TO THE PUBLISHED GUIDELINES FOR THE USE OF MECHANICAL COUPLINGS AS ESTABLISHED BY AND SECOND PRIOR TO THE EXCAVATION, POTENTIAL HAZARDS, HAZARDOUS WORK, OR WORK HAZARDOUS TO THE ENVIRONMENT OR FACILITIES WERE NOT ADEQUATELY IDENTIFIED FOR THE PLANNED PIPELINE REPLACEMENT. IN ORDER TO PREVENT SIMILAR FUTURE EVENTS, MECHANICAL PIPELINE REPAIR TAPPING AND JOINING PROCEDURE SHOULD BE DISTRIBUTED TO PROJECT TEAM AND TO ADEQUATELY IDENTIFY ALL POTENTIAL HAZARDS IN EACH PROJECT TO THE ENVIRONMENT OR FACILITIES , INCORPORATE PRE-JOB PLANNING PROCEDURE AND CHECKLIST PER PROJECT BY PROJECT TEAM.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190131 | 33083 | 2019-12-16 16:36 | ORIGINAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2019-11-15 13:26 | 2019 |  |  | 43.1654 | -96.0445 | 1264146 | 2019-11-15 14:12 |  | NATURAL GAS |  | 154 | 38 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-11-15 14:30 | 2019-11-16 00:56 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-11-15 13:26 | 2019-11-15 14:20 | ONSHORE | IA | 51234 | Not Within a Municipality | SIOUX | MILEPOST | 5.24 | BOYDEN BRANCH LINE | IAB66701 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 40 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 2.375 |  | 0.154 | 35000 | UNKNOWN | LONGITUDINAL ERW - LOW FREQUENCY |  | REPUBLIC | COAL TAR | [28 empty] | 1954 | 1954 | CARBON STEEL |  | MECHANICAL PUNCTURE | 2 | 6 | [7 empty] | CLASS 1 LOCATION | NO |  | 46 |  | NO | NO | NO |  | 10 | 10.2034832059712 | 100 | 102.034832059712 | 385 | 385 | 2000 | 2040.69664119424 | 40000 | 40813.9328238848 | 0 | 0 |  |  | 42495 | 20122.0730523577 | 43351.8677803448 | [8 empty] | 655 |  | 800 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 33000 | NO | [5 empty] | YES | 2-INCH PIPELINE | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LOCAL SHERIFF CALLED TO REPORT THE INCIDENT AT THE SAME TIME THE CONTROL ROOM DETECTED THE DROP IN PRESSURE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | TRENCHER | AGRICULTURE | NO | [5 empty] | YES | 12 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | JOHN A GORMLEY | SR CORROSION SPECIALIST - PIPELINE SAFETY | john.gormley@nngco.com | 402-398-7494 |  |  |  |  | THOMAS CORRELL | VP PIPELINE SAFETY AND RISK | 402-398-7715 | thomas.correll@nngco.com | ON NOVEMBER 15, 2019, AT 1326 HOURS, THE SIOUX COUNTY, IOWA, SHERRIFF'S DEPARTMENT REPORTED KNOWN PIPELINE DAMAGE ABOUT 2 MILES SOUTHWEST OF BOYDEN, IOWA (POP ~700). THE EXACT LOCATION IS ON THE BOYDEN 2-INCH BRANCH LINE (IAB66701) AT MILEPOST 5.24. IT IS ASSUMED A FARMER WAS LAYING DRAINAGE TILE IN HIS FIELD WHEN HE PUNCTURED AND COMPLETELY SEVERED THE PIPELINE. PAULLINA SENIOR OPERATIONS AND MAINTENANCE TECHNICIANS ISOLATED THE LEAK AT 1430 HOURS. WHEN ARRIVING AT THE LEAK LOCATION AT 1448 HOURS, NO EQUIPMENT OR PERSONNEL WERE PRESENT. LOCAL LAW ENFORCEMENT FOUND THE EXCAVATOR LATER THAT DAY AFTER INTERVIEWING THE LANDOWNER AND NEIGHBORS. NO ONE CALL FOR THE WORK HAD BEEN MADE. THE BOYDEN, IOWA, #1 TOWN BORDER STATION (737111) LOST SERVICE IMMEDIATELY AFTER THE LINE HIT. TWO FARM TAPS ALSO LOST SERVICE. REPAIR SERVICES WERE MOBILIZED AT 1500 HOURS AND ARRIVED ON SITE AT 1600 HOURS. THE PIPELINE WAS REPAIRED BY REPLACING A CYLINDER OF PIPE USING PRE-TESTED PIPE 43-FEET LONG. SERVICE TO THE TOWN OF BOYDEN WAS RESTORED ON NOVEMBER 16, 2019, AT 0056 HOURS. THE INITIAL NRC REPORT NUMBER IS 1264042 AND THE 48-HOUR FOLLOW-UP IS 1264147.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190132 | 33258 | 2019-12-17 17:02 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-11-18 13:14 | 2019 |  |  | 35.1591 | -88.2205 | 1264245 | 2019-11-18 14:46 |  | NATURAL GAS |  | 116172 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE STATION WAS OFFLINE AND BEING BYPASSED BY MAINLINE AT TIME OF INCIDENT. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-11-18 13:14 | 2019-11-18 13:14 | ONSHORE | TN | 38372 | MADDOX | HARDIN | MILEPOST | VENT VALVE | TGP SAVANNAH CS 856 | UNIT #2 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1999 |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENTIONAL VENTING THROUGH THE UNIT #2 VENT VALVE (IN PROPER OPEN POSITION) BECAUSE OF COMPRESSOR LOADING VALVE BEING OPENED. | CLASS 2 LOCATION | NO |  | 633 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 232925 | 232925 | 0 | 0 | 500 | 510.17416029856 | 1000 | 1020.34832059712 | ESTIMATED COST OF THE INVESTIGATION |  | 234425 | 242186.474088886 | 234455.522480896 | [8 empty] | 135 |  | 936 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS DEEMED INDEPENDENT OF CONTROLLER ACTION. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | YES |  |  |  | YES | COLD FRONT CAUSED SOME INSTRUMENTATION COMPONENTS TO FREEZE. TEMPERATURE WAS APPROXIMATELY 22 DEGREES FAHRENHEIT ON 11/12/19 WHEN THE COMPRESSOR LOADING VALVE OPENED. | [301 empty] | CLAYTON THEDINGER | PIPELINE ENGINEER - CODES AND COMPLIANCE | clayton_thedinger@kindermorgan.com | 713-420-5629 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR - CODES AND COMPLIANCE | 713-369-9443 | jaime_hernandez@kindermorgan.com | DAY OF DISCOVERY: ON 11/18/19, A KM MEASUREMENT TECH ARRIVED AT THE UNMANNED TGP STATION 856 FOR THE PURPOSE OF READING FUEL METER INDEXES. HE NOTICED A GAS RELEASE SOUND UPON EXITING HIS VEHICLE NEAR THE COMPRESSOR BUILDING. THE TECH REPORTED THE ISSUE TO THE OPERATIONS SUPERVISOR AND WAS INSTRUCTED TO TRY TO IDENTIFY THE LEAK. HE IDENTIFIED IT WAS COMING FROM THE BLOWDOWN SILENCER AS THE TECH COULD VISUALLY SEE THE GAS VENTING AND ALSO OBSERVED FROSTING ON THE SILENCER. THE TECH THEN PROCEEDED TO THE CONTROL ROOM AND ULTIMATELY IDENTIFIED THAT THE NORMALLY CLOSED REMOTED OPERATED 4IN COMPRESSOR LOADING VALVE WAS OPEN ON THE UNIT #2 LOAD LINE ALLOWING GAS TO VENT THROUGH THE NORMALLY OPEN COMPRESSOR VENT VALVE. THE TECH PROCEEDED TO CLOSE THE MANUAL BLOCK VALVE ON THE LOAD LINE ASSEMBLY AT 1:36PM TO STOP THE LEAK. THE LEAK STOPPAGE WAS REPORTED TO KM MANAGEMENT AT 1:40PM. AT THE TIME OF THE INCIDENT, IT WAS UNKNOWN THE QUANTITY OF GAS RELEASED BUT ON THE 2:35PM ERL CALL IT WAS DETERMINED TO REPORT TO THE NRC AS A PRECAUTION. IT WAS REPORTED TO THE NRC AT 2:46PM LOCAL TIME WITH THE UNKNOWN AMOUNT. THE REPORT NUMBER WAS 1264245. 48 HOUR UPDATE: DURING INVESTIGATION, IT WAS DETERMINED THAT THE GAS HAD BEEN VENTING THROUGH THE BLOWDOWN SILENCER FOR ABOUT 6 DAYS. THIS WAS REPORTED TO THE NRC (#1264366) ON THE 48 HR UPDATE AT 4:54PM LOCAL TIME ON 11/19/19. INVESTIGATION: DURING INVESTIGATION, IT WAS IDENTIFIED THAT THE UNIT #2 LOAD LINE VALVE OPENED ON 11/12/19 AT 11:43PM. THE LOAD LINE VALVE OPENED AS A RESULT OF FREEZING UP OF MOISTURE IN THE SOLENOID CONTROL BOX. AT STA 856, THE TEMPERATURE ON 11/12/19 WENT BELOW FREEZING AT 4PM AND WAS APPROXIMATELY 22 °F AT THE TIME OF THE EVENT. THIS AREA DOES HAVE WINTERIZATION PROCEDURES AND PLANS IN PLACE AND IS SCHEDULED IN MAXIMO TO BE PERFORMED MONTHLY NOVEMBER THROUGH MARCH. HOWEVER, SINCE THIS OCCURRED MID-MONTH, THE PLAN WAS NOT COMPLETED AT THE TIME OF THE INCIDENT. THE TIMING OF THE EVENT IS VALIDATED BY THE VALVE EVENT LOGS, THE ALARMS, AND THE PRESSURE RISE IN THE UNIT #2 PIPING AT THAT TIME OF THE EVENT. THE PRESSURE ON THE DISCHARGE OF UNIT #2 WHERE THE VENT VALVE IS LOCATED AVERAGED 135 PSI. THIS BACKPRESSURE FLUCTUATED WITH THE MAINLINE LINE PRESSURE AND WAS CREATED BY THE RESTRICTION OF AN ORIFICE PLATE ON THE INLET TO THE SILENCER. THE ORIFICE PLATE ON THE SILENCER IS A DESIGNED PLATE WITH 4 X 1.25" HOLES FOR CUTTING THE PRESSURE GOING INTO THE SILENCER. WHEN CALCULATING GAS LOSS IT WAS ASSUMED THAT THE ORIFICE PLATE ACTED AS 4 INDEPENDENT HOLES. THE TOTAL GAS LOSS CALCULATED WAS 116,172 MCF. THE GAS THAT PRESSURIZED THE UNIT #2 COMPRESSOR CASE ALSO PRESSURIZED THE UNIT #1 CASE. WHEN THE PLC SAW THE CASE PRESSURE ELEVATED ON UNIT #2, IT TRIGGERED THE UNIT TO TRY TO MAINTAIN SEAL OIL PRESSURE TRIGGERING ALARMS AND EVENT STATUSES. OVER THE COURSE OF THE EVENT THERE WERE 3 STATION WARNING CALLOUTS THAT WERE TRIGGERED THROUGH ALARMS ORIGINATING FROM THE LOAD LINE VALVE OPERATING. THESE ALARMS INDICATED ISSUES WITH UNIT 1 AND UNIT 2 IN RELATION TO THE SEAL OIL SYSTEMS. THE TECH RESPONDING TO THE CALLOUTS LOGGED IN REMOTELY TO ASSESS THE SCADA ALARMS. THE TECH VIEWED ONLY THE STATION LEVEL ALARM SCREEN AND UNIT 1A ALARM SCREEN, AND EITHER DIDN'T LOOK AT OR DIDN'T RECOGNIZE THE SIGNIFICANCE OF THE EVENTS. THE TECH ALSO DIDN'T LOG INTO THE UNIT 2A LEVEL MACHINES TO VIEW THE UNIT SPECIFIC ALARM SCREEN. IN ADDITION TO THE 2 EVENTS ON THE NIGHT THE INCIDENT ORIGINATED THERE WAS ALSO A CALLOUT 3 DAYS LATER AGAIN AS A RESULT OF A UNIT 2A ALARM THAT WAS NOT FOLLOWED UP ON. FOLLOW-UP ACTION ITEMS: OPERATIONS HAS CHANGED THE MAXIMO WORK ORDER TO BEGIN WINTERIZATION PLANS IN OCTOBER INSTEAD OF NOVEMBER. ALSO, THE TECH WAS PREVIOUSLY TRAINED ON SCADA AND HOW TO MANAGE ALARMS; HOWEVER AFTER THIS INCIDENT, OPERATIONS HELD RE-TRAINING FOCUSING ON ALARM LOG REVIEW AND ACKNOWLEDGEMENT RESPONSES. THE TECH IN QUESTION HAD OQ REVOKED AND WAS REQUIRED TO RETEST FOR THE OQ TASK.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190133 | 34260 | 2019-12-18 17:11 | SUPPLEMENTAL FINAL | 31424 | AMERICAN MIDSTREAM (SIGCO INTRASTATE), LLC | BLACK BEAR TRANSMISSION, LLC 1501 MCKINNEY, SUITE 800 | HOUSTON | TX | 77010 | 2019-11-04 15:35 | 2019 | CENTRAL | NO | 29.8768 | -89.7604 | 1263070 | 2019-11-04 17:02 | 1263279 | NATURAL GAS |  | 10000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-11-04 17:25 | 2019-12-15 09:00 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-11-04 17:18 | VALVE CLOSURE |  | 2019-11-04 17:25 | 0 | 2019-11-03 15:45 | 2019-11-04 15:35 | ONSHORE | LA | 70085 | Not Within a Municipality | SAINT BERNARD | SURVEY STATION NO. | VERETTE LEVY | 8" CHALMETTE PIPELINE | MARSH TO LEVY SECTION | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 78 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 | NO | 0.25 | 52000 | API 5L X52M | SEAMLESS |  | UNKNOWN | COAL TAR |  | UNKNOWN | [26 empty] | 1962 | 1962 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 188 |  | NO | NO |  |  | 1800 | 1836.62697707482 | 0 | 0 | 25000 | 25000 | 75000 | 76526.1240447841 | 500 | 510.17416029856 | 0 | 0 |  | 2.5 | 102300 | 62123.389035896 | 103872.925182157 | 0 | 0 | 0 | 0 | NO |  |  |  | 750 | 0.75 | 998 | 192.619(A)(1) |  | 1963-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 26400 | NO |  |  | YES | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLERS FOLLOWED THE OPERATIONS AND MAINTENANCE PLAN, AS WELL AS THE CRM UPON SEEING THE CHANGE IN PRESSURE FROM SCADA. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [52 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | SUBSIDENCE |  |  |  | ,,, | NO | [306 empty] | KEVIN STANLEY | SR. MANAGER EHS | kstanley@3cmidstream.com | 346-241-3585 |  | ROBIN ASEVADO | rasevado@3cmidstream.com | 504-681-6925 | KEVIN STANLEY | SR. MANAGER EHS | 346-241-3585 | kstanley@3cmidstream.com | OPERATIONS CONTROL CENTER NOTICED THROUGH SCADA ON SUNDAY, NOVEMBER 3 AT 15:45 THAT THE CHALMETTE PIPELINE WAS EXPERIENCING A DROP IN PRESSURE, ALONG WITH THE VOLUME OF GAS BEING DELIVERED. THEY IMMEDIATELY NOTIFIED THE OPERATIONS MANAGER FOR THE PIPELINE ASSET AND AERIAL PATROL WAS DISPATCHED TO DETERMINE IF THERE WERE VISIBLE SIGNS OF A LEAK. WITH NONE FOUND AND DUE TO THE LATE TIME, OCC CONTINUED TO MONITOR THE LINE THROUGH THE NIGHT. ON MONDAY, NOVEMBER 4, 2019, A HELICOPTER AND BOAT WERE BOTH DISPATCHED AT 0800 TO MADE ADDITIONAL PATROLS SINCE OCC CONTINUED TO SEE THE SAME INDICATIONS WITH THEIR SYSTEM. NO LEAKS WERE FOUND. AT 15:12, AN OFF DUTY OFFICER FOR THE SAINT BERNARD PARISH NOTICED DIRT AND MUD BEING SPRAYED FROM THE GROUND AND CONTACTED THIRD COAST MIDSTREAM OCC. OCC MADE NOTIFICATIONS PER THE CRM AND OPERATIONS RESPONDED TO THE VERETTE LEVY TO SHUT VALVES AND ENSURE THE BYPASS PORTION OF THE PIPELINE WAS NOT UTILIZED UNTIL REPAIRS COULD BE MADE. REPAIRS BEGAN ON DECEMBER 9, 2019 AND WERE COMPLETED ON MONDAY, DECEMBER 16, 2019 BY REPLACING A 24' SECTION OF CARBON STEEL PIPE. THE PIPE WAS DISCOVERED TO HAVE BEEN INSTALLED IN 1963 CROSSING A CONCRETE PIER BEAM (SIMILAR TO A CURB STOP) AND DUE TO THE PIPE BEING IN A MARSH AREA, APPEARED TO HAVE SETTLED, CAUSING THE PIPE TO FAIL. ANALYSIS PERFORMED BY A THIRD PARTY INDICATED SAMPLE MOST LIKELY FAILED BY CRACKING FROM THE OUTSIDE IN DUE TO COMBINATION OF EXTERNAL WALL THINNING FROM CORROSION, CORROSION FATIGUE AND SHEAR OVERLOAD FROM BENDING.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190134 | 33111 | 2019-12-19 12:18 | ORIGINAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2019-12-11 03:22 | 2019 |  |  | 32.4742 | -93.5086 | 1266121 | 2019-12-11 12:43 |  | NATURAL GAS |  | 6468 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | VALVE WAS OPENED; NO FURTHER ACTION REQUIRED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-12-11 03:22 | 2019-12-11 04:00 | ONSHORE | LA | 71037 | HAUGHTON | BOSSIER | MILEPOST | 47+4499 | HAUGHTON COMPRESSOR STATION | SHC 20-1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | ESD CONTROL VALVE ACTIVATED PREMATURELY | CLASS 2 LOCATION | NO |  | 383 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 16280 | 16280 | 70 | 71.4243824417985 | 300 | 306.104496179136 | 0 | 0 |  |  | 16650 | 17051.5109401755 | 16657.5288786209 | [8 empty] | 630 |  | 770 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | YES | [34 empty] | YES | COLD AND OLD O-RINGS | [161 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 270-688-6357 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 270-688-6497 | tina.baker@bwpipelines.com | DECEMBER 11, 2019 AT 03:22, GAS CONTROL RECEIVED AN ALARM FOR A VENT VALVE OPEN ON ITS SHC 4-6 ESD CONTROL VALVE ACCOMPANIED BY PRESSURE LOSS. WHILE AN OPERATIONS REPRESENTATIVE WAS EN ROUTE TO THE SITE, GAS CONTROL CALLED HIM STATING THAT NEIGHBORS HAD CALLED AND THAT THE POLICE AND FIRE DEPARTMENT WERE RESPONDING. ADDITIONALLY, THE GAS PRESSURE CONTINUED TO FALL. OPERATIONS REPRESENTATIVE CALLED 911 TO LET THEM KNOW HE WAS ON THE WAY TO THE SITE. OPERATIONS REPRESENTATIVE ARRIVED AT APPROXIMATELY 04:00, CLOSED THE POWER GAS THAT CONTROLS THE VALVE, AND MANUALLY CLOSED THE VALVE WHICH HAD OPENED PREMATURELY. HE INFORMED POLICE THAT THE SITE WAS SECURE. THE VALVE WAS SECURE AT 04:15. OPERATIONS REPRESENTATIVE ALSO CONTACTED GAS CONTROL TO VERIFY THE STATION PRESSURE WAS RETURNING TO NORMAL PRESSURE. A NEW REPAIR KIT WAS INSTALLED ON THE ESD CONTROL VALVE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190136 | 33135 | 2019-12-26 10:24 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2019-12-11 21:52 | 2019 |  |  | 38.4953 | -81.3122 | 1266172 | 2019-12-11 21:54 |  | NATURAL GAS |  | 7890 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THIS WAS AN ACTIVATION OF A COMPRESSOR STATION EMERGENCY SHUTDOWN SYSTEM (ESD). | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-12-11 14:05 | 2019-12-11 14:05 | ONSHORE | WV | 25045 | CLENDENIN | KANAWHA | MILEPOST | CLENDENIN CS | CLENDENIN COMPRESSOR STATION | CLENDENIN COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENTIONAL ACTIVATION OF THE COMPRESSOR STATION EMERGENCY SHUTDOWN SYSTEM (ESD). | CLASS 1 LOCATION | NO |  | 785 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 18857 | 18857 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 18857 | 19549.9081364829 | 18857 | [8 empty] | 673 |  | 1000 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL ROOM DID NOT CONTRIBUTE TO THE CAUSE OF THE INCIDENT. THE KNOWN CAUSE WAS THE ACTIVATION OF THE ESD SYSTEM. THE CONTROL ROOM WAS IN COMMUNICATION WITH THE COMPRESSOR STATION DURING THE INCIDENT AND WAS ABLE TO ASSIST IN PROVIDING DATA/INFORMATION, FUNCTIONING NORMALLY. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | A TRIGGER VALVE ON AN AIR SUPPLY WAS FROZEN WHICH CAUSED THE ESD TO ACTIVATE. | [161 empty] | CHRIS LEGG | US REGULATORY COMPLIANCE SPECIALIST | chris_legg@tcenergy.com | 304-545-4350 | 304-722-8530 |  |  |  | GEORGE HAMATY | MANAGER - US REGULATORY COMPLIANCE - EAST | 304-357-3728 | george_hamaty@tcenergy.com | AN UNINTENTIONAL RELEASE OF NATURAL GAS OCCURRED WHEN THE EMERGENCY SHUTDOWN SYSTEM (ESD) AT CLENDENIN CS ACTIVATED. THE EVENT RELEASED A CALCULATED VOLUME OF 7890 MCF OF NATURAL GAS, EXCEEDING PHMSA'S REPORTABLE QUANTITY OF 3000 MCF. THE ESD SYSTEM RELEASED GAS, AS DESIGNED, THROUGH VARIOUS BLOW-OFF STACKS AROUND THE STATION. ONE OF THE BLOCK VALVES (24") ON THE ESD SYSTEM FAILED TO CLOSE AND REMAINED OPEN FOR APPROXIMATELY 21 MINUTES. THE STATION WAS MANNED AT THE TIME OF THE INCIDENT. NO FIRES, DEATHS, INJURIES, EVACUATIONS, OR ROAD CLOSURES OCCURRED AS RESULT OF THE INCIDENT. AN INVESTIGATION OF THE PROBABLE CAUSE OF THE ESD REVEALED A TRIGGER VALVE, ON AN AIR SUPPLY, WHICH CONTROLS THE SYSTEM, WAS FROZEN WHICH CAUSING THE ESD TO ACTIVATE. IT WAS DETERMINED A PROGRAMMING ERROR CAUSED THE BLOCK VALVE TO REMAIN OPEN FOR THE ADDITIONAL TIME. LOGIC WAS ADDED TO THE PROGRAMMABLE LOGIC CONTROLLER (PLC) TO ALLOW THE VALVE TO CLOSE CORRECTLY FOR FUTURE ESD ACTIVATIONS.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200001 | 34196 | 2020-01-03 13:18 | SUPPLEMENTAL FINAL | 1007 | TALLGRASS INTERSTATE GAS TRANSMISSION, LLC | 370 VAN GORDON ST | LAKEWOOD | CO | 80228 | 2019-11-30 13:05 | 2019 | CENTRAL | NO | 41.0755 | -103.6199 | 1265633 | 2019-12-05 15:19 | 1265936 | NATURAL GAS |  | 4034 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | IDLE | [5 empty] | NO |  |  | NO | [11 empty] | 0 | 2019-12-01 10:55 | 2019-12-01 10:55 | ONSHORE | NE | 69145 | Not Within a Municipality | KIMBALL COUNTY | MILEPOST | COMPRESSOR | KIMBALL COMPRESSOR STATION | KIMBALL COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | PNEUMATIC ACTUATOR | 2004 | 2004 | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | RUBBER O-RING | OTHER | [8 empty] | RELEASE OF NATURAL GAS. | CLASS 1 LOCATION | NO |  | 418 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 9669 | 9669 | 0 | 0 | 410 | 418.34281144482 | 215 | 219.374888928381 | LABOR AND MATERIALS. | 2.397 | 10294 | 10317.0205904043 | 10306.7177003732 | 0 | 0 | 0 | 0 | NO |  |  |  | 633 | 35000 | 1170 | 192.619(A)(1) |  | 1997-07-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | CONTROLLER |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES |  |  | YES | [16 empty] | YES | [136 empty] | YES | [36 empty] | KAYLA ROBINSON | COMPLIANCE COORDINATOR | kayla.robinson@tallgrassenergylp.com | 303-763-3464 |  |  |  |  | KAYLA ROBINSON | COMPLIANCE COORDINATOR | 303-763-3464 | kayla.robinson@tallgrassenergylp.com | ON 11/30/2019 KIMBALL COMPRESSOR STATION HAD A RELEASE OF NATURAL GAS DUE TO HIGH WINDS AND HEAVY BLOWING SNOW. THERE WAS A LOSS OF COMMERCIAL POWER, FOLLOWED BY LOSS OF THE BACKUP UPS, RESULTING IN AN ESD AT THE STATION. AS THE ESD OCCURRED, A PNEUMATIC VALVE DID NOT TRANSFER TO THE CLOSED POSITION AND VENTED GAS THROUGH A 2 INCH ESD LINE. THE VALVE WAS CLOSED AT 10:55 AM MST ON SUNDAY DECEMBER 1, 2019. SECOND NRC REPORT (48 HOUR UPDATE) FILED ON 12/9/2019, NRC# 1265936
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200002 | 34741 | 2020-01-08 11:34 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2019-12-10 13:39 | 2019 | EASTERN | NO | 40.5078 | -83.8219 | 1266049 | 2019-12-10 17:49 | 1266185 | NATURAL GAS |  | 2064 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-12-12 18:45 | 2020-12-08 10:00 |  | NO |  |  | NO | [11 empty] | 0 | 2019-12-10 14:23 | 2019-12-10 15:45 | ONSHORE | OH | 43310 | BELL CENTER | LOGAN | MILEPOST | 704+97 | DAYTON LAKE | MS704997 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 4 | NO | 0.236 |  | UNKNOWN | SINGLE SAW |  | UNKNOWN | PAINT |  | YES | [26 empty] | 1951 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 2 LOCATION | NO |  | 110 |  | NO | NO |  |  | 10000 | 10203.4832059712 | 0 | 0 | 4396 | 4396 | 1780000 | 1816220.01066288 | 0 | 0 | 0 | 0 |  | 2.13 | 1794396 | 842934.110025388 | 1830819.49386885 | 1 | 0 | 1 | 1 | NO |  |  |  | 220 | 1690 | 300 | OTHER | 192.557 | 1973-04-19 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | OTHER | DOWNSTREAM CUSTOMER- VECTERAN |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [9 empty] | UNKNOWN | [5 empty] | YES | 60 |  | PASSENGER CAR | ROADWAY | 18 | YES |  |  |  | YES | INSIDE A BULDING | [233 empty] | KAMRAN ROSTAMI ASRABADI | COMPLIANCE SPECIALIST | kamran_rostami@tcenergy.com | [5 empty] | PAUL SHAFFER | US REGULATORY COMPLIANCE MANAGER EAST | (304)550-4866 | paul_shaffer@tcenergy.com | ON DECEMBER 10, 2019, AT 14:23 EASTERN STANDARD TIME (EST), COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA) GAS CONTROLLER RECEIVED A CALL FROM VECTREN, THE LOCAL DISTRIBUTION COMPANY (LDC), REGARDING LOW PRESSURE INDICATIONS AT DAYTON LAKE DELIVERY MEASURING STATION (MS) 704997. AN OPERATIONS PERSONNEL WAS DISPATCHED AND ARRIVED ON SITE AT 15:45 EST WHERE HE CONFIRMED THAT THE LOW-PRESSURE ALARM WAS DUE TO A CAR ACCIDENT. A CAR DAMAGED THE MS BUILDING AND INITIATED AN UNINTENTIONAL NATURAL GAS RELEASE FROM COLUMBIA FACILITY (MS704997). THE DRIVER WAS SENT TO A NEARBY HOSPITAL JUST FOR ROUTINE CHECK-UP AND WAS RELEASED FROM HOSPITAL ON THE SAME DAY. AT 18:45 EST, THE LEAK WAS ISOLATED, AND THE FACILITY WAS REMOVED FROM SERVICE. THE INITIAL NATIONAL RESPONSE CENTER (NRC) REPORT NO.1266049 AND THE NRC 48-HOUR REPORT NO. 1266185 HAVE BEEN CALLED-IN ON DECEMBER 10TH AND DECEMBER12TH RESPECTIVELY . THE CONSTRUCTION OF THE NEW MS FACILITY HAS BEEN COMPETED, COMMISSIONED AND WAS READY TO START THE FLOW AS OF DECEMBER 8TH, 2020. THIS FLOW WILL START ONCE THE DOWNSTREAM LDC COMPLETES THEIR TIE-IN TO THE MS. TO AVOID ANY FUTURE SIMILAR VEHICULAR DAMAGE TO THE NEWLY FACILITY FROM RE-OCCURRING , THE NEW MS WAS CONSTRUCTED ABOUT 100 FEET OFF OF THE ROAD.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200003 | 33358 | 2020-01-09 12:54 | SUPPLEMENTAL FINAL | 31451 | KINDER MORGAN TEXAS PIPELINE CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-12-12 12:15 | 2019 | CENTRAL | NO | 29.7477 | -94.9133 | 1266544 | 2019-12-16 10:35 | 1266704 | NATURAL GAS |  | 30 | 1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-12-12 14:00 | 2020-02-05 07:45 |  | NO |  |  | NO | [11 empty] | 0 | 2019-12-12 12:15 | 2019-12-12 12:15 | ONSHORE | TX | 77523 | Not Within a Municipality | CHAMBERS | MILEPOST | MP 4.20 | INDEX 128-18 | CEDAR BAYOU TANK SITE REGULATOR | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 60 | YES | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 193 |  | NO | NO |  |  | 0 | 0 | 2 | 2.04069664119424 | 66 | 66 | 126165 | 128732.245868136 | 904 | 922.394881819797 | 0 | 0 |  | 2.1935 | 127137 | 59584.2632100012 | 129722.681446597 | 0 | 0 | 0 | 0 | NO |  |  |  | 700 | 930 | 780 | 192.619(A)(1) |  | 1970-08-11 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  |  | NO | [5 empty] | YES | THE FAILURE WAS ON A REGULATOR VALVE | YES |  |  |  |  | YES | THE FAILURE WAS ON A REGULATOR VALVE | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE WAS OPERATING UNDER MAOP AND CONTROLLERS WERE NOT MAKING ANY CHANGES TO PIPELINE CONDITIONS. NO CHANGES WERE MADE TO EITHER SETPOINT OR HORSEPOWER. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | SEAL (NOT COMPRESSOR SEAL) OR PACKING | [17 empty] | YES | AGE OF THE STEM SEALS | [161 empty] | KRISTIN VAN DER LAAN | MANAGER - CODES AND COMPLIANCE | kristin_vanderlaan@kindermorgan.com | 303-914-7753 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR - CODE AND COMPLIANCE | 713-369-9443 | jaime_hernandez@kindermorgan.com | AT APPROXIMATELY 12:00 PM ON DECEMBER 12, 2019, A KINDER MORGAN TEXAS PIPELINE LLC (KMTP) EMPLOYEE ARRIVED AT THE KMTP CEDAR BAYOU TANK SITE TO PERFORM REGULARLY SCHEDULED OPERATIONS AND MAINTENANCE WORK. AT APPROXIMATELY 12:15 PM, THE EMPLOYEE NOTICED NATURAL GAS LEAKING OUT OF A BREATHER FITTING ON A COMPONENT OF THE ACTUATOR ON THE 10-INCH PRIMARY REGULATOR. THE EMPLOYEE CALLED HIS SUPERVISOR WHO THEN INITIATED THE INTERNAL EMERGENCY RESPONSE LINE (ERL) NOTIFICATIONS PER COMPANY PROCEDURES TO DISCUSS THE NATURAL GAS RELEASE EVENT. DURING THE CALL IT WAS DETERMINED THAT THE AMOUNT OF GAS LOSS DID NOT MEET THE INCIDENT REPORTING CRITERIA AND REPAIR COSTS WERE NOT EXPECTED TO REACH THE $50,000 REPORTING THRESHOLD. THERE WERE NO INJURIES OR PROPERTY DAMAGE ASSOCIATED WITH THE LEAK. IN ORDER TO SECURE THE LOCATION, THE EMPLOYEE CHANGED PRIMARY REGULATION FROM THE LEAKING REGULATOR TO A SECONDARY REGULATOR IN ORDER TO CONTINUE SUPPLYING GAS TO DOWNSTREAM CUSTOMERS. ONCE THE SECONDARY REGULATOR PICKED UP THE LOAD, THE UPSTREAM MONITOR VALVE AND DOWNSTREAM ISOLATION VALVES ON THE LEAKING PRIMARY REGULATOR RUN WERE SHUT AND SECURED USING COMPANY LOCKOUT/TAGOUT (LOTO) PROCEDURES ISOLATING THE PRIMARY REGULATOR RUN. THE PRIMARY REGULATOR RUN WAS THEN ALLOWED TO BLEED OUT TO ATMOSPHERE THROUGH THE BREATHER FITTING AND BODY BLEED ON THE PRIMARY REGULATOR. ON DECEMBER 16 AT APPROXIMATELY 10:00 AM, AFTER FURTHER INVESTIGATION AND REPAIR EVALUATION, FIELD OPERATIONS DETERMINED THAT THE COSTS OF REPAIR WOULD LIKELY EXCEED THE $50,000 REPORTABLE THRESHOLD. THE COSTS OF ESTIMATED REPAIRS HAD INCREASED BECAUSE THE EXCAVATION COSTS TO EXCAVATE THE BELOWGROUND REGULATOR EXCEEDED THE ORIGINAL ESTIMATE. A FOLLOW-UP ERL NOTIFICATION WAS INITIATED AND DURING THE CALL IT WAS DETERMINED THAT NOTIFICATION TO THE NRC AND RAILROAD COMMISSION OF TEXAS SAFETY DIVISION WAS REQUIRED. TRRC INCIDENT REPORT 2105 48 HOUR NRC REPORT 1266704 INITIALLY IT WAS DETERMINED THAT THE LEAKAGE WAS CAUSED BY BROKEN STEM SEALS ON THE PRIMARY REGULATOR. AFTER REPLACING THE STEM SEALS THERE WAS STILL SOME SMALL LEAKAGE DETECTED. AFTER CONSULTING WITH THE VALVE SERVICE COMPANY AND FURTHER INSPECTING THE VALVE STEM, IT WAS DETERMINED THAT THE VALVE STEM NEEDED TO BE REPLACED. THE NEW VALVE STEM WAS REPLACED ON FEBRUARY 3, 2020 AND AFTER PURGING, PACKING, AND OPERATING THE REGULATOR IT WAS CONFIRMED THAT NO LEAKAGE REMAINED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200004 | 33431 | 2020-01-09 13:30 | SUPPLEMENTAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2019-12-17 16:05 | 2019 | CENTRAL | NO | 27.2561 | -98.9003 | 1266709 | 2019-12-17 21:22 | 1266770 | NATURAL GAS |  | 6156 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-12-17 16:05 | 2019-12-17 16:40 |  | NO |  |  | NO | [11 empty] | 0 | 2019-12-17 16:40 | 2019-12-17 16:40 | ONSHORE | TX | 78361 | Not Within a Municipality | JIM HOGG | MILEPOST | 0.0 + 0.0 | THOMPSONVILLE TO PRAIRIE LEA SYSTEM | 3017 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2007 | UNKNOWN | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 581 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 14159 | 14159 | 1400 | 1428.48764883597 | 0 | 0 | 0 | 0 |  | 2.3 | 15559 | 15334.9917393034 | 15587.487648836 | 0 | 0 | 0 | 0 | NO |  |  |  | 674.24 | 0 | 1100 | 192.619(A)(1) |  | 1991-11-04 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 1 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INVESTIGATION IDENTIFIED NO CONTROLLER ISSUES. CONTROLLER ACTIONS WERE CONSISTENT WITH COMPANY PROTOCOLS | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [23 empty] | YES | [167 empty] | CHRISTOPHER PALAFOX | REGULATORY COMPLIANCE SPECIALIST | christopher.palafox@energytransfer.com | 713-989-4464 |  |  |  |  | CHRIS KRESTA | MANAGER-INTRASTATE REGULATORY COMPLIANCE | 713-989-7077 | chris.kresta@energytransfer.com | ON DECEMBER 17, 2019 AT APPROXIMATELY 16:05 HRS., ENERGY TRANSFER EXPERIENCED A GAS RELEASE ON THE ESD SYSTEM ON A REGULATED CLASS 1 TRANSMISSION LINE, THE 3017 THOMPSONVILLE TO PRAIRIE LEA SYSTEM 24 INCH PIPELINE INSIDE THE THOMPSONVILLE COMPRESSOR STATION. THE COMPRESSOR STATION IS LOCATED IN JIM HOGG COUNTY 14 MILES SOUTHWEST OF HEBBRONVILLE, TX. GAS CONTROL OBSERVED AN ESD VALVE POSITION FAULT AND NOTIFIED OPERATIONS. OPERATIONS PERSONNEL WERE DISPATCHED TO INVESTIGATE AND WHEN THEY ARRIVED ON LOCATION THEY FOUND THE BLOW DOWN VALVE WAS OPENED, RELEASING GAS. AT APPROXIMATELY 16:40 HRS., THE MANUAL VALVE UNDERNEATH THE AUTOMATED BLOW DOWN VALVE WAS CLOSED, SECURING THE GAS RELEASE. ONCE THE ESD WAS RESET, OPERATIONS PERSONNEL NOTICED A 1/4 INCH RELIEF VALVE FOR THE SUPPLY TO THE BETTIS ESD ACTUATOR WAS LEAKING. THE LEAK, OVER TIME, DID NOT PROVIDE AMPLE POWER GAS TO THE ACTUATOR WHICH TRIGGERED THE ESD WHICH THEN CAUSED THE BLOW DOWN VALVE TO OPEN. OPERATIONS PERSONNEL REPLACED THE 1/4 INCH RELIEF VALVE. AT APPROXIMATELY 16:40 HRS. ON DECEMBER 17, 2019 THE SYSTEM WAS BACK IN OPERATION. THIS PIPELINE IS UNDER THE JURISDICTION OF THE TEXAS RAILROAD COMMISSION. ON DECEMBER 17, 2019, THIS INCIDENT WAS TELEPHONICALLY REPORTED TO THE NATIONAL RESPONSE CENTER (NRC#1266709) AT 21:22 HRS. AND TO THE TXRRC (INCIDENT#2106) AT 21:45 HRS. A 48 HOUR NRC UPDATE WAS MADE ON DECEMBER 18, 2019 AT 13:40 HRS. (NRC#1266770). AFTER CLOSER INSPECTION AND REACHING OUT TO GENERANT VALVE MANUFACTURE FOR FAILURE ANALYSIS, IT WAS FOUND THAT SMALL PAINT CHIPS WERE ON THE SEATING AREA OF THE VALVE DUE TO PAINT OVER SPRAYING ON THE HEADER PIPING. THE VALVE WAS NOT COMPLETELY COVERED WITH PLASTIC WRAP AND TAPED OFF, ALLOWING PAINT PARTICLES TO BE SPRAYED ONTO THE BACKSIDE OF THE RELIEF VALVE NOZZLE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200005 | 33574 | 2020-01-17 22:23 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | ONE ENERGY PLAZA | DETROIT | MI | 48226 | 2019-12-20 05:30 | 2019 | EASTERN | NO | 42.7869 | -82.531 | 1266902 | 2019-12-20 10:21 |  | NATURAL GAS |  | 0 | 67 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-12-20 05:30 | 2019-12-28 20:00 |  | NO |  |  | NO | [11 empty] | 0 | 2019-12-20 05:30 | 2019-12-20 05:30 | ONSHORE | MI | 48054 | EAST CHINA | ST. CLAIR | MILEPOST | DEHY | BELLE RIVER COMPRESSOR STATION | BELLE RIVER DEHY | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | DEHYDRATOR/DRIER/TREATER/SCRUBBER | [38 empty] | 2001 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | REBOILER BURNER TUBE HAD A WELD DEFECT. THE REBOILER BURNER TUBE ALLOWS THE GLYCOL TO BE HEATED FOR DEHYDRATION. WHEN THE REBOILER TUBE FAILED IT RELEASED GLYCOL AND THE GLYCOL CAUGHT FIRE. | CLASS 1 LOCATION | NO |  | 478 |  | NO | NO |  |  | 0 | 0 | 177 | 180.60165274569 | 0 | 0 | 150000 | 153052.248089568 | 5000 | 5101.74160298561 | 0 | 0 |  | 2.6418 | 155177 | 72679.7553758663 | 158334.591345299 | 0 | 0 | 0 | 0 | NO |  |  |  | 1000 | 76.08 | 1200 | 192.619(A)(2) |  | 2001-11-06 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 80 | NO |  |  | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM RESPONDED APPROPRIATE AND TIMELY TO THE ALARMS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | REBOILER BURNER TUBE HAD A WELD DEFECT. THE REBOILER BURNER TUBE ALLOWS THE GLYCOL TO BE HEATED FOR DEHYDRATION. WHEN THE REBOILER TUBE FAILED IT RELEASED GLYCOL AND THE GLYCOL CAUGHT FIRE. |  |  |  | YES | [174 empty] | FRENAE F. SMITH | MANAGER CODES AND STANDARDS | frenae.smith@dteenergy.com | 313-389-7762 |  |  |  |  | FRENAE F. SMITH | MANAGER CODES AND STANDARDS | 313-389-7762 | frenae.smith@dteenergy.com | ON DECEMBER 20, 2019 AT 05:30, THE LOCAL ONSITE PERSONNEL IDENTIFIED A FIRE IN THE REBOILER UNIT OF THE DEHY AND SHORTLY AFTER IT WAS CONFIRMED BY GAS CONTROL. GAS CONTROL MADE THE APPROPRIATE NOTIFICATIONS. THE NATIONAL RESPONSE CENTER AND THE MICHIGAN PUBLIC SERVICE COMMISSION WERE NOTIFIED. THE UNIT WAS SHUT DOWN AND FIRE WAS EXTINGUISHED. THERE WAS NO IMPACT TO GAS SUPPLY TO CUSTOMERS. THE EXTENT OF THE DAMAGE WAS ASSESSED. THE DEHY ALARM HISTORY AND OPERATIONAL DATA WAS EVALUATED FOR THE INITIAL ROOT CAUSE ANALYSIS. ON DECEMBER 21, 2019, THE TUBE BUNDLE WAS REMOVED, AND AN INSPECTION WAS COMPLETED. IT WAS DETERMINED THAT THE REBOILER BURNER TUBE HAD A WELD DEFECT. THE REBOILER BURNER TUBE ALLOWS THE GLYCOL TO BE HEATED FOR DEHYDRATION. WHEN THE REBOILER TUBE FAILED IT RELEASED GLYCOL AND THE GLYCOL CAUGHT FIRE. IT WAS DETERMINED THAT THE BUNDLE NEEDED TO BE REPLACED. ON DECEMBER 26, 2019, THE BURNER ASSEMBLY WAS INSTALLED AND ALIGNED INSIDE OF FIRE TUBES. THE FIRE TUBES WERE LEAK CHECKED OVERNIGHT. ON DECEMBER 26, 2019, THE VESSEL HEAD WAS INSTALLED AND LEAK CHECKED. ADDITIONALLY, THE BURNER ASSEMBLY, EXHAUST STACK, BURNER BOX, FUEL LINE AND TEG WERE INSTALLED AND REFILLED. ON DECEMBER 27, 2019, THE REBOILER WAS REFILLED WITH GLYCOL. ON DECEMBER 28, 2019, ALL REPAIR WORK WAS COMPLETED ON THE BELLE RIVER DEHY. THE UNIT WAS BROUGHT ONLINE AT 16:30 AND WAS RUNNING CONTINUOUSLY. THE REBOILER TEMPERATURE WAS INITIAL HELD AT 300 DEGREES F AND BEING RAISED BY 25 DEGREES PER 1/2 HOUR. WE WERE FLOWING 3 MMCF/HR OF GAS THROUGH IT. ONCE IT REACHED FULL OPERATING TEMPERATURE OF 360 DEGREES F (AT APPROXIMATELY 20:00), IT RAN FOR A 24-HOUR TEST PERIOD. TEST PERIOD OF 24-HOURS WAS SUCCESSFULLY AND WAS AVAILABLE FOR GAS CONTROL FOR FULL USE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200006 | 34797 | 2020-01-21 19:26 | SUPPLEMENTAL FINAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-12-22 23:49 | 2019 | CENTRAL | NO | 41.3572 | -92.0577 | 1267113 | 2019-12-23 01:19 | 1267191 | NATURAL GAS |  | 22510 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | ONLY UNIT #14 WAS SHUTDOWN TEMPORARILY |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2019-12-23 00:38 | 2019-12-23 00:38 | ONSHORE | IA | 52231 | Not Within a Municipality | KEOKUK | SURVEY STATION NO. | 3612943 | COMPRESSOR STATION 109 HARPER | AMARILLO #4 LINE (108 TO 109) | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1984 | 1984 | CARBON STEEL |  | OTHER | [8 empty] | NATURAL GAS RELEASED TO ATMOSPHERE THROUGH UNIT #14 8-INCH VENT VALVE ONCE THERE WAS NO CONTROL SIGNAL FROM PLC TO COMMAND THE VENT VALVE TO REMAIN CLOSED; | CLASS 1 LOCATION | NO |  | 663 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 52899 | 52899 | 1520 | 1550.92944730762 | 585 | 596.903767549316 | 0 | 0 |  | 2.35 | 55004 | 55828.7073957256 | 55046.8332148569 | 0 | 0 | 0 | 0 | NO |  |  |  | 647 | 220000 | 712 | 192.619(C) |  | 1960-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NEARBY PUBLIC NOTIFIED NGPL GAS CONTROL OF LOUD NOISE (NATURAL GAS RELEASE); | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  | YES | [27 empty] | YES | [159 empty] | YES | [6 empty] | WILLIAM MARTIN MULLER | SPECIALIST-PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 2053253863 | 2053253592 | MICHAEL BOHANNAN | mike_bohannan@kindermorgan.com | 3197282208 | JAIME HERNANDEZ | DIRECTOR ENGINEERING CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | NRC REPORT #1267113 AND NRC 48-HOUR UPDATE REPORT #1267191: 23:49-HOUR, 12/22/2019, RESIDENTS LIVING NEAR NGPL STATION 109 CALLED NGPL GAS CONTROL REPORTING A LOUD NOISE. 23:56-HOUR, 12/22/2019, NGPL GAS CONTROL STAFF CONTACTED NGPL ON-CALL STAFF. 00:38-HOUR, 12/23/2019, NGPL STAFF ARRIVED AT STATION 109, SAFELY ENTERED THE AREA AND FOUND NATURAL GAS RELEASING TO ATMOSPHERE FROM THE 8-INCH VENT VALVE ASSOCIATED WITH UNIT #14 THEREBY CONFIRMING THE INCIDENT. NGPL STAFF IMMEDIATELY CLOSED TWO MANIFOLD VALVES SERVING UNIT #14 TO TERMINATE THE NATURAL GAS RELEASE. 01:30-HOUR NGPL STAFF SPECIALIST ARRIVED ON SITE TO BEGIN INVESTIGATION OF THE INCIDENT AND BEGIN SUBSEQUENT REPAIRS AS NEEDED. INVESTIGATION OF THE INCIDENT FOUND THE UNIT #14 PLC ELECTRONIC CARD CONTROLLING SIGNAL OUT DISTRIBUTION HAD FAILED. WHEN THE PLC ELECTRONIC CARD SIGNAL OUT WAS NO LONGER AVAILABLE; THERE WAS NO SIGNAL COMMANDING THE VENT VALVE TO REMAIN IN THE CLOSED POSITION THEREFORE THIS VALVE OPENED AND RELEASED NATURAL GAS. BY DESIGN, WITH NO SIGNAL RECEIVED FROM THE PCL ELECTRONIC SIGNAL OUT DISTRIBUTION CARD, UNIT #14 CEASED RUNNING. HOWEVER THE MANIFOLD VALVES REMAINED OPEN IN THEIR RESPECTIVE POSITION AS LAST COMMANDED BY THE PLC. WITH FAILURE OF THE PLC ELECTRONIC SIGNAL OUT DISTRIBUTION CARD, THE PLC WAS UNABLE TO COMMAND THE MANIFOLD VALVES TO PROPER CLOSED POSITION WHICH WOULD HAVE RETAINED THE UNIT BLOW DOWN TO A TYPICAL NON-REPORTABLE VOLUME. 2:45-HOUR, NECESSARY REPAIRS WERE COMPLETED WHICH INCLUDED REPLACING THE PLC ELECTRONIC SIGNAL OUT DISTRIBUTION CARD AND FOLLOWING GENERAL INTEGRITY INSPECTION, UNIT #14 WAS AVAILABLE FOR SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200007 | 34301 | 2020-01-30 13:00 | SUPPLEMENTAL FINAL | 2731 | CHEVRON PIPE LINE CO | 1400 SMITH STREET | HOUSTON | TX | 77002 | 2019-12-31 14:50 | 2019 | CENTRAL | NO | 29.6655 | -91.2547 | 1267695 | 2019-12-31 16:11 |  | NATURAL GAS |  | 173.3 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | IDLE | [5 empty] | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-01-01 | VALVE CLOSURE |  | 2020-01-01 | 0 | 2019-12-31 15:50 | 2019-12-31 15:50 | ONSHORE | LA | 77563 | BAYOU VISTA | ST. MARY | MILEPOST | MP 1.3 | FLOODWAY SYSTEM | LAL13321A | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 54 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 | NO | 0.562 | 52000 | X60 ERW | OTHER | THIS IS A DEAD LEG SCHEDULED FOR ABANDONMENT. | UNKNOWN | OTHER | CEMENT | NO | [26 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 330 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 320000 | 326511.462591079 | 0 | 0 | 307035 | 313282.646614537 | ENLINK INVOICE TO CHEVRON | 0 | 627035 | 293682.378265505 | 639794.109205616 | 0 | 0 | 0 | 0 | NO |  |  |  | 850 | 0 | 1404 | OTHER | THIS IS A DEAD LEG THAT IS SCHEDULED FOR ABANDONMENT | 2001-05-24 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 1500 | NO | [5 empty] | YES | THIS IS 1500 FT. OF PIPE THAT IS A DEAD LEG AND SCHEDULED FOR ABANDONMENT. | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | LOCALIZED PITTING |  |  |  |  | YES | [5 empty] | YES |  |  |  | YES | YES | [12 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [20 empty] | YES | [42 empty] | GARRETT S. PARKER | DOT SPECIALIST | parkerg@chevron.com | 832-854-4596 |  |  |  |  | GARRETT S. PARKER | DOT SPECIALIST | 8328544596 | parkerg@chevron.com | AT APPROXIMATELY 1450 CDT A PROPERTY OWNER NOTIFIED CHEVRON PIPE LINE CONTROL CENTER OF BUBBLES IN A SHALLOW DITCH. CHEVRON PIPE LINE ROUTED AN EMPLOYEE TO INVESTIGATE WHERE THEY FOUND A LEAK HAD OCCURRED ON THE 30" FLOODWAY TRUNKLINE. THIS IS DEAD LEG LINE THAT THE LEAK OCCURRED ON THAT WAS SCHEDULED FOR ABANDONMENT IN 2021 AND CHEVRON PIPE LINE IS EVALUATING HOW TO MOVE SCHEDULE UP TO ABANDON. AFTER DIGGING UP THE LINE TO EVALUATE AND REPAIR IT WAS FOUND THAT INTERNAL CORROSION WAS A CONTRIBUTING FACTOR TO THE RELEASE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200008 | 33339 | 2020-02-03 15:32 | SUPPLEMENTAL FINAL | 32166 | SEMGAS, L.P. | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-01-08 11:40 | 2020 | CENTRAL | NO | 36.658 | -98.7529 | 1268323 | 2020-01-09 17:06 | 1268361 | NATURAL GAS |  | 1078 | 1004 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-01-08 11:40 | 2020-01-14 17:38 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-01-08 11:40 | VALVE CLOSURE |  | 2020-01-08 11:40 | 0 | 2020-01-08 11:40 | 2020-01-08 11:40 | ONSHORE | OK | 73746 | HOPETON | WOODS | SURVEY STATION NO. | 3657.5-3706.8 | ENABLE RESIDUE 16 INCH | ROSE VALLEY ENABLE RESIDUE SALES LINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 16 |  | 0.25 | 65000 | API-5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | PARAGON | EPOXY |  | YES | [26 empty] | 2014 | 2014 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 385 |  | NO | NO |  |  | 5000 | 5000 | 2149 | 2149 | 2307 | 2307 | 53650 | 53650 | 0 | 0 | 0 | 0 |  | 2.14 | 63106 | 30300.1169465852 | 63106 | 0 | 0 | 0 | 0 | NO |  |  |  | 880 | 0 | 1216 | 192.619(A)(1) |  | 2014-06-06 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 11035 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | YES | YES | [13 empty] | YES | MANUFACTURE SEAM DEFECT | [13 empty] | YES | MANUFACTURE SEAM DEFECT | UNKNOWN | [54 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [44 empty] | YES | [18 empty] | CHRIS PALAFOX | SPECIALIST REGULATORY COMPLIANCE | christopher.palafox@energytransfer.com | 7138984464 |  |  |  |  | CHRIS KRESTA | MANAGER - INTRASTATE REGULATORY COMPLIANCE | 7139897077 | chris.kresta@energytransfer.com | ON JANUARY 7, 2020, AT APPROXIMATELY 11:30 HRS, SEMGAS EXPERIENCED A GAS LEAK ON A REGULATED CLASS 1 TRANSMISSION LINE, THE ENABLE RESIDUE 16 INCH ON THE ROSE VALLEY PLANT SALES PIPELINE. THIS PIPELINE IS LOCATED IN WOODS COUNTY, 11 MILES SOUTHWEST OF ALVA, OKLAHOMA. OPERATIONS PERSONNEL WAS CONDUCTING A PIPELINE LEAK DETECTION SURVEY IN THE AREA AND DETECTED A HIGH HYDROCARBON LEL READING AND NOTICED BARE VEGETATION IN THE AREA. OPERATIONS PERSONNEL NOTIFIED THEIR SUPERVISOR OF A POTENTIAL LEAK. AT APPROXIMATELY 11:40 HRS, OPERATIONS PERSONNEL CLOSED THE UPSTREAM AND DOWNSTREAM BLOCK VALVES TO ISOLATED THE POTENTIAL LEAK AND BEGAN TO REDUCE THE PRESSURE. ON JANUARY 8, 2020 A CONTRACT CREW BEGAN EXCAVATION OF THE PIPELINE. ONCE THE PIPELINE WAS EXPOSED, OPERATIONS PERSONNEL DISCOVERED A PINHOLE LEAK ON THE PIPELINE'S LONGITUDINAL SEAM. A TOTAL OF 51 FEET OF PIPE WAS REMOVED AND THE AFFECTED PIPE SEGMENT WAS SENT TO THE LAB FOR ANALYSIS. THE 51 FEET OF PIPE WAS REPLACED WITH NEW PIPE TO PREVENT OTHER LEAKS FROM OCCURRING. ON JANUARY 14, 2020 AT APPROXIMATELY 17:38 HRS, THE PIPELINE WAS PUT BACK INTO SERVICE. THIS PIPELINE IS UNDER THE JURISDICTION OF THE OKLAHOMA CORPORATION COMMISSION. ON JANUARY 9, 2020, THIS INCIDENT WAS TELEPHONICALLY REPORTED TO THE NATIONAL RESPONSE CENTER (NRC#1268323) AT 17:06 HRS. AND TO THE OCC AT 17:10 HRS. THIS INCIDENT BECAME A REPORTABLE INCIDENT ONCE THE ESTIMATED REPAIR COST WENT OVER THE $50,000.00 LIMIT. A 48 HOUR NRC UPDATE WAS MADE ON JANUARY 10, 2020 AT 11:21 HRS. (NRC#1268361) ON FEBRUARY 7, 2020, LAB RESULTS CONFIRMED THE LEAK WAS DUE TO MANUFACTURER'S DEFECT IN THE PIPELINE'S LONGITUDINAL SEAM WELD. FURTHER CONSIDERATIONS WILL BE MADE FOR FUTURE ILI ASSESSMENTS IN ORDER TO DETERMINE THE OVERALL CONDITION OF THE REMAINING PIPE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200009 | 33326 | 2020-02-12 13:30 | ORIGINAL | 2620 | COLUMBIA GULF TRANSMISSION, LLC | 700 LOUISIANA ST. SUITE 700 | HOUSTON | TX | 77002 | 2020-01-17 10:39 | 2020 | CENTRAL | NO | 29.4821 | -91.0514 | 1268930 | 2020-01-17 10:58 | 1269061 | NATURAL GAS |  | 668 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | MINOR LEAK SUSPECTED ON TAP VALVE, CLASS 1, NO NEARBY STRUCTURES, NON-HAZARDOUS |  |  |  | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | MINOR LEAK ON TAP VALVE |  | OPERATIONAL CONTROL | MINOR LEAK ON TAP VALVE |  | 0 | 2020-01-09 10:00 | 2020-01-09 11:00 | ONSHORE | LA | 70380-1000 | Not Within a Municipality | TERREBONNE PARISH | SURVEY STATION NO. | STA 5222+30 | EL300 | MS4185 CABOT TAP | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | IN SOIL UNDER WATER | 102 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | TAP | 2006 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 765 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 1597 | 1597 | 64446 | 64446 | 0 | 0 | 0 | 0 | ESTIMATED COSTED IS FOR DIVERS TO EVALUATE LEAK. | 2.39 | 66043 | 31238.0969405189 | 66043 | 0 | 0 | 0 | 0 | NO |  |  |  | 828 | 8450 | 1037 | 192.619(A)(1) |  | 1964-10-25 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL |  | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA IS IN PLACE FOR EL300, BUT DUE TO THE NATURE OF THE MINOR LEAK, NO INDICATIONS WERE SEEN ON THE SCADA SYSTEM AND THEREFORE THE CONTROLLER WAS NOT INVESTIGATED. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [146 empty] | PAUL SHAFFER | COMPLIANCE SPECIALIST | paul_shaffer@tcenergy.com | 304-357-2245 |  |  |  |  | PAUL SHAFFER |  | 304-357-2245 | paul_shaffer@tcenergy.com | DURING NORMAL ROUNDS MADE BY A LANDOWNER IN THE RIGHT-OF-WAY (ROW) OF THE EAST LATERAL 300 (EL 300) PIPELINE OWNED AND OPERATED BY COLUMBIA GULF TRANSMISSION LLC (CGT) IN SOUTH LOUISIANA, A CONTINENTAL LAND AND FUR REPRESENTATIVE (LAND OWNER) NOTICED BUBBLES DEVELOPING RIGHT OFF THE CGT ROW. THE LAND OWNER INFORMED LOCAL CGT TEAM MEMBERS, PERFORMING MAINTENANCE ON NEARBY COMPANY ASSETS, AND THEY CONDUCTED A PRELIMINARY INVESTIGATION INTO THE AREA IN QUESTION. THE LEAK LOCATION WAS GRADED AS NON-HAZARDOUS TO ANYONE IN THE LOCAL VICINITY AS THIS IS LOCATED IN A REMOTE AREA. PLANS WERE MADE TO FURTHER INVESTIGATE THE FOLLOWING DAY. GAS SAMPLES WERE TAKEN TO DETERMINE IF THIS WAS MARSH GAS OR PIPELINE GAS. AFTER TWO SEPARATE GAS SAMPLES WERE PULLED AND BROUGHT IN TO A LOCAL LABORATORY, THE CGT INTEGRITY TEAM MADE A DETERMINATION BY COMPARING PIPELINE QUALITY GAS TO THE SAMPLES THAT THE CHARACTERISTICS OF THE GAS WERE SIMILAR ENOUGH TO MERIT NAMING THIS A LEAK ON THE EL 300 SYSTEM. THIS LEAK IS SUSPECTED TO BE ON AN ISOLATED 4-INCH TAP VALVE THAT USED TO BE A CABOT GAS FEED. INTEGRITY ENGINEERING ALONG WITH THE INVESTIGATING DIVE PARTY WILL WORK TO ANALYZE THE LEAK AND DEVELOP PLANS TO DETERMINE HOW TO ADDRESS AND MITIGATE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200010 | 33373 | 2020-02-18 15:07 | SUPPLEMENTAL FINAL | 15105 | PANHANDLE EASTERN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-01-19 06:21 | 2020 | CENTRAL | NO | 38.8448 | -93.3656 | 1269064 | 2020-01-19 11:46 | 1269170 | NATURAL GAS |  | 25882 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | ONLY UNIT 816 |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-01-19 06:21 | 2020-01-19 07:00 | ONSHORE | MO | 65337 | LA MONTE | PETTIS | SURVEY STATION NO. | 0+00 | HOUSTONIA COMPRESSOR STATION | HOUSTONIA 300/400 DISCHARGE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2016 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | RELIEF VALVE | [5 empty] | CLASS 1 LOCATION | NO |  | 137 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 48658 | 48658 | 1465 | 1465 | 497 | 497 | 0 | 0 |  | 1.88 | 50620 | 51346.5677762151 | 50620 | 0 | 0 | 0 | 0 | NO |  |  |  | 815 | 220 | 898 | 192.619(A)(1) |  | 1965-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  |  | NO | [5 empty] | YES | COMPRESSOR STATION PIPING. | YES |  |  |  |  | YES | COMPRESSOR STATION PIPING. | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | CONTROLLER |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | SOLENOID VALVE MALFUNCTIONED. | [22 empty] | YES | SOLENOID VALVE FROZE. | [161 empty] | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | AFTER PLACING UNIT 816 ONLINE AT 06:21, GAS CONTROL NOTICED THE SUCTION AND DISCHARGE PRESSURES DROPPING. GAS CONTROL NOTIFIED ON CALL PERSONNEL. WHEN ON-CALL PERSONNEL ARRIVED AT THE PLANT, THE UNIT WAS SHUT DOWN BECAUSE THE UNIT BLOWDOWN VALVE WAS OPEN. THE UNIT WAS SHUT DOWN AT 07:13. UPON INVESTIGATION, IT WAS DISCOVERED THAT THE SOLENOID VALVE FROZE UP WHICH PREVENTED PRESSURE FROM BEING APPLIED TO THE DOME OF THE UNIT BLOWDOWN/RELIEF VALVE. AIR OPERATED SOLENOID WAS REPLACED WITH AN ELECTRONIC SOLENOID.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200011 | 33353 | 2020-02-20 13:48 | ORIGINAL FINAL | 39193 | ROVER PIPELINE, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-01-25 04:33 | 2020 | EASTERN | NO | 41.3578 | -84.3636 | 1269538 | 2020-01-25 09:36 | 1269646 | NATURAL GAS |  | 15620 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | UNIT 4204 WAS SHUT DOWN. DEFIANCE FACILITY WAS NOT SHUT DOWN. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-01-25 04:33 | 2020-01-25 05:50 | ONSHORE | OH | 43512 | DEFIANCE | DEFIANCE | NOT APPLICABLE |  | DEFIANCE CS | DEFIANCE COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2017 | 2015 | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 107 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 27491 | 27491 | 1874 | 1874 | 240 | 240 | 0 | 0 |  | 1.76 | 29605 | 29471.549760767 | 29605 | 0 | 0 | 0 | 0 | NO |  |  |  | 1172 | 264 | 1500 | 192.619(A)(1) |  | 2017-10-05 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 60 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | THREADED FITTING | [9 empty] | YES | [172 empty] | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 7138575479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | 7138575479 | nathan.hlavaty@energytransfer.com | AT APPROXIMATELY 04:33 EST ON SATURDAY, JANUARY 25TH, 2020, THE DISCHARGE PSV FOR UNIT 4204 OPENED WHILE THE UNIT WAS RUNNING. A LOCAL SHERIFF WAS CONTACTED DUE TO A HIGH NOISE COMPLAINT, HE THEN CONTACTED AN ANR EMPLOYEE. AFTER ANR VERIFIED IT WAS NOT AN ISSUE WITH THEIR STATION, THE ANR EMPLOYEE CONTACTED A ROVER EMPLOYEE AT 05:15 EST. THE ROVER EMPLOYEE RESPONDED BY DRIVING TO THE STATION, DETERMINING THE ISSUE WAS UNIT 4204, AND SHUTDOWN UNIT 4204 AT 05:55 EST. FITTINGS WERE REPLACED AND TIGHTENED AND THE VALVE WAS MODIFIED (PULLED APART, INSPECTED, SOFT PARTS REPLACED) BEFORE RETURNING TO SERVICE, NO FURTHER ISSUES IDENTIFIED. ONCE IT WAS DETERMINED THAT ESTIMATES OF POTENTIAL GAS LOSS WERE GREATER THAN 3 MMCF, THE DIRECTOR OF REGULATORY COMPLIANCE WAS NOTIFIED TO MAKE A TELEPHONIC REPORT TO THE NATIONAL RESPONSE CENTER.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200012 | 33659 | 2020-02-20 14:14 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 4720 PIEDMONT ROW DR. | CHARLOTTE | NC | 28210 | 2020-01-20 08:57 | 2020 | EASTERN | NO | 34.0932 | -78.0428 | 1269165 | 2020-01-21 08:40 | 1269881 | NATURAL GAS |  | 0.5 | 0.025 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | BEING MONITORED DAILY. |  |  |  | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | BEING MONITORED |  | OPERATIONAL CONTROL | BEING MONITORED |  | 0 | 2020-01-20 08:42 | 2020-01-20 08:42 | ONSHORE | NC | 28479 | WINNABOW | BRUNSWICK | SURVEY STATION NO. | 34 5' 33.8" N | LINE 99 | 1181913 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | IN A WETLAND AREA | 60 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 | NO | 0.199 | 60000 | UNKNOWN | OTHER | UNKNOWN | UNKNOWN | EPOXY |  | UNKNOWN | [26 empty] | 1992 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | PREVIOUS LEAK CLAMP | [5 empty] | CLASS 1 LOCATION | NO |  |  | NOT FLAMMABLE | NO | NO |  |  | 0 | 0 | 2 | 2 | 45 | 45 | 626000 | 626000 | 210 | 210 | 0 | 0 |  | 89 | 626257 | 287494.485294591 | 626257 | 0 | 0 | 0 | 0 | NO |  |  |  | 477 | 477 | 477 | 192.619(A)(2) |  | 1992-08-16 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 36960 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS A GRADE 2 LEAK. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | [204 empty] | EQUIPMENT NOT INSTALLED PROPERLY |  |  |  | YES |  |  |  |  | NON-ROUTINE OPERATING CONDITIONS (ABNORMAL OPERATIONS OR EMERGENCIES) | NO | [145 empty] | YES |  |  |  |  | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | PIPELINE SAFETY MANAGER | 704-731-4618 | farris.berry@duke-energy.com | SUPERVISOR WAS CALLED TO A LEAK ON LINE 99 1/2 MILE SOUTH OF FUNSTON FARM. THE LEAK WAS INVESTIGATED ON THE RIGHT OF WAY. THE LEAK IS NOT BLOWING ABOVE GROUND BUT THERE ARE BUBBLES RISING FROM THE GROUND WATER AND CANNOT OBTAIN A % READING. THE LEAK HAS BEEN MONITORED DAILY WITH NO CHANGE IN STATE OR GRADE. THE AREA IS WET WITH STANDING WATER. CHECKED THE SURROUNDING AREA WITH NO MIGRATION DETECTED. THE GRADE 2 LEAK WAS A RESULT OF AN IMPROPERLY INSTALLED LEAK CLAMP FROM 1992. ONE SECTION OF PIPE WAS CUT OUT AND REPLACED TO REPAIR.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200013 | 34076 | 2020-02-23 20:17 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2020-01-24 15:52 | 2020 | EASTERN | NO | 42.7532 | -84.5611 | 1269701 | 2020-01-27 16:08 | 1269774 | NATURAL GAS |  | 2220 | 28 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-01-27 | 2020-02-01 13:47 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-01-24 20:20 | VALVE CLOSURE |  | 2020-01-24 20:41 | 0 | 2020-01-24 15:52 | 2020-01-24 15:53 | ONSHORE | MI | 48906 | LANSING | INGHAM | NOT APPLICABLE |  | LINE 1027 | BTW GRAND RIVER AND MLK BLVD. | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 120 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 | NO | 0.25 | 35000 | API 5L | OTHER | UNKNOWN | UNKNOWN | OTHER | WAX | UNKNOWN | [26 empty] | 1956 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | NO |  | 165 |  | NO | NO |  |  | 0 | 0 | 81 | 81 | 6416 | 6416 | 55651 | 55651 | 996 | 996 | 0 | 0 |  | 2.89 | 63144 | 32691.4074024296 | 63144 | 0 | 0 | 0 | 0 | NO |  |  |  | 382 | 7716 | 400 | 192.619(A)(2) |  | 1971-07-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 4843 | NO | YES |  | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1971 | YES | NO | [8 empty] | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | CARMELLA KING |  | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON PIONK | GAS COMPLIANCE MANAGER | 989-791-5749 | jason.pionk@cmsenergy.com | ON FRIDAY, JANUARY 24, 2020 AT APPROXIMATELY 15:53 HOURS A LEAK WAS IDENTIFIED ON A 12" HP PIPELINE OWNED AND OPERATED BY CONSUMERS ENERGY (CE). THE PIPELINE WAS INSTALLED IN 1956 AND IS LOCATED ALONG THE NE CORNER OF THE PROPERTY AT THE CE LANSING SERVICE CENTER, 530 W WILLOW ST, LANSING. A SECTION OF THE PIPELINE WAS ISOLATED BETWEEN N. GRAND RIVER AND N. MARTIN LUTHER KING BLVD ON FRIDAY, JANUARY 24 AT APPROXIMATELY 20:41 HOURS. FURTHER LEAK INVESTIGATION ACTIVITIES WERE PERFORMED ON SATURDAY, JANUARY 25, 2020 AND THE SITE WAS CONTINUOUSLY MONITORED THROUGHOUT THE WEEKEND. THERE WERE NO FATALITIES OR INJURIES THAT OCCURRED AS A RESULT OF THE INCIDENT. REMEDIATION WORK BEGAN ON THURSDAY, JANUARY 30, 2020. A VISUAL INSPECTION PERFORMED AT THE LEAK LOCATION, IDENTIFIED THE LEAK SOURCE AS LOCALIZE PITTING. A TEMPORARY REPAIR, BY INSTALLING A BOLTED PLIDCO FITTING WAS COMPLETED ON FEBRUARY 1, 2020 AND NORMAL OPERATIONS RESUMED IMMEDIATELY FOLLOWING REPAIRS AT APPROXIMATELY 13:47 HOURS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200014 | 33407 | 2020-02-28 12:44 | SUPPLEMENTAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2020-01-29 14:45 | 2020 | EASTERN | NO | 40.1366 | -77.0425 | 1269937 | 2020-01-30 09:26 | 1270051 | NATURAL GAS |  | 232.6 | 8.45 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | STOPPLE BYPASS INSTALLED TO ALLOW PIPELINE TO REMAIN IN SERVICE. |  |  |  | YES | OPERATOR | 2020-01-30 13:15 | NO | [5 empty] | OPERATIONAL CONTROL | MANUAL OPERATION OF MAINLINE VALVE UPSTREAM |  | OPERATIONAL CONTROL | MANUAL OPERATION OF MAINLINE VALVE DOWNSTREAM |  | 0 | 2020-01-29 14:45 | 2020-01-29 14:45 | ONSHORE | PA | 17019 | DILLSBURG | YORK COUNTY | SURVEY STATION NO. | 1380+40 | 1655 NORTH | 1655-050 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 45 | NO | YES |  |  |  |  | YES | CASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10 | NO | 0.188 | 60000 | X60 | LONGITUDINAL ERW - HIGH FREQUENCY |  | US STEEL- NATIONAL TUBE | COAL TAR |  | UNKNOWN | [26 empty] | 1972 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 2 LOCATION | NO |  | 227 |  | NO | NO |  |  | 0 | 0 | 20 | 20 | 556 | 556 | 1000000 | 1000000 | 0 | 0 | 0 | 0 | COSTS ARE TO BE DETERMINED. | 2.39 | 1000576 | 459611.99780664 | 1000576 | 0 | 0 | 0 | 0 | NO |  |  |  | 702 | 29.14 | 936 | 192.619(A)(2) |  | 1972-01-06 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 36651 | NO | [5 empty] | YES | INVESTIGATION IS UNDERWAY AS TO IF THIS SECTION OF LINE IS FULLY CONFIGURED FOR INTERNAL PIPELINE INSPECTION TOOLS. | YES |  |  |  |  | YES | PLEASE SEE DISCRIPTION IN QUESTION 7 | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS IS A LEAK IN A ROAD CROSSING, REPORTED DUE TO COST. AN INVESTIGATION WAS NOT NECESSARY DUE TO THE FACT THAT CONTROLLERS DO NOT HAVE CONTROL OF ANY DEVICES AT THIS SITE. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [146 empty] | WILLIAM YOUSE | COMPLIANCE SPECIALIST | william_youse@tcenergy.com | 304-357-3596 | 304-357-3522 | WILLIAM YOUSE | william_youse@tcenergy.com | 304-357-3596 | GEORGE HAMATY | MANAGER US REGULATORY COMPLIANCE EAST | 304-357-3728 | george_hamaty@tcenergy.com | PLEASE NOTE: QUESTION E1A. WOULD NOT ACCEPT 12140 (MSCF/D) AS AN ENTRY FOR FLOW RATE. THE FLOW RATE AT THE TIME OF THE INCIDENT HAS BEEN ENTERED AS 12.14 (MMCF/D). THE FOLLOWING IS AN ACCOUNT OF ACTIONS TAKEN RELATIVE TO THE DETECTION OF NATURAL GAS IN A ROAD CROSSING VENT ON PIPELINE 1655 NEAR DILLSBURG, YORK COUNTY, PENNSYLVANIA. PIPELINE 1655 IS A 10-INCH COATED AND PROTECTED CARBON STEEL PIPELINE WITH AN MAOP OF 936 PSIG. THIS PIPELINE IS OWNED AND OPERATED BY COLUMBIA GAS TRANSMISSION, LLC (OPID 2616). WHILE PERFORMING ROUTINE PIPELINE MAINTENANCE WORK, EMPLOYEES NOTICED THE ODOR OF NATURAL GAS AND INVESTIGATED ITS SOURCE. NATURAL GAS WAS FOUND IN A NEARBY ROAD CASING VENT. GAS SAMPLES WERE TAKEN FROM THE VENT PIPE AND A NEARBY METERING STATION ON LINE 1655 AND SENT TO AN INDEPENDENT LABORATORY FOR ANALYSIS. RESULTS CONFIRMED THAT THE SOURCE OF NATURAL GAS WAS FROM PIPELINE 1655. A PRESSURE DEDUCTION OF 100 TO 150 PSIG WAS PUT IN PLACE TO MAINTAIN APPROXIMATELY 42000 UPSTREAM CUSTOMERS. THE NATIONAL RESPONSE CENTER AND PHMSA ACCIDENT INVESTIGATION DIVISION WERE NOTIFIED OF THE INCIDENT (NRC# 1269937). PIPELINE STOPPLES AND BYPASS PIPING WAS INSTALLED, THIS REQUIRED THE CLOSING OF STATE ROUTE 74. MAINLINE PIPE REPLACEMENT IS COMPLETE, THE ORIGINAL CASING HAS BEEN REUSED, BYPASS PIPING HAS BEEN REMOVED AND PIPELINE 1655 HAS BEEN RETURNED TO SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200015 | 33953 | 2020-03-03 19:21 | SUPPLEMENTAL FINAL | 6660 | GREAT LAKES GAS TRANSMISSION CO | 700 LOUISIANA STREET | HOUSTON | TX | 77002 | 2020-02-02 10:00 | 2020 | EASTERN | NO | 43.9401 | -84.9411 | 1270167 | 2020-02-02 11:06 | 1270344 | NATURAL GAS |  | 672 | 852 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-02-02 10:13 | 2020-02-12 11:43 |  | NO |  |  | NO | [11 empty] | 0 | 2020-02-02 10:12 | 2020-02-02 10:12 | ONSHORE | MI | 48633 | LAKE GEORGE | CLARE | MILEPOST | 815.7 | GREAT LAKES GAS TRANSMISSION COMPANY | CS 12 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 72 | NO | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | WELD/FUSION |  | 2.375 |  | 0.218 | 35000 | UNKNOWN | SEAMLESS |  | US STEEL | COAL TAR |  | YES | [7 empty] | PIPE GIRTH WELD |  | NO | [16 empty] | 1990 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 52 |  | NO | NO |  |  | 0 | 0 | 2130 | 2130 | 1680 | 1680 | 549327 | 549327 | 0 | 0 | 14000 | 14000 | METALLURGICAL | 2.5 | 567137 | 261301.415902728 | 567137 | 0 | 0 | 0 | 0 | NO |  |  |  | 826 | 0 | 974 | 192.619(A)(1) |  | 1990-06-25 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | UPON REVIEW, IT WAS DETERMINED CONTROLLERS' ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES |  |  |  | YES | OTHER | REVERSE BENDING FATIGUE RELATED TO THERMAL EXPANSION AND CONTRACTION. | [15 empty] | YES | [8 empty] | 974 | [54 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | ROBERTA PRIMERA | COMPLIANCE SPECIALIST | roberta_primera@tcenergy.com | 248-561-7803 |  |  |  |  | ERIK HUGHES | SENIOR MANAGER - US REGULATORY COMPLIANCE | 402-490-7253 | erik_hughes@tcenergy.com | ON FEBRUARY 2, 2020, AT 1000 (ALL TIMES ARE EASTERN STANDARD TIME), A FARWELL CS TECHNICIAN RESPONDED TO THE SOUND OF AN APPARENT NATURAL GAS RELEASE WITHIN THE COMPRESSOR STATION YARD. AT 1012, THE TECHNICIAN CONFIRMED THE RELEASE ASSOCIATED WITH THE 36 INCH HEADER INLET TO A GAS COOLER. AT 1013, THE TECHNICIAN ACTIVATED AN EMERGENCY SHUT DOWN (ESD) AND THE STATION WAS ISOLATED FROM ANY GAS SOURCES WITH THE BLOW DOWN SUCCESSFULLY COMPLETED. AT 1025 THE STATION WAS CONFIRMED ISOLATED. AT 1106, THE INCIDENT WAS REPORTED TO THE NATIONAL RESPONSE CENTER (NRC); REPORT # 1270167. THE INCIDENT WAS REPORTED DUE TO ANTICIPATED REPAIR COSTS EXCEEDING THE REPORTABLE THRESHOLD OF $50,000. FIELD INVESTIGATION INDICATED THE SOURCE WAS DUE TO A FAILED WELD ASSOCIATED WITH THE WELD-O-LET 2 INCH SIPHON DRAIN LINE CONNECTED TO THE 36 INCH HEADER. THE FAILED SIPHON DRAIN LINE WAS REMOVED AND PLUGGED. THE 2 INCH SIPHON DRAIN LINE ASSEMBLY WAS SENT FOR METALLURGICAL ANALYSIS TO DETERMINE THE CAUSE OF THE FAILURE. 20200514 UPDATE: RCFA RECEIVED ON 1 MAY 2020; WILL INCLUDE FINAL SUMMARY AFTER PAGE-TURN MEETING WITH MPSC ON 21 MAY 2020. 20200609 UPDATE: RCFA WAS RECEIVED AND RESULTS REVIEWED WITH THE MPSC ON 5/21. ADDITIONAL QUESTIONS WERE ASKED AND RESPONSES WERE PROVIDED ON 6/8. 20200625 UPDATE: METALLURGICAL ANALYSIS DETERMINED THE PIPE CRACKED DUE TO REVERSED BENDING FATIGUE, WHICH WAS A RESULT OF THERMAL LATERAL, AND THERMAL EXPANSION AND CONTRACTION OF THE FIXED (IN CONCRETE) 2" DRAIN LINE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200016 | 33413 | 2020-03-04 15:19 | ORIGINAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2020-02-07 17:19 | 2020 | CENTRAL | NO | 30.3544 | -93.7063 | 1270705 | 2020-02-07 17:19 | 1270824 | NATURAL GAS |  | 10.368 | 1861 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | ATTEMPTED REPAIR BEFORE ISOLATION |  |  |  | YES | OPERATOR | 2020-02-07 17:19 | NO | [5 empty] | OPERATIONAL CONTROL | MONITORED LEAK AND REDUCED PRESSURE |  | OPERATIONAL CONTROL | MONITORED LEAK AND REDUCED PRESSURE |  | 0 | 2020-02-05 17:00 | 2020-02-05 | ONSHORE | LA | 70661 | STARKS | CALCASIEU | MILEPOST | 438.84 | VALVE 40A40 | MAINLINE A | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 3 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | MAINLINE | GATE |  | GROVE |  |  |  | 1952 | 1952 | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 2 LOCATION | NO |  | 578 |  | NO | NO |  |  | 0 | 0 | 3860 | 3860 | 22 | 22 | 59172 | 59172 | 0 | 0 | 0 | 0 |  | 2.074 | 63054 | 28956.1596137894 | 63054 | 0 | 0 | 0 | 0 | NO |  |  |  | 640 | 48000 | 780 | 192.619(A)(3) |  | 1970-06-15 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 111144 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | EXCAVATION FOR PREPARATION OF REMOVAL OF VALVE |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A VISIBLE CRACK ON 1/4" NIPPLE | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | OTHER | VALVE NIPPLE | [8 empty] | YES | [172 empty] | EDGAR RODRIGUEZ | REGULATORY COMPLIANCE SPECIALIST SR. | edgar.x.rodriguez@williams.com | 7132152846 |  | JOHN BELL | john.bell@williams.com | 3375697670 | TYSON GREEN | MANAGER PIPELINE SAFETY | 7132152535 | tyson.green@williams.com | FEBRUARY 5TH 2020: THE 40A40 MAINLINE BLOCK VALVE IS A REDUCED PORT VALVE THAT IS SCHEDULED FOR REPLACEMENT IN JUNE. IN PREPARATION FOR THAT PROJECT A CREW WAS HAND EXCAVATING THE VALVE ON FEBRUARY 5TH TO LOCATE THE WELD AND CONCRETE SUPPORTS. WHILE BACKFILLING THE EXCAVATION BY HAND, A SMALL GAS LEAK WAS HEARD AND A STOP WORK WAS CALLED. INVESTIGATION OF THE GAS LEAK IDENTIFIED THAT THE LEAK WAS COMING FROM A SMALL CRACK ON A FITTING CONNECTED TO THE BODY DRAIN VALVE. IT WAS KNOWN THAT IF THE PRESSURE COULD BE RELIEVED FROM THE VALVE BODY, THE LEAK WOULD BE STOPPED. FEBRUARY 5TH - 6TH: SEVERAL EFFORTS WERE MADE TO STOP THE LEAK BUT THOSE EFFORTS WERE UNSUCCESSFUL. FEBRUARY 7TH: DUE TO THE INABILITY TO STOP THE LEAK BY BLOWING DOWN THE VALVE BODY, THE ONLY OTHER OPTION TO STOP THE LEAK WAS TO REMOVE THE PRESSURE FROM THE PIPELINE. DUE TO THE LEAK BEING LOCATED ON A MAINLINE BLOCK VALVE, ONE SECTION OF THE PIPELINE UPSTREAM AND DOWNSTREAM HAD TO BE ISOLATED TO RELIEVE PRESSURE. OPERATIONS AND PROJECT PERSONNEL INVESTIGATED OPTIONS TO ACCELERATE VALVE REPLACEMENT OR REPAIRS. AFTER CONSIDERING ALL ALTERNATIVES THE $50,000 THRESHOLD WAS GOING TO BE EXCEEDED AND THE NRC WAS NOTIFIED. FEBRUARY 10TH: THE PIPELINE WAS ISOLATED AND DECOMPRESSION STARTED TO AVOID BLOWING DOWN ~26MMSCF IN GAS. THE LEAK WAS FREQUENTLY CHECKED BY OPERATIONS TO ENSURE THAT THE LEAK RATE DID NOT INCREASE. RECOMPRESSION WAS COMPLETE AND THE REMAINING PRESSURE (44 PSIG) WAS BLOWN DOWN TO ATMOSPHERE. 2/28/2020 - UPDATE - AFTER FURTHER INVESTIGATION, THE LEAK WAS NOT DUE TO CORROSION. THE 1/4 INCH NIPPLE HAS A VISIBLE CRACK INSIDE WHERE THE THREADS STOPPED ENTERING THE 1/2 INCH X 1/4 INCH REDUCER. IT APPEARS THAT THE 1/4 INCH NIPPLE WAS BENT AT SOME POINT IN TIME CAUSING THE CRACK SINCE THE CRACK AREA ITSELF IS CLEAN AND SHINY.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200018 | 33427 | 2020-03-06 11:26 | ORIGINAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2020-02-06 14:50 | 2020 | CENTRAL | NO | 29.974 | -91.8093 | 1270587 | 2020-02-06 17:03 | 1270666 | NATURAL GAS |  | 1 | 80 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-02-19 09:00 | 2020-02-19 18:00 |  | YES | OPERATOR | 2020-02-06 16:35 | NO | [5 empty] | OPERATIONAL CONTROL | ADJUSTED PRESSURE CONTROL VALVE 20 PERCENT LOWER THAN OPERATING PRESSURE |  | OPERATIONAL CONTROL | ADJUSTED PRESSURE CONTROL REGULATOR TO LOWER PIPELINE PRESSURE |  | 0 | 2020-02-06 14:50 | 2020-02-06 16:05 | ONSHORE | LA | 70562 | NEW IBERIA | IBERIA | MILEPOST | 136.6 | LAFAYETTE TO FRANKLIN 8" LINE | INDEX 205 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | MECHANICAL COUPLING | 1931 | 1931 | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | NO |  | 137 |  | NO | NO |  |  | 1500 | 1500 | 150 | 150 | 2 | 2 | 90000 | 90000 | 1200 | 1200 | 0 | 0 |  | 1.88 | 92852 | 42622.6735082307 | 92852 | 0 | 0 | 0 | 0 | NO |  |  |  | 275 | 11000 | 480 | 192.619(C) |  | 2018-03-20 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES |  |  | 20064 | NO |  | YES | YES | YES |  | YES | DRESSER COUPLED PIPE SEGMENTS | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | MECHANICAL COUPLING | [7 empty] | YES | [174 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 270.688.6357 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 270.688.6497 | tina.baker@bwpipelines.com | ON 2-6-2020 AT 14:50, GULF SOUTH PIPELINE RECEIVED A PHONE CALL THAT THERE WAS A GAS SMELL NEAR ITS FACILITY. GULF SOUTH TECHNICIANS ARRIVED AT THE LOCATION AT APPROXIMATELY 16:05, SMELLED ODORANT, AND LOCATED A LEAK USING A GAS DETECTOR. TECHNICIANS CONTACTED AREA MANAGER AT 16:10, PROVIDED LEAK LOCATION DETAILS, AND A CONTRACTOR WAS CONTACTED TO EXCAVATE THE LEAK LOCATION. PRESSURE CONTROL VALVE SET POINT WAS LOWERED BY 20% OF THE OPERATING PRESSURE AT THE TIME OF DISCOVERY (FROM 275 PSIG TO 225 PSIG). AREA MANAGER NOTIFIED LAHAZMAT TO REPORT THE LEAK AT 16:35 AND MADE ADDITIONAL INTERNAL NOTIFICATIONS. AT APPROXIMATELY 18:00, CONTRACTOR ARRIVED ONSITE, HAND EXCAVATED THE LEAK LOCATION, AND DISCOVERED A LEAKING MECHANICAL COUPLING. CONTRACTOR BACK-FILLED HOLE AND TECHNICIANS MONITORED AREA. THE LEAK COULD ONLY BE DETECTED BY MONITOR WITHIN INCHES OF THE GROUND AND WAS DETERMINED TO BE LOW GRADE. THE LEAK LOCATION WAS MONITORED UNTIL THE BLOW DOWN AND REPAIR OCCURRED ON 2-19-2020. LEAK STOPPED AFTER LINE WAS DEPRESSURIZED AT 10:45 ON 2-19-2020. WELD OVER WAS INSTALLED AND LINE RETURNED TO SERVICE AT APPROXIMATELY 18:00 ON 2-19-2020.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200019 | 33453 | 2020-03-12 16:30 | ORIGINAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 STATE ROUTE 56; BOX 20010 | OWENSBORO | KY | 42301 | 2020-02-17 11:54 | 2020 | CENTRAL | NO | 35.9051 | -97.0448 | 1271412 | 2020-02-17 12:46 | 1271569 | NATURAL GAS |  | 430 | 3343 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-02-17 15:45 | 2020-02-19 19:46 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-02-17 15:45 | VALVE CLOSURE |  | 2020-02-17 15:45 | 0 | 2020-02-17 11:54 | 2020-02-17 11:54 | ONSHORE | OK | 74832 | Not Within a Municipality | LINCOLN | SURVEY STATION NO. | 120/180506 | EDMUND-DRUMRIGHT 12" | LINE XD | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | OTHER | CREEK EXPOSURE |  |  | YES | [6 empty] | YES | UNCASED | UNNAMED CREEK | 1 | BELOW WATER, PIPE ON OR ABOVE BOTTOM | NO | [10 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | TAP FITTING(STOPPLE, THREAD-O-RING, WELD-O-LET, ETC.) | [38 empty] | 1946 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 282 |  | NO | NO |  |  | 0 | 0 | 5416 | 5416 | 697 | 697 | 232000 | 232000 | 0 | 0 | 0 | 0 |  | 1.62 | 238113 | 109702.820204831 | 238113 | 0 | 0 | 0 | 0 | NO |  |  |  | 446 | 11000 | 498 | 192.619(C) |  | 1967-06-27 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 93750 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | AIR PATROL |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS SMALL ENOUGH THAT IT WAS NOT DETECTABLE BY THE GAS CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [52 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | CREEK BANK EROSION EXPOSED A 1 INCH TAP AT THIS LOCATION. DEBRIS CAUGHT ON THE 1 INCH LINE AND CRACKED THE TAP VALVE. | NO | [306 empty] | ERIC GLAHN | PIPELINE COMPLIANCE ENGINEER | eric.glahn@southernstar.com | 2708524414 | 2708525016 | CRAIG THOMAS | craig.thomas@southernstar.com | 2708524435 | SHAWN PATTERSON | VP CHIEF OPERATIONS OFFICER | 2708524670 | shawn.patterson@southernstar.com | ON FEBRUARY 17, 2020 SOUTHERN STAR CENTRAL GAS PIPELINE (SSCGP) WAS NOTIFIED BY AIR LEAK PATROL OF A POSSIBLE LEAK AT A CREEK CROSSING ON A SSCGP PIPELINE. BY 11:54 AM SSCGP OPERATIONS WAS ON SITE AND VERIFIED THE LEAK WAS ON A COMPANY PIPELINE, LINE XD. THE LEAK ITSELF WAS IDENTIFIED AS A 1 INCH TAP VALVE THAT HAD BEEN EXPOSED DUE TO BANK EROSION AND CRACKED DUE TO DEBRIS BUILD UP. THE LEAK ITSELF WAS MINOR BUT DUE TO THE REMOTE LOCATION THE NRC WAS NOTIFIED AT 12:46 AM BECAUSE THE ESTIMATED REPAIR WOULD BE IN EXCESS OF $50,000. THE FOLLOW UP CALL TO THE NRC WAS MADE ON 2/19/2020 AT 10:53 AM TO CONFIRM THERE WERE NO FIRE OR INJURIES AS A RESULT OF THIS LEAK. THE SEGMENT OF PIPELINE WAS ISOLATED BY 3:45 PM ON 2/17/2020 AND ALLOWED TO BLOW DOWN. THE 1 INCH LINE FOR THIS TAP WAS NO LONGER IN USE SO IT WAS DETERMINED THAT THE 1 INCH LINE COULD BE ABANDONED AND A PERMANENT REPAIR SLEEVE COULD BE INSTALLED. THE REPAIR SLEEVE WAS INSTALLED AND LINE XD WAS PLACED BACK IN SERVICE BY 7:46 PM ON 2/19/2020.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200020 | 33454 | 2020-03-12 16:34 | ORIGINAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 STATE ROUTE 56; BOX 20010 | OWENSBORO | KY | 42301 | 2020-02-14 09:49 | 2020 | CENTRAL | NO | 38.1728 | -95.3002 | 1271229 | 2020-02-14 10:32 | 1271254 | NATURAL GAS |  | 7164 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | RELIEF VALVE WAS ISOLATED AND OVERHAULED |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-02-14 00:26 | 2020-02-14 00:26 | ONSHORE | KS | 66091 | WELDA | ANDERSON | SURVEY STATION NO. | 100/0 | WELDA COMPRESSOR STATION | LINE DS | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | UNKNOWN | 1996 | CARBON STEEL |  | OTHER | [8 empty] | PRESSURE RELIEF VALVE MALFUNCTION | CLASS 1 LOCATION | NO |  | 363 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 11606 | 11606 | 500 | 500 | 0 | 0 | 0 | 0 |  | 1.62 | 12106 | 12261.9803850174 | 12106 | 0 | 0 | 0 | 0 | NO |  |  |  | 585 | 142000 | 690 | 192.619(A)(2) |  | 1970-10-29 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 48623 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE WELDA OPERATOR IMMEDIATELY NOTIFIED GAS CONTROL OF POSSIBLE RELIEF VALVE ACTIVATION. GAS CONTROL CONFIRMED A PRESSURE DROP. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | DUE TO DEBRIS IN THE PILOT, THE RELIEF VALVE MALFUNCTIONED | [147 empty] | YES | [13 empty] | ERIC GLAHN | PIPELINE COMPLIANCE ENGINEER | eric.glahn@southernstar.com | 2708524414 | 2708525016 | CRAIG THOMAS | craig.thomas@southernstar.com | 2708524435 | SHAWN PATTERSON | VP CHIEF OPERATIONS OFFICER | 2708524670 | shawn.patterson@southernstar.com | ON 2/14/2020 AT 12:26 AM LOCAL TIME, SOUTHERN STAR CENTRAL GAS PIPELINE (SSCGP) GAS CONTROL RECEIVED A CALL FROM THE OPERATOR AT THE WELDA COMPRESSOR STATION OF A POSSIBLE RELIEF VALVE ACTIVATION. GAS CONTROL CONFIRMED A PRESSURE DROP BUT THERE WAS NO MAOP EXCEEDANCE. GAS CONTROL RECEIVED ANOTHER CALL FROM THE ANDERSON COUNTY SHERIFF'S DEPARTMENT AT 12:31 AM DUE TO THE SOUND OF HISSING GAS. AT 12:34 AM THE WELDA OPERATOR IDENTIFIED THE LOCATION OF THE ACTIVATED RELIEF VALVE. SINCE THIS WAS NOT AN OVERPRESSURE EVENT, THE RELIEF VALVE WAS ISOLATED BY 12:48 AM. INITIAL GAS LOSS CALCULATIONS INDICATED THAT THIS WAS NOT A REPORTABLE EVENT. THE RELIEF VALVE WAS REMOVED, REBUILT AND PLACED BACK IN SERVICE AT APPROXIMATELY 10:00 AM ON 2/14/2020. THE GAS LOSS WAS RECALCULATED AT 9:49 AM AND IT WAS DETERMINED THAT ACTUAL GAS LOSS WAS APPROXIMATELY 7.1 MMCF. THE CALL TO THE NRC WAS PLACED AT 10:32 AM TO MAKE THE NOTIFICATION OF THE GAS LOSS AT THE RELIEF VALVE. THE NRC WAS ALSO NOTIFIED THAT THERE WERE NO INJURIES, FIRE OR PROPERTY DAMAGE AS A RESULT OF THIS RELEASE. THE FOLLOW UP CALL TO THE NRC WAS MADE ON 2/14/2020 AT 2:34 PM TO CONFIRM THAT THE EVENT WAS OVER AND THERE WERE NO INJURIES OR PROPERTY DAMAGE. THE TEMPERATURE AT THE TIME OF THE RELIEF VALVE MALFUNCTION WAS 2 DEGREES F. WHEN THE RELIEF VALVE WAS REMOVED FOR REBUILD, DEBRIS WAS PRESENT IN THE PILOT. SSCGP DETERMINED THAT DEBRIS IN THE PILOT CAUSED THE RELIEF VALVE TO MALFUNCTION.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200021 | 33480 | 2020-03-13 15:37 | SUPPLEMENTAL FINAL | 32163 | ROCKIES EXPRESS PIPELINE LLC | 370 VAN GORDON ST | LAKEWOOD | CO | 80228 | 2020-02-27 17:21 | 2020 | EASTERN | NO | 39.714 | -82.8717 | 1272273 | 2020-02-27 17:21 | 1272373 | NATURAL GAS |  | 5748.15 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | ICE BUILDUP CAUSED INSTRUMENT AIR TO OPEN VALVE AND ALLOW UNINTENTIONAL VENTING. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-02-27 06:20 | 2020-02-27 06:20 | ONSHORE | OH | 43103 | Not Within a Municipality | PICKAWAY | NOT APPLICABLE |  | COLUMBUS COMPRESSOR STATION | COLUMBUS COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2016 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | WHEN OPERATIONS PERSONNEL ARRIVED TO THE COLUMBUS COMPRESSOR STATION A RELEASE OF GAS WAS DISCOVERED ESTIMATED AT 6483 MCF. A REPAIR WAS MADE (DE-ICED). DUE TO DROPPING TEMPERATURE, IT IS SUSPECTED THAT ICE BUILDUP INSIDE A PNEUMATIC SOLENOID HAD ALLOWED INSTRUMENT AIR TO SLOWLY PRESSURIZE THE ACTUATOR AND SUBSEQUENTLY OPEN THE VALVE IN TURN ALLOWING THE COMPRESSOR TO BE PRESSURIZED WHILE STILL VENTING AT ROUGHLY 730 PSI. | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 10059 | 10059 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.75 | 10059 | 10428.6220472441 | 10059 | 0 | 0 | 0 | 0 | NO |  |  |  | 730 | 0 | 1480 | OTHER | 0.8 DESIGN FACTOR. | 2016-07-21 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 3 | NO | [5 empty] | YES | IN STATION PIPING. | YES |  |  |  |  | YES | IN STATION PIPING. | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS SPECIFIC COMPONENT IS NOT MONITORED BY GAS CONTROL. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | OTHER | ICE BUILDUP CAUSED INSTRUMENT AIR TO OPEN VALVE AND ALLOW UNINTENTIONAL VENTING. | [20 empty] | YES | WEATHER REALTED - ICE BUILDUP. | [123 empty] | YES | [24 empty] | YES | [12 empty] | LAURA ARELLANO-BRIOT | SR. COMPLIANCE COORDINATOR | laura.arellano-briot@tallgrassenergylp.com | 3072424493 |  | LAURA ARELLANO-BRIOT | laura.arellano-briot@tallgrassenergylp.com | 3072424493 | LAURA ARELLANO-BRIOT | SR. COMPLIANCE COORDINATOR | 3072424493 | laura.arellano-briot@tallgrassenergylp.com | WHEN OPERATIONS PERSONNEL ARRIVED TO THE COLUMBUS COMPRESSOR STATION A RELEASE OF GAS WAS DISCOVERED THAT WAS ESTIMATED TO BE 6483 MCF. A REPAIR WAS MADE (DE-ICED). DUE TO DROPPING TEMPERATURE, IT IS SUSPECTED THAT ICE BUILDUP INSIDE A PNEUMATIC SOLENOID HAD ALLOWED INSTRUMENT AIR TO SLOWLY PRESSURIZE THE ACTUATOR AND SUBSEQUENTLY OPEN THE VALVE IN TURN ALLOWING THE COMPRESSOR TO BE PRESSURIZED WHILE STILL VENTING AT ROUGHLY 730 PSI. THE FINAL DETERMINATION OF THE GAS VOLUME RELEASED IS 5748.15 MCF.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200022 | 33807 | 2020-03-16 16:09 | SUPPLEMENTAL FINAL | 9171 | MARKWEST JAVELINA PIPELINE COMPANY, L.L.C. | 1515 ARAPAHOE STREET TOWER 1, SUITE 1600 | DENVER | CO | 80202 | 2020-02-17 10:09 | 2020 | CENTRAL | NO | 27.803 | -97.4305 | 1271395 | 2020-02-17 09:21 |  | OTHER GAS | REFINERY OFF GAS (RAW GAS) | 2598 | 161 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-02-17 10:03 | 2020-04-25 11:00 |  | YES | OPERATOR | 2020-02-17 08:37 | YES | 2020-02-17 08:35 | OTHER | ONCE WE ISOLATED THE GAS TO THE PIPELINE THE FIRED BURNED OUT | 2280 | YES | VALVE CLOSURE |  | 2020-02-17 09:55 | VALVE CLOSURE |  | 2020-02-17 10:02 | 10 | 2020-02-17 10:09 | 2020-02-17 08:45 | ONSHORE | TX | 78408 | CORPUS CHRISTI | NUECES | MILEPOST | I37 EXIT 1E | JAVELINA | RG-800 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 | NO | 0.25 | 35000 | GRADE B | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | EPOXY |  | NO | [26 empty] | 1990 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 74.5 | 3.7 |  | CLASS 3 LOCATION | NO |  | 226 |  | NO | NO |  |  | 320000 | 320000 | 402 | 402 | 6482 | 6482 | 260000 | 260000 | 75000 | 75000 | 2650000 | 2650000 | 7.D - PIPELINE CLEANING, ILI ATTEMPTS, HYDRO-TESTING | 2.495 | 3311884 | 1523986.92081664 | 3311884 | 0 | 0 | 0 | 1 | NO |  |  |  | 55 | 11100 | 240 | 192.619(A)(2) |  | 1990-08-21 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | YES | MANUAL | MANUAL | 1062 | NO |  |  | YES | YES |  | YES | LINE WAS DESIGNED TO RUN MAINTENANCE PIGS FROM THE 20" TO A 24", NOT SMART TOOLS. THERE ARE TIGHT BACK TO BACK 90'S AS WELL AS NO RECEIVER ON THE 20" (RG-800). | YES | YES | YES | YES |  | YES | TIGHT RADIUS BENDS | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [5 empty] | YES | MARKWEST IDENTIFIED THAT ADDITIONAL ALARMS OR PRESSURE INDICATORS WOULD HELP IN IDENTIFYING PRESSURE INCREASES OR DECREASES AT OFF-SITES. | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  | YES | DIFFERENTIAL AERATION PRODUCED BY THE DEPOSITS WHICH COLLECTED ON THE BOTTOM OF THE PIPE. THE COLLECTION OF THESE DEPOSITS WAS LIKELY EXACERBATED BY THE LOW VOLUME AND/OR FLOW RATES. |  | YES |  |  | YES | [5 empty] | NO | NO | NO | NO | [168 empty] | NO | [63 empty] | YES | 2019 | 172 | NO | [13 empty] | NO | [20 empty] | YES | [42 empty] | TONY MINUTILLO | PIPELINE COMPLIANCE SUPERVISOR | tminutillo@mplx.com | 303-489-3275 |  | KEVIN THOMPSON | krthompson@mplx.com | (361) 289-4755 | DENNIS THEBEAU | ENGINEERING MGR | (303) 531-9089 | dthebeau@mplx.com | A FIRE IGNITED AT THE INTERSECTION OF BUDDY LAWRENCE AND I37 FRONTAGE ROAD AT MILE MARKER 1E. WITH THE AMOUNT OF PIPELINES IN THE AREA AND CONGESTION IT WAS DIFFICULT AT FIRST TO IDENTIFY WHO'S PIPELINE WAS LEAKING. WITH SUCH LOW PRESSURES ON OUR RG PIPELINES IT CAN BE DIFFICULT TO SEE DRASTIC PRESSURE INTERRUPTIONS. IN THE PROCESS OF ISOLATION WE WERE ABLE TO 100% COMMIT TO THE LEAK BEING OUR PIPELINE. IN THE INVESTIGATION THE CAUSE OF THE INCIDENT HAS BEEN DETERMINED TO BE INTERNAL CORROSION. UPON A VISUAL EXAMINATION, LOCALIZED PITTING WAS DISCOVERED THAT HAS BEEN ATTRIBUTED TO DIFFERENTIAL AERATION PRODUCED BY THE DEPOSITS WHICH COLLECTED ON THE BOTTOM OF THE PIPELINE. THE COLLECTION OF THESE DEPOSITS LIKELY EXACERBATED BY THE LOW VOLUME AND/OR FLOW RATES. THE ENTIRE EAST SIDE SYSTEM OF THE SYSTEM INCLUDING THE RG-800 HAS BEEN PUT THROUGH A RIGOROUS CLEANING REGIME, AND PRESSURE TESTED TO SHOW THE INTEGRITY OF THE LINE TO 433 PSIG. THIS WAS ONLY DONE AFTER MULTIPLE FAILED ATTEMPTS TO SMART TOOL THE LINE, DUE TO THE LINE NOT BEING PEGGABLE ALTHOUGH WE DID SPEND COUNTLESS RESOURCES ON TRYING TO MAKE THE SYSTEM SMART PIGGABLE. THIS PIPELINE CONTAINS MULTIPLE TIGHT BENDS THAT DID NOT ALLOW THE PASSING OF THE SMART TOOLS. INVESTIGATION HAS NOT SHOWN ANY INDICATION OF GENERAL CORROSION ALONG THE ENTIRE SYSTEM, BUT SHOWED TO BE LOCALIZED TO THE AREA THAT FAILED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200023 | 33723 | 2020-03-18 12:39 | SUPPLEMENTAL FINAL | 4900 | KINDER MORGAN TEJAS PIPELINE | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2020-02-18 03:35 | 2020 | CENTRAL | NO | 28.6779 | -96.9382 | 1271457 | 2020-02-18 04:24 | 1271623 | NATURAL GAS |  | 22240 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-02-18 03:35 | 2020-04-21 13:45 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-02-18 03:30 | NO | [5 empty] | VALVE CLOSURE |  | 2020-02-18 03:35 | VALVE CLOSURE |  | 2020-02-18 03:35 | 0 | 2020-02-18 02:54 | 2020-02-18 03:30 | ONSHORE | TX | 77951 | BLOOMINGTON | VICTORIA | SURVEY STATION NO. | 7876 | DUPONT LATERAL | INDEX 127-9 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 8.625 |  | 0.188 | 46000 | API 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | YOUNGSTOWN | COAL TAR |  | UNKNOWN | [26 empty] | 1950 | 1950 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 61 | 15 |  | CLASS 1 LOCATION | NO |  | 168 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 45370 | 45370 | 50000 | 50000 | 1500 | 1500 | 0 | 0 |  | 2.04 | 96870 | 70676.9980294961 | 96870 | 0 | 0 | 0 | 0 | NO |  |  |  | 744 | 3401 | 795 | 192.619(A)(1) |  | 1950-03-16 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 18321 | NO |  |  |  | YES |  | YES | NO PIG LAUNCHER AND RECEIVER | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT OCCURRED INDEPENDENT OF THE CONTROL ROOM. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) |  | YES | [13 empty] | YES | LACK OF FUSION | [7 empty] | YES | [7 empty] | UNKNOWN | [54 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [44 empty] | YES | [18 empty] | SHELLEY DIETZ | PIPELINE ENGINEER | shelley_dietz@kindermorgan.com | 7134204417 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | AT 2:54AM ON FEBRUARY 18, 2020, KINDER MORGAN TEJAS PIPELINE COMPANY, LLC (TEJAS) GAS CONTROL RECEIVED A PHONE CALL FROM THE INVISTA PLANT IN BLOOMINGTON, TEXAS NOTIFYING TEJAS OF A GAS RELEASE COMING FROM THE TEJAS RIGHT OF WAY. TEJAS EMPLOYEES ARRIVED ON SITE AT 3:30AM AND AT 3:35AM CONFIRMED DISCOVERY OF A REPORTABLE RELEASE OF NATURAL GAS. AT 3:35, TEJAS ISOLATED THE PIPE SEGMENT BY CLOSING THE UPSTREAM AND DOWNSTREAM ISOLATION VALVES. TO REPAIR THE PIPELINE, THE RUPTURED SEGMENT OF PIPE WAS CUT OUT, REPLACED, AND HYDROTESTED. THE LINE WAS RETURNED TO SERVICE AT 13:45 ON APRIL 21, 2020. THE FAILED PIPE SEGMENT WAS CUT OUT AND SENT TO A KINDER MORGAN DESIGNATED METALLURGICAL LABORATORY FOR TESTING. THE METALLURGICAL REPORT REVEALED THAT THE GAS RELEASE WAS CAUSED BY A RUPTURE THAT ORIGINATED IN THE ERW LONG SEAM. AREAS OF LACK OF FUSION IN THE WELD BOND LINE DECREASED THE WELD STRENGTH AND CAUSED THE FAILURE. THE LACK OF FUSION OCCURRED DURING THE ORIGINAL MANUFACTURING OF THE ERW PIPE.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20200025 | 33534 | 2020-03-25 13:02 | SUPPLEMENTAL FINAL | 39352 | GENESIS OFFSHORE HOLDINGS, LLC | 919 MILAM STREET SUITE 2100 | HOUSTON | TX | 77002 | 2020-02-28 07:00 | 2020 | CENTRAL | YES | 28.259 | -94.013 | 1274191 | 2020-03-25 11:10 | 1274270 | NATURAL GAS |  | 2860 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-03-01 09:00 | 2020-03-18 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-03-01 09:00 | VALVE CLOSURE |  | 2020-03-01 12:00 | 0 | 2020-02-28 07:00 | 2020-02-28 07:00 | OFFSHORE | [6 empty] | HIOS | HI582 TO HI 264 | [20 empty] | 203 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | HIGH ISLAND | 470 | BELOW WATER, PIPE ON OR ABOVE SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1978 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 1138 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 5434 | 5434 | 778000 | 778000 | 0 | 0 | 0 | 0 |  | 1.9 | 783434 | 362756.20349653 | 783434 | 0 | 0 | 0 | 0 | NO |  |  |  | 875 | 1200 | 1440 | 192.619(A)(1) |  | 1978-07-06 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 283574 | NO | YES | [6 empty] | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | YES | YES | YES | NO | NO | AIR PATROL |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK TOO LOW TO BE DETECTED BY SCADA. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [29 empty] | YES | [153 empty] | YES | [9 empty] | JORGE MORICE | PIPELINE COMPLIANCE SPECIALIST | jorge.morice@genlp.com | 713-725-1663 |  | NORMAN GIBSON | norman.gibson@genlp.com |  | JOHN JEWETT | MANAGER DOT COMPLIANCE AND SECURITY | 713-860-2605 | john.jewett@genlp.com | DURING A ROUTINE HELICOPTER FLYOVER ON FEBRUARY 22ND, A RELATIVELY LOW LEVEL OF GAS BUBBLES WERE SEEN NEAR THE HIGH ISLAND OFFSHORE SYSTEM (HIOS) 30" GAS PIPELINE IN THE HI-470 BLOCK. THE PERSONNEL DID NOT OBSERVE ANY SHEEN ON THE WATER. DIVERS ARRIVED ON LOCATION AND DISCOVERED A LEAK OF THE VALVE #1 GREASE FITTING AT A SUBSEA ASSEMBLY. PLANS WERE MADE TO REPLACE REMAINING GREASE FITTINGS ON THE SSTI ASSEMBLY TO PREVENT THEM FROM LEAKING AT A LATER DATE. ON MARCH 18, 2020 DIVERS COMPLETED THE REPLACEMENT OF FITTINGS, THE PIPELINE WAS RE-PRESSURED AND REMAINED WITHOUT ANY SIGNS OF LEAKAGE AFTERWARDS. UPON CLOSE INSPECTION OF THE LEAKING FITTING, IT WAS DETERMINED THAT THE FITTING'S INTERNAL SEAL PROVIDED BY THE CHECK BALL WAS BROKEN DUE TO CORROSION INSIDE THE FITTING. SUPPLEMENTAL (03/30/20) - 48 HOUR NRC CONFIRMATION RECORDED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200026 | 33515 | 2020-03-26 08:16 | ORIGINAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2020-03-18 19:06 | 2020 | CENTRAL | YES | 32.144 | -94.2666 | 1273779 | 2020-03-18 20:32 | 1273816 | NATURAL GAS |  | 13532 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | ONLY THE UNIT (T6) WAS TAKEN OFFLINE. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-03-18 19:06 | 2020-03-18 19:56 | ONSHORE | TX | 75633 | CARTHAGE | PANOLA | MILEPOST | 0 | CARTHAGE JUNCTION COMPRESSOR STATION | INDEX 816-1 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 13 | NO | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2007 | 2007 | CARBON STEEL |  | OTHER | [8 empty] | TURBINE NO. 6 BYPASS VALVE FAILED OPEN. | CLASS 1 LOCATION | NO |  | 115 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 24628 | 24628 | 2500 | 2500 | 200 | 200 | 0 | 0 |  | 1.82 | 27328 | 26772.3371237134 | 27328 | 0 | 0 | 0 | 0 | NO |  |  |  | 694 | 600000 | 1202 | 192.619(A)(1) |  | 2012-03-19 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  |  | NO | [5 empty] | YES | COMPRESSOR STATION | YES |  |  |  |  | YES | COMPRESSOR STATION | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | OTHER | POWER SUPPLY WAS BAD | [20 empty] | YES | POWER SUPPLY WAS BAD | [161 empty] | SHANNON M MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 270.688.6357 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 270.688.6497 | tina.baker@bwpipelines.com | GULF SOUTH GAS CONTROL NOTICED A LOSS OF COMMUNICATION ALARM AND SOME UNUSUAL PRESSURE DIFFERENCES BETWEEN THE RUNNING UNITS AT THE CARTHAGE JUNCTION COMPRESSOR STATION ON 03/18/2020 AT 19:06. GAS CONTROL CONTACTED LOCAL OPERATIONS PERSONNEL TO INVESTIGATE. UPON ARRIVAL, AT 19:56, OPERATIONS PERSONNEL DISCOVERED THE NO. 6 TURBINE (T6) RECYCLE VALVE WAS OPEN AND VENTING GAS TO THE 4" BLOW DOWN. HE MANUALLY CLOSED THE VALVE WHICH STOPPED THE BLOW DOWN. FROM THE TIME GAS CONTROL RECEIVED THE ALARMS AND OPERATIONS PERSONNEL WERE ABLE TO RESPOND, ASSESS AND CORRECT THE ISSUE, T6 VENTED GAS FOR APPROXIMATELY 1 HOUR AT 694 PSIG. IT WAS DETERMINED THAT THE POWER SUPPLY FOR T6 WAS BAD. THIS POWER LOSS CAUSED BOTH THE LOSS OF COMMUNICATION AND THE RECYCLE VALVE TO REMAIN OPEN. POWER SUPPLY WAS REPLACED AND ISSUE WAS RESOLVED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200027 | 33861 | 2020-04-02 19:57 | SUPPLEMENTAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2020-03-05 03:20 | 2020 | EASTERN | NO | 32.7875 | -84.2545 | 1272740 | 2020-03-05 04:24 | 1272876 | NATURAL GAS |  | 55527 | 911 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-03-05 04:13 | 2020-03-05 08:13 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-03-05 03:45 | NO | [11 empty] | 0 | 2020-03-05 03:17 | 2020-03-05 03:45 | ONSHORE | GA | 30286 | THOMASTON | UPSON | MILEPOST | 346.9 | THOMASTON COMPRESSOR STATION | 8" EMERGENCY RELIEF VALVE - 001, SOUTH MAIN | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2003 | 2002 | CARBON STEEL |  | OTHER | [8 empty] | GAS RELEASE THROUGH VENT STACK | CLASS 1 LOCATION | NO |  | 191 |  | NO | NO |  |  | 0 | 0 | 1567 | 1567 | 95506 | 95506 | 3000 | 3000 | 250 | 250 | 0 | 0 |  | 1.72 | 100323 | 101226.53692952 | 100323 | 0 | 0 | 0 | 0 | NO |  |  |  | 1076 | 0 | 1200 | 192.619(A)(1) |  | 1951-07-03 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE STATION WAS OFFLINE WITH NO CHANGES TO HORSEPOWER OR SETPOINTS BEING MADE | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | INCORRECT ASSESSMENT OF TIMEFRAME FOR REPAIR |  |  |  | YES | UNAWARENESS OF VALVE OPERATORS FAIL SAFE MODE | ROUTINE MAINTENANCE | NO | [136 empty] | YES |  |  | YES | [10 empty] | DANIEL GRANT | PIPELINE ENGINEER | daniel_grant@kindermorgan.com | 2545483437 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR - ENGINEERING | 7133699443 | jaime_hernandez@kindermorgan.com | AT 3:17 AM SOUTHERN NATURAL GAS COMPANY, L.L.C. (SNG) GAS CONTROL RECEIVED A PHONE CALL FROM THE PUBLIC REGARDING A LOUD NOISE COMING FROM A PIPELINE FACILITY. A SNG TECHNICIAN WAS CALLED OUT TO THE SITE AND ARRIVED AT 3:45 AM. UPON ARRIVAL THE TECHNICIAN MET WITH EMERGENCY RESPONDER PERSONNEL WHO PROCEEDED TO BLOCK THE ACCESS ROAD TO THE COMPRESSOR STATION. THE TECHNICIAN ATTEMPTED TO CLOSE THE EMERGENCY BLOWDOWN VALVE AND WAS UNABLE TO, SO THE DECISION WAS MADE TO ESD THE STATION, THUS ENDING THE GAS RELEASE. AN ERL (EMERGENCY RESPONSE LINE) CONFERENCE CALL WAS HELD AT 4:10 AM ABOUT THE EVENT. ON THE CALL IT WAS FORECASTED THAT THE GAS LOSS FROM THE EVENT WOULD EXCEED THE REPORTABLE THRESHOLD OF 3,000 MCF. AT THIS TIME (4:10 AM) SNG HAD CONFIRMED DISCOVERY OF THE INCIDENT. THE PILOT IN THE EMERGENCY BLOWDOWN VALVE WAS REPLACED. AFTER INVESTIGATING, IT WAS DETERMINED THAT THE PILOT ACTUATOR OF THE EMERGENCY BLOWDOWN VALVE HAD A LEAKING SEAL ON THE POWER GAS SIDE. IT IS BELIEVED THAT THE ESCAPING GAS FROM THE SEAL MADE ITS WAY TO THE VENT WHERE IT FROZE OVER THE EXHAUST PORT, PREVENTING THE LEAKING GAS FROM REACHING ATMOSPHERE. THE PRESSURE FROM THE LEAKING GAS CONTINUED TO BUILD, AND UPON REACHING 150 PSI THE VALVE OPERATOR ACTIVATED TO ITS "SAFE STATE" AS IT IS DESIGNED TO DO, AND IN THIS CONFIGURATION THE SAFE STATE HAS THE VALVE IN THE OPEN POSITION. THE VALVE OPERATOR'S SAFE STATE CONFIGURATION RESULTED IN THE EMERGENCY BLOWDOWN VALVE OPENING WITHOUT SNG'S COMMAND. BEFORE THE EVENT, SNG HAD IDENTIFIED THE VALVE OPERATOR AS LEAKING AND MADE PLANS TO ADDRESS THE LEAK, BUT DUE TO NOT BEING AWARE OF THIS OPERATOR'S FAIL SAFE MODE AN INCORRECT ASSESSMENT OF THE TIMEFRAME FOR REPAIR WAS MADE. AT THOMASTON COMPRESSOR STATION, SNG HAS MODIFIED ITS LEAK SURVEY WORK ORDERS ON ESD VENT VALVES WITH THIS TYPE OF OPERATOR SO THAT THE TECHNICIANS WHO COMPLETE THE WORK ORDER ARE INSTRUCTED TO PROMPTLY REPAIR ANY FOUND LEAK ON THE OPERATOR.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200028 | 33573 | 2020-04-06 11:01 | SUPPLEMENTAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2020-03-21 14:52 | 2020 | CENTRAL | YES | 32.3106 | -93.9672 | 1273980 | 2020-03-21 17:06 | 1274038 | NATURAL GAS |  | 1 | 2709 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-03-21 21:00 | 2020-03-25 15:00 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-03-21 21:00 | VALVE CLOSURE |  | 2020-03-21 20:30 | 0 | 2020-03-21 14:52 | 2020-03-21 16:30 | ONSHORE | LA | 71129 | KEITHVILLE | CADDO | MILEPOST | 77+2014 | SHARON CARTHAGE 20" NO. 1 | SHC 20-1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 42 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 20 |  | 0.25 | 52000 | API 5L | FLASH WELDED |  | AO SMITH | COAL TAR |  | UNKNOWN | [7 empty] | PIPE GIRTH WELD |  | NO | [16 empty] | 1949 | 1949 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 2 LOCATION | NO |  | 461 |  | NO | NO |  |  | 0 | 0 | 4930 | 4930 | 2 | 2 | 85000 | 85000 | 1500 | 1500 | 0 | 0 |  | 1.82 | 91432 | 41970.8560389282 | 91432 | 0 | 0 | 0 | 0 | NO |  |  |  | 690 | 165000 | 931 | 192.619(A)(1) |  | 1949-12-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 52800 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [8 empty] | YES | CONSTRUCTION-RELATED CAUSES WHICH RESULTED IN THE GIRTH WELD PIN HOLE LEAK | [13 empty] | YES | [5 empty] | YES | LEAK WAS CAUSED BY A PIN HOLE DEFECT IN GIRTH WELD. | 1219 | [54 empty] | YES | YES |  |  | YES |  |  | YES | 2017 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2010 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [21 empty] | 2017 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | 2010 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | [8 empty] | MAPPING | 2017 | FREE SWIMMING | 2010 | FREE SWIMMING |  | YES | 1967 | 1219 | NO | [13 empty] | NO | [63 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 270.688.6357 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 270.688.6497 | tina.baker@bwpipelines.com | AT APPROXIMATELY 6:15 PM ON SATURDAY, MARCH 21, 2020 A LANDOWNER NOTIFIED A LOCAL FIRE DEPARTMENT WHO, IN TURN, NOTIFIED TEXAS GAS' CONTROL ROOM OF A POTENTIAL NATURAL GAS LEAK ON THE SHARON CARTHAGE LINE, (SHC 20-1) NEAR BLOCK VALVE #5. THE CADDO PARISH FIRE DEPARTMENT STATED THAT THE LANDOWNER REPORTED BUBBLING FROM THE PIPELINE AND EXPRESSED CONCERN. THE CONTROL ROOM CONTACTED OPERATIONS PERSONNEL WHO TOOK IMMEDIATE STEPS TO ISOLATE THE LEAK AND CLOSE BOTH BLOCK VALVE #5 AND BLOCK VALVE #6. WITH THE LEAK ISOLATED, PLANS WERE MADE TO INVESTIGATE ON MONDAY, MARCH 23. UPON EXCAVATION, IT WAS DISCOVERED THAT THERE WAS A VERY SMALL PINHOLE LEAK ON THE OUTSIDE EDGE OF A GIRTH WELD. A LEAK CLAMP WAS INSTALLED AND THE LEAK WAS STOPPED. ON TUESDAY, MARCH 24, A DRESSER STYLE 220 SLEEVE WAS INSTALLED OVER THE LEAK. THIS REPORT IS REQUIRED BASED ON THE COST OF REPAIR EXCEEDING $50,000. THE RESPONSE TO QUESTION A7 IS SHOWN AS 1 MCF BUT THE ACTUAL ANSWER IS UNKNOWN; TEXAS GAS DOES NOT KNOW HOW LONG THIS LEAK OCCURRED NOR DO WE KNOW THE ORIFICE SIZE SINCE THE REPAIR HAS BEEN COMPLETED. 4-9-2020 UPDATE PER PHMSA'S REQUEST. A LACK OF FUSION DURING CONSTRUCTION RESULTED IN A PIN HOLE DEFECT LEAK IN THE GIRTH WELD. PHMSA ALSO ASKED FOR CONFIRMATION THAT THE OPID RESPONSIBLE FOR THIS INCIDENT IS 19270; THAT IS CORRECT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200029 | 33570 | 2020-04-08 11:11 | ORIGINAL FINAL | 39597 | VALLEY CROSSING PIPELINE, LLC | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2020-03-12 13:44 | 2020 | CENTRAL | YES | 27.7474 | -97.8141 | 1273364 | 2020-03-12 17:08 | 1273633 | NATURAL GAS |  | 3538 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-03-12 13:44 | 2020-03-12 16:45 |  | NO |  |  | NO | [11 empty] | 0 | 2020-03-12 13:44 | 2020-03-12 13:44 | ONSHORE | TX | 78380 | ROBSTOWN | NUECES | MILEPOST | 2.91 | AGUA DULCE COMPRESSOR STATION | AGUA-BROW | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2018 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | EMERGENCY SHUTDOWN OF COMPRESSOR STATION | CLASS 1 LOCATION | NO |  | 1386 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 6651 | 6651 | 1007 | 1007 | 0 | 0 | 0 | 0 |  | 1.88 | 7658 | 7357.63327232794 | 7658 | 0 | 0 | 0 | 0 | NO |  |  |  | 1572 | 0 | 1750 | 192.619(A)(1) |  | 2018-11-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  |  | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS DETERMINED THE CONTROLLERS ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. THE ESD WAS ACTIVATED BY A FAULTY FUSE IN THE ESD MASTER X22-16 PANEL AND THIS EVENT COULD NOT BE ASSOCIATED WITH THE ROLES AND RESPONSIBILITIES OF A CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | THE ESD WAS ACTIVATED BY A FAULTY FUSE IN THE ESD MASTER X22-16 PANEL. | [22 empty] | YES | THE ESD WAS ACTIVATED BY A FAULTY FUSE IN THE ESD MASTER X22-16 PANEL. | [148 empty] | YES | [12 empty] | MAYRA SALINAS | SENIOR ENGINEER | mayra.salinas@enbridge.com | 832-748-0908 |  | NATHAN ATANU | nathan.atanu@enbridge.com | 713-627-5008 | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: AT APPROXIMATELY 1:45 PM CDT ON MARCH 12, 2020 AN EMERGENCY SHUTDOWN (ESD) SYSTEM WAS ACTIVATED AT AGUA DULCE COMPRESSOR STATION ON THE VALLEY CROSSING PIPELINE (VCP) SYSTEM IN NUECES COUNTY, TEXAS. VCP COMPLETED THE REPORT TO THE NATIONAL RESPONSE CENTER AT APPROXIMATELY 5:08 PM CDT ONCE IT WAS DETERMINED THE GAS VOLUME EXCEEDED 3 MMSCF. THE ESD WAS ACTIVATED BY A FAULTY FUSE IN THE ESD MASTER X22-16 PANEL. TETLP'S INVESTIGATION DETERMINED THAT THE ESD WAS FUNCTIONING AS DESIGNED AT THE TIME OF THE ESD. AS PART OF THE MITIGATIVE PLAN, THE FAULTY FUSE WAS REPLACED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200030 | 33740 | 2020-04-10 12:52 | SUPPLEMENTAL FINAL | 2620 | COLUMBIA GULF TRANSMISSION, LLC | 700 LOUISIANA ST. SUITE 700 | HOUSTON | TX | 77002 | 2020-03-14 13:40 | 2020 | CENTRAL | NO | 32.4106 | -91.4874 | 1273519 | 2020-03-14 17:16 | 1273598 | NATURAL GAS |  | 7313 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | THE INCIDENT INVOLVED ONLY A SINGLE UNIT BLOW DOWN. |  |  |  | YES | OPERATOR | 2020-03-14 21:06 | NO | [11 empty] | 0 | 2020-03-14 13:02 | 2020-03-14 13:38 | ONSHORE | LA | 71232-6405 | Not Within a Municipality | RICHLAND | NOT APPLICABLE |  | DELHI COMPRESSOR STATION | UNIT 811 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2006 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | UNIT 811 FAULTED AND WAS SHUTDOWN DUE TO A PROGRAMMABLE LOGIC CONTROLLER INPUT/OUTPUT CARD PROGRAM FAILURE. THIS RESULTED IN THE UNIT SUCTION AND DISCHARGE VALVES FAILING TO CLOSE, RESULTING IN AN UNINTENDED RELEASE OF NATURAL GAS INTO ATMOSPHERE. | CLASS 1 LOCATION | NO |  | 152 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 12725 | 12725 | 0 | 0 | 0 | 0 | 1000 | 1000 | THE FAULT OCCURRED BECAUSE OF AN I/O CARD ERROR; REPLACED CARD. | 1.74 | 13725 | 13651.61168867 | 13725 | 0 | 0 | 0 | 0 | NO |  |  |  | 725 | 278061 | 1007 | 192.619(A)(2) |  | 2006-09-02 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM PERSONNEL WERE NOT INPUTTING ANY OPERATIONAL MODE CHANGES TO THE PIPELINE SYSTEM TO BE CONSIDERED AS A CONTRIBUTING FACTOR THAT LED TO THIS INCIDENT. (PLC I/O CARD FAILURE WAS IDENTIFIED AS PROBABLE CAUSE) | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | YES | [33 empty] | YES | I/O CARD FAILURE | [148 empty] | YES | [12 empty] | BENSON HUNLEY | REGULATORY COMPLIANCE SPECIALIST | ben_hunley@tcenergy.com | (304) 539-9311 |  |  |  |  | PAUL SHAFFER | MANAGER US REGIONAL COMPLIANCE EAST | (304) 550-4866 | paul_shaffer@tcenergy.com | ON MARCH 14, 2020, AN ALARM WAS ACKNOWLEDGED BY THE US NATURAL GAS CONTROL, EAST TEAM, SUBJECT TO AN EMERGENCY SHUTDOWN (ESD) AT DELHI COMPRESSOR STATION (CS) UNIT 811 FAULT SIGNAL. COLUMBIA GULF TRANSMISSION, LLC (COLUMBIA) OPERATES AND MAINTAINS DELHI CS WHICH IS CLASSIFIED AS A TRANSMISSION CS, IS LOCATED IN RICHLAND PARISH, LOUISIANA AND NEAR THE CITY OF DELHI. AFTER RECEIVING THE NOTIFICATION FROM COLUMBIA MONITORING CENTER, CS PERSONNEL RESPONDED TO THIS ESD EVENT AT DELHI CS AND ADDRESSED THE UNINTENDED RELEASE OF NATURAL GAS (MATERIAL) THAT WAS VENTING INTO ATMOSPHERE FROM THE BLOW DOWN DISCHARGE STACKS. THE CS PERSONNEL INSPECTED AND SECURED THE AREA TO ENSURE THAT IT WAS SAFE TO OPERATE DISCHARGE VALVES BEFORE MANUALLY CLOSING THEM. PRELIMINARY INVESTIGATION IDENTIFIED THE PROBABLE CAUSE THAT LED TO THIS UNINTENDED RELEASE AT UNIT 811 WAS DUE TO A FAULT SIGNAL ISSUED BY THE PROGRAMMABLE LOGIC CONTROLLER (PLC) AT THE INPUT/OUTPUT (I/O) BLOCK. THE ISSUED COMMAND INITIATED THE ACTIVATION OF THE BLOW DOWN VALVE TO OPEN (AS IT WAS DESIGNED TO) HOWEVER, THE SEQUENCING HAD FAILED TO CLOSE THESE VALVES TO STOP THE FLOW AND REMAINED OPEN FOR APPROXIMATELY 38 MINUTES. THE FAULTY PLC I/O CARD AS INDICATED AT THE UNIT CONTROL PANEL WAS REPLACED. ALL ALARMS WERE CLEARED AT THE PLC CONTROL PANEL, REQUIRED FUNCTIONAL TESTS WERE CONDUCTED WITH NO NEW ERRORS GENERATED (TO ENSURE NORMAL OPERATION OF THE UNIT), THEN THE UNIT WAS RETURNED BACK TO SERVICE. ROUTINE SAFETY CHECKS WERE CONDUCTED WHERE THE UNIT WAS MONITORED FOR A WHILE, VERIFIED THAT ALL SYSTEMS ARE RUNNING IN NORMAL MODE WITH NO NEW ERRORS WERE GENERATED THEREAFTER. A CALCULATED VOLUME OF UNINTENDED RELEASED MATERIAL WAS 7,313 MCF INTO ATMOSPHERE WHERE THE RELEASED MATERIAL DID NEITHER IGNITE NOR CAUSE ANY DAMAGE TO ANY OF THE CS DEVICES.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200031 | 33704 | 2020-04-15 11:36 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 STATE ROUTE 56; BOX 20010 | OWENSBORO | KY | 42301 | 2020-03-20 22:11 | 2020 | MOUNTAIN | YES | 40.7438 | -104.217 | 1273946 | 2020-03-20 22:47 | 1273996 | NATURAL GAS |  | 3924 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | RELIEF VALVE WAS ISOLATED, INSPECTED AND RESET |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-03-20 20:02 | 2020-03-20 21:33 | ONSHORE | CO | 80611 | Not Within a Municipality | WELD | SURVEY STATION NO. | 120/8 | NOBLE KEOTA INTERCONNECT | W-040 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 2015 | 2014 | CARBON STEEL |  | OTHER | [8 empty] | PRESSURE RELIEF VALVE MALFUNCTION | CLASS 1 LOCATION | NO |  | 428 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 6357 | 6357 | 500 | 500 | 0 | 0 | 0 | 0 |  | 1.62 | 6857 | 6820.10374459746 | 6857 | 0 | 0 | 0 | 0 | NO |  |  |  | 954 | 20438 | 960 | 192.619(A)(2) |  | 2016-05-19 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE FLUCTUATIONS DID NOT EXCEED OR DROP BELOW ALARM LIMITS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | RELIEF VALVE CALIBRATION | [147 empty] | YES | [13 empty] | ERIC GLAHN | PIPELINE COMPLIANCE ENGINEER | eric.glahn@southernstar.com | 2708524414 | 2708525016 | CRAIG THOMAS | craig.thomas@southernstar.com | 2708524435 | SHAWN PATTERSON | VP CHIEF OPERATIONS OFFICER | 2708524670 | shawn.patterson@southernstar.com | ON 3/20/2020 AT 8:02 PM MDT, SOUTHERN STAR CENTRAL GAS PIPELINE (SSCGP) GAS CONTROL RECEIVED A CALL FROM A NOBLE KEOTA EMPLOYEE ABOUT NOISE COMING FROM THE INTERCONNECT METER FACILITY. SSCGP EMPLOYEE ARRIVED ON SITE AT 9:33 PM AND CONFIRMED THE RELIEF VALVE WAS VENTING. AFTER CONFIRMING THERE WAS NO OVERPRESSURE EVENT THE RELIEF VALVE WAS ISOLATED AT 9:42 PM. THE RELIEF VALVE WAS INSPECTED AND TESTED, IT WAS FOUND THAT THE SET POINT HAD DRIFTED TO 954 PSIG. THE TEMPERATURE AT THE TIME OF THE RELEASE WAS 16 DEGREES F. THE SET POINT WAS ADJUSTED BACK TO 988 PSIG. GAS LOSS WAS CALCULATED AT 10:11 PM AT 3.9 MMCF. THE NRC WAS NOTIFIED AT 10:47 PM. THE RELIEF VALVE WAS PLACED BACK IN SERVICE BY 11:00 PM. IN RESPONSE TO QUESTIONS SUBMITTED BY PHMSA, THE FOLLOWING RESPONSES ARE INCLUDED IN THIS SUPPLEMENTAL REPORT: Q: DID DEBRIS CONTRIBUTE TO THE FAILURE? A: WHEN THE PRESSURE RELIEF VALVE (PRV) WAS INSPECTED AFTER THE RELEASE NO DEBRIS WAS FOUND INSIDE OF THE PRV. THE AS FOUND SET POINT MATCHED THE PRESSURE ACHIEVED (954 PSI) SO THE PRV RELEASED AS SET. Q: HAS THE SET POINT DRIFTED BEFORE? A: THIS PRV RECEIVED ITS LAST ANNUAL INSPECTION ON 8/27/2019 AND THE AS FOUND SET POINT WAS 986 PSI. THE SET POINT WAS READJUSTED TO 988 AT THAT TIME. AT THE TIME, THE 2 PSI DRIFT WAS NOT CONSIDERED ENOUGH FOR CONCERN. Q: WHAT PREVENTATIVE MEASURES ARE BEING TAKEN TO PREVENT THIS IN THE FUTURE? A: THE PRV AT THIS RECEIPT POINT IS SPRING CONTROLLED. THROUGH OUR RESEARCH OF MANUFACTURE INFORMATION AND DISCUSSION WITH OPERATIONS, THE SPRING CONTROLLED PRVS SEEM TO BE MORE SUBJECT TO DRIFTING OF SET POINT AND RESEATING PRESSURES DURING RAPID PRESSURE FLUCTUATIONS AND LOW TEMPERATURES. IN THIS CASE THE VALVE DID NOT RESEAT UNTIL ALL PRESSURE WAS RELIEVED WHEN IT WAS ISOLATED. WE ARE SCOPING A PROJECT TO REPLACE THIS SPRING CONTROLLED PRV WITH A PILOT CONTROLLED PRV. WE ARE LOOKING AT ALL OF OUR RECEIPT POINTS WITH SIMILAR CONFIGURATIONS AND PRIORITIZING REPLACEMENT PROJECTS FOR THOSE ALSO.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200032 | 33604 | 2020-04-15 15:26 | SUPPLEMENTAL FINAL | 31994 | PANTHER OPERATING COMPANY, LLC | THIRD COAST MIDSTREAM, LLC PO BOX 1227 | HOUSTON | TX | 77251 | 2019-08-15 15:45 | 2019 | CENTRAL | NO | 27.9641 | -94.3889 | 1255308 | 2019-08-15 20:08 | 1268214 | NATURAL GAS |  | 5000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | THE LEAK WAS MINOR AND ALLOWED A PLIDCO FULL ENCIRCLEMENT CLAMP TO BE APPLIED. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2019-08-15 15:45 | 2019-08-15 17:00 | OFFSHORE | [6 empty] | HI 563 | 24" | [20 empty] | 210 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | HI | 563 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PLATFORM, INCLUDING PLATFORM-MOUNTED EQUIPMENT AND PIPING | PIPE | PIPE BODY | 24 | NO | 0.5 | 52000 | UNKNOWN | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | EPOXY |  | YES | [26 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 628 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 6250 | 6250 | 130000 | 132645.281677626 | 50000 | 51017.4160298561 | 4025 | 4106.90199040341 | CONSULTING FEES AND TAXES | 1.25 | 190275 | 92670.8596989953 | 194019.599697885 | 0 | 0 | 0 | 0 | NO |  |  |  | 700 | 2 | 1440 | 192.619(A)(1) |  | 1975-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 79200 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER WAS NOT INVOLVED IN THE INCIDENT CAUSE, NOR IDENTIFICATION. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  |  | YES | [7 empty] | YES |  |  |  | NO | [11 empty] | YES | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KEVIN STANLEY | SR. MANAGER EHS | kstanley@3cmidstream.com | 3462413585 |  |  |  |  | KEVIN STANLEY | SR MANAGER EHS | 3462413585 | kstanley@3cmidstream.com | A PINHOLE LEAK WAS DISCOVERED ON THE HIGH ISLAND PIPELINE SYSTEM OPERATED BY PANTHER OPERATING COMPANY AFTER THE PRODUCER SHUT IN BOTH THEIR INLET AND OUTLET OF THEIR SYSTEM INTO OUR LINE. WHEN THE LINE BEGAN PRESSURING UP (STILL WITHIN MAOP), THE LEAK WAS DISCOVERED. THE LEAK IS ON A RISER COMING ONTO PLATFORM HI A563B. THE LEAK WAS IMMEDIATELY CLAMPED AS A TEMPORARY REPAIR, AND THEN A PERMANENT REPAIR WAS MADE WITH THE AFFECTED SECTION OF PIPE REPLACED. ALL REPAIR WORK COMPLETED ON 9/3/2019.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200034 | 33892 | 2020-04-22 13:49 | SUPPLEMENTAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2020-03-26 13:15 | 2020 | CENTRAL | YES | 32.3738 | -93.9437 | 1274308 | 2020-03-26 16:23 | 1274411 | NATURAL GAS |  | 157000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-03-26 19:25 | 2020-03-27 14:25 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-03-26 15:00 | NO | [5 empty] | VALVE CLOSURE |  | 2020-03-26 19:25 | VALVE CLOSURE |  | 2020-03-26 19:25 | 0 | 2020-03-26 13:15 | 2020-03-26 15:11 | ONSHORE | LA | 71129 | GREENWOOD | CADDO | NOT APPLICABLE |  | LINE N | LINE N | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 12 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 | NO | 0.25 | 42000 | UNKNOWN | DSAW |  | UNKNOWN | OTHER | PARTIALLY WRAPPED IN TAPE WITH A TAR LIKE SUBSTANCE BETWEEN TAPE AND PIPE OD. | YES | [26 empty] | 1950 | 1950 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 30 | 24 |  | CLASS 1 LOCATION | NO |  | 175 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 274750 | 274750 | 165000 | 165000 | 10000 | 10000 | 0 | 0 |  | 1.75 | 449750 | 365175.418220658 | 449750 | 0 | 0 | 0 | 0 | NO |  |  |  | 225 | 4000 | 250 | 192.619(C) |  | 2012-11-28 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 32105 | NO | [5 empty] | YES | LACK OF PIG TRAPS | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [9 empty] | YES |  |  | YES | YES | 1951 | YES | NO | [8 empty] | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [14 empty] | YES | [48 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  | CASEY ROBERTS | casey.roberts@enablemidstream.com | 4055584647 | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | ON MARCH 26TH, 2020 AT 13:15 ENABLE GAS TRANSMISSION LINE N EXPERIENCED A FAILURE IN CADDO PARISH LOUISIANA. THE FAILED SECTION WAS LOCATED IN A SEASONAL CREEK 12" UNDERGROUND AND THE FAILURE OCCURRED NEAR THE 12 O'CLOCK AREA OF THE PIPE. THE FAILED SECTION WAS REMOVED AND SENT TO PRECISION ENGINEERING FOR METALLURGICAL ANALYSIS. THE NRC WAS NOTIFIED ON 3/26/2020 (NRC # 1274308). A 48 HR FOLLOW UP CALL WAS PROVIDED TO THE NRC ON 3/28/2020 (NRC # 1274411). ENABLE MIDSTREAM PARTNERS HAS NOT RECEIVED THE RESULTS OF THE LAB ANALYSIS. THE FAILURE INVESTIGATION IS ON-GOING. _______________________________________________________________________________________________________________________THE LAB ANALYSIS PERFORMED ON THE RUPTURED LINE PIPE INDICATE THAT THE INITIATION OF THE FRACTURE WAS DUE TO DUCTILE OVERLOAD. THE WALL THICKNESS OF THE LINE PIPE IN THE REGION OF THE FACTURE WAS FOUND TO HAVE BEEN REDUCED DUE TO HEAVY O.D. CORROSION AT THE 12 O'CLOCK POSITION (TOP OF LINE). THE WALL IN THIS REGION WAS REDUCED (WALL THICKNESS RANGING FROM 0.013 INCH TO 0.088 INCH MEASURED NEAR RUPTURE) TO THE POINT WHERE IT COULD NO LONGER SUPPORT THE HOOP STRESS GENERATED BY THE INTERNAL LINE PRESSURE (225 PSIG). BY USING THE BARLOW'S FORMULA AND THE TENSILE STRENGTH OBTAINED IN THE MECHANICAL TESTING, IT IS CALCULATED THAT WITH AN INTERNAL PRESSURE OF 225 PSIG AND A TENSILE STRENGTH OF 66,542 PSI, RUPTURE WOULD BE EXPECTED TO OCCUR AT A WALL THICKNESS OF APPROXIMATELY 0.027. THE ANALYSIS PERFORMED ON THE FAILED SECTION OF LINE N SHOW EXTENSIVE O.D. CORROSION OF THE TOP PORTION OF THE PIPE. WALL THICKNESS MEASUREMENTS CONFIRMED THE WALL LOSS WAS CONFINED TO THE 12 O'CLOCK POSITION OF THE PIPE. THIS SECTION OF LINE N WAS LOCATED IN A SEASONAL CREEK AREA WHERE THE PIPE IS BELIEVED TO HAVE BEEN 8-12 INCHES BELOW THE SURFACE PRIOR TO FAILURE. WHEN FULLY EVACUATED, STANDING WATER COULD BE SEEN INSIDE THE FAILED PIPE SEGMENT. THE GAS IN LINE N IS TARIFF QUALITY GAS INDICATING WATER WAS PRESENT ABOVE THE PIPE PRIOR TO RUPTURE. IT IS DETERMINED THAT 70 YEARS OF SEASONAL EXPOSURE TO WATER AND ATMOSPHERE, WITH COATING DETERIORATION AT THE 12 O'CLOCK POSITION, REDUCED THIS SECTION OF PIPE TO WHERE IT COULD NO LONGER SUPPORT THE HOOP STRESS GENERATED BY THE INTERNAL LINE PRESSURE (225 PSIG). ______________________________________________________________________________________________________________________ THE FAILED SECTION OF LINE HAS NEVER BEEN EXPOSED. ALONG WITH ANNUAL PATROLS THERE HAVE BEEN ADDITIONAL EXPOSURE INSPECTIONS ON THIS LINE. A CLOSE INTERVAL SURVEY WAS PERFORMED IN 2016 AND THE CREW DID NOT SEE ANY PIPE EXPOSED AND IN 2018 THE OPS SOUTHERN DIVISION LAUNCHED AN EXPOSED PIPE INITIATIVE. DURING THIS INITIATIVE THE FAILED SECTION WAS NOT SEEN OR DETERMINED TO BE EXPOSED. THERE WAS AN EXPOSURE ROUGHLY 700 FEET TO THE NORTH OF THE FAILURE SITE THAT WAS DISCOVERED IN 2006. THE EXPOSURE WAS ENTERED INTO MAXIMO, WORK ORDERS FOR INSPECTION WERE REGENERATED, AND THE COATING WAS REPAIRED IN 2013. THE SITE CONTINUES TO BE INSPECTED TODAY WITH WORK ORDERS BEING GENERATED FOR FOLLOW UP. IF THE FAILED SECTION WAS ABOVEGROUND, OR VISIBLE, WE WOULD HAVE SEEN IT. THE EXPOSURE WOULD HAVE FOLLOWED THE SAME INSPECTION PROCESS AS THE EXPOSURE 700 FEET DOWNSTREAM. MOST LIKELY THE FAILURE SITE HAS ALWAYS BEEN COVERED BY WATER AND A SMALL AMOUNT OF SOIL. WHEN THE FAILED SECTION WAS REPLACED TAPE COULD BE SEEN ON THE PIPE THROUGH THE ENTIRE EXCAVATION (ROUGHLY 90'). ALSO, IN LOOKING AT EXPOSED SECTIONS OF ORIGINAL LINE N PIPE, THE TAPE HAS BEEN PRESENT AT OTHER LOCATIONS AS WELL. TAPE WAS NOTED ON DOCUMENTATION FOR THE EXPOSURE MENTIONED ABOVE, AS WELL AS, SEEN ON A DIRECT ASSESSMENT DIG NEAR THE SHREVEPORT AREA. DUE TO THE ABOVE EXAMPLES THE TEAM BELIEVES THE TAPE IS PART OF ORIGINAL CONSTRUCTION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200035 | 33698 | 2020-04-22 14:23 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2020-03-24 13:32 | 2020 | EASTERN | NO | 37.6055 | -83.9246 | 1274209 | 2020-03-25 14:02 | 1274329 | NATURAL GAS |  | 15900 | 528 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-03-24 18:03 | 2020-04-06 11:10 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-03-24 17:09 | VALVE CLOSURE |  | 2020-03-24 18:03 | 0 | 2020-03-24 13:32 | 2020-03-24 13:32 | ONSHORE | KY | 40336 | IRVINE | ESTILL | SURVEY STATION NO. | 761+46 | KA1S | STATION CAMP | NO | OPERATOR-CONTROLLED PROPERTY | TRANSITION AREA | SOIL/AIR INTERFACE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 | NO | 0.322 | 35000 | UNKNOWN | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | OTHER | CANUSA TAPE WRAP | YES | [26 empty] | 1990 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 189 |  | NO | NO |  |  | 0 | 0 | 818 | 818 | 24645 | 24645 | 270900 | 270900 | 0 | 0 | 0 | 0 |  | 1.55 | 296363 | 150276.322328591 | 296363 | 0 | 0 | 13 | 0 | NO |  |  |  | 600 | 5830 | 1000 | 192.619(A)(2) |  | 1990-03-16 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | YES | MANUAL | MANUAL | 42240 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER WAS NOTIFIED BY OPERATING PERSONNEL ABOUT THE LEAK AND OTHER MEMBERS OF OPERATIONS WAS ALSO MADE AWARE. CONTROLLER WAS NOT A CONTRIBUTING FACTOR TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  |  | YES | [7 empty] | YES |  |  |  | YES | YES | 1991 | YES | YES |  | YES |  |  |  | 2010 |  |  | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | MARK NEWMAN | REGIONAL COMPLIANCE SPECIALIST | mark_newman@tcenergy.com | 304-549-0532 | 304-722-8420 | TRAVIS ROBERTS | travis_roberts@tcenergy.com | 859-595-3154 | PAUL SHAFFER | COMPLIANCE MANAGER EAST | 304-550-4866 | paul_shaffer@tcenergy.com | ON MARCH 24, 2020 AT 1:32 PM EASTERN STANDARD TIME (EST), COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA), OPID 2616 COMPANY PERSONNEL WHILE PERFORMING MAINTENANCE TASKS AT STATION CAMP COMPRESSOR DISCOVERED A PINHOLE LEAK DUE AT THE SOIL-TO-AIR INTERFACE AT THE LAUNCHER ON LINE KA-1S, CLASSIFIED AS TRANSMISSION CARBON STEEL PIPELINE WITH 8.625-INCH IN DIAMETER, 0.322-INCH OF WALL THICKNESS AND GRADE B PIPELINE NEAR STATION CAMP COMPRESSOR. THE LEAK WAS EXPOSED BY HYDROVAC. APPROXIMATELY FIFTEEN FEET OF PRE-TESTED 8.625-INCH, 0.322 WALL, GRADE B, REPLACED THE CORRODED SECTION, WAS COATED, THEN THE EXPOSED PIPE WAS INSPECTED AND RECOATED, AND THE AREA WAS BACK-FILLED WITH FLOWABLE FILL AND OTHER MATERIAL. THIRTEEN CONSUMER TAPS SERVED BY COLUMBIA GAS OF KENTUCKY (CKY) THE LOCAL DISTRIBUTION OPERATOR WERE AFFECTED DURING REPAIRS AND CONVERTED TO BOTTLE GAS AND MONITORED AND MANAGED BY CKY. THE PIPELINE WAS RETURNED TO SERVICE ON APRIL 6, 2020 AT 09:12 EST. LINE KA-1S HAS A MAXIMUM ALLOWABLE OPERATING PRESSURE OF 1,000 PSIG, AND OPERATES AT APPROXIMATELY 650 PSIG.
2021-02-26 10:37 | YES | YES | GT (Gas Transmission) | 20200036 | 34060 | 2020-04-22 17:59 | SUPPLEMENTAL FINAL | 15105 | PANHANDLE EASTERN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-03-26 14:00 | 2020 | CENTRAL | YES | 37.2104 | -100.3536 | 1274304 | 2020-03-26 16:04 | 1274395 | NATURAL GAS |  | 0.3 | 285 | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-03-27 07:00 | 2020-07-15 13:00 |  | YES | OPERATOR | 2020-03-26 14:09 | NO | [5 empty] | OPERATIONAL CONTROL | NO FAILURE THEREFORE NO ACTION TAKEN. |  | OPERATIONAL CONTROL | NO FAILURE THEREFORE NO ACTION TAKEN. |  | 0 | 2020-03-26 14:00 | 2020-03-26 14:00 | ONSHORE | KS | 67864 | MEADE | MEADE | NOT APPLICABLE |  | BORCHERS STORAGE FIELD | EAST 10" LATERAL - RECEIVER | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | SCRAPER/PIG TRAP | [38 empty] | 1981 | 1981 | CARBON STEEL |  | OTHER | [8 empty] | INCIDENT WAS RESULT OF RELEASE OF STORED ENERGY DURING PIGGING RECEIPT OPERATIONS | CLASS 1 LOCATION | NO |  | 381 |  | NO | NO | NO |  | 0 | 0 | 194 | 194 | 0 | 0 | 0 | 0 | 305 | 305 | 20640 | 20640 | INCIDENT INVESTIGATION. | 0.68 | 21139 | 9703.35879125664 | 21139 | 0 | 1 | 0 | 0 | NO |  |  |  | 936 | 50000 | 1875 | 192.619(A)(2) |  | 1981-11-17 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 14 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PIGGING OPERATION IS A MANUAL OPERATION; THEREFORE, IT WOULD NOT GENERATE AN ACTIONABLE RESPONSE FROM THE CONTROL CENTER. NOTHING WOULD BE OBSERVABLE WITHIN SCADA FOR THE CONTROL CENTER TO SEE AS IT PERTAINS TO PULLING THE PIG CLEANER FROM THE PIG RECEIVER. | [12 empty] | YES | 6 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | ALTHOUGH THE TRAP DOOR WAS OPEN, EMPLOYEE POSITIONED HIMSELF IN FRONT OF THE OPEN RECEIVER IN THE PROJECTED PATH OF THE PIG WITHOUT VERIFYING THAT THE PRESSURE BEHIND THE PIG HAD BEEN RELIEVED. SOP I.13 PIGGING AND PIG TRAP OPERATION WARNS OF THE DANGERS OF STANDING IN FRONT OF THE RECEIVER DOOR AND INSTRUCTS EMPLOYEES TO ENSURE THAT THE TRAP IS DEPRESSURIZED. AS PART OF ON THE JOB TRAINING, EMPLOYEES ARE TAUGHT THE DANGERS OF STANDING IN FRONT OF THE RECEIVER. |  |  | YES |  |  | ROUTINE MAINTENANCE | NO | [149 empty] | YES | KATHRYN HARRYMAN | SENIOR SPECIALIST REGULATORY COMPLIANCE | kathryn.harryman@energytransfer.com | 832-660-5977 |  |  |  |  | DANNY NICHOLS | SENIOR DIRECTOR REGULATORY COMPLIANCE | 713-989-7232 | danny.nichols@energytransfer.com | ON MARCH 26, 2020, EMPLOYEE WAS RECEIVING A CLEANING PIG ON THE TEN-INCH EAST LINE AT BORCHERS STATION WHEN THE PIG BECAME LODGED IN THE RECEIVER. THE DOOR TO THE RECEIVER WAS OPENED, AND EMPLOYEE HAD POSITIONED HIMSELF IN FRONT OF THE PIG RECEIVER IN AN ATTEMPT TO DISLODGE THE STUCK PIG. SUDDENLY, THE PIG BECAME DISLODGED AND DISCHARGED OUT OF THE BARREL, STRIKING EMPLOYEE. ANOTHER EMPLOYEE CALLED 911 AND ASSISTED INJURED EMPLOYEE UNTIL MEDICAL ASSISTANCE ARRIVED. HIGHWAY PATROL ARRIVED AND ASSISTED WITH FIRST AID UNTIL THE AMBULANCE ARRIVED. EMPLOYEE WAS TRANSPORTED TO MEADE COUNTY HOSPITAL WHERE THE EMPLOYEE PASSED AWAY. PLEASE REFER TO PART G (APPARENT CAUSE). AS IT APPLIES TO PART K (CONTRIBUTING FACTORS), SOP I.13 PIGGING AND PIG TRAP OPERATION REQUIRES A SITE SPECIFIC PIGGING PROCEDURE. HOWEVER, AT THE TIME OF THE INCIDENT, A SITE SPECIFIC PIGGING PROCEDURE WAS NOT LOCATED. IT HAS NOT BEEN DETERMINED THAT THE PRESENCE OF A SITE SPECIFIC PIGGING PROCEDURE AT BORCHERS STATION WOULD HAVE PREVENTED THIS INCIDENT. IN TERMS OF PROCESS IMPROVEMENT, WE HAVE CREATED A SITE SPECIFIC PIGGING PLAN FOR BORCHERS EAST 10" TRAP. A SAFETY ALERT HAS BEEN DISTRIBUTED COMPANY-WIDE IN ORDER TO REINFORCE OUR CURRENT PIGGING PROCEDURES AND STRESS THE IMPORTANCE OF PROPER SAFETY PROTOCOLS WHEN ENGAGING IN PIGGING ACTIVITIES. WE HAVE WORKED WITH LOCAL FIELD PERSONNEL TO REINFORCE OUR PIGGING PROCEDURES. ALSO, WE HAVE DEVELOPED A TEAM TO REVIEW AND ASSESS CURRENT PIGGING PROCEDURES.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200037 | 34851 | 2020-04-23 14:54 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2020-03-26 08:45 | 2020 | EASTERN | YES | 40.2731 | -81.5744 | 1274263 | 2020-03-26 11:17 | 1274397 | NATURAL GAS |  | 8538 | 84.7 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-03-28 18:55 | 2020-04-24 12:00 |  | YES | OPERATOR | 2020-03-26 10:21 | NO | [5 empty] | VALVE CLOSURE |  | 2020-03-28 14:09 | VALVE CLOSURE |  | 2020-03-28 18:50 | 0 | 2020-03-26 08:45 | 2020-03-26 09:58 | ONSHORE | OH | 43832 | NEWCOMERSTOWN | TUSCARAWAS | SURVEY STATION NO. | 62+61 | O-1460 | O-1460-100 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | UNDER THE RIVER |  | NO | YES | [6 empty] | YES | UNCASED | TUSCARAWAS RIVER | 7 | BELOW WATER, PIPE ON OR ABOVE BOTTOM | YES | [10 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 | NO | 0.25 | 35000 | GRADE B | SEAMLESS |  | UNKNOWN | NONE |  | UNKNOWN | [26 empty] | 1954 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 140 |  | NO | NO |  |  | 0 | 0 | 131 | 131 | 3966 | 3966 | 2268855 | 2268855 | 0 | 0 | 0 | 0 |  | 1.55 | 2272952 | 1045636.17763747 | 2272952 | 0 | 0 | 0 | 0 | NO |  |  |  | 185 | 328 | 280 | 192.619(C) |  | 1976-05-07 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 32594 | NO | YES | [6 empty] | YES |  | YES |  |  |  |  | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION | [6 empty] | YES | EROSION |  |  | YES | YES |  |  | YES | YES | 1954 | NO | NO | [8 empty] | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KAMRAN ROSTAMI ASRABADI | COMPLIANCE SPECIALIST | kamran_rostami@tcenergy.com | (304)357-2351 |  |  |  |  | PAUL SHAFFER | US REGULATORY COMPLIANCE MANAGER EAST | (304)550-4866 | paul_shaffer@tcenergy.com | ON MARCH 26, 2020 AT 08:45 EASTERN DAYLIGHT TIME (EDT), COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA) MONITORING CENTER RECEIVED A CALL FROM A PASSER-BY REGARDING THE OBSERVATION OF GAS BUBBLING IN TUSCARAWAS RIVER. COLUMBIA OPERATIONS PERSONNEL WERE ON SITE AT 09:58 EDT AND CONFIRMED THAT THE UNINTENDED NATURAL GAS (MATERIAL) RELEASE WAS FROM LINE O-1460. THE INVOLVED SECTION OF LINE O-1460 IN THIS EVENT CROSSED AT THE BOTTOM A RIVER. LINE O-1460 IS CARBON STEEL TRANSMISSION PIPELINE WITH 6 INCH IN DIAMETER AND MAXIMUM ALLOWABLE OPERATING PRESSURE OF 280 PSIG OPERATED AND MAINTAINED BY COLUMBIA. ON MARCH 28, 2020 AT APPROXIMATELY 18:55 EDT, THE AFFECTED SECTION OF LINE O-1460 WAS ISOLATED AND EMERGENCY BLOWDOWN OF THE AFFECTED SECTION WAS INITIATED. THE BLOWDOWN WAS COMPLETED AT 19:28 EDT. THE LEAK WAS ISOLATED AND THE AFFECTED SECTION OF THE LINE O-1460 WAS ISOLATED AND REMOVED FROM SERVICE. A COMPRESSED NATURAL GAS TANKER WAS CONNECTED AND STARTED FEEDING THE DOWNSTREAM CUSTOMERS WHOSE SERVICE IS PROVIDED BY THE LOCAL DISTRIBUTION OPERATOR. THE RIVER-CROSSING SECTION OF LINE O-1460 WAS CUT AND CAPPED ON BOTH ENDS. THE INITIAL NATIONAL RESPONSE CENTER REPORT NO.1278263 AND THE NRC 48-HOUR REPORT NO. 1274397 HAVE BEEN CALLED-IN ON MARCH 26TH AND MARCH 28TH RESPECTIVELY. THE INVOLVED SEGMENTS OF LINE O-1460 IN THIS INCIDENT WERE SENT TO A METALLURGICAL FAILURE ANALYSIS LABORATORY TO ESTABLISH THE ROOT CAUSE BEHIND THIS RIVER-CROSSING PIPELINE FAILURE. THE METALLURGICAL FAILURE ANALYSIS REPORT OF LINE O-1460 IDENTIFIED THAT THE CAUSE OF THE LEAK IS EROSION-CORROSION. THE CONSTRUCTION OF THE REPLACEMENT SECTION FOR LINE O-1460 WAS COMPLETED BY USING HORIZONTAL DIRECTIONAL DRILLING (HDD) METHOD FOR INSTALLING PIPE UNDER THE TUSCARAWAS RIVER. THE HDD METHOD WILL HELP PROTECT THE PIPE TO AVOID FUTURE EVENTS FROM RE-OCCURRING.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200038 | 33730 | 2020-04-24 16:21 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2020-04-24 00:39 | 2020 | CENTRAL | YES | 42.0471 | -94.046 | 1275984 | 2020-04-24 10:00 |  | NATURAL GAS |  | 3508 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | REGULATOR FAILED OPEN, RELIEF VALVE KEPT MAOP WHILE STILL SERVING |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-04-24 00:09 | 2020-04-24 00:30 | ONSHORE | IA | 50212 | Not Within a Municipality | BOONE | MILEPOST | 0 | NORTHERN NATURAL GAS | 179IAB66001 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE OPENED AFTER A REGULATOR FAILURE. | CLASS 1 LOCATION | YES | METHOD2 | 166 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 6314 | 6314 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.8 | 6314 | 6546.01049868766 | 6314 | 0 | 0 | 0 | 0 | NO |  |  |  | 465 | 8400 | 500 | 192.619(A)(3) |  | 1970-07-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | NO | NO | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE EVENT WAS NOT DRIVEN BY A CONTROL ROOM FACTOR | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [52 empty] | LIGHTNING |  |  | SECONDARY IMPACT SUCH AS RESULTING NEARBY FIRES |  |  | NO | [267 empty] | YES | [38 empty] | JEFFREY CULLISON |  | j.cullison@nngco.com | 402-398-7439 |  |  |  |  | TOM CORRELL |  | 402-398-7715 | thomas.correll@nngco.com | AT 0009 THE OCC RECEIVED A CALL FROM LOCAL POLICE THAT A NOISE WAS HEARD AT THE OGDEN COMPRESSOR STATION THAT SOUNDED LIKE A JET. TECHNICIANS ARRIVED AND COULD HEAR VENTING GAS AND WENT TO HMI TO SEE WHERE THE GAS COULD BE VENTING FROM. ONCE DETECTED, TECHNICIANS WENT TO THE REGULATOR LOCATION AND STARTED TO BRING PRESSURE DOWN BY CLOSING THE ISOLATION VALVE UPSTREAM OF THE REGULATOR. ONCE THE PRESSURE CAME DOWN, THE RELIEF VALVE SET AND THE GAS WAS NO LONGER VENTING. IT WAS FOUND THAT THE CIRCUIT CARD THAT CONTROLS THE READINGS FOR THE REGULATOR WAS DAMAGED BY A LIGHTNING STRIKE. THE CARD WAS REPLACED, AND THE SYSTEM TESTED AND RETURNED TO NORMAL OPERATION.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200039 | 34134 | 2020-04-28 12:48 | SUPPLEMENTAL FINAL | 11248 | LAS VEGAS NATURAL GAS SYSTEM | 905 12TH ST. P.O. BOX 179 | LAS VEGAS | NM | 87701 | 2020-04-01 13:40 | 2020 | MOUNTAIN | YES | 35.8677 | -104.8773 | 1274991 | 2020-04-07 15:04 | 1275182 | NATURAL GAS |  | 156.2 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | NORMAL OPERATION |  |  |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-04-01 13:40 | NO | [5 empty] | OPERATIONAL CONTROL | LOWERED PRESSURE |  | OPERATIONAL CONTROL | LOWERED PRESSURE |  | 0 | 2020-04-01 13:40 | 2020-04-01 14:20 | ONSHORE | NM | 87701 | WATROUS NM | MORA COUNTY | MILEPOST | 371 | LAS VEGAS NATURAL GAS SYSTEM | 11248 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 24 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 | NO | 0.322 | 42000 | UNKNOWN | CONTINUOUS WELDED |  | UNKNOWN | COAL TAR |  | YES | [26 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | [9 empty] | CLASS 1 LOCATION | NO |  | 96 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 12824 | 12824 | 63594 | 63594 | 2000 | 2000 | 1000 | 1000 | LABOR | 82.1 | 79418 | 43863.6263018503 | 79418 | 0 | 0 | 0 | 0 | NO |  |  |  | 295 | 4489 | 300 | 192.619(A)(1) |  | 2008-04-10 | NO | PRESSURE DID NOT EXCEED MAOP | YES | NO | STATE | NO |  |  |  | 158840 | NO |  | YES | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | OTHER | GAS LINE HIT BY DOZER |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  |  |  | YES | [6 empty] | UNKNOWN/OTHER | UNKNOWN/OTHER | GRADING | NO | [5 empty] | NO |  | OTHER |  |  |  | NO LOCATES WERE CALLED IN TO 811 | [262 empty] | KENNY LUCERO | GAS MANAGER | klucero@lasvegasnm.gov | 505-429-3202 |  | KENNY LUCERO | klucero@lasvegasnm.gov | 505-429-3202 | KENNY LUCERO | GAS MANAGER | 505-429-3202 | klucero@lasvegasnm.gov | ZACH BARLETT RANCH HAND WAS OPERATING DOZER WHEN HE HIT THE TRANSMISSION GAS LINE AT MILE MARKER 371 NORTH OF WATROUS, NM, OPERATOR DID NOT CALL 811 FOR LOCATES. 8'' BOLTED WRAP AROUND CLAMP WAS TEMPORARY INSTALLED AND WAS MONITORED DAILY . UNTIL CONTRACTOR PERMANENTLY REPAIRED IT . WORK STARTED ON 4/15/2020 AND COMPLETED ON 4/17/2020. REPAIRED BY INSTALLING TWO 8" STOPPLE FITTINGS, PLUGGED LINE AND INSTALLED 3"FEET OF 8'' PIPE . ALSO INSTALLED ONE 2'' BY-PASS . ALL FITTINGS WERE PRESSURE TESTED AT 500LBS. PIPE WAS PIPE WRAPPED. LEAK IS COMPLETELY REPAIRED AND FINISHED BY THE CONTRACTOR.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200040 | 34016 | 2020-04-28 16:08 | SUPPLEMENTAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-04-07 19:53 | 2020 | CENTRAL | YES | 28.686 | -96.8194 | 1275005 | 2020-04-07 21:30 | 1275048 | NATURAL GAS |  | 0 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | POST-MAINTENANCE/REPAIR | [5 empty] | NO |  |  | NO | [11 empty] | 0 | 2020-04-07 19:00 | 2020-04-07 19:53 | ONSHORE | TX | 77977 | PLACEDO | VICTORIA | MILEPOST | PLACEDO CG | PLACEDO CITY GATE STATION | 4793 PLACEDO CGSTA AND 2IN LINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1991 | 1989 | CARBON STEEL |  | OTHER | [8 empty] | DISRUPTION ONLY | CLASS 1 LOCATION | NO |  | 45 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO |  |  |  | 117 | 0.01 | 668 | 192.619(A)(1) |  | 1990-12-05 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | NO | OTHER | CENTER POINT PERSONNEL |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A REVIEW OF THE DISRUPTION DETERMINED THAT THERE WERE NO CONTROL ROOM ACTIONS THAT CONTRIBUTED TO THE EVENT. | [12 empty] | YES | 1 | 0 | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [204 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | [5 empty] | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [142 empty] | YES | [5 empty] | YES | CHRIS PALAFOX | REGULATORY COMPLIANCE SPECIALIST | christopher.palafox@energytransfer.com | 713-989-4464 |  |  |  |  | CHRIS KRESTA | MANAGER-INTRASTATE REGULATORY COMPLIANCE | 713-989-7077 | chris.kresta@energytransfer.com | ON APRIL 7, 2020 AT APPROXIMATELY 19:53, A DISRUPTION OF GAS FLOW TO THE PLACEDO, TX CITY GATE STATION OCCURRED. THE PLACEDO CITY GATE STATION IS LOCATED HALF A MILE SOUTHEAST FROM THE CITY OF PLACEDO, TX IN VICTORIA COUNTY. AT APPROXIMATELY 19:00, CENTERPOINT NOTIFIED COMPANY PERSONNEL THAT THERE WAS A DISRUPTION OF GAS FLOW AT THE PLACEDO CITY GATE STATION. AT APPROXIMATELY 19:53, COMPANY PERSONNEL ARRIVED AT THE PLACEDO CITY GATE STATION AND CONFIRMED THAT THE PRIMARY RUN VALVE WAS CLOSED. THE VALVE WAS OPENED RESUMING GAS FLOW BACK TO THE CITY GATE. COMPANY MEASUREMENT TECHNICIAN WAS DOING SOME ROUTINE TESTING ON THE METER/REGULATOR ON THE CITY GATE STATION. THE TECHNICIAN OPENED UP THE BYPASS ON THE STATION AND CLOSED THE PRIMARY RUN ON THE METER TO ALLOW HIM TO COMPLETE HIS TESTING. ONCE HE COMPLETED HIS TESTING, HE CLOSED THE STATION BYPASS AND DID NOT OPEN THE VALVE TO PLACE THE PRIMARY RUN ON THE METER/REGULATOR BACK INTO SERVICE. THIS SHUT IN/STOPPED THE GAS SUPPLY FOR THE STATION. THE TECHNICIANS' OPERATOR QUALIFICATION FOR THE TASK WERE PULLED AND THE INDIVIDUAL WILL BE RE-TRAINED TO PREVENT FURTHER DISRUPTIONS. THIS PIPELINE IS UNDER THE JURISDICTION OF THE TEXAS RAILROAD COMMISSION. ON APRIL 7, 2020, THIS INCIDENT WAS TELEPHONICALLY REPORTED TO THE NATIONAL RESPONSE CENTER (NRC#1275005) AT 21:30 AND TO THE TXRRC (INCIDENT#2178) AT 21:40. A 48 HOUR NRC UPDATE WAS MADE ON APRIL 8, 2020 AT 11:35 (NRC#1275048)
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200041 | 34111 | 2020-05-01 13:20 | SUPPLEMENTAL FINAL | 32626 | THIRD COAST ALABAMA, LLC | BLACK BEAR TRANSMISSION 1501 MCKINNEY, SUITE 800 | HOUSTON | TX | 77010 | 2020-03-28 09:14 | 2020 | CENTRAL | YES | 33.3506 | -87.6798 | 1274435 | 2020-03-29 02:27 | 1274549 | NATURAL GAS |  | 148.129 | 1025 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-03-28 11:41 | 2020-05-15 08:25 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-03-28 09:55 | VALVE CLOSURE |  | 2020-03-28 10:00 | 0 | 2020-03-28 09:14 | 2020-03-28 09:55 | ONSHORE | AL | 35452 | MONTGOMERY | TUSCALOOSA | MILEPOST | 6.045 | MONTGOMERY | COLUMBUS | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 | NO | 0.25 | 36 | X-42 | SEAMLESS |  | UNKNOWN | COAL TAR |  | NO | [26 empty] | 1949 | 1948 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 185 |  | NO | NO |  |  | 0 | 0 | 2076 | 2076 | 300 | 300 | 225000 | 225000 | 5000 | 5000 | 0 | 0 | OPERATOR'S COST - UNKNOWN, STILL UNDER INVESTIGATION | 2.025 | 232376 | 106840.031372635 | 232376 | 0 | 0 | 0 | 0 | NO |  |  |  | 460 | 20000 | 500 | 192.619(A)(1) |  | 1948-12-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 5280 | NO | [5 empty] | YES | NO LAUNCHERS / RECEIVERS | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE DROP IS PRESSURE WAS NOT ENOUGH TO TRIGGER AN ALARM AND THE EVENT WAS DUE TO CORROSION NOT A CONTROLLERS ACTIONS. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1971 | YES | YES | YES |  |  |  | 2019 |  |  |  | NO | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KEVIN STANLEY | SR. MANAGER EHS | kstanley@3cmidstream.com | 3462413585 |  | KEVIN STANLEY | kstanley@3cmidstream.com | 3462413585 | KEVIN STANLEY | SR. MANAGER EHS | 3462413585 | kstanley@3cmidstream.com | THE LEAK OCCURRED ON THE THIRD COAST ALABAMA, LLC., 12 INCH MONTGOMERY COLUMBUS PIPELINE DUE TO EXTERNAL CORROSION (LOCALIZED PITTING). A COUPON HAS BEEN CUT OUT AND SENT TO A THIRD PARTY FOR METALLURGICAL ANALYSIS AT THE POINT OF FAILURE AS A PART OF THE INVESTIGATION INTO THE ROOT CAUSE. A NEW PIECE OF PIPE WAS PRE-HYDROTESTED AND WELDED INTO PLACE AND THE LINE WAS PLACED BACK INTO SERVICE. CORROSION CONTROL-CORROSION MONITORING SUBPART I REQUIREMENTS FOR CORROSION CONTROL IN ACCORDANCE WITH SCOPE 192.451 IT IS THE INTENT OF THIRD COAST ALABAMA, LLC TO CONTINUE TO MAINTAIN REQUIREMENTS FOR THE PROTECTION OF METALLIC PIPELINES FROM EXTERNAL, INTERNAL, AND ATMOSPHERIC CORROSION PROGRAMS ESTABLISHED. IT IS ALSO A CRITICAL REQUIREMENT THAT THIRD COAST ALABAMA, LLC WILL MAINTAIN AND SUPPORT UNDER 195.453 AND UNDER THE CORROSION CONTROL PROCEDURES REQUIRED BY 192.605(B)(2), INCLUDING THOSE FOR DESIGN, INSTALLATION, OPERATION, AND MAINTENANCE OF CATHODIC PROTECTION SYSTEMS, MUST BE CARRIED OUT BY, OR UNDER THE DIRECTION OF , A PERSON QUALIFIED IN PIPELINE CORROSION CONTROL METHODS. I. EXTERNAL CORROSION CONTROL PROGRAM THE CURRENT EXTERNAL CATHODIC PROTECTION PROGRAM AND GOING FORWARD WILL ADHERE TO THE STRINGENT REQUIREMENTS OF 192.457, 192.459, 192.461, 192.463, 192.467, 192.469, 192.471, 192.473 THE CURRENT EXTERNAL CORROSION CONTROL: MONITORING PROGRAM AND GOING FORWARD WILL ADHERE TO THE STRINGENT REQUIREMENTS OF 192.465 (A-E). II. INTERNAL CORROSION CONTROL PROGRAM THE CURRENT INTERNAL CORROSION CONTROL PROGRAM AND GOING FORWARD WILL ADHERE TO THE STRINGENT REQUIREMENTS OF 192.475, 192.476, 192.461, 192.463, 192.467, 192.469, 192.471, 192.473 THE CURRENT INTERNAL CORROSION CONTROL: MONITORING PROGRAM AND GOING FORWARD WILL ADHERE TO THE STRINGENT REQUIREMENTS OF 192.477. III. ATMOSPHERIC CORROSION CONTROL PROGRAM THE CURRENT ATMOSPHERIC CORROSION CONTROL PROGRAM AND GOING FORWARD WILL ADHERE TO THE STRINGENT REQUIREMENTS OF 192.479 THE CURRENT ATMOSPHERIC CORROSION CONTROL: MONITORING PROGRAM AND GOING FORWARD WILL ADHERE TO THE STRINGENT REQUIREMENTS OF 192.481. IV. CORROSION CONTROL PROGRAM REMEDIAL MEASURES THE CURRENT REMEDIAL CORROSION CONTROL PROGRAM AND GOING FORWARD WILL ADHERE TO THE STRINGENT REQUIREMENTS OF 192.483, 192.485. THIRD COAST ALABAMA, LLC RESERVES THE RIGHT TO CONDUCT DIRECT ASSESSMENT UNDER 192.490 AS DEFINED IN 192.903. FURTHERMORE, THIRD COAST ALABAMA, LLC WILL CONTINUE TO MAINTAIN A STRICT GUIDELINE TO CORROSION CONTROL RECORDS AS MANDATED BY STATUTE UNDER 192.491. 8-5-2020 UPDATE AN ANALYSES PERFORMED BY A THIRD PARTY INDICATED THAT THE SAMPLE PERFORATED FROM WALL LOSS DUE TO UNDERGROUND EXTERNAL CORROSION IN THE LOCATIONS WITH INADEQUATE COATING OR COATING DISBONDMENT AND INSUFFICIENT CATHODIC PROTECTION. SIDERITE IN THE OUTSIDE SURFACE DEPOSITS AND THE GHOST PEARLITE OBSERVED IN THE CORROSION SCALE INDICATED CONTRIBUTION FROM CARBONIC ACID CORROSION, WHICH REQUIRES PRESENCE OF CO2 AND WATER. THE SOURCE OF THE C02 IS LIKELY FROM THE GEOCHEMICAL REACTIONS IN THE SOIL.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200042 | 34242 | 2020-05-01 15:59 | SUPPLEMENTAL FINAL | 13769 | NORTHERN BORDER PIPELINE COMPANY | 700 LOUISIANA STREET | HOUSTON | TX | 77002 | 2020-04-02 00:58 | 2020 | CENTRAL | YES | 45.5331 | -98.7855 | 1274697 | 2020-04-02 11:43 | 1274807 | NATURAL GAS |  | 35490 | 700 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-04-02 01:40 | 2020-04-02 07:45 |  | NO |  |  | NO | [11 empty] | 0 | 2020-04-02 01:30 | 2020-04-02 02:17 | ONSHORE | SD | 57481 | WETONKA | EDMUNDS | MILEPOST | 505.95 | NORTHERN BORDER PIPELINE | WETONKA COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | UNKNOWN | UNKNOWN | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | VARIOUS MATERIALS IN THE VALVE OPERATOR. | OTHER | [8 empty] | MALFUNCTION OF STATION VENT VALVE OPERATOR. | CLASS 1 LOCATION | NO |  | 1221 |  | NO | NO |  |  | 0 | 0 | 1218 | 1218 | 61753 | 61753 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.74 | 62971 | 64581.2332467738 | 62971 | 0 | 0 | 0 | 0 | NO |  |  |  | 1020 | 200900 | 1435 | 192.619(A)(1) |  | 1992-12-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ALARMS PRESENTED TO THE CONTROLLER DID NOT INDICATE A GAS RELEASE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | MALFUNCTION OF STATION VENT VALVE OPERATOR. | [15 empty] | YES | COMPONENTS OF THE VENT VALVE OPERATOR FAILED. | [161 empty] | ARTHUR GRELL | MANAGER US REGULATORY COMPLIANCE WEST | art_grell@tcenergy.com | 509-413-7603 |  |  |  |  | LEE ROMACK | DIRECTOR PIPELINE REGULATORY COMPLIANCE | 832-320-5315 | lee_romack@tcenergy.com | AUGUST 31, 2020 - THE STATION VENT/BLOWDOWN VALVE OPERATOR WAS INSPECTED AND COMPONENTS OF THE ELEMENTARY CONTROL SENSOR (ECS) WERE DIRTY, WORN, AND DEGRADED. THE ECS MONITORS GAS PRESSURE ON THE PIPING AND WHEN THE PRESSURE LOWERS TO A SPECIFIED VALUE THE ECS WILL SIGNAL THE REVERSE RELAY TO ACTIVATE AND SEND SIGNAL TO SOLENOID TO OPEN VALVE. THE ECS, REVERSE RELAY AND TWO SOLENOIDS WERE REPLACED AT THIS LOCATION AND TESTED. THE SYSTEM IS NOW FUNCTIONING CORRECTLY.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200043 | 34275 | 2020-05-01 16:18 | SUPPLEMENTAL FINAL | 4060 | DOMINION ENERGY OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2020-04-05 18:00 | 2020 | EASTERN | YES | 40.0499 | -80.9638 | 1274863 | 2020-04-05 19:33 | 1274988 | NATURAL GAS |  | 4780 | 8998 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-04-05 21:18 | 2020-04-17 11:38 |  | YES | OPERATOR | 2020-04-05 19:08 | NO | [5 empty] | VALVE CLOSURE |  | 2020-04-05 20:35 | VALVE CLOSURE |  | 2020-04-05 21:18 | 0 | 2020-04-05 19:00 | 2020-04-05 19:00 | ONSHORE | OH | 43950 | Not Within a Municipality | BELMONT | SURVEY STATION NO. | 87529 | TPL 15 | L#268 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 216 | NO | YES |  |  |  |  | YES | UNCASED | [16 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 | NO | 0.375 | 60000 | API 5L | SINGLE SAW |  | REPUBLIC/BETHLEHEM STEEL | COAL TAR |  | UNKNOWN | [26 empty] | 1965 | 1965 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | YES | METHOD2 | 633 |  | NO | NO |  |  | 66919 | 66919 | 16871 | 16871 | 8963 | 8963 | 807905 | 807905 | 56144 | 56144 | 0 | 0 |  | 1.875 | 956802 | 444375.460550493 | 956802 | 0 | 0 | 0 | 0 | NO |  |  |  | 733 | 489000 | 820 | 192.619(A)(2) |  | 1965-09-04 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 35376 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS CAUSED BY DAMAGE TO THE PIPE. THE LEAKING AREA WAS TOO SMALL TO HAVE TRIGGERED ANY PRESSURE OR FLOW ALARMS. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [64 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | [10 empty] | NO | YES | COUNTY ROAD | [9 empty] | CONTRACTOR | AUGER | ROAD WORK | YES | A93110237200AEOB |  | UTILITY OWNER | YES | YES | NO |  | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO MAINTAIN CLEARANCE | [118 empty] | YES | YES | YES |  | YES |  |  |  | 2018 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2011 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2018 | FREE SWIMMING | HIGH RESOLUTION | [17 empty] | 2018 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | 2011 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | [13 empty] | YES | NO |  |  | NO | [13 empty] | NO | [63 empty] | JEFFERY BURDETTE | SUPERVISOR - PIPELINE COMPLIANCE | jeffery.l.burdette@dominionenergy.com | 3307545524 |  | JEFFERY BURDETTE | jeffery.l.burdette@dominionenergy.com | 3307545524 | REID HESS | MANAGER GAS PIPELINE COMPLIANCE | 8013243374 | reid.hess@dominionenergy.com | TPL-15 WAS TAKEN OUT OF SERVICE FOR A REPAIR RESULTING FROM AN ILI INSPECTION. A SECOND PARTY CONTRACTOR WAS HIRED TO INSTALL A RETAINING WALL AS PART OF THE REPAIR PROJECT. THE CONTRACTOR HIT THE PIPELINE WHILE AUGURING TO INSTALL SUPPORT BEAMS FOR THE RETAINING WALL BUT THE DAMAGE WAS NOT SEEN OR DETECTED AT THE TIME. THE LINE WAS PLACED BACK IN SERVICE ON DECEMBER 19TH, 2019 WITH NO APPARENT ISSUES. ON APRIL 5, 2020, DOMINION RECEIVED THE NOTICE OF A POTENTIAL GAS LEAK ON AIRPORT ROAD NEAR ST. CLAIRSVILLE, OHIO. DOMINION REPRESENTATIVES REPORTED TO THE AREA AND VERIFIED THE LEAK. THE LINE WAS TAKEN OUT OF SERVICE AND THE AREA MADE SAFE BY APPROXIMATELY 22:54 ON THE SAME DAY. EXCAVATION BEGAN ON APRIL 6, 2020, THE LEAK AREA WAS CONFIRMED ON APRIL 10, 2020, AND EXCAVATION WAS COMPLETED ON APRIL 13, 2020. THE REPLACEMENT OF THE DAMAGED PIPELINE SEGMENT WAS COMPLETED ON APRIL 16, 2020.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200044 | 33970 | 2020-05-01 21:41 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2020-04-03 13:40 | 2020 | CENTRAL | YES | 32.9086 | -96.916 | 1274764 | 2020-04-03 13:53 | 1274837 | NATURAL GAS |  | 258 | 308 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-04-03 18:19 | 2020-04-04 04:58 |  |  |  |  | NO | [11 empty] | 0 | 2020-04-03 11:38 | 2020-04-03 11:56 | ONSHORE | TX | 75234 | DALLAS | DALLAS | SURVEY STATION NO. | 4599+15 | LINE D | 119313489 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | METER | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | SKIDSTEER SCRAPER/GRADER CAME IN CONTACT WITH ABOVEGROUND TAP CAUSING IT TO BEND AND BREAK | CLASS 4 LOCATION | YES | METHOD1 | 276 |  | NO | NO |  |  | 0 | 0 | 1186 | 1186 | 994 | 994 | 73275 | 73275 | 9351 | 9351 | 0 | 0 |  | 3.852 | 84806 | 39502.4444676062 | 84806 | 0 | 0 | 0 | 1 | NO |  |  |  | 311 | 48000 | 400 | 192.619(A)(1) |  | 1974-12-04 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY DAMAGE OF PIPELINE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO | YES | INTERSTATE HIGHWAY | [9 empty] | CONTRACTOR | GRADER/SCRAPER | LANDSCAPING | NO | [5 empty] | YES | 11 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | JEFF BROWN | OPERATIONS SUPERVISOR | jeffrey.brown@atmosenergy.com | 972-360-4404 |  |  |  |  | MARLO SUTTON | VP TECHNICAL SERVICES | 214-206-2033 | marlo.sutton@atmosenergy.com | AT APPROXIMATELY 11:00 AM ON APRIL 3, 2020 , A THIRD PARTY CONTRACTOR WAS LEVELING GROUND AND INSTALLING UNDERGROUND IRRIGATION NEAR THE INTERSECTION OF COMMERCE RD. AND I-635 SERVICE ROAD IN DALLAS, TX. ATMOS ENERGY DID NOT RECEIVE PRIOR NOTIFICATION OF THE EXCAVATION ACTIVITY, AND NO NOTIFICATION WAS MADE BY THE CONTRACTOR TO THE ONE-CALL CENTER. THE CONTRACTOR STRUCK A TAP ON ATMOS' LINE D, CAUSING A RELEASE OF GAS. ATMOS ENERGY WAS NOTIFIED OF THE INCIDENT BY THE FARMERS BRANCH FIRE DEPARTMENT AT 11:11 AM. THE RELEASE WAS SECURED AT 6:19 PM WHEN LINE D WAS TAKEN OUT OF SERVICE TO MAKE REPAIRS. LINE D WAS PLACED BACK IN SERVICE AT 4:58 AM ON APRIL 4, 2020. 48 HOUR NRC # 1274837
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200045 | 33724 | 2020-05-01 22:10 | SUPPLEMENTAL FINAL | 19610 | TRANSWESTERN PIPELINE COMPANY LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-04-07 07:00 | 2020 | CENTRAL | YES | 32.8015 | -103.8025 | 1274969 | 2020-04-07 14:03 | 1275108 | NATURAL GAS |  | 13266 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | ISOLATED VENTING RELIEF VALVE |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-04-07 07:00 | 2020-04-07 07:00 | ONSHORE | NM | 88220 | CARLSBAD | LEE | SURVEY STATION NO. | 511+54.7 | MALJAMAR COMPRESSOR STATION | NMBW119G | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | UNKNOWN | 1997 | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE OPENED AT A LOWER PRESSURE THAN DESIRED AND FAILED TO RESET. | CLASS 1 LOCATION | NO |  | 236 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 15389 | 15389 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.16 | 15389 | 15954.4750656168 | 15389 | 0 | 0 | 0 | 0 | NO |  |  |  | 978 | 26.9 | 1172 | 192.619(A)(2) |  | 1995-06-22 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WERE NO SAFETY RELATED ALARMS FOR THE CONTROL ROOM PERSONNEL TO RESPOND TO. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | PRV OPERATED UNEXPECTEDLY AT LOWER THAN SET PRESSURE. | [161 empty] | KATHRYN HARRYMAN | REGULATORY COMPLIANCE SENIOR SPECIALIST | kathryn.harryman@energytransfer.com | 713-989-7085 |  |  |  |  | DANNY NICHOLS | SENIOR DIRECTOR REGULATORY COMPLIANCE | 713-823-3795 | danny.nichols@energytransfer.com | AT 0700 NOTIFIED BY DURANGO PLANT EMPLOYEE THAT THE RELIEF VALVE WAS VENTING AT THE MALJAMAR CS. UPON INVESTIGATION ET OPERATIONS PERSONNEL VERIFIED THAT THE RELIEF VALVE WAS VENTING AND BLOCKED IT IN. THE RELIEF VALVE WAS REPAIRED AND TESTED BY COMPANY EMPLOYEES PRIOR TO BEING PUT BACK IN SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200046 | 34427 | 2020-05-05 14:36 | SUPPLEMENTAL FINAL | 32005 | ENLINK PROCESSING SERVICES, LLC | 1722 ROUTH STREET SUITE 1300 | DALLAS | TX | 75201 | 2020-04-06 02:04 | 2020 | CENTRAL | YES | 31.9111 | -93.2461 | 1274875 | 2020-04-06 07:53 | 1274998 | NATURAL GAS |  | 11600 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-04-06 07:58 | 2020-05-23 14:00 |  | YES | OPERATOR | 2020-04-06 08:08 | NO | [5 empty] | VALVE CLOSURE |  | 2020-04-06 09:00 | VALVE CLOSURE |  | 2020-04-06 07:58 | 0 | 2020-04-06 07:30 | 2020-04-06 07:30 | ONSHORE | LA | 71019 | Not Within a Municipality | NATCHITOCHES PARISH | MILEPOST | MP1.16 | CAMPTI 8" LATERAL-P1330 | CAMPTI 8" LATERAL - RED RIVER CROSSING/P1330 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO LOSS OF COVER |  |  | NO | YES | [6 empty] | YES | UNCASED | RED RIVER | 60 | BELOW WATER, PIPE IN BORED/DRILLED CROSSING | YES | [10 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 8 |  | 0.5 | 35000 | 5L GRADE B | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | REPUBLIC STEEL | COAL TAR |  | UNKNOWN | [26 empty] | 1974 | 1973 | CARBON STEEL |  | OTHER | [8 empty] | UNKNOWN DUE TO NOT BEING ABLE TO INSPECT THE PIPE DUE TO SAFETY REASONS. DECISION WAS MADE TO REPLACE THE CROSSING. WATER DEPTH AND VELOCITY IN THE RED RIVER WAS CONSIDERED TO DANGEROUS FOR DIVERS. | CLASS 1 LOCATION | NO |  | 160 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 20080 | 20080 | 960360 | 960360 | 0 | 0 | 0 | 0 |  | 1.731 | 980440 | 461648.428627689 | 980440 | 0 | 0 | 0 | 0 | NO |  |  |  | 347 | 11600 | 720 | 192.619(A)(2) |  | 1974-03-19 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 5 | NO | [5 empty] | YES | LINE DOES NOT HAVE LAUNCHERS OR RECEIVERS INSTALLED. | YES |  |  |  |  | YES | CUSTOMER CONCERNED WITH LOSING SUPPLY | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | CAUSE OF THE INCIDENT IS UNKNOWN. INCIDENT IS LOCATED AT A MAJOR RIVER CROSSING. THE CROSSING WILL BE REPLACED AND ABANDONED IN PLACE. SEE PART C COMMENTS. | [145 empty] | CORDELL THERIOT | SR. DOT SPECIALIST | cordell.theriot@enlink.com | 3373226682 |  | CORDELL THERIOT | cordell.theriot@enlink.com | 3373226682 | CORDELL THERIOT | SR. DOT SPECIALIST | 3373226682 | cordell.theriot@enlink.com | PIPELINE CONTROL DETERMINED LOSS OF VOLUMES OF GAS AND LOSS OF PRESSURE THROUGH THE SCADA SYSTEM. AT 02:04 AM, OPERATIONS PERSONNEL WERE IMMEDIATELY CALLED OUT TO INVESTIGATE. AFTER CONFIRMED DISCOVERY WAS MADE, AT 07:30 AM, ON WHICH PIPELINE THE INCIDENT WAS LOCATED ON, OPERATIONS IMMEDIATELY ISOLATED THE AFFECTED PORTION OF THE PIPELINE AND ALLOWED THE LINE TO DEPRESSURIZE COMPLETELY. TO ADD MORE COMMENTS FOR PART E8. THE SINGLE CUSTOMER IS SOMEWHAT ADVERSE TO ONSTREAM PIGGING AS ENLINK IS THEIR SOLE SUPPLIER AND THEY ARE CONCERNED ABOUT SUPPLY INTERRUPTION. PART C QUESTION 3 IS UNKNOWN IF PIPE BODY OR PIPE SEAM. CHOSE PIPE SEAM DUE TO QUESTION REQUIRES AND ANSWER TO SUBMIT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200047 | 34015 | 2020-05-06 14:20 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2020-04-09 18:35 | 2020 | CENTRAL | YES | 29.3668 | -98.2089 | 1275138 | 2020-04-09 20:44 | 1275231 | NATURAL GAS |  | 30300 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-04-09 18:37 | 2020-04-11 22:05 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-04-09 18:50 | NO | [5 empty] | VALVE CLOSURE |  | 2020-04-09 18:37 | VALVE CLOSURE |  | 2020-04-09 18:37 | 3 | 2020-04-09 18:35 | 2020-04-09 20:25 | ONSHORE | TX | 78101 | ST. HEWDIG | BEXAR | SURVEY STATION NO. | 2956+80 | BURNELL TO ADKINS | 9122 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 | NO | 0.25 | 46000 | API-5L-X-46-46000 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | YOUNGSTOWN STEEL | COAL TAR |  | UNKNOWN | [26 empty] | 1949 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 16 | 28 |  | CLASS 2 LOCATION | NO |  | 342 |  | NO | NO |  |  | 50000 | 50000 | 0 | 0 | 46965 | 46965 | 46965 | 46965 | 10000 | 10000 | 2000 | 2000 | EVACUATION EXPENSES | 1.55 | 155930 | 98708.5582727222 | 155930 | 0 | 0 | 0 | 0 | NO |  |  |  | 505 | 0 | 612 | 192.619(A)(2) |  | 2011-11-04 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | AUTOMATIC | AUTOMATIC | 79200 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO EMPLOYEES WERE FOUND TO BE HAVING CONTRIBUTED TO THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) |  | YES | [13 empty] | YES | BRITTLE FRACTURE INITIATING IN THE CONTACT MARKS AT THE EDGE OF THE HAZ | [13 empty] | YES | BRITTLE FRACTURE INITIATING IN THE CONTACT MARKS AT THE EDGE OF THE HAZ | UNKNOWN | [54 empty] | YES | YES |  |  | YES |  |  | YES | 2018 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2011 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [21 empty] | 2018 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | 2011 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | [8 empty] | TDW SPIRAL MFL | 2018 | FREE SWIMMING |  |  |  | YES | 2011 | 888 | NO | [13 empty] | YES |  |  | 2018 | 2018 | [5 empty] | YES | YES | [33 empty] | YES | [18 empty] | AMIT SHAMGAR | SR. PIPELINE COMPLIANCE SPECIALIST | ashamgar@eprod.com | 713-381-6741 |  |  |  |  | NHAN TRUONG | PIPELINE COMPLIANCE MANAGER | 713-381-2493 | nvtruong@eprod.com | AT 18:35, HOUSTON CONTROL CENTER (HCC) RECEIVED A LOW PRESSURE ALARM AND NOTICED PRESSURES DROPPING ON THE PIPELINE. THE CONTROLLER IMMEDIATELY BLOCKED IN TWO REGULATORS AND DISPATCHED FIELD PERSONNEL TO INVESTIGATE. AT 18:50, HCC WAS NOTIFIED BY THE LOCAL FIRE DEPARTMENT THERE WAS GAS BLOWING FROM A PIPELINE. AT THE TIME, IT WAS NOT KNOWN IF THE SOURCE OF THE FAILURE WAS ENTERPRISE'S OR A 3RD PARTY CONNECTING PIPELINE. LOCAL TECHNICIANS CLOSED MANUAL VALVES TO FURTHER ISOLATE THE SEGMENT. AT 20:25, ENTERPRISE PERSONNEL WERE PERMITTED TO INSPECT THE SITE OF THE LEAK AND CONFIRMED THAT IT WAS ENTERPRISE'S PIPELINE. CONCERNING QUESTION E1A. - THE VALUE ENTERED .00 IS CORRECT AS PRODUCT WAS NOT FLOWING IN THE LINE AT THE POINT AND TIME OF THE INCIDENT. CONCERNING QUESTION E.11 - NO EMPLOYEES WERE FOUND TO BE HAVING CONTRIBUTED TO THIS INCIDENT. CONTROL ROOM SYSTEMS FUNCTIONED AS DESIGNED. THE CONTROLLER REACTED SWIFTLY AND APPROPRIATELY TO THE INCIDENT. ENTERPRISE EVACUATED 3 MEMBERS OF THE GENERAL PUBLIC; HOWEVER, THE NUMBER EVACUATED BY THE LOCAL FIRE DEPARTMENT ARE STILL (AS OF JUNE 16TH, 2020) NOT AVAILABLE. THERE WERE NO FIRES OR INJURIES. METALLURGICAL ANALYSIS FOUND THAT THE PRIMARY CAUSE OF THE FAILURE WAS A BRITTLE FRACTURE INITIATING IN THE CONTACT MARKS AT THE EDGE OF THE HEAT AFFECTED ZONE (HAZ). BASED ON THE FINDINGS, ENTERPRISE PLANS TO CONDUCT A HYDROTEST IN THE AFFECTED SEGMENT TO DETECT AND REMOVE SIMILAR LOCATIONS. TRRC INCIDENT NUMBER 2180.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20200048 | 33735 | 2020-05-06 17:17 | SUPPLEMENTAL FINAL | 31994 | PANTHER OPERATING COMPANY, LLC | THIRD COAST MIDSTREAM, LLC PO BOX 1227 | HOUSTON | TX | 77251 | 2020-01-06 13:45 | 2020 | CENTRAL | YES | 28.6981 | -89.9964 | 1268088 | 2020-01-06 18:37 | 1268214 | NATURAL GAS |  | 132.409 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | REPAIR TEAM REQUESTED LINE STAY ACTIVE TO ASSIST WITH LOCATING THE LEAK |  |  |  | YES | OPERATOR | 2020-01-06 19:44 | NO | [5 empty] | OPERATIONAL CONTROL | INVESTIGATION OF LEAK SOURCE |  | OPERATIONAL CONTROL | INVESTIGATION OF LEAK SOURCE |  | 0 | 2020-01-06 13:45 | 2020-01-07 08:00 | OFFSHORE | [6 empty] | VENICE GATHERING SYSTEM | PSN - 11375 | [20 empty] | 164 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | GRAND ISLE | 82 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 24 | NO | 0.517 | 65000 | X-65 | OTHER | RESEARCHING ORIGINAL PIPELINE CONSTRUCTION DOCUMENTS | UNKNOWN | EPOXY |  | UNKNOWN | [26 empty] | 1997 | 1997 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 628 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 352 | 352 | 265000 | 265000 | 3000 | 3000 | 0 | 0 |  | 2.657 | 268352 | 123384.006054368 | 268352 | 0 | 0 | 0 | 0 | NO |  |  |  | 670 | 15489 | 1480 | 192.619(A)(2) |  | 1997-02-20 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | REMOTELY CONTROLLED |  | 277262 | YES | [7 empty] | NO | [6 empty] | OFFSHORE GATHERING | YES | YES | YES | NO | NO | OTHER | HELICOPTER CONTRACTED BY ANOTHER OPERATOR SAW AND REPORTED THE LEAK |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM WAS OPERATING AND NO INDICATION OF A LEAK WAS SEEN DURING EXPLORATORY CORRESPONDENCE WITH FIELD PERSONNEL AND THE CONTROL ROOM | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  |  | YES | [7 empty] | YES |  |  |  | YES | YES | 1997 | NO | NO | [8 empty] | NO | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KEVIN STANLEY | SR. MANAGER EHS | kstanley@3cmidstream.com | 346-241-3585 |  |  |  |  | KEVIN STANLEY | SR. MANAGER EHS | 356-241-3585 | kstanley@3cmidstream.com | ON JANUARY 6TH AN AIR PATROL WITNESSED BUBBLING IN OCS WATERS IN GRAND ISLE BLOCK 82. INITIALLY REPORTED BY ARENA AND THEN PANTHER OPERATING COMPANY (POC) VERIFIED WITH ARENA THAT THE LEAK WAS ON PSN-11375. POC CONTRACTED WITH ARENA AND MOBILIZED A REPAIR CREW TO THE SITE. THE AREA OF THE LEAK ON THE PIPE WAS UNCOVERED AND VERIFIED LEAK FROM A PINHOLE. A CLAMP WAS INSTALLED, THE PIPELINE WAS PLACED BACK INTO SERVICE AND VISUALLY VERIFIED THAT THE LEAK WAS REPAIRED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200049 | 33739 | 2020-05-12 12:39 | ORIGINAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2020-04-18 20:45 | 2020 | CENTRAL | YES | 30.0892 | -92.0291 | 1275703 | 2020-04-20 10:55 | 1275714 | NATURAL GAS |  | 4100 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | ONLY ENGINE #5 SHUT DOWN |  |  |  | YES | OPERATOR | 2020-04-18 21:42 | NO | [11 empty] | 0 | 2020-05-18 20:45 | 2020-04-18 21:08 | ONSHORE | LA | 70592 | YOUNGSVILLE | LAFAYETTE | MILEPOST | 40.1899 | YOUNGSVILLE COMPRESSOR STATION | EUNICE-THIBODEAUX SYSTEM | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1956 | 1956 | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE ACTIVATED PREMATURELY | CLASS 1 LOCATION | NO |  | 101 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 6683 | 6683 | 215 | 215 | 189 | 189 | 0 | 0 |  | 1.63 | 7087 | 7114.01621408619 | 7087 | 0 | 0 | 0 | 0 | NO |  |  |  | 998 | 400000 | 1050 | 192.619(A)(1) |  | 1956-12-20 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | ELECTRICAL STORMS IN AREA - SEE PART H NARRATIVE | [161 empty] | SHANNON M MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 270.688.6357 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 270.688.6497 | tina.baker@bwpipelines.com | TEXAS GAS' GAS CONTROL RECEIVED A CALL ABOUT NOISE AT ITS YOUNGSVILLE COMPRESSOR STATION ON 4/18/20 AT 20:45. GAS CONTROL DISPATCHED OPERATIONS PERSONNEL WHO ARRIVED AT THE SITE AT 21:08. UPON ARRIVAL, THEY FOUND THAT ENGINE #5 HAD SHUT DOWN DUE TO FIN FAN FAILURE WHICH CLOSED THE UNIT VALVES; THUS, RELIEF VALVE VENTED AND PRESSURE WENT TO 0 PSIG. ALTHOUGH NO EVIDENCE OF DAMAGE WAS FOUND, THE HIGH SIDE PILOT WAS REPLACED TO ENSURE ITS INTEGRITY. EVERYTHING OPERATED AS IT SHOULD. NEAR THE TIME THIS INCIDENT OCCURRED, ELECTRICAL STORMS WERE IN THE AREA. WHILE IT IS UNCLEAR WHETHER TEXAS GAS EXPERIENCED A LIGHTNING STRIKE, THE LIGHTNING STORM CAUSED THE COOLING FANS TO SHUT DOWN ON THIS ENGINE AND ANOTHER. AT THIS TIME PRESSURE DROP WAS SEEN ON THE ENGINE DISCHARGE TRANSMITTER WHICH CONTINUED UNTIL UNIT #5 HIGH TURBO OIL TEMPERATURE SHUT THE UNIT DOWN AT 21:08 INDICATING FAILURE ON HIGH SIDE PILOT FOR RELIEF. UNIT VALVES THEN CLOSED AND THE RELIEF VALVE VENTED TO 0 PSIG. PRESSURE INDICATION WAS NEVER OVER THE SET POINT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200050 | 33764 | 2020-05-13 08:26 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2020-04-25 11:20 | 2020 | CENTRAL | YES | 31.1153 | -93.9621 | 1276064 | 2020-04-25 11:50 | 1276147 | NATURAL GAS |  | 330 | 680 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-04-26 14:00 | 2020-04-26 18:00 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-04-26 14:00 | VALVE CLOSURE |  | 2020-04-26 14:00 | 0 | 2020-04-25 10:18 | 2020-04-25 10:45 | ONSHORE | TX | 75931 | Not Within a Municipality | JASPER | SURVEY STATION NO. | 4607+70 | BEAUMONT LINE | TPL 64 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 32 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 14 |  | 0.312 | 24000 | API 5LX | LAP WELDED |  | UNKNOWN | ASPHALT |  | YES | [7 empty] | PIPE GIRTH WELD |  | NO | [16 empty] | 1924 | 1924 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 172 |  | NO | NO |  |  | 0 | 0 | 1108 | 1108 | 538 | 538 | 60000 | 60000 | 200 | 200 | 0 | 0 |  | 1.63 | 61846 | 28699.7587528111 | 61846 | 0 | 0 | 0 | 0 | NO |  |  |  | 150 | 471 | 292 | 192.619(C) |  | 2018-04-03 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 65627 | NO | YES |  | YES |  |  |  |  | YES |  | YES | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [8 empty] | YES | LEAK WAS IN AN ACETYLENE WELD THAT CRACKED | [12 empty] | YES | [8 empty] | UNKNOWN | [54 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | SHANNON M MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 270-688-6357 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 270-688-6497 | tina.baker@bwpipelines.com | ON 4/25/2020, A LANDOWNER DISCOVERED A POTENTIAL LEAK NEAR GULF SOUTH'S PIPELINE AND CALLED GAS CONTROL AT APPROXIMATELY 10:18 A.M. GAS CONTROL DISPATCHED OPERATIONS PERSONNEL WHO VERIFIED THE LEAK AT 10:45 A.M. ATTEMPTS TO SEAL OFF THE LEAK BY INSTALLING A LEAK CLAMP ON 4/25/2020 WERE UNSUCCESSFUL AND A CONSTRUCTION CREW WAS SCHEDULED TO MOBILIZE THE NEXT DAY. AT THAT POINT, THE LINE SECTION WAS BLOWN DOWN AND A TYPE B WELDOVER PRESSURE CONTAINING SLEEVE WAS INSTALLED. 5/18/2020 UPDATED REPORT AS INSTRUCTED BY PHMSA: UPDATED QUESTION B4 TO INDICATE THAT THE LEAK LOCATION IS NOT WITHIN A MUNICIPALITY. UPDATED QUESTION C6 TO INDICATE "LEAK" AS THE TYPE OF RELEASE WITH "CRACK" AS THE TYPE OF LEAK. ADDITIONALLY, PHMSA ASKED WHAT PART SCADA PLAYED IN IDENTIFYING THIS LEAK SINCE THE THE INITIAL INDICATION WAS NOTIFICATION FROM THE PUBLIC. THE GAS CONTROLLER ON DUTY NOTICED, AFTER TRENDING, THAT THERE WAS A SLIGHT PRESSURE DROP.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200051 | 33756 | 2020-05-14 20:40 | ORIGINAL FINAL | 15105 | PANHANDLE EASTERN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-04-14 09:20 | 2020 | CENTRAL | YES | 39.472 | -90.9141 | 1275372 | 2020-04-14 09:38 | 1275497 | NATURAL GAS |  | 3800 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | ROUTINE TEST WAS BEING CONDUCTED ON ESD SYSTEM. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-04-14 09:00 | 2020-04-14 08:00 | ONSHORE | IL | 62366 | PLEASANT HILL | PIKE | NOT APPLICABLE |  | PLEASANT HILL COMPRESSOR STATION | 300 DISCHARGE RELIEF | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | AIR LEAK ON ESD TUBING PREVENTED ESD SIGNAL PRESSURE FROM REACHING THE TRIP POINT OF THE VALVE. THE VALVE DIDN'T CLOSE TO ISOLATE THE GAS FLOW TO THE RELIEF VALVE. | CLASS 1 LOCATION | NO |  | 179 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 8664 | 8664 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2.28 | 8664 | 8982.36220472441 | 8664 | 0 | 0 | 0 | 0 | NO |  |  |  | 500 | 350 | 900 | 192.619(A)(2) |  | 1954-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATIONS PERSONNEL WERE CONDUCTING AN ESD TEST AND HAD NOTIFIED THE CONTROL ROOM PRIOR TO TESTING. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | AN AIR LEAK ON THE ESD SIGNAL TUBING PREVENTED THE PRESSURE FROM BUILDING UP HIGH ENOUGH TO TRIP THE 300 SUCTION SIDE GATE VALVE. | [15 empty] | YES | O-RING AND POPPETS PREMATURELY REACHED END OF LIFE. | [161 empty] | KATHIE HARRYMAN | SENIOR SPECIALIST REGULATORY COMPLIANCE | kathryn.harryman@energytransfer.com | 713-989-7085 |  |  |  |  | DANNY NICHOLS | SENIOR DIRECTOR REGULATORY COMPLIANCE | 713-989-7232 | danny.nichols@energytransfer.com | WHILE CONDUCTING AN ESD TEST THE STATION VENTED 3.8 MMSCF OF NATURAL GAS. DURING A NORMAL ESD, IT TAKES SOME TIME TO BLOWDOWN THE YARD PIPING AFTER ACTIVATION OF THE SYSTEM. WHEN THE BLOWDOWN VALVE CONTINUED TO BLOW, OPERATIONS PERSONNEL BEGAN TO INVESTIGATE AND FOUND THE 300 SUCTION SIDE GATE VALVE TO STILL BE OPEN. THE ISOLATION VALVE UNDER THE BLOWDOWN VALVE WAS CLOSED. OPERATIONS PERSONNEL ISOLATED THE SUCTION SIDE GATE VALVE, THEN TESTED THE VALVE AND IT OPERATED AS DESIGNED. OPERATIONS PERSONNEL TESTED THE ESD SYSTEM AND FOUND THERE WAS AN AIR LEAK ON THE ESD TUBING. THE AIR LEAK WAS REPAIRED AND THE SYSTEM WAS TESTED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200052 | 34329 | 2020-05-15 12:12 | SUPPLEMENTAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2020-04-16 13:00 | 2020 | CENTRAL | YES | 35.2145 | -92.4078 | 1275515 | 2020-04-16 13:18 | 1275610 | NATURAL GAS |  | 200 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | A 20% REDUCTION WAS IMPLEMENTED |  |  |  | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | 20% OPERATING PRESSURE REDUCTION IMPLEMENTED AT SOURCE FOR PIPELINE. |  | OPERATIONAL CONTROL | PIPELINE IS STILL IN SERVICE AT A 20% REDUCTION. |  | 0 | 2020-04-15 12:30 | 2020-04-15 12:30 | ONSHORE | AR | 72508 | GREENBRIAR | CLEBURNE | NOT APPLICABLE |  | LINE BM-21 | LINE BM-21 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 4 |  | 0.188 | 30000 | UNKNOWN | FURNACE BUTT WELDED |  | UNKNOWN | COAL TAR |  | YES | [7 empty] | PIPE GIRTH WELD |  | NO | [16 empty] | 1957 | 1957 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | NO |  | 55 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 348 | 348 | 122800 | 122800 | 1000 | 1000 | 0 | 0 |  | 1.74 | 124148 | 57188.2540914642 | 124148 | 0 | 0 | 0 | 0 | NO |  |  |  | 295 | 1000 | 310 | 192.619(A)(2) |  | 2018-12-15 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES |  |  | 61776 | NO |  | YES |  |  |  | YES | LACK OF LAUNCHER/RECEIVER | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DISCOVERED DURING PATROL. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [8 empty] | YES | CORROSION | [19 empty] | YES | ORIGINAL WELD WITH CORROSION WITH CLAMP CORROSION. | UNKNOWN | [54 empty] | NO | [63 empty] | YES | 2018 | 388 | Yes, but the point of the Accident was not identified as a dig site |  | 2013 |  |  |  |  | CLOSE INTERVAL SURVEY | 2013 |  |  |  |  | YES | NO | [14 empty] | YES | [48 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  | CASEY ROBERTS | casey.roberts@enablemidstream.com | 4055584647 | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | DURING A ROUTINE PATROL, A SMALL LEAK WAS DISCOVERED ON EGT LINE BM-21. ENABLE OPERATIONS REMOVED DIRT FROM THE AFFECTED AREA AND FOUND THE MINOR LEAK TO BE COMING FROM A LEGACY GIRTH WELD THAT HAD A CLAMP INSTALLED OVER IT. THE WELD WAS COMPLETED IN 1957 AND IT CANNOT BE DETERMINED WHEN THE CLAMP WAS INSTALLED. THE LINE WAS LOWERED 20% AFTER DISCOVERY AND REMEDIATION IS PLANNED TO BEGIN IN LATE JUNE. CURRENTLY, THE LINE IS OPERATING AT REDUCED PRESSURE AND SNIFFED PERIODICALLY. AT THE LOWERED OPERATING PRESSURE THE LEAK CANNOT BE DETECTED USING LEAK DETECTION EQUIPMENT. STOPPLES WILL BE INSTALLED ALLOWING CUSTOMERS TO MAINTAIN SERVICE. REPAIR IS EXPECTED TO EXCEED $50,000. WHEN THE REPAIR IS COMPLETE A SUPPLEMENTAL REPORT WILL BE COMPLETED. THE LINE WAS REPAIRED ON JULY 15TH AND THE LINE WAS RETURNED TO NORMAL OPERATING PRESSURE ON JULY 16TH. THE LEAK WAS DUE TO CORROSION IN THE LEGACY WELD AND CLAMP. THE NRC (#1275515) WAS NOTIFIED ON 4/16/2020 AND A 48 HOUR FOLLOW UP (#1275610) WAS PROVIDED ON 4/18/20. SUPPLEMENTAL 07/27/2020 PART A.5 32.214456 TO 35.214456 PART D.7.C ADDED $1,000 PART H. NARRATIVE SUPPLEMENTAL 10/02/2020 PART H NARRATIVE BT-21 CHANGED TO BM-21
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200053 | 34294 | 2020-05-15 15:18 | SUPPLEMENTAL FINAL | 12874 | DOMINION ENERGY QUESTAR PIPELINE, LLC | 333 SOUTH STATE STREET P.O. BOX 45360 | SALT LAKE CITY | UT | 84145-0360 | 2020-04-20 14:30 | 2020 | MOUNTAIN | YES | 41.5157 | -109.4587 | 1275729 | 2020-04-20 15:30 |  | NATURAL GAS |  | 98 | 4404 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-04-15 17:21 | 2020-05-13 13:47 |  | YES | OPERATOR | 2020-04-15 16:18 | YES | 2020-04-15 16:04 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 98 | NO | VALVE CLOSURE |  | 2020-04-15 16:36 | VALVE CLOSURE |  | 2020-04-15 16:34 | 0 | 2020-04-15 16:04 | 2020-04-15 16:29 | ONSHORE | WY | 82935 | GREEN RIVER | SWEETWATER | SURVEY STATION NO. | 6132+20 | MAIN LINE 1 | CROSSOVER 19 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | TUBING | [35 empty] | STAINLESS STEEL | RIGID |  | 2014 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | APPROXIMATELY 0.1" X 0.1" HOLE | [5 empty] | CLASS 3 LOCATION | YES | METHOD2 | 370 |  | NO | NO |  |  | 0 | 0 | 5967 | 5967 | 133 | 133 | 110000 | 110000 | 2000 | 2000 | 0 | 0 |  | 1.355 | 118100 | 54287.8529146018 | 118100 | 0 | 0 | 0 | 0 | NO |  |  |  | 700 | 45000 | 849 | 192.619(A)(4) |  | 2014-05-23 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | REMOTELY CONTROLLED | 49464 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WERE NO CONCERNS WITH CONTROLLER ACTIONS OR CONTROL ROOM ISSUES | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | [103 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [261 empty] | CALEB BENTLEY | ENGINEER II | caleb.a.bentley@dominionenergy.com | 8012099761 |  |  |  |  | LORI CREER | VP WESTERN PIPELINE OPERATIONS | 8013245349 | lori.creer@dominionenergy.com | DOMINION ENERGY AND LOCAL EMERGENCY RESPONDERS WERE ALERTED TO AND MITIGATED A FIRE AT A COMPANY FACILITY ON 4/15/2020. THE FIRE WAS CAUSED BY AN ELECTRICAL ARC WHICH DAMAGED ACTUATOR POWER GAS TUBING AND IGNITED THE LEAK IT CAUSED. THIS INCIDENT OCCURRED AT A FACILITY LOCATED NEAR GREEN RIVER, WY ON ML001. INITIAL DAMAGE ESTIMATES WERE BELOW THE $50,000 INCIDENT REPORTING THRESHOLD; HOWEVER, SUBSEQUENT ANALYSIS THAT LED TO A DECISION TO REPLACE ADDITIONAL PIPING OUT OF AN ABUNDANCE OF CAUTION, INCREASED THE ESTIMATED REPLACEMENT COSTS ABOVE THE $50,000 THRESHOLD. THIS REPORTING CRITERIA WAS MET ON 4/20/2020 AT 14:30 AND A NRC REPORT WAS SUBSEQUENTLY MADE. ADDITIONAL TESTING DETERMINED THAT THE REPLACED EQUIPMENT WAS NOT ADVERSELY AFFECTED BY THE FIRE. NOTES ON SPECIFIC QUESTIONS: D2) THE PIR OF THE FAILED TUBING WOULD NOT CREATE AN HCA IN THE AREA; HOWEVER, THE FACILITY IS LOCATED WITHIN AN HCA ON ML001 D3) REPORTED PIR IS FOR ML001 DUE TO ML001 BEING USED IN QUESTION D2 E1A) REPORTED FLOW RATE IS FOR ML001 E2A) MAOP DETERMINATION METHOD REPORTED IN QUESTION E2A IS FOR THE TUBING THAT LEAKED. THE MAXIMUM SAFE OPERATING PRESSURE FOR THE TUBING IS DETERMINED PER 192.619(A)(4) TO BE THE MAIN LINE MAOP. MAIN LINE PIPING MAOP ON THIS SECTION OF ML001 WAS DETERMINED BY 192.619(A)(1). E6) LENGTH BETWEEN VALVES DOES NOT INCLUDE THE BLOCK VALVES LOCATED AT THE FACILITY INVOLVED IN THE INCIDENT
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200054 | 34815 | 2020-05-20 16:20 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2020-04-20 10:05 | 2020 | EASTERN | YES | 42.6684 | -83.3322 | 1276020 | 2020-04-24 15:59 | 1276117 | NATURAL GAS |  | 1008 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | LEAK WAS INVESTIGATED AND CLASSIFIED |  |  |  | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | LOWER PRESSURE AT THE ORION CITY GATE FROM 259 PSIG TO 207 PSIG |  | VALVE CLOSURE |  | 2020-04-21 18:25 | 0 | 2020-04-20 10:28 | 2020-04-20 10:28 | ONSHORE | MI | 48328 | WATERFORD | OAKLAND | NOT APPLICABLE |  | LINE 1014 | VALVE HA-15 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 84 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | FLANGE ASSEMBLY | [38 empty] | 1968 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | YES | METHOD2 | 182 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 2953 | 2953 | 1005527 | 1005527 | 140 | 140 | 0 | 0 |  | 2.93 | 1008620 | 464689.198553242 | 1008620 | 0 | 0 | 0 | 0 | NO |  |  |  | 259 | 8136 | 275 | 192.619(C) |  | 1969-10-27 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES |  | MANUAL | 25940 | NO | YES |  | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | GASKET | [12 empty] | YES | [167 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON PIONK | GAS COMPLIANCE MANAGER | 989-791-5749 | jason.pionk@cmsenergy.com | ON APRIL 20, 2020 AT APPROXIMATELY 10:05 HOURS, CONSUMERS ENERGY WAS NOTIFIED BY THEIR CONTRACTOR PERFORMING LEAK SURVEY OF A POTENTIAL LEAK ON LINE 1014. LINE 1014 IS A 16" HIGH PRESSURE CW STEEL PIPELINE INSTALLED IN 1968 AND LOCATE IN WATERFORD, MICHIGAN (OAKLAND COUNTY). A GAS SERVICE WORKER (GSW) WAS DISPATCHED AND ARRIVED ON-SITE AT APPROXIMATELY 10:28 HOURS. THE GSW CONFIRMED THE PRESENCE OF A LEAK AND REQUESTED A GAS DISTRIBUTION CREW BE DISPATCHED TO THE LOCATION. AN INVESTIGATION DETERMINED THE LEAK SOURCE AS A 16" VALVE (VALVE HA-15). THE VALVE WAS INJECTED WITH GREASED IN AN ATTEMPTED TO SEAL THE LEAK ON APRIL 20, 2020 AND APRIL 21, 2020. THE AREA WAS ALSO AERATED TO ELIMINATE ANY RESIDUAL GAS TRAPPED IN THE SOIL. THE SITE WAS MONITOR OVERNIGHT. ON APRIL 21, 2020 AT APPROXIMATELY 18:25 HOURS THE PIPELINE PRESSURE WAS LOWERED FROM 259 PSIG TO 207 PSIG IN PREPARATION FOR THE SITE TO BE EXCAVATED AND THE VALVE FACILITY ASSESSED TO CONFIRM THE GAS RELEASE WAS SECURE. THE CREW CONTINUED THEIR INVESTIGATION AND AS A SAFETY PRECAUTION, PERSONNEL REMAINED ON SITE. ON APRIL 22, 2020 THE LOCATION WAS EXCAVATED AND THE SOURCE OF THE LEAK WAS DETERMINED TO BE AT THE FLANGE. THE LEAK WAS CLASSIFIED AND PLANS TO RETURN TO THE SITE THE FOLLOWING DAY TO TIGHTEN AND/OR REPLACE THE BOLTS. ON APRIL 23, 2020 IT WAS DETERMINE THE ATTEMPT TO TIGHTEN BOLTS TO RESOLVE THE LEAK WAS UNSUCCESSFUL AND VALVE REPLACEMENT WOULD BE REQUIRED. THE LEAK WAS EVALUATED AND RECLASSIFIED PENDING ENGINEERING REVIEW AND REPLACEMENT PLAN DEVELOPMENT. THE SITE EXCAVATION REMAINS OPEN AND HAS BEEN SECURED TO PREVENT POTENTIAL HAZARDS TO THE PUBLIC. A VALVE REPLACEMENT PLAN IS BEING DEVELOPED. IN AUGUST 2020 (AUGUST 15 - SEPTEMBER 2) THE EXISTING 16" S-HP-20%SMYS (HA-15) VALVE WAS REMOVED AND REPLACED WITH AN 8" S-HP (HA-69) VALVE. FOLLOWING VALVE REPLACEMENT, NORMAL OPERATION WAS RESUMED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200055 | 33815 | 2020-05-28 10:17 | SUPPLEMENTAL FINAL | 12498 | MIDWESTERN GAS TRANSMISSION CO | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2020-05-07 18:06 | 2020 | CENTRAL | YES | 41.0655 | -88.0882 | 1276856 | 2020-05-07 20:52 | 1276923 | NATURAL GAS |  | 7032 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-05-07 19:03 | 2020-05-07 21:45 |  | NO |  |  | NO | [11 empty] | 0 | 2020-05-07 18:06 | 2020-05-07 19:00 | ONSHORE | IL | 60941 | Not Within a Municipality | KANKAKEE | MILEPOST | M.P. 323 | MIDWESTERN GAS TRANSMISSION HERSCHER COMPRESSOR | 2100-2121 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | INSTRUMENTATION | [38 empty] | UNKNOWN | UNKNOWN | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | TRIPPED CIRCUT BREAKER | OTHER | [8 empty] | VALVE POSITION FAILURE | CLASS 1 LOCATION | NO |  | 760 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 13565 | 13565 | 0 | 0 | 250 | 250 | 0 | 0 |  | 1.929 | 13815 | 14178.2080402777 | 13815 | 0 | 0 | 0 | 0 | NO |  |  |  | 817 | 584904 | 936 | 192.619(C) |  | 1970-08-19 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO CONTROLLER ACTIONS HAD TAKEN PLACE AT THE TIME OF THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | YES |  | YES | [27 empty] | YES | [166 empty] | NEAL JONES | REQULATORY COMPLIANCE MANAGER | neal.jones@oneok.com | 580-395-6304 | 580-395-2933 | DENIS JUDY | denis.judy@oneok.com | 815-467-5645 | JOHNNIE JARRED | DIRECTOR OF PIPELINE OPERATIONS | 918-588-7827 | johnnie.jarred@oneok.com | AT APPROXIMATELY 18:06 ON MAY 7, 2020 MIDWESTERN GAS TRANSMISSION GAS CONTROLLERS RECEIVED AN ALARM FOR "UNIT CONTROL PANEL TO SYSTEM CONTROL PANEL COMMUNICATION FAILURE K100" AT THE HERSCHER COMPRESSOR STATION. FIELD OPERATIONS PERSONNEL WERE DISPATCHED TO THE LOCATION. UPON ARRIVAL AT THE STATION, OPERATIONS EMPLOYEE IDENTIFIED NATURAL GAS VENTING FROM THE UNIT BLOW DOWN VALVE AS THE UNIT SUCTION AND DISCHARGE VALVES HAD NOT CLOSED. EMPLOYEE ACTIVATED THE STATION EMERGENCY SHUTDOWN WHICH CLOSED THE SUCTION AND DISCHARGE VALVE, STOPPING THE RELEASE. MIDWESTERN GAS TRANSMISSION'S INVESTIGATION FOUND A TRIPPED CIRCUIT BREAKER IN THE STATION CONTROL LOGIC SYSTEM WHICH ALLOWED THE UNIT TO SHUTDOWN WITHOUT CLOSURE OF THE UNIT SUCTION AND DISCHARGE VALVE. 5/28/20 CHANGED REPORT TO FINAL - NEAL JONES
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200056 | 34682 | 2020-05-29 14:33 | SUPPLEMENTAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2020-05-03 12:28 | 2020 | EASTERN | YES | 39.4627 | -82.3118 | 1276580 | 2020-05-03 15:04 | 1276670 | NATURAL GAS |  | 79.83 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-05-03 13:17 |  | YES | NO |  |  | NO | [11 empty] | 0 | 2020-05-03 12:53 | 2020-05-03 12:53 | ONSHORE | OH | 43138 | Not Within a Municipality | HOCKING | SURVEY STATION NO. | 3+25 | LAURAL RUN E-2 | LINE E-336 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 2 | NO | 0.154 | 35000 | GRADE B | SEAMLESS |  | UNKNOWN | PAINT |  | YES | [26 empty] | 1956 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 2 LOCATION | NO |  | 98 |  | NO | NO |  |  | 10000 | 10000 | 0 | 0 | 127 | 127 | 200000 | 200000 | 0 | 0 | 5000 | 5000 | BOTTLE GAS EXPENSES | 1.59 | 215127 | 98822.3398356991 | 215127 | 0 | 1 | 7 | 0 | NO |  |  |  | 204 | 0.5 | 225 | 192.619(A)(3) |  | 1950-07-12 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | OTHER | COLUMBIA GAS OF OHIO (COH), THE LOCAL DISTRIBUTION COMPANY |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [9 empty] | UNKNOWN | [5 empty] | UNKNOWN |  | YES | SMALL TRUCK | ROADWAY | 23 | YES |  | YES | [236 empty] | KAMRAN ROSTAMI ASRABADI | COMPLIANCE SPECIALIST | kamran_rostami@tcenergy.com | (304)357-2351 |  |  |  |  | PAUL SHAFFER | US REGULATORY COMPLIANCE MANAGER EAST | (304)550-4866 | paul_shaffer@tcenergy.com | ON MAY 3, 2020, AT 12:28 EASTERN DAYLIGHT TIME (EDT), COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA) OPERATIONS PERSONNEL RECEIVED A CALL FROM COLUMBIA GAS OF OHIO (COH), THE LOCAL DISTRIBUTION COMPANY, REGARDING A GAS LEAK AT LAUREL RUN MEASURING AND REGULATING STATION (M&R) 701767 ON LINE E-336. COLUMBIA OPERATIONS PERSONNEL WAS DISPATCHED AND ARRIVED ON SITE AT 12:53 EDT WHERE HE CONFIRMED THAT THE UNINTENDED NATURAL GAS RELEASE WAS DUE TO A VEHICLE ACCIDENT. THE M&R BUILDING WAS DAMAGED DUE TO SIDE IMPACT BY A TRAVELING VEHICLE ALONG LAUREL RUN ROAD THAT LOST CONTROL. AS A RESULT, TO THIS VEHICLE ACCIDENT, AN UNINTENTIONAL NATURAL GAS RELEASE INTO ATMOSPHERE FROM COLUMBIA FACILITY (LAUREL RUN M&R 701767) WAS NOTED. AT 13:17 EDT, THE UNINTENDED RELEASE OF NATURAL GAS WAS ISOLATED, AND THE FACILITY WAS REMOVED FROM SERVICE. THE INITIAL NATIONAL RESPONSE CENTER (NRC) REPORT NO.1276580 AND THE NRC 48-HOUR REPORT NO.1276670 HAVE BEEN CALLED-IN ON MAY 3RD AND MAY 5TH RESPECTIVELY. ENGINEERING ASSESSMENT AND EVALUATION TO THE LAUREL RUN M&R 701767 FACILITY AND ITS OPERATIONAL REQUIREMENTS WAS COMPLETED, WHERE IT WAS DECIDED TO ABANDON THIS PIPELINE, HENCE DISCONTINUING NATURAL GAS FLOW INTO THIS FACILITY. THIS PROJECT IS EXPECTED TO BE COMPLETED IN THE 2ND HALF OF 2021. THE FINAL REPORT WILL BE SUBMITTED AFTER COMPLETION OF THE ABANDONMENT PROJECT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200057 | 33836 | 2020-06-02 10:02 | ORIGINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2020-05-04 16:36 | 2020 | EASTERN | YES | 38.3024 | -83.6017 | 1276640 | 2020-05-04 17:40 | 1276770 | NATURAL GAS |  | 51684 | 96400 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-05-04 17:23 |  | YES | YES | OPERATOR | 2020-05-04 16:45 | YES | 2020-05-04 16:36 | ALLOWED TO BURN OUT |  | 51684 | YES | VALVE CLOSURE |  | 2020-05-04 17:23 | VALVE CLOSURE |  | 2020-05-04 17:05 | 2 | 2020-05-04 16:36 | 2020-05-04 17:01 | ONSHORE | KY | 41049 | HILLSBORO | FLEMING | MILEPOST | 509.898 | LINE 10 | OWSV-WHEE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 54 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 | NO | 0.375 | 52000 | API-5LX | DSAW |  | NATIONAL TUBE WORKS | COAL TAR |  | UNKNOWN | [26 empty] | 1952 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | THE INCIDENT IS UNDER NTSB INVESTIGATION | 48 | 80 |  | CLASS 1 LOCATION | NO |  | 633 |  | NO | NO |  |  | 700000 | 700000 | 191836 | 191836 | 102851 | 102851 | 10000000 | 10000000 | 1000000 | 1000000 | 0 | 0 |  | 1.99 | 11994687 | 5565296.81372441 | 11994687 | 0 | 0 | 0 | 0 | YES |  |  | YES | 858 | 0 | 936 | 192.619(A)(1) |  | 2014-10-07 | YES | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 77669 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | YES, BUT THE INVESTIGATION OF THE CONTROL ROOM AND/OR CONTROLLER ACTIONS HAS NOT YET BEEN COMPLETED BY THE OPERATOR (SUPPLEMENTAL REPORT REQUIRED) | [13 empty] | YES | 5 | 0 | YES | 1 | 0 | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [146 empty] | MAYRA SALINAS | SENIOR ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  | NATHAN ATANU | nathan.atanu@enbridge.com | 713-627-5008 | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 713-627-5008 | nathan.atanu@enbridge.com | AT APPROXIMATELY 4:36 PM EDT ON MAY 4, 2020, TETLP'S 30-INCH DIAMETER LINE 10 TRANSPORTING NATURAL GAS FROM WHEELERSBURG COMPRESSOR STATION TO OWINGSVILLE COMPRESSOR STATION IN KENTUCKY FAILED AT M.P. 509.898. THE FAILURE RESULTED IN AN EXPLOSION AND FIRE. TETLP RECEIVED A CALL ATTENDANT ALARM AT 4:39 PM EDT FROM THE OWINGSVILLE COMPRESSOR STATION. DURING THE ENSUING MINUTES, TETLP BEGAN RECEIVING REPORTS FROM THE PUBLIC OF A FIRE NORTH OF THE OWINGSVILLE COMPRESSOR STATION. TETLP PERSONNEL WERE IMMEDIATELY DISPATCHED TO CLOSE MAINLINE BLOCK VALVE, MLV 10-367 AT MP 517 AND MLV 10-351 AT THE OWINGSVILLE COMPRESSOR STATION, THUS ISOLATING THE FAILED SEGMENT AT 5:23 EDT. TETLP INITIATED THE NOTIFICATION TO THE NRC AT 5:23 PM EDT AFTER RECEIVING CONFIRMED DISCOVERY OF THE PIPELINE FAILURE AND GATHERING THE INITIAL INFORMATION TO MAKE THE NRC NOTIFICATION WITH THE CALL TERMINATING AT 5:40 PM EDT. NOTE THAT THE NRC RECORDS THE TIME THE CALL WAS TERMINATED ON THE NRC REPORT AND NOT THE TIME OF THE CALL WAS INITIATED. THE APPARENT CAUSE OF THE INCIDENT IS UNDER INVESTIGATION BY THE NTSB. THE INCIDENT CAUSE IS BEING REPORTED AS OTHER INCIDENT CAUSE UNTIL THE NTSB RELEASES INFORMATION ABOUT THE INCIDENT CAUSE. THE APPARENT CAUSE WILL BE UPDATED WHEN IT BECOMES AVAILABLE FROM THE NTSB. PART J WILL BE SUPPLEMENTED AS WELL ALONG WITH CAUSE. NOTE THAT E.1.A ESTIMATED GAS FLOW IN PIPE SEGMENT AT THE POINT AND TIME OF THE INCIDENT (MSCF/D): IS WAS APPROXIMATELY 1,433,000 DTH/D RATE THROUGH THE OWINGSVILLE COMPRESSOR STATION WHICH INCLUDES BOTH LINES 10 AND 25. LINE 15, WHICH SHARES THE RIGHT OF WAY WITH LINES 10 AND 25 WAS ISOLATED AT THE TIME OF THE INCIDENT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200058 | 33840 | 2020-06-02 15:49 | ORIGINAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2020-05-05 18:30 | 2020 | CENTRAL | YES | 34.4342 | -92.9037 | 1276720 | 2020-05-05 22:04 | 1276794 | NATURAL GAS |  | 4862 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | THE RELIEF VALVE WAS ISOLATED AND REPAIRED. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-05-05 18:30 | 2020-05-05 19:20 | ONSHORE | AR | 72104 | MAGNET COVE CITY | HOT SPRING | NOT APPLICABLE |  | BM-28 | LAKE CATHERINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | NIPPLE FAILURE | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | NO |  | 219 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 8460 | 8460 | 500 | 500 | 500 | 500 | 0 | 0 |  | 1.74 | 9460 | 9229.89252856499 | 9460 | 0 | 0 | 0 | 0 | NO |  |  |  | 130 | 2000 | 175 | 192.619(A)(1) |  | 2012-03-30 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | MECHANICAL FAILURE OF RELIEF VALVE | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | PIPE NIPPLE |  |  |  |  | YES | [165 empty] | YES | [11 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  | CASEY ROBERTS | casey.roberts@enablemidstream.com | 4055584647 | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | ON MAY 5TH, 2020 AT 18:30 ENABLE GAS TRANSMISSION SYSTEM CONTROL RECEIVED AN ALARM THAT A RELIEF WAS VENTING AT THE LAKE CATHERINE POWER PLANT. AT 18:35 AN ENABLE O&M TECH WAS DISPATCHED TO THE SCENE. THE O&M TECH REPORTED THAT THE RELIEF VALVE BELONGED TO ENABLE (BM-28) AND CONFIRMED IT WAS VENTING WHEN HE ARRIVED. THE RELIEF WAS ISOLATED AT 19:20 CEASING THE GAS RELEASE. A 3/4' BROKEN NIPPLE ON A GAS SENSING LINE IS THE CAUSE FOR THE MALFUNCTION. IT WAS DETERMINED BY FIELD ENGINEERS THE NIPPLE MOST LIKELY FAILED DUE TO A MIXTURE OF VIBRATION AND THE LENGTH OF THE NIPPLE. THE NIPPLE WAS REPLACED, AND FIELD ENGINEERING IS ACQUIRING A SPECIAL TEST VALVE FOR REPLACEMENT TO ELIMINATE THE POSSIBILITY OF THIS INCIDENT HAPPENING AGAIN. THE GAS RELEASE WAS CONFIRMED TO BE OVER 3,000 MCF ON MAY 5TH AT 21:24 PROMPTING THE NRC TO BE NOTIFIED (MAY 5TH AT 22:04 CST # 1276720). A FINAL GAS LOSS TOTAL (4,862 MCF) WAS DETERMINED ON MAY 6TH AND PROVIDED TO THE NRC DURING THE 48 HOUR FOLLOW UP (MAY 7TH AT 8:12 CST #1276794).
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200059 | 34006 | 2020-06-09 14:11 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2020-05-11 11:30 | 2020 | EASTERN | YES | 37.9172 | -83.9856 | 1277114 | 2020-05-12 15:50 | 1277250 | NATURAL GAS |  | 2342 | 0 | 0.27 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | NORMAL ESD BLOWDOWN. |  |  |  | YES | OPERATOR | 2020-05-11 18:00 | NO | [11 empty] | 0 | 2020-05-11 11:30 | 2020-05-11 11:30 | ONSHORE | KY | 40312 | CLAY CITY | POWELL | SURVEY STATION NO. | 106 | CLAY CITY COMPRESSOR STATION | STATION 106 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2017 | 2017 | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | WIRING | OTHER | [8 empty] | RELEASE THROUGH DESIGNED ESD BLOWDOWN PIPING | CLASS 1 LOCATION | NO |  | 820 |  | NO | NO |  |  | 100000 | 100000 | 0 | 0 | 4192 | 4192 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.79 | 104192 | 50248.6754286777 | 104192 | 0 | 0 | 10 | 0 | NO |  |  |  | 737 | 562080 | 748 | 192.619(C) |  | 1968-07-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CAUSED BY A LOOSE WIRE; NO CONTROLLER INVOLVEMENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [13 empty] | YES | [10 empty] | YES | LOOSE WIRE | [161 empty] | KENNETH C. PETERS | SR. ENGINEER | ken_peters@kindermorgan.com | 2053257554 | 2053253729 | DEAN HUNTLEY | dean_huntley@kindermorgan.com | 9312153680 | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | ON MAY 11, 2020, A LOOSE WIRE ON THE PLC TERMINAL CAUSED A LOSS OF POWER TO THE SAFETY PLC, INITIATING AN ESD AT TENNESSEE GAS PIPELINE'S STATION 106 IN CLAY CITY, KY. THE VOLUME OF GAS VENTED TO ATMOSPHERE WAS BELOW THE PHMSA REPORTABLE THRESHOLD OF 3,000 MCF. HOWEVER, TGP PERSONNEL DISCOVERED LATER THAT DAY THAT A MIST OF COMPRESSOR LUBRICATING OIL AND PIPELINE DISTILLATE WAS RELEASED WITH THE NATURAL GAS. WIND CAUSED THE MIST TO TRAVEL TO SURROUNDING PROPERTIES RESULTING IN A VERY LIGHT COATING ON RESIDENCES. THE NEXT DAY, MAY 12, 2020, IT WAS DETERMINED THAT THE COST OF CLEAN-UP WOULD EXCEED THE PHMSA REPORTABLE AMOUNT OF $50,000 AND THE OCCURRENCE WAS REPORTED TO THE NRC AS A PIPELINE INCIDENT. CLEAN-UP WAS COMPLETED LATER THAT SAME WEEK. A 48-HOUR UPDATE WAS PROVIDED TO THE NRC ON MAY 14, 2020, REPORT #1277250. THIS OCCURRENCE WAS ONLY REPORTABLE AS A PHMSA INCIDENT BECAUSE OF THE COST OF CLEAN-UP OF SURROUNDING PROPERTIES.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200060 | 33900 | 2020-06-13 00:37 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2020-05-14 16:20 | 2020 | PACIFIC | YES | 35.6444 | -119.2766 | 1277298 | 2020-05-14 19:57 | 1277427 | NATURAL GAS |  | 8230 | 1690 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-05-15 09:00 | 2020-05-16 04:04 |  |  |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-05-15 09:00 | VALVE CLOSURE |  | 2020-05-15 09:00 | 0 | 2020-05-14 16:20 | 2020-05-14 17:45 | ONSHORE | CA | 93280 | WASCO | KERN | MILEPOST | 14.73 | LINE 7000 | MILE POST 14.73 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 4 | NO | YES | [6 empty] | YES | UNCASED | POSO CREEK | UNKNOWN | SHORELINE/BANK/MARSH CROSSING | NO | [10 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 | NO | 0.25 | 46000 | API 5L | OTHER | UNKNOWN | UNKNOWN | COAL TAR |  | YES | [26 empty] | 1964 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 3 | 0.4 | [7 empty] | CLASS 1 LOCATION | NO |  | 296 |  | NO | NO |  |  | 0 | 0 | 3938 | 3938 | 19176 | 19176 | 600000 | 600000 | 1000000 | 1000000 | 0 | 0 |  | 2.33 | 1623114 | 756130.494764941 | 1623114 | 0 | 0 | 2 | 33 | NO |  |  |  | 610 | 44000 | 718 | 192.619(A)(2) |  | 2018-05-21 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 37700 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD-PARTY EXCAVATION DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [7 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SITE DEVELOPMENT | NO | [5 empty] | YES | 24 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | ALI MATIN | PIPELINE SAFETY AND COMPLIANCE ADVISOR | amatin@socalgas.com | 909-919-0463 |  |  |  |  | ALI MATIN | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 909-919-0463 | amatin@socalgas.com | ON MAY 14, 2020, SOUTH VALLEY FARMS DAMAGED A 16-INCH STEEL TRANSMISSION LINE WHILE OPERATING A FRONT-END LOADER OVER THE PIPELINE. SOCALGAS CREWS RESPONDED, CONTROLLED THE GAS BY OPERATING MAIN LINE VALVES, AND BLEW DOWN THE LINE TO ASSESS DAMAGES. THERE WERE NO INJURIES OR FURTHER DAMAGE RESULTING FROM THIS INCIDENT. THE 16-INCH MAIN WAS REPAIRED BY WELDING TWO WEDDING BANDS. INVESTIGATION OF THE INCIDENT SHOWED THAT THERE WAS NO VALID USA TICKET FOR THE CONTRACTOR AND NO STANDBY WAS PRESENT DURING THE EXCAVATION ACTIVITY NEAR THE TRANSMISSION LINE. THIS INCIDENT WAS REPORTED TO DOT AND CPUC DUE TO GAS RELEASE AND ESTIMATED PROPERTY DAMAGE OF $50,000 OR MORE. FOR ANY FURTHER QUESTIONS, CONTACT ALI MATIN AT (909) 919-0463.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200061 | 33919 | 2020-06-17 19:31 | ORIGINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2020-05-19 19:25 | 2020 | CENTRAL | YES | 29.5218 | -89.7206 | 1277681 | 2020-05-19 23:28 | 1277804 | NATURAL GAS |  | 448 | 1261 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-05-19 22:30 |  | YES | YES | OPERATOR | 2020-05-19 23:21 | NO | [5 empty] | VALVE CLOSURE |  | 2020-05-19 22:30 | VALVE CLOSURE |  | 2020-05-19 22:30 | 0 | 2020-05-19 22:42 | 2020-05-20 12:34 | ONSHORE | LA | 70082 | PORT SULPHUR | PLAQUEMINES | MILEPOST | 527-1 + 0.675 | TGP 500 SYSTEM | 500-1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | INVESTIGATION STILL ONGOING |  | NO | YES | [6 empty] | YES | UNCASED | MISSISSIPPI RIVER | 98 | BELOW WATER, PIPE BURIED BELOW BOTTOM (NOT IN BORED/DRILLED CROSSING) | YES | [10 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 | NO | 0.656 | 52000 | API-5LX | DSAW |  | NATIONAL TUBE | OTHER | SOMASTIC | NO | [26 empty] | 1959 | 1959 | CARBON STEEL |  | LEAK |  |  | OTHER | INVESTIGATION STILL ONGOING | [5 empty] | CLASS 1 LOCATION | NO |  | 695 |  | NO | NO |  |  | 0 | 0 | 2333 | 2333 | 829 | 829 | 0 | 0 | 0 | 0 | 0 | 0 | REPAIR COSTS STILL UNKNOWN. | 1.85 | 3162 | 1930.37050273793 | 3162 | 0 | 0 | 0 | 0 | NO |  |  |  | 814 | 7000 | 1000 | 192.619(A)(2) |  | 1959-11-02 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | REMOTELY CONTROLLED | 5064 | YES | [7 empty] | YES |  |  |  |  | YES | IDENTIFIED EXPOSURE MAY LIMIT ILI RUN | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WAS NO INDICATION THAT ANY ACTIONS ON THE PART OF THE CONTROLLER CONTRIBUTED TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [146 empty] | JORGE LOPEZ | MANAGER ENGINEERING - CODES AND COMPLIANCE | jorge_lopez@kindermorgan.com | 701-609-6218 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR ENGINEERING - CODES AND COMPLIANCE | 281-384-5609 | jaime_hernandez@kindermorgan.com | AT APPROXIMATELY 7:55 PM ON 5/19/2020, KINDER MORGAN RECEIVED AN EMAIL FROM PHMSA. IT STATED THAT A PRIVATE CITIZEN REPORTED TO THE NRC, THAT THERE WERE BUBBLES IN THE RIVER NEAR THE TENNESSEE GAS PIPELINE COMPANY (TGP) - 500 SYSTEM LINES, LOCATED IN PLAQUEMINES PARISH, LOUISIANA, ON THE EASTERN SIDE OF THE MISSISSIPPI RIVER. TGP OPERATIONS PERSONNEL STARTED THE GAS LEAK INVESTIGATION. AT 10:30 PM, TGP CONFIRMED THE GAS LEAK ON LINE 500-1 AND STARTED THE EMERGENCY RESPONSE LINE (ERL) PROTOCOL. THE LINE WAS ISOLATED AND BLOWN DOWN. TGP CONSULTED WITH A DIVE COMPANY TO SURVEY LINE 500-1. HOWEVER, THE CURRENT RIVER CONDITIONS PREVENTS THE DIVER FROM SAFELY REACHING AND ASSESSING THE LEAK. GIVEN THESE CONDITIONS ON 5/27/2020, TGP HIRED T BAKER SMITH (TBS) TO PERFORM A SONAR SURVEY TO MAP THE LEAK LOCATION. ON 6/15/2020, TGP RECEIVED THE FINAL REPORT FROM TBS. THE INITIAL ASSESSMENT SHOWED UNSUPPORTED PIPE EXPOSURE. THIS EXPOSURE COULD LIMIT THE RUNNING OF A ILI ASSESSMENT IN ITS CURRENT STATE AS NOTED IN SECTION E8. TGP IS ASSESSING THE DATA IN ORDER TO ESTABLISH A PATH FORWARD. THE LINE WILL REMAIN ISOLATED AND SHUT DOWN UNTIL REPAIRS CAN BE MADE. TGP CONTINUES ITS INVESTIGATION AND WILL PROVIDE SUPPLEMENTAL REPORTS AS UPDATES ARE OBTAINED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200062 | 33921 | 2020-06-18 09:57 | ORIGINAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2020-05-22 00:43 | 2020 | EASTERN | YES | 38.7076 | -82.8533 | 1277824 | 2020-05-22 02:54 | 1277962 | NATURAL GAS |  | 2920 | 49 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-05-22 03:06 | 2020-05-24 12:04 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-05-22 03:06 | VALVE CLOSURE |  | 2020-05-22 03:06 | 11 | 2020-05-22 00:43 | 2020-05-22 01:54 | ONSHORE | OH | 45694 | WHEELERSBURG | SCIOTO | SURVEY STATION NO. | 00+00 | LINE R-688 | R688-001 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 2 | NO | 0.154 | 35000 | TYPE B | SEAMLESS |  | UNKNOWN | PAINT |  | YES | [26 empty] | 1986 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | DUE TO A CAR ACCIDENT 2-INCH PIPE WAS BROKEN | CLASS 3 LOCATION | NO |  | 86 |  | NO | NO |  |  | 19000 | 19000 | 78 | 78 | 4643 | 4643 | 500000 | 500000 | 0 | 0 | 64000 | 64000 | DOWNSTREAM CUSTOMERS GAS RELIGHT | 1.59 | 587721 | 272461.796505527 | 587721 | 0 | 0 | 200 | 13 | NO |  |  |  | 130 | 361 | 225 | 192.619(A)(2) |  | 1986-05-06 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 18400 | NO | [5 empty] | YES | THIS A 2-INCH SHORT STUB LATERAL LINE. | YES |  | YES |  |  |  |  | TRANSMISSION SYSTEM | NO |  |  |  |  | OTHER | COLUMBIA GAS OF OHIO (COH), THE LOCAL DISTRIBUTION COMPANY |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [9 empty] | UNKNOWN | [5 empty] | UNKNOWN |  | YES | PASSENGER CAR | ROADWAY | 25 | YES |  |  | YES | [235 empty] | KAMRAN ROSTAMI ASRABADI | COMPLIANCE SPECIALIST | kamran_rostami@tcenergy.com | (304)357-2351 |  | KAMRAN ROSTAMI ASRABADI | kamran_rostami@tcenergy.com | (304)357-2351 | PAUL SHAFFER | US REGULATORY COMPLIANCE MANAGER EAST | (304)550-4866 | paul_shaffer@tcenergy.com | ON MAY 22, 2020, AT 00:19 EASTERN DAYLIGHT TIME (EDT), A COLUMBIA GAS TRANSMISSION, LLC (COMPANY) PIPELINE MECHANIC (TECH) RECEIVED A CALL FROM COMPANY MONITORING CENTER REGARDING A PRESSURE DROP AT DOGWOOD RIDGE MEASURING STATION (MS) 713550 THAT WAS REPORTED BY COLUMBIA GAS OF OHIO, THE LOCAL DISTRIBUTION COMPANY. OPERATIONS PERSONNEL WAS DISPATCHED AND ARRIVED ON SITE AT 01:54 EDT WHERE HE CONFIRMED THAT THERE WAS AN UNINTENDED RELEASE OF NATURAL GAS DUE TO A VEHICLE THAT DAMAGED THE ABOVE GROUND PIPELINE. AT 03:06 EDT, THE UNINTENDED RELEASE OF NATURAL GAS WAS ISOLATED, AND AT 03:20 LINE R-688 WAS BLOWN DOWN AND THE FACILITY WAS ISOLATED AND REMOVED FROM SERVICE. ON MAY 24, 2020 LINE R-688 WAS RETURNED BACK INTO SERVICE. THE INITIAL NATIONAL RESPONSE CENTER (NRC) REPORT NO.1277824 AND THE NRC 48-HOUR REPORT NO.1277962 HAVE BEEN CALLED-IN ON MAY 22ND AND MAY 23RD RESPECTIVELY.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200063 | 33922 | 2020-06-18 11:44 | ORIGINAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 STATE ROUTE 56; BOX 20010 | OWENSBORO | KY | 42301 | 2020-05-24 15:00 | 2020 | CENTRAL | YES | 38.4705 | -96.2835 | 1278002 | 2020-05-24 15:25 | 1278122 | NATURAL GAS |  | 12513 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-05-24 13:25 | 2020-05-24 14:10 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-05-24 13:25 | VALVE CLOSURE |  | 2020-05-24 13:56 | 0 | 2020-05-24 13:25 | 2020-05-24 13:45 | ONSHORE | KS | 66835 | Not Within a Municipality | LYON | SURVEY STATION NO. | 100/591 | AMERICUS COMPRESSOR STATION | 181-02-001 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1962 | 1961 | CARBON STEEL |  | OTHER | [8 empty] | DURING ESD OF THE AMERICUS COMPRESSOR STATION, THE STATION ISOLATION GATE VALVE #32 FAILED TO CLOSE ALLOWING MAINLINE GAS TO VENT DURING THE STATION BLOW-DOWN | CLASS 1 LOCATION | NO |  | 538 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 20271 | 20271 | 400 | 400 | 0 | 0 | 0 | 0 |  | 1.62 | 20671 | 21199.4766964654 | 20671 | 0 | 0 | 0 | 0 | NO |  |  |  | 833 | 322134 | 900 | 192.619(C) |  | 1970-01-25 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | AUTOMATIC | AUTOMATIC | 1000 | NO | YES |  |  |  |  | YES | COMPRESSOR STATION LINE | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE AUTOMATIC ESD WAS TRIGGERED AND THE UNINTENTIONAL GAS RELEASE BECAUSE THE ISOLATION VALVE DID NOT CLOSE, THE CONTROLLER WAS NOT AT FAULT. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [204 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | [5 empty] | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | ERIC GLAHN | PIPELINE COMPLIANCE ENGINEER | eric.glahn@southernstar.com | 2708524414 | 2708525016 | CRAIG THOMAS | craig.thomas@southernstar.com | 2708524435 | SHAWN PATTERSON | VP AND CHIEF OPERATIONS OFFICER | 2708524670 | shawn.patterson@southernstar.com | ON 5/24/2020 AT 1:25 PM CDT SOUTHERN STAR CENTRAL GAS PIPELINE (SSCGP) OPERATIONS RECEIVED NOTICE THE AMERICUS COMPRESSOR STATION WENT INTO AN ESD CONDITION DUE TO A FIRE DETECTION EYE INDICATING "LATCHED". RESOURCES ARRIVED ON SITE AT 1:45 PM AND NOTICED GAS WAS STILL BEING VENTED AT THE DISCHARGE STACK. IT WAS DETERMINED THAT THE STATION ISOLATION VALVE #32 LOCATED ON THE STATION DISCHARGE LINE DID NOT CLOSE. IT WAS DETERMINED THAT THE ISOLATION VALVE DID NOT CLOSE DUE TO THE POWER GAS TO THE VALVE BEING SHUT OFF. POWER GAS WAS TURNED ON AND THE ISOLATION VALVE WAS CLOSED AT 1:56 PM STOPPING THE GAS RELEASE. IT WAS DETERMINED THAT ALL EQUIPMENT WAS OPERATIONAL AND UNDAMAGED AND THE STATION WAS RETURNED TO SERVICE AT 2:10 PM ON 5/24/2020. AT 3:00 PM IT WAS DETERMINED THAT THE GAS LOSS EXCEEDED THE REPORTABLE THRESHOLD AND THE NRC WAS NOTIFIED AT 3:25 PM. FURTHER INVESTIGATION DETERMINED THAT THE POWER GAS WAS SHUT OFF DURING MAINTENANCE AND NOT REOPENED. SSCGP CONDUCTED CORRECTIVE ACTION TRAINING TO REMIND ALL PERSONNEL TO KEEP POWER GAS ACTIVE TO ISOLATION VALVES AND REMINDER FOR LOCKOUT/TAGOUT FOR POWER GAS SUPPLY LINES FOR MAINTENANCE TO ENSURE POWER GAS IS RETURNED AFTER MAINTENANCE ACTIVITIES.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200064 | 34002 | 2020-06-18 16:57 | SUPPLEMENTAL FINAL | 18152 | SEA ROBIN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-05-17 17:21 | 2020 | CENTRAL | YES | 28.8528 | -92.0271 | 1277657 | 2020-05-19 14:06 | 1277765 | NATURAL GAS |  | 354 | 22692 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-05-18 07:40 | 2020-05-22 18:12 |  |  |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-05-18 07:40 | VALVE CLOSURE |  | 2020-05-18 08:00 | 0 | 2020-05-17 17:21 | 2020-05-19 12:00 | OFFSHORE | [6 empty] | SEA ROBIN PIPELINE | LINE 702 #3334 | [20 empty] | 90 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | SOUTH MARSH ISLAND | 26 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 26 | NO | 0.5 | 60000 | API 5LX | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | SAW CRISPIN (S.V.) DUNKERQUE, FRANCE | OTHER | CONCRETE WITH SOMASTIC | NO | [26 empty] | 1970 | 1970 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 634 |  | NO | NO |  |  | 0 | 0 | 36307 | 36307 | 566 | 566 | 252639 | 252639 | 25000 | 25000 | 0 | 0 |  | 1.6 | 314512 | 144696.295940844 | 314512 | 0 | 0 | 0 | 0 | NO |  |  |  | 775 | 11000 | 1250 | 192.619(A)(2) |  | 1970-03-10 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 122364 | NO |  |  | YES | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A SMALL PINHOLE LEAK. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | PINHOLE LEAK. |  |  |  |  | YES | LOW FLOW. |  |  | YES | HISTORICAL DATA. |  |  |  |  | YES | LEAK LOCATED AT THE 6 O'CLOCK POSITION. | YES | NO | YES | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | TODD NARDOZZI | DIRECTOR - REGULATORY COMPLIANCE | todd.nardozzi@energytransfer.com | 713-989-7126 | 877-917-0448 |  |  |  | TODD NARDOZZI | SR. MANAGER - DOT COMPLIANCE | 713-989-7126 | todd.nardozzi@energytransfer.com | SUNDAY, MAY 17, 2020 LATE AFTERNOON OPERATIONS WAS CONTACTED ABOUT BUBBLES IN THE SMI 27 AREA, NEAR TWO OF THE SEA ROBIN WEST PIPELINES. IN TALKING TO THE USCG, BOTH A PRODUCER AND BSEE CALLED IN THE REPORTED BUBBLES BUT WERE UNABLE TO OFFER COORDINATES. SEVERAL ATTEMPTS WERE MADE TO CONTACT THE NRC BUT NO ONE ANSWERED THE HOTLINE. DUE TO THE TIME OF DAY AND WEATHER WE WERE UNABLE TO MAKE A FLIGHT AT THAT TIME. MONDAY, MAY 18, 2020 OUR OVERFLIGHT THIS MORNING CONFIRMS BUBBLES AND A DARK COLORED SHEEN ARE PRESENT. CURRENTS ARE STRONG BUT COORDINATES DO INDICATE IT IS LIKELY TO BE OUR LINE, ALTHOUGH RESPONSIBILITY CANNOT BE CONFIRMED AS OF YET. GIVEN ASSET HISTORY WE ARE GOING TO ISOLATE THE 26" LINE 702 ON BOTH ENDS AND MONITOR PRESSURE. WE WILL ALSO BEGIN SOURCING A DSV TO MAKE AN INVESTIGATION DIVE FOR US AS SOON AS POSSIBLE. THE AFTERNOON OVERFLIGHT HAS SEEN THE SAME AMOUNT OF BUBBLES, BUT NO SHEEN. THE NRC NUMBER WE WERE GIVEN IS1277495; WE HAVE NOT TAKEN RESPONSIBILITY FOR THE LEAK AS WE HAVE YET TO CONFIRM SOURCE. A DSV HAS BEEN IDENTIFIED AND IS EXPECTED TO BE ON LOCATION MID-DAY TOMORROW TO INVESTIGATE. TUESDAY, MAY 19, 2020 THE DSV AND OUR OVERFLIGHT REPORT BUBBLES WITH NO SHEEN PRESENT. THE DSV USED A MESOTECH TO TAKE A SONAR SHOT OF THE LEAK, IT APPEARS TO BE ON THE 26" LINE. WE ARE ALSO IN THE PROCESS OF TAKING THE LINE DOWN TO BOTTOM PRESSURE. GIVEN WE KNOW THE LINE IS OURS WE HAVE UPDATED THE NRC WITH A NEW INCIDENT NUMBER OF 1277657. WEDNESDAY, MAY 20, 2020 OVERFLIGHT AND THE DSV BOTH BUBBLES BUT NO SHEEN AS OF NOW. THE LINE PRESSURE CONTINUES TO DROP AND IS NEAR ENOUGH TO BOTTOM PRESSURE THAT OUR FIRST DIVER IS JETTING THE AREA NOW. ONCE WE ARE AT BOTTOM PRESSURE AND ARE DONE JETTING THE DIVER CAN INSPECT THE LINE THAT WILL TELL US FAILURE METHOD AND REPAIR APPROACH. THE DSV IS STAFFED TO WORK 24 HOURS SO WE WILL CONTINUE TO MAKE PROGRESS OVERNIGHT. USCG HAS BEEN UPDATED EARLIER TODAY. DIVERS ARE REPORTING THE LEAK IS IN THE 6 O'CLOCK POSITION OF THE LINE. PLANS OVERNIGHT ARE TO FINISH REDUCING PRESSURE TO MATCH BOTTOM, COMPLETE THE MASTIC REMOVAL AND UT THE AREA OF THE LEAK TO EVALUATE PIPE FOR A LEAK CLAMP REPAIR. THE NRC WAS UPDATED EARLIER TODAY, WHICH SATISFIES THE PHMSA 48 HOUR UPDATE NRC # 1277765. THURSDAY, MAY 21, 2020 AS OF 3:26PM LEAK CLAMP HAS BEEN INSTALLED CURRENTLY IN THE PROCESS OF BRINGING THE PRESSURE UP TO THE FIRST CHECKPOINT. OVERFLIGHTS INDICATE THERE HAS BEEN NO SHEEN ASSOCIATED WITH THIS EVENT. THE USCG HAS BEEN UPDATED AS TO PROGRESS. 6:12PM ALL PRESSURE CHECKS AND OVERFLIGHTS ARE COMPLETE, WITH NO SIGNS OF ANY LEAKS. THE SEGMENT IS AT LINE PRESSURE AND HAS BEEN RETURNED TO SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200065 | 34502 | 2020-06-19 09:15 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2020-05-19 12:46 | 2020 | EASTERN | NO | 44.7702 | -85.0746 | 1277651 | 2020-05-19 14:33 | 1277764 | NATURAL GAS |  | 26.5 | 2156 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-05-19 13:20 |  | YES | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-05-19 13:50 | NO | [11 empty] | 0 | 2020-05-19 12:46 | 2020-05-19 13:19 | ONSHORE | MI | 49646 | EXCELSIOR TOWNSHIP | KALKASKA | NOT APPLICABLE |  | EXCELSIOR 6 COMPRESSOR STATION | ANR STORAGE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | PIPE | PIPE SEAM | 20 |  | 0.375 | 60000 | API-5L PLS2 X60 | LONGITUDINAL ERW - HIGH FREQUENCY |  | SALZGITTER MANNESMANN LINE PIPE | PAINT |  | YES | [26 empty] | 2018 | 2017 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 62.8 | 62.8 |  | CLASS 1 LOCATION | NO |  | 467 |  | NO | NO |  |  | 0 | 0 | 3751 | 3751 | 46 | 46 | 400000 | 400000 | 0 | 0 | 0 | 0 |  | 1.74 | 403797 | 185380.052998807 | 403797 | 0 | 0 | 0 | 0 | NO |  |  |  | 2961 | 0 | 1050 | 192.619(A)(1) |  | 2018-09-22 | NO | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 | NO |  |  | NO | [19 empty] | TRANSMISSION IN STORAGE FIELD | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) | [5 empty] | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [16 empty] | YES | [176 empty] | ROBERTA PRIMERA | COMPLIANCE SPECIALIST | roberta_primera@tcenergy.com | 248-561-7803 |  |  |  |  | LEE ROMACK | DIRECTOR PIPELINE REGULATOR COMPLIANCE | 832-320-5315 | lee_romack@tcenergy.com | A ROOT CAUSE FAILURE ANALYSIS (RCFA) FINAL REPORT, WHICH INCORPORATED THE FINDINGS FROM THE MECHANICAL AND METALLURGICAL TESTING REPORT SUMMARIZED THE EVENT AS, "... A RUPTURE OF FACILITY PIPING ON THE SHELL SIDE OF THE GAS-GAS HEAT EXCHANGER (E-2053) LEADING TO THE EJECTION OF PROCESS PIPING AS WELL AS THE RELEASE OF NATURAL GAS TO THE ENVIRONMENT. CAUSAL FACTORS WERE RECOGNIZED FOR THE EVENT SEQUENCES PERTAINING TO (1) A NATURAL GAS LEAK FROM THE HIGH PRESSURE INJECTION HEADER TO LOWER PRESSURE PROCESS PIPING THROUGH ISOLATION VALVE XV-2070 AND XV-2071 AND (2) INADEQUATE SAFETY SYSTEMS IN THE SHELL SIDE OF THE HEAT EXCHANGER LOOP TO PREVENT RUPTURE OF THE LOWER MAOP PIPING." METALLURGICAL LAB COMPLETED THE FAILURE ANALYSIS OF THE FRACTURED PIPING AND CONCLUDED THAT THE RUPTURE OF THE SHELL SIDE PIPING WAS CAUSED BY DUCTILE OVERLOAD FROM PIPE OVER-PRESSURIZATION. CAUSAL FACTORS WERE IDENTIFIED AS: LEAKING ISOLATION VALVES; INADEQUATE DESIGN-NO OVERPRESSURE PROTECTION OR ALARMS; NO POSITIVE ISOLATION OF SHELL SIDE LOOP. BASED ON THE RCFA, RECOMMENDATIONS AND POTENTIAL IMPROVEMENT OPPORTUNITIES IDENTIFIED, CORRECTIVE ACTIONS HAVE BEEN ASSIGNED TO ADDRESS EACH CONTRIBUTING FACTOR.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200066 | 33954 | 2020-06-26 08:48 | ORIGINAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2020-05-30 21:06 | 2020 | CENTRAL | YES | 35.6919 | -100.2275 | 1278467 | 2020-05-30 23:30 | 1278559 | NATURAL GAS |  | 16100 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | RELIEF VALVE WAS ISOLATED. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-05-30 21:06 | 2020-05-30 23:00 | ONSHORE | TX | 79011 | BRISCOE | HEMPHILL | NOT APPLICABLE |  | WOODALL PLANT YARD | AD-23 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1978 | 1978 | CARBON STEEL |  | OTHER | [8 empty] | PREMATURE GAS RELEASE. | CLASS 1 LOCATION | NO |  | 175 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 28175 | 28175 | 500 | 500 | 1000 | 1000 | 0 | 0 |  | 1.75 | 29675 | 29898.8414175194 | 29675 | 0 | 0 | 0 | 0 | NO |  |  |  | 973 | 2000 | 1000 | 192.619(A)(2) |  | 2012-03-30 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | SETPOINT ON PILOT VALVE. | [147 empty] | YES | [13 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  | CASEY ROBERTS | casey.roberts@enablemidstream.com | 4055584647 | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | ON MAY 3OTH , AT 21:06, ENABLE SYSTEM CONTROL RECEIVED A CALL FROM A LANDOWNER NEAR THE WOODALL PLANT THAT A RELIEF VALVE WAS GOING OFF ON LINE AD-23 IN HEMPHILL COUNTY, TEXAS. A O&M TECHNICIAN WAS DISPATCHED TO THE METER LOCATION AND BACKED OFF THE RELIEF VALVE, LOCKED IT OUT, AND RESET IT. APPROXIMATELY 16.1 MMCF OF NATURAL GAS WAS RELEASED. NO INJURIES, NO DAMAGE TO COMPANY PROPERTY. NRC WAS NOTIFIED ON 5/30 (#1278467) AND A 48HR. FOLLOW UP ON 6/1 (#1278559). UPON INVESTIGATION, IT WAS DETERMINED THE SETPOINT HAD LOWERED TO 973 PSIG ON THE PILOT VALVE. THE VALVE WAS INSPECTED AND SET AT 996 PSIG ON MAY 5TH 2020. LINE AD-23 HAS A 1000 PSIG MAOP AND WAS OPERATING AROUND 975 AT THE TIME. ON MAY 31ST, THE PILOT WAS RESET TO THE PROPER SETPOINT (996 PSIG) AND PLACED BACK INTO SERVICE. A SIMILAR INCIDENT OCCURRED IN 2018 WITH THIS RELIEF VALVE AND A LOWER SETPOINT. LINE AD-23 ROUTINELY OPERATES AT THE 975 PSIG RANGE. A STUDY IS CURRENTLY BEING CONDUNCTED TO DETERMINE IF THE 400 SERIES RELIEF SHOULD BE REPLACED WITH A 200 SERIES TO LIMIT THIS OCCURRENCE FROM HAPPENING AGAIN.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200067 | 34153 | 2020-06-28 13:38 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | ONE ENERGY PLAZA | DETROIT | MI | 48226 | 2020-05-27 07:41 | 2020 | EASTERN | NO | 42.5419 | -83.5606 | 1278180 | 2020-05-27 07:41 |  | NATURAL GAS |  | 12000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | IDLE | [5 empty] | NO |  |  | NO | [11 empty] | 0 | 2020-05-27 03:24 | 2020-05-27 04:36 | ONSHORE | MI | 48381 | MILFORD | OAKLAND | MILEPOST | 1009 | MILFORD COMPRESSOR STATION | 1009 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2017 | 2017 | CARBON STEEL |  | OTHER | [8 empty] | UNINTENTIONAL RELEASE OF GAS THROUGH COMPRESSOR ESD VENT. UPSTREAM PIPELINE VALVE 1009 FAILED OPEN CAUSING RELEASE OF APPROXIMATELY 12 MMCF. | CLASS 3 LOCATION | NO |  | 600 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 19560 | 19560 | 125 | 125 | 100 | 100 | 0 | 0 |  | 1.63 | 19785 | 20382.0210945177 | 19785 | 0 | 0 | 0 | 0 | NO |  |  |  | 638 | 0 | 1000 | 192.619(A)(1) |  | 2018-10-29 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS CONTROL RESPONDED TO THE ALARM IDENTIFYING THAT THE VENT VALVE WAS OPEN AND TOOK THE APPROPRIATE ACTIONS AND MADE THE NECESSARY NOTIFICATIONS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | SOLENOID FAILURE CAUSED VENT VALVE TO OPEN AND RELEASED GAS. | [22 empty] | YES | SOLENOID FAILURE CAUSED VENT VALVE TO OPEN AND RELEASED GAS. | [161 empty] | FRENAE F. SMITH | MANAGER CODES AND STANDARDS | frenae.smith@dteenergy.com | 313-389-7762 |  |  |  |  | FRENAE F. SMITH | MANAGER CODES AND STANDARDS | 313-389-7762 | frenae.smith@dteenergy.com | DTE GAS (GAS CONTROL) RESPONDED TO A RELEASE OF NATURAL GAS AT THE MILFORD COMPRESSOR STATION ON 5/27/2020 AT APPROXIMATELY 03:24. NATURAL GAS BLEW FOR 1 HOUR AND 12 MINUTES. A TECHNICIAN ARRIVED ON SITE AT APPROXIMATELY 04:26. THE MILFORD TECHNICIAN FOUND VENT VALVE 1009 OPEN AND BLOWING. THE TECH CLOSED THE MANUAL VALVE TO THE BLOWDOWN STACK DOWNSTREAM OF 1009 TO STOP THE RELEASE AND THEN MANUALLY CLOSED VALVE 1009. THIS VALVE SERVES PLANT 1 WHICH WAS NOT OPERATING. AFTER CALCULATING THE AMOUNT OF LOST GAS, IT WAS DETERMINED THAT THIS WAS A REPORTABLE GAS RELATED INCIDENT. UPON FURTHER INVESTIGATION BY MILFORD AND CONTROL MAINTENANCE, IT WAS DETERMINED THE SOLENOID FOR VALVE 1009 WHICH KEEPS THE VALVE CLOSED DURING NORMAL OPERATION SHORTED OUT AND FAILED CAUSING THE VALVE TO OPEN. ADDITIONAL SOLENOIDS WERE REMOVED FROM ALL 6 VENT VALVES AT MILFORD AND RECONNECT THE ESD POWER AND PILOT GAS FOR TRADITIONAL NON- ELECTRONIC OPERATION. THIS WAS COMPLETED ON WEDNESDAY, MAY 27, 2020.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200068 | 34838 | 2020-06-30 18:51 | SUPPLEMENTAL FINAL | 2879 | AMERICAN MIDSTREAM (LOUISIANA INTRASTATE), LLC | BLACK BEAR TRANSMISSION, LLC 1501 MCKINNEY, SUITE 800 | HOUSTON | TX | 77010 | 2020-05-29 15:31 | 2020 | CENTRAL | YES | 29.7698 | -90.0296 | 1278400 | 2020-05-29 17:48 | 1278551 | NATURAL GAS |  | 869 | 214 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-05-29 17:00 | 2020-06-20 11:15 |  | YES | OPERATOR | 2020-05-29 16:15 | NO | [5 empty] | VALVE CLOSURE |  | 2020-05-29 17:00 | VALVE CLOSURE |  | 2020-05-29 17:00 | 5 | 2020-05-29 16:00 | 2020-05-29 16:30 | ONSHORE | LA | 70037-0000 | BELLE CHASE | PLAQUEMINES |  |  | GLORIA-CHEVRON OAK PT 6-INCH PIPELINE | GLORIA-CHEVRON OAK PT 6-INCH PIPELINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 57 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 | NO | 0.28 | 42000 | X-42 | SEAMLESS |  | UNKNOWN | EPOXY |  | YES | [26 empty] | 2000 | 2000 | CARBON STEEL |  | MECHANICAL PUNCTURE | 1 | [8 empty] | CLASS 3 LOCATION | YES | METHOD1 | 157 |  | NO | NO |  |  | 0 | 0 | 636 | 636 | 2581 | 2581 | 69084 | 69084 | 5633 | 5633 | 12335 | 12335 | PERMITTING, ACCESS FEES, TRAFFIC SOLUTIONS, ENGINEERING SUPPORT, NDE SERVICES | 2.97 | 90269 | 42926.9457035997 | 90269 | 0 | 0 | 3 | 0 | NO |  |  |  | 550 | 550 | 989 | 192.619(A)(2) |  | 2006-10-19 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | NO | MANUAL | MANUAL | 26400 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY EXCAVATION ACTIVITY. LINE WAS HIT AFTER A ONE CALL WAS NOT CALLED IN FOR WORK BEING COMPLETED ON MAY 29TH 2020. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO |  |  |  |  | NO |  |  |  |  | NO | YES | STATE HIGHWAY |  |  |  |  | YES |  |  |  |  | CONTRACTOR | DIRECTIONAL DRILLING | UNKNOWN/OTHER | NO | [5 empty] | YES | 592 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | TODD RIVERA | SR MANAGER OFFSHORE EHS AND TRAINING | trivera@3cmidstream.com | 346-241-3663 |  |  |  |  | TODD RIVERA | SR MANAGER OFFSHORE EHS AND TRAINING | 3462413663 | trivera@3cmidstream.com | REVISED 2-10-2021 BY AMERICAN MIDSTREAM (LOUISIANA INTRASTATE), LLC. 3CM RECEIVED A CALL AT 1750 HOURS FROM BEVERLY CONSTRUCTION CO., LLC (BEVERLY CONSTRUCTION) STATING THAT THEIR SUBCONTRACTOR, MIXSON BORING, WAS CONDUCTING BORING ACTIVITY AND STRUCK OUR LINE AS THEY WERE RETRIEVING A CASING ACROSS HIGHWAY 23. BEVERLY CONSTRUCTION WAS ORIGINALLY SUPPOSED TO CONDUCT THE DIRECTIONAL DRILLING OPERATIONS ALONG E. OAK GROVE LN. BEVERLY CONSTRUCTION HAD SUBMITTED A ONE CALL TICKET FOR THE DIRECTIONAL DRILLING; HOWEVER, AT A LATER DATE BEVERLY CONSTRUCTION SUBCONTRACTED MIXSON BORING TO COMPLETE THE DIRECTIONAL DRILLING. THE 6-INCH PIPELINE WAS PROPERLY MARKED BY 3CM AFTER THE ONE CALL TICKET WAS RECEIVED FROM BEVERLY CONSTRUCTION, BUT DUE TO THE TIME LAPSE ON BEVERLY GETTING STARTED THEIR ONE CALL TICKET HAD EXPIRED AND A NEW TICKET WAS REQUIRED. TO 3CM'S KNOWLEDGE, MIXSON BORING DID NOT SUBMIT A ONE CALL TICKET PRIOR TO BEGINNING DIRECTIONAL DRILLING OPERATIONS. WITH THAT SAID, THIS INCIDENT WAS PREVENTABLE AND MIXSON BORING & BEVERLY CONSTRUCTION ARE THE LIABLE PARTY AS THEY STRUCK THE 6-INCH NATURAL PIPELINE WHILE CONDUCTING DIRECTIONAL DRILLING OPERATIONS. THE FIRST DROP IN PRESSURE WAS IDENTIFIED AT 1531 AND THE INCIDENT WAS IDENTIFIED AS REPORTABLE AT 1632. THE NOTIFICATION WAS MADE AT 1748 TO THE NATIONAL RESPONDER CENTER.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200069 | 33981 | 2020-06-30 19:34 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2020-06-04 14:27 | 2020 | EASTERN | YES | 38.2857 | -83.4015 | 1278874 | 2020-06-04 17:21 | 1278946 | NATURAL GAS |  | 11029.8 | 0 | 0.6 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-06-04 14:45 | 2020-06-05 00:38 |  | NO |  |  | NO | [11 empty] | 0 | 2020-06-04 14:20 | 2020-06-04 14:32 | ONSHORE | KY | 40351 | MOREHEAD | ROWAN | NOT APPLICABLE |  | LINE 100-7 | VALVE 1D7 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2020 | 2016 | CARBON STEEL |  | OTHER | [8 empty] | GAS WAS RELEASED THROUGH THE STATION BLOW DOWN SILENCER. | CLASS 2 LOCATION | NO |  | 458 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 17648 | 17648 | 450 | 450 | 500 | 500 | 4221 | 4221 | CLEAN-UP OF OIL MIST RESIDUE. | 1.6 | 22819 | 20670.1083859445 | 22819 | 0 | 0 | 0 | 0 | NO |  |  |  | 501 | 171000 | 765 | 192.619(A)(2) |  | 1964-12-28 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM WAS NOT A CONTRIBUTING FACTOR IN THE EVENT. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | [204 empty] | EQUIPMENT NOT INSTALLED PROPERLY | [5 empty] | YES |  |  | OTHER MAINTENANCE | NO | [111 empty] | YES | [38 empty] | DANIEL GRANT | PIPELINE ENGINEER | daniel_grant@kindermorgan.com | 7134204409 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR - ENGINEERING | 7133699443 | jaime_hernandez@kindermorgan.com | AT 2:20 PM TENNESSEE GAS PIPELINE COMPANY, L.L.C. (TGP) CONTROL ROOM RECEIVED AN ALARM OF AN EMERGENCY SHUTDOWN (ESD) AT STATION 110 IN MOREHEAD, KENTUCKY. AT 2:32 PM, AN OPERATOR ARRIVED ON SITE TO BEGIN ASSESSING THE ESD SYSTEM. THE RELEASED WAS STOPPED AT 2:45 PM AND AT 4:30 PM, WHILE ATTEMPTING TO RESET THE ESD SYSTEM, IT WAS DISCOVERED THAT VALVE 1D7, WHICH IS ON A SUCTION LINE COMING OFF OF LINE 100-7, DID NOT CLOSE AS DESIGNED DURING THE ESD. BECAUSE THE VALVE DID NOT CLOSE DURING THE ESD, GAS FROM THE MAINLINE WAS MAKING ITS WAY THROUGH THE SUCTION SIDE OF THE STATION AND OUT OF THE STATION SILENCER, VENTING TO ATMOSPHERE. AN EMERGENCY RESPONSE CALL WAS HELD AT 5:00 PM TO DISCUSS THE EVENT. BECAUSE THE 1D7 VALVE DID NOT CLOSE IT WAS FORECASTED THAT THE GAS LOSS QUANTITY WOULD EXCEED 3,000 MCF. AS A RESULT OF THIS FORECAST THE EVENT WAS REPORTED TO THE NRC. THE INITIAL ASSESSMENT DISCOVERED THAT A LIGHTNING EVENT CAUSED THE STATION TO ESD. AFTER FURTHER INVESTIGATION, IT WAS FOUND THAT THE VALVE OPERATOR ON VALVE 1D7 HAD RECENTLY BEEN REPLACED WITHOUT A MANAGEMENT-OF-CHANGE (MOC). THE VALVE OPERATOR HAD A DEFAULT CONFIGURATION FOR "PRESSURE-UP" ACTIVATION ON AN ESD SYSTEM; HOWEVER, THE ESD SYSTEM AT STATION 110 FUNCTIONS AS A "PRESSURE-DOWN" ESD SYSTEM. INSTALLATION OF THE VALVE OPERATOR WITHOUT AWARENESS OF ITS DEFAULT DESIGN CONFIGURATION, CAUSED VALVE 1D7 NOT TO CLOSE DURING THE ESD AT THE STATION. AS A CORRECTIVE ACTION, TGP REVIEWED ITS MOC PROCEDURE WITH OPERATORS AT STATION 110. OPERATORS WERE RETRAINED TO RECOGNIZE THAT A MOC IS NEEDED FOR MAKING CHANGES TO THE NORMAL DESIGN CONDITIONS OR DESIGN PARAMETERS OF PIPELINE OPERATIONS.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200070 | 33989 | 2020-07-02 09:57 | ORIGINAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2020-06-03 16:20 | 2020 | CENTRAL | YES | 33.6526 | -102.5601 | 1278791 | 2020-06-03 16:39 | 1278876, 1278883 | NATURAL GAS |  | 1712 | 13919 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-06-03 18:01 | 2020-06-04 01:00 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-06-03 18:00 | VALVE CLOSURE |  | 2020-06-03 18:01 | 0 | 2020-06-03 13:40 | 2020-06-03 15:31 | ONSHORE | TX | 79379 | WHITEFACE | HOCKLEY | MILEPOST | 154+1400 | 1102 - DUMAS TO EUNICE | TAP 27-334 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | 1" THREADED TAP RISER | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | THREADED CONNECTION FAILED | [5 empty] | CLASS 1 LOCATION | NO |  | 19 |  | NO | NO |  |  | 0 | 0 | 20739 | 20739 | 2551 | 2551 | 2000 | 2000 | 3750 | 3750 | 0 | 0 |  | 1.49 | 29040 | 14803.88749362 | 29040 | 0 | 0 | 0 | 0 | NO |  |  |  | 655 | 0 | 780 | 192.619(C) |  | 1948-07-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 91483 | NO | [5 empty] | YES | 1" TAP IS NOT PIGGABLE | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM WAS NOT CONTRIBUTING FACTOR TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [9 empty] | NO | [5 empty] | UNKNOWN |  | YES | LARGE TRUCK | OFF-ROAD | 0 | YES |  |  | YES | [235 empty] | DANIEL GRANT | PIPELINE ENGINEER | daniel_grant@kindermorgan.com | 7134204409 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR - ENGINEERING | 7133699443 | jaime_hernandez@kindermorgan.com | ON JUNE 3RD AT 1:40 PM, EL PASO NATURAL GAS COMPANY, L.L.C. (EPNG) GAS CONTROL WAS NOTIFIED BY A FARMER THAT THERE WAS A POTENTIAL NATURAL GAS LEAK IN AN AGRICULTURAL FIELD. AN OPERATOR WAS SENT TO THE SITE AND ARRIVED AT 3:31 PM TO CONFIRM THE LEAK. AN ERL (EMERGENCY RESPONSE LINE) CONFERENCE CALL WAS HELD AT 4:20 PM. AT THAT TIME THE GAS LOSS QUANTITY AND POTENTIAL DAMAGES WERE UNKNOWN, BUT OUT OF AN ABUNDANCE OF CAUTION A NOTIFICATION TO THE NRC WAS MADE. THE NRC WAS CALLED AT 4:25 PM. THE CALLER WAS PUT ON HOLD, AND THE NRC REPORT WAS TAKEN AT 4:39 PM. AS THE INVESTIGATION CONTINUED, EPNG DEEMED THE INCIDENT TO BE SIGNIFICANT PER INTERNAL PROCESSES. IN ORDER TO MINIMIZE CUSTOMER IMPACT, EPNG COMMUNICATED THE SITUATION WITH ITS CUSTOMERS ON THE LINE 1102 VALVE SEGMENT PRIOR TO THE VALVE SEGMENT BEING SHUT-IN AT 6:01 PM. AFTER THE PIPE WAS BLOWN DOWN, IT WAS DISCOVERED THAT THE GUARD RAILS WERE DAMAGED AND THE 1" RISER HAD BEEN BROKEN OFF AT THE THREADED CONNECTION TO THE ELBOW BELOW GRADE BY A FARMER OPERATING A TRACTOR ON THE PROPERTY NOT PERFORMING ANY EXCAVATION ACTIVITIES. TO REPAIR THE TAP EPNG CLOSED THE TAP VALVE, AND PLUGGED AND COATED THE PIPE. ON JUNE 4TH, 2020 AT 1:00 AM THE VALVE SEGMENT ON LINE 1102 WAS BROUGHT BACK INTO SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200071 | 34654 | 2020-07-09 09:53 | SUPPLEMENTAL FINAL | 30028 | EGAN HUB STORAGE, LLC (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2020-06-19 13:53 | 2020 | CENTRAL | NO | 30.2601 | -92.574 | 1279959 | 2020-06-19 13:53 | 1280056 | NATURAL GAS |  | 2 | 59 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | ROUTINE START-UP | YES |  | 2020-06-19 13:32 | 2020-06-24 08:30 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-06-19 13:17 | NO | [11 empty] | 0 | 2020-06-19 13:17 | 2020-06-19 13:53 | ONSHORE | LA | 70531 | EVANGELINE | ACADIA | MILEPOST | 0.732 | EGAN STORAGE FACILITY | EGAN PR3 SKID | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  |  | NO | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 2 | NO | 0.218 | 35000 | GRADE B | SEAMLESS |  | UNKNOWN | OTHER | FBE | UNKNOWN | [26 empty] | 2008 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 63 |  | NO | NO |  |  | 0 | 0 | 200 | 200 | 7 | 7 | 140000 | 140000 | 0 | 0 | 0 | 0 |  | 3.39 | 140207 | 64362.7566517936 | 140207 | 0 | 0 | 0 | 0 | NO |  |  |  | 800 | 0 | 1480 | 192.619(A)(1) |  | 2009-09-04 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | NO | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS DETERMINED THE CONTROLLERS ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. THE LEAK WAS TOO SMALL TO BE IDENTIFIED BY THE CONTROL ROOM PERSONNEL. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | GENERAL CORROSION |  |  | YES |  |  |  |  | YES | YES |  |  | YES | YES |  |  |  |  | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [19 empty] | YES | [43 empty] | MICHAEL MCGRATH | PIPELINE COMPLIANCE SPECIALIST | michael.mcgrath@enbridge.com | [5 empty] | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 713-627-5008 | nathan.atanu@enbridge.com | AT APPROXIMATELY 1:17 PM EDT ON JUNE 19, 2020, TETLP PERSONNEL CONDUCTING A LEAKAGE SURVEY IDENTIFIED A RELEASE OF NATURAL GAS NEAR TETLP'S 24-INCH DIAMETER PIPING BETWEEN THE PR3 SKID AND THE 670 CONTACTOR AT THE EGAN COMPRESSOR STATION IN TEXAS. THE SECTION OF THE PIPE SEGMENT WAS DOWN FOR A PLANNED OUTAGE AND THE RELEASE OF GAS WAS IDENTIFIED WHILE BRINGING THE PIPE SEGMENT BACK TO SERVICE. TETLP SUBSEQUENTLY ISOLATED AND DEPRESSURIZED THIS PIPE SEGMENT. THE LEAK WAS IDENTIFIED ON A 2-INCH LOW POINT DRAIN. THE INVESTIGATION AND METALLURGICAL ANALYSIS DETERMINED THAT THE LEAK WAS THE RESULT OF INTERNAL CORROSION CAUSED BY A BUILD UP A CARBONIC ACID IN THE 2-INCH LOW POINT DRAIN. THE SEGMENT OF PIPE HAS BEEN CUT OUT AND REPLACED AND THE LINE HAS BEEN RESTORED TO IT'S PREVIOUS PRESSURE. UPDATED 12-23-2020 EGAN COMPLETED THE INVESTIGATION AND DETERMINED THE CAUSE OF THE FAILURE WAS INTERNAL CORROSION WITHIN THE LOW POINT DRAIN. UPDATED PART D.3. AND PART G.
2021-02-26 10:37 | YES | YES | GT (Gas Transmission) | 20200072 | 34783 | 2020-07-09 12:11 | SUPPLEMENTAL FINAL | 31225 | AK STEEL CORP | 1801 CRAWFORD ST | MIDDLETOWN | OH | 45043 | 2020-05-15 15:00 | 2020 | EASTERN | YES | 39.4892 | -84.3958 | 1277360 | 2020-05-15 16:53 |  | NATURAL GAS |  | 5153 | 0 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-05-15 15:15 | 2020-05-16 18:00 |  | YES | OPERATOR | 2020-05-15 15:00 | YES | 2020-05-15 15:00 | ALLOWED TO BURN OUT |  | 5153 | NO | VALVE CLOSURE |  | 2020-05-15 15:15 | VALVE CLOSURE |  | 2020-05-15 15:22 | 20 | 2020-05-15 15:00 | 2020-05-15 15:10 | ONSHORE | OH | 45043 | MIDDLETOWN | BUTLER | NOT APPLICABLE |  | AK STEEL NATURAL GAS PIPELINE | AIR PRODUCTS INLET PIPING AND METERING | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 3.5 | NO | 0.256 | 23242 | API 5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | EPOXY |  | YES | [26 empty] | 2012 | 2012 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 3 | 3 |  | CLASS 3 LOCATION | NO |  | 45 |  | NO | NO | NO |  | 7000 | 7000 | 0 | 0 | 46892 | 46892 | 75000 | 75000 | 0 | 0 | 0 | 0 |  | 9.1 | 128892 | 86255.22933708 | 128892 | 0 | 1 | 0 | 1 | NO |  |  |  | 160 | 12000 | 340 | 192.619(A)(2) |  | 2012-04-25 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 80 | NO | YES | [6 empty] | YES |  |  |  |  | YES | SMALL DIAMETER PIPE | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [9 empty] | YES | YES | YES |  |  |  | NO | 85 |  | PASSENGER CAR | ROADWAY | 25 | YES |  |  |  | YES | JERSEY BARRIERS | [203 empty] | YES | [29 empty] | JOHN JOHNSON |  | jjohnson@uti-corp.com | 5135948600 |  |  |  |  | JOHN JOHNSON |  | 5135948600 | jjohnson@uti-corp.com | ON 5/15/20 AT APPROXIMATELY 3:00PM, A CAR TRAVELING NORTH ON YANKEE RD IN MIDDLETOWN, OHIO STRUCK AN INLET RISER TO AN AIR PRODUCTS FACILITY. THE VEHICLE WAS TRAVELING AT A HIGH RATE OF SPEED AND CROSSED THE CENTER LINE OF YANKEE RD. THE VEHICLE WENT OFF OF THE ROAD FOR A DISTANCE OF ABOUT 300 FEET BEFORE IT STRUCK AND RUPTURED A 3" NATURAL RISER AND METER SETTING THAT FEEDS THE AIR PRODUCTS FACILITY. THE 3" NATURAL GAS RISER AND METER SETTING IS OPERATED BY AK STEEL CORPORATION (OPID 31225). THE PIPELINE IGNITED WHEN IT WAS RUPTURED BY THE VEHICLE AND CAUGHT THE VEHICLE ON FIRE. ONE OCCUPANT IN THE VEHICLE WAS INJURED AND SUFFERED 2ND AND 3RD DEGREE BURNS. THE OCCUPANT WAS WAS TRANSPORTED TO THE HOSPITAL BUT DID SURVIVE THE ACCIDENT. THE 3" NATURAL GAS PIPELINE WAS SHUT OFF AT THE REGULATOR STATION OUTLET VALVE. REPAIRS WERE MADE TO THE 3" NATURAL GAS PIPELINE AND THE PIPELINE WAS PUT BACK INTO SERVICE THE FOLLOWING DAY.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200073 | 34512 | 2020-07-10 14:04 | SUPPLEMENTAL FINAL | 13845 | NORTHWEST PIPELINE LLC | 295 CHIPETA WAY | SALT LAKE CITY | UT | 84108 | 2020-06-12 15:21 | 2020 | MOUNTAIN | YES | 42.6539 | -113.0082 | 1279463 | 2020-06-12 16:39 | 1279598 | NATURAL GAS |  | 2462 | 5749 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-06-10 16:05 | 2020-08-12 16:52 |  | YES | OPERATOR | 2020-06-10 18:50 | NO | [5 empty] | VALVE CLOSURE |  | 2020-06-10 16:05 | VALVE CLOSURE |  | 2020-06-10 16:05 | 0 | 2020-06-10 13:29 | 2020-06-10 13:15 | ONSHORE | ID | 83211 | Not Within a Municipality | POWER | MILEPOST | 626.8 | WILLIAMS NORTHWEST PIPELINE | MAINLINE 1400 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 42 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 22 | NO | 0.25 | 52000 | API 5LX | DSAW |  | CONSOLIDATED WESTERN | ASPHALT |  | UNKNOWN | [26 empty] | 1955 | 1955 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 443 |  | NO | NO |  |  | 0 | 0 | 8853 | 8853 | 0 | 0 | 600000 | 600000 | 0 | 0 | 0 | 0 |  | 1.54 | 608853 | 279479.592702255 | 608853 | 0 | 0 | 0 | 0 | NO |  |  |  | 383 | 10000 | 850 | 192.619(A)(3) |  | 1970-11-12 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 91783 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | GAS DETECTION IN RESPONSE TO ANOMALIES IDENTIFIED THROUGH IN-LINE INSPECTION |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIN HOLE LEAKS WERE OF A MINOR NATURE IN TERMS OF GAS LOSS, AND SCADA IS NOT WELL SUITED FOR IDENTIFYING THESE TYPES OF LEAKS. LEAKS WERE DISCOVERED DURING FOLLOW UP ACTIVITIES ASSOCIATED WITH IN-LINE INSPECTION OF THE LINE. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1975 | YES | YES | YES |  |  |  | 2019 |  |  |  | NO | [190 empty] | YES | YES | [6 empty] | 2020 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2012 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [45 empty] | NO |  |  | Yes, and an investigative dig was cunducted at the point of the Accident | 2020 |  |  |  |  | 2020 | [5 empty] | YES |  | NO | [63 empty] | BRET BURKHART | ENGINEER III - PIPELINE SAFETY | bret.burkhart@williams.com | 801-584-6892 |  | DAVE DICKERSON | david.s.dickerson@williams.com | 208-884-4300 | TYSON GREEN | MANAGER PIPELINE SAFETY | 713-215-2535 | tyson.green@williams.com | IN APRIL OF 2020 WILLIAMS CONTRACTED WITH AN IN-LINE INSPECTION VENDOR TO COMPLETE TOOL RUNS ON THE WILLIAMS NORTHWEST PIPELINE 1400 POCATELLO TO BURLEY SEGMENT. HIGH-RES MFL TOOL RUNS WERE CONDUCTED, AND A PRELIMINARY REPORT WAS PROVIDED TO WILLIAMS WITH CERTAIN HIGH-PRIORITY ANOMALIES ON THE WEEK OF 5/25/2020. A PROJECT WAS INITIATED TO ADDRESS PRELIMINARY HIGH-PRIORITY ANOMALIES. IN PREPARATION TO EXCAVATE, WILLIAMS OPERATIONS CONDUCTED A LEAK SURVEY OF THE EXCAVATION AREA AND IDENTIFIED GAS READINGS AT THREE ANOMALIES WITHIN AN APPROXIMATE 350FT. SPAN ON 6/10/2020 NEAR M.P. 626.8. IN RESPONSE, THE LINE SEGMENT BETWEEN VALVES 9-1 AND 9-2 WAS SHUT-IN AND BLOWN DOWN ON THE SAME DATE. EXCAVATIONS OF THE ANOMALIES CONFIRMED PIN-HOLE LEAKS RESULTING FROM CORROSION. AFTER ASSESSING REPAIR OPTIONS WILLIAMS PROJECT MANAGEMENT DETERMINED THAT REPAIRS WOULD BE BEST ACCOMPLISHED THROUGH PIPE REPLACEMENT OF APPROXIMATELY 400'. THE PRELIMINARY COST OF REPAIRS EXCEEDS $50,000, WITH COST OF CONTRACTOR AND INTERNAL LABOR APPROACHING $600,000. IT WAS DETERMINED THAT THIS QUALIFIED AS A DOT REPORT-ABLE INCIDENT BASED ON COST WHEN WILLIAMS MANAGEMENT SETTLED ON PIPE REPLACEMENT AS THE PREFERRED REPAIR OPTION ON 6/12/2020. THE NRC WAS INITIALLY NOTIFIED OF THE INCIDENT ON 6/12/2020. AT THE TIME OF THIS REPORT THE LINE IS SHUT-IN AND BLOWN-DOWN. THE ANTICIPATED START DATE FOR THE REPLACEMENT PROJECT IS 7/13/2020 WITH ANTICIPATED PROJECT COMPLETION 8/1/2020. ON 8/12/2020 ALL REPAIRS ON THE LINE WERE COMPLETED, AND THE PIPELINE WAS RETURNED TO SERVICE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200074 | 34055 | 2020-07-13 13:10 | SUPPLEMENTAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-06-16 18:40 | 2020 | CENTRAL | NO | 28.9033 | -96.7143 | 1279731 | 2020-06-16 19:39 | 1279859 | NATURAL GAS |  | 9 | 2768 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-06-16 20:59 | 2020-06-17 19:10 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-06-16 20:47 | VALVE CLOSURE |  | 2020-06-16 20:59 | 0 | 2020-06-16 18:40 | 2020-06-16 18:30 | ONSHORE | TX | 77957 | EDNA | JACKSON | SURVEY STATION NO. | 209+71 | TOM O CONNOR | 3022 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 51 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 | NO | 0.312 | 52000 | API5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | YOUNGSTOWN | COAL TAR |  | YES | [26 empty] | 1958 | 1958 | CARBON STEEL |  | MECHANICAL PUNCTURE | 0.1 | 0.1 | [7 empty] | CLASS 1 LOCATION | NO |  | 346 |  | NO | NO |  |  | 0 | 0 | 5038 | 5038 | 16 | 16 | 60000 | 60000 | 1500 | 1500 | 0 | 0 |  | 1.82 | 66554 | 30559.285653584 | 66554 | 0 | 0 | 0 | 0 | NO |  |  |  | 665 | 15000 | 880 | 192.619(C) |  | 2014-11-03 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 40656 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INVESTIGATION IDENTIFIED NO CONTROLLER ISSUES. CONTROLLER ACTIONS WERE CONSISTENT WITH COMPANY PROTOCOL. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | TRENCHER | WATER | NO | [5 empty] | YES | 25 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | TIMOTHY BUNAG | ENGINEER - REGULATORY COMPLIANCE | timothy.bunag.@energytransfer.com | 832-294-5324 |  | TIMOTHY BUNAG | timothy.bunag@energytransfer.com | 832-294-5324 | CHRIS KRESTA | MANAGER - REGULATORY COMPLIANCE | 713-989-7077 | christopher.kresta@energytransfer.com | ON JUNE 16, 2020, AT APPROXIMATELY 6:10 PM, ENERGY TRANSFER GAS CONTROL RECEIVED A CALL FROM A 3RD PARTY CONTRACTOR ABOUT A LINE STRIKE ON THE 3022 TOM O CONNOR 16 IN NATURAL GAS PIPELINE. THIS PIPELINE IS A TRANSMISSION LINE IN A CLASS 1 AREA LOCATED IN JACKSON COUNTY, APPROXIMATELY 4 MILES SOUTH OF EDNA, TX. OPERATIONS PERSONNEL WERE DISPATCHED AND ARRIVED ON LOCATION AT 6:30 PM TO INVESTIGATE. AT 6:40 PM, THE INVESTIGATION CONFIRMED THE 3RD PARTY LINE STRIKE ON THE 16 IN ETC PIPELINE. OPERATIONS PROCEEDED WITH LINE ISOLATION PROCEDURES AND BEGAN PROCESS TO REPAIR. THE UPSTREAM AND DOWNSTREAM VALVES WERE CLOSED TO ISOLATE THE PIPELINE AT 8:47 PM AND 8:59 PM. THE PIPELINE BLOW DOWN WAS COMPLETED AT 11:25 PM. THE REPAIRS WERE MADE AND LINE WAS PUT BACK IN SERVICE AS OF 7:10 PM ON JUNE 17, 2020. THE INVESTIGATION REVEALED THAT THE 3RD PARTY CONTRACTOR WAS TRENCHING ACROSS THE RIGHT-OF-WAY AND HIT THE PIPELINE WITH EXCAVATION EQUIPMENT. THE CONTRACTOR FAILED TO MAKE A ONE CALL NOTIFICATION PRIOR TO EXCAVATING. THIS PIPELINE IS UNDER THE JURISDICTION OF THE TEXAS RAILROAD COMMISSION. ON JUNE 16, 2020, THIS INCIDENT WAS TELEPHONICALLY REPORTED TO THE NATIONAL RESPONSE CENTER (NRC#1279731) AT 7:39 PM AND TO THE TXRRC (INCIDENT #2221) AT 8:03 PM. A 48 HOUR NRC UPDATE WAS MADE ON JUNE 18, 2020 AT 9:29 AM (NRC#1279859) **07/16/2020 UPDATED GPS COORDINATES **07/20/2020 UPDATED NARRATIVE DESCRIPTION & INCIDENT TIMES UNDER A4 AND A13
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200075 | 34558 | 2020-07-23 19:50 | SUPPLEMENTAL FINAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2020-06-24 19:32 | 2020 | CENTRAL | YES | 41.3793 | -91.1951 | 1280350 | 2020-06-25 09:17 | 1280436 | NATURAL GAS |  | 50866 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | ROUTINE SHUTDOWN | [5 empty] | NO |  |  | NO | [11 empty] | 0 | 2020-06-25 08:07 | 2020-06-25 08:07 | ONSHORE | IA | 52752 | LETTS | MUSCATINE | MILEPOST | 821 | COMPRESSOR STATION 199 | AMARILLO LINE #2 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1968 | 1968 | CARBON STEEL |  | LEAK |  |  | OTHER | LEAK THROUGH VALVE | [5 empty] | CLASS 1 LOCATION | NO |  | 479 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 79860 | 79860 | 175 | 175 | 150 | 150 | 0 | 0 |  | 1.57 | 80185 | 82943.671764697 | 80185 | 0 | 0 | 0 | 0 | NO |  |  |  | 550 | 91 | 712 | 192.619(C) |  | 1947-12-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WAS NO INDICATION OF CONTROLLER INVOLVEMENT IN THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [30 empty] | YES | NORMAL WEAR AND TEAR | [161 empty] | SHELLEY DIETZ | PIPELINE ENGINEER | shelley_dietz@kindermorgan.com | 713-420-4417 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | ON THE AFTERNOON OF JUNE 24, 2020, EMPLOYEES AT NATURAL GAS PIPELINE COMPANY OF AMERICA, LLC (NGPL) STATION 199 WERE PERFORMING OPERATIONAL TESTS ON THE BACKUP COMPRESSOR UNIT. WHEN THE TESTS WERE COMPLETE, THE EMPLOYEES STARTED THE SHUTDOWN PROCESS ON THE UNIT AND CHECKED IN THE STATION PLC THAT ALL UNIT VALVES WERE IN THE PROPER POSITION BEFORE LEAVING THE SITE FOR THE DAY. WHEN EMPLOYEES ARRIVED ON SITE THE NEXT MORNING, JUNE 25, 2020 AT 8:07, THEY DISCOVERED THAT GAS WAS VENTING AND CONFIRMED DISCOVERY OF AN INCIDENT. THEY DETERMINED THAT THE 36 INCH DISCHARGE MANIFOLD VALVE ON THE UNIT WAS NOT FULLY CLOSED, DESPITE INDICATING CLOSED ON THE PLC. THIS THEREFORE ALLOWED GAS TO CONTINUE TO VENT. THE EMPLOYEES MANUALLY CLOSED THE VALVE TO STOPPED THE RELEASE AND INITIATED THE ERL PROTOCOL. DURING THE ERL CALL THE INCIDENT WAS DEEMED REPORTABLE AND THE CALL TO THE NRC WAS INITIATED AT 9:01. HOWEVER, DUE TO HOLD TIMES, THE REPORT WAS NOT TAKEN UNTIL 9:17. THE INVESTIGATION IN TO THE RELEASE REVEALED THAT A CRACKED AND PUNCTURED VALVE DIAPHRAGM WAS RESPONSIBLE FOR THE BLOCK VALVE'S FAILURE TO FULLY CLOSE. THE PILOT OPERATOR WAS REPAIRED BY REPLACING THE DAMAGED DIAPHRAGM WITH A NEW DIAPHRAGM. IN ORDER TO PREVENT A REOCCURRENCE, ALL CONTROL DIAPHRAGMS ON SIMILAR PILOT OPERATING VALVES AT THIS STATION WERE INSPECTED AND REPLACED. FINALLY, A PRESSURE MONITORING ALGORITHM WAS ADDED TO THE PLC AND WILL ISSUE A CALL OUT ALARM IF THE COMPRESSOR HAS NOT BLOWN DOWN AFTER A SET TIME
2021-02-26 10:37 | YES | YES | UNGS (Underground Natural Gas Storage) | 20200076 | 34636 | 2020-07-30 11:04 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 STATE ROUTE 56; BOX 20010 | OWENSBORO | KY | 42301 | 2020-06-30 16:09 | 2020 | CENTRAL | YES | 36.8513 | -97.4884 | 1280759 | 2020-06-30 16:45 | 1280912 | NATURAL GAS |  | 0 | 14.9 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | ROUTINE SHUTDOWN | [5 empty] | YES | OPERATOR | 2020-06-30 12:23 | NO | [11 empty] | 0 | 2020-06-30 12:10 | 2020-06-30 07:15 | ONSHORE | OK | 74646 | Not Within a Municipality | GRANT | NOT APPLICABLE |  | WEBB STORAGE FIELD | WEBB WELL NUMBER 30 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | UNDERGROUND GAS STORAGE OR CAVERN | [38 empty] | 1965 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | INTENTIONAL GAS RELEASE FOR MAINTENANCE WORK AT STORAGE WELL | CLASS 1 LOCATION | NO |  | 204 |  | NO | NO | NO |  | 0 | 0 | 24 | 24 | 0 | 0 | 0 | 0 | 3000 | 3000 | 0 | 0 |  | 1.62 | 3024 | 1388.09579378211 | 3024 | 0 | 1 | 0 | 0 | NO |  |  |  | 1429 | 941 | 1850 | OTHER | FERC DOCKET IN01-2-000 | 2000-12-26 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE WELL WAS ISOLATED FOR MAINTENANCE, NO CONTROLLER INVOLVEMENT | [12 empty] | YES | 2 | 0 | YES | 3 | 0 | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | DURING ROUTINE MAINTENANCE AT THIS WELLHEAD, A THREADED FITTING ON THE CONTRACTOR'S ASSEMBLY ROTATED DURING BLOW DOWN RESULTING IN INJURY. THE EXISTING PROCEDURE DID NOT CALL FOR THESE TYPE FITTINGS TO BE SECURED TO PREVENT ROTATION DURING ROUTINE MAINTENANCE. | YES |  |  |  |  | ROUTINE MAINTENANCE | NO | [150 empty] | ERIC GLAHN | PIPELINE COMPLIANCE ENGINEER | eric.glahn@southernstar.com | 2702310561 | 2708525016 | CRAIG THOMAS | craig.thomas@southernstar.com | 2703138424 | SHAWN PATTERSON | VP CHIEF OPERATIONS OFFICER | 2708524670 | shawn.patterson@southernstar.com | ON 6/30/2020 AT 12:49 PM CDT, SOUTHERN STAR CENTRAL GAS PIPELINE (SSCGP) RECEIVED NOTICE FROM FIELD PERSONNEL THAT THERE HAD BEEN AN ACCIDENT WITH INJURY AT A WELLHEAD LOCATED IN GRANT COUNTY, OKLAHOMA. THE WELL LOCATED IN THE SSCGP WEBB STORAGE FIELD, WELL NUMBER 30 WAS IN THE PROCESS OF BEING ISOLATED AND BLOWN DOWN FOR SCHEDULED MAINTENANCE. DURING THE BLOW DOWN A FITTING ROTATED AT 12:10 PM CDT, CAUSING AN APPARENT INJURY TO THE SSCGP EMPLOYEE. THE EMS WERE CALLED AT 12:23 PM CDT AND ARRIVED ON SITE AT 12:55 PM CDT. THE EMPLOYEE ARRIVED AT THE HOSPITAL AND WAS PLACED UNDER OBSERVATION. AT 4:09 PM CDT, THE EMPLOYEE WAS ADMITTED TO THE HOSPITAL FOR FURTHER TESTING AND OBSERVATION. AT 4:45 PM CDT ON 6/30/2020 THE NRC WAS NOTIFIED OF THE EVENT WITH THE FOLLOW UP CALL AT 12:45 PM CDT ON 7/2/2020. THE EMPLOYEE WAS RELEASED FROM THE HOSPITAL ON 7/5/2020. DURING THE MAINTENANCE ACTIVITY, THE PUMP-IN-SUB AND LUBRICATOR SHOULD HAVE REMAINED STATIONARY BUT THE ASSEMBLY ROTATED, STRIKING THE EMPLOYEE IN THE HEAD. ADDITIONAL INFORMATION IN SUPPLEMENTAL REPORT: ALTHOUGH THIS TYPE OF MAINTENANCE ACTIVITY HAS BEEN PERFORMED NUMEROUS TIMES FOLLOWING THE ESTABLISHED PROCEDURE RESULTING IN NO PREVIOUS ROTATION OR INJURIES, SSCGP HAS UPDATED THE O&M PROCEDURE 85.02.03 PER PHMSA'S RECOMMENDATION TO REQUIRE EQUIPMENT TO BE SECURED TO PREVENT ROTATION SO THE RISK FOR UNINTENDED MOVEMENT IS ELIMINATED TO THE EXTENT POSSIBLE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200077 | 34865 | 2020-07-30 16:21 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2020-07-02 07:34 | 2020 | CENTRAL | YES | 30.4591 | -93.1457 | 1280884 | 2020-07-02 08:33 | 1281173 | NATURAL GAS |  | 404 | 176 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | THE STATION WAS CURRENTLY NOT RUNNING. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-07-02 07:34 | 2020-07-02 07:34 | ONSHORE | LA | 70657 | RAGLEY | BEAUREGARD | MILEPOST | 64.4 | GILLIS COMPRESSOR STATION | GILL-OPEL | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 66 | YES | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 10 | NO | 0.5 | 35000 | API 5L | SEAMLESS |  | UNKNOWN | COAL TAR |  | UNKNOWN | [26 empty] | 1969 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 281 |  | NO | NO |  |  | 0 | 0 | 297 | 297 | 683 | 683 | 275000 | 275000 | 0 | 0 | 0 | 0 |  | 1.69 | 275980 | 127076.684328745 | 275980 | 0 | 0 | 0 | 0 | NO |  |  |  | 850 | 0 | 1440 | 192.619(A)(1) |  | 1969-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS DETERMINED THE CONTROLLERS ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. THE LEAK WAS TOO SMALL TO BE IDENTIFIED BY THE CONTROL ROOM PERSONNEL. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  | YES | YES |  | YES | ROOT CAUSE OF THE CORROSION FOUND IN THESE SAMPLES IS ELECTROCHEMICAL CORROSION EXACERBATED BY CHLORIDES, FREE SULFUR AND FREE WATER. A SECONDARY CAUSE OF THE CORROSION IS THE ACCUMULATED WATER WET SOLIDS FOUND AT THE 6:00 POSITION IN THE SAMPLES. POTENTIAL TERTIARY CAUSES OF CORROSION INCLUDE CARBON DIOXIDE AND BIOLOGICAL ACTIVITY. |  | YES |  |  | YES |  | YES |  |  |  | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | MICHAEL MCGRATH | SENIOR ENGINEER | michael.mcgrath@enbridge.com | 16128056542 |  |  |  |  | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 281-686-3829 | nathan.atanu@enbridge.com | ORIGINAL REPORT: AT APPROXIMATELY 7:34 AM CDT ON JULY 2, 2020 AN ENBRIDGE CONTRACTOR DISCOVERED A NATURAL GAS RELEASE BELOW GROUND AT THE GILLIS COMPRESSOR STATION ON THE TEXAS EASTERN TRANSMISSION (TETLP) SYSTEM IN BEAUREGARD PARISH, LA. THE LEAK WAS LOCATED ON THE 10-INCH EQUALIZER LINE. THE LINE WAS ISOLATED AND BLOWN DOWN ON JULY 2, 2020 AT 8:05 A.M. CDT, AND IT REMAINED ISOLATED UNTIL REPAIR WAS COMPLETE. THE PIPE WAS REPLACED ON JULY 19, 2020. THE APPARENT CAUSE IS INTERNAL CORROSION AND IS UNDER METALLURGICAL INVESTIGATION. 02/16/2021 METALLURGICAL ANALYSIS CONCLUDED THAT THE INTERNAL CORROSION WAS A RESULT OF A COMBINATION OF THE PRESENCE OF SULFUR AND CHLORIDES. THE CORROSION WAS EXACERBATED BY THE PRESENCE OF SOLIDS BUILDUP IN THE STATION PIPING. THIS PIPING AND SIMILAR PIPING IS INCLUDED IN THE ENBRIDGE FACILITY INTEGRALITY PLAN. UNDER THIS PLAN THE NEED FOR DESIGN MODIFICATIONS, PERIODIC ASSESSMENTS AND CLEANING WILL BE CONSIDERED FOR THIS LOCATION AND OTHER SIMILAR LOCATIONS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200078 | 34848 | 2020-08-04 21:27 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2020-07-05 00:37 | 2020 | EASTERN | YES | 42.8091 | -82.8654 | 1283199 | 2020-07-30 12:45 | 1283435 | NATURAL GAS |  | 1376 | 114 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-07-05 03:03 |  | YES |  |  |  | YES | 2020-07-05 00:37 | ALLOWED TO BURN OUT |  | 1376 | YES | [6 empty] | 0 | 2020-07-05 01:31 | 2020-07-05 02:12 | ONSHORE | MI | 48062 | ARMADA | MACOMB | NOT APPLICABLE |  | RAY COMPRESSOR STATION | UNIT 2-6 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE OTHER ENCLOSED SPACE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | INSTRUMENTATION | [38 empty] | 2013 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | A MECHANICAL SEAL FAILURE OCCURRED IN THE REACTION TURBINE CAUSING OIL TO LEAK INTO THE EXHAUST CHAMBER WHICH RESULTED IN A FIRE. THE PLC SHUT-DOWN AND NO LONGER COMMUNICATE TO THE UNIT. THE ESD SYSTEM DID NOT COMMUNICATE WITH THE PLC TO SHUT DOWN THE UNIT, AND THE PROCESS GAS SUCTION AND DISCHARGE VALVES FAILED TO CLOSE, ALLOWING NATURAL GAS INTO THE ENCLOSURE THROUGH THE SEAL OIL SYSTEM. AN IGNITION OCCURRED WHEN NATURAL GAS CAME INTO CONTACT WITH THE OIL FIRE AT THE TOP OF THE EXHAUST. | CLASS 1 LOCATION | NO |  | 702 |  | NO | NO |  |  | 0 | 0 | 261 | 261 | 3151 | 3151 | 2000000 | 2000000 | 980 | 980 | 0 | 0 |  | 2.29 | 2004392 | 921889.21018838 | 2004392 | 0 | 0 | 0 | 0 | NO |  |  |  | 1133 | 50 | 1800 | 192.619(A)(2) |  | 1969-02-03 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | NO | NO | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLERS HAD NO INDICATION OTHER THAN A CHANGE IN RATE THAT ANYTHING WAS OCCURRING UNTIL NOTIFIED BY LOCAL EMERGENCY RESPONDERS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  | YES | [27 empty] | YES | [166 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON PIONK | GAS COMPLIANCE MANAGER | 989-791-5749 | jason.pionk@cmsenergy.com | ON JULY 5, 2020 AT APPROXIMATELY 00:13 HOURS CONSUMERS ENERGY'S RAY COMPRESSOR STATION UNIT 2-6 EXPERIENCED AN UNPLANNED SHUTDOWN RESULTING IN A NATURAL GAS FIRE. THE FACILITY IS LOCATED AT 69333 OMO ROAD, ARMADA, MICHIGAN (MACOMB COUNTY). THE FIRE WAS INITIATED IN THE TURBINE EXHAUST CHAMBER DUE TO THE INTERACTION OF OIL AND HIGH TEMPERATURE GAS. THE PRESENCE OF OIL WAS DUE TO A MECHANICAL SEAL FAILURE IN THE TURBINE.THE MECHANICAL SEAL FAILURE RESULTED IN UNSTABLE TURBINE SPEED SENDING MULTIPLE ALARMS TO THE PROGRAMMABLE LOGIC CONTROLLER (PLC). THE PLC FAILED TO CONTINUE OPERATIONS ONCE DATA POINTS REACHED A MAXIMUM OF 959 POINTS. THE PLC REGISTER FAULTED AND COULD NOT OVERWRITE THE DATA WHICH PREVENTED THE EQUIPMENT FROM SHUTTING DOWN PROPERLY. AS A RESULT OF THE PLC FAILURE, THE PROCESS GAS SUCTION, DISCHARGE AND FUEL GAS VALVES FAILED TO CLOSE. A GASKET FAILURE OCCURRED BETWEEN THE TURBINE REACTION CHAMBER AND THE TURBINE RESULTING IN A FIRE IN THE INSULATION PROVIDING A HEAT SOURCE TO IGNITE THE GAS NEAR THE EXHAUST STACK. THE FIRE WAS LIMITED TO THE 2-6 SKID AND EXHAUST STACK. THE LOCAL FIRE DEPARTMENT REPORTED TO THE SITE ENTRANCE BUT WERE NOT UTILIZED TO EXTINGUISH THE FIRE. THE STATION OPERATOR ISOLATED THE FUEL AND PROCESS GAS PIPING SYSTEMS ALLOWING THE FUEL SOURCE TO BURN OFF, EXTINGUISHING THE FIRE. CONSUMERS ENERGY'S RAY COMPRESSOR STATION (PLANT 2) REMAINS OUT OF SERVICE AND REPAIR OPTIONS ARE BEING EVALUATED. A SUPPLEMENTAL/FINAL REPORT WILL BE SUBMITTED WHEN A FINAL RESTORATION PLAN A IS DEVELOPED AND NORMAL OPERATIONS RESUMED. FOLLOWING AN EVALUATION OF OPERATIONAL NEEDS, IT WAS DETERMINED THE RAY COMPRESSOR STATION PLANT 2 UNIT 2-6 WOULD BE RETIRED. THE RETIREMENT OF THE UNIT WAS COMPLETED ON DECEMBER 8, 2020.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200079 | 34437 | 2020-08-11 19:08 | SUPPLEMENTAL FINAL | 39193 | ROVER PIPELINE, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-07-12 12:33 | 2020 | EASTERN | YES | 40.4521 | -81.2273 | 1281699 | 2020-07-12 13:33 | 1281846 | NATURAL GAS |  | 3700 | 2800 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-07-12 01:56 | 2020-07-12 03:10 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-07-12 02:08 | NO | [11 empty] | 0 | 2020-07-12 01:34 | 2020-07-12 01:54 | ONSHORE | OH | 44621 | DENNISON | CARROLL | NOT APPLICABLE |  | ROVER MAINLINE | COMPRESSOR STATION 1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | TUBING | [35 empty] | STAINLESS STEEL | RIGID |  | 2018 | 2018 | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 1 |  | NO | NO |  |  | 0 | 0 | 4004 | 4004 | 5291 | 5291 | 100 | 100 | 0 | 0 | 0 | 0 |  | 1.43 | 9395 | 7369.264239068 | 9395 | 0 | 0 | 0 | 0 | NO |  |  |  | 1262 | 407000 | 1440 | 192.619(A)(1) |  | 2017-10-05 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A REVIEW OF THE INCIDENT DETERMINED THAT THERE WERE NO CONTROL ROOM ACTIONS THAT CONTRIBUTED TO THE EVENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | THREADED FITTING | [9 empty] | YES | [172 empty] | KATHRYN HARRYMAN | SR. SPECIALIST REGULATORY COMPLIANCE | kathryn.harryman@energytransfer.com | 8326605977 |  |  |  |  | TODD NARDOZZI | DIRECTOR - REGULATORY COMPLIANCE | 713-989-7126 | todd.nardozzi@energytransfer.com | ON 7/12/20 AT 01:34 EST THE HOUSTON CONTROL CENTER RECEIVED A SCADA ALARM FOR SOUND LEVEL AT THE LEESVILLE COMPRESSOR STATION. CONTROL CENTER IMMEDIATELY CONTACTED LOCAL OPERATIONS PERSONNEL TO RESPOND TO THE STATION AND INVESTIGATE. LOCAL OPERATIONS PERSONNEL ARRIVED ONSITE AT APPROXIMATELY 01:54 AND THE STATION WAS SHUTDOWN AT 01:56. AT 02:08 HOUSTON CONTROL CENTER WAS CONTACTED BY LOCAL FIRE DEPT. REGARDING A NOISE COMPLAINT AND EXPLAINED THAT THE SITUATION WAS BEING ADDRESSED. UPON FURTHER INVESTIGATION AFTER THE AREA WAS SAFE OPERATIONS PERSONNEL DISCOVERED FAILED SMALL DIAMETER TUBING ON UNIT 205. THE TUBING WAS REPLACED AND UNIT 205 WAS RETURNED TO SERVICE AT 03:10. AFTER VOLUME RELEASED CALCULATIONS WERE COMPLETED IT WAS DETERMINED THAT THIS EVENT MET REPORTING THRESHOLDS AT WHICH TIME THE NRC WAS NOTIFIED. TO PREVENT RECURRENCE ADDITIONAL SUPPORT WAS PROVIDED FOR THE TUBING. OTHER FACILITIES OF SIMILAR DESIGN WILL BE INSPECTED AND ADDITIONAL SUPPORT WILL BE PROVIDED AS NECESSARY.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200080 | 34435 | 2020-08-13 08:39 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2020-07-23 08:30 | 2020 | EASTERN | YES | 29.1788 | -92.2235 | 1282605 | 2020-07-23 08:52 | 1282744 | NATURAL GAS |  | 0.036 | 0 | 0.1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | POST-MAINTENANCE/REPAIR | [5 empty] | NO |  |  | NO | [11 empty] | 0 | 2020-07-17 13:00 | 2020-07-17 13:00 | OFFSHORE | [6 empty] | 20" FROM VERMILLION 67 TO SHORE | 22-6004 | [20 empty] | 40 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | VERMILLION | 67 | PLATFORM | INTERSTATE | OFFSHORE PLATFORM, INCLUDING PLATFORM-MOUNTED EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1968 | 1968 | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 380 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 66801 | 66801 | 0 | 0 | 0 | 0 |  | 2 | 66801 | 30663.4216668118 | 66801 | 0 | 0 | 0 | 0 | NO |  |  |  | 760 | 0 | 1168 | 192.619(C) |  | 1970-07-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A VERY SMALL LEAK NOT CAPTURED BY SCADA | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | VALVE STEM SEAL FAILED DUE TO NORMAL WEAR AND TEAR. | [14 empty] | YES | [163 empty] | EDGAR RODRIGUEZ | REGULATORY COMPLIANCE SPECIALIST | edgar.x.rodriguez@williams.com | 7132152846 |  | TRAVIS LABOVE | travis.labove@williams.com | 3372633899 | TYSON GREEN | MANAGER PIPELINE SAFETY | 7132152535 | tyson.green@williams.com | WILLIAMS TECH AND APV VALVE SERVICE WERE TROUBLESHOOTING THE WILLIAMS OWNED VERMILLION 67 PLATFORM LC 300 20 INCH PIG LAUNCHER BLOCK VALVE EIM ACTUATOR. WHILE OPERATING THE VALVE BEGAN TO LEAK GAS AND OIL MIX INTERMITTENTLY FROM THE STEM SEAL. TROUBLESHOOTING WAS STOPPED AND NOTIFICATIONS WERE MADE TO THE OPERATIONS SUPERVISOR. THE SUPERVISOR THEN MADE NOTIFICATIONS TO THE SOC, OFFSHORE REGULATORY LEAD, AND THE MANAGEMENT TEAM. THERE IS CURRENTLY NO IMPACT TO WATER, OIL PADS WERE PLACED ON THE ACTUATOR AND A DRIP PAN PLACED UNDER THE VALVE TO PREVENT ANY IMPACT TO THE WATER. ALTHOUGH THE LEAK HAPPENED ON JULY 17TH IT WAS NOT DETERMINED THAT THE COST OF REPAIR THRESHOLD FOR REPORTING WAS GOING TO BE MET UNTIL JULY 23RD HENCE THE CALL TO THE NRC. 8/19/2020 UPDATE. LEAK DETERMINED TO BE DUE TO NORMAL WEAR AND TEAR OF THE VALVE SEAL. ON 8/13/2020 PRESSURE WAS REDUCED AND RECOMPRESSED AND AT THAT TIME THE LEAK STOPPED. THE LEAK TOOK PLACE AFTER THE DEMARCATION POINT AS TO WHAT WILLIAMS CONSIDERS GATHERING AND WHAT IS TRANSMISSION. AS PART OF OUR RESPONSE, WILLIAMS REALIZED THAT THERE IS A MISTAKE WITHIN OUR GIS MAPS AND THIS LINE WAS REPORTED ABANDONED DURING THE 2020 ANNUAL REPORT AND NPMS SUBMITTAL. WILLIAMS IS WORKING ON FIXING THIS ISSUE AND CREATING A SUPPLEMENTAL REPORT OF THE ANNUAL REPORT AND NPMS SUBMITTAL.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20200081 | 34138 | 2020-08-13 09:23 | ORIGINAL FINAL | 18152 | SEA ROBIN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-07-14 10:00 | 2020 | CENTRAL | NO | 28.3858 | -90.1448 | 1281840 | 2020-07-14 10:52 | 1282148 | NATURAL GAS |  | 1488 | 200 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-07-14 10:00 |  | YES | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-07-14 10:00 | VALVE CLOSURE |  | 2020-07-14 17:00 | 0 | 2020-07-20 10:00 | 2020-07-14 10:00 | OFFSHORE | [6 empty] | SEA ROBIN PIPELINE | 10941 | [20 empty] | 236 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | SOUTH TIMBALIER | 229 | BELOW WATER, PIPE ON OR ABOVE SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 10 | NO | 0.5 | 42000 | API 5L | SEAMLESS |  | US STEEL | EPOXY |  | YES | [26 empty] | 1996 | 1995 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 239 |  | NO | NO |  |  | 0 | 0 | 344 | 344 | 2559 | 2559 | 228870 | 228870 | 4000 | 4000 | 0 | 0 |  | 1.72 | 235773 | 109704.411274866 | 235773 | 0 | 0 | 0 | 0 | NO |  |  |  | 939 | 0.5 | 1200 | 192.619(A)(1) |  | 2011-08-02 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 59664 | NO |  |  | YES |  |  |  |  | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT DUE TO A SMALL PINHOLE LEAK. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | PINHOLE LEAK |  |  |  |  | YES | LOW FLOW | YES | [7 empty] | YES | PINHOLE AT THE 7:00 O'CLOCK POSITION | YES | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | TODD NARDOZZI |  | todd.nardozzi@energytransfer.com | [5 empty] | TODD NARDOZZI |  | 713-989-7126 | todd.nardozzi@energytransfer.com | TUESDAY, JULY 14, 2020 A LEAK WAS CALLED INTO OUR HOUMA OFFICE BY THE PRODUCER PLATFORM IN ST 229 A SHORT TIME AGO. OVERFLIGHT FOUND A 1 MILE BY 15 MILE SHEEN, RANGING FROM DARK BROWN AT THE SOURCE TO RAINBOW AND SILVER ON OUTER EDGES. WE HAVE CALLED THE NRC WITH CASE NUMBER 1281840 ASSIGNED AND ARE WORKING TO ISOLATE OUR LINE FROM THE REST OF THE SYSTEM, PRODUCTION IS GOING OFFLINE AT ST 229 AS WELL. WEDNESDAY, JULY 15, 2020 OVERFLIGHT THIS MORNING SHOWS THE BUBBLES TO BE REDUCED IN SIZE, WITH A SHEEN APPROXIMATELY 100 FEET BY 15 MILES THAT IS SILVER TO RAINBOW IN COLOR AND DISSIPATING. WE ANTICIPATE A DSV TO BE IN THE FIELD EITHER SATURDAY OR SUNDAY, WATER DEPTH HERE REQUIRES A SAT VESSEL AND THERE IS LIMITED AVAILABILITY. LINE PRESSURE IS DOWN TO 370 PSIG AND FALLING, WE PLAN TO TAKE IT TO BOTTOM PRESSURE AS IS OUR NORMAL. WE HAVE UPDATED THE USCG WITH TODAY'S FINDINGS AND OUR PATH FORWARD. AT THIS TIME WE STILL HAVE NOT CONFIRMED RESPONSIBILITY BUT INDICATIONS ARE THAT IT IS LIKELY OURS. FRIDAY, JULY 17, 2020 WEATHER HAS PREVENTED OVER FLIGHTS THE LAST TWO DAYS BUT THE PRODUCER PLATFORM IS REPORTING NO BUBBLES THIS MORNING WITH A GOLD TO RAINBOW COLORED SHEEN, 150 YDS. BY 2 MILES. WE WILL RESUME OVERFLIGHTS AS SOON AS WEATHER CONDITIONS ALLOW. THE LINE IS CURRENTLY AT APPROXIMATE BOTTOM PRESSURE AND WILL REMAIN SO. THE DIVE VESSEL HAS AN ETA TO THE SITE OF SUNDAY MORNING, THE REPAIR CLAMP WILL BE ONBOARD. WE HAVE BEEN IN DAILY CONTACT WITH THE USCG PROVIDING UPDATES. THE NRC AND USCG WILL BE UPDATED AGAIN TODAY WITH THE INFORMATION AND THAT ALL INDICATIONS ARE THE LEAK IS OUR LINE. MONDAY, JULY 20, 2020 THE LEAK HAS BEEN CONFIRMED AS BEING ON OUR 10 IN. LINE, AT THE 7 O'CLOCK POSITION. THERE HAS BEEN NO SHEEN PRESENT IN THE AREA SINCE THE MORNING OF 7/18. THE PROTECTIVE COATING HAS BEEN REMOVED FROM THE LINE AND THE UT INSPECTION PERFORMED. THE REPAIR CLAMP WAS SUCCESSFULLY INSTALLED ONTO THE LINE AND COVERED, WITH THE LINE REMAINING OUT OF SERVICE. WE ARE RELEASING THE VESSEL PENDING INSTRUCTIONS FOLLOWING FURTHER DISCUSSIONS BETWEEN COMMERCIAL AND THE PRODUCER AT ST 229. BOTH THE NRC AND USCG HAVE BEEN KEPT UPDATED ON OUR STATUS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200082 | 34513 | 2020-08-13 10:17 | SUPPLEMENTAL FINAL | 13845 | NORTHWEST PIPELINE LLC | 295 CHIPETA WAY | SALT LAKE CITY | UT | 84108 | 2020-07-15 16:00 | 2020 | MOUNTAIN | YES | 42.6492 | -113.0188 | 1282107 | 2020-07-16 15:13 | 1282238 | NATURAL GAS |  | 821 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-06-10 16:05 | 2020-08-12 16:52 |  | YES | OPERATOR | 2020-06-10 18:50 | NO | [5 empty] | VALVE CLOSURE |  | 2020-07-10 16:05 | VALVE CLOSURE |  | 2020-07-10 16:05 | 0 | 2020-07-15 16:00 | 2020-06-10 18:50 | ONSHORE | ID | 83211 | Not Within a Municipality | POWER | MILEPOST | 627.4 | WILLIAMS NORTHWEST PIPELINE | MAINLINE 1400 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 42 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 22 | NO | 0.25 | 52000 | API 5LX | DSAW |  | CONSOLIDATED WESTERN | ASPHALT |  | UNKNOWN | [26 empty] | 1955 | 1955 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 443 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 1264 | 1264 | 200000 | 200000 | 0 | 0 | 0 | 0 |  | 1.54 | 201264 | 93115.7235607675 | 201264 | 0 | 0 | 0 | 0 | NO |  |  |  | 1.5 | 0 | 850 | 192.619(A)(3) |  | 1970-11-12 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 91783 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | CORROSION FEATURE IDENTIFIED THROUGH IN-LINE INSPECTION |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIN HOLE LEAKS WERE OF A MINOR NATURE IN TERMS OF GAS LOSS, AND SCADA IS NOT WELL SUITED FOR IDENTIFYING THESE TYPES OF LEAKS. LEAKS WERE DISCOVERED DURING FOLLOW UP ACTIVITIES ASSOCIATED WITH IN-LINE INSPECTION OF THE LINE | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1975 | YES | YES | YES |  |  |  | 2019 |  |  |  | NO | [190 empty] | YES | YES | [6 empty] | 2020 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2012 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [45 empty] | NO |  |  | Yes, and an investigative dig was cunducted at the point of the Accident | 2020 |  |  |  |  | 2020 | [5 empty] | YES |  | NO | [63 empty] | BRET BURKHART | ENGINEER III - PIPELINE SAFETY | bret.burkhart@williams.com | 801-584-6892 |  | DAVE DICKERSON | david.s.dickerson@williams.com | 208-884-4300 | TYSON GREEN | MANAGER PIPELINE SAFETY | 713-215-2535 | tyson.green@williams.com | THIS INCIDENT IS RELATED TO CORROSION FEATURES ASSOCIATED WITH PRIOR INCIDENT NO. 20200073-34025. IT IS SUBMITTED SEPARATELY DUE TO THE TIME ELAPSED BETWEEN DISCOVERY OF THE INITIAL THROUGH WALL ANOMALIES AND THIS ADDITIONAL THROUGH WALL ANOMALY. AT THE TIME OF DISCOVERY, THE LINE WAS ISOLATED AND BLOWN DOWN DUE TO MAINTENANCE WORK ON THE OTHER FEATURES IDENTIFIED THROUGH IN-LINE INSPECTION. IN APRIL OF 2020 WILLIAMS CONTRACTED WITH AN IN-LINE INSPECTION VENDOR TO COMPLETE TOOL RUNS ON THE WILLIAMS NORTHWEST PIPELINE 1400 POCATELLO TO BURLEY SEGMENT. HIGH-RES MFL TOOL RUNS WERE CONDUCTED, AND A PRELIMINARY REPORT WAS PROVIDED TO WILLIAMS WITH CERTAIN HIGH-PRIORITY ANOMALIES ON THE WEEK OF 5/25/2020. A PROJECT WAS INITIATED TO ADDRESS PRELIMINARY HIGH-PRIORITY ANOMALIES. IN PREPARATION TO EXCAVATE, WILLIAMS OPERATIONS CONDUCTED A LEAK SURVEY OF THE EXCAVATION AREA AND IDENTIFIED GAS READINGS AT THREE ANOMALIES WITHIN AN APPROXIMATE 350FT. SPAN ON 6/10/2020 NEAR M.P. 626.8. IN RESPONSE, THE LINE SEGMENT BETWEEN VALVES 9-1 AND 9-2 WAS SHUT-IN AND BLOWN DOWN ON THE SAME DATE. EXCAVATIONS OF THE ANOMALIES CONFIRMED PIN-HOLE LEAKS RESULTING FROM CORROSION. AFTER ASSESSING REPAIR OPTIONS WILLIAMS PROJECT MANAGEMENT DETERMINED THAT REPAIRS WOULD BE BEST ACCOMPLISHED THROUGH PIPE REPLACEMENT OF THE AFFECTED AREAS. THE PRELIMINARY COST OF REPAIRS EXCEEDS $50,000, WITH COST OF CONTRACTOR AND INTERNAL LABOR APPROACHING $200,000 PER FEATURE. IT WAS DETERMINED THAT THIS QUALIFIED AS A DOT REPORT-ABLE INCIDENT BASED ON COST. THE NRC WAS INITIALLY NOTIFIED OF THE INCIDENT ON 6/16/2020. AT THE TIME OF THIS REPORT THE LINE IS SHUT-IN AND BLOWN-DOWN. AS OF THE DATE OF THIS REPORT, CUT-OUTS/REPLACEMENTS ARE COMPLETE AND THE PIPELINE WAS RETURNED TO SERVICE ON 8/12/2020. A SUPPLEMENTAL REPORT WAS FILED ON 8/19/2020 PER THE REQUEST OF BRIAN PIERZINA (PHMSA) - WHO REQUESTED THAT ITEM A4 BE UPDATED TO THE TIME THAT THE FEATURE WAS FIRST DISCOVERED, RATHER THAN THE TIME WHEN IT WAS DETERMINED THROUGH EVALUATION AND COST ESTIMATES THAT THIS QUALIFIED AS A DOT REPORTABLE INCIDENT. THE THROUGH WALL FEATURE WAS UNCOVERED 7/15/20 AT 16:00 MT. WE DETERMINED THE NEXT DAY THAT REPLACEMENT COSTS WOULD EXCEED $50K AND THAT THIS COULD NOT BE INCLUDED WITH A REVISION OF A FORMER INCIDENT REPORT RELATED TO THE SAME PIGGING PROJECT FOR THE LINE IN QUESTION. THE COST DETERMINATION WAS MADE 7/16/2020 AT 12:48 MT, AND A NOTIFICATION TO THE NRC WAS MADE ON THE SAME DATE AT 15:13 MT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200083 | 34383 | 2020-08-13 10:28 | SUPPLEMENTAL FINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2020-07-14 15:35 | 2020 | CENTRAL | NO | 35.7774 | -89.9931 | 1282100 | 2020-07-16 15:31 | 1282893 | NATURAL GAS |  | 3841 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | TWO WAY FED SYSTEM |  |  |  | YES | OPERATOR | 2020-07-14 15:35 | NO | [5 empty] | VALVE CLOSURE |  | 2020-07-14 16:00 | OPERATIONAL CONTROL | INSTALLED SLIT TEE STOOPLE FITTING |  | 0 | 2020-07-14 15:39 | 2020-07-14 15:39 | ONSHORE | AR | 72370 | VICTORIA | MISSISSIPPI | NOT APPLICABLE |  | ARKANSAS LSG | P-600 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 12 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 | NO | 0.18 |  | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COLD APPLIED TAPE |  | NO | [26 empty] | 1953 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 10 | 4 | [7 empty] | CLASS 1 LOCATION | NO |  | 120 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 13059 | 13059 | 3889 | 3889 | 16951 | 16951 | 4688 | 4688 | NON STOCK/OUT OF SERVICE COST/MISC. | 3.4 | 38587 | 25256.8838707819 | 38587 | 0 | 0 | 0 | 0 | NO |  |  |  | 250 | 5000 | 400 | 192.619(A)(4) |  | 1954-01-01 | YES | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL |  | 36873 | NO |  | YES | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  |  |  | YES | [6 empty] | CONTRACTOR | GRADER/SCRAPER | GRADING | NO | [5 empty] | NO |  | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | PRESTON WALKER | SENIOR COMPLIANCE COORDINATOR | preston.walker@blackhillscorp.com | 4794350170 |  | GARY SWAIN | gary.swain@blackhillscorp.com | 8707639260 | PRESTON WALKER | SENIOR COMPLIANCE COORDINATOR | 4794350170 | preston.walker@blackhillscorp.com | ON JULY 14,2020 @ 15:35 PM BLACK HILLS ENERGY WAS NOTIFIED THAT A 6 INCH TRANSMISSION LINE HAD SUSTAINED SOME DAMAGE IN A FIELD LOCATED ON HIGHWAY 158 NORTH NEAR VICTORIA, AR BY MANN LAND LEVELING COMPANY WHILE IN THE PROCESS OF PUTTING A FIELD TO GRADE FOR VICTORIA PARTNERSHIP. BHEA OPERATIONS TECH WAS DISPATCHED TO THE SCENE ARRIVING ON SITE @ 15:39 PM TO DISCOVER THE SEVERED 6 INCH TRANSMISSION MAIN. BHEA MAINTENANCE CREW WAS DISPATCHED TO THE SITE AND STARTED THE GAS CONTROL PROCESS BY UTILIZING AN ONE EXISTING VALVE TO THE SOUTH AND INSTALLING A SPLIT TEE ON THE NORTHSIDE OF THE DAMAGED SEGMENT TO GAIN CONTROL OF THE ESCAPING GAS. BHEA MAINTENANCE CREW REPLACED THE DAMAGE SEGMENT AND RETURN THE TRANSMISSION LINE BACK TO NORMAL OPERATION.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200084 | 34315 | 2020-08-18 15:52 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2020-07-23 15:50 | 2020 | CENTRAL | YES | 42.4716 | -94.0414 | 1282671 | 2020-07-23 16:40 | 1282806 | NATURAL GAS |  | 4800 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-07-23 19:10 | 2020-07-25 12:00 |  | YES | OPERATOR | 2020-07-23 16:00 | NO | [5 empty] | VALVE CLOSURE |  | 2020-07-23 19:10 | VALVE CLOSURE |  | 2020-07-23 19:10 | 2 | 2020-07-23 15:50 | 2020-07-23 16:18 | ONSHORE | IA | 50532 | Not Within a Municipality | WEBSTER | MILEPOST | 27.37 | OGDEN TO VENTURA | M520A | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 | YES | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 2.375 | NO | 0.179 | 30000 | UNKNOWN | SEAMLESS |  | UNKNOWN | NONE |  | UNKNOWN | [26 empty] | 1931 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 47 |  | NO | NO |  |  | 126 | 126 | 0 | 0 | 14256 | 14256 | 4000 | 4000 | 10000 | 10000 | 0 | 0 |  | 2.97 | 28382 | 21264.0492600839 | 28382 | 1 | 0 | 0 | 0 | NO |  |  |  | 238 | 10 | 380 | 192.619(A)(4) |  | 2017-01-03 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 46464 | NO |  | YES |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | YES | 2 | 0 | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [9 empty] | YES |  |  | YES | YES |  | NO | YES | YES |  |  |  | 2020 |  |  |  | N/A Bare/Ineffectively Coated Pipe | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [51 empty] | YES | [11 empty] | JOHN A GORMLEY | SR PIPELINE SAFETY SPECIALIST | john.gormley@nngco.com | 402-398-7494 |  |  |  |  | THOMAS CORRELL | VP PIPELINE SAFETY AND RISK | 402-398-7715 | thomas.correll@nngco.com | NORTHERN IS IN THE PROCESS OF ABANDONING THE M520A MAINLINE BETWEEN OGDEN, IOWA AND VENTURA, IOWA. IN PREPARATION FOR ABANDONMENT, TOWNS SERVED OFF OF THE A-LINE ARE BEING MOVED TO A PARALLEL MAINLINE. ON JULY 23, 2020, MANHATTAN PIPELINE, THE CONTRACTOR WORKING FOR NORTHERN, WAS CAREFULLY EXCAVATING THE TAKE-OFF VALVE ASSEMBLY THAT SERVES THE TOWN OF DUCOMBE, IOWA. UNKNOWN TO THE CONTRACTOR, THERE WAS AN ABANDONED 2-INCH TAKE-OFF VALVE JUST 4 FEET DOWNSTREAM (NORTH) OF THE IN-SERVICE TAKE-OFF VALVE. THE CONTRACTOR DID NOT HIT OR STRIKE THE UNKNOWN, ABANDONED VALVE. ABOUT 3:30 PM, DURING THE EXCAVATION PROCESS, THE COMBINATION OF FORCES FROM THE HAND-DIGGING EFFORTS AND RELEASE OF OVERBURDEN CAUSED THE ABANDONED, 2-INCH-DIAMETER, 1931 VINTAGE, BRANCH CONNECTION AND VALVE ASSEMBLY TO FAIL, RESULTING IN BLOWING GAS. THE FAILURE APPEARS TO BE IN THE THREADED CONNECTION BETWEEN THE NIPPLE WELDED TO THE A-LINE AND THE VALVE. THE ABANDONED VALVE AND NIPPLE WERE SENT TO A LABORATORY FOR FURTHER ANALYSIS. THE M520A LINE WAS OPERATING AT APPROXIMATELY 238 PSIG AT THE TIME OF THE EVENT, AND ULTIMATELY VENTED 4.8 MMSCF OF NATURAL GAS. THE COMPANY HAS INSTITUTED AN EXPANDED PROGRAM OF RECORDS RESEARCH IN AN ATTEMPT TO LOCATE THESE ABANDONED FACILITIES TO PREVENT REOCCURRENCE. ONE CONTRACT EMPLOYEE WAS INJURED WHILE ESCAPING THE EXCAVATION. HE SUSTAINED A BRUISE TO HIS RIGHT WRIST AND ELBOW. HE WAS EXAMINED AND RELEASED FROM THE LOCAL HOSPITAL IN FORT DODGE, IOWA. UPDATE 9/29/20: METALLURGICAL ANALYSIS INDICATED THE ROOT CAUSE WAS THE RESULT OF DEFECTIVE WELDING ,EXTERNAL FORCES BENDING AND FLATTENING THE DAMAGED NIPPLE, AND POSSIBLY DEFECTS IN THE VALVE BODY. PHOTO OBSERVATIONS IN THE REPORT ALSO NOTE SIGNIFICANT CORROSION OF THE THREADED SECTION OF THE VALVE. WHILE IT APPEARS THERE WAS SOME EXTERNAL FORCE TO HAVE CAUSED THE BENDING AND FLATTENING, THE CORROSION OF THE THREADED PIPE NIPPLE IN THE "AS RECEIVED" CONDITION WOULD INDICATE THAT THE EXTERNAL FORCE OCCURRED SOMETIME IN THE PAST AND ONCE THE THREAD WAS DEFORMED AND EXPOSED TO THE ENVIRONMENT, CORROSION INITIATED. WITH THE POOR QUALITY OF THE FORGED VALVE FITTING THE CORROSION OF THE THREADS COULD HAVE BEEN RAPID.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200085 | 34367 | 2020-08-19 16:26 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2020-07-25 02:27 | 2020 | EASTERN | YES | 37.5555 | -81.4041 | 1282801 | 2020-07-25 14:49 | 1282856 | NATURAL GAS |  | 300 | 50 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-07-25 15:00 | 2020-09-11 16:00 |  | NO |  |  | YES | 2020-07-25 02:27 | OPERATOR/CONTRACTOR |  | 300 | NO | VALVE CLOSURE |  | 2020-07-25 14:45 | VALVE CLOSURE |  | 2020-07-25 15:00 | 0 | 2020-07-25 02:27 | 2020-07-25 12:47 | ONSHORE | WV | 26267 | Not Within a Municipality | WYOMING COUNTY | MILEPOST | MPID 205117 | LINE KA4 | MPID 205117 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 | NO | 0.15 | 24000 | UNKNOWN | OTHER | UNKNOWN | UNKNOWN | NONE |  | UNKNOWN | [26 empty] | 1933 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 52 |  | NO | NO |  |  | 0 | 0 | 82 | 82 | 489 | 489 | 300000 | 300000 | 0 | 0 | 0 | 0 |  | 1.63 | 300571 | 138252.52471747 | 300571 | 0 | 0 | 0 | 0 | NO |  |  |  | 70 | 250 | 93 | 192.619(A)(4) |  | 1933-10-08 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 1586 | NO |  | YES | YES | YES |  |  |  | YES |  | YES | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | INITIAL NOTIFICATION CAME FROM LOCAL PRODUCER INVESTIGATING FIRES IN THE AREA |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER DID NOT INTRODUCE ANY SIGNALS TO OPEN/CLOSE A VALVE, NO OTHER OPERATIONAL INTERACTION WITH GAS CONTROL PERSONNEL EVEN BEFORE THE INCIDENT TOOK PLACE OR SOMETHING SIMILAR. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [8 empty] | YES |  |  |  | YES | NO |  | NO | NO | [8 empty] | N/A Bare/Ineffectively Coated Pipe | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | MARK NEWMAN | COMPLIANCE SPECIALIST | mark_newman@tcenergy.com | 3045490532 | 3047228420 |  |  |  | PAUL SHAFFER | COMPLIANCE MANAGER | 3045504866 | paul-shaffer@tcenergy.com | ON JULY 25, 2020 AT 02:27 EASTERN DAYLIGHT TIME (EDT), COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA), MONITORING CENTER RECEIVED A CALL FROM A LOCAL PRODUCER (DIVERSIFIED) OF A PIPELINE FIRE. AT 04:16 EDT COLUMBIA IDENTIFIED A FIRE WAS ON PIPELINE KA-4 LOCATED IN WYOMING COUNTY, WV NEAR THE UNINCORPORATED COMMUNITY OF TRALEE, WV SOUTH OF ELMORE, WV. . WITH THE ASSISTANCE OF THE LOCAL FIRE DEPARTMENT COLUMBIA WAS ABLE TO ACCESS THE SITE AND USE FIRE EXTINGUISHERS TO EXTINGUISH THE FIRES. THE FIRES WERE SMALL IN SIZE AND REMAINED CONTAINED WITHIN THE PIPELINE RIGHT OF WAY. HOW THE FIRES WERE IGNITED IS UNDER INVESTIGATION. FIRES WERE FUELED BY A (NUISANCE) GAS LEAK ON PIPELINE KA-4. AT APPROXIMATELY 15:00 EDT PIPELINE KA-4 WAS ISOLATED AND SHUTDOWN. INFORMATION ON THE SOURCE OF IGNITION WILL BE PROVIDED WITH A SUPPLEMENT REPORT. THIS SECTION OF PIPELINE KA-4 IS UNCOATED COUPLED PIPELINE WITH NO CATHODIC PROTECTION. THE LEAK ON THE PIPELINE WAS CAUSED BY EXTERNAL CORROSION. PERMANENT REPAIRS WERE MADE TO TWO SECTIONS. SECTION ONE (1) - 40 FEET OF 6 INCH OD IPS, SDR 11, HDPE PIPE WITH COUPLINGS AND 20 FEET OF 6.625 OD, 0.280 WALL, X52 STEEL PIPE WAS COMPLETED ON 09/02/2020. SECTION TWO (2) HAD 5 FEET OF 6 INCH OD IPS, SDR 11, HDPE PIPE WITH COUPLINGS AND 20 FEET OF 6.625 OD, 0.280 WALL, X52 STEEL PIPE WAS COMPLETED ON 9/11/2020. BOTH REPLACEMENT SECTIONS WAS PRESSURE TESTED TO 150 PSIG FOR 1 HOUR. LINE KA-4 WAS RETURNED TO SERVICE ON 9/11/2020.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200087 | 34199 | 2020-08-26 17:37 | ORIGINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2020-07-29 19:21 | 2020 | EASTERN | YES | 39.443 | -78.9561 | 1283140 | 2020-07-29 19:10 | 1283363 | NATURAL GAS |  | 174 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | THIS LINE IS A SINGLE FEED TO THE KEYSER INDUSTRIAL PARK, KEYSER WV |  |  |  | YES | OPERATOR | 2020-07-29 19:10 | NO | [5 empty] | OPERATIONAL CONTROL | LEAK MONITORED. PLANS TO INSTALL PRESSURE REGULATION TO REDUCE PRESSURE. DIVERS TO EVALUATE LEAK. |  | OPERATIONAL CONTROL | INSTALL PRESSURE REGULATION TO LOWER DOWNSTREAM PRESSURE. |  | 0 | 2020-07-28 14:00 | 2020-07-28 14:45 | ONSHORE | MD | 21562 | MCCOOLE | ALLEGANY | SURVEY STATION NO. | 104+53 | LINE 18039 | 2001654 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | UNDER THE NORTH BRANCH POTOMAC RIVER | 12 | NO | YES | [6 empty] | YES | UNCASED | NORTH BRANCH OF THE POTOMAC RIVER | UNKNOWN | BELOW WATER, PIPE ON OR ABOVE BOTTOM | YES | [10 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 | NO | 0.219 | 35000 | GRADE B | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | EPOXY |  | YES | [26 empty] | 1966 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | HAS NOT BEEN DETERMINED | [5 empty] | CLASS 1 LOCATION | NO |  | 140 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 350000 | 350000 | 0 | 0 | 0 | 0 |  | 1.63 | 350000 | 160659.235391448 | 350000 | 0 | 0 | 0 | 0 | NO |  |  |  | 250 | 8 | 273 | 192.619(A)(2) |  | 1966-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 11786 | NO |  | YES | YES |  |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [146 empty] | WILLIAM YOUSE | COMPLIANCE SPECIALIST | william_youse@tcenergy.com | (304)357-3596 |  | WILLIAM YOUSE | william_youse@tcenergy.com | 304-357-3596 | PAUL SHAFFER | US REGULATORY COMPLIANCE EAST MANAGER | (304)357-2245 | paul_shaffer@tcenergy.com | PIPELINE 18039 IS A TRANSMISSION PIPELINE THAT IS OPERATED AND MAINTAINED BY COLUMBIA GAS TRANSMISSION, LLC (OPID 2616). COLUMBIA HAS EXPERIENCED A LEAK ON THIS PIPELINE IN THE NORTH BRANCH OF THE POTOMAC RIVER NEAR THE TOWN OF MCCOOLE, ALLEGANY COUNTY, MD. PIPELINE 18039 IS A 6-INCH CARBON STEEL, 0.219-INCH WALL THICKNESS, ERW, GRADE B PIPE COATED IN THE AREA OF THE REPORTED LEAK. LINE 18039 MAXIMUM ALLOWABLE OPERATING PRESSURE IS 273 PSIG AND ITS OPERATING PRESSURE AT THE TIME OF DISCOVERY WAS APPROXIMATELY 250 PSIG. LOCAL OPERATIONS WERE NOTIFIED OF A LEAK IN THE POTOMAC RIVER, THE LEAK WAS EVALUATED AND DETERMINED NOT TO BE A HAZARD TO LIFE OR PROPERTY. THE PIPELINE IS A SINGLE FEED TO THE KEYSER INDUSTRIAL PARK LOCATED ACROSS THE POTOMAC RIVER IN KEYSER, WEST VIRGINIA, THEREFORE; FROM AN OPERATIONAL-PERSPECTIVE, IT IS NOT FEASIBLE TO DISCONTINUE THE FLOW OR SHUT DOWN THE PIPELINE. IN ORDER TO REDUCE THE GAS LOSS, PRESSURE REGULATING EQUIPMENT WAS INSTALLED TO REDUCE PRESSURE TO APPROXIMATELY 60 PSIG. CURRENTLY, REPAIR METHODS ARE BEING DETERMINED AND DIVE COMPANIES ARE BEING SOUGHT OUT WHO ARE QUALIFIED AND AVAILABLE TO FACILITATE AN EVALUATION AND POSSIBLE REPAIR OF THIS LEAK. ENGINEERING ANALYSIS AND PERMITTING IS BEING PURSUED TO CONDUCT A PIPE INSERTION OR DIRECTIONAL BORE UNDER THE RIVER.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200088 | 34814 | 2020-08-26 22:50 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2020-07-12 00:17 | 2020 | EASTERN | YES | 42.8113 | -82.8666 | 1284994 | 2020-08-19 17:45 | 1285084 | NATURAL GAS |  | 29 | 24 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-07-12 01:19 | 2020-12-09 08:00 |  | NO |  |  | NO | [11 empty] | 0 | 2020-07-12 00:17 | 2020-07-12 00:47 | ONSHORE | MI | 48005 | ARMADA | MACOMB | NOT APPLICABLE |  | RAY COMPRESSOR STATION UNIT 3-1 (THROW 3) | PISTON ROD - CROSS HEAD NUT | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2011 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 702 |  | NO | NO |  |  | 0 | 0 | 55 | 55 | 66 | 66 | 136557 | 136557 | 500 | 500 | 0 | 0 |  | 2.29 | 137178 | 63006.4511482568 | 137178 | 0 | 0 | 0 | 0 | NO |  |  |  | 1206.4 | 100 | 1800 | 192.619(A)(2) |  | 2010-02-26 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | APPROPRIATE ACTIONS/NOTIFICATIONS WERE COMPLETED WHEN SCADA ALARMS WERE RECEIVED BY THE CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | OTHER | PISTON ROD - LOSS OF TENSION OF THE CROSS HEAD NUT CAUSING IT TO BACK OUT | [5 empty] | YES | [5 empty] | YES | [171 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON PIONK | GAS COMPLIANCE MANAGER | 989-791-5749 | jason.pionk@cmsenergy.com | ON JULY 12, 2020 AT APPROXIMATELY 00:17 HOURS CONSUMERS ENERGY GAS CONTROLLED RECEIVED SCADA ALARMS INDICATING MULTIPLE ENGINES WERE OFFLINE AT THE RAY COMPRESSOR STATION PLANT 3. THE FACILITY IS LOCATED AT 69333 OMO ROAD, ARMADA, MICHIGAN (MACOMB COUNTY). STATION PERSONNEL WERE NOTIFIED AND ARRIVE ONSITE AT APPROXIMATELY 00:47 HOURS AND CONFIRMED HIGH GAS LEL IN THE PLANT 3 COMPRESSOR BUILDING. STATION PERSONNEL THEN PROCEEDED TO DEPRESSURIZE UNIT 3-1 BY OPENING VALVES VGV-701 AND VGV-702. THE GAS LEVEL WITHIN THE COMPRESSOR BUILDING GRADUALLY DECREASED TO ZERO. IT WAS THEN CONFIRMED THAT UNIT 3-1 WAS THE CAUSE OF THE GAS LEAK. FOLLOWING THE INCIDENT, THE STATION PERSONNEL HAVE WORKED THROUGH DISCOVERY ON THE UNIT BY DISASSEMBLING THROW #3 ON UNIT 3-1, AS WELL AS INSPECTING THE INTEGRITY OF THE OTHER THROWS. AT THIS TIME THE DAMAGE IS ISOLATED TO THROW #3; HOWEVER, THE ROOT CAUSE HAS NOT BEEN IDENTIFIED. COMPONENTS OF THROW #3 HAVE BEEN SENT TO CONSUMERS ENERGY'S LABORATORY FOR FURTHER ANALYSIS TO ASSIST WITH THE IDENTIFICATION OF THE ROOT CAUSE OF FAILURE. THE INCIDENT INVESTIGATION AND LABORATORY ANALYSIS DETERMINED A SERIES OF FAILURES OCCURRED RESULTING IN THE RELEASE OF GAS WITH PROPERTY DAMAGE IN EXCESS OF $50,000. A MECHANICAL FAILURE ON UNIT 3-1 THROW 3 CAUSED BY LOSS OF TENSION OF THE CROSS HEAD BALANCE NUT WHICH ALLOWED THE PISTON AND ROD ASSEMBLY TO BACK OUT AND MAKE CONTACT WITH THE FIXED VOLUME CLEARANCE POCKET RESULTING IN FAILURE OF THE PISTON ROD. MAINTENANCE RECORDS FOR THE TORQUEING OF THE CROSS-HEAD BALANCE NUT WERE NOT AVAILABLE. THE EXCESSIVE VIBRATION THAT OCCURRED AS A RESULT OF THE MECHANICAL FAILURE CAUSED THE BOLTS ON THE SUCTION VALVE UNLOADER TO LOOSEN AND GAS TO BE RELEASED. THE SAFETY SYSTEM DESIGNED TO ISOLATE AND EVACUATED GAS THROUGH THE VENT VALVE DID NOT TRAVEL AUTOMATICALLY DURING THE EVENT AND INSTEAD REQUIRED MANUAL ACTIVATION. PROBLEM SOLVING WAS COMPLETED FOR THE MECHANICAL AND SAFETY SYSTEM FAILURES AND ACTION ITEMS DEVELOPED TO MINIMIZE FUTURE RE-OCCURRENCE. RESTORATION OF THE EQUIPMENT IS UNDERWAY, A FINAL REPORT WILL BE SUBMITTED WHEN THE NORMAL OPERATIONS IS RESUMED. FOLLOWING THE INCIDENT INVESTIGATION A COMPRESSOR RESTORATION PLAN WAS DEVELOPED FOR THROW #3. THE PLAN INVOLVED REPLACING THE PISTON ROD, PISTON, THE CROSSHEAD, BALANCE NUT, INNER-CYLINDER HEAD AND THE FIXED VOLUME CLEARANCE POCKET. THE SUCTION VALVE UNLOADERS WERE DISASSEMBLED, INSPECTED AND REBUILT. ACTIONS WERE ALSO TAKEN TO CORRECT THE VALVE POSITIONING ALLOWING THE SAFETY MECHANISM TO AUTOMATICALLY TRAVEL WHEN SPECIFIED PERCENTAGE OF GAS IS DETECTED IN THE BUILDING. FOLLOWING REMEDIATION NORMAL OPERATIONS WERE RESUMED ON DECEMBER 9, 2020.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200089 | 34224 | 2020-09-03 10:36 | ORIGINAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2020-08-12 14:38 | 2020 | CENTRAL | YES | 32.989 | -89.5509 | 1284397 | 2020-08-12 15:40 | 1284539 | NATURAL GAS |  | 35.96 | 22375 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-08-12 14:38 | 2020-08-22 11:58 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-08-12 15:00 | VALVE CLOSURE |  | 2020-08-12 14:45 | 0 | 2020-08-12 14:38 | 2020-08-12 14:38 | ONSHORE | MS | 39090 | KOSCIUSKO | ATTALA | MILEPOST | 376.495 | LINE 31 | CLIN-KOSC | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | MAINLINE | GATE |  | WKM |  |  |  | 1969 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 759 |  | NO | NO |  |  | 0 | 0 | 48106 | 48106 | 77 | 77 | 75000 | 75000 | 0 | 0 | 0 | 0 |  | 2.15 | 123183 | 56588.7317737529 | 123183 | 0 | 0 | 0 | 0 | NO |  |  |  | 743 | 350000 | 936 | 192.619(A)(1) |  | 2015-05-01 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 60192 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS DETERMINED THE CONTROLLERS ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. THE LEAK WAS TOO SMALL TO BE IDENTIFIED BY THE CONTROL ROOM PERSONNEL. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | PIPE NIPPLE | [19 empty] | YES | PRESSURE OF VALVE PIPE NIPPLE AGAINST CONCRETE BLOCK | [161 empty] | MAYRA SALINAS | SENIOR ENGINEER | mayra.salinas@enbridge.com | 832-748-0908 |  |  |  |  | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 281-686-3829 | nathan.atanu@enbridge.com | AT APPROXIMATELY 2:38 PM CDT ON AUGUST 12, 2020 A TEXAS EASTERN TRANSMISSION'S (TETLP) EMPLOYEE WAS PERFORMING A LEAK SURVEY AND DISCOVERED A NATURAL GAS RELEASE FROM TETLP'S LINE 31 AT THE KOSCIUSKO COMPRESSOR STATION IN ATTALA COUNTY, LA. THE LEAK WAS LOCATED ON THE 1/2" THREADED NIPPLE ON MAINLINE VALVE 31-46. THE PIPELINE WAS ISOLATED AND BLOWN DOWN ON AUGUST 12, 2020 AND REMAINED ISOLATED UNTIL THE REPAIR WAS COMPLETED. THE CAUSE OF THE LEAK WAS A NIPPLE OFF THE BODY OF THE VALVE THAT WAS IN CONTACT WITH A CONCRETE SUPPORT WHICH APPLIED PRESSURE TO CAUSE THREADS TO BREAK ON THE NIPPLE. THE PIPELINE WAS RETURNED TO SERVICE ON AUGUST 22, 2020.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200090 | 34245 | 2020-09-03 12:07 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2020-08-13 10:00 | 2020 | CENTRAL | YES | 32.1176 | -90.3012 | 1285170 | 2020-08-21 11:23 | 1285174 | NATURAL GAS |  | 66 | 48 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-08-13 07:00 | 2020-08-15 16:00 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-08-06 16:30 | OPERATIONAL CONTROL | REDUCED PRESSURE CONTROL SET POINT FOR INDEX 302 BY 20% FROM 390 PSIG TO 310 PSIG |  | 0 | 2020-08-06 13:15 | 2020-08-06 13:45 | ONSHORE | MS | 39170 | Not Within a Municipality | HINDS | SURVEY STATION NO. | 744+07 | INDEX 302 | MCCOMB 6-INCH PIPELINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 | NO | 0.28 | 24000 | API 5L | LAP WELDED |  | UNKNOWN | COAL TAR |  | UNKNOWN | [26 empty] | 1931 | 1931 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 2 LOCATION | NO |  | 104 |  | NO | NO |  |  | 0 | 0 | 89 | 89 | 122 | 122 | 285000 | 285000 | 0 | 0 | 0 | 0 |  | 1.85 | 285211 | 130989.856535383 | 285211 | 0 | 0 | 0 | 0 | NO |  |  |  | 390 | 6000 | 447 | 192.619(A)(1) |  | 2018-04-05 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL |  | 15048 | NO |  | YES | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | NOTIFICATION FROM A CENTERPOINT ENERGY EMPLOYEE |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) | [5 empty] | YES | YES | [6 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  | YES | PHOTOS REVIEWED BY CORROSION DEPARTMENT FOR CONFIRMATION | YES | YES | 1960 | NO | YES |  | YES |  |  |  | 2014 |  |  | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 2709035764 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 2703146547 | tina.baker@bwpipelines.com | ON AUGUST 6, 2020, A CENTERPOINT ENERGY EMPLOYEE REPORTED A POSSIBLE NATURAL GAS LEAK ON GULF SOUTH PIPELINE'S MCCOMB 6-INCH (INDEX 302) LINE IN TERRY, MS. GULF SOUTH OPERATIONS EMPLOYEES WERE DISPATCHED TO INVESTIGATE AND DETERMINED A MINOR LEAK OF UNKNOWN CAUSE. THE PRESSURE ON THE PIPELINE WAS REDUCED BY 20% UNTIL REPAIRS COULD BE MADE. PREPARATIONS WERE MADE TO INSTALL A WELD OVER BUT, UPON EXCAVATION, IT WAS DETERMINED THAT THIS WOULD NOT BE A FEASIBLE APPROACH. AT THIS POINT, THIS BECAME A REPORTABLE INCIDENT. THE LINE WAS TAKEN OUT OF SERVICE ON AUGUST 13, 2020 AT 07:00 FOR REPAIRS. INITIALLY, THE CAUSE WAS SUSPECTED TO BE A LEAKING DRESSER COUPLING BUT THE CAUSE WAS DETERMINED TO BE EXTERNAL CORROSION. APPROXIMATELY 250 FEET OF PIPE WAS REPLACED AND THE LINE RETURNED TO SERVICE ON AUGUST 15, 2020 AT 16:00. ON PART G, QUESTION 4A OF THIS REPORT, THE RESPONSE TO THE YEAR THAT CATHODIC PROTECTION ON THIS PIPELINE STARTED IS SPECULATION BASED ON EMPLOYEE HISTORICAL KNOWLEDGE; THE EXACT YEAR IS UNKNOWN. 9-8-2020 SUPPLEMENTAL REPORT SUBMITTED TO CORRECT RESPONSES TO QUESTIONS B4 AND C6 AS DIRECTED BY PHMSA AND CORRECT RESPONSE TO QUESTION A20C.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200091 | 34235 | 2020-09-03 18:47 | ORIGINAL FINAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2020-08-10 17:10 | 2020 | CENTRAL | YES | 41.2077 | -93.9893 | 1284223 | 2020-08-10 17:15 | 1284327 | NATURAL GAS |  | 338 | 34306 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-08-10 17:25 | 2020-08-13 15:58 |  | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | GAS CONTROL MONITORED PRESSURE AND OPERATIONS REMAINED ON SITE. |  | OPERATIONAL CONTROL | GAS CONTROL MONITORED PRESSURE AND OPERATIONS REMAINED ON SITE. |  | 0 | 2020-08-10 13:08 | 2020-08-10 13:08 | ONSHORE | IA | 50273 | Not Within a Municipality | MADISON | MILEPOST | MP582+0270 | NGPL/X893E2 | AMARILLO LINE NO.2 GRAND RIVER TO CLANTON CREEK | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | MAINLINE | PLUG |  | UNKNOWN |  |  |  | 1957 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 368 |  | NO | NO |  |  | 0 | 0 | 85765 | 85765 | 845 | 845 | 60283 | 60283 | 1000 | 1000 | 0 | 0 |  | 2.5 | 147893 | 68374.9619997426 | 147893 | 0 | 0 | 0 | 0 | NO |  |  |  | 665 | 0 | 712 | 192.619(C) |  | 1957-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 60092 | NO | [5 empty] | YES | PIPING THAT CONTAINS THE VALVE IS CONSIDERED X-OVER PIPING AND CANNOT BE DIRECTLY PIGGED. | YES |  |  |  |  | YES | THE X-OVER PIPING CANNOT BE PIGGED. | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLERS ACTIONS COULD NOT HAVE RESULTED IN THE VALVE PACKING LEAK. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [30 empty] | YES | GAS SEAL PROVIDED BY GREASED VALVE-PACKING MATERIAL NO LONGER EFFECTIVE. | [152 empty] | YES | [8 empty] | STEPHEN R. DINES | ENGINEER | stephen_dines@kindermorgan.com | (719) 351-3199 | (719) 329-5673 | MIKE BUCHANAN | mike_bohannan@kindermorgan.com | 319-461-7890 | JAIME HERNANDEZ | DIRECTOR-ENGINEERING | (281) 384-5609 | jaime_hernandez@kindermorgan.com | ON AUGUST 10, 2020 AT APPROXIMATELY 12:45 PM LOCAL TIME, NGPL GAS CONTROL CONTACTED LOCAL OPERATIONS OF A REPORT RECEIVED FROM A THIRD PARTY OF GAS VENTING NEAR VALVE V893 IN MADISON COUNTY, IOWA. AT 13:08 PM LOCAL TIME, NGPL OPERATIONS ARRIVED ON LOCATION AND FOUND THAT THE VALVE OPERATOR ON A CROSSOVER, ISOLATION VALVE WAS VENTING FROM A SMALL (1/8' DIAMETER) VENT ON THE VALVE ACTUATOR. AT THAT TIME, THE ESTIMATED QUANTITY GAS RELEASED WAS DETERMINED TO BE 39 MCF FROM THE INITIAL NOTIFICATION RECEIVED FROM THE PUBLIC BY GAS CONTROL AT 12:41 PM LOCAL TIME TO THE TIME OPERATION'S PERSONNEL ARRIVED ON SITE. AT THIS TIME, OPERATIONS BEGAN SERVICING THE VALVE TO STOP THE LEAK FROM THE ACTUATOR VENT. AT 17:00 PM LOCAL TIME, NGPL OPERATIONS REPORTED THAT ATTEMPTS TO STOP THE LEAK WITH APPLICATION OF VALVE GREASE WAS NOT COMPLETELY SUCCESSFUL AS THE LEAKING STOPPED BRIEFLY BUT CONTINUED INTERMITTENTLY. AT 17:10 PM LOCAL TIME, OPERATIONS DECIDES TO REMOVE THE VALVE FROM SERVICE AND ESTIMATES THE COST WOULD BE GREATER THAN $50,000. AT 17:15 PM LOCAL TIME, THE NATIONAL RESPONSE CENTER WAS NOTIFIED (NRC REPORT NO. 1284223). THE 48-HOUR UPDATE COMMUNICATING NO SIGNIFICANT CHANGES WAS COMPLETED AT 16:25 PM LOCAL TIME ON 08/11/2020 (NRC REPORT NO. 1284327). INVESTIGATION: RESULTS OF THE INVESTIGATION SHOWED THAT THE VALVE X893E2, 20' PLUG VALVE INSTALLED IN 1957, PROVIDES CROSSOVER ISOLATION BETWEEN THE #2 AND #3 AMARILLO MAINLINES. APPLICATION OF GREASE DOWN THE CENTER GREASE FITTING FORCES THE STEM PACKING AROUND THE VALVE STEM, SEALING IT, AND PREVENTING GAS FROM TRAVELING UP THE VALVE STEM AND EXITING THE ACTUATOR VENT. AS DISCUSSED ABOVE, OPERATIONS ATTEMPTED TO STOP THE LEAK FROM THE ACTUATOR VENT BY SERVICING THE VALVE WITH GREASE; HOWEVER, THIS ACTION DID NOT COMPLETELY STOP THE LEAK. AT THAT TIME (APPROXIMATELY 17:10 PM LOCAL TIME), NGPL OPERATIONS DECIDED TO REMOVE THE VALVE AND ASSOCIATED CROSSOVER PIPING FROM SERVICE TO AVOID HAVING TO TAKE BOTH THE NGPL AMARILLO MAINLINES NO. 2 AND NO. 3 OUT OF SERVICE, ADVERSELY AFFECTING NATURAL GAS DELIVERIES TO CUSTOMERS DOWNSTREAM FROM THE LOCATION. THE INVESTIGATION DETERMINED THAT ONLY A SMALL AMOUNT OF HARD AND INEFFECTIVE STEM PACKING REMAINED IN THE PLUG ASSEMBLY. THE IMMEDIATE/DIRECT CAUSE OF THE EVENT WAS DETERMINED TO BE THE STEM PACKING IN THE SERVICE LINE WAS DEPLETED AND NO LONGER SERVICEABLE. THE BASIC/ROOT CAUSES INCLUDED THE AGE AND SERVICEABILITY OF THE STEM PACKING. CORRECTIVE ACTIONS: REVIEW VALVE SERVICING AND MAINTENANCE PROCEDURES WITH ALL NGPL OPERATORS INVOLVED IN VALVE SERVICING/MAINTENANCE FOR THESE TYPES OF VALVES TO LIMIT VALVE-PACKING LEAKAGE GOING FORWARD. NGPL REMOVED THE VALVE FROM SERVICE AS DESCRIBED ABOVE.
2021-02-26 10:37 | YES | NO | UNGS (Underground Natural Gas Storage) | 20200092 | 34239 | 2020-09-04 13:21 | ORIGINAL | 11824 | LOUISVILLE GAS & ELECTRIC CO | 220 W MAIN ST, PO BOX 32010 | LOUISVILLE | KY | 40202 | 2020-08-06 16:15 | 2020 | EASTERN | YES | 37.9954 | -86.0671 | 1283906 | 2020-08-06 16:15 |  | NATURAL GAS |  | 12324 | 0 | 428 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | STORAGE FIELD WAS NOT SHUT DOWN. SEE NARRATIVE (SEC. 8) RE STEPS TAKEN ON WELL. |  |  |  | YES | OPERATOR | 2020-08-06 15:45 | NO | [11 empty] | 0 | 2020-08-06 14:30 | 2020-08-06 15:15 | ONSHORE | IN | 47135 | LACONIA, IN | HARRISON COUNTY, IN | NOT APPLICABLE |  | DOE RUN STORAGE FIELD | A. H. PERKINS 5 GAS STORAGE WELL | NO | PIPELINE RIGHT-OF-WAY | BELOWGROUND STORAGE OR ABOVEGROUND STORAGE VESSEL, INCLUDING ATTACHED APPURTENANCE |  |  |  |  | NO | [22 empty] | INTRASTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | OTHER | [37 empty] | WELL CASING PIPE AT THREADED COLLAR | 1984 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | WELL CASING PIPE FAILURE AT CASING COLLAR. | CLASS 1 LOCATION | NO |  | 3500 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 30136 | 30136 | 42222 | 42222 | 758855 | 758855 | 0 | 0 |  | 2.4453 | 831213 | 398958.840464839 | 831213 | 0 | 0 | 0 | 0 | NO |  |  |  | 179 | 4000 | 305 | OTHER | WELL CASING THAT FAILED DOES NOT FALL UNDER 192.619 OR 192.620 | 1970-07-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION IN STORAGE FIELD | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | YES | 4 | 0 | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | OTHER | WELL CASING PIPE AT THREADED CASING COLLAR | [18 empty] | YES | NOT KNOWN AT THIS TIME. | [161 empty] | BARRY WALKER | DIRECTOR GAS CONTROL AND STORAGE | barry.walker@lge-ku.com | 502-627-3038 |  | BARRY WALKER | barry.walker@lge-ku.com | 502-627-3038 | J. GREGORY CORNETT | DIRECTOR LEGAL SERVICES-ASSOCIATE GENERAL COUNSEL | 502-627-2756 | greg.cornett@lge-ku.com | AT APPROXIMATELY 2:30 PM ON AUGUST 6, 2020, THE 4.5-INCH WELL CASING PIPE ON THE A.H. PERKINS #5 GAS STORAGE WELL FAILED AT AN ABOVE GROUND THREADED CASING COLLAR BELOW THE STORAGE WELL MASTER VALVE, RESULTING IN THE ACCIDENTAL RELEASE OF NATURAL GAS AND BRINE WATER. AT THE TIME OF THE FAILURE A COMPANY CONTRACTOR CREW WAS INSTALLING AN UNDERGROUND PIPELINE DRIP ON A PIPELINE SEGMENT CONNECTED TO THE STORAGE WELL. NO INJURIES, IGNITION, OR EXPLOSION RESULTED FROM THE INCIDENT. COMPANY GAS EMERGENCY PROCEDURES WERE IMPLEMENTED AND A WELL CONTROL RESPONSE TEAM FROM WILD WELL CONTROL WAS MOBILIZED. A WELL CAPPING PLAN WAS DEVELOPED AFTER WILD WELL CONTROL PERFORMED AN ON-SITE ASSESSMENT. SITE PREPARATION, EQUIPMENT MOBILIZATION, AND WELL CASING PIPE PREPARATION FOR THE WELL CAPPING OPERATION WAS CONDUCTED AUGUST 7TH THROUGH AUGUST 10TH. THE WELL WAS SUCCESSFULLY CAPPED AND GAS FLOW WAS STOPPED AT 8:53 AM ON AUGUST 11TH. AT THIS TIME, THE CAUSE OF THE FAILURE AT THE CASING COLLAR IS NOT KNOWN. D3 - COMPONENT THAT FAILED IS GAS STORAGE WELL CASING, SO PIR DOESN'T APPLY. THE 3,500 IS BASED ON THE NEAREST OCCUPIED BUILDING. E2-3 - BECAUSE THE FIELD REQUIRED A NUMERICAL VALUE WE USED THE PIPELINE SYSTEM MAOP. HOWEVER, THE WELL CASING THAT FAILED DOES NOT FALL UNDER 192.619 OR 192.620. E9 - THERE IS NOT A CHOICE FOR RESERVOIR GAS STORAGE WELL. WE CHOSE THE CLOSEST AVAILABLE OPTION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200093 | 34266 | 2020-09-11 17:11 | ORIGINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2020-08-12 00:13 | 2020 | CENTRAL | YES | 30.4663 | -92.5226 | 1284343 | 2020-08-12 02:47 | 1284470 | NATURAL GAS |  | 50200 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-08-12 01:36 | 2020-08-12 08:20 |  | YES | OPERATOR | 2020-08-12 02:11 | NO | [11 empty] | 0 | 2020-08-12 00:13 | 2020-08-12 01:25 | ONSHORE | LA | 70535 | EUNICE | ACADIA | NOT APPLICABLE |  | EUNICE COMPRESSOR STATION | ANR 501 MAINLINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1973 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | VALVE FAILED TO CLOSE COMPLETELY | CLASS 1 LOCATION | NO |  | 731 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 109938 | 109938 | 55000 | 55000 | 0 | 0 | 0 | 0 |  | 2.19 | 164938 | 139224.167811232 | 164938 | 0 | 0 | 0 | 0 | NO |  |  |  | 643 | 2000 | 903 | 192.619(A)(2) |  | 2015-11-08 | YES | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER RESPONDED APPROPRIATELY ACCORDING TO PROCEDURES AND DISPATCHED A TECHNICIAN TO THE SITE WHEN THE ALARM WAS DETECTED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [5 empty] | YES | [19 empty] | YES | [167 empty] | ROGER R STREET | COMPLIANCE SPECIALIST | roger_street@tcenergy.com | 615-465-5123 |  | ROGER R STREET | roger_street@tcenergy.com | 615-465-5123 | ERIK HUGHES | SENIOR COMPLIANCE MANAGER USGO AND KEYSTONE | 402-492-7447 | erik_hughes@tcenergy.com | ON 12 AUGUST 2020, TC ENERGY/ ANR PIPELINE COMPANY (ANR) REPORTED AN INCIDENT TO THE NATIONAL RESPONSE CENTER (NRC) (NRC REPORT NUMBER 1284343) FOLLOWING THE UNINTENTIONAL RELEASE OF 50.2 MILLION CUBIC FEET OF GAS TO THE ATMOSPHERE FROM THE EUNICE COMPRESSOR STATION LOCATED AT 4202 FOURNERAT ROAD IN EUNICE LOUISIANA (30.46632200, -92.52257600). THE RELEASE WAS CAUSED WHEN THE STATION FIRE DETECTION SYSTEM RECEIVED AN INDICATION OF A FLAME AND INITIATED THE EMERGENCY SHUTDOWN (ESD) SYSTEM. WHEN THE ESD WAS INITIATED, THE GAS CONTROLLER RECEIVED A SCADA ALARM AND DISPATCHED A TECHNICIAN TO THE SITE TO INVESTIGATE. WHEN THE TECHNICIAN ARRIVED AT THE SITE, NATURAL GAS WAS DISCOVERED BEING RELEASED THROUGH THE STATION BLOWDOWN. IMMEDIATE ACTION WAS TAKEN TO STOP THE RELEASE BY CLOSING BLOWDOWN VALVE AND SECURING THE SITE. SINCE THE INCIDENT, EUNICE COMPRESSOR STATION HAS REMAINED STAFFED 24-HOURS A DAY UNTIL REPAIRS CAN BE COMPLETED ON THE ISOLATION VALVE. INITIAL INVESTIGATION HAS INDICATED THAT THE ACTIVATION OF THE ESD SYSTEM AND FAILURE OF THE ISOLATION VALVE TO COMPLETELY OPERATE CONTRIBUTED TO THE GAS LOSS. NO EVIDENCE OF FLAME OR FIRE WERE OBSERVED IN THE COMPRESSOR BUILDING FOLLOWING THE INCIDENT THAT WOULD INITIATE THE ESD. ADDITIONALLY, AN AUTOMATIC ISOLATION VALVE FAILED TO COMPLETELY CLOSE RESULTING IN THE CONTINUING RELEASE OF GAS TO THE ATMOSPHERE THROUGH THE STATION'S BLOWDOWN STACK. INVESTIGATION HAS DETERMINED THAT THREE-WAY PILOT GAS VALVES AND END-OF-TRAVEL STOP VALVES ASSOCIATED WITH AUTOMATIC OPERATION CONTRIBUTED TO THE INCOMPLETE CLOSURE OF THE ISOLATION VALVE. ANR IS CURRENTLY EVALUATING THE COMPONENTS NEEDED TO REPAIR THE ISOLATION VALVE AND ADDITIONALLY ANY OTHER VALVES ASSOCIATED WITH THE ESD SYSTEM WITH A SIMILAR DESIGN. THE STATION WILL REMAIN STAFFED 24 HOURS PER DAY UNTIL REPAIRS ON THE VALVES ARE COMPLETED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200094 | 34268 | 2020-09-14 09:50 | ORIGINAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2020-08-20 09:25 | 2020 | CENTRAL | YES | 29.9807 | -91.8208 | 1285056 | 2020-08-20 10:13 | 1285144 | NATURAL GAS |  | 142.9 | 102 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | MINOR LEAK; ARRANGEMENTS TO KEEP CUSTOMERS IN SERVICE DURING REPAIR |  |  |  | YES | OPERATOR | 2020-08-20 09:03 | NO | [5 empty] | OPERATIONAL CONTROL | LOWERED OPERATING PRESSURE BY 20% AT JEANERETTE CHECK STATION. |  | OPERATIONAL CONTROL | LINE IS CUT AND CAPPED ON NORTH END. INSERTED A PLUG IN A STOPPLE FITTING ON AUG.31 |  | 0 | 2020-08-20 09:03 | 2020-08-20 08:40 | ONSHORE | LA | 70560 | Not Within a Municipality | IBERIA | SURVEY STATION NO. | 7170+98 | CALL JUNCTION TO FRANKLIN | INDEX 205 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | DRESSER COUPLING | 1931 | 1931 | CARBON STEEL |  | LEAK |  |  | OTHER | LEAKING DRESSER COUPLING | [5 empty] | CLASS 2 LOCATION | NO |  | 137 |  | NO | NO |  |  | 0 | 0 | 189 | 189 | 264 | 264 | 108000 | 108000 | 0 | 0 | 0 | 0 |  | 1.85 | 108453 | 49935.3065524455 | 108453 | 0 | 0 | 0 | 0 | NO |  |  |  | 262 | 600 | 480 | 192.619(C) |  | 2018-03-20 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES |  |  | 21397 | NO | [5 empty] | YES | DRESSER COUPLES | YES |  | YES |  |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | MECHANICAL COUPLING | [19 empty] | YES | EXPANSION & CONTRACTION OF PIPE OVER THE YEARS CAUSING COUPLING TO BECOME LOOSE | [161 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 2709035764 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 2703146547 | tina.baker@bwpipelines.com | ON 8/20/2020 AT 07:40, GULF SOUTH GAS CONTROL RECEIVED CALL FROM LANDOWNER REGARDING SUSPECTED SMELL OF GAS. GAS CONTROL CONTACTED LOCAL OPERATIONS PERSONNEL. AT 08:40 OPERATIONS PERSONNEL CONFIRMED GAS SMELL AND PROBABLE LEAK ON AND NEAR GULF SOUTH ASSETS. GULF SOUTH LOWERED THE PRESSURE ON THE PIPELINE BY 20% OF OPERATING PRESSURE (FROM 262 PSIG TO 209 PSIG) PRIOR TO EXCAVATION DUE TO PIPELINE HAVING KNOWN DRESSER COUPLES AS CONNECTORS. AT 08:45, A CONTRACTOR WAS CONTACTED TO EXCAVATE POTENTIAL LEAK SITE. AT 09:03 LA HAZMAT WAS CONTACTED TO REPORT POTENTIAL LEAK. AT 09:30 IT WAS CONFIRMED THAT THE LEAK WAS ON GULF SOUTH'S PIPELINE AND CAUSED BY LEAKING DRESSER COUPLE. LOCAL OPERATIONS PERSONNEL CONTACTED GAS CONTROL AT 09:45 TO INFORM THAT REPAIRS WOULD EXCEED $50,000 DUE TO TYPE OF REPAIR NEEDED. AT 10:13, GAS CONTROL CONTACTED NRC TO REPORT LEAK EXCEEDING $50,000 COST TO REPAIR. ON 8/31/20 THE LEAK WAS STOPPED BY ISOLATING SECTION OF PIPELINE WITH STOPPLE FITTING AND BLOWING DOWN GAS. A TYPE 220 WELD OVER SLEEVE WAS INSTALLED AND THE LINE WAS RETURNED TO SERVICE. TEMPORARY GAS SUPPLY WAS UTILIZED TO PREVENT LOSS OF SERVICE TO CUSTOMERS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200095 | 34870 | 2020-09-16 10:39 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2020-08-18 08:32 | 2020 | CENTRAL | YES | 31.7322 | -101.8011 | 1284828 | 2020-08-18 09:41 | 1285016 | NATURAL GAS |  | 20747 | 107 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-08-18 09:36 | 2020-08-23 19:05 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-08-18 08:50 | YES | 2020-08-18 08:32 | ALLOWED TO BURN OUT |  | 20747 | YES | VALVE CLOSURE |  | 2020-08-18 08:44 | VALVE CLOSURE |  | 2020-08-18 09:36 | 0 | 2020-08-18 09:36 | 2020-08-18 08:47 | ONSHORE | TX | 79755 | MIDKIFF | MIDLAND | MILEPOST | MP 6-0865 | EPNG L3125 | LAUNCHER TO SPRAYBERRY PLANT | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 57 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 | NO | 0.335 | 52000 | API 5L | FLASH WELDED |  | AO SMITH | COAL TAR |  | YES | [26 empty] | 1953 | 1953 | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | PIPE WAS RUPTURED LONGITUDINALLY AT THE 12 O'CLOCK POSITION AND 10' OF PIPE WAS EJECTED FROM THE DITCH. |  |  |  | CLASS 1 LOCATION | NO |  | 593 |  | NO | NO |  |  | 591348 | 591348 | 173 | 173 | 33589 | 33589 | 159136 | 159136 | 2000 | 2000 | 59481 | 59481 | INVESTIGATION COSTS - 3RD PARTY METALLURGICAL ANALYSIS, SITE SURVEY, TRAVEL, ETC | 1.619 | 845727 | 407616.013219359 | 845727 | 0 | 0 | 0 | 0 | NO |  |  |  | 570 | 18800 | 820 | 192.619(A)(1) |  | 1953-07-01 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | REMOTELY CONTROLLED | MANUAL | 62832 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [103 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [261 empty] | DANIEL GRANT | PIPELINE ENGINEER | daniel_grant@kindermorgan.com | 7134204409 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR - ENGINEERING | 7133699443 | jaime_hernandez@kindermorgan.com | ON AUGUST 18, 2020 EL PASO NATURAL GAS COMPANY, L.L.C. (EPNG) 30-INCH L3125 EXPERIENCED AN IN-SERVICE FAILURE AT A 3RD PARTY LINE CROSSING WITH A TARGA PIPELINE. AUGUST 18, 2020 - ALL TIMES ARE CDT: 7:37 AM TARGA EDWARDS RECEIPT METER (041787) FLOW WENT TO ZERO ON EPNG'S SCADA AND EMERGENCY 911 CALL RECEIVED BY MIDLAND DISPATCH ["TANK BATTERY FIRE" NOTED AT 07:38] 8:03 AM EPNG GAS CONTROL (GC) RECEIVED A CALL FROM AMERICAN PIPELINE PATROL PILOT STATING THERE WAS A FIRE POSSIBLY OVER TARGA'S OR EPNG'S PIPE. 8:07 AM EPNG GC MADE A PHONE CALL TO EPNG DAMAGE PREVENTION SUPERVISOR TO INFORM OF POSSIBLE FIRE. EPNG DAMAGE PREVENTION INITIATES PROCESS TO DISPATCH SOMEONE TO INVESTIGATE. 8:29 AM MIDLAND FIRE DEPARTMENT BATTALION CHIEF (BAT2) ARRIVED ON-SITE. 8:32 AM EPNG GC OBSERVED THAT PRESSURE AT TARGA OWENS RECEIPT RANCH AND TARGA MIDKIFF RECEIPT METER DROPPED TO AT OR NEAR 0 PSI. ROC ALARMS RECEIVED. 8:36 AM SECONDARY EXPLOSION WITNESSED BY MIDLAND FIRE DEPARTMENT (BAT2) 8:39 AM EPNG GC SET TARGA OWENS RECEIPT RANCH CONTROL VALVE TO ZERO TO ENSURE THAT FLOW WOULD NOT OCCUR. THE METER FLOW WAS ALREADY AT ZERO. 8:44 AM EPNG GC ADJUSTED JAMESON POOL CHECK METER (301166) PRESSURE CONTROL VALVE SETPOINT SET TO ZERO TO ENSURE THAT THE VALVE WAS CLOSED TO ISOLATE L3130 FROM L3125. 8:47 AM EPNG LINE PATROLLER ARRIVED AT MUSTER SITE WITH MIDLAND FIRE DEPARTMENT & TARGA ON SITE AND CONTROLLING THE SITE ACCESS 8:56 AM EPNG GC CONFIRMED TARGA MIDKIFF RECEIPT METER FLOW SHUT OFF 9:00 AM EPNG GC SPOKE TO NAVITAS AND ASKED TO TAKE NAVITAS PHILLIPS SPRAYBERRY RECEIPT METER METER FLOW TO ZERO. 9:36 AM MLV 3 ON L3125 SHUT (LOTO OCCURRED SHORTLY AFTER), ISOLATING THE SEGMENT. BASED ON FIELD OBSERVATION OF FIRE DIMINISHING UPON MLV 3 BEING SHUT, EPNG CONFIRMED DISCOVERY OF THE INCIDENT 9:41 AM EPNG PLACED THE CALL TO THE NRC, MAKING OFFICIAL NOTIFICATION OF THE EVENT. 10:05 AM MLV 0.5 (L3130) SHUT-IN & LOTO BY OPERATIONS. (VALVE IS A SECONDARY VALVE TO THE PRESSURE CONTROL VALVE AT JAMESON POOL CHECK) 10:20 AM MLV 4 (L3125) SHUT-IN & LOTO BY OPERATIONS. AT APPROXIMATELY 11:45 AM - 12:00 PM MIDLAND FIRE DEPARTMENT LEFT THE SITE, HOWEVER EPNG DID NOT GAIN ACCESS TO THE SITE DUE TO 24" TARGA PIPELINE IN THE VICINITY. TARGA WANTED TO BLOW DOWN PIPELINE BEFORE ALLOWING EPNG INTO SITE. AT APPROXIMATELY 4:10 PM TARGA COMPLETED DEPRESSURIZATION OF 24" PIPELINE AND EPNG OPERATIONS WAS ABLE TO ACCESS RUPTURE SITE & OWENS RANCH TAP FOR LOTO. TARGA PERSONNEL, ONCOR PERSONNEL, AND A REPRESENTATIVE OF THE TEXAS RAILROAD COMMISSION PIPELINE SAFETY DEPARTMENT ALSO ENTERED THE SITE. AFTER COMPLETION OF REPAIRS THE PIPE WAS PLACED BACK INTO SERVICE ON AUGUST 23, 2020. AS A PART OF THE EVENT THERE WERE DAMAGES TO A NEARBY ELECTRIC POWER TRANSMISSION FACILITY. THE CAUSE OF THE FIRE WAS A CROSSING TARGA PIPELINE THAT HAD RUPTURED UNDERNEATH THE EPNG 30-INCH L3125 PIPELINE. THE RUPTURE ON THE EPNG 30-INCH L3125 PIPELINE OCCURRED ON THE PIPE BODY WHERE THE PIPE WALL HAD THINNED TO THE LOWEST MEASURED VALUE OF 0.111" FROM AN OTHERWISE NOMINAL WALL THICKNESS OF 0.335". THE LOCALLY THINNED AREA OF THE EPNG PIPE WAS DUE TO HEAT EXPOSURE AND INTERNAL PRESSURE. THERE WAS NO EVIDENCE OF OTHER DAMAGE MECHANISMS OR MATERIAL FAILURES INCLUDING, BUT NOT LIMITED TO, WALL LOSS DUE TO INTERNAL OR EXTERNAL CORROSION, ENVIRONMENTALLY-ASSISTED CRACKING, LONGITUDINAL OR GIRTH WELD ISSUES, DENTS/GOUGES, OR MANUFACTURING DEFECTS.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200096 | 34685 | 2020-09-17 10:40 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2020-08-29 08:45 | 2020 | CENTRAL | YES | 29.8141 | -93.0926 | 1285937 | 2020-08-29 12:46 | 1286038 | NATURAL GAS |  | 7062 | 6000 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-08-29 13:30 | 2020-11-16 10:00 |  | YES | OPERATOR | 2020-08-29 08:30 | NO | [5 empty] | VALVE CLOSURE |  | 2020-08-29 13:24 | OPERATIONAL CONTROL | NO DOWNSTREAM ACTION REQUIRED. THIS IS THE END OF THE PIPELINE. |  | 0 | 2020-08-29 08:45 | 2020-08-29 13:24 | ONSHORE | LA | 70632 | Not Within a Municipality | CAMERON | SURVEY STATION NO. | 89+23 | CREOLE 6" LINE | INDEX 192 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 44 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1960 | 1960 | CARBON STEEL |  | LEAK |  |  | OTHER | BROKEN BODY BLEED SET VALVE | [5 empty] | CLASS 1 LOCATION | NO |  | 149 |  | NO | NO |  |  | 0 | 0 | 11100 | 11100 | 13065 | 13065 | 20000 | 20000 | 21500 | 21500 | 0 | 0 |  | 1.85 | 65665 | 37689.866687558 | 65665 | 0 | 0 | 0 | 0 | NO |  |  |  | 650 | 1 | 965 | 192.619(C) |  | 2018-03-19 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL |  | 34268 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | AIR PATROL |  | CONTRACTOR WORKING FOR THE OPERATOR | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [52 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | HURRICANE LAURA | YES | YES | [305 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 270.903.5764 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 270.314.6547 | tina.baker@bwpipelines.com | ON 8/27/2020 AT 19:58, GULF SOUTH RECEIVED REPORT OF A POSSIBLE LEAK DUE TO AIR PATROL OBSERVING BUBBLES IN THE FLOODED STORM SURGE IN CREOLE, LA. GULF SOUTH ACQUIRED A HELICOPTER TO FLY PERSONNEL TO THE SITE AS SOON AS POSSIBLE; ATTEMPTS TO ACCESS THE LOCATION WERE MADE ON 8/28/2020 AT 07:00 AND 13:00 BUT WERE UNSUCCESSFUL DUE TO STORM SURGE FLOODING AND AREA BEING UNDER WATER. ON 8/29/2020, LOCAL OPERATIONS MANAGEMENT NOTIFIED LA HAZMAT AT 08:38. THE LEAK WAS VERIFIED AND WAS LIKELY ON GULF SOUTH'S PIPELINE ALTHOUGH THE SITE STILL COULD NOT BE REACHED. THE 20" MAIN LINE (INDEX 195) WAS SHUT IN AND THE SECTION WAS ISOLATED. THE ONLY CUSTOMER SERVED BY THIS PIPELINE, CENTERPOINT, WAS NOTIFIED. ON 8/31/2020 THE LEAK WAS CHECKED AGAIN AND PERSONNEL WERE ABLE TO ACCESS THE 6" TAP VALVE AND CLOSE IT AT 11:00. BY 9/1/2020 AT 08:30, THE LEAK HAD SUBSIDED. TO DATE, THE AREA REMAINS INACCESSIBLE FOR EVALUATION. ONCE SITE BECOMES ACCESSIBLE FURTHER EVALUATION WILL BE DONE AND A SUPPLEMENTAL REPORT WILL BE SUBMITTED. THE RESPONSE PROVIDED TO PART E, QUESTION 1A SHOULD ACTUALLY BE .133 MCF; HOWEVER, THE PORTAL WILL NOT ALLOW A VALUE LESS THAN 1, THEREFORE, 1 IS THE PROVIDED RESPONSE. 1/5/2021 UPDATE FOR FINAL REPORT INCLUDING CHANGE REQUESTED BY PHMSA, COST, LEAK TYPE. GULF SOUTH WAS ABLE TO ACCESS THE SITE ON 11/12/2020; EXCAVATED VALVE SITE AND DISCOVERED A BROKEN BODY BLEED ON A VALVE. THE VALVE WAS FLANGED ON THE PIPELINE SO GULF SOUTH REMOVED THE VALVE AND BOLTS AND BLIND FLANGED THE TAP FLANGE ON THE PIPELINE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200097 | 34751 | 2020-09-17 13:04 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2020-08-19 12:59 | 2020 | PACIFIC | YES | 39.1783 | -123.21 | 1285001 | 2020-08-19 15:43 | 1285110 | NATURAL GAS |  | 25 | 0.41 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | POST-MAINTENANCE/REPAIR | [5 empty] | YES | OPERATOR | 2020-08-19 12:59 | YES | 2020-08-19 12:59 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 25 | NO | VALVE CLOSURE |  | 2020-08-19 17:30 | VALVE CLOSURE |  | 2020-08-19 19:41 | 75 | 2020-09-08 12:59 | 2020-08-19 12:59 | ONSHORE | CA | 95482 | UKIAH | MENDOCINO | MILEPOST | 116.24-.39 | L021E | MP 116.24-.39 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER PAVEMENT |  |  | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 | YES | 0.188 | 42000 | API_5LX-X42 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | ASPHALT |  | YES | [26 empty] | 1968 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 0.1 | 0.1 | [7 empty] | CLASS 3 LOCATION | YES | METHOD1 | 147 |  | NO | NO |  |  | 0 | 0 | 1 | 1 | 75 | 75 | 100000 | 100000 | 18000 | 18000 | 0 | 0 |  | 3 | 118076 | 54243.3285781583 | 118076 | 0 | 0 | 0 | 2 | NO |  |  |  | 420 | 420 | 610 | 192.619(A)(2) |  | 1968-05-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 1 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT, A PINHOLE BLOW THROUGH, OCCURRED DURING A WELDING ON A CLEARANCE, SO OPERATOR EMPLOYEES AND CONTRACTORS WERE ALREADY ON SITE. | [12 empty] | NO |  |  | YES | 1 | 0 | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | [204 empty] | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | [6 empty] | YES | A QUALIFIED PROCEDURE WAS USED AS WELL AS A QUALIFIED WELDER. PG&E HAD CONTINUAL OBSERVATION OF THE WORK VERIFYING COMPLIANCE TO THE PROCEDURE. THE LEAK LOCATION ON THE PIPE WAS DESTROYED IN THE PROCESS OF RESTORING THE SYSTEM BACK TO SERVICE, SO NO ROOT CAUSE COULD BE CONCLUSIVELY DEVELOPED. | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | VINCENZA BARBATO | PROGRAM MANAGER | e1bo@pge.com | [5 empty] | SUSIE RICHMOND | MANAGER OF GAS REGULATORY COMPLIANCE | 925-786-0267 | gsr8@pge.com | ON WEDNESDAY, AUGUST 19, 2020 AT 1259 HOURS, PG&E WAS NOTIFIED OF AN UNINTENTIONAL RELEASE OF GAS WITH IGNITION AT 2147 N. STATE ST IN UKIAH, CA. DURING A CLEARANCE ON PLANNED PROJECT R-583 TO RE-ROUTE L-21E, A WELDER WAS WELDING A 2" SAV-A-VALVE ON L-21E MP 115.5 WHEN HE BREACHED THE PIPELINE, CREATING A PIN HOLE LEAK THAT SUBSEQUENTLY IGNITED. ONSITE EMPLOYEES CALLED 911. POLICE PERFORMED STREET CLOSURES AND TRAFFIC CONTROL, AND FIRE DEPARTMENT PERFORMED LOCAL EVACUATIONS (MENDOCINO SHERIFF'S OFFICE ISSUED AN EVACUATION ORDER TO THE GENERAL PUBLIC FROM 3 ZONES SURROUNDING THE INCIDENT. THE NUMBER POPULATED IN A23 IS AN ESTIMATE BASED ON THE NUMBER OF BUILDINGS IN THESE ZONES). THE LINE WAS ISOLATED AT 1730 HOURS AND WAS RETURNED TO SERVICE BY 1941 HOURS. THERE ARE NO REPORTED INJURIES OR FATALITIES. TWO LARGE VOLUME CUSTOMERS WERE IMPACTED FROM 2200 HOURS TO 900 HOURS THE NEXT MORNING. A QUALIFIED PROCEDURE WAS USED AS WELL AS A QUALIFIED WELDER. PG&E HAD CONTINUAL OBSERVATION OF THE WORK VERIFYING COMPLIANCE TO THE PROCEDURE. THE LEAK LOCATION ON THE PIPE WAS DESTROYED IN THE PROCESS OF RESTORING THE SYSTEM BACK TO SERVICE, SO NO ROOT CAUSE COULD BE CONCLUSIVELY DEVELOPED. THIS SAFETY MATTER WAS REPORTED AS A DOT INCIDENT (#1285001) DUE TO THE COMBINATION OF A RELEASE OF GAS RESULTING IN ESTIMATED PROPERTY DAMAGE OF AT LEAST $50K REQUIRING IMMEDIATE MITIGATION TO PROTECT PEOPLE OR PROPERTY. PLEASE NOTE: AN ALCOHOL TEST OF THE CONTRACTOR INVOLVED WAS NOT GIVEN WITHIN 8 HOURS DUE TO EXIGENT CIRCUMSTANCES RELATED TO THE CALIFORNIA WILDFIRES, A DRUG TEST WAS GIVEN AND PASSED. THIS DELAY WAS THE RESULT OF THE UNPRECEDENTED CONFLUENCE OF UNCOMMON OCCURRENCES INCLUDING A CONTRACTOR-INVOLVED DOT-REPORTABLE INCIDENT AND WILDFIRE RELATED TRAFFIC AND PERSONNEL EVACUATION ACTIVITIES. AS SUCH, IT HAS BEEN EVALUATED AS UNLIKELY TO REOCCUR, EVEN WITHOUT THE IMPLEMENTATION OF ANY CORRECTIVE ACTIONS.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200098 | 34881 | 2020-09-24 13:51 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2020-08-28 05:00 | 2020 | PACIFIC | YES | 38.5924 | -121.5556 | 1285835 | 2020-08-28 08:00 | 1285915 | NATURAL GAS |  | 531 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-08-28 11:55 | 2020-08-28 21:34 |  |  |  |  | NO | [11 empty] | 0 | 2020-08-28 05:00 | 2020-08-28 05:25 | ONSHORE | CA | 95605 | WEST SACRAMENTO | YOLO | NOT APPLICABLE |  | WS-004 | WS-004 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1975 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | VEHICLE IMPACT | CLASS 3 LOCATION | YES | METHOD1 | 44 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 1593 | 1593 | 46000 | 46000 | 8000 | 8000 | 0 | 0 |  | 3 | 55593 | 26438.9603220372 | 55593 | 0 | 0 | 0 | 0 | NO |  |  |  | 45 | 45 | 50 | 192.619(A)(2) |  | 1975-06-10 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [9 empty] | UNKNOWN | [5 empty] | UNKNOWN |  | YES | LARGE TRUCK | ROADWAY | 10 | YES |  |  |  | YES | FENCING | [233 empty] | ENZA BARBATO | PROGRAM MANAGER | e1bo@pge.com | [5 empty] | SUSIE RICHMOND | MANAGER REGULATORY COMPLIANCE | 925-786-0267 | gsr8@pge.com | ON FRIDAY, AUGUST 28, 2020, AT APPROXIMATELY 05:00 HOURS, PG&E WAS NOTIFIED OF VEHICLE IMPACT TO A REGULATOR STATION, CAUSING A RELEASE OF GAS NEAR 3500 REED AVE, WEST SACRAMENTO. PG&E'S GAS SERVICE REPRESENTATIVE WAS ON SITE APPROXIMATELY AT 05:25 HOURS. PG&E CREWS ARRIVED ON-SITE AND STOPPED THE FLOW OF GAS AT 11:55 HOURS. THE CREW CUT AND CAPPED 8 FEET OF 4" PIPE GOING INTO THE REGULATOR STATION. THE 2" TRANSMISSION WAS TURNED OFF AT VALVE V-1 AND A BLIND FLANGE WAS INSTALLED IN THE STATION. 1 CUSTOMER WAS AFFECTED BUT WAS RETURNED TO SERVICE BY 21:38 HOURS. PG&E IS CURRENTLY ASSESSING A REBUILD AND POSSIBLE RELOCATION OF THIS STATION. THERE WERE NO OF INJURIES AND NO FATALITIES. THERE WAS MEDIA (CHANNEL 31), POLICE, FIRE DEPARTMENT REPORTED. THIS SAFETY MATTER WAS REPORTED AS A DOT INCIDENT (#1285835) DUE TO THE COMBINATION OF A RELEASE OF GAS RESULTING IN ESTIMATED PROPERTY DAMAGE OF AT LEAST $50K REQUIRING IMMEDIATE MITIGATION TO PROTECT PEOPLE OR PROPERTY.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200099 | 34917 | 2020-09-30 11:48 | SUPPLEMENTAL FINAL | 2564 | COLORADO INTERSTATE GAS CO | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2020-08-31 16:44 | 2020 | MOUNTAIN | YES | 41.6995 | -110.3646 | 1286190 | 2020-09-01 09:06 | 1286364 | NATURAL GAS |  | 150000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | ROUTINE SHUTDOWN | [5 empty] | NO |  |  | NO | [11 empty] | 0 | 2020-09-01 06:50 | 2020-09-01 06:50 | ONSHORE | WY | 83101 | KEMMERER | LINCOLN | NOT APPLICABLE |  | ROBERSON CREEK COMPRESSOR STATION | RUBY MAINLINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2010 | 2010 | CARBON STEEL |  | LEAK |  |  | OTHER | RELEASE THROUGH VENT | [5 empty] | CLASS 1 LOCATION | NO |  | 1100 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 321000 | 321000 | 100 | 100 | 100 | 100 | 0 | 0 |  | 2.14 | 321200 | 332887.080867918 | 321200 | 0 | 0 | 0 | 0 | NO |  |  |  | 1250 | 245 | 1440 | 192.619(A)(2) |  | 2011-07-27 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WERE NO INDICATIONS THAT CONTROLLER ACTION CONTRIBUTED TO THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | PLC MALFUNCTION SIGNALED DISCHARGE VALVE TO OPEN. FURTHER DETAILS PROVIDED IN THE NARRATIVE. | [22 empty] | YES | LISTED SUB CAUSES ARE N/A, SEE NARRATIVE FOR ADDITIONAL SUB CAUSE DISCUSSION | [161 empty] | SHELLEY DIETZ | PIPELINE ENGINEER | shelley_dietz@kindermorgan.com | [5 empty] | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | ON AUGUST 31, 2020, THE ROBERSON CREEK COMPRESSOR STATION WAS ON LINE AND ONE OF THE THREE UNITS WAS OPERATING. DURING THE DAY, OPERATIONS WAS WORKING WITH THE ORIGINAL EQUIPMENT MANUFACTURER TO INSPECT UNIT #2 VARIABLE FREQUENCY DRIVE (VFD) FOR THE PRIMARY DRIVER/ELECTRIC MOTOR. DURING THE INSPECTION, ONLY THE POWER TO THE VFD HAD BEEN LOCKED OUT AND NOTHING WAS TOUCHED ON THE GAS PIPING. AT APPROXIMATELY 2:10 PM MT, OPERATIONS STARTED UNIT #2 AT THE ROBERSON CREEK COMPRESSOR STATION TO CHECK THE OPERATION OF THE VFD. AFTER OPERATING THE UNIT FOR APPROXIMATELY 10 MINUTES THE UNIT WAS SHUT DOWN AT APPROXIMATELY 2:20 PM MT BY LOCAL OPERATIONS. EACH TIME A UNIT SHUTS DOWN, A TWO HOUR TIMER STARTS TO BLOWDOWN THE COMPRESSOR CASE. AT APPROXIMATELY 4:00 PM MT, KM PERSONNEL LEFT FOR THE DAY. AT 4:26 PM MT, THE UNIT VENT VALVE OPENED TO VENT THE COMPRESSOR CASE. NORMALLY IN THIS SITUATION, THE UNIT DISCHARGE VALVE WOULD BE IN THE CLOSED POSITION; HOWEVER, THE DISCHARGE VALVE WAS IN THE OPEN POSITION. THIS ALLOWED GAS TO CONTINUE TO VENT FROM THE STATION DISCHARGE. ON SEPTEMBER 1, 2020, AT APPROXIMATELY 6:50 AM MT, STATION PERSONNEL ARRIVED AT THE FACILITY, HEARD THE GAS BLOWING AND CLOSED THE VENT VALVE THAT THEY FOUND IN THE OPEN POSITION. GAS LOSS WAS CALCULATED TO BE APPROXIMATELY 150 MMCF. THE INVESTIGATION REVEALED THAT THE UNIT DISCHARGE VALVE WAS COMMANDED OPEN BY THE UNIT PLC AT 2:25PM. IT COULD NOT BE DETERMINED WHY THE VALVE WAS COMMANDED OPEN OR WHERE THE COMMAND CAME FROM. THE INVESTIGATION TEAM WAS UNABLE TO REPLICATE THE CAUSE OF THE EVENT DURING THEIR INVESTIGATION AND SUSPECTS THAT THE PLC EXPERIENCED A MALFUNCTION THAT CAUSED IT TO SEND THE UNINTENDED SIGNAL TO OPEN. THE INVESTIGATION ALSO REVEALED THAT THERE WAS A FLAW IN THE PLC PROGRAMMING. THERE WAS A LOGIC PATH THAT ALLOWED THE CONFIRMATION OF THE UNIT VALVE CLOSURES TO BE BYPASSED WHEN BLOWING DOWN THE COMPRESSOR UNIT. IN ORDER TO PREVENT A REOCCURRENCE, THE PLC LOGIC WAS MODIFIED TO ENSURE THAT THE UNIT SUCTION AND DISCHARGE VALVES ARE CLOSED BEFORE THE UNIT VENT VALVE IS OPENED. ADDITIONALLY, CIG ASSESSED THE PLC LOGIC OF THE OTHER TWO COMPRESSOR UNITS AND MADE CHANGES AS APPROPRIATE. IN ADDITION, A CALLOUT ALARM WAS ADDED IN THE EVENT THAT UNIT VENT VALVE IS OPEN AT THE SAME TIME AS A UNIT SUCTION OR DISCHARGE VALVE. FINALLY, A VENT STACK FLOW SWITCH WAS INSTALLED TO HELP DETECT ANY FUTURE UNINTENDED RELEASES.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200100 | 34625 | 2020-09-30 15:24 | SUPPLEMENTAL FINAL | 31286 | ONEOK GAS TRANSPORTATION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2020-08-29 17:55 | 2020 | CENTRAL | YES | 34.9939 | -95.0541 | 1285969 | 2020-08-29 18:51 | 1286134 | NATURAL GAS |  | 22 | 36 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-08-29 17:23 | 2020-09-03 08:00 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-08-29 17:55 | YES | 2020-08-29 17:31 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 22 | YES | [6 empty] | 0 | 2020-08-29 17:23 | 2020-08-29 17:55 | ONSHORE | OK | 74563 | Not Within a Municipality | LATIMER | NOT APPLICABLE |  | RED OAK COMPRESSOR STATION | R-913 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 1992 | 1992 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 1.2 | 1.2 |  | CLASS 1 LOCATION | NO |  | 250 |  | NO | NO |  |  | 0 | 0 | 78 | 78 | 48 | 48 | 2500000 | 2500000 | 1500 | 1500 | 0 | 0 |  | 2.16 | 2501626 | 1148340.07449972 | 2501626 | 0 | 0 | 0 | 1 | NO |  |  |  | 680 | 133 | 960 | 192.619(A)(1) |  | 1992-04-02 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER HANDLED THE ISSUE PROPERLY THROUGH SUDA ACTIONS AND EVERBRIDGE CALL. COMMUNICATIONS WITH THE FIELD, PIPELINE CONTROL MANAGEMENT AND OPERATIONS WERE ALL RECEIVED THROUGH PHONE AND EMAIL. LEADERSHIP REVIEWED THE AOC WITH PIPELINE CONTROL. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | PIPE NIPPLE |  |  |  |  | YES |  | YES | [175 empty] | JACK CROW | REGULATORY COMPLIANCE SPECIALIST | jack.crow@oneok.com | 405-323-2492 |  |  |  |  | DAVID MCMULLEN | DIRECTOR OF OPERATIONS | 405-833-4219 | david.mcmullen@oneok.com | AT APPROXIMATELY 17:30 ON 8/29/20 AN EMERGENCY CALL WAS RECEIVED BY ONEOK GAS TRANSPORTATION GAS CONTROL CENTER OF A FIRE AT THE ONEOK RED OAK COMPRESSOR STATION. THE EMERGENCY SHUTDOWN DEVICE AT THE STATION ACTIVATED, ISOLATING THE STATION AND SHUTTING IT DOWN. ONEOK'S INVESTIGATION DETERMINED A 1 1/2 NIPPLE FAILED ALLOWING GAS TO BLOW DIRECTLY INTO THE COMPRESSOR BUILDING WHICH WAS IGNITED AND CAUSED THE FIRE. THE INVESTIGATION ALSO DETERMINED THE 1 1/2 NIPPLE WAS REPLACED WITH A SCHEDULE 80 GRADE NIPPLE AND NOT THE PREFERRED SCHEDULE 160. THE NIPPLE HAD ALSO NOT BEEN PROPERLY SECURED TO THE COMPRESSOR SKID ALLOWING IT TO VIBRATE. ONEOK ALSO REDESIGNED THE PIPING CONFIGURATION OF THE RELIEF LINE TO ELIMINATE STRESS LOADS ON THE RELIEF PIPING. STATION VIBRATION STUDIES WERE CONDUCTED AT THE SITE AFTER THE INSTALLATION AND SECURING OF THE PIPING WITH THE NEW DESIGN. ONEOK CONTACTED THE NRC REGARDING THE ACCIDENT ON 8/29/20 AT 18:50 AND UPDATED THE REPORT ON 8/31/20 AT 16:54.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200101 | 34326 | 2020-09-30 19:58 | ORIGINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2020-09-02 12:06 | 2020 | CENTRAL | YES | 30.425 | -92.3555 | 1286340 | 2020-09-02 12:59 | 1286500 | NATURAL GAS |  | 5218 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-09-02 12:33 |  | YES |  |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-09-02 12:33 | OPERATIONAL CONTROL | END OF LINE. UPSTREAM VALVE WAS CLOSED. |  | 0 | 2020-09-02 12:35 | 2020-09-02 12:30 | ONSHORE | LA | 70535 | Not Within a Municipality | ACADIA | SURVEY STATION NO. | 0+4233 | HUNDLEY 4" LINE | HUN 4-1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 18 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 4 |  | 0.237 | 24000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | OTHER | UNKNOWN | UNKNOWN | [26 empty] | 1951 | 1951 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 36 | 6 |  | CLASS 1 LOCATION | NO |  | 143 |  | NO | NO |  |  | 1800 | 1800 | 0 | 0 | 13462 | 13462 | 75000 | 75000 | 0 | 0 | 0 | 0 |  | 2.58 | 90262 | 49209.8931754187 | 90262 | 0 | 0 | 0 | 0 | NO |  |  |  | 824 | 1 | 1100 | 192.619(C) |  | 2019-08-27 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL |  | 4280 | NO | [5 empty] | YES | NOT EQUIPPED WITH LAUNCHER OR RECEIVER | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [146 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 2709035764 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 2703146547 | tina.baker@bwpipelines.com | ON 9-2-2020 AT 12:06 PM, TEXAS GAS'S GAS CONTROL RECEIVED A CALL FROM THE SHERIFF'S DEPARTMENT REPORTING A POTENTIAL PIPELINE LEAK. GAS CONTROL CONTACTED OPERATIONS PERSONNEL AT 12:13 PM. A PIPELINE TECHNICIAN WHO WAS ALREADY IN THE FIELD PERFORMING MAINTENANCE WAS DISPATCHED TO THE SITE AT 12:15 PM. LOCAL OPERATIONS PERSONNEL ARRIVED AT THE HUN 4" TAP VALVE AT APPROXIMATELY 12:30 PM. PERSONNEL SHUT THE TAP VALVE AND OPENED BLOWDOWN VALVE AT 12:33 PM. THE LINE WAS SECURED AND BLOWN DOWN AT 12:33 PM. NO ONE WAS INJURED. SOME GROUND DISTURBANCE OCCURRED. THE PIPELINE BLEW FOR 20 MINUTES AT 824 PSIG. AT THIS TIME THE FAILED PORTION OF PIPELINE IS STILL ATTACHED AND HAS NOT BEEN REMOVED. TEXAS GAS INTENDS TO ABANDON THIS PORTION OF PIPELINE AND REMOVE IT FROM SERVICE. CURRENTLY, THE AREA IS TOO WET TO COMPLETE THIS SCOPE AND, THEREFORE, TEXAS GAS HAS NOT YET HAD THE OPPORTUNITY TO COMPLETELY ASSESS THE CAUSE OF THIS INCIDENT ALTHOUGH IT APPEARS TO BE CORROSION RELATED. EVALUATION IS ONGOING AND A SUPPLEMENTAL/FINAL INCIDENT REPORT WILL BE REQUIRED. THE RESPONSE PROVIDED TO PART E, QUESTION 1A IS 1.0 BUT THE ACTUAL FLOW WAS TOO LOW TO CALCULATE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200102 | 34910 | 2020-10-02 10:49 | SUPPLEMENTAL FINAL | 3 | ACADIAN GAS PIPELINE SYSTEM | 1100 LOUISIANA ST. | HOUSTON | TX | 77002 | 2020-09-06 18:18 | 2020 | CENTRAL | YES | 29.9301 | -91.0653 | 1286663 | 2020-09-06 19:21 | 1286817 | NATURAL GAS |  | 12000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-09-06 18:57 | 2020-11-16 12:33 |  | YES | OPERATOR | 2020-09-06 18:33 | NO | [5 empty] | VALVE CLOSURE |  | 2020-09-06 18:57 | VALVE CLOSURE |  | 2020-09-06 18:59 | 0 | 2020-09-06 18:18 | 2020-09-06 18:57 | ONSHORE | LA | 70390 | NAPOLEONVILLE | ASSUMPTION | MILEPOST | MP 1 | LAKE VERRET 12" | 307-0308 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 | NO | 0.219 | 42000 | API 5L | OTHER | ERW - DIRECT CURRENT | YOUNGSTOWN STEEL | COAL TAR |  | UNKNOWN | [26 empty] | 1964 | 1964 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 182 | 12 |  | CLASS 1 LOCATION | NO |  | 265 |  | NO | NO |  |  | 562000 | 562000 | 0 | 0 | 30960 | 30960 | 118000 | 118000 | 0 | 0 | 0 | 0 |  | 2.58 | 710960 | 344235.580841518 | 710960 | 0 | 0 | 0 | 0 | NO |  |  |  | 883 | 0 | 909 | 192.619(A)(2) |  | 1964-03-07 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 47505 | NO | YES | [6 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PIPELINE WAS NOT FLOWING AT THE TIME OF THE INCIDENT. | [12 empty] | YES | 1 | 0 | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  | YES | [5 empty] | YES |  |  | YES | [5 empty] | NO | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | NATHAN L. GRAY JR. | PIPELINE COMPLIANCE SPECIALIST | ngray@eprod.com | 985 493 4629 |  | NATHAN L. GRAY JR. | ngray@eprod.com | 985 493 4629 | NHAN TRUONG | COMPLIANCE MANAGER | 713 381 2493 | nvtruong@eprod.com | ON SEPTEMBER 6 AT 18:18, HOUSTON CONTROL CENTER (HCC) RECEIVED A LOW-PRESSURE ALARM AT THE ELM HALL REGULATOR STATION AND A PRESSURE DROP AT THE CHAPARRAL OAKLEY STATION. THE PIPELINE WAS NOT FLOWING AT THE TIME OF THE INCIDENT. HCC CONTACTED THE OPERATIONS SUPERVISOR WHO DISPATCHED TECHNICIANS TO CLOSE THE MANUAL VALVES AT THE ENDS OF THE PIPELINE. AT APPROXIMATELY 18:33, LOCAL EMERGENCY RESPONDERS WERE NOTIFIED OF THE INCIDENT. AT APPROXIMATELY 18:57, TECHNICIANS ARRIVED ONSITE AND FOUND THE PIPELINE HAD RUPTURED IN A SUGAR CANE FIELD. THE PIPELINE WAS ISOLATED AND VENTED TO ATMOSPHERE. ON SEPTEMBER 9, 2020, THE RUPTURED PIPELINE SEGMENT WAS CUT OUT AND REPLACED. METALLURGICAL ANALYSIS INDICATED PIPE WALL THINNING OCCURRED AS A RESULT OF INTERNAL PITTING AND CREVICE CORROSION. THE POTENTIAL MECHANISM FOR THE METAL LOSS COULD BE WATER AND CHLORIDE ACCUMULATION AT THE BOTTOM OF THE PIPE. THE NRC 48 HOUR NOTIFICATION TOOK PLACE ON SEPTEMBER 8, 2020 AT 17:26 CST, #1286817
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200103 | 34518 | 2020-10-08 15:02 | SUPPLEMENTAL FINAL | 2620 | COLUMBIA GULF TRANSMISSION, LLC | 700 LOUISIANA ST. SUITE 700 | HOUSTON | TX | 77002 | 2020-09-12 23:20 | 2020 | CENTRAL | YES | 32.4106 | -91.4874 | 1287197 | 2020-09-13 | 1287311 | NATURAL GAS |  | 5695.6 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | ONLY ASSOCIATED PIPING OR EQUIPMENT WERE SHUTDOWN |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-09-12 22:22 | 2020-09-12 22:45 | ONSHORE | LA | 71232-6405 | Not Within a Municipality | RICHLAND | NOT APPLICABLE |  | DELHI COMPRESSOR STATION | 30 INCH SUCTION HEADER | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | BLOWDOWN VALVE WAS PARTIALLY OPENED. | CLASS 1 LOCATION | NO |  | 176 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 14011 | 14011 | 0 | 0 | 0 | 0 | 200 | 200 | REPLACEMENT PARTS REPAIR (ARMATURE, SPRING, ORING, AND COIL) | 2.46 | 14211 | 14617.6451723797 | 14211 | 0 | 0 | 0 | 0 | NO |  |  |  | 938 | 820169 | 1007 | OTHER | ANSI 600 VALVE | 1970-10-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE VALVE WAS NOT OPERATED BY CONTROLLERS REMOTELY TO LEAD TO THIS INCIDENT; THE SOLENOID COIL HAD FAILED AS INDICATED BY THE UNUSUALLY HIGH RESISTANCE MEASURE ACROSS IT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | SOLENOID FAILURE | [161 empty] | BENSON HUNLEY | REGULATORY COMPLIANCE SPECIALIST | ben_hunley@tcenergy.com | 304-539-9311 |  |  |  |  | PAUL SHAFFER | MANAGER US REGIONAL COMPLIANCE EAST | 304-550-4866 | paul_shaffer@tcenergy.com | ON SEPTEMBER 12, 2020, AN ALARM WAS ACKNOWLEDGED BY THE US NATURAL GAS CONTROL, EAST TEAM, SUBJECT TO A POSSIBLE ALARM AT DELHI COMPRESSOR STATION (CS) UNIT 811. COLUMBIA GULF TRANSMISSION, LLC (COLUMBIA) OPERATES AND MAINTAINS DELHI CS WHICH IS CLASSIFIED AS A TRANSMISSION CS, IS LOCATED IN RICHLAND PARISH, LOUISIANA AND NEAR THE CITY OF DELHI. AFTER RECEIVING THE NOTIFICATION FROM COLUMBIA MONITORING CENTER, CS PERSONNEL RESPONDED TO THIS POSSIBLE ALARM AT DELHI CS AND ADDRESSED THE UNINTENDED RELEASE OF NATURAL GAS (MATERIAL) THAT WAS VENTING INTO ATMOSPHERE FROM BLOW DOWN DISCHARGE STACK 8SH-1BD. THE CS PERSONNEL INSPECTED AND SECURED THE AREA TO ENSURE THAT IT WAS SAFE TO OPERATE DISCHARGE VALVES BEFORE MANUALLY CLOSING THEM. INVESTIGATION INTO THE INCIDENT IDENTIFIED THE PROBABLE CAUSE THAT LED TO THIS UNINTENDED RELEASE WAS DUE TO THE OPEN COMMAND SOLENOID VALVE COIL (8SH-1BD) FAILING AS DETERMINED BY AN UNUSUALLY HIGH RESISTANCE MEASURED AT THE COIL. THIS SOLENOID VALVE IS A FAIL OPEN SOLENOID THAT REQUIRES VOLTAGE TO THE COIL TO KEEP THE VALVE IN THE CLOSED POSITION. ONCE THE COIL FAILED THE VALVE (8SH-1BD) BEGAN TO OPEN UNTIL THE CLOSED LIMITS WERE BROKEN. ONCE THE LIMITS WERE BROKEN THE CLOSE SOLENOID WHICH IS A FAIL CLOSED SOLENOID ENERGIZED AND ATTEMPTED TO CLOSE THE VALVE UNTIL THE CLOSE LIMIT SWITCHES WERE MADE. THE SOLENOID VALVE WAS REBUILT BY REPLACING ARMATURE, SPRING, ORING, AND COIL. THE LIMIT SWITCH CAMS WERE ADJUSTED AND TIGHTENED TO ENSURE THIS ISSUE DOESN'T RE-OCCUR. ALL ALARMS WERE CLEARED AT THE PLC CONTROL PANEL, REQUIRED FUNCTIONAL TESTS WERE CONDUCTED WITH NO NEW ERRORS GENERATED (TO ENSURE NORMAL OPERATION OF THE UNIT), THEN THE UNIT WAS RETURNED BACK TO SERVICE. ROUTINE SAFETY CHECKS WERE CONDUCTED WHERE THE UNIT WAS MONITORED FOR A WHILE, VERIFIED THAT ALL SYSTEMS ARE RUNNING IN NORMAL MODE WITH NO NEW ERRORS WERE GENERATED THEREAFTER. A CALCULATED VOLUME OF UNINTENDED RELEASED MATERIAL WAS 5,695.60 MCF INTO ATMOSPHERE WHERE THE RELEASED MATERIAL DID NEITHER IGNITE NOR CAUSE ANY DAMAGE TO ANY OF THE CS DEVICES.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200104 | 34355 | 2020-10-08 20:00 | ORIGINAL | 31485 | ENBRIDGE OFFSHORE (GAS GATHERING) L.L.C. | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2020-09-11 13:00 | 2020 | CENTRAL | YES | 28.5735 | -91.9594 | 1287127 | 2020-09-11 15:55 | 1287227 | NATURAL GAS |  | 65 | 48181 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | ROUTINE START-UP | NO | THE PLATFORM WAS SHUT-IN DUE TO HURRICANE LAURA |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-09-11 13:00 | 2020-09-11 13:00 | OFFSHORE | [6 empty] | ENBRIDGE OFFSHORE GAS GATHERING, L.L.C. | PHMSA OPID #: 31485 | [20 empty] | 140 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | SM | 76P | PLATFORM | INTERSTATE | OFFSHORE PLATFORM, INCLUDING PLATFORM-MOUNTED EQUIPMENT AND PIPING | PIPE | PIPE BODY | 2 | NO | 0.218 | 35000 | UNKNOWN | SEAMLESS |  | UNKNOWN | PAINT |  | YES | [26 empty] | 1997 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 73 |  | NO | NO |  |  | 0 | 0 | 113240 | 113240 | 153 | 153 | 111000 | 111000 | 0 | 0 | 0 | 0 | COST OF $83,000 FOR CONTRACTORS, $28,000 FOR BOAT SERVICE. | 2.3503 | 224393 | 103090.699030611 | 224393 | 0 | 0 | 0 | 0 | NO |  |  |  | 788 | 0 | 1975 | 192.619(A)(2) |  | 1997-02-17 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS DETERMINED THE CONTROLLERS ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. THE LEAK WAS TOO SMALL TO BE IDENTIFIED BY THE CONTROL ROOM PERSONNEL. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  |  | YES | [7 empty] | YES |  |  |  | NO | [11 empty] | YES | NO | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [14 empty] | YES | [48 empty] | LISA WU | ENGINEER SPECIALIST OPERATIONAL COMPLIANCE | lisa.wu@enbridge.com | 7136274889 | 7133864466 |  |  |  | NATHAN ATANU | MANAGER - OPERATIONAL COMPLIANCE | 7136275008 | nathan.atanu@enbridge.com | AT APPROXIMATELY 1:00 PM. CDT ON SEPTEMBER 11, 2020, ENBRIDGE OFFSHORE GAS GATHERING L.L.C.'S (ENBRIDGE OFFSHORE) DISCOVERED A LEAK ON A 2-INCH DIAMETER BY-PASS LINE ON A PLATFORM (SMI 76) LOCATED ON SM 76P IN THE GULF OF MEXICO. ENBRIDGE OFFSHORE SUBSEQUENTLY DEPRESSURIZED THE LINE AFTER ATTEMPTING TO ISOLATE THE PIPELINE AND STOP THE LEAK. ENBRIDGE OFFSHORE NOTIFIED THE NRC AT 3:55 CDT AFTER MAKING ATTEMPTS TO ISOLATE THE LINE AND STOP THE LEAK. THE PIPELINE REMAINS OUT OF SERVICE AT THIS TIME DUE TO HURRICANE LAURA AND HURRICANE DELTA. THE CAUSE OF THE LEAK IS ATMOSPHERIC CORROSION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200105 | 34732 | 2020-10-10 22:12 | SUPPLEMENTAL FINAL | 5304 | FLORIDA GAS TRANSMISSION CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-09-10 00:47 | 2020 | EASTERN | YES | 28.8441 | -81.3411 | 1286952 | 2020-09-10 02:24 | 1287145 | NATURAL GAS |  | 22000 | 0 | 0.1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-09-10 02:08 |  | YES | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-09-10 02:35 | YES | 2020-09-10 00:53 | OPERATOR/CONTRACTOR |  | 2200 | NO | VALVE CLOSURE |  | 2020-09-10 02:08 | VALVE CLOSURE |  | 2020-09-10 02:09 | 20 | 2020-09-10 01:48 | 2020-09-10 02:29 | ONSHORE | FL | 32771 | SANFORD | SEMINOLE | MILEPOST | 15 | 12" SANFORD LATERAL | FLBOD | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 37 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 12 |  | 0.219 | 42000 | API 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | YOUNGSTOWN SHEET | COLD APPLIED TAPE |  | YES | [26 empty] | 1959 | 1959 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 317 | 24 |  | CLASS 1 LOCATION | NO |  | 235 |  | NO | NO |  |  | 68000 | 68000 | 0 | 0 | 48180 | 48180 | 2054568 | 2054568 | 2000 | 2000 | 0 | 0 |  | 2.19 | 2172748 | 1025183.16632118 | 2172748 | 0 | 0 | 32 | 93 | NO |  |  |  | 695 | 0 | 713 | 192.619(C) |  | 1989-09-26 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 38544 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 2 | 0 | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED |  | YES | [15 empty] | STRESS CORROSION CRACKING | [12 empty] | YES | NEAR NEUTRAL PH STRESS CORROSION CRACKING. | 1062 | [54 empty] | YES | YES |  |  | YES |  |  |  | 2019 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2014 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [21 empty] | 2019 | FREE SWIMMING | HIGH RESOLUTION |  | INSIDE ILI CUPS | 2014 | FREE SWIMMING | HIGH RESOLUTION |  | INSIDE ILI CUPS | [14 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KATHRYN HARRYMAN | SENIOR SPECIALIST REGULATORY COMPLIANCE | kathryn.harryman@energytransfer.com | 713-989-7085 |  |  |  |  | TODD NARDOZZI | DIRECTOR REGULATORY COMPLIANCE | 713-989-7126 | todd.nardozzi@energytransfer.com | 09/10/20 AT 00:47 AM EASTERN FGT GAS CONTROL DETECTED A LOW PRESSURE ALARM AT THE DEBARY POWER PLANT. INVESTIGATION BY FIELD OPERATIONS CONFIRMED A FAILURE ON THE 12IN SANFORD LATERAL THAT HAD IGNITED. 09/10/20 AT 02:35 AM EASTERN LOCAL EMERGENCY RESPONDER MADE CONTACT WITH FGT PERSONNEL ON THE SCENE. THE LOCATION OF THE INCIDENT IS IN SEMINOLE COUNTY IN THE NORTHERN PART OF THE ORLANDO METROPOLITAN AREA. THE INCIDENT OCCURRED IN A POWER LINE CORRIDOR AND RESULTED IN DAMAGE TO A DUKE ENERGY 230KV TRANSMISSION LINE. THE PIPELINE WAS ISOLATED AT APPROXIMATELY 2:08 AM. 09/10/20 AT 07:55 AM EASTERN - THREE MARLIN CNG TRUCKS ARRIVED ON SITE AND WAS ABLE TO MOBILIZE ADDITIONAL TANKERS TO THE METER STATIONS TO MEET THE SUPPLY NEEDS FOR FPU CUSTOMERS. 09/10/20 AT 16:00 PM CONSTRUCTION UNDERWAY TO RETURN THE UPSTREAM PORTION OF THE 12IN SANFORD LATERAL TO SERVICE AT A REDUCED PRESSURE (344 PSIG). THIS IS 50% OF THE OPERATING PRESSURE AT THE TIME OF THE FAILURE. UPSTREAM SECTION IS CURRENTLY IN-SERVICE AT 50% MAOP. DOWNSTREAM FAILED SECTION IS STILL OUT OF SERVICE AND ISOLATED. THE ISOLATED SEGMENT IS UNDER A PHMSA CORRECTIVE ACTION ORDER AND THE FAILED PIPE IS UNDERGOING METALLURGICAL ANALYSIS, A SUPPLEMENTAL INCIDENT REPORT WILL BE FILED ONCE THE CAUSE IS DETERMINED. UPDATE: THE PIPELINE HAS SINCE BEEN REPAIRED AND WAS RESTARTED ON 12/7/2020 AS PER THE RESTART AGREEMENT WITH PHMSA. THE FAILED SECTION WAS SENT TO THE LABORATORY FOR ANALYSIS AND THROUGH METALLURGICAL ANALYSIS, THE FAILURE WAS IDENTIFIED TO BE NEAR NEUTRAL PH STRESS CORROSION CRACKING.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200106 | 34376 | 2020-10-13 17:34 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2020-09-15 08:55 | 2020 | CENTRAL | YES | 31.9507 | -103.108 | 1287376 | 2020-09-15 10:18 | 1287490, 1287493 | NATURAL GAS |  | 34161.7 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-09-15 08:30 | 2020-09-18 17:30 |  | NO |  |  | NO | [11 empty] | 0 | 2020-09-15 08:41 | 2020-09-15 08:41 | ONSHORE | TX | 79745 | KERMIT | WINKLER | NOT APPLICABLE |  | KEYSTONE COMPRESSOR STATION | KEYSTONE STATION SUCTION LINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1952 | 1952 | CARBON STEEL |  | LEAK |  |  | OTHER | MAOP EXC. LED TO PRV RELEASE | [5 empty] | CLASS 1 LOCATION | NO |  | 496 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 61491 | 61491 | 0 | 0 | 100 | 100 | 450 | 450 | RELIEF VALVE TESTING | 1.8 | 62041 | 64002.9763237816 | 62041 | 0 | 0 | 0 | 0 | NO |  |  |  | 620.6 | 0 | 575 | 192.619(A)(3) |  | 1952-06-30 | BI-DIRECTIONAL | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [5 empty] | YES | TWO ACTIVITIES WERE SCHEDULED TO OCCUR ON 9/15/2020 AND A MISUNDERSTANDING OF WHICH ACTIVITIES WERE REQUESTED LED TO THE OVERPRESSURE EVENT AND RELEASE OF NATURAL GAS. | NO |  |  | NO |  |  | INCORRECT OPERATION | PIPELINE OR EQUIPMENT OVERPRESSURED | INCORRECT OPERATION | PIPELINE/EQUIPMENT OVERPRESSURED | [204 empty] | PIPELINE OR EQUIPMENT OVERPRESSURED | [5 empty] | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | KRISTIN VAN DER LAAN | ENGINEERING MANAGER IC - CODES AND COMPLIANCE | kristin_vanderlaan@kindermorgan.com | [5 empty] | JAIME HERNANDEZ | ENGINEERING DIRECTOR - CODES AND COMPLIANCE | 713-369-9443 | jaime_hernandez@kindermorgan.com | THE EPNG KEYSTONE CS (A.K.A. KEYSTONE ML OR KML) HAD A SCHEDULED OUTAGE ON 9/15/20 STARTING AT 9:00AM (START OF GAS DAY) TO PERFORM AN ANNUAL ESD TEST. ON 9/14/20, KEYSTONE AREA OPERATIONS WAS TOLD BY EPNG GAS CONTROL THAT THE EPNG WINK CS NEEDED TO BE ONLINE BEFORE THE OUTAGE TO ENSURE THAT THE PRESSURE DID NOT EXCEED MAOP. THE REQUIREMENT OF HAVING THE WINK CS OPERATING WAS NOT INCLUDED IN THE OUTAGE PLAN AND WAS NOT DISCUSSED DURING THE PRE-JOB OR JSA. ON 9/15/20 AT 8:15AM, EPNG OPERATIONS SPECIALIST MADE A CALL TO EPNG GAS CONTROL TO REQUEST PERMISSION TO TAKE KML DOWN EARLIER THAN PLANNED AS OPERATIONS HAD COMPLETED THE PRE-JOB / JSA REVIEWS WITH ALL OF THE KM/EPNG EMPLOYEES AND CONTRACTORS. THE EPNG GAS CONTROLLER STATED HE WOULD CHECK AND CALL THE EPNG OPERATIONS SPECIALIST BACK. AT 8:25AM, THE EPNG GAS CONTROLLER CALLED EPNG OPERATIONS SPECIALIST AND GAVE THE OKAY TO START THE OUTAGE AT 8:33 AM. THE WINK CS WAS NOT ONLINE. BASED ON THE INVESTIGATION INTO THIS EVENT IT WAS LATER DETERMINED THAT THE EPNG GAS CONTROLLER WAS REFERRING TO STARTING THE WINK CS IN PREPARATION FOR THE KEYSTONE ESD SYSTEM TEST. LOCAL OPERATIONS PERSONNEL PUSHED THE ESD BUTTON TO INITIATE THE ESD SYSTEM TEST AT KML. AT 8:41AM, A PRV ON THE 30-INCH PLANT SUCTION LINE, WHICH HAS A MAOP OF 575 PSIG, STARTED TO RELIEVE GAS DUE TO OVER PRESSURE (SET POINT 580 PSI). AT 8:45AM, A SECOND PRV LIFTED ON LINE 3026 (SET POINT 605 PSIG), WHICH HAS A MAOP OF 651 PSIG. AT 8:59AM, THE EPNG OPERATIONS SUPERVISOR FOR KML AND WINK CS CALLED KM KEYSTONE GAS STORAGE (KEYSTOR) TO STOP DELIVERING GAS TO EPNG LINE 3026. AT 9:20AM, THE THIRD PRV LIFTED ON LINE 3026 (SET POINT OF 630 PSIG). THE FOURTH PRV ON LINE 3026 (SET POINT 580 PSIG) DID NOT OPERATE. AT 9:50AM, IN CONFORMANCE WITH O&M PROCEDURE 159 ' EMERGENCY REPORTING AND INVESTIGATION, AN ERL CALL WAS HELD. DURING THE CALL IT WAS DETERMINED THAT THE UNINTENTIONAL GAS RELEASED THROUGH THE RELIEF VALVES WOULD MEET AND EXCEED THE 3,000 MCF REPORTABILITY THRESHOLD. THE ACTUAL GAS LOSS WAS UNKNOWN AT THE TIME. AT 9:55AM THE MAOP EXCEEDED 110% (632.5PSIG) WITH A PRESSURE OF 633 PSIG FOR APPROXIMATELY 1 MINUTE. IN ORDER TO REDUCE THE PRESSURES TO NORMAL AND STOP THE RELEASE OF GAS THROUGH THE RELIEF VALVES: - AT 9:05AM, KEYSTOR STOPPED WITHDRAWAL INTO THE EPNG SYSTEM - AT 9:20AM, THE GC LEADS WORKED WITH KEYSTONE CS SUPERVISION TO ISOLATE SUPPLY INTO KEYSTONE CS. THE L3006, L3028, AND L3082 WERE SHUTOFF AT THE KEYSTONE FIELD VALVE YARD. L1115 WAS OPENED AT GOLDSMITH TO DIVERT THE GAS NORTH TOWARDS PLAINS. ONCE THE WARREN WADDELL INTERCONNECT SHUTDOWN, L3146 VALVE 2 WAS OPENED, AND WINK WAS BROUGHT ONLINE, L1105 VALVE 0 WAS CLOSED. THESE TWO VALVE CLOSURES ISOLATE THE KEYSTONE CS SUCTION PIPING. - AT 10:01AM, KEYSTORE STARTED INJECTION - GAS CONTROL CALLED PERMIAN PRODUCERS ASKING THEM TO SHUT IN EARLY - AT 10:27AM, THE EPNG OPERATIONS SPECIALIST WAS SENT TO LINE 3026 TO CLOSE VALVE 3. - AT 10:14AM, A SECOND EPNG OPERATIONS SPECIALIST OPENED LINE 1115 TO ALLOW GAS TO FLOW NORTH TO PLAINS. BY 11:25AM, ALL OF THE RELIEF VALVES HAD RESEATED AND PRESSURES RETURNED TO BELOW MAOP BY 12:16PM. THE INVESTIGATION DETERMINED THAT THERE WAS A FAILURE OF CLEAR COMMUNICATIONS BETWEEN EPNG OPERATIONS AND THE CONTROL CENTER. NOTES: THE TIME ESTIMATE FOR INCIDENT REPORTING THRESHOLD IS A COMBINATION OF THE RELIEF VALVE ON THE INLET SUCTION PIPING AND ONE OF THE RELIEF VALVES ON LINE 3026 RELIEVING. 1) INLET SUCTION RV, RELEASE TIME: 8:41AM - 9:20AM, TOTAL 5936 MCF 2) RV L3026, RELEASE TIME: 8:45AM - 11:25AM, TOTAL 1586.7 MCF 3) RV L3026, RELEASE TIME: 9:20AM - 11:25AM, TOTAL 12363 MCF FOR PART E1 PRESSURE NOTED IS THE PRESSURE AT 8:55AM CENTRAL TIME WHEN THE GAS LOSS MET THE REPORTING THRESHOLD. A SEPARATE MAOP EXCEEDANCE REPORT (PHMSA REPORT 20-191933) WAS SUBMITTED TO PHMSA ASSOCIATED WITH THIS EVENT AND IN CONFORMANCE WITH 49CFR 191.25(B). L3026 MAOP OF 651PSIG WAS NOT EXCEEDED.
2021-02-26 10:37 | YES | NO | UNGS (Underground Natural Gas Storage) | 20200107 | 34628 | 2020-10-16 17:16 | SUPPLEMENTAL FINAL | 31632 | NORTHWESTERN CORPORATION | 3010 W. 69TH ST. | SIOUX FALLS | SD | 57108 | 2020-09-18 12:00 | 2020 | MOUNTAIN | YES | 45.2519 | -109.1165 | 1287711 | 2020-09-18 12:48 | 1287832 | NATURAL GAS |  | 333186 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-09-21 17:00 | 2020-12-01 12:04 |  | YES | OPERATOR | 2020-09-18 20:37 | NO | [11 empty] | 0 | 2020-09-16 14:30 | 2020-09-16 07:00 | ONSHORE | MT | 59014 | Not Within a Municipality | CARBON | NOT APPLICABLE |  | DRY CREEK STORAGE | STORAGE WELL BN 8-3 | NO | OPERATOR-CONTROLLED PROPERTY | BELOWGROUND STORAGE OR ABOVEGROUND STORAGE VESSEL, INCLUDING ATTACHED APPURTENANCE |  |  |  |  | NO | [22 empty] | INTRASTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | UNDERGROUND GAS STORAGE OR CAVERN | [38 empty] | 1983 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | UNKNOWN | [5 empty] | CLASS 1 LOCATION | NO |  | 266 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 565283 | 565283 | 650000 | 650000 | 150000 | 150000 | 0 | 0 |  | 1.6966 | 1365283 | 953275.663271942 | 1365283 | 0 | 0 | 0 | 0 | NO |  |  |  | 1140 | 7872 | 1600 | OTHER | WELL CASING MAOP BELIEVED TO BE EQUAL TO OR EXCEED THE MAOP OF THE FIELD | 1983-08-16 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WERE NO ACTIONS THAT THE GAS CONTROLLERS COULD HAVE DONE THAT CAUSED THIS ISSUE. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | NWE IS CHANGING TO INTERNAL CORROSION BECAUSE OF DATA THAT WAS GATHERED FROM RUNNING A HIGH RESOLUTION VERTALOG, WHICH CAN DIFFERENTIATE BETWEEN INTERNAL AND EXTERNAL CORROSION. THE INTERNAL CORROSION WAS ALSO VERIFIED WITH A CALIPER LOG THAT WAS RUN DOWN THE CASING WITH THE VERTALOG TOOL. |  |  |  |  | YES | IT IS BELIEVED THAT A WATER INTERFACE OCCURRED AT THIS LOCATION BASED ON NWE CATHODIC NACE SMES. THIS COULD NOT BE VERIFIED. MICROBIOLOGICAL TESTING WAS NOT COMPLETED BECAUSE THE WELL HAD HAD BIOCIDE ADDED AND FOREIGN WATER ADDED TO KILL THE WELL. |  |  | YES | INTERNAL CORROSION WAS SELECTED BECAUSE OF DATA THAT WAS GATHERED FROM RUNNING A HIGH RESOLUTION VERTALOG, WHICH CAN DIFFERENTIATE BETWEEN INTERNAL AND EXTERNAL CORROSION. THE INTERNAL CORROSION WAS ALSO VERIFIED WITH A CALIPER LOG THAT WAS RUN DOWN THE CASING WITH THE VERTALOG TOOL. |  |  |  |  | YES | WELL CASING AT ~1900' BELOW SURFACE. | YES | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [313 empty] | KEITH MEAGOR | MANAGER OF GAS TRANSMISSION COMPLIANCE | keith.meagor@northwestern.com | 406-461-1211 |  |  |  |  | KEITH MEAGOR | MANAGER OF GAS TRANSMISSION COMPLIANCE | 406-497-1211 | keith.meagor@northwestern.com | THIS IS A SUPPLEMENTAL FINAL REPORT FOR INCIDENT REPORT 20200107-34393 SUBMITTED ON 10/16/20. PLEASE REFER TO THAT INCIDENT REPORT FOR THE INITIAL NARRATIVE. THE CAUSE OF THE INCIDENT HAS BEEN CHANGED IN PART G FROM EXTERNAL CORROSION TO INTERNAL CORROSION. THIS CHANGE HAS OCCURRED BECAUSE OF DATA THAT WAS GATHERED FROM RUNNING A HIGH RESOLUTION VERTALOG, WHICH CAN DIFFERENTIATE BETWEEN INTERNAL AND EXTERNAL CORROSION. THE INTERNAL CORROSION WAS ALSO VERIFIED WITH A CALIPER LOG THAT WAS RUN DOWN THE CASING WITH THE VERTALOG TOOL. AS NOTED IN THE INITIAL REPORT, THE WELL WAS KILLED AND THEN A COMPOSITE PLUG WAS PLACED AT 4479' JUST ABOVE THE PERFORATIONS. A PRODUCTION CASING WAS INSTALLED FROM SURFACE TO 4431'. THE PRODUCTION CASING WAS CEMENTED IN PLACE. CEMENT WAS RUN DOWN THE INSIDE OF THE INNER CASING AND THERE WERE RETURNS TO SURFACE THROUGH THE ANNULAR SPACE BETWEEN THE NEW PRODUCTION CASING AND THE OUTER CASING. THIS SEALED THE LEAK IN THE OUTER CASING AND PROVIDES A MITIGATION AGAINST ADDITIONAL LEAKS. A CEMENT BOND LOG WAS RUN FOR THE CEMENTING WORK OF THE INNER CASING AND NO DEFICIENCIES WERE NOTED IN THE LOG. A PRESSURE TEST WAS COMPLETED ON THE NEW INSTALLATION AND NO ISSUES WERE NOTED DURING THE TEST. FOLLOWING THE INTEGRITY TESTING, THE COMPOSITE PLUG WAS DRILLED OUT. THE WELL WAS THEN RE-COMMISSIONED ON 12/01/20. THE WELL HAS BEEN OPERATING FOR TWO WEEKS WITH NO IDENTIFIED ISSUES. AS AN ADDITIONAL MITIGATION, LEAK SURVEYS HAVE BEEN COMPLETED AROUND THE WELL AND ALONG THE PREVIOUS INCIDENT PLUME BOUNDARY. THE PLUME FROM THE INCIDENT HAS DISSIPATED SIGNIFICANTLY. READINGS WITHIN THE PLUME AREA ARE UNDER A PERCENT GAS IN BAR HOLES. NWE IS CONTINUING TO MONITOR THE PLUME AND WILL DO SO UNTIL IT HAS DISSIPATED. THERE ARE NO SAFETY OR PUBLIC SAFETY CONCERNS. THIS WILL BE THE FINAL REPORT FOR THIS INCIDENT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200108 | 34833 | 2020-10-17 12:13 | SUPPLEMENTAL FINAL | 31356 | VECTOR PIPELINE, L.P. | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2020-09-16 12:44 | 2020 | EASTERN | NO | 42.1429 | -85.2644 | 1287496 | 2020-09-16 13:31 | 1287691 | NATURAL GAS |  | 292 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | POST-MAINTENANCE/REPAIR | [5 empty] | YES | OPERATOR | 2020-09-16 12:46 | YES | 2020-09-16 12:44 | ALLOWED TO BURN OUT |  | 292 | NO | [6 empty] | 0 | 2020-09-16 12:44 | 2020-09-16 12:44 | ONSHORE | MI | 49011 | Not Within a Municipality | CALHOUN | MILEPOST | MP 168 | VECTOR ATHENS COMPRESSOR STATION | ATHENS COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2009 | 2009 | CARBON STEEL |  | OTHER | [8 empty] | OPEN BODY BLEED VALVES ON SUCTION AND DISCHARGE VALVES. | CLASS 1 LOCATION | NO |  | 655 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 599 | 599 | 70000 | 70000 | 2000 | 2000 | 0 | 0 |  | 2.05 | 72599 | 33670.9103506427 | 72599 | 0 | 0 | 0 | 0 | NO |  |  |  | 748 | 0 | 1000 | 192.619(A)(2) |  | 2000-12-01 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE STATION WAS BEING MONITORED REMOTELY (SCADA), BUT WAS UNDER LOCAL CONTROL AT TIME OF THE EVENT. | [12 empty] | YES | 2 | 0 | YES | 2 | 0 | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [204 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE |  |  |  | YES |  |  |  |  | ROUTINE MAINTENANCE | NO | [143 empty] | YES | [6 empty] | MICHAEL MCGRATH | PIPELINE PERFORMANCE AND COMPLIANCE SPECIALIST | michael.mcgrath@enbridge.com | 16128056542 |  |  |  |  | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 713-627-5008 | nathan.atanu@enbridge.com | AT APPROXIMATELY 12:44 PM EDT ON SEPTEMBER 16, 2020, VECTOR PIPELINE, L.P.'S (VECTOR) ATHEN'S COMPRESSOR STATION HAD A FIRE DURING THE STARTING SEQUENCE OF THE TURBINE UNIT. DURING THE ENSUING MINUTES, VECTOR EVACUATED THE FACILITY AND SUBSEQUENTLY NOTIFIED THE FIRST RESPONDERS. THE ESD WAS ACTIVATED BY A FLAME DETECTOR IN THE FACILITY, THUS ISOLATING THE COMPRESSOR STATION. THE CAUSE OF THE INCIDENT WAS INCORRECT OPERATION OF THE VALVES. THE BODY BLEEDS ON THE UNIT SUCTION AND DISCHARGE VALVES WERE INADVERTENTLY LEFT OPEN FOLLOWING ROUTINE (SEMI ANNUAL) MAINTENANCE AND AS A RESULT VENTED GAS DURING THE UNIT STARTING SEQUENCE. USING THE BODY BLEEDS AS AND ADDITIONAL SAFETY MEASURE IS A COMMON PRACTICE AND THE LOCK OUT TAG OUT (LOTO) ISOLATION PLAN HAS BEEN UPDATED TO INCLUDE THESE VALVES. VECTOR IS REVIEWING PROCEDURES AND TRAINING TO PREVENT RECURRENCE. 01/04/2021 UPDATED PART G7 (3) AND PART H.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200109 | 34514 | 2020-10-22 00:38 | SUPPLEMENTAL FINAL | 13845 | NORTHWEST PIPELINE LLC | 295 CHIPETA WAY | SALT LAKE CITY | UT | 84108 | 2020-09-24 15:57 | 2020 | MOUNTAIN | YES | 42.6531 | -113.0101 | 1288206 | 2020-09-24 17:18 | 1288427 | NATURAL GAS |  | 123.2 | 10555 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-09-24 18:43 | 2020-10-21 11:15 |  | YES | OPERATOR | 2020-09-24 18:05 | NO | [5 empty] | VALVE CLOSURE |  | 2020-09-24 18:43 | VALVE CLOSURE |  | 2020-09-24 18:25 | 0 | 2020-09-24 15:57 | 2020-09-24 15:57 | ONSHORE | ID | 83211 | Not Within a Municipality | POWER | MILEPOST | 626.9 | WILLIAMS NORTHWEST PIPELINE | MAINLINE 1400 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 42 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 22 | NO | 0.25 | 52000 | API 5LX | DSAW |  | CONSOLIDATED WESTERN | ASPHALT |  | UNKNOWN | [26 empty] | 1955 | 1955 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 443 |  | NO | NO |  |  | 0 | 0 | 12772 | 12772 | 149 | 149 | 200000 | 200000 | 0 | 0 | 0 | 0 |  | 1.21 | 212921 | 97822.437444786 | 212921 | 0 | 0 | 0 | 0 | NO |  |  |  | 591 | 178500 | 850 | 192.619(A)(3) |  | 1970-11-12 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 91783 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIN HOLE LEAKS WERE OF A MINOR NATURE IN TERMS OF GAS LOSS, AND SCADA IS NOT WELL SUITED FOR IDENTIFYING THESE TYPES OF LEAKS. LEAKS WERE DISCOVERED DURING FOLLOW UP ACTIVITIES ASSOCIATED WITH IN-LINE INSPECTION OF THE LINE. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1975 | YES | YES | YES |  |  |  | 2019 |  |  |  | NO | [190 empty] | YES | YES | [6 empty] | 2020 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2012 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [45 empty] | NO |  |  | Yes, and an investigative dig was cunducted at the point of the Accident | 2020 |  |  |  |  | 2020 | [5 empty] | YES |  | NO | [63 empty] | BRET BURKHART | ENGINEER III - PIPELINE SAFETY | bret.burkhart@williams.com | 801-584-6892 |  | DAVE DICKERSON | david.s.dickerson@williams.com | 208-884-4300 | TYSON GREEN | MANAGER PIPELINE SAFETY | 713-215-2535 | tyson.green@williams.com | IN APRIL OF 2020 WILLIAMS CONTRACTED WITH AN IN-LINE INSPECTION VENDOR TO COMPLETE TOOL RUNS ON THE WILLIAMS NORTHWEST PIPELINE 1400 POCATELLO TO BURLEY SEGMENT. HIGH-RES MFL TOOL RUNS WERE CONDUCTED, AND A PRELIMINARY REPORT WAS PROVIDED TO WILLIAMS WITH ANOMALIES ON THE WEEK OF 5/25/2020. WILLIAMS INITIATED PROJECTS TO ADDRESS ANOMALIES IN ORDER OF PRIORITY. THIS PARTICULAR DIG DID NOT MEET THE SAME CRITERIA AS OTHER'S IN THE AREA - UNDER CALLED BY THE TOOL. AS A RESULT THIS PIN HOLE WAS NOT DISCOVERED UNTIL REMEDIATION OF OTHER LEAKS IN THE SAME GENERAL AREA HAD BEEN COMPLETED. SIMILAR TO OTHER ANOMALIES IN THE AREA EXCAVATION UNCOVERED A PIN-HOLE LEAK RESULTING FROM CORROSION. LEAK SURVEYS PRIOR TO FEATURE ASSESSMENT DID NOT SHOW ANY SIGNS OF LEAKING. ASSESSMENTS INCLUDED AERIAL LEAK SURVEY 9/22/2020, AND GROUND SURVEY 9/23/2020. THERE WAS NO INDICATION OF FOUL ODORS OR DISCOLORED VEGETATION PRIOR TO DIGGING. THE FIRST INDICATION OF GAS OCCURRED AFTER THE FEATURE WAS UNCOVERED. IT IS ESTIMATED THAT THE FEATURE LEAKED FROM THE FIRST INDICATION OF GAS FOR APPROXIMATELY 3 HOURS BEFORE THE LINE WAS SHUT IN AND BLOWN DOWN FROM AN OPERATING PRESSURE OF ABOUT 600PSIG TO 14PSIG. AFTER ASSESSING REPAIR OPTIONS WILLIAMS PROJECT MANAGEMENT DETERMINED THAT REPAIRS WOULD BE BEST ACCOMPLISHED THROUGH PIPE REPLACEMENT. THE PRELIMINARY COST OF REPAIRS EXCEEDS $50,000, WITH COST OF CONTRACTOR AND INTERNAL LABOR APPROACHING $200,000. IT WAS DETERMINED THAT THIS QUALIFIED AS A DOT REPORT-ABLE INCIDENT BASED ON COST WHEN WILLIAMS MANAGEMENT SETTLED ON PIPE REPLACEMENT AS THE PREFERRED REPAIR OPTION ON 9/24/2020. THE NRC WAS INITIALLY NOTIFIED OF THE INCIDENT ON 9/24/2020. THE LINE WAS RETURNED TO SERVICE ON 10/21/2020
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200110 | 34415 | 2020-10-22 17:53 | SUPPLEMENTAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2020-09-24 00:44 | 2020 | MOUNTAIN | NO | 32.8153 | -104.1645 | 1288123 | 2020-09-24 05:53 | 1288243 | NATURAL GAS |  | 31757 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-09-24 04:40 |  | YES | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-09-24 03:19 | VALVE CLOSURE |  | 2020-09-24 04:40 | 0 | 2020-09-24 04:40 | 2020-09-24 06:00 | ONSHORE | NM | 88255 | LOCO HILLS | EDDY |  |  | INDIAN BASIN PIPELINE | INDIAN BASIN PIPELINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 20 |  | 0.235 | 60000 | API 5L GRADE X60 | LONGITUDINAL ERW - LOW FREQUENCY |  | YOUNGSTOWN SHEET AND TUBE | ASPHALT |  | YES | [26 empty] | 1965 | 1965 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 810 | 29 |  | CLASS 1 LOCATION | NO |  | 436 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 44460 | 44460 | 114590 | 114590 | 1794 | 1794 | 30000 | 30000 | INVESTIGATION COST.- 3RD PARTY METALLURGICAL ANALYSIS, SITE SURVEY, TRAVEL, ETC | 1.4 | 190844 | 113287.819397521 | 190844 | 0 | 0 | 0 | 0 | NO |  |  |  | 964 | 1500 | 1000 | 192.619(A)(1) |  | 1965-12-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | AUTOMATIC | 89760 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | YES |  |  |  | YES | [10 empty] | YES | INVESTIGATION STILL ONGOING | [13 empty] | YES | INVESTIGATION STILL ONGOING | 1268 | [54 empty] | YES | YES |  |  | YES |  |  | YES | 2017 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2002 | FREE SWIMMING | METAL LOSS |  | STANDARD RESOLUTION | [21 empty] | 2017 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | 2017 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | [8 empty] | IMU | 2017 | FREE SWIMMING |  |  |  | YES | 2020 | 1268 | NO | [13 empty] | NO | [63 empty] | JORGE LOPEZ | MANAGER ENGINEERING CODES AND COMPLIANCE | jorge_lopez@kindermorgan.com | [5 empty] | JAIME HERNANDEZ | DIRECTOR ENGINEERING CODES AND COMPLIANCE | 713-369-9443 | jaime_hernandez@kindermorga.com | ON SEPTEMBER 24, 2020 THE NATURAL GAS PIPELINE COMPANY OF AMERICA, LLC (NGPL) 20-INCH INDIAN BASIN PIPELINE EXPERIENCED AN IN-SERVICE FAILURE RESULTING IN A PIPELINE RUPTURE WITH NO FIRE. 00:44 - MEASUREMENT TECH 1 WAS CALLED OUT ON LOW-PRESSURE ALARM AT PIN 1753 OXY INDIAN BASIN. 01:20- MEASUREMENT TECH 1 ARRIVED ON SITE PIN 1753 AND STARTED INVESTIGATING. MEASUREMENT TECH 1 PUT HIS PRECISION GAUGE ON MAINLINE AND SAW LINE PRESSURE DROPPING DRASTICALLY. CONSEQUENTLY, CALLED LEAD TECH AND BOTH LOGGED ON CONCENTRATOR (SCADA) TO LOOK OVER MAINLINE PRESSURES USING METER STATION DATA. 01:54 - MEASUREMENT SUPERVISOR RECEIVED CALL FROM LEAD TECH REGARDING A POTENTIAL LINE LEAK AT INDIAN HILL STATION. AFTER CONFIRMING OTHER STATION PRESSURES ALONG THE LINE VIA SCADA, MEASUREMENT SUPERVISOR ADVISED TECHS TO START SHUTTING IN STATIONS. 01:55 - OXY INDIAN BASIN PIN 1753 SHUT -IN IB-4 MAINLINE VALVE ALSO SHUT. 02:20 - FASKEN NORTH INDIAN HILLS PIN 37613 SHUT-IN. 03:12 - EMERGENCY RESPONSE LINE (ERL) CALL NOTIFICATIONS INITIATED PER COMPANY PROCEDURES TO DISCUSS THE POTENTIAL INCIDENT. 03:19A- IB-3 SHUT IN. 04:00 - DCP FUEL PIN 1791 SHUT IN. 04:22 - OPERATIONS FOUND IB-1 OPEN AND HOLDING PRESSURE. 04:40- IB-2 FOUND CLOSED. 04:50 - HOLLY PIN 44836 MANUAL ISOLATION VALVE WAS SHUT IN; MEASUREMENT TECH 1 OPENED IT UP TO MONITOR LINE PRESSURE BETWEEN THAT SEGMENT- VALVES DOWN STREAM OF METER WERE LOCKED GOING TO CUSTOMER. 05:20- DCP BIG EDDY PIN 25776 - SHUT IN. 05:53- CALL TO NRC INITIATED (#1288123). 06:00- NGPL PERSONAL ON SITE CONFIRMED THE RUPTURED ON THE INDIAN BASIN PIPELINE. 06:18-ERL+ CALL NOTIFICATION INITIATED PER COMPANY PROCEDURES TO DISCUSS THE RUPTURE INCIDENT. ON SEPTEMBER 28, PIPE WAS REPLACED AND COVERED. NGPL SENT THE FAILED SPECIMEN TO A THIRD PARTY METALLURGICAL LAB AND IS CURRENTLY WAITING FOR THE METALLURGICAL REPORT. ON OCTOBER 1, 2020, NGPL RECEIVED CORRECTIVE ACTION ORDER (CAO) CPF NO. 2-2020-001-CAO FROM PHMSA. NGPL IS COMPLYING WITH THE REQUIRED CORRECTIVE ACTIONS IN THE CAO.
2021-02-26 10:37 | YES | NO | UNGS (Underground Natural Gas Storage) | 20200111 | 34416 | 2020-10-23 07:46 | ORIGINAL FINAL | 26330 | ENABLE OKLAHOMA INTRASTATE TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2020-09-24 11:00 | 2020 | CENTRAL | NO | 35.1441 | -96.1576 | 1288296 | 2020-09-25 18:34 | 1288409 | NATURAL GAS |  | 1000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | THE STORAGE FIELD WAS INJECTING AND THE WELL WAS ISOLATED. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-09-24 11:00 | 2020-09-24 12:00 | ONSHORE | OK | 74883 | WETUMKA | HUGHES | NOT APPLICABLE |  | WETUMKA STORAGE FACILITY | IW-40 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 4 | NO | NO | [22 empty] | INTRASTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | UNDERGROUND GAS STORAGE OR CAVERN | [38 empty] | 1997 | 1997 | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 309 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 2800 | 2800 | 120000 | 120000 | 5000 | 5000 | 0 | 0 |  | 2.8 | 127800 | 60281.1854931962 | 127800 | 0 | 0 | 0 | 0 | NO |  |  |  | 715 | 20000 | 827 | 192.619(A)(4) |  | 2018-09-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS MINOR AND IT COULD NOT HAVE BEEN DETECTED BY SCADA. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | SEAL (NOT COMPRESSOR SEAL) OR PACKING | [17 empty] | YES | P-SEAL ID PREP FAILED RESULING IN THE DSA RING GASKETS TO FAIL. | [150 empty] | YES | [10 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 626 3981 |  | CASEY ROBERTS | casey.roberts@enablemidstream.com | 405 626 3981 | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 626 3981 | casey.roberts@enablemidstream.com | ON 9/24/20 A THIRD-PARTY WEED CONTROL CONTRACTOR DISCOVERED AND REPORTED A LEAK AT THE IW-40 WELL IN THE WETUMKA STORAGE FACILITY. THE CONTRACTOR REPORTED THE LEAK TO AN ENABLE O&M TECHNICIAN. THE O&M TECHNICIAN ARRIVED AND OBSERVED WATER AROUND THE WELLHEAD AND BUBBLES. THE LEAK WAS MINOR AND WHEN THE WELL WAS ISOLATED (THE STORAGE FIELD WAS INJECTING AT THE TIME) THE LEAK CONTINUED BUT WAS REDUCED. IT WAS DETERMINED THE COST FOR REPAIR WOULD EXCEED $50,000 SO A CALL WAS PLACED TO THE NRC ON 9/25/2020 AT 18:34 CST (NRC#1288296) AND A 48-HR. FOLLOW UP (NRC#1288409) WAS PROVIDED 9/27/20 AT 15:31 CST. A CONTRACTOR WAS HIRED AND UPON INVESTIGATION, IT WAS DETERMINED THE LEAK STARTED IN THE INTERNAL P-SEAL INSIDE THE 11' 3K X 7-1/16' 3K 7-5/8' P-SEAL ID PREP THAT ULTIMATELY MADE ITS WAY ACROSS THE RING GASKET BETWEEN THE P-SEAL ID PREP AND THE DOUBLE-STUDDED ADAPTER (DSA), AND SEPARATELY ACROSS THE RING GASKET BETWEEN THE DSA AND THE CASING HEAD LOCATED BELOW THE DSA. THE WELL WAS FIXED AND WAS PLACED BACK INTO SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200112 | 34733 | 2020-10-23 22:42 | SUPPLEMENTAL FINAL | 5304 | FLORIDA GAS TRANSMISSION CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-09-24 09:48 | 2020 | EASTERN | YES | 26.6186 | -80.1734 | 1288141 | 2020-09-24 10:53 | 1288281 | NATURAL GAS |  | 12000 | 0 | 0.1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-09-24 10:13 |  | YES | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-09-24 10:45 | NO | [5 empty] | VALVE CLOSURE |  | 2020-09-24 10:06 | VALVE CLOSURE |  | 2020-09-24 10:13 | 0 | 2020-09-24 09:49 | 2020-09-24 09:52 | ONSHORE | FL | 33467 | LAKE WORTH | PALM BEACH | MILEPOST | 844.25 | 18IN MAINLINE | FLMEA21 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 38 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 18 | NO | 0.25 | 52000 | API 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | YOUNGSTOWN SHEET & TUBE | COLD APPLIED TAPE |  | YES | [26 empty] | 1959 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 264 | 18 |  | CLASS 3 LOCATION | YES | METHOD2 | 365 |  | NO | YES |  |  | 190000 | 190000 | 0 | 0 | 22920 | 22920 | 1360000 | 1360000 | 2000 | 2000 | 0 | 0 |  | 1.91 | 1574920 | 736171.157088774 | 1574920 | 0 | 0 | 0 | 0 | NO |  |  |  | 846 | 4.8 | 866 | 192.619(A)(1) |  | 2004-01-05 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 81312 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 3 | 0 | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED |  | YES | [15 empty] | STRESS CORROSION CRACKING | [12 empty] | YES | HIGH-PH STRESS CORROSION CRACKING. | 1088 | [54 empty] | YES | YES |  |  | YES |  |  |  | 2017 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2007 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [21 empty] | 2017 | FREE SWIMMING | HIGH RESOLUTION |  | INSIDE ILI CUPS | 2007 | FREE SWIMMING | HIGH RESOLUTION |  | INSIDE ILI CUPS | [14 empty] | YES | 2018 | 1447 | NO | [13 empty] | NO | [63 empty] | KATHRYN HARRYMAN | SENIOR SPECIALIST REGULATORY COMPLIANCE | kathryn.harryman@energytransfer.com | 713-989-7085 |  |  |  |  | TODD NARDOZZI | DIRECTOR REGULATORY COMPLIANCE | 713-989-7126 | todd.nardozzi@energytransfer.com | AT ~9:48 EDT ON 9/24/2020, LOCAL OPERATIONS PERSONNEL RECEIVED A CALL FROM LAKE WORTH DRAINAGE DISTRICT ABOUT A GAS LINE RUPTURE JUST NORTH OF THE INTERSECTION OF LAKE WORTH ROAD AND THE FLORIDA TURNPIKE. AT THE SAME TIME THE CONTROL CENTER SAW THE PRESSURE DROP ON THE DISCHARGE SIDE OF COMPRESSOR STATION 21 AND TOOK ACTION TO SHUT DOWN THE PIPELINE. LOCAL OPERATIONS CONFIRMED THE INCIDENT AT ~9:52 AND THE SEGMENT WAS ISOLATED BY CLOSING THE UPSTREAM AND DOWNSTREAM MLV'S. AT ~10:53 EDT ON 9/24/20, INITIAL NOTIFICATION WAS MADE TO THE NRC (REPORT# 1288141) AND AGAIN ON 09/25/20 AT ~4:47 EDT WITH THE 48 HOUR UPDATE NOTIFICATION; NRC # 128828. UPDATE: THE PIPELINE HAS SINCE BEEN REPAIRED AND WAS RESTARTED ON 12/11/2020 AS PER THE RESTART AGREEMENT WITH PHMSA. THE FAILED SECTION WAS SENT TO THE LABORATORY FOR ANALYSIS AND THROUGH METALLURGICAL ANALYSIS, THE FAILURE WAS IDENTIFIED TO BE HIGH PH - STRESS CORROSION CRACKING.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200113 | 34425 | 2020-10-26 08:25 | ORIGINAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2020-09-29 14:50 | 2020 | EASTERN | NO | 40.4173 | -75.6214 | 1288593 | 2020-09-29 15:02 | 1288776 | NATURAL GAS |  | 226.8 | 16384.89 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-09-30 15:00 | 2020-10-06 12:00 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-09-30 15:00 | VALVE CLOSURE |  | 2020-09-30 15:00 | 0 | 2020-09-28 08:30 | 2020-09-28 08:30 | ONSHORE | PA | 19504 | Not Within a Municipality | BERKS | MILEPOST | 223.54 | BECHTELSVILLE COMPRESSOR STATION | BECHTELSVILLE COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | MAINLINE | CHECK |  | WHEATLEY |  |  |  | 1988 | 1987 | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 671 |  | NO | NO |  |  | 0 | 0 | 44895 | 44895 | 621 | 621 | 70000 | 70000 | 0 | 0 | 0 | 0 |  | 2.74 | 115516 | 53383.6556127819 | 115516 | 0 | 0 | 0 | 0 | NO |  |  |  | 957 | 27738 | 1050 | 192.619(A)(2) |  | 1987-06-24 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 63360 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE VOLUME OF THE LEAK WAS TOO MINIMAL TO BE DETERMINED BY THE CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [5 empty] | YES | [29 empty] | YES | O-RING FAILURE | [161 empty] | MICHAEL MCGRATH | PIPELINE PERFORMACE AND COMPLIANCE | michael.mcgrath@enbridge.com | (612)805-6542 |  |  |  |  | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 713-627-5008 | nathan atanu | AT APPROXIMATELY 8:30 AM EDT ON SEPTEMBER 28, 2020 AN ENBRIDGE CONTRACTOR DISCOVERED A NATURAL GAS LEAK BELOW GROUND AT THE BECHTELSVILLE COMPRESSOR STATION ON THE TEXAS EASTERN TRANSMISSION (TETLP) SYSTEM IN BERKS COUNTY, PA. TETLP SUBSEQUENTLY PERFORMED ADDITIONAL INVESTIGATIONS BY PROBING HOLES AROUND THE SUSPECTED LEAK AREA. TETLP DETERMINED THAT THE SOURCE OF THE LEAK WAS FROM A CHECK VALVE ON 09/29/2020 AND DETERMINED COST OF REPAIR WILL EXCEED THE DOT INCIDENT REPORTING THRESHOLD ON 09/29/2020 AT APPROXIMATELY 2:50 PM EDT . TETLP IMMEDIATELY NOTIFIED THE NRC WITHIN ONE HOUR OF CONFIRMED DISCOVERY AT APPROXIMATELY 3:02 PM EDT. THE LINE WAS DEPRESSURIZED AND THE VALVE WAS EXCAVATED FOR INSPECTION. TETLP DETERMINED THAT THE VALVE SEALS WERE LEAKING AND REPLACED THE SEALS. THE LINE WAS RETURNED BACK TO SERVICE ON OCTOBER 6, 2020. THE APPARENT CAUSE OF THE LEAK WAS EQUIPMENT FAILURE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200115 | 34452 | 2020-10-29 12:57 | ORIGINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2020-09-30 04:28 | 2020 | EASTERN | NO | 44.7786 | -85.1223 | 1288774 | 2020-10-01 12:11 | 1288939 | NATURAL GAS |  | 7970 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | SHUT DOWN FACILITY WAS NOT REQUIRED AS TECHNICIAN WAS ABLE TO ISOLATE RELEASE |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-09-30 06:05 | 2020-09-30 06:05 | ONSHORE | MI | 49646 | KALKASKA | KALKASKA | NOT APPLICABLE |  | ANR PIPELINE CO. RAPID RIVER 35 | BLUE LAKE AREA | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ABOVEGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | PRESSURE SAFETY VALVE (PSV) #9402 PREMATURELY ACTIVATED AUTOMATICALLY RELEASING GAS FROM PIPING. | CLASS 1 LOCATION | NO |  | 406 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 12752 | 12752 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.6 | 12752 | 13220.5774278215 | 12752 | 0 | 0 | 0 | 0 | NO |  |  |  | 723 | 0 | 1050 | 192.619(A)(1) |  | 1979-10-20 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL CENTER DID NOT RECEIVE ANY ALARMS OR OTHER INDICATIONS THAT THERE WAS A RELEASE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | O-RING | [161 empty] | ROBERTA PRIMERA | US REGULATORY COMPLIANCE SPECIALIST | roberta_primera@tcenergy.com | 248-561-7803 |  |  |  |  | LEE ROMACK | DIRECTOR PIPELINE REGULATOR COMPLIANCE | 832-320-5315 | lee_romack@tcenergy.com | ON OCTOBER 1, 2020 AT 12:11 ( ALL TIMES ARE EASTERN STANDARD TIME) TC ENERGY/ANR PIPELINE COMPANY (ANR) REPORTED AN INCIDENT TO THE NATIONAL RESPONSE CENTER FOLLOWING THE UNINTENTIONAL RELEASE OF 7. 97 MILLION CUBIC FEET OF GAS TO THE ATMOSPHERE FROM THE RAPID RIVER 35 STORAGE FACILITY NEAR KALKASKA MICHIGAN. TECHNICIAN WAS CONTACTED BY GAS CONTROL BASED ON A NOISE COMPLAINT. TECHNICIAN CONFIRMED THERE WAS NOT AN OVER PRESSURE EVENT AND PROCEEDED TO ISOLATE PSV #9402. PSV #9402 IS A PILOT OPERATED VALVE ON A 4 INCH BRANCH CONNECTION THAT IS CONNECTED TO A 20 INCH PIPE. AFTER ISOLATING PSV #9402 THE TECHNICIAN REMOVED AND INSPECTED THE VALVE. AN O-RING WAS REPLACED AND THE PSV WAS PLACED INTO SERVICE ON THE SAME DAY.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200116 | 34464 | 2020-11-02 17:58 | ORIGINAL | 31451 | KINDER MORGAN TEXAS PIPELINE CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2020-10-04 07:41 | 2020 | CENTRAL | YES | 30.5665 | -94.9448 | 1288965 | 2020-10-04 08:27 | 1288967, 1289056 | NATURAL GAS |  | 118724 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-10-04 08:43 |  | YES | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-10-04 08:05 | NO | [5 empty] | VALVE CLOSURE |  | 2020-10-04 08:24 | VALVE CLOSURE |  | 2020-10-04 08:43 | 0 | 2020-10-04 07:41 | 2020-10-04 08:05 | ONSHORE | TX | 77335 | GOODRICH | POLK | MILEPOST | 47.6 | GOODRICH INDEX 85 | CROSBY LAUNCHER TO GOODRICH RECEIVER | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 1 | NO | YES | [6 empty] | YES | UNCASED | TRINITY RIVER | UNKNOWN | BELOW WATER, PIPE BURIED BELOW BOTTOM (NOT IN BORED/DRILLED CROSSING) | YES | [10 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 | NO | 0.485 | 60000 | API 5L | DSAW |  | UNKNOWN | COAL TAR |  | NO | [26 empty] | 1982 | 1982 | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | STILL UNDER INVESTIGATION. FIELD ASSESSMENT STILL ONGOING. APPROXIMATE SIZE INFORMATION BELOW WAS REQUIRED FOR SUBMITTAL OF REPORT. AS THIS TIME, THE APPROXIMATE SIZE IS TO BE DETERMINED. THE NUMBERS BELOW ARE PLACEHOLDERS. | 1 | 1 |  | CLASS 1 LOCATION | NO |  | 532 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 219639 | 219639 | 3500000 | 3500000 | 9267 | 9267 | 20000 | 20000 | METALLURGICAL EVALUATION | 1.85 | 3748906 | 1847736.40358736 | 3748906 | 0 | 0 | 0 | 0 | NO |  |  |  | 926 | 165 | 1032 | 192.619(A)(2) |  | 1982-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 42346 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  |  |  |  | YES |  |  |  |  | YES | STILL UNDER INVESTIGATION. METALLURGICAL REPORT STILL IN PROGRESS. | [19 empty] | YES | STILL UNDER INVESTIGATION. METALLURGICAL REPORT STILL IN PROGRESS. | UNKNOWN | [54 empty] | YES | YES |  |  | YES |  |  |  | 2017 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2017 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [21 empty] | 2017 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | 2017 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | [14 empty] | YES | 1999 | 1920 | Yes, but the point of the Accident was not identified as a dig site |  | 2017 |  |  | 2017 | [5 empty] | YES |  |  | NO | [63 empty] | SHELLEY DIETZ | PIPELINE ENGINEER | shelley_dietz@kindermorgan.com | [5 empty] | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | ON OCTOBER 4, 2020 THE KINDER MORGAN TEXAS PIPELINE (KMTP) 24-INCH INDEX 85 PIPELINE EXPERIENCED AN IN-SERVICE FAILURE RESULTING IN A PIPELINE RUPTURE WITH NO FIRE. THE SEQUENCE OF EVENTS IS BELOW. 7:41AM LANDOWNER 1 CALLED OPERATOR 1 SPEAKING ABOUT NOISE 7:44AM OPERATOR 1 BEGAN DISPATCH PROCESS 7:44AM LOW ALARM RECEIVED AT PIN 42680 4367 REGULATOR 7:47AM OPERATIONS SUPERVISOR CALLED OPERATOR 1 7:50AM LOW LOW PRESSURE ALARM RECEIVED AT NELSON CS, GAS CONTROL NOTIFIED OPERATOR 1 7:51AM OPERATIONS SUPERVISOR DISPATCHED OPERATOR 2 TO MLV 4364 7:52AM OPERATIONS SUPERVISOR DISPATCHED OPERATOR 3 TO THE PLANT 7:53AM OPERATIONS SUPERVISOR DISPATCHED OPERATOR 4 TO THE PLANT 7:54AM OPERATIONS SUPERVISOR DISPATCHED OPERATOR 5 TO MLV 4367 7:55AM OPERATIONS SUPERVISOR NOTIFIED OPERATIONS MANAGER 7:55AM GAS CONTROL RECEIVED NOTIFICATION FROM LANDOWNER 2 OF A RUPTURE NEAR NELSON CS/GOODRICH AREA 8:00AM OPERATIONS SUPERVISOR INITIATED ERL (EMERGENCY RESPONSE LINE) PROCESS. GAS CONTROL SENT ERL CALL @8:10 POSSIBLE LEAK AND NOTIFIED GAS CONTROL MANAGER ON CALL 8:01AM OPERATIONS SUPERVISOR DIRECTED OPERATOR 6 TO SHUT IN ALL VALVES TIED TO INDEX 85 AT THE PLANT 8:05AM OPERATOR 1 ARRIVED AT TRINITY RIVER BRIDGE. GAS WAS BLOWING FROM THE NORTH RIVER BANK. DPS TROOPER AND GOODRICH FIRE CHIEF WERE ON SITE. DPS HAD STOPPED ALL TRAFFIC ON US 59. 8:10AM OPERATOR 1 NOTIFIED OPERATIONS SUPERVISOR THAT DPS HAD SHUT DOWN BOTH SIDES OF HWY 59 AND RESIDENTS WERE BEING EVACUATED. (KMTP HAS NOT BEEN ABLE TO CONFIRM THAT EVACUATIONS WERE IN FACT ORDERED, SEE ANSWER TO A23.) 8:13AM GAS CONTROL SHUT IN DAYTON STORAGE 200 MMBTU INJECTION. 8:17AM OPERATIONS SUPERVISOR DISPATCHED PERSONNEL TO GOODRICH PLANT (OPERATOR 6), GOODRICH STATION (OPERATOR 1), HWY 223 MLBV (OPERATOR 5), AND PELICAN RD. MLBV (OPERATOR 2). 8:22AM GAS CONTROL NOTIFIED NGPL, MIDCOASTAL, AND TEJAS THAT THEY WERE GOING TO HAVE TO SHUT IN 8:24AM MLV 4367 AND REGULATOR 10IN BYPASSES CLOSED 8:27AM INITIAL REPORT MADE TO NRC (#1288965) 8:31AM GAS CONTROL SENT ERL+ CALL @ 8:40AM KMTP LINE RUPTURE 8:41AM PIN 41835 WELL CONNECT SUPPLYING GAS TO INDEX 85 SHUT IN BY OPERATOR 6 8:43AM OPERATOR 6 REPORTED INDEX 85 SHUT IN AT PLANT 8:51AM INDEX 85 BLOWN DOWN PER ONSITE FIELD PERSONNEL (OPERATOR 1) 9:40AM OPERATIONS CONFIRMED KMTP INDEX 85 24IN LINE RUPTURE LOCATED ON THE NORTH BANK OF THE TRINITY RIVER AND SOUTH OR SUCTION SIDE OF NELSON CS. OPERATIONS SHUT IN MLBV HWY 223 AND NELSON CS SHUT IN. 9:47AM GAS CONTROL SENT ERL + UPDATE INFO ONLY, LINE ISOLATED, INVESTIGATION UNDERWAY. REPORTABLE TO NRC AND TRRC GAS VOLUME LOSS. PIPELINE REMOVAL AND REPAIR IS ONGOING. THE CAUSE OF THIS INCIDENT IS STILL UNDER INVESTIGATION. KMTP WILL PROVIDE REPAIR INFORMATION AND INVESTIGATION RESULTS IN A SUPPLEMENTAL REPORT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200117 | 34472 | 2020-11-04 10:36 | ORIGINAL FINAL | 38932 | BLUESTONE PIPELINE COMPANY OF PA, LLC | ONE ENERGY PLAZA - WCB 2130 | DETROIT | MI | 48226 | 2020-10-05 11:30 | 2020 | EASTERN | YES | 41.983 | -75.547 | 1289015 | 2020-10-05 12:13 | 1289039 | NATURAL GAS |  | 14600 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | IDLE | [5 empty] | NO |  |  | NO | [11 empty] | 0 | 2020-10-05 08:20 | 2020-10-05 08:50 | ONSHORE | PA | 18847 | Not Within a Municipality | SUSQUEHANNA | NOT APPLICABLE |  | BLUESTONE OF PA | HARMONY COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | UNKNOWN | 2015 | CARBON STEEL |  | OTHER | [8 empty] | FAILURE OF THE REGULATOR RESULTED IN THE OPERATION OF AN OVER PRESSURE PROTECTION DEVICE TO OPERATE AND VENTED GAS TO ATMOSPHERE | CLASS 1 LOCATION | NO |  | 712 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 40004 | 40004 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2.74 | 40004 | 41473.9632545932 | 40004 | 0 | 0 | 0 | 0 | NO |  |  |  | 170 | 0 | 220 | 192.619(A)(2) |  | 2015-03-09 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO SCADA SENSING ON THAT LEG OF THE FUEL SKID | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [24 empty] | YES | [163 empty] | PATRICK J RAICHEL | SUPERVISOR - CODES AND COMPLIANCE | patrick.raichel@dteenergy.com | 716-327-6630 |  | MICHAEL GRAVES | michael.graves@dteenergy.com | 212-303-0722 | PHILIP COLEMAN | DIRECTOR - CODES AND REGULATORY | 7347304870 | philip.coleman@dteenergy.com | AT APPROXIMATELY 0435 HOURS ON SATURDAY OCT. 3, 2020, A FAILURE OF THE WORKING MONITOR REGULATOR SET UP ON THE FUEL GAS SKID AT HARMONY STATION RESULTED IN THE OPERATION OF THE OVER PRESSURE PROTECTION DEVICE IMMEDIATELY DOWNSTREAM. THIS RESULTED IN THE RELEASE OF 14.6 MMCF OF NATURAL GAS OVER THE NEXT TWO DAYS. THE RELEASE OF GAS WAS SECURED UPON ITS DISCOVERY ON THE MORNING OF MONDAY, OCTOBER 5TH. INTERNAL INVESTIGATION OF THE EVENT DETERMINED THE LIKELY CAUSE OF THE REGULATOR FAILURE WAS EXCESSIVE CYCLING (CHATTERING) OF THE REGULATOR LEADING TO A PREMATURE FAILURE OF THE INTERNAL SOFT COMPONENTS. ENGINEERING IS EVALUATING A CHANGE OF DESIGN AND/OR COMPONENTS TO PREVENT REOCCURRENCE.
2021-02-26 10:37 | NO | NO | UNGS (Underground Natural Gas Storage) | 20200118 | 34517 | 2020-11-05 14:58 | SUPPLEMENTAL FINAL | 32396 | BOBCAT GAS STORAGE (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2020-10-09 20:30 | 2020 | CENTRAL | YES | 30.542 | -91.9156 | 1289408 | 2020-10-09 22:00 | 1289485 | NATURAL GAS |  | 2718 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-10-09 20:30 | 2020-10-11 21:30 |  | NO |  |  | NO | [11 empty] | 0 | 2020-10-09 20:30 | 2020-10-09 20:30 | ONSHORE | LA | 70577 | Not Within a Municipality | ST. LANDRY | NOT APPLICABLE |  | BOBCAT GAS STORAGE | BOBCAT GAS STORAGE | NO | OPERATOR-CONTROLLED PROPERTY | BELOWGROUND STORAGE OR ABOVEGROUND STORAGE VESSEL, INCLUDING ATTACHED APPURTENANCE |  |  |  |  | NO | [22 empty] | INTERSTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | UNDERGROUND GAS STORAGE OR CAVERN | [38 empty] | 2008 | 2008 | CARBON STEEL |  | OTHER | [8 empty] | EMERGENCY SHUTDOWN SYSTEM (ESD) | CLASS 1 LOCATION | NO |  | 804 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 7475 | 7475 | 0 | 0 | 5000 | 5000 | 0 | 0 |  | 2.75 | 12475 | 10044.803850174 | 12475 | 0 | 0 | 0 | 0 | NO |  |  |  | 920 | 0 | 3395 | 192.619(A)(2) |  | 2014-02-25 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CAUSE OF THE ESD WAS THE RESULT OF COMMERCIAL POWER LOSS AS RESULT OF HURRICANE DELTA. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | BACKUP GENERATOR FAILED TO START WITH LOSS OF COMMERCIAL POWER. |  |  |  |  | YES | [173 empty] | MICHAEL MCGRATH | PIPELINE PERFORMANCE AND COMPLIANCE SPECIALIST | michael.mcgrath@enbridge.com | 612-805-6542 |  |  |  |  | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 713-627-5008 | nathan.atanu@enbridge.com | AT APPROXIMATELY 8:30 PM CDT ON OCTOBER 9, 2020, BOBCAT STORAGE LLC'S (BOBCAT STORAGE) FACILITY LOST COMMERCIAL DUE TO HURRICANE DELTA. FOLLOWING THE LOSS OF COMMERCIAL POWER, THE BACKUP GENERATOR FAILED TO START. AS A RESULT, THE STATION SHUT IN AND CAVERN 5 TOP SIDE VENTED (188 MSCF). AT APPROXIMATELY 12:17 AM CDT ON OCTOBER 10, 2020, THE ESD BATTERIES HAD DRAINED AND THE REMAINING TOPSIDE CAVERN'S VENTED (2530 MSCF). THE TOTAL GAS VENTED FROM THE STATION WAS 2718 MMCF. AN ADDITIONAL GENERATOR WAS BROUGHT TO SITE AND THE STATION WAS RETURNED TO NORMAL OPERATION ON OCTOBER 11, 2020. THERE WERE NO DELIVERIES OR RECEIPTS FLOWING TO ANY CUSTOMERS AT THE TIME OF THE COMMERCIAL POWER OUTAGE. A NEW BACKUP GENERATOR(S) WILL BE PURCHASED AND INSTALLED TO MITIGATE A SIMILAR EVENT. PART D.3. IS THE LARGEST PIR ASSOCIATED WITH THE PIPING AT THE STATION. PART E.2.A-C IS THE MAOP OF THE PIPE ASSOCIATED WITH THE LARGEST PIR.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20200119 | 34904 | 2020-11-06 13:11 | SUPPLEMENTAL FINAL | 39352 | GENESIS OFFSHORE HOLDINGS, LLC | 919 MILAM STREET SUITE 2100 | HOUSTON | TX | 77002 | 2020-10-11 13:00 | 2020 | CENTRAL | YES | 28.0974 | -93.5021 | 1289495 | 2020-10-11 14:34 | 1289544 | NATURAL GAS |  | 25846 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | ROUTINE SHUTDOWN | [5 empty] | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-10-12 18:00 | NO | [11 empty] | 0 | 2020-10-11 12:00 | 2020-10-12 12:30 | OFFSHORE | [6 empty] | HI 330 | PLATFORM | [20 empty] | 255 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | HIGH ISLAND | 330 | PLATFORM | INTERSTATE | OFFSHORE PLATFORM, INCLUDING PLATFORM-MOUNTED EQUIPMENT AND PIPING | PIPE | PIPE BODY | 30 | NO | 0.5 | 60000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | STELCO | ASPHALT |  | UNKNOWN | [26 empty] | 1977 | 1976 | CARBON STEEL |  | OTHER | [8 empty] | PIPE WAS SEVERED. | CLASS 1 LOCATION | NO |  | 1138 |  | NO | YES |  |  | 0 | 0 | 0 | 0 | 54277 | 54277 | 100000000 | 100000000 | 0 | 0 | 0 | 0 |  | 2.1 | 100054277 | 45958910.1137171 | 100054277 | 0 | 0 | 0 | 0 | NO |  |  |  | 705 | 0 | 1440 | 192.619(A)(1) |  | 1977-08-06 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | OFFSHORE GATHERING | YES | YES | NO | NO | NO | AIR PATROL |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS CAUSED BY A NATURAL DISASTER. CONTROLLER ACTION HAD NO CAUSE IN THE EVENT. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | [52 empty] | HIGH WINDS |  |  |  |  | ,,, | YES | YES | [305 empty] | JORGE MORICE | PIPELINE COMPLIANCE SPECIALILST | jorge.morice@genlp.com | 7137251663 |  | NORMAN GIBSON | norman.gibson@genlp.com | 9857463981 | JOHN JEWETT | SR. MANAGER DOT COMPLIANCE | 7138602605 | john.jewett@genlp.com | HURRICANE DELTA PASSED THROUGH THE HIGH ISLAND AREA OF THE GOM BETWEEN 10/8 AND 10/10. GENESIS OFFSHORE FACILITIES WERE EVACUATED ON 10/6, PRIOR TO THE PASSING OF THE HURRICANE. SCADA ALSO SHOWS THAT COMMUNICATIONS WERE LOST TO HI 330 ON 10/6. ON 10/11 A PATROL HELICOPTER WAS SENT TO PATROL THE AREA FOR STATUS IDENTIFICATION. AT 1:00PM THE OFFSHORE PIPELINE MANAGER FOR HIOS RECEIVED A PHONE CALL FROM HI 264 THAT THE PLATFORM ON HI 330A WAS NOT VISIBLE ABOVE THE WATER SURFACE. WHAT REMAINS OF THE STRUCTURE IS THE FOUR LEGS AT VARYING HEIGHTS ABOVE THE WATER SURFACE. NRC CALL WAS MADE AND THE COMPANY HAS WORKED WITH SEVERAL AGENCIES INCLUDING BSEE, PHMSA, AND USCG IN THE DISSEMINATION OF INVESTIGATION DATA. THE DOT ASSETS THAT WERE AFFECTED BY THIS INCIDENT IS A 24" NATURAL GAS PIPELINE FROM HI 370 TO HI 330 AND A 30" HI 330 TO HI 343. THIS REPORT INCLUDES THE PIPE INFORMATION FOR THE 30" HI 330 TO HI 343. BOTH PIPELINES WERE SEVERED ABOVE THE WATER SURFACE. PART A, QUESTION 7: FOR CLARIFICATION THE HIOS 30" HAS A NATURAL GAS VOLUME LOST OF 19,054 MCF AND THE HIOS 24" HAS A NATURAL GAS VOLUME LOST OF 6,792 MCF. THE VOLUME ENTERED IN THIS QUESTION IS THE SUM OF THE VOLUME LOST IN BOTH PIPELINES. PART D, QUESTION 7: DUE TO THE MAGNITUDE OF THE ASSETS LOST, GENESIS IS STILL CALCULATING THE COST OF DAMAGE. SUPPLEMENTAL (2/24/2021): DUE TO THE AFFECTS OF THE HIOS ASSETS (HIA330M PLATFORM/24" PIPELINE/30" PIPELINE) CAUSED BY HURRICANE DELTA, ALL OF THE AFOREMENTIONED ASSETS WILL NOT BE RE-BUILT NOR RETURNED TO SERVICE. ORIGINAL CONSTRUCTION COSTS WERE INCURRED ALMOST 50 YEARS AGO AND THOSE ASSOCIATED COSTS ARE NO LONGER AVAILABLE. A VERY HIGH LEVEL ESTIMATE IN TODAY'S NUMBERS COULD BE AS MUCH AS 100 MILLION PLUS DOLLARS.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20200120 | 34521 | 2020-11-11 16:28 | ORIGINAL | 40069 | STINGRAY PIPELINE COMPANY, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-10-11 14:55 | 2020 | CENTRAL | YES | 28.0973 | -93.5027 | 1289546 | 2020-10-12 11:51 | 1289549 | NATURAL GAS |  | 63214 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | IDLE | [5 empty] | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | BLOW DOWN |  | VALVE CLOSURE |  | 2020-10-12 10:00 | 0 | 2020-10-11 14:55 | 2020-10-12 10:00 | OFFSHORE | [6 empty] | 24" 100 LINE | 4813 | [20 empty] | 255 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | HIGH ISLAND | 330 | PLATFORM | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 24 | NO | 0.5 | 60000 | X60 | SINGLE SAW |  | UNKNOWN | OTHER | CONCRETE | UNKNOWN | [26 empty] | 1977 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 75.4 | 24 |  | CLASS 1 LOCATION | NO |  | 585 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 141599 | 141599 | 0 | 0 | 0 | 0 | 100000 | 100000 | ESTIMATED COSTS UNKNOWN UNTIL RECOVERY PLAN IS FULLY DEVELOPED AND IMPLEMENTED. | 2.24 | 241599 | 192704.751544163 | 241599 | 0 | 0 | 0 | 0 | NO |  |  |  | 720 | 0 | 1250 | 192.619(A)(1) |  | 1983-11-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  | MANUAL | 10560 | YES | [7 empty] | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | YES | YES | YES | NO | NO | OTHER | GENESIS OPERATOR OF PLATFORM HI 330 |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NATURAL ENVIRONMENTAL FACTORS. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [52 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | ,,,,,,CATEGORY 3 HURRICANE DELTA | YES | YES | [268 empty] | YES | [36 empty] | TODD NARDOZZI | DIRECTOR - REGULATORY COMPLIANCE | todd.nardozzi@energytransfer.com | 7139897126 |  |  |  |  | TODD NARDOZZI | DIRECTOR - REGULATORY COMPLIANCE | 7139897126 | todd.nardozzi@energytransfer.com | THE HI 330 PLATFORM WAS COMPLETELY DESTROYED BY HURRICANE DELTA ON OCTOBER 11TH, 2020. THE CATEGORY 3 STORM IMPACTED THE AREA WITH 125MPH + WINDS AND 10-25 FT WAVES. THE 24" PIPELINE HAD BEEN SHUTDOWN PRIOR TO THE STORM DUE TO PRODUCERS NOT HAVING COME BACK ONLINE YET FROM PRIOR STORMS IN THE GULF. UPON INSPECTION OF THE HI-330 PLATFORM ON OCTOBER 12TH, 2020 AND NOTING THE 24" FAILURE, THE DOWNSTREAM VALVE WAS CLOSED AND THE LINE ISOLATED. A RECOVERY PLAN IS STILL BEING DEVELOPED AND EVALUATED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200121 | 34543 | 2020-11-17 12:03 | ORIGINAL FINAL | 19610 | TRANSWESTERN PIPELINE COMPANY LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-10-19 06:02 | 2020 | MOUNTAIN | YES | 32.5324 | -103.8093 | 1290106 | 2020-10-19 07:44 | 1290280 | NATURAL GAS |  | 7894 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-10-18 08:22 | 2020-10-18 08:35 |  | NO |  |  | NO | [11 empty] | 0 | 2020-10-18 08:11 | 2020-10-18 08:15 | ONSHORE | NM | 88220 | CARLSBAD | LEA | MILEPOST | 79.4 | WT-1 CARLSBAD COMPRESSOR STATION | NMBW119 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1960 | 1959 | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE OPERATION - MALFUNCTION OF RELIEF VALVE DUE TO CONTROL PILOT. | CLASS 1 LOCATION | NO |  | 526 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 4736 | 4736 | 0 | 0 | 500 | 500 | 0 | 0 |  | 0.6 | 5236 | 5139.53944013551 | 5236 | 0 | 0 | 0 | 0 | NO |  |  |  | 988 | 423 | 1008 | 192.619(C) |  | 1960-01-01 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A RELIEF VALVE FAILURE WAS THE CAUSE OF THE GAS RELEASE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | SHORTER THAN NORMAL LIFE OF THE PARTS IN THE PILOT THAT CONTROLS THE RELIEF VALVE. | [22 empty] | YES | RELIEF VALVE PILOT FAILURE. | [161 empty] | KATHRYN HARRYMAN |  | kathryn.harryman@energytransfer.com | 713-989-7085 |  |  |  |  | TODD NARDOZZI |  | 713-989-7126 | todd.nardozzi@energytransfer.com | 08:11 MTN, OCTOBER 18TH TECHNICIAN CONTACTED GAS CONTROL TO NOTIFY THEM OF GAS BLOWING. AT 08:22 MTN ISOLATED RELIEF VALVE THEN TESTED AND FOUND THAT THE RELIEF CONTROL PILOT WOULD NOT HOLD A SET POINT. REPLACED WITH SPARE RELIEF CONTROL PILOT, RETESTED AND SET PRESSURE. 08:35 MTN, RESTARTED UNITS AND FOUND THAT EVERYTHING WAS BACK TO NORMAL. 06:46 MTN, OCTOBER 19TH ROUGH CALCULATION OF GAS VOLUME LOSS WAS COMPLETED, NOTIFIED REGULATORY. 07:44 MTN, OCTOBER 19TH NRC NOTIFICATION WAS MADE NRC #1290106. 06:08 MTN, OCTOBER 21ST 48 HOUR NRC NOTIFICATION WAS MADE NRC #1290280, UPDATED GAS VOLUME.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200122 | 34841 | 2020-11-19 16:59 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2020-11-07 11:30 | 2020 | EASTERN | YES | 46.4958 | -88.7313 | 1291637 | 2020-11-07 11:41 | 1291732 | NATURAL GAS |  | 1958 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | THE INCIDENT WAS A SMALL LEAK THAT DID NOT REQUIRE TO BE SHUT DOWN. |  |  |  | YES | OPERATOR | 2020-11-07 13:00 | NO | [5 empty] | OPERATIONAL CONTROL | WAKEFIELD COMPRESSOR STATION LOWERED PRESSURE |  | OPERATIONAL CONTROL | MONITORED PRESSURE AT BLOCK VALVE 5 |  | 0 | 2020-11-03 15:05 | 2020-11-04 20:00 | ONSHORE | MI | 49961 | Not Within a Municipality | HOUGHTON | MILEPOST | 63.5 | WAKEFIELD TO MARQUETTE | M433B | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 40 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 16 |  | 0.203 | 60000 | API-5LX | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | YOUNGSTOWN | COLD APPLIED TAPE |  | UNKNOWN | [7 empty] | PIPE GIRTH WELD |  | NO | [16 empty] | 1965 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 339 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 206646 | 206646 | 688146 | 688146 | 0 | 0 |  | 0 | 894792 | 410733.138726813 | 894792 | 0 | 0 | 0 | 0 | NO |  |  |  | 782 | 60000 | 945 | 192.619(A)(2) |  | 1965-12-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 306240 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | CONTRACTOR WORKING FOR THE OPERATOR | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [8 empty] | YES | A CRACK IN THE GIRTH WELD APPROXIMATELY 80% OF THE WALL THICKNESS | [12 empty] | YES | [8 empty] | 1202 | [54 empty] | YES |  |  |  |  | YES | [44 empty] | 2018 | FREE SWIMMING | 2014 | FREE SWIMMING | [10 empty] | NO |  |  | NO | [13 empty] | NO | [41 empty] | YES | [21 empty] | J. DAVID CULLISON | SR. PIPELINE SAFETY ENGINEER | j.cullison@nngco.com | 402-398-7439 |  |  |  |  | TOM CORRELL | VICE PRESIDENT OF PIPELINE SAFETY AND RISK | 402-398-7715 | thomas.correll@nngco.com | ON 11/4/20, A CONTRACTOR WAS EVALUATING THE RIGHT-OF-WAY AND DISCOVERED BUBBLES. LEAK DETECTION FOUND VERY LIMITED AMOUNT OF GAS DETECTED. OPERATIONS CONFIRMED THIS LOCATION HAD A LEAK IN 2017 THAT WAS REMEDIATED WITH A PIPE REPLACEMENT AND ANTICIPATED THE EXISTING STOPPLE MAY BE LEAKING. A STOPPLE TECHNICIAN REPLACED THE BLEED VALVE ON THE STOPPLE AND THE LEAK WAS NO LONGER DETECTED. IT WAS CONFIRMED 11/5/20 AT 0800 HOURS THE LEAK HAD BEEN REMEDIATED. ON 11/6/20, A CONTRACTOR HEARD BUBBLES NEAR THE EDGE OF THE EXCAVATION THAT APPEARED TO BE MIGRATING FROM A SEPARATE LOCATION. HAND EXCAVATION FOUND A GIRTH WELD WAS THE SOURCE OF THE LEAK NOW DETECTED. A TECHNICIAN ARRIVED ON 11/7/20 TO INSTALL A CLAMP TO REMEDIATE THE LEAK. IT WAS DETERMINED THAT CLEARING OFF THE COATING AND PREPARING THE PIPE FOR A CLAMP THAT IT WOULD BE SAFER TO PERFORM A STOPPLE BYPASS. ONCE THIS WAS DETERMINED, THE NRC WAS NOTIFIED AS THE REPAIR WOULD EXCEED THE REPORTING THRESHOLD. A STOPPLE CREW ARRIVED ON SITE 11/9/20. THE PIPE WAS ON BYPASS AT 1103 ON 11/10/20. THE REPAIRS WHERE MADE AND THE PIPE WAS RETURNED TO SERVICE AT 1213 ON 11/11/20. METALLURGICAL EVALUATION DETERMINED THAT THE AMOUNT OF CORROSION PRESENT ON THE SURFACE AS WELL AS THE 80% OF THE WALL THICKNESS, TRANS GRANULAR BRITTLE FRACTURING THE CRACK, POSSIBLY OCCURRED DURING OR SHORTLY AFTER WELDING THE TWO JOINTS OF PIPE, WHICH PRESENTED THE LOCATION OF THE FAILURE POINT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200123 | 34792 | 2020-11-20 12:58 | SUPPLEMENTAL FINAL | 19580 | TRANSCOLORADO GAS TRANSMISSION COMPANY LLC | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2020-10-27 12:45 | 2020 | MOUNTAIN | YES | 37.3484 | -108.2041 | 1290817 | 2020-10-27 13:43 | 1290916 | NATURAL GAS |  | 3820 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-10-26 18:25 | 2020-10-29 10:00 |  | NO |  |  | NO | [11 empty] | 0 | 2020-10-26 18:25 | 2020-10-26 19:12 | ONSHORE | CO | 81328 | Not Within a Municipality | MONTEZUMA | MILEPOST | MP 242 | TRANSCOLORADO MAINLINE/MANCOS COMPRESSOR STATION | DOLORES TO RED MESA | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | BLOWDOWN FROM THE VENT VALVE. | CLASS 1 LOCATION | NO |  | 545 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 6876 | 6876 | 0 | 0 | 500 | 500 | 0 | 0 |  | 1.8 | 7376 | 7358.17461073919 | 7376 | 0 | 0 | 0 | 0 | NO |  |  |  | 960 | 63218 | 1287 | 192.619(A)(2) |  | 2004-06-22 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS CONTOLLER ACTIONS WERE NOT DETERMINED TO CAUSE THE ESD OR GAS RELEASE FROM VENT PIPING. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | BUILDUP OF WATER-ICE IN ESD VENT VALVE SUPPLY PIPING REDUCING PRESSURE REQUIRED TO KEEP THE ESD VENT VALVE SHUT. | [13 empty] | YES | [8 empty] | YES | WATER VAPOR IN DRIED AIR SYSTEM ENDPOINT DEVICES. PERIOD PURGING REQUIRED. | [161 empty] | STEPHEN R. DINES | ENGINEER | stephen_dines@kindermorgan.com | 719 351-4199 |  | MIKE JOHNSON | mike_johnson2@kindermorgan.com | 505 632-6042 | JAIME HERNANDEZ | DIRECTOR-ENGINEERING | 713 369-9443 | jaime_hernandez@kindermorgan.com | ON 10/26/2020 AT 18:25 LOCAL TIME, THE TRANS COLORADO GAS TRANSMISSION COMPANY LLC (TCP)- MANCOS COMPRESSOR STATION EXPERIENCED AN UNPLANNED ESD EVENT. UNIT 380 WAS ONLINE AT THE TIME OF THE ESD AND SHUT DOWN. WHEN THE LOCAL OPERATION'S TECHNICIAN ARRIVED ON SITE AT 19:12 LOCAL TIME THAT DAY, THE STATION COMPRESSOR UNIT NOS. 380 AND 381 WERE BOTH OBSERVED TO BE OFF-LINE AND BLOWN-DOWN AS DESIGNED BY THE STATION AUTOMATION SYSTEM. THE ON-SITE GENERATOR UNIT 382 WITH FUEL SYSTEM WAS ALSO COMPLETELY BLOWN-DOWN. THE OPERATION'S TECHNICIAN ALSO CONFIRMED THE STATION YARD PIPING WAS FULLY BLOWN DOWN WITH THE SUCTION SIDE ESD VENT VALVE STUCK IN TRANSITION BETWEEN THE CLOSED AND OPEN POSITIONS. SIDE GATE VALVES WITH THE MAINLINE PIPE WERE IN THE CLOSED POSITION. THE TOTAL ESTIMATED GAS LOSS WAS 184 MSCF AND CALCULATED USING STATION PIPE VOLUME AND PRESSURE AND DETERMINED NOT TO BE A REPORTABLE EVENT SINCE A REPORTABLE QUANTITY HAD NOT BEEN EXCEEDED. WHILE INVESTIGATING THE IMMEDIATE CAUSE, THE OPERATION'S TECHNICIAN OBSERVED THE DISCHARGE SIDE ESD VENT VALVE IN THE CLOSED POSITION. THE EXPECTED POSITION OF THE ESD VENT VALVES AFTER A STATION ESD IS FULL OPEN. PER KINDER MORGAN PROCEDURES, A STATION ESD THAT RESULTS IN A RELEASE OF NATURAL GAS UNDER THE PHMSA REPORTING THRESHOLD FOR NATURAL GAS MUST BE INVESTIGATED AS AN ABNORMAL OPERATION. THE INITIAL INVESTIGATION FOUND ICE PRESENT IN THE PNEUMATIC SYSTEM THAT CONTROLS THE STATIONS TWO MAIN ESD VENT VALVES. OPERATIONS DECIDED TO LEAVE THE STATION DOWN AND RESUME THE INVESTIGATION THE FOLLOWING DAY SINCE THE AMBIENT TEMPERATURES WERE BELOW FREEZING AND IT WAS BECOMING TOO DARK TO WORK SAFELY. ADDITIONAL INVESTIGATION ON 10/27/2020 REVEALED THAT THE SUCTION SIDE ESD VENT VALVE OPENED PRIOR TO THE ESD AT 16:59:08 ON 10/26/2020, ABOUT 86 MINUTES PRIOR TO THE ESD EVENT. BASED ON THIS INFORMATION, AT 12:45 LOCAL TIME, IT WAS DETERMINED THAT GAS LOSS VOLUMES EXCEEDED THE REPORTABLE THRESHOLD OF 3,000 MSCF. AT 13:05 LOCAL TIME ON 10/27/2020, CONFIRMATION OF DISCOVERY THAT A REPORTABLE INCIDENT WAS IMMEDIATELY REPORTED TO THE NRC AT 13:43 LOCAL TIME. THE INVESTIGATION TEAM CONCLUDED THAT THE BUILDUP OF WATER OVER TIME FROZE AND BLOCKED THE SUPPLY OF AIR TO THE SUCTION-ESD BLOWDOWN VENT VALVE OPERATOR, THEREBY REDUCING THE PRESSURE REQUIRED TO KEEP THE SUCTION-ESD VENT VALVE SHUT AND ALLOWING IT TO OPEN SLOWLY AND RELEASE GAS. ONCE THE SUCTION-ESD VALVE OPENED FAR ENOUGH, IT ACTIVATED THE "OPEN" LIMIT SWITCH ON THE SUCTION-ESD BLOWDOWN VALVE AND ALONG WITH SENSING FLOW WITHIN THE ESD VENT PIPING RESULTING IN A FULL STATION ESD. THE ROOT CAUSE OF THE EVENT WAS DETERMINED TO BE FAILURE TO REALIZE THAT END-POINT DEVICES ON A DRIED AIR SYSTEM STILL REQUIRE PERIODIC PURGING/DRAINING TO PREVENT ACCUMULATION OF WATER OVER EXTENDED PERIODS OF TIME. TCP IS WORKING TO IMPLEMENT ADDITIONAL MAINTENANCE PROCEDURES FOR REGULAR PURGING AND DRAINING OF ESD PIPING/ENDPOINT DEVICES ON INSTRUMENT AIR SYSTEMS AND ENTER THEM INTO OUR OPERATION\MAINTENANCE WORK-TRACKING SYSTEM. TCP PLANS TO EVALUATE OTHER STATIONS ON THE TCP SYSTEM TO DETERMINE IF PURGING AND DRAINING MAINTENANCE OF ESD PIPING/ENDPOINT DEVICES IS REQUIRED TO MINIMIZE THE POTENTIAL FOR A REOCCURRENCE OF THIS TYPE OF EVENT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200124 | 34604 | 2020-11-23 16:36 | SUPPLEMENTAL FINAL | 5304 | FLORIDA GAS TRANSMISSION CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-10-28 00:05 | 2020 | CENTRAL | YES | 31.1169 | -88.0122 | 1290975 | 2020-10-29 13:00 | 1291048 | NATURAL GAS |  | 84000 | 0 | 0.1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | LOST POWER DUE TO HURRICANE ZETA |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-10-28 22:00 | 2020-10-28 23:59 | ONSHORE | AL | 36560 | MOUNT VERNON | MOBILE | MILEPOST | 190.8 | COMPRESSOR STATION 11 MOUNT VERNON | MSMEA -24 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | FILTER/STRAINER/SEPARATOR | [38 empty] | 2019 | 2019 | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL | LEAK |  |  | OTHER | ACTUATOR FILTER CLOGGED | [5 empty] | CLASS 1 LOCATION | NO |  | 517 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 261240 | 261240 | 100 | 100 | 2000 | 2000 | 0 | 0 |  | 3.11 | 263340 | 271803.325491089 | 263340 | 0 | 0 | 0 | 0 | NO |  |  |  | 784 | 250 | 973 | 192.619(C) |  | 1958-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LOSS OF POWER DUE TO HURRICANE ZETA ESD'D THE COMPRESSOR STATION, CONTROLLERS HAD NO PART IN THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | OTHER | ACTUATOR FILTER CLOGGED CAUSING THE ACTUATOR NOT TO ACTIVATE WHICH DID NOT CLOSE THE VALVE. | [5 empty] | YES | [173 empty] | KATHIE HARRYMAN |  | kathie.harryman@sbcglobal.net | 7139897085 |  |  |  |  | TODD NARDOZZI |  | 7139897126 | todd.nardozzi@energytransfer.com | 10/28/20, 22:00 CST - COMPRESSOR STATION 11 LOST POWER DUE TO HURRICANE ZETA CAUSING THE STATION TO ESD WHEN A SIDE VALVE DID NOT SHUT. 10/28/20, 23:59 CST - THE PIPELINE TECHNICIAN MANUALLY OPERATED THE VALVE WITH HAND PUMP CLOSING THE VALVE. UPON INVESTIGATION THE PIPELINE TECHNICIAN CHECKED THE POWER GAS FILTER AND FOUND IT TO BE CLOGGED WITH GREASE NOT ALLOWING GAS TO OPERATE THE VALVE. ONCE THE GREASE WAS DISCOVERED IN THE FILTER THE TECHNICIAN CHANGED THE FILTER, TOOK ALL TUBING OFF CLEANING IT OUT. ALSO CLEANED ALL THE GREASE OUT OF THE POWER GAS LINE BACK TO THE 2" PLUG VALVE THEN RESTARTED UNITS AND FOUND THAT EVERYTHING WAS BACK TO NORMAL.
2021-02-26 10:37 | YES | YES | GT (Gas Transmission) | 20200125 | 34563 | 2020-11-24 08:44 | ORIGINAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2020-10-28 13:35 | 2020 | CENTRAL | NO | 30.6737 | -89.9991 | 1290892 | 2020-10-28 14:47 | 1290953 | NATURAL GAS |  | 598 | 0 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | PIPELINE WAS NEVER SHUT DOWN. ONLY TAP VALVE TO CUSTOMER'S METER |  |  |  | YES | OPERATOR | 2020-10-28 13:41 | YES | 2020-10-28 13:15 | ALLOWED TO BURN OUT |  | 598 | NO | VALVE CLOSURE |  | 2020-10-28 14:33 | OPERATIONAL CONTROL | DOWNSTREAM VALVE WAS BROKEN OFF. |  | 0 | 2020-10-28 13:15 | 2020-10-28 13:41 | ONSHORE | LA | 70427 | Not Within a Municipality | WASHINGTON | MILEPOST | 1.969 | INDEX 301-4-2-14 | FRANKLINTON 4" LINE | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | YES |  |  |  |  | YES | UNCASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | METER | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | VEHICLE ACCIDENT CAUSED TRUCK TO LEAVE ROAD AND STRIKE 1" RISER BREAKING RISER BELOW GROUND. | CLASS 2 LOCATION | NO |  | 90 |  | NO | NO | NO | VEHICLE ACCIDENT THAT RESULTED IN A DEATH DUE TO ACCIDENT IMPACT AND NOT FROM FIRE FROM PIPELINE THAT WAS ALSO IMPACTED. | 0 | 0 | 0 | 0 | 1256 | 1256 | 5200 | 5200 | 500 | 500 | 0 | 0 |  | 2.1 | 6956 | 3918.60263591757 | 6956 | 0 | 0 | 1 | 0 | NO |  |  |  | 374 | 1000 | 715 | 192.619(A)(2) |  | 2019-05-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL |  | 55 | NO | [5 empty] | YES | NO PIG TRAPS | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [9 empty] | UNKNOWN | [5 empty] | UNKNOWN |  | YES | LARGE TRUCK | ROADWAY | 22 | YES |  |  | YES | [235 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 2709035764 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 2703146547 | tina.baker@bwpipelines.com | ON OCTOBER 28, 2020 AT APPROXIMATELY 13:15, GULF SOUTH'S GAS CONTROL RECEIVED A CALL REPORTING A WRECK ON HIGHWAY 16 IN ISABEL, LOUISIANA THAT INVOLVED A PIPELINE AND FIRE. GAS CONTROL DISPATCHED LOCAL OPERATIONS PERSONNEL AND, AFTER NOTICING A SLIGHT PRESSURE DROP FOLLOWED BY AN INCREASED FLOW AT MANDEVILLE JUNCTION, LOWERED THE PRESSURE ON THE NEAREST REGULATOR. AT APPROXIMATELY 13:41 GULF SOUTH PERSONNEL WERE ONSITE. IT WAS NOT IMMEDIATELY CLEAR WHETHER GULF SOUTH ASSETS WERE IMPACTED BECAUSE BOTH GULF SOUTH AND CENTERPOINT HAVE FACILITIES IN THE IMMEDIATE AREA; THE AREA MANAGER COORDINATED WITH CENTERPOINT PERSONNEL TO IDENTIFY WHICH ASSETS WERE INVOLVED. IN THIS AREA, GULF SOUTH'S INDEX 301-4-2-14 RUNS PARALLEL TO HIGHWAY 16. A 1-INCH LINE FROM INDEX 301-4-2-14 CROSSES HIGHWAY 16 AND FEEDS A CENTERPOINT METER. AT 14:00, THE AREA MANAGER REPORTED THAT THE ACCIDENT INVOLVED A FATALITY AND THAT THEY WERE DIGGING DOWN TO THE VALVE TO SHUT OFF GAS FLOW. AT 14:33 GULF SOUTH TAP WAS SHUT OFF AND IT WAS CONFIRMED THAT THE LEAK WAS ON A GULF SOUTH 1" RISER. HIGHWAY 16 WAS BLOCKED OFF, AND AT APPROXIMATELY 14:35 THE FIRE WAS OUT. AT 14:47 NRC NOTIFICATION WAS MADE. OPERATIONS PERSONNEL REPORTED THAT AN 18-WHEELER LOG TRUCK WAS SITTING ON TOP OF THE RISER AND HAD BEEN BURNED. THE DRIVER OF THE 18-WHEELER LOG TRUCK DID NOT HAVE SIGNIFICANT INJURIES. THE FATALITY WAS THE DRIVER OF THE SECOND VEHICLE WHICH WAS CAUSED BY VEHICULAR IMPACT AND NOT THE RESULT OF THE GAS RELEASE OR FIRE. GULF SOUTH COMPLETED REPAIRS TO ITS FACILITIES ON OCTOBER 29, 2020. THE RESPONSES PROVIDED FOR QUESTIONS D3, E1, E1A, E2, E2A, E2B, AND E2C PERTAIN TO THE 4-INCH PARENT PIPE (INDEX 301-2-4-14) BECAUSE THE INCIDENT OCCURRED ON A FARM TAP. THE RESPONSE TO QUESTION D7A IS ZERO BUT THE ACTUAL NUMBER IS UNKNOWN. THIS INCIDENT INCLUDED VEHICLE DAMAGE AND A DEATH BUT THOSE WERE NOT GULF SOUTH'S RESPONSIBILITY AND GULF SOUTH HAS NO KNOWLEDGE OF THE COST ASSOCIATED WITH THESE DAMAGES.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200126 | 34567 | 2020-11-24 10:57 | ORIGINAL | 18152 | SEA ROBIN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-10-29 14:10 | 2020 | CENTRAL | YES | 28.9883 | -92.2975 | 1290991 | 2020-10-29 15:10 | 1291102 | OTHER GAS | CONDENSTATE | 0 | 0 | 0.1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-10-29 16:10 |  | YES | NO |  |  | NO | [11 empty] | 0 | 2020-10-29 14:10 | 2020-10-29 14:10 | OFFSHORE | [6 empty] | SEA ROBIN PIPELINE | V-149A | [20 empty] | 80 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | VERMILION | 149 | PLATFORM | INTERSTATE | OFFSHORE PLATFORM, INCLUDING PLATFORM-MOUNTED EQUIPMENT AND PIPING | VALVE | [31 empty] | MAINLINE | BALL |  | CAMERON |  |  |  | 1977 | 1977 | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 860 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 585000 | 585000 | 2000 | 2000 | 0 | 0 |  | 2.95 | 587000 | 269448.4890708 | 587000 | 0 | 0 | 0 | 0 | NO |  |  |  | 710 | 0 | 1200 | 192.619(A)(1) |  | 2012-07-18 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NOT REQUIRED, POWER OUTAGE DUE TO HURRICANE ZETA. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | SEAL (NOT COMPRESSOR SEAL) OR PACKING | [6 empty] | YES | [173 empty] | ANDREW MARTINEZ |  | andrew.martinez@energytransfer.com | 7139894339 |  |  |  |  | TODD NARDOZZI |  | 713-989-7126 | todd.nardozzi@energytransfer.com | 10/29/20, VERMILLION 149 LOST POWER DUE TO HURRICANE ZETA. UPON INVESTIGATION TECHNICIAN DISCOVERED VALVE SEAL FAILED ALLOWING CONDENSATE TO FILL PLATFORM PIPING. 10/29/20, 15:10 CST INITIAL NOTIFICATION MADE TO THE NRC # 1290991. 10/31/20, 10:25 CST 48 HOUR NOTIFICATION MADE TO THE NRC # 1291102. 11/17/20 - CURRENTLY PUMPING LIQUID OFF THE PLATFORM, BLOWING DOWN PIPELINE, AND INCREASING SIZE OF GENERATOR TO TRANSITION TO A 24HR OPERATION. 11/24/20 - STILL PUMPING LIQUIDS OFF THE PLATFORM, NO SHEEN PRESENT. PIPELINE REPAIRS ARE STILL NEEDED AND WILL BE PERFORMED WEATHER PERMITTING.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20200127 | 34569 | 2020-11-24 11:38 | ORIGINAL | 18152 | SEA ROBIN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-10-29 15:42 | 2020 | CENTRAL | YES | 28.1219 | -92.9758 | 1290995 | 2020-10-29 15:42 | 1291104 | NATURAL GAS |  | 3563 | 0 | 0.1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | PIPELINE WAS PREVIOUSLY SHUTDOWN DUE TO HURRICANE ZETA. |  |  |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-10-26 12:00 | VALVE CLOSURE |  | 2020-10-29 14:00 | 0 | 2020-10-29 15:42 | 2020-10-29 14:42 | OFFSHORE | [6 empty] | SEA ROBIN EC 335 | 4093 | [20 empty] | 240 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | EAST CAMERON | 335 | PORTION OF RISER OUTSIDE OF SPLASH ZONE, INCLUDING RISER BEND | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 20 | NO | 0.5 | 60000 | API5L | OTHER | UNKNOWN | UNKNOWN | PAINT |  | YES | [26 empty] | 1977 | 1977 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 488 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 10511 | 10511 | 100000 | 100000 | 2000 | 2000 | 0 | 0 |  | 2.95 | 112511 | 57717.9224280649 | 112511 | 0 | 0 | 0 | 0 | NO |  |  |  | 704 | 0 | 984 | 192.619(A)(1) |  | 2012-07-18 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 237600 | NO | YES |  | YES |  |  |  |  | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NOT REQUIRED, POWER OUTAGE DUE TO HURRICANE ZETA. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  |  | YES | [7 empty] | YES |  |  |  | NO | [11 empty] | YES | NO | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | ANDREW MARTINEZ |  | andrew.martinez@energytransfer.com | 7139894339 |  |  |  |  | TODD NARDOZZI |  | 7139897126 | todd.nardozzi@energytransfer.com | 10/29/20, 14:42 CST PRODUCER NOTIFIED OPERATIONS PERSONNEL OF PINHOLE LEAK ON THE RISER CLAMP AREA OF THE PIPELINE DUE TO CORROSION. 10/29/20, 15:42 CST INITIAL NOTIFICATION MADE TO THE NRC # 1290995. ON 10/31/20, PIPELINE WAS ISOLATED AND PRODUCER IS MAKING ARRANGEMENTS TO BLOWDOWN THEIR LATERAL TO BLEED THE PRESSURE OFF THE LEAK SITE. CURRENTLY WAITING ON PRODUCER TO BLOWDOWN THEIR EQUIPMENT ON PLATFORM IN ORDER TO MAKE NECESSARY REPAIRS. 10/31/20, 10:40 CST 48 HOUR NOTIFICATION MADE TO THE NRC # 1291104. 11/24/20 - ONCE PRODUCER BLOWS DOWN THEIR LINE, WE WILL BE WORKING TO INSTALL JUMPER LINE TO BLEED OFF OUR PRESSURE TO THE PRODUCER AND MAKE NECESSARY REPAIRS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200128 | 34826 | 2020-11-24 12:22 | SUPPLEMENTAL FINAL | 31159 | KANSAS GAS SERVICE COMPANY, A DIVISION OF ONE GAS, INC. | 7421 W 129TH | OVERLAND PARK | KS | 66213 | 2020-10-24 10:28 | 2020 | CENTRAL | YES | 38.3622 | -98.678 | 1290636 | 2020-10-25 10:50 | 1290767 | NATURAL GAS |  | 617.4 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-10-24 14:25 | 2020-10-24 22:40 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-10-24 14:25 | VALVE CLOSURE |  | 2020-10-24 14:35 | 0 | 2020-10-24 10:28 | 2020-10-24 13:11 | ONSHORE | KS | 67530 | Not Within a Municipality | BARTON | MILEPOST | 3.7 | P0445 | MP 3.7 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 35 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 4.5 | NO | 0.237 | 24000 | UNKNOWN | OTHER | UNKNOWN | UNKNOWN | COAL TAR |  | YES | [26 empty] | 1953 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 6 | 3 | [7 empty] | CLASS 1 LOCATION | NO |  | 69 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 1828 | 1828 | 0 | 0 | 0 | 0 | 173457 | 173457 | TOTAL EQUIPMENT/LABOR/MISC COSTS OF REPAIR, RESPONSE & RESTORATION | 2.96 | 175285 | 81516.5105845158 | 175285 | 0 | 0 | 901 | 125 | NO |  |  |  | 350 | 184.56 | 459 | 192.619(A)(3) |  | 1970-07-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 39564 | NO | [5 empty] | YES | NO LAUNCHERS OR RECEIVERS | YES |  |  |  |  | YES | NO LAUNCHERS OR RECEIVERS | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE BY THIRD PARTY EXCAVATOR | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES |  |  |  | NO |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | CONTRACTOR | GRADER/SCRAPER | DRAINAGE | YES | 20525737 |  | CONTRACT LOCATOR | NO | YES | YES | 9 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO MAINTAIN THE MARKS | [263 empty] | JUSTIN W CLEMENTS | REGULATORY COMPLIANCE SPECIALIST | justin.clements@onegas.com | 913-599-8980 |  | SCOTT BORNHOLDT | scott.bornholdt@onegas.com | 620-672-1622 | RANDY SPECTOR | DIRECTOR OF ENGINEERING | 913-599-8931 | randalrandy.spector@onegas.com | A 3RD PARTY CONTRACTOR MOVING DIRT WITH A SCRAPER OVER THE COMPANY'S 4" TRANSMISSION LINE CAUSED DAMAGE. EVIDENCE SHOWS THAT THE CONTRACTOR MOVED APPROXIMATELY 36" OF DIRT BEFORE MAKING CONTACT WITH THE TRANSMISSION LINE THAT HAD BEEN PROPERLY LOCATED AND MARKED PRIOR TO THE DAY OF DAMAGE. THE DAMAGE CAUSED THE DOWNSTREAM PRESSURE TO DROP TO 0 PSI. THE COMPANY CLOSED THE UPSTREAM AND DOWNSTREAM VALVES TO ISOLATE THE LINE AND TO ALLOW FOR THE SAFE REPAIR OF THE LINE BY REPLACING APPROXIMATELY 18' OF 4" PIPE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200129 | 34594 | 2020-12-04 16:36 | ORIGINAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2020-11-06 17:30 | 2020 | CENTRAL | NO | 32.4672 | -91.5978 | 1291840 | 2020-11-10 13:50 | 1291982 | NATURAL GAS |  | 5000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-11-06 17:44 | 2020-11-06 23:00 |  | YES | OPERATOR | 2020-11-06 17:30 | NO | [11 empty] | 0 | 2020-11-06 17:30 | 2020-11-06 17:40 | ONSHORE | LA | 71232 | DELHI | RICHLAND | MILEPOST | MP 151.3 | DELHI COMPRESSOR STATION | ANR 501 MAINLINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1956 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | VALVE FAILURE | CLASS 1 LOCATION | NO |  | 787 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 13350 | 13350 | 1000 | 1000 | 0 | 0 | 0 | 0 | NONE | 2.67 | 14350 | 14299.5775679351 | 14350 | 0 | 0 | 0 | 0 | NO |  |  |  | 786 | 2000 | 858 | 192.619(A)(3) |  | 1967-07-26 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER IDENTIFIED THE ISSUE VIA SCADA ALARMS AND INITIATED A CALL-OUT OF FIELD OPERATIONAL PERSONNEL, WHO IDENTIFIED THE INCIDENT AND TOOK CORRECTIVE ACTIONS. GAS CONTROL DOES NOT HAVE THE CAPABILITY TO REMOTELY CLOSE VALVES AND THEREFORE COULD PREVENT THE INCIDENT THROUGH THEIR ACTIONS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [5 empty] | YES | [23 empty] | YES | [163 empty] | ROGER R STREET | COMPLIANCE SPECIALIST | roger_street@tcenergy.com | 6154655123 |  |  |  |  | ERIK HUGHES | SENIOR COMPLIANCE MANAGER USGO AND KEYSTONE | 4024927447 | erik_hughes@tcenergy.com | ON NOVEMBER 6 AT 17:30 CT, ANR PIPELINE'S GAS CONTROL RECEIVED AN EMERGENCY SHUTDOWN (ESD) ALARM AT DELHI COMPRESSOR STATION LOCATED AT 1984 HWY 80 W, DELHI, LA 71232 (32.46707, -91.59751). WHEN THE ALARM WAS DETECTED, A TECHNICIAN WAS DISPATCHED TO THE COMPRESSOR STATION TO INVESTIGATE. UPON ARRIVAL AT THE SITE AT 17:40 CT, THE TECHNICIAN DISCOVERED NATURAL GAS BEING RELEASED THROUGH THE STATION'S BLOWDOWN STACKS. IMMEDIATE ACTION WAS TAKEN BY VERIFYING NO EMERGENCY EXISTED AND CLOSING THE VALVES, WHICH ENDED THE RELEASE AT 17:44 CT. UNINTENTIONAL GAS LOSS WAS CALCULATED TO 5.0 MILLION CUBIC FEET (MMCF). NO PROPERTY DAMAGE OR INJURIES WERE DOCUMENTED, AND NO EVACUATIONS WERE REQUIRED. FOLLOWING THE RELEASE, INITIAL SITE INSPECTIONS WERE COMPLETED TO LOOK FOR EVIDENCE OF FIRE OR OTHER DAMAGE. NO DAMAGE WAS OBSERVED, AND THE STATION WAS PLACED BACK INTO PARTIAL SERVICE AT 23:00 CT ON NOVEMBER 6. WHEN THE SYSTEM ACTIVATED, STATION ISOLATION VALVE 501-13-25 FAILED TO FULLY CLOSE RESULTING IN THE UNINTENTIONAL RELEASE OF GAS. FOLLOWING THE INCIDENT, VALVE 501-13-25 WAS REMOVED FROM SERVICE FOR INSPECTION. A POPPET BLOCK VALVE, ATTACHED TO THE VALVE OPERATOR WAS REMOVED, DISASSEMBLED, AND INSPECTED FOR POTENTIAL DAMAGE. DAMAGED AND WORN SEALS ON THE POPPET VALVE WERE IDENTIFIED WHICH PREVENTED THE VALVE FROM FULLY CLOSING WHEN ACTUATED. THE POPPET BLOCK VALVES ASSOCIATED WITH VALVE 501-13-25 WERE CLEANED AND THE SEALS WERE REPLACED. AFTER REPAIRING THE VALVES, AN ESD SYSTEM INSPECTION WAS COMPLETED ACCORDING TO PROCEDURES ON NOVEMBER 17, 2020. THE TEST WAS INITIATED BY TRIGGERING THE FLAME DETECTORS AND THEN MONITORING ALL EMERGENCY SYSTEM VALVES FOR OPERATIONS AND TIMING. DURING THE TEST, ALL SYSTEM VALVES PROPERLY OPERATED AND FULLY CLOSED.
2021-02-26 10:37 | NO | NO | UNGS (Underground Natural Gas Storage) | 20200130 | 34606 | 2020-12-10 14:34 | ORIGINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2020-11-11 21:49 | 2020 | EASTERN | YES | 40.1409 | -80.4463 | 1291972 | 2020-11-11 22:50 | 1292099 | NATURAL GAS |  | 7687.2 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-11-11 21:49 |  | YES | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-11-11 21:45 | NO | [11 empty] | 0 | 2020-11-11 21:00 | 2020-11-11 21:49 | ONSHORE | PA | 15323 | CLAYSVILLE | WASHINGTON | NOT APPLICABLE |  | 9190 / DONEGAL STORAGE FIELD WELL 3951 | 9190 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [22 empty] | INTERSTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | PIPE | PIPE BODY | 4 | NO | 0.237 | 35000 | UNKNOWN | SEAMLESS |  | UNKNOWN | NONE |  | NO | [26 empty] | 1948 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 4.5 | 4.5 |  | CLASS 1 LOCATION | NO |  | 99 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 17296 | 17296 | 1 | 1 | 1 | 1 | 0 | 0 | ALL COSTS ARE TO BE DETERMINED | 2.25 | 17298 | 17932.4666092041 | 17298 | 0 | 0 | 0 | 0 | NO |  |  |  | 1117 | 574350 | 1280 | 192.619(A)(2) |  | 1969-12-15 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | [8 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [146 empty] | BEN HUNLEY | COMPLIANCE SPECIALIST | ben_hunley@tcenergy.com | 304-539-9311 |  |  |  |  | PAUL SHAFFER | MANAGER USRC EAST | 304-550-4866 | paul_shaffer@tcenergy.com | ON THE EVENING OF NOVEMBER 11TH, 2020, COLUMBIA GAS TRANSMISSION, LLC (COMPANY), A TC ENERGY ENTITY, RESPONDED TO AN EVENT AT DONEGAL STORAGE FIELD WHICH IS OWNED AND OPERATED BY THE COMPANY. AT 9:33 PM, MONITORING CENTER PERSONNEL RECEIVED A CALL FROM GAS CONTROL REGARDING A PRESSURE DROP. THE PRESSURE HAD DROPPED FROM 1,190 TO 1,156 PSIG, FOLLOWED BY A SUBSEQUENT DROP TO 1,035 PSIG AFTER SHUTTING IN PRESSURE REGULATION. AT 9:35 PM, FIELD PERSONNEL WERE CONTACTED BY A NEAR-BY PROPERTY OWNER REPORTING THE SOUND OF A GAS LINE LEAK; SUBSEQUENTLY COMPANY OPERATIONS TEAM LEAD AND OTHER COMPANY PERSONNEL WERE NOTIFIED TO RESPOND TO THE LOCATION. FIRST RESPONDER ARRIVED ON SCENE AT 9:45 PM AND OBSERVED GAS BLOWING; THE LOCAL FIRE DEPARTMENT CLOSED CUNNINGHAM ROAD AT THIS TIME. AT 9:54 PM A COMPANY STORAGE FIELD TECHNICIAN CONFIRMED THAT THE REPORTED LEAK HAD BEEN ISOLATED BY SHUTTING OPERATING CRITICAL VALVE. THE NATIONAL RESPONSE CENTER (NRC) AND PHMSA AID WERE CONTACTED WITHIN 1 HOUR OF CONFIRMED DISCOVERY AT 10:50PM. NATIONAL RESPONSE CENTER ONE HOUR (1291972) AND 48-HR (1292099) REPORTS WERE COMPLETED ON NOVEMBER 11TH AND NOVEMBER 13TH RESPECTIVELY. THE FAILED STORAGE LINE (9190) WAS SECURED AND SENT TO A METALLURGICAL FAILURE ANALYSIS LABORATORY TO EVALUATE AND DETERMINE THE PROBABLE CAUSE BEHIND THIS PIPELINE FAILURE. THE FAILURE ANALYSIS REPORT HAS NOT BEEN COMPLETED YET. NOTE: ALL TIMES WERE RECORDED IN EASTERN STANDARD TIME
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200131 | 34793 | 2020-12-18 10:25 | SUPPLEMENTAL FINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2020-12-09 10:53 | 2020 | MOUNTAIN | YES | 39.4805 | -107.2045 | 1293896 | 2020-12-09 10:53 | 1294036 | NATURAL GAS |  | 37162 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | IDLE | [5 empty] | NO |  |  | NO | [11 empty] | 0 | 2020-11-23 00:36 | 2020-11-23 11:35 | ONSHORE | CO | 81601 | Not Within a Municipality | GARFIELD | SURVEY STATION NO. | SPRING VALLEY | SPRING VALLEY COMPRESSOR STATION | SPRING VALLEY COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2014 | 2014 | CARBON STEEL |  | OTHER | [8 empty] | PURGING VALVE LEFT OUT OF POSITION | CLASS 1 LOCATION | NO |  | 300 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 80567 | 80567 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2.168 | 80567 | 83527.467191601 | 80567 | 0 | 0 | 0 | 0 | NO |  |  |  | 833 | 0 | 1200 | 192.619(A)(3) |  | 2014-08-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES |  | YES | [6 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [204 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE |  |  |  | YES |  |  |  |  | NORMAL OPERATING CONDITIONS | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | STONEY DAVIDSON | COMPLIANCE COORDINATOR | stoney.davidson@blackhillsenergy.com | 719 359-0586 |  | THOMAS WARNES | thomas.warnes@blackhillsenergy.com | 970 406-1467 | STONEY DAVIDSON | COMPLIANCE COORDINATOR | 719 359-0586 | stoney.davidson@blackhillsenergy.com | ON NOVEMBER 22 THE SPRING VALLEY COMPRESSOR STATION WAS PURGED, PACKED AND MADE READY TO BE PUT ONLINE. THE STATION WAS ON STANDBY WITH NO COMPRESSION RUNNING. ON NOVEMBER 23, 2020 0036 ' THREE HIGH PRIORITY ALARMS WERE RECEIVED BY CONTROLLER 0059 ' CONTROLLER ACKNOWLEDGED ALL THREE ALARMS DID NOT NOTIFY FIELD OPERATIONS. 11:35AM- FIELD OPERATIONS PERSONNEL VISITED THE SITE TO CLEAN UP FROM WEEKEND WORK AND DISCOVERED BLOWING GAS OUT OF THE BLOW-DOWN SILENCER. SECURED THE SITE AND EVALUATED THE SITUATION ON STATION HMI. 11:39AM- RESET ESD SYSTEM SHUTTING IN THE VENTING GAS. IT WAS FOUND THAT A MALFUNCTION OF A FIRE EYE DETECTION DEVICE CAUSED AN EMERGENCY SHUTDOWN (ESD). THERE WERE STATION PURGE LINES LEFT IN THE OPEN POSITION AFTER CHARGING THE STATION WHICH CAUSED A BYPASS OF ESD BLOCK VALVES RESULTING IN THE BLOWING GAS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200132 | 34695 | 2020-12-22 15:40 | SUPPLEMENTAL FINAL | 38987 | KINETICA ENERGY EXPRESS LLC | 1001 MCKINNEY STREET, SUITE 900 | HOUSTON | TX | 77002 | 2020-12-10 10:10 | 2020 | CENTRAL | YES | 28.5798 | -91.8712 | 1293926 | 2020-12-10 17:58 | 1284035 | NATURAL GAS |  | 636 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-12-11 06:00 |  | YES | YES | OPERATOR | 2020-12-10 17:58 | NO | [5 empty] | VALVE CLOSURE |  | 2020-12-10 12:30 | VALVE CLOSURE |  | 2020-12-11 06:00 | 0 | 2020-12-10 10:10 | 2020-12-10 12:07 | OFFSHORE | [28 empty] | 140 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | SOUTH MARSH | 78 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 | NO | 0.375 | 33000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | OTHER | CONCRETE | NO | [26 empty] | 1991 | 1989 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  |  | NOT FLAMMABLE | NO | NO |  |  | 0 | 0 | 0 | 0 | 1272 | 1272 | 250000 | 250000 | 40000 | 40000 | 0 | 0 |  | 2 | 291272 | 134436.392338966 | 291272 | 0 | 0 | 0 | 0 | NO |  |  |  | 760 | 0 | 1250 | 192.619(A)(1) |  | 1991-05-24 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 8610 | NO | [5 empty] | YES | PIG LAUNCHER AND SUBSEA NO RECEIVER | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | NO |  |  |  |  | OTHER | OTHER OPERATOR NOTIFICATION |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | BECAUSE MAOP WAS NOT EXCEEDED AND GAS CONTROL WAS NOT THE CAUSE. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  |  | YES | [5 empty] | YES | HISTORY OF SIMILAR PIPES |  |  |  |  | YES | 6 O'CLOCK POSITION | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KURT CHERAMIE | SENIOR VICE PRESIDENT | kurt.cheramie@kineticallc.com | 9852092283 |  |  |  |  | KURT CHERAMIE | SENIOR VICE PRESIDENT | 9852092283 | kurt.cheramie@kineticallc.com | KINETICA WAS NOTIFIED OF POTENTIAL LEAK IN SM ISLAND AREA. KINETICA PERFORMED FLY OVER AND PLOTTED COORDINATES. KINETICA WENT TO UPSTREAM VALVE AT PRODUCER PLATFORM AND CLOSED AND LOCKED THE VALVE TO ISOLATE. OBTAINED A DSV AND HEADED TO LOCATION. DOVE ON LEAK TO CONFIRM OWNERSHIP. ONCE OWNERSHIP WAS CONFIRMED TO BE KINETICA'S 16" PIPELINE, DSV RELOCATED TO SUBSEA TIE IN WITH KINETICA'S MAINLINE. DSV THEN CLOSED DOWNSTREAM 16" VALVE TO TOTALLY ISOLATED 16" LINE. PRESSURE WAS BLED DOWN TO BOTTOM PRESSURE. LINE HAS BEEN TOTALLY ISOLATED, BLED DOWN, AND WILL BE ABANDONED IN 2021. THE LEAK WAS FROM UNDER CONCRETE COATING. THE LEAK WAS IN THE 6 O'CLOCK POSITION.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200133 | 34676 | 2020-12-28 19:08 | SUPPLEMENTAL FINAL | 31565 | GULFSTREAM MANAGEMENT & OPERATING SERVICES,LLC | 1905 INTERMODAL CIRCLE, SUITE 310 | PALMETTO | FL | 34221 | 2020-11-29 02:15 | 2020 | EASTERN | NO | 27.7483 | -81.85 | 1293196 | 2020-11-29 16:15 | 1293256 | NATURAL GAS |  | 4200 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-11-29 12:00 | 2020-12-10 16:15 |  | NO |  |  | NO | [11 empty] | 0 | 2020-11-29 01:00 | 2020-11-29 02:15 | ONSHORE | FL | 33841 | FORT MEADE | POLK | SURVEY STATION NO. | 6+65 | STATION 415 | TIGER BAY M&R | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2020 | 2020 | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE ACTUATION | CLASS 1 LOCATION | NO |  | 338 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 10416 | 10416 | 600 | 600 | 0 | 0 | 0 | 0 |  | 2.48 | 11016 | 11074.1559895799 | 11016 | 0 | 0 | 0 | 0 | NO |  |  |  | 465 | 30 | 1480 | 192.619(A)(2) |  | 2002-03-26 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | NOTIFICATION BY CUSTOMER |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS DUE TO VALVE NOT RESETTING (EQUIPMENT FAILURE). | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES |  |  | YES | [24 empty] | YES | YES | METAL PIN WAS FOUND WEDGED IN THE RELIEF | [161 empty] | STEPHANIE ROSS | PIPELINE SAFETY ENGINEER | stephanie.ross@williams.com | 713-215-4163 |  |  |  |  | TYSON GREEN | PIPELINE SAFETY MANAGER | 713-215-2535 | tyson.green@williams.com | ON 11/29/2020 AT THE GULFSTREAM TIGER BAY M&R STATION, THERE WAS A COMBINED RELEASE OF 4.2 MMCF OF GAS (2.1 MMCF FROM WILLIAMS AND 2.1 MMCF FROM THE CUSTOMER). WILLIAMS DETERMINED THE RELEASE WAS DUE TO THE FAILURE OF A MOONEY FLEXIBLE ELEMENT REGULATOR COUPLED WITH A RELIEF VALVE THAT FAILED TO RESET ONCE THE PRESSURE DROPPED BELOW THE SET POINT. THE CUSTOMER CAME OFFLINE, AT WHICH TIME, THE MOONEY REGULATOR FAILED TO LOCKUP DUE TO INTERNAL DAMAGE TO THE FLEXIBLE ELEMENT (WEAR AND TEAR: SEEING FLEXIBLE ELEMENT LIFE HAS SHORTENED FROM 6 MONTHS TO 2 MONTHS). THE RELIEF VALVE BEGAN TO VENT BUT DID NOT RESET ONCE THE PRESSURE DECREASED BELOW THE SET POINT. THE RELIEF VALVE CONTINUED TO VENT UNTIL THE RESPONDING TECHNICIAN ARRIVED AND SECURED THE FACILITY. WHEN THE RELIEF WAS TORE DOWN TO BE REBUILT AND PUT BACK IN SERVICE, A METAL PIN WAS FOUND TO BE WEDGED IN THE RELIEF AND WAS NOT ALLOWING IT TO RESET. THE VALVE MANUFACTURER WAS CONTACTED TO ASK IF IT WAS AN ALIGNMENT PIN LEFT IN THERE BY MISTAKE BUT THEY HAVE INDICATED THEY DO NOT USE ANYTHING LIKE THAT DURING MANUFACTURING. IT IS UNKNOWN AS TO WHERE THE PIN MAY HAVE COME FROM.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20200134 | 34660 | 2020-12-28 21:31 | ORIGINAL | 4900 | KINDER MORGAN TEJAS PIPELINE | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2020-12-04 17:02 | 2020 | CENTRAL | NO | 27.8171 | -97.4528 | 1293563 | 2020-12-04 17:02 | 1293611 | NATURAL GAS |  | 104 | 642 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-12-04 18:52 |  | YES | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-12-04 18:52 | VALVE CLOSURE |  | 2020-12-04 18:52 | 0 | 2020-12-04 16:40 | 2020-12-04 18:00 | ONSHORE | TX | 78407 | CORPUS CHRISTI | NUECES | SURVEY STATION NO. | 21853.85 | TRANSCO TO AVERY | GOLDSTON TO AVERY 12 INCH | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | UNDERGROUND PIPELINE CASING. | 46 | NO | YES |  |  |  |  | YES | CASED | [16 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12.75 | NO | 0.25 | 52000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | OTHER | FBE | UNKNOWN | [26 empty] | 1988 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 252 |  | NO | NO |  |  | 0 | 0 | 1733 | 1733 | 281 | 281 | 74846 | 74846 | 500 | 500 | 0 | 0 | NA | 2.7 | 77360 | 35672.620329996 | 77360 | 0 | 0 | 0 | 0 | NO |  |  |  | 669 | 40000 | 819 | 192.619(A)(2) |  | 1988-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 16913 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLERS ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  |  |  |  | YES |  |  |  |  | YES | SUB-CAUSE IS TENTATIVE AT THIS TIME. | [19 empty] | YES | THE IMMEDIATE AND ROOT CAUSE IS PENDING AT THIS TIME. | UNKNOWN | [54 empty] | YES | YES |  |  | YES |  |  | YES | 2017 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [27 empty] | 2017 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | [13 empty] | IMU | 2017 | FREE SWIMMING |  |  |  | NO |  |  | NO | [13 empty] | NO | [63 empty] | STEPHEN R. DINES | ENGINEER | stephen_dines@kindermorgan.com | (719) 351-3199 |  | TONY PALACIOS | tony_palacios@kindermorgan.com | (361) 438-3411 | JAIME HERNANDEZ | DIRECTOR-ENGINEERING | 713 369-9443 | jaime_hernandez@kindermorgan.com | ON DECEMBER 4, 2020 AT APPROXIMATELY 15:00 HRS. LOCAL TIME, TEJAS PIPELINE RECEIVED A CALL FROM A LOCAL GAS OPERATING COMPANY OF NATURAL GAS VAPORS OBSERVED FROM A PIPELINE CASING VENT LOCATED NEAR AVERY POINT IN NUECES COUNTY, TEXAS. AT 15:20 HRS. LOCAL TIME, A TEJAS FIELD TECHNICIAN INSPECTED THE LOCATION BUT COULD NOT LOCATE THE LEAK. THE LOCAL GAS OPERATING COMPANY, ORIGINALLY REPORTING THE LEAK, REVISED THE LOCATION DESCRIPTION TO NAVIGATION BLVD IN NUECES COUNTY, TEXAS. UPON ARRIVAL AT NAVIGATION BLVD., THE TEJAS FIELD TECHNICIAN CONFIRMED THE LEAK BELONGED TO TEJAS AT 16:20 HRS. LOCAL TIME BY OBSERVING A LOW-LEVEL EMISSION OF VAPORS FROM THE PIPELINE CASING VENT. THE TEJAS FIELD TECHNICIAN AND MANAGEMENT COMPLETED A ERL TELEPHONE CALL AND DECIDED TO REPORT THE EVENT AS AN INCIDENT SINCE IT WAS DETERMINED THAT THE COST OF REPAIRS WOULD EXCEED $50,000. AS SUCH, TEJAS COMPLETED THE REPORT TO THE NRC AT 17:02 HRS. THE SAME DAY. TEJAS COMPLETED A 48-HOUR NRC UPDATE THE FOLLOWING DAY CITING NO SIGNIFICANT CHANGES. THE PIPELINE HAS BEEN ISOLATED AND THE IMMEDIATE AND ROOT CAUSE OF THE EVENT IS PENDING A COMPLETE INVESTIGATION. THIS REPORT WILL UNDERGO AN UPDATE WITH THE FINDINGS FROM THAT INVESTIGATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20200135 | 34667 | 2020-12-30 20:34 | ORIGINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2020-12-03 13:20 | 2020 | EASTERN | YES | 39.6315 | -82.5549 | 1293457 | 2020-12-03 14:54 | 1293539 | NATURAL GAS |  | 200 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-12-03 15:00 |  | YES | NO |  |  | NO | [11 empty] | 0 | 2020-12-03 08:30 | 2020-12-03 08:30 | ONSHORE | OH | 43155 | SUGAR GROVE | FAIRFIELD | NOT APPLICABLE |  | SR-696 | SR-696 CRAWFORD COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 30 | NO | 0.328 | 65000 | X65 | DSAW |  | UNKNOWN | COAL TAR |  | YES | [26 empty] | 1977 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 2 LOCATION | NO |  | 698 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 410 | 410 | 150000 | 150000 | 0 | 0 | 30000 | 30000 | OTHER COSTS INCLUDE METALLURGICAL ANALYSIS | 2.05 | 180410 | 83049.8152466855 | 180410 | 0 | 0 | 0 | 0 | NO |  |  |  | 460 | 155000 | 850 | 192.619(A)(1) |  | 1977-09-15 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE UNINTENDED RELEASE OF GAS WAS DUE TO A NUISANCE LEAK. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [146 empty] | KAMRAN ROSTAMI ASRABADI | COMPLIANCE SPECIALIST | kamran_rostami@tcenergy.com | (304)357-2351 |  | KAMRAN ROSTAMI ASRABADI | kamran_rostami@tcenergy.com | (304)357-2351 | PAUL SHAFFER | US REGULATORY COMPLIANCE MANAGER EAST | (304)550-4866 | paul_shaffer@tcenergy.com | ON DECEMBER 3, 2020, AT APPROXIMATELY 08:30 THE PRESENCE OF NATURAL GAS WAS IDENTIFIED BY A COMPANY PERSONNEL PASSING BY ONE OF THE COMPRESSOR BUILDINGS IN CRAWFORD COMPRESSOR STATION (CS). CRAWFORD CS IS A TRANSMISSION FACILITY LOCATED IN FAIRFIELD COUNTY, STATE OF OHIO THAT IS OPERATED AND MAINTAINED BY COLUMBIA GAS TRANSMISSION, LLC (COMPANY). COMPANY PERSONNEL CONDUCTED LEAKAGE SURVEY AT THE DEPICTED LEAK LOCATION AND ITS SURROUNDING TO INVESTIGATE THE SOURCE OF THE POTENTIAL NATURAL GAS LEAK. FURTHERMORE, THROUGHOUT A THOROUGH INVESTIGATION, IT WAS IDENTIFIED THAT THE POTENTIAL RELEASE WAS ALONG LINE SR-696. AT APPROX. 14:25 LINE SR-696 HAD BEEN ISOLATED ON BOTH ENDS OF THE AFFECTED SECTION AND BLOWDOWN COMMENCED FROM 460 PSIG LINE OPERATING PRESSURE. AT APPROX. 15:00 THE LINE AFFECTED SEGMENT OF LINE SR-696 WAS FULLY BLOWN DOWN TO ATMOSPHERIC PRESSURE. THE INITIAL NATIONAL RESPONSE CENTER (NRC) REPORT NO.1293457 AND THE NRC 48-HOUR REPORT NO.1293539 HAVE BEEN CALLED-IN ON DECEMBER 3RD AND DECEMBER 5TH RESPECTIVELY. THE FAILED SECTION OF THE PIPELINE WAS SENT TO A METALLURGICAL LABORATORY TO DETERMINE THE PROBABLE CAUSE BEHIND THE FAILURE OF THE PIPELINE. NOTE: ALL TIMES WERE RECORDED IN EASTERN STANDARD TIME
2021-02-26 10:37 | NO | NO | GG (Gas Gathering) | 20210001 | 34672 | 2021-01-04 11:30 | ORIGINAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2020-12-09 14:08 | 2020 | CENTRAL | NO | 29.1617 | -91.1041 | 1293924 | 2020-12-09 14:30 | 1294002 | NATURAL GAS |  | 0.1 | 20 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-12-09 14:10 |  | YES | YES | OPERATOR | 2020-12-09 14:15 | NO | [5 empty] | VALVE CLOSURE |  | 2020-12-09 14:10 | VALVE CLOSURE |  | 2020-12-09 14:10 | 0 | 2020-12-09 14:08 | 2020-12-09 14:08 | ONSHORE | LA | 70726 | Not Within a Municipality | TERREBONE | MILEPOST | 131 | MOSQUITO BAY | 20" CROSSOVER PIPE | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | OTHER | UNDERWATER | 72 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 | NO | 0.5 | 52000 | API 5L | SEAMLESS |  | NATIONAL TUBE | COAL TAR |  | YES | [26 empty] | 1962 | 1962 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 373 |  | NO | NO |  |  | 0 | 0 | 50 | 50 | 0 | 0 | 50001 | 50001 | 0 | 0 | 10000 | 10000 | DIVING TEAM | 2.48 | 60051 | 27564.993555691 | 60051 | 0 | 0 | 0 | 0 | NO |  |  |  | 730 | 20 | 1168 | 192.619(A)(2) |  | 1962-09-15 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 185 | NO | [5 empty] | YES | CROSSOVER PIPE BETWEEN ONSHORE PLATFORMS. | YES |  |  |  |  | YES | NO PIG TRAPS | TYPE B GATHERING | YES | YES | YES | NO | NO | AIR PATROL |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PINHOLE LEAK FOUND BY AERIAL PATROL. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  |  | YES | [5 empty] | YES | PAST EXPERIENCE OF SIMILAR LEAKS OF AN AGING SYSTEM. | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | EDGAR RODRIGUEZ | REGULATORY COMPLIANCE SPECIALIST SR. | edgar.x.rodriguez@williams.com | 713-215-2846 |  | ERNEST DAIGLE | ernest.daiglejr@williams.com | (985) 446-7142 | TYSON GREEN | MANAGER PIPELINE SAFETY | 713-215-2535 | tyson.green@williams.com | APPROXIMATELY 2:08PM ON APPROACH TO MOSQUITO BAY, TECHNICIANS NOTICED BUBBLES BETWEEN A AND B PLATFORMS. AT THAT TIME THEY REALIZED THE LEAK WAS CLOSE TO THE PROXIMITY OF OUR 20" CROSSOVER PIPE. TECHNICIANS CLOSED AND ISOLATED THE LINE AND BUBBLES STOPPED. LINE STOPPED LEAKING AT 2:40PM AFTER CLOSING AND ISOLATING THE LINE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20210002 | 34675 | 2021-01-04 18:14 | ORIGINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2020-12-05 07:20 | 2020 | EASTERN | YES | 42.7187 | -82.7159 | 1293954 | 2020-12-10 08:40 | 1294029 | NATURAL GAS |  | 15.5 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-12-05 07:24 |  | YES | NO |  |  | NO | [11 empty] | 0 | 2020-12-05 07:23 | 2020-12-25 07:23 | ONSHORE | MI | 48023 | IRA | ST. CLAIR | NOT APPLICABLE |  | ST. CLAIR COMPRESSOR STATION PLANT 4 (DEHYDRATION) | DEHYDRATION SYSTEM | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | DEHYDRATOR/DRIER/TREATER/SCRUBBER | [38 empty] | 2018 | 2018 | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL | OTHER | [8 empty] | THE PLANT SAFETY SYSTEM IDENTIFIED A HIGH HEAT SIGNATURE ON THE THERMAL OXIDIZER WHICH INITIATED THE FIREGATE ACTIVATION. | CLASS 3 LOCATION | YES | METHOD1 | 680 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 51 | 51 | 200000 | 200000 | 125 | 125 | 0 | 0 |  | 3.3 | 200176 | 91915.5296806439 | 200176 | 0 | 0 | 0 | 0 | NO |  |  |  | 1060 | 1060 | 1440 | 192.619(A)(2) |  | 1969-10-27 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM OPERATOR RESPONDED AS REQUIRED WHEN ALARM WAS GENERATED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | FAILURE OF EQUIPMENT BODY (EXCEPT COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL | MATERIAL/WELD/EQUIP FAILURE | FAILURE OF EQUIPMENT BODY | [166 empty] | FAILURE OF EQUIPMENT BODY (EXCEPT COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL | [33 empty] | YES | [164 empty] | CARMELLA KING |  | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON PIONK | GAS COMPLIANCE MANAGER | 989-791-5749 | jason.pionk@cmsenergy.com | ON DECEMBER 5, 2020 AT APPROXIMATELY 07:20 HOURS CONSUMERS ENERGY GAS CONTROL RECEIVED AN ALARM NOTIFICATION WHICH INDICATED A POSSIBLE FIRE AT THE ST. CLAIR COMPRESSOR STATION (PLANT 4 - DEHYDRATION SYSTEM BUILDING). THE CONSUMERS ENERGY ST. CLAIR COMPRESSOR STATION IS LOCATED IN IRA, MICHIGAN (ST. CLAIR COUNTY). A STATION MECHANIC AT THE SITE WAS NOTIFIED AND CONFIRMED ACTIVATION OF THE PLANT FIREGATE SYSTEM OCCURRED DUE TO THE FIRE DETECTION ALARM. FOLLOWING THE EVENT, THE PLANT WAS REMOVED FROM SERVICE AND THE SCENE WAS MADE SAFE. ADDITIONAL PERSONNEL WERE DISPATCHED TO THE STATION TO DETERMINE THE POTENTIAL CAUSE OF THE ACTIVATION. DURING THE INCIDENT INVESTIGATION, SCORCH MARKS WERE DISCOVERED ON INSULATION ON THE REBOILER VENT STACK. THE PLANT SAFETY SYSTEM IDENTIFIED A HIGH HEAT SIGNATURE ON THE THERMAL OXIDIZER WHICH INITIATED THE FIREGATE ACTIVATION. THE EQUIPMENT WAS TAKEN OFF-LINE AND PHYSICALLY INSPECTED. SEVERAL CRACKED WELDS WERE IDENTIFIED ON THE EXHAUST LINE OF THE THERMAL OXIDIZER. ADDITIONAL INVESTIGATION SUBSEQUENT TO THE EVENT HAS IDENTIFIED A CONCERN RELATIVE TO DESIGN/ACTUAL UNIT OPERATING TEMPERATURE, MATERIAL TEMPERATURE LIMITS OF THE EXHAUST SYSTEM COMPONENTS, AND EXCESSIVE THERMAL CYCLING CAUSED BY SYSTEM PROGRAMMING. FURTHER PROBLEM SOLVING IS REQUIRED TO DETERMINE THE ROOT CAUSE OF THE FAILURE. HOWEVER WITH THE CONCERNS DEFINED, CONSUMERS ENERGY HAS TAKEN ACTION TO REMEDIATE EACH CONCERN THROUGH A DECREASE IN THE OPERATING TEMPERATURE OF THE SYSTEM AND A REDUCTION IN THERMAL CYCLING OF THE EQUIPMENT. ALL DAMAGED MATERIALS HAVE BEEN REPLACED AND WELDS HAVE BEEN IMPROVED IN THE RESTORATION PROCESS.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20210003 | 34702 | 2021-01-08 16:31 | ORIGINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 4720 PIEDMONT ROW DR. | CHARLOTTE | NC | 28210 | 2020-12-08 08:46 | 2020 | EASTERN | YES | 36.1731 | -76.4724 | 1293797 | 2020-12-08 12:38 | 1293931 | NATURAL GAS |  | 0 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | PIPELINE WAS PLACED ON A BYPASS TO MAINTAIN SERVICE. |  |  |  | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | NO MAINLINE VALVES WERE CLOSED. |  | OPERATIONAL CONTROL | NO MAINLINE VALVES WERE CLOSED. |  | 25 | 2020-12-08 09:28 | 2020-12-08 09:28 | ONSHORE | NC | 27944 | HERTFORD | PERQUIMANS | SURVEY STATION NO. | 2641+00 | TRANSMISSION LINE 208 | LINE 208 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | BELOWGROUND UNDERWATER | 360 | NO | YES | [6 empty] | YES | UNCASED | RACOON CREEK | 11 | BELOW WATER, PIPE IN BORED/DRILLED CROSSING | YES | [10 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10 | NO | 0.256 | 42000 | 10 INCH 256 API5L GRADE X42 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | OTHER | FBE WITH POWERCRETE | UNKNOWN | [26 empty] | 2002 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | YES | METHOD2 | 195 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | NO |  |  |  | 276 | 2520 | 800 | 192.619(A)(1) |  | 2002-06-17 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES |  |  | 38500 | NO |  |  |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | 3RD PARTY LINE DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO |  |  |  |  | NO |  |  |  |  | NO | YES | OTHER | [9 empty] | CONTRACTOR | UNKNOWN/OTHER | ROAD WORK | NO | [5 empty] | NO |  | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | MANAGER- PIPELINE SAFETY | 704-731-4618 | farris.berry@duke-energy.com | A THIRD-PARTY CONTRACTOR WAS REPLACING A BRIDGE USING A PILE DRIVER WHEN A 10" STEEL TRANSMISSION LINE WAS STRUCK APPROXIMATELY 30 FEET DEEP BELOW WATER SURFACE. 25 RESIDENTS WERE INITIALLY EVACUATED AND RELOCATED AT THE TIME OF INCIDENT. ON THE FIRST DAY 18 RESIDENTS WERE ALLOWED BACK INTO THE HOMES AND 7 REMAINED RELOCATED FOR THE DURATION OF THE LEAK. AS LOCATION OF PIPELINE AND DAMAGE IS IN DRILLED SECTION BELOW WATER, PIPE WAS NOT EXPOSED. THEREFORE ACTUAL SIZE OF MECHANICAL PUNCTURE IS UNKNOWN. FINAL DAMAGE COST AND GAS VOLUME WILL BE SUBMITTED IN THE FINAL REPORT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20210004 | 34705 | 2021-01-11 13:53 | ORIGINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2020-12-13 09:39 | 2020 | EASTERN | NO | 39.3815 | -79.1523 | 1294187 | 2020-12-13 12:56 | 1294323 | NATURAL GAS |  | 98.43 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | PIPELINE 8025 IS THE SINGLE FEED TO THE TOWN OF KITZMILLER, MD. |  |  |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-12-13 11:54 | NO | [11 empty] | 0 | 2020-12-13 10:50 | 2020-12-13 10:50 | ONSHORE | WV | 26717 | ELK GARDEN | MINERAL | NOT APPLICABLE |  | LINE 8025 | V-182 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | TAP FITTING(STOPPLE, THREAD-O-RING, WELD-O-LET, ETC.) | [38 empty] | 1974 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | NO |  | 74 |  | NO | NO |  |  | 40000 | 40000 | 0 | 0 | 202 | 202 | 50000 | 50000 | 5000 | 5000 | 0 | 0 |  | 2.05 | 95202 | 43816.9293212858 | 95202 | 0 | 0 | 0 | 1 | NO |  |  |  | 25 | 105 | 30 | 192.619(A)(1) |  | 1974-07-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | OTHER | REPORTED BY LOCAL DISTRIBUTION COMPANY PERSONNEL |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT DUE TO VEHICULAR STRIKE AND REPORTED ON COST OF REPAIR. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [9 empty] | UNKNOWN | [5 empty] | YES |  | YES | SMALL TRUCK | ROADWAY | 18 | NO | [238 empty] | WILLIAM YOUSE | COMPLIANCE SPECIALIST | william_youse@tcenergy.com | 3043573596 |  | WILLIAM YOUSE | william_youse@tcenergy.com | 3043573596 | PAUL SHAFFER | US REGULATORY COMPLIANCE EAST MANAGER | 3043572245 | paul_shaffer@tcenergy.com | PIPELINE 8025 IS A TRANSMISSION PIPELINE OPERATED AND MAINTAINED BY COLUMBIA GAS TRANSMISSION, LLC (OPID 2616), A TC ENERGY ENTITY. THIS IS A 3.5 INCH CARBON STEEL PIPELINE WITH A MAXIMUM ALLOWABLE OPERATING PRESSURE OF 30 PSIG. ON DECEMBER 13, 2020 AN ABOVE GROUND SECTION CONNECTED TO 8025 WAS STRUCK BY A PICKUP TRUCK DAMAGING A PIPE NIPPLE BELOW GROUND AND CAUSING AN UNINTENTIONAL RELEASE OF NATURAL GAS. THE VEHICLE WAS BEING OPERATED ON THE NEAR BY STATE ROUTE 42, AKA COTTAGE STREET IN ELK GARDEN, MINERAL COUNTY WEST VIRGINIA, WHEN IT LEFT THE ROADWAY AND STRUCK THE ABOVE GROUND PIPELINE APPURTENANCE. THE DRIVER WAS EXAMINED BY EMS AT THE SCENE AND RELEASED. PIPELINE 8025 IS A SINGLE FEED FOR THE NEARBY TOWN OF KITZMILLER, MARYLAND THAT REQUIRED THE PIPELINE TO STAY IN SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20210005 | 34761 | 2021-01-13 08:15 | SUPPLEMENTAL FINAL | 19610 | TRANSWESTERN PIPELINE COMPANY LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-12-14 02:05 | 2020 | CENTRAL | NO | 35.6205 | -100.9744 | 1294211 | 2020-12-14 03:02 | 1294327 | NATURAL GAS |  | 36994 | 0 | 0.1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-12-14 02:45 | 2020-12-14 06:00 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-12-14 02:15 | NO | [11 empty] | 0 | 2020-12-14 02:05 | 2020-12-14 02:30 | ONSHORE | TX | 79065 | PAMPA | GRAY | SURVEY STATION NO. | 4509+30.9 | P-3 PAMPA COMPRESSOR STATION | TXBP132 24IN LINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 1 | NO | 0.179 | 35000 | API 5L | SEAMLESS |  | US STEEL | PAINT |  | YES | [26 empty] | 1983 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | FIRE DETECTOR FAULT ON UNIT 304 TURBINE CAUSED THE STATION TO ESD. SUCTION VALVE DIDN'T CLOSE DUE TO THE POWER GAS SUPPLY LINE BEING FROZEN CAUSING GAS TO RELEASE UNTIL TECHNICIAN ARRIVED ONSITE AND ISOLATED THE STATION. | CLASS 1 LOCATION | NO |  | 526 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 79406 | 79406 | 500 | 500 | 0 | 0 | 0 | 0 |  | 2.33 | 79906 | 82553.3189676946 | 79906 | 0 | 0 | 0 | 0 | NO |  |  |  | 710 | 25 | 1008 | 192.619(A)(1) |  | 1994-12-01 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER RECEIVED AN ALARM FROM SCADA AND CALLED TECHNICIAN IMMEDIATELY REQUESTING THEM TO GO TO THE SITE FOR FURTHER INVESTIGATION. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | POWER GAS LINE FROZE PREVENTING CLOSURE OF THE STATION SUCTION VALVE. | [161 empty] | KATHRYN HARRYMAN |  | kathryn.harryman@energytransfer.com | 7139897085 |  |  |  |  | TODD NARDOZZI |  | 7139897126 | todd.nardozzi@energytransfer.com | 02:05 CST SCADA INDICATED A DROP IN PRESSURE AT P-3 PAMPA COMPRESSOR STATION, CONTROLLER CONTACTED TECHNICIAN. 02:30 CST TECHNICIAN ARRIVED ON SITE AND MANUALLY SHUT SUCTION VALVE. THE TECHNICIAN WAS ABLE TO DETERMINE A FIRE DETECTOR FAULT ON UNIT 304 TURBINE CAUSED THE STATION TO ESD. SUCTION VALVE DIDN'T CLOSE DUE TO THE POWER GAS SUPPLY LINE BEING FROZEN CAUSING GAS TO RELEASE UNTIL TECHNICIAN ARRIVED ONSITE AND ISOLATED THE STATION. THE POWER GAS LINE WAS STEAM CLEANED TO DEFROST THEN RE-PRESSURED THE POWER GAS LINE AND PUT THE STATION BACK INTO SERVICE. CURRENTLY THE POWER GAS LINE COMES OFF THE SIDE OF THE 24" DISCHARGE LINE, THEN DIVES BELOW GROUND. TO PREVENT THIS FROM HAPPENING AGAIN, OPERATIONS PLANS TO RELOCATE THE POWER GAS LINE CLOSER TO THE SUCTION VALVE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20210006 | 34719 | 2021-01-14 08:00 | ORIGINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2020-12-18 15:22 | 2020 | CENTRAL | NO | 33.0026 | -93.9451 | 1294597 | 2020-12-18 16:18 | 1294630 | NATURAL GAS |  | 22575 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-12-18 16:49 | 2020-12-19 05:00 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-12-18 16:02 | NO | [5 empty] | VALVE CLOSURE |  | 2020-12-18 16:30 | VALVE CLOSURE |  | 2020-12-18 16:49 | 0 | 2020-12-18 15:22 | 2020-12-18 16:40 | ONSHORE | LA | 71044 | IDA | CADDO | NOT APPLICABLE |  | LINE A-SOUTH | LINE A-SOUTH | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 | NO | 0.312 | 46000 | API 5LX | LONGITUDINAL ERW - LOW FREQUENCY |  | UNKNOWN | OTHER | WAX | YES | [26 empty] | 1947 | 1947 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 16 | 0.2 |  | CLASS 1 LOCATION | NO |  | 192 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 58469 | 58469 | 101550 | 101550 | 5000 | 5000 | 0 | 0 |  | 2.59 | 165019 | 109526.728708626 | 165019 | 0 | 0 | 0 | 0 | NO |  |  |  | 276 | 11 | 300 | 192.619(A)(1) |  | 2012-10-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 22964 | NO |  | YES |  |  |  | YES | DRESSER COUPLERS | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE RUPTURE | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [7 empty] | YES | [21 empty] | YES | ACETYLENE GIRTH WELD | UNKNOWN | [54 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [41 empty] | YES | [10 empty] | YES | [10 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 626 3981 |  | CASEY ROBERTS | casey.roberts@enablemidstream.com | 405 626 3981 | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 626 3981 | casey.roberts@enablemidstream.com | ON DECEMBER 18TH, 2020 AT 15:22 ENABLE GAS TRANSMISSION LINE A-SOUTH EXPERIENCED A FAILURE IN CADDO PARISH LOUISIANA. THE FAILURE WAS AT AN ORIGINAL ACETYLENE GIRTH WELD COMPLETED IN 1947. THE FAILED SECTION WAS REMOVED AND SENT TO A LAB FOR METALLURGICAL ANALYSIS. THE NRC WAS NOTIFIED ON 12/18/2020 (NRC # 1294597). A 48 HR FOLLOW UP CALL WAS PROVIDED TO THE NRC ON 12/20/2020 (NRC # 1294630). AT TIME OF REPORT SUBMISSION, ENABLE MIDSTREAM PARTNERS HAS NOT YET RECEIVED THE RESULTS OF THE LAB ANALYSIS. A SUPPLEMENTAL REPORT WILL BE FILED WHEN THE REPORT IS COMPLETED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20210007 | 34878 | 2021-01-20 13:48 | SUPPLEMENTAL FINAL | 13845 | NORTHWEST PIPELINE LLC | 2800 POST OAK BLVD | HOUSTON | TX | 77056 | 2020-12-20 23:28 | 2020 | PACIFIC | NO | 45.7243 | -121.49 | 1294705 | 2020-12-21 01:24 | 1294836 | NATURAL GAS |  | 1068 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-12-21 02:20 | 2020-12-23 14:00 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-12-21 00:08 | NO | [11 empty] | 1 | 2020-12-20 23:28 | 2020-12-21 01:05 | ONSHORE | WA | 98672 | WHITE SALMON | KLICKITAT | MILEPOST | 4.6 | HOOD RIVER METER STATION | HOOD RIVER LATERAL | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | METER | [38 empty] | 1972 | 1972 | CARBON STEEL |  | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 1 LOCATION | NO |  | 116 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 2670 | 2670 | 1200000 | 1200000 | 100000 | 100000 | 0 | 0 | ECONOMIC IMPACT TO COMMUNITIES OF WHITE SALMON AND HOOD RIVER NOT CALCULATED | 2.5 | 1302670 | 599502.413118742 | 1302670 | 1 | 0 | 0 | 1 | NO |  |  |  | 372 | 5150 | 946 | 192.619(A)(2) |  | 1972-11-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS THE RESULT OF A MOTOR VEHICLE INCIDENT INVOLVING AN IMPAIRED DRIVER COLLIDING WITH OUR FACILITY. FOR FURTHER INFORMATION REFERENCE FULL NARRATIVE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [9 empty] | YES | YES | YES | YES |  |  | UNKNOWN | 50 |  | PASSENGER CAR | ROADWAY | 70 | NO | [238 empty] | BRET BURKHART | ENGINEER SR. | bret.burkhart@williams.com | 8015846892 |  | LARRY WEST | larry.west@williams.com | 3606662141 | TYSON GREEN | MANAGER PIPELINE SAFETY | 7132152535 | tyson.green@williams.com | DETAILS FROM WILLIAMS OPERATOR LOG (12/20/2020 TO 12/21/2020): THE HOOD RIVER METER STATION ALARMED FOR "LOW LOW" AT 280 PSIG FROM 372PSIG. FLOW WENT FROM A RANGE OF 1800-8500MCFD JUMPING TO 10500MCFD BETWEEN SCANS. LOCAL OPERATIONS PERSONNEL WERE INITIALLY CONTACTED AT 11:35PM (LOCAL TIME). WILLIAMS CONTACTED NORTHWEST NATURAL AT 11:45PM LOCAL TIME, AND THEY REPORTED SEEING ABNORMAL FLUCTUATIONS AS WELL. SOON AFTERWARDS A NORTHWEST NATURAL REPRESENTATIVE CALLED BACK TO REPORT THAT A CAR HAD CRASHED INTO THE METER STATION AND THAT THE KLIKITAT FIRE DEPARTMENT WAS CLOSING THE HOOD RIVER BRIDGE AT HWY 14. AT 12:08PM KLICKITAT EMERGENCY DISPATCH CALLED TO LET US KNOW ABOUT THE INCIDENT AND ALSO REPORTED A STRONG ODOR OF GAS AND LOUD NOISE. AT 12:17PM THE LOCAL DISTRICT MANAGER WAS INFORMED OF THE SITUATION, AND ADDITIONAL LOCAL PERSONNEL WERE DISPATCHED. AT 12:36PM THE INCIDENT WAS REPORTED TO WILLIAMS SAFETY OPERATIONS CENTER. AT ABOUT 1:00AM TECHNICIANS FROM NORTHWEST NATURAL AND WILLIAMS ARRIVED ON SITE. AT 1:35AM IT WAS DETERMINED THAT THE LATERAL FEEDING THE STATION WOULD NEED TO BE COMPLETELY SHUT-IN TO ISOLATE THE INCIDENT. AT 2:20AM VALVES 75-0 AND 75-0X WERE CLOSED TO ISOLATE THE LATERAL, AND BY 3:15AM THE FLOW AND PRESSURE REACHED 0. BY 2PM THAT DAY THE STATION WAS ISOLATED AT ITS TAP VALVE, AND THE LATERAL WAS RE-PACKED IN ANTICIPATION OF A MOBILE METER STATION, AND REPAIRS/RETURN TO SERVICE OF THE PERMANENT FACILITY. CASE SUMMARY FROM DEPUTY REPORT FOR INCIDENT 20-B1728: "ON 12/20/2020, AT ABOUT 2330 HOURS, I WAS DISPATCHED TO AN MVC INVOLVING UNKNOWN INJURIES NEAR BRIDGEMART ON HWY 14. ON ARRIVAL AT THE COLLISION SCENE, I OBSERVED A VEHICLE THAT APPEARED TO HAVE COLLIDED WITH A GAS PLANT LOCATED ON THE NORTH SIDE AT THE INTERSECTION OF HWY 14 AND THE HOOD RIVER BRIDGE. I ATTEMPTED TO MAKE CONTACT WITH THE VEHICLE, BUT WAS UNABLE TO DUE TO MULTIPLE POTENTIAL HAZARDS. LOCAL FIRE DEPARTMENTS, EMS, AND LAW ENFORCEMENT AGENCIES ARRIVED TO ASSIST WITH VARIOUS TASKS. NW NATURAL, OWNER OF THE GAS PLANT, SENT CREWS TO SHUT OFF LINES THAT WERE DAMAGED AND RELEASING GAS INTO THE SURROUNDING ATMOSPHERE. THIS CREATED A HAZARDOUS RISK FOR ANYONE WITHIN .5 MILES OF THE COLLISION SCENE. THE DRIVER OF THE VEHICLE, BENJAMIN SOLORIO, WAS ABLE TO SELF EXTRICATE AND MAKE CONTACT WITH A WASHINGTON STATE PATROL TROOPER. SOLORIO WAS EVALUATED BY EMS AND TAKEN TO SKYLINE HOSPITAL ER, WHERE HE WAS TREATED FOR MINOR INJURIES. IT WAS DETERMINED BY THE WSP TROOPER THAT SOLORIO WAS DRIVING UNDER THE INFLUENCE OF ALCOHOL DURING THE TIME OF THE COLLISION AND AT AN EXCESS SPEED OF AT LEAST TWICE THAT OF THE POSTED SPEED LIMIT, 25 MPH OR MORE, ON THE HOOD RIVER BRIDGE AND THROUGH THE INTERSECTION AT HWY 14. ALL AGENCIES INVOLVED TOOK APPROPRIATE PRECAUTIONS, AND THE COLLISION SCENE WAS HANDLED PER STANDARD PROTOCOLS. THE COMMUNITY, INCLUDING THE SURROUNDING COMMUNITY OF HOOD RIVER, OR. WAS GREATLY AFFECTED BY THIS INCIDENT. MANY WERE... LEFT WITHOUT NATURAL GAS FOR HEATING, COOKING, ETC. SOLORIO WAS PROCESSED FOR DUI THE NIGHT OF THE INCIDENT AND CITED FOR RECKLESS DRIVING ON 12/27/2020" ADDITIONAL DETAIL FROM POLICE REPORT: "BRIDGEMART WAS CLOSED AND THE STORE EMPLOYEE WAS ADVISED TO EVACUATE. THE RESIDENTS STAYING AT THE RV PARK WERE ALSO ADVISED TO STAY CLEAR OF THE INCIDENT AS FAR AWAY AS POSSIBLE. RESIDENCES NORTH OF THE COLLISION, INCLUDING SE OAK ST FROM SE 1ST TO SE 7TH ST, WERE ADVISED TO SHELTER IN PLACE BY CLOSING ALL DOORS AND WINDOWS. DISPATCH ASSISTED BY USING A REVERSE 911 SYSTEM TO ADVISE AND FIRE UNITS ALSO WENT DOOR-TO-DOOR TO RESIDENCES." A TEMPORARY SKID, PROVIDING PRESSURE REGULATION AND METERING, WAS PUT INTO SERVICE ON 12/23/2020 TO RETURN SERVICE TO THE CUSTOMER. THIS WILL REMAIN IN SERVICE UNTIL A FULL METER STATION REBUILD (PLANNED FOR SUMMER 2021) CAN BE COMPLETED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20210008 | 34864 | 2021-01-21 09:37 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2020-12-24 15:19 | 2020 | CENTRAL | NO | 41.9007 | -96.5246 | 1294941 | 2020-12-24 16:11 | 1295014 | NATURAL GAS |  | 8180 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-12-24 16:41 | 2020-12-26 22:29 |  |  |  |  | YES | 2020-12-24 15:19 | ALLOWED TO BURN OUT |  | 8180 | YES | VALVE CLOSURE |  | 2020-12-24 16:37 | VALVE CLOSURE |  | 2020-12-24 16:41 | 0 | 2020-12-24 15:20 | 2020-12-24 16:00 | ONSHORE | NE | 68038 | Not Within a Municipality | BURT | MILEPOST | 21.32 | HOOPER TO SOUTH SIOUX CITY C-LINE | NEM50103-M570C | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 40 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 | NO | 0.312 | 52000 | 5LX | LONGITUDINAL ERW - LOW FREQUENCY |  | AO SMITH | COAL TAR |  | YES | [26 empty] | 1961 | 1961 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 102 | 72 |  | CLASS 1 LOCATION | NO |  | 468 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 21922 | 21922 | 100000 | 100000 | 50000 | 50000 | 0 | 0 |  | 2.68 | 171922 | 91581.4908333053 | 171922 | 0 | 0 | 0 | 0 | NO |  |  |  | 745 | 225 | 800 | 192.619(C) |  | 1970-07-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 70072 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [64 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | [10 empty] | NO |  |  | YES | PRIVATE LANDOWNER | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | GRADING | YES | 203021735 |  | UTILITY OWNER | NO | NO | YES | 36 | LOCATING PRACTICES NOT SUFFICIENT |  | FACILITY MARKING OR LOCATION NOT SUFFICIENT | [119 empty] | YES | YES |  |  | YES |  |  |  | 2020 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [27 empty] | 2020 | FREE SWIMMING | HIGH RESOLUTION |  | INSIDE ILI CUPS | [18 empty] | YES | NO |  |  | NO | [13 empty] | YES |  |  |  | 2020 | [6 empty] | YES | [51 empty] | YES | JOHN GORMLEY | SR PIPELINE SAFETY SPECIALIST | john.gormley@nngco.com | 402-398-7494 |  | JOHN GORMLEY | john.gormley@nngco.com | 402-398-7494 | TOM CORRELL | VP PIPELINE SAFETY AND RISK | 402-398-7715 | thomas.correll@nngco.com | AT 15:19 ON DECEMBER 24, 2020, NORTHERN NATURAL GAS RECEIVED NOTIFICATION FROM THE LYONS NE VOLUNTEER FIRE DEPARTMENT OF A PIPELINE RUPTURE SOUTH OF COUNTY ROAD P IN BURT COUNTY, NEBRASKA. THE RUPTURED LINE WAS IDENTIFIED AS THE 179NEM50103-M570C HOOPER TO SOUTH SIOUX CITY C-MAINLINE AT MILEPOST 21.32. THIS LOCATION IS 3.8 MILES SOUTH OF THE NEB56001 LYONS, NEBRASKA BRANCH LINE TAKE-OFF. OPERATIONS STAFF ISOLATED THE RUPTURED SEGMENT AT 16:46 HOURS AFTER 8.18 MILLION CUBIC FEET OF GAS LOSS. INITIAL OBSERVATIONS BY THE FIELD INVESTIGATION TEAM INDICATED THE FAILURE MAY HAVE BEEN CAUSED BY PREVIOUS THIRD PARTY DAMAGE. THE FIELD INVESTIGATION TEAM IDENTIFIED A SERIES OF GOUGES AND SCORES ACROSS A SEGMENT OF PIPE WHICH WAS FOUND ABOUT 100 YARDS SOUTH OF THE FAILURE SITE. THE ROOT CAUSES OF THIS EVENT ARE A THIRD PARTY CONTRACTOR COMMENCING EXCAVATION PRIOR TO THE CLEARING OF A ONE CALL TICKET. THERE WERE TWO ONE CALL TICKETS REGARDING THIS PROPERTY. ONE FOR OCT 30 TO CLEAR TREES AND REMOVE TERRACES AND ONE FROM DEC 4 TO BURY LEFT OVER DEBRIS FROM A BURN PILE. THE DAMAGE TO THE PIPELINE PROBABLY OCCURRED AT THE OCT 30 WORK. A CONTRIBUTING FACTOR WAS A FIELD OPERATIONS FAILURE TO FOLLOW NORTHERN PROCEDURE BY GIVING VERBAL APPROVAL FOR EXCAVATION ACTIVITIES IN PROXIMITY TO A PIPELINE BEGIN BEFORE THE EMPLOYEE ARRIVED ON SITE. BOTH TIMES THE ONE CALL TICKETS WERE COMPLETED BY THE SAME EMPLOYEE AND THE PIPELINES MARKED IN ACCORDANCE WITH COMPANY PROCEDURES. THE EMPLOYEE REMAINED ON SITE UNTIL ALL WORK WAS COMPLETED. NORTHERN NATURAL GAS MOBILIZED THE EMERGENCY RESPONSE TEAM AND CONSTRUCTION RESOURCES TO THE INCIDENT SITE AND COMPLETED REPAIRS AT 22:29 HOURS DECEMBER 25, 2020.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20210009 | 34757 | 2021-01-23 10:01 | ORIGINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2020-12-26 05:21 | 2020 | EASTERN | NO | 32.6133 | -84.8203 | 1295001 | 2020-12-26 06:43 | 1295064 | NATURAL GAS |  | 85900 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-12-26 06:30 | 2020-12-26 22:15 |  | NO |  |  | NO | [11 empty] | 0 | 2020-12-26 05:19 | 2020-12-26 06:04 | ONSHORE | GA | 31807 | Not Within a Municipality | HARRIS | MILEPOST | MP 311 - 30+4 | ELLERSLIE COMPRESSOR STATION | SOUTH MAIN LINE SYSTEM, | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 12 | NO | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1958 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 2 LOCATION | NO |  | 860 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 225917 | 225917 | 5800 | 5800 | 300 | 300 | 5545 | 5545 | APPROXIMATE INVESTIGATION COST ESTIMATE = $5,545; | 2.63 | 237562 | 239563.774348158 | 237562 | 0 | 0 | 0 | 0 | NO |  |  |  | 856 | 1743 | 1200 | 192.619(C) |  | 1953-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | STATION ESD CAUSED BY CRACK IN 1/2" ESD SYSTEM PIPE THREAD; LEAK AT THREAD ACTIVATED ESD SYSTEM; | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | INVESTIGATION IS STILL ONGOING | [161 empty] | WILLIAM MARTIN MULLER | SPECIALIST-PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 2053253863 |  | CAROL PARRAMORE | carol_parramore@kindermorgan.com | 2292264744 | JAIME HERNANDEZ | DIRECTOR ENGINEERING CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | ON DECEMBER 26, 2020, SOUTHERN NATURAL GAS COMPANY (SNG) COMPRESSOR STATION KNOWN AS ELLERSLIE COMPRESSOR STATION ON THE SOUTH MAIN SYSTEM NEAR MILEPOST 311 EXPERIENCED AN EMERGENCY SHUT DOWN (ESD) EVENT. AT 05:19-HOURS, GAS CONTROL RECEIVED A SCADA ALARM ALERTING THE ON-DUTY CONTROLLER THE ESD HAD BEGUN. THE CONTROLLER, USING THE CALL-OUT SYSTEM, NOTIFIED THE PROPER OPERATIONS PERSONNEL AT THAT TIME. AT 06:04-HOURS, OPERATIONS PERSONNEL ARRIVED AT ELLERSLIE COMPRESSOR STATION AND CONFIRMED NATURAL GAS WAS VENTING. UPON SAFELY ENTERING THE COMPRESSOR STATION PROPERTY, THE OPERATIONS PERSONNEL BEGAN INSPECTING THE COMPRESSOR STATION TO DETERMINE WHY NATURAL GAS WAS STILL VENTING FOLLOWING THE ESD FUNCTION. THE SPECIALIST FOUND VALVE #19 WHICH IS PART OF THE ESD SYSTEM LOCATED IN THE SUCTION SIDE OF THE STATION PIPING HAD NOT FULLY CLOSED. VALVE #19 WAS MANUALLY CLOSED AND THE STATION WAS SHUT DOWN AT 6:30-HOURS. FIELD OPERATIONS INITIATED THE EMERGENCY RESPONSE LINE (ERL) PROCESS FOLLOWING INTERNAL PROCEDURES AND THE INCIDENT WAS DEEMED REPORTABLE DURING THE ERL CALL. AS PART OF SNG'S POST INCIDENT INVESTIGATION PROCESS THE OPERATIONS PERSONNEL ON SITE DISCOVERED AN EXIT POINT IN THE COMPRESSOR STATION YARD WITH SOME ICE FORMED NEAR AN UNDERGROUND ESD FACILITY PIPE. SNG STARTED THE EXCAVATION PROCESS TO IDENTIFY THE SOURCE OF THE UNDERGROUND LEAK. AFTER EXPOSING THE UNDERGROUND ESD PIPE, SNG DISCOVERED THAT THE 1/2-INCH ESD PIPE HAD A CRACK IN A THREADED CONNECTION. DURING THE ROOT-CAUSE ANALYSIS IT WAS DETERMINED THAT THE CRACKED UNDERGROUND ESD PIPE WAS THE CAUSE OF THE ESD EVENT. FURTHERMORE, THE ANALYSIS ALSO REVEALED THAT VALVE #19 DID NOT FULLY CLOSE AS DESIGNED ALLOWING THE VOLUME OF GAS RELEASED TO BE ABOVE THE PHMSA REPORTABLE THRESHOLD. OPERATIONS MANAGEMENT EXPEDITED A CONTRACTOR TO COME ON SITE AND REPLACE THE BURIED 1/2-INCH ESD LINE. THE CRACKED PIPE WAS SENT TO A LAB FOR FURTHER ASSESSMENT AND THE LINE REPLACEMENT WAS COMPLETED ON DECEMBER 26, 2020. OPERATIONS PERSONNEL CHECKED AND CYCLED VALVE #19 WITH NO ISSUE. VALVE #19 IS CLOSED AND LOCKED OUT OF SERVICE UNTIL THE VALVE OPERATOR CAN BE REPLACED. WITH GENERAL SAFETY INSPECTION OF THE COMPRESSOR STATION AND COORDINATION WITH GAS CONTROL, THE COMPRESSOR STATION RETURNED TO SERVICE AT 22:15-HOURS, DECEMBER 26, 2020. THE INVESTIGATION STILL ONGOING AWAITING THE LAB RESULTS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20210010 | 34772 | 2021-01-27 10:10 | ORIGINAL FINAL | 31286 | ONEOK GAS TRANSPORTATION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2021-01-02 10:40 | 2021 | CENTRAL | YES | 35.728 | -98.8614 | 1295377 | 2021-01-02 11:00 | 1295443 | NATURAL GAS |  | 127718.8 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-01-02 09:34 | 2021-01-04 12:00 |  | NO |  |  | NO | [11 empty] | 0 | 2021-01-02 09:30 | 2021-01-02 09:30 | ONSHORE | OK | 73669 | Not Within a Municipality | Not Within a County or Parish | NOT APPLICABLE |  | THOMAS COMPRESSOR STATION | M-2 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2015 | 2015 | CARBON STEEL |  | OTHER | [8 empty] | THE LEAK OCCURRED THROUGH THE RELIEF VALVE. | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 291837 | 291837 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2.285 | 291837 | 302560.669291339 | 291837 | 0 | 0 | 0 | 0 | NO |  |  |  | 868 | 15 | 985 | 192.619(A)(1) |  | 2015-12-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CAUSE WAS DUE TO FIELD RELATED ISSUES. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [204 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | [6 empty] | YES | TRANSMITTER MANIFOLD VALVE WAS LEFT CLOSED. | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | JACK CROW | COMPLIANCE SPECIALIST | jack.crow@oneok.com | [5 empty] | RANDY MASHBURN | OPERATIONS MANAGER | 918-497-8407 | randy.mashburn@oneok.com | JAN 2ND, 2021 AT 12:39AM THE THOMAS COMPRESSOR STATION STARTED VENTING GAS THROUGH THE STATION VENT STACK. IT WAS DETERMINED THE LOSS OF SUPPLY AIR ALLOWED THE SUCTION & DISCHARGE VALVES TO OPEN RELEASING GAS. A ONEOK EMPLOYEE WAS DRIVING BY APPROXIMATELY AT 9:20AM AND HIT THE ESD AT 9:34AM.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20210011 | 34840 | 2021-02-11 09:17 | ORIGINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2021-01-27 12:08 | 2021 | CENTRAL | NO | 32.0841 | -95.1518 | 1296806 | 2021-01-27 12:08 | 1296886 | NATURAL GAS |  | 487 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | MINOR LEAK ONLY |  |  |  | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | MINOR LEAK ONLY. NO ACTION TAKEN |  | OPERATIONAL CONTROL | MINOR LEAK ONLY. NO ACTION TAKEN |  | 0 | 2021-01-27 12:08 | 2021-01-27 12:08 | ONSHORE | TX | 75789 | Not Within a Municipality | CHEROKEE | SURVEY STATION NO. | 1898+44 | LONGVIEW CS TO BOGGY CREEK TO HUNTSVILLE ML | INDEX 11 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 24 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | REPAIR SLEEVE OR CLAMP | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | EXISTING SPLIT SLEEVE/CLAMP | [5 empty] | CLASS 1 LOCATION | NO |  | 121 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 1203 | 1203 | 50000 | 49022.3702185793 | 0 | 0 | 0 | 0 |  | 2.47 | 51203 | 23749.7661998193 | 50225.3702185793 | 0 | 0 | 0 | 0 | NO |  |  |  | 345 | 8000 | 430 | 192.619(C) |  | 2021-01-28 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 33992 | NO |  | YES | YES |  |  | YES | NO PIG TRAPS | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | SPLIT SLEEVE/CLAMP |  |  |  | YES | [174 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 2709035764 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 2703146547 | tina.baker@bwpipelines.com | GULF SOUTH'S GAS CONTROL RECEIVED A CALL ON 1/27/21 AT 10:30 AM REPORTING A POTENTIAL LEAK. OPERATIONS PERSONNEL RESPONDED AT 12:08 PM AND CONFIRMED THE LEAK. UPON EXCAVATION, A LEAKING CLAMP AND SPLIT SLEEVE WERE FOUND. AFTER INSPECTING THE LEAK AND PIPELINE, THE LEAK WAS CONSIDERED GRADE 3 (MINOR LEAK) AND GULF SOUTH WILL CONTINUE TO MONITOR UNTIL REPAIRED. GULF SOUTH IS IN THE PROCESS OF SCHEDULING A SHUTDOWN TO REPLACE PIPE AND MUST COORDINATE WITH CENTERPOINT BECAUSE THEY HAVE TO PROVIDE CNG TRUCKS AT CITY GATES TO PREVENT ANY CUSTOMER LOSS. GULF SOUTH DETERMINED THAT THE REPAIR WOULD BE PIPE REPLACEMENT WHICH WOULD EXCEED $50,000 AND MADE THE REQUIRED NRC NOTIFICATION. A SUPPLEMENTAL/FINAL REPORT WILL BE SUBMITTED ONCE REPAIRS ARE COMPLETED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20210012 | 34845 | 2021-02-11 13:59 | ORIGINAL | 32655 | EAST CHEYENNE GAS STORAGE, LLC | 34511 COUNTY ROAD 39 | PEETZ | CO | 80747 | 2021-01-18 14:53 | 2021 | MOUNTAIN | NO | 40.5628 | -103.1317 | 1296264 | 2021-01-18 16:10 | 1296366 | NATURAL GAS |  | 384 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-01-18 14:53 | 2021-01-20 20:59 |  | YES | OPERATOR | 2021-01-18 17:39 | NO | [11 empty] | 0 | 2021-01-18 14:53 | 2021-01-18 14:53 | ONSHORE | CO | 80747 | Not Within a Municipality | LOGAN | NOT APPLICABLE |  | EAST CHEYENNE GAS STORAGE | UNGS FACILITY - COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 20 | NO | 0.594 | 52000 | API 5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | SALZGITTER MANNESMANN | PAINT |  | NO | [26 empty] | 2012 | 2012 | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 524 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 1018 | 1018 | 15000 | 14706.7110655738 | 0 | 0 | 0 | 0 |  | 2.65 | 16018 | 7806.17526676994 | 15724.7110655738 | 0 | 0 | 0 | 0 | NO |  |  |  | 1000 | 0 | 1440 | 192.619(A)(1) |  | 2012-08-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | NO | YES | OTHER | LOUD NOISE FROM THE FACILITY HEADER BLOWDOWN |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | HYDRATE FORMATION INSIDE FACILITY PIPING | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | OTHER | HYDRATE FORMATION IN FACILITY PIPING | NO | [295 empty] | YES | [10 empty] | JOE CARDOSO | PHMSA COMPLIANCE SPECIALIST | joe.cardoso@enstorinc.com | 432-741-1403 |  | CHASE BENNETT | chase.bennett@enstorinc.com | 970-580-1726 | TODD CASH | COMPLIANCE DIRECTOR | 281-374-3085 | todd.cash@enstorinc.com | ON THE AFTERNOON OF MONDAY, JANUARY 18 AT APPROXIMATELY 14:53 MOUNTAIN TIME ENSTOR PERSONNEL RESPONDED TO AN INCIDENT (LOUD AUDIBLE NOISE) AT THE EAST CHEYENNE GAS STORAGE FACILITY, LOCATED IN A REMOTE AREA MORE THAN 20 MILES NORTH OF STERLING, COLORADO. NO INJURIES OR FATALITIES OCCURRED. THE FACILITY SUSTAINED MINOR PIPING DAMAGE WHEN SOME ICE THAT HAD COLLECTED IN A SECTION OF PIPE GAVE WAY WHILE THE LINE WAS BEING PRESSURED UP FOR USE AND DAMAGED A BLOWDOWN VALVE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20210013 | 34863 | 2021-02-15 10:41 | ORIGINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2021-01-28 08:30 | 2021 | CENTRAL | NO | 29.9617 | -91.7881 | 1296876 | 2021-01-28 09:55 | 1296952 | NATURAL GAS |  | 1 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | REDUCED PRESSURE BY 20% |  |  |  | YES | OPERATOR | 2021-01-28 08:55 | NO | [5 empty] | OPERATIONAL CONTROL | REDUCE PRESSURE BY 20% |  | OPERATIONAL CONTROL | REDUCED PRESSURE BY 20% |  | 0 | 2021-01-28 08:30 | 2021-01-28 08:30 | ONSHORE | LA | 70560 | Not Within a Municipality | IBERIA | MILEPOST | 138.15 | IOWA TO FRANKLIN | INDEX 205 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 45 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | MECHANICAL COUPLING | 1931 | 1931 | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 2 LOCATION | NO |  | 128 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 2 | 2 | 120000 | 117653.68852459 | 0 | 0 | 0 | 0 |  | 2.47 | 120002 | 54008.2210317973 | 117655.68852459 | 0 | 0 | 0 | 0 | NO |  |  |  | 254 | 1800 | 480 | 192.619(C) |  | 1971-03-12 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES |  |  | 21397 | NO |  | YES | YES | YES |  | YES | NO PIG TRAPS, PIPE CONNECTED WITH COUPLINGS AND ACETYLENE WELDS | YES |  | YES | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | MECHANICAL COUPLING | [19 empty] | YES | MINOR PIPELINE MOVEMENT DUE TO TEMPERATURE CHANGES CAUSED MINOR SEEPAGE OF GAS | [161 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 2709035764 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 2703146547 | tina.baker@bwpipelines.com | ON 1/23/21, A GULF SOUTH TECHNICIAN, WHO WAS PERFORMING ROUTINE INSPECTIONS USING A LASER LEAK DETECTION DEVICE, FOUND A GAS LEAK INDICATION. FIELD OPERATIONS PERSONNEL MONITORED THE SITE UNTIL THE POTENTIAL LEAK COULD BE VERIFIED. ON 1/25/21 THE PRESSURE WAS LOWERED FROM 254 PSIG TO 200 PSIG IN PREPARATION FOR EXCAVATION DUE TO THE LINE BEING CONSTRUCTED WITH MECHANICAL COUPLINGS. ON 1/28/21, THE LINE WAS EXPOSED AND A MINOR LEAK THROUGH A DRESSER COUPLE WAS CONFIRMED. THE PIPELINE BELL HOLE WAS BACKFILLED AND PROPER NOTIFICATIONS WERE MADE INCLUDING AN NRC NOTIFICATION DUE TO THE ANTICIPATED REPAIR COST EXCEEDING $50,000. THE LEAK REPAIR WILL REQUIRE THE PIPELINE TO BE SHUT DOWN. ON 1/28/21, GULF SOUTH CONTACTED CENTERPOINT ENERGY TO COORDINATE ALTERNATIVE GAS SUPPLY FOR THEIR CUSTOMERS DURING THE OUTAGE. THE REPAIR IS CURRENTLY SCHEDULED FOR 2/24/21 BUT THAT IS CONTINGENT ON WEATHER/TEMPERATURES. A SUPPLEMENTAL/FINAL REPORT WILL BE SUBMITTED ONCE REPAIRS ARE COMPLETE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20210014 | 34873 | 2021-02-18 09:14 | ORIGINAL FINAL | 31978 | ATMOS PIPELINE - TEXAS | 5420 LBJ FREEWAY, SUITE 1500 | DALLAS | TX | 75240 | 2021-01-19 15:20 | 2021 | CENTRAL | NO | 32.6814 | -99.8031 | 1296316 | 2021-01-19 16:17 | 1296448 | NATURAL GAS |  | 1667.5 | 0.89 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | INSTALLED TWO 12 INCH STOPPLE FITTINGS AND BUILT A BY-PASS BETWEEN THEM |  |  |  | YES | OPERATOR | 2021-01-19 11:00 | NO | [5 empty] | OPERATIONAL CONTROL | NO ACTION REQUIRED. UPSTREAM PIPELINE PRESSURE AND FLOW WERE ADEQUATE |  | OPERATIONAL CONTROL | USED STEEL SQUEEZERS ON 1 INCH TAP TO SQUEEZE OFF LEAK |  | 0 | 2021-01-19 10:03 | 2021-01-19 10:17 | ONSHORE | TX | 79525 | HAWLEY | JONES | SURVEY STATION NO. | 936+67 | KC 17 1" FARM TAP | N/A | NO | PIPELINE RIGHT-OF-WAY | TRANSITION AREA | SOIL/AIR INTERFACE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 1.25 | NO | 0.126 | 24000 | UNKNOWN | OTHER | UNKNOWN | UNKNOWN | COAL TAR |  | YES | [26 empty] | 1953 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | VALVE KNOCKED OFF OF 1.25" RISER | CLASS 1 LOCATION | NO |  | 24 |  | NO | NO |  |  | 0 | 0 | 5 | 4.90223702185792 | 9785 | 9785 | 161563 | 158404.023992486 | 0 | 0 | 0 | 0 |  | 5.868 | 171353 | 82858.4308549546 | 168193.926229508 | 0 | 0 | 0 | 0 | NO |  |  |  | 650 | 0 | 800 | 192.619(A)(1) |  | 1953-12-14 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES |  |  | 37561 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS TOO SMALL TO BE PICKED UP BY CONTROLLERS | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO |  |  |  |  | YES | ACTIVITY IS EXEMPT AND DID NOT EXCEED THE LIMITS OF THE EXEMPTION |  | RAILROAD COMMISSION OF TEXAS | FARMER WAS TILLING AT A DEPTH OF LESS THAN 16 INCHES | NO |  |  |  |  | YES | [6 empty] | FARMER | FARM EQUIPMENT | AGRICULTURE | NO | [5 empty] | NO |  | ABANDONED FACILITY | [266 empty] | ROBERT O'DELL | OPERATIONS SUPERVISOR | robert.odell@atmosenergy.com | 325-280-1778 |  |  |  |  | MARLO SUTTON | VICE PRESIDENT - TECHNICAL SERVICES | 214-206-2033 | marlo.sutton@atmosenergy.com | ON JANUARY 19, 2021, A FARMER STRUCK A FARM TAP OFF OF LINE KC 17 WITH A PLOW NEAR HAWLEY, TEXAS. ATMOS ENERGY WAS NOTIFIED OF THE INCIDENT AT 10:03 AM, AT WHICH POINT WORK BEGAN TO DETERMINE HOW TO MAKE REPAIRS. THE DECISION WAS MADE TO SQUEEZE OFF THE 1.25" STEEL RISER AND AFTER THE SQUEEZE OFF OCCURRED AT APPROXIMATELY 1 PM, IT WAS DISCOVERED THAT A THREADED CONNECTION WAS LEAKING UNDER THE SQUEEZED OFF SECTION OF THE RISER. WORK THEN BEGAN ON A BYPASS ON KC17 TO ENSURE CONTINUED SERVICE ON THE LINE. AT THE POINT IT WAS DETERMINED A BYPASS WOULD BE NEEDED TO MAKE THE NECESSARY REPAIRS, IT WAS ANTICIPATED THAT THE COST ASSOCIATED WITH REPAIRING THE DAMAGE WOULD EXCEED $50,000. A CALL WAS MADE TO THE NATIONAL RESPONSE CENTER AT 16:17 CT ON 1/19/2021. STOPPLES WERE WELDED ON FOR THE BYPASS, WHICH WAS COMPLETED ON JANUARY 20, 2021. ON JANUARY 21, 2021, 5 FEET OF 12" PIPE WAS REPLACED AND LINE KC17 WAS THEN RETURNED TO NORMAL OPERATION.
2021-02-26 10:37 | NO | NO | GG (Gas Gathering) | 20210015 | 34920 | 2021-02-26 09:57 | ORIGINAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2021-02-22 09:29 | 2021 | CENTRAL | NO | 36.9872 | -107.8759 | 1298777 | 2021-02-23 11:49 | 1 | NATURAL GAS |  | 587 | 172 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-01-16 12:00 | 2021-01-31 17:00 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2021-01-16 12:05 | VALVE CLOSURE |  | 2021-01-16 12:10 | 0 | 2021-01-16 12:00 | 2021-01-16 12:00 | ONSHORE | NM | 87410 | Not Within a Municipality | SAN JUAN | SURVEY STATION NO. | 223+41 | MD-7 LOOP | MD-7 LOOP | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 72 | YES | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 16 |  | 0.188 | 52000 | API-5L-X-52-52000 | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | EPOXY |  | NO | [7 empty] | PIPE GIRTH WELD |  | YES | 0.375 | 52000 | API-5L-X-52-52000 | SEAMLESS |  | US STEEL | EPOXY OTHER THAN FBE |  | NO | [7 empty] | 1997 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 2 LOCATION | NO |  | 175 |  | NO | NO |  |  | 0 | 0 | 258 | 252.955430327869 | 881 | 881 | 85000 | 83338.0293715847 | 0 | 0 | 0 | 0 |  | 1.5 | 86139 | 39283.8404288219 | 84471.9848019126 | 0 | 0 | 0 | 0 | NO |  |  |  | 85 | 3000 | 250 | 192.619(A)(1) |  | 1997-01-23 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 23543 | YES | [7 empty] | NO | [6 empty] | TYPE A GATHERING | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK DID NOT GENERATE ANY ALARMS AND PIPELINE CONTROL CANNOT ACTUATE EQUIPMENT ON THE PIPELINE. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [7 empty] | YES | [21 empty] | YES | BENDING STRESS FROM CONSTRUCTION AND BACKFILL. | 1054 | [54 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | YES | 2018 | [6 empty] | YES | [33 empty] | YES | YES | [20 empty] | GORDON WILLIAMS | ENGINEER - PIPELINE COMPLIANCE | gswilliams@eprod.com | 713-381-6211 |  | GORDON WILLIAMS | gswilliams@eprod.com | 713-381-6211 | GORDON WILLIAMS | ENGINEER - PIPELINE COMPLIANCE | 713-381-6211 | gswilliams@eprod.com | ON JANUARY 16, AN ENTERPRISE TECHNICIAN PATROLLING LINE MD-7 LOOP DETECTED A GAS LEAK IN A CLASS 2 LOCATION. THE LINE MD-7 LOOP WAS ISOLATED AND DE-PRESSURED. ON THE SAME DAY, THE NMPRC WAS NOTIFIED BECAUSE ENTERPRISE BELIEVED THE COST TO REPAIR THE LINE MAY EXCEED THE $5,000 BUT LESS THAN $50,000 AT THE TIME. THE FAILED WELD WAS EXAMINED AND IT WAS DETERMINED THE WELD FAILED DUE TO CRACKING ALONG THE TOE OF THE WELD. ENTERPRISE EXPANDED THE EXCAVATION TO RELIEVE BENDING STRESS AND THE PIPELINE WAS CUT-OUT AND REPLACED. LINE MD-7 LOOP WAS PLACED BACK INTO SERVICE ON 1/31/2021. ON FEBRUARY 22, 2021, ENTERPRISE RECEIVED AN UPDATED INVOICE WHICH EXCEEDED THE ORIGINAL ESTIMATE AND, CONSEQUENTLY, RESULTED IN THE RELEASE MEETING THE DEFINITION OF AN INCIDENT PER §191.3 DUE TO THE COST EXCEEDING $50,000.