## gtggungs2010toPresentFields
Gas Transmission, Gas Gathering, and Underground Natural Gas Storage Incident Reports for 2010 - present (PHMSA Form 7100.2 Rev. 4-2019) - Data Dictionary for Flagged Data file
Field Name | Data Type | Field Name Description | Form Location
DATAFILE_AS_OF | DATE | Data as of date | Not on the form
SIGNIFICANT | VARCHAR2 | Identify if record meets the significant criteria or not: If there was fatality, injury, or total property damage is $50K or more in 1984 dollars, then SIGNIFICANT=’YES’, else SIGNIFICANT=’NO’. | Not on the form
SERIOUS | VARCHAR2 | Identify if record meets the SERIOUS criteria or not: If there was fatality or injury then SERIOUS = ‘YES’ else SERIOUS = ’NO’. | Not on the form
SYSTEM_TYPE | VARCHAR2 | System Type = 'UNGS (Underground Natural Gas Storage)' when Part A14 (SYSTEM_PART_INVOLVED) = 'Belowground Storage, Including Associated Equipment and Piping' and incident date is 01/01/2017 or later. For remaining reports, System Type = 'GT (Gas Transmission)' when Part E9 (PIPELINE_FUNCTION) = Transmission System, Transmission Line of Distribution System, or Transmission in Storage Field. For remaining reports, System Type = 'GG (Gas Gathering)' | Not on the form
REPORT_NUMBER | NUMBER | PHMSA DOT assigned unique identifier for report | Top of first page
SUPPLEMENTAL_NUMBER | NUMBER | PHMSA DOT assigned unique identifier for report submission | Top of first page
REPORT_RECEIVED_DATE | DATE | Date when Original Report submitted | Top of first page
REPORT_TYPE | VARCHAR2 | Report Type (Original, Supplemental, Final) | PART A – KEY REPORT INFORMATION
OPERATOR_ID | NUMBER | Operator's OPS-issued Operator Identification number | PART A – KEY REPORT INFORMATION
NAME | VARCHAR2 | Operator Name | PART A – KEY REPORT INFORMATION
OPERATOR_STREET_ADDRESS | VARCHAR2 | Operator Address - Street | PART A – KEY REPORT INFORMATION
OPERATOR_CITY_NAME | VARCHAR2 | Operator Address - City | PART A – KEY REPORT INFORMATION
OPERATOR_STATE_ABBREVIATION | VARCHAR2 | Operator Address - State | PART A – KEY REPORT INFORMATION
OPERATOR_POSTAL_CODE | VARCHAR2 | Operator Address - Zip | PART A – KEY REPORT INFORMATION
LOCAL_DATETIME | DATE | Local time (24-hr clock) and date of the Incident | PART A – KEY REPORT INFORMATION
IYEAR | NUMBER | Year incident occurred, derived from incident date | Not on the form
TIME_ZONE | VARCHAR2 | Time Zone for local time | PART A – KEY REPORT INFORMATION
DAYLIGHT_SAVINGS_IND | VARCHAR2 | Is Daylight Saving in effect? (Yes/No) | PART A – KEY REPORT INFORMATION
LOCATION_LATITUDE | NUMBER | Incident Location Latitude | PART A – KEY REPORT INFORMATION
LOCATION_LONGITUDE | NUMBER | Incident Location Longitude | PART A – KEY REPORT INFORMATION
NRC_RPT_NUM | VARCHAR2 | National Response Center Report Number | PART A – KEY REPORT INFORMATION
NRC_RPT_DATETIME | DATE | National Response Center time and date of initial telephonic report | PART A – KEY REPORT INFORMATION
ADDITIONAL_NRC_REPORT_NUMBERS | VARCHAR2 | Additional NRC Report numbers submitted by the operator | PART A – KEY REPORT INFORMATION
COMMODITY_RELEASED_TYPE | VARCHAR2 | Type of Gas released (Natural, Propane, Synthetic, Hydrogen, or Other gas) | PART A – KEY REPORT INFORMATION
COMMODITY_DETAILS | VARCHAR2 | Other Commodity Name | PART A – KEY REPORT INFORMATION
UNINTENTIONAL_RELEASE | NUMBER | Estimated volume of gas released unintentionally in Thousand Cubic Feet (MCF) | PART A – KEY REPORT INFORMATION
INTENTIONAL_RELEASE | NUMBER | Estimated volume of intentional and controlled release/blowdown in Thousand Cubic Feet (MCF) | PART A – KEY REPORT INFORMATION
ACCOMPANYING_LIQUID | NUMBER | Estimated volume of accompanying liquid released in Barrels | PART A – KEY REPORT INFORMATION
FATALITY_IND | VARCHAR2 | Fatalities (Yes, No) | PART A – KEY REPORT INFORMATION
NUM_EMP_FATALITIES | NUMBER | Number of Fatalities of Operator Employees | PART A – KEY REPORT INFORMATION
NUM_CONTR_FATALITIES | NUMBER | Number of Fatalities of Contractor Employees working for the Operator | PART A – KEY REPORT INFORMATION
NUM_ER_FATALITIES | NUMBER | Number of Fatalities of Non-Operator emergency responders | PART A – KEY REPORT INFORMATION
NUM_WORKER_FATALITIES | NUMBER | Number of Fatalities of Workers working on the right-of-way, but not associated with this Operator | PART A – KEY REPORT INFORMATION
NUM_GP_FATALITIES | NUMBER | Number of Fatalities of General Public | PART A – KEY REPORT INFORMATION
FATAL | NUMBER | Total number of Fatalities | PART A – KEY REPORT INFORMATION
INJURY_IND | VARCHAR2 | Injuries (Yes, No) | PART A – KEY REPORT INFORMATION
NUM_EMP_INJURIES | NUMBER | Number of Injuries of Operator Employees | PART A – KEY REPORT INFORMATION
NUM_CONTR_INJURIES | NUMBER | Number of Injuries of Contractor Employees working for the Operator | PART A – KEY REPORT INFORMATION
NUM_ER_INJURIES | NUMBER | Number of Injuries of Non-Operator emergency responders | PART A – KEY REPORT INFORMATION
NUM_WORKER_INJURIES | NUMBER | Number of Injuries of Workers working on the right-of-way, but not associated with this Operator | PART A – KEY REPORT INFORMATION
NUM_GP_INJURIES | NUMBER | Number of Injuries of General Public | PART A – KEY REPORT INFORMATION
INJURE | NUMBER | Total number of Injuries | PART A – KEY REPORT INFORMATION
STATUS_WHEN_IDENTIFIED | VARCHAR2 | Operational Status at time Operator identified failure | PART A – KEY REPORT INFORMATION
SHUTDOWN_DUE_ACCIDENT_IND | VARCHAR2 | The pipeline/facility shutdown due to the Incident (Yes, No, Null) | PART A – KEY REPORT INFORMATION
SHUTDOWN_EXPLAIN | VARCHAR2 | if PART A.16 is "No" - The pipeline/facility shutdown due to the Incident - Explain No shutdown | PART A – KEY REPORT INFORMATION
SHUTDOWN_DATETIME | DATE | The pipeline/facility shutdown due to the Incident - Local time and date of shutdown | PART A – KEY REPORT INFORMATION
RESTART_DATETIME | DATE | The pipeline/facility shutdown due to the Incident - Local time pipeline/facility restarted | PART A – KEY REPORT INFORMATION
STILL_SHUTDOWN_IND | VARCHAR2 | The pipeline/facility shutdown due to the Incident - Still shut down (Yes, Null) | PART A – KEY REPORT INFORMATION
COMMUNICATION_STATE_FED_IND | VARCHAR2 | Did the operator communicate with Local, State, or Federal Emergency Responders about the incident? (Yes/No) | PART A – KEY REPORT INFORMATION
PARTY_INITIATED_COMMUNICATION | VARCHAR2 | Which party initiated communication about the incident? (Operator/Local/State/Federal Emergency Responder) | PART A – KEY REPORT INFORMATION
INITIAL_RESPONDER_COM_DATETIME | DATE | Local time of initial Operator and Local/State/Federal Emergency Responder communication (year/month/day/hr) | PART A – KEY REPORT INFORMATION
IGNITE_IND | VARCHAR2 | Commodity ignite (Yes, No) | PART A – KEY REPORT INFORMATION
IGNITE_DATETIME | DATE | If gas ignite, Local time of ignition (year/month/day/hr) | PART A – KEY REPORT INFORMATION
HOW_EXTINGUISHED | VARCHAR2 | How was the fire extinguished? | PART A – KEY REPORT INFORMATION
HOW_EXTINGUISHED_OTHER_DETAIL | VARCHAR2 | If how was the fire extinguished is "Other", specify | PART A – KEY REPORT INFORMATION
GAS_CONSUMED_BY_FIRE_IN_MCF | NUMBER | Estimated volume of gas consumed by fire (in mcf) | PART A – KEY REPORT INFORMATION
EXPLODE_IND | VARCHAR2 | Commodity explode (Yes, No) | PART A – KEY REPORT INFORMATION
UPSTREAM_ACTION_TAKEN | VARCHAR2 | Initial action taken to control flow upstream of failure location | PART A – KEY REPORT INFORMATION
UPSTREAM_OPRTNL_CNTRL_DETAIL | VARCHAR2 | If initial action taken to control flow upstream of failure location is "Operational Control", specify | PART A – KEY REPORT INFORMATION
UPSTREAM_VALVE_CLOSE_DATETIME | DATE | If initial action taken to control flow upstream of failure location is "Valve Closure", provide Local time of final upstream valve closure (year/month/day/hr) | PART A – KEY REPORT INFORMATION
DOWNSTREAM_ACTION_TAKEN | VARCHAR2 | Initial action taken to control flow downstream of failure location | PART A – KEY REPORT INFORMATION
DOWNSTREAM_OPRTNL_CNTRL_DETAIL | VARCHAR2 | If initial action taken to control flow downstream of failure location is "Operational Control", specify | PART A – KEY REPORT INFORMATION
DOWNSTREAM_VLV_CLOSE_DATETIME | DATE | If initial action taken to control flow downstream of failure location is "Valve Closure", provide Local time of final upstream valve closure (year/month/day/hr) | PART A – KEY REPORT INFORMATION
NUM_PUB_EVACUATED | NUMBER | Number of general public evacuated | PART A – KEY REPORT INFORMATION
INCIDENT_IDENTIFIED_DATETIME | DATE | Time sequence - Local time operator identified Incident | PART A – KEY REPORT INFORMATION
ON_SITE_DATETIME | DATE | Time sequence - Local time operator resources arrived on site | PART A – KEY REPORT INFORMATION
ON_OFF_SHORE | VARCHAR2 | Origin of Incident Onshore or Offshore | PART B – ADDITIONAL LOCATION INFORMATION
ONSHORE_STATE_ABBREVIATION | VARCHAR2 | Onshore - State | PART B – ADDITIONAL LOCATION INFORMATION
ONSHORE_POSTAL_CODE | VARCHAR2 | Onshore - Zip Code | PART B – ADDITIONAL LOCATION INFORMATION
ONSHORE_CITY_NAME | VARCHAR2 | Onshore - City | PART B – ADDITIONAL LOCATION INFORMATION
ONSHORE_COUNTY_NAME | VARCHAR2 | Onshore - County or Parish | PART B – ADDITIONAL LOCATION INFORMATION
DESIGNATED_LOCATION | VARCHAR2 | Onshore - Operator-designated location | PART B – ADDITIONAL LOCATION INFORMATION
DESIGNATED_NAME | VARCHAR2 | Onshore - Operator-designated location name | PART B – ADDITIONAL LOCATION INFORMATION
PIPE_FAC_NAME | VARCHAR2 | Onshore - Pipeline/facility name | PART B – ADDITIONAL LOCATION INFORMATION
SEGMENT_NAME | VARCHAR2 | Onshore - Segment Name | PART B – ADDITIONAL LOCATION INFORMATION
FEDERAL | VARCHAR2 | Onshore - Federal land (Yes, No, Null) | PART B – ADDITIONAL LOCATION INFORMATION
LOCATION_TYPE | VARCHAR2 | Onshore - Location of Incident | PART B – ADDITIONAL LOCATION INFORMATION
INCIDENT_AREA_TYPE | VARCHAR2 | Onshore - Area of Incident | PART B – ADDITIONAL LOCATION INFORMATION
INCIDENT_AREA_SUBTYPE | VARCHAR2 | Onshore - Area of Incident Sub-type | PART B – ADDITIONAL LOCATION INFORMATION
INCIDENT_AREA_DETAILS | VARCHAR2 | Onshore - Describe Other Area of Incident | PART B – ADDITIONAL LOCATION INFORMATION
DEPTH_OF_COVER | VARCHAR2 | Onshore Underground - Depth-of-Cover (in) | PART B – ADDITIONAL LOCATION INFORMATION
OTHER_UNDERGROUND_FACILITIES | VARCHAR2 | Area of Incident - Underground - Other, specify | PART B – ADDITIONAL LOCATION INFORMATION
CROSSING | VARCHAR2 | Onshore - Incident occurred in a crossing (Yes, No, Null) | PART B – ADDITIONAL LOCATION INFORMATION
BRIDGE_CROSSING_IND | VARCHAR2 | Onshore - Bridge Crossing (Yes, Null) | PART B – ADDITIONAL LOCATION INFORMATION
BRIDGE_TYPE | VARCHAR2 | Onshore - Bridge Type | PART B – ADDITIONAL LOCATION INFORMATION
RAILROAD_CROSSING_IND | VARCHAR2 | Onshore - Railroad Crossing (Yes, Null) | PART B – ADDITIONAL LOCATION INFORMATION
RAILROAD_TYPE | VARCHAR2 | Onshore - Railroad Type | PART B – ADDITIONAL LOCATION INFORMATION
ROAD_CROSSING_IND | VARCHAR2 | Onshore - Road Crossing (Yes, Null) | PART B – ADDITIONAL LOCATION INFORMATION
ROAD_TYPE | VARCHAR2 | Onshore - Road Type | PART B – ADDITIONAL LOCATION INFORMATION
WATER_CROSSING_IND | VARCHAR2 | Onshore - Water Crossing (Yes, Null) | PART B – ADDITIONAL LOCATION INFORMATION
WATER_TYPE | VARCHAR2 | Onshore - Water Type | PART B – ADDITIONAL LOCATION INFORMATION
WATER_NAME | VARCHAR2 | Onshore - Name of body of water, if commonly known | PART B – ADDITIONAL LOCATION INFORMATION
WATER_DEPTH | VARCHAR2 | Onshore - Approx. water depth (ft) at the point of the Incident | PART B – ADDITIONAL LOCATION INFORMATION
WATER_SUBTYPE | VARCHAR2 | Onshore - Water Crossing Sub-type | PART B – ADDITIONAL LOCATION INFORMATION
CROSSING_100_FEET | VARCHAR2 | Is this water crossing 100 feet or more in length from high water mark to high water mark? (Yes/No) | PART B – ADDITIONAL LOCATION INFORMATION
OFF_WATER_DEPTH | VARCHAR2 | Offshore - Approximate water depth (ft.) | PART B – ADDITIONAL LOCATION INFORMATION
OFF_ACCIDENT_ORIGIN | VARCHAR2 | Offshore - Origin of Incident (State, Outer Continental Shelf=OCS) | PART B – ADDITIONAL LOCATION INFORMATION
OFFSHORE_STATE_ABBREVIATION | VARCHAR2 | Offshore State waters - State | PART B – ADDITIONAL LOCATION INFORMATION
OFF_INSTATE_AREA | VARCHAR2 | Offshore State waters - Area | PART B – ADDITIONAL LOCATION INFORMATION
OFF_INSTATE_BLOCK | VARCHAR2 | Offshore State waters - Block/Tract | PART B – ADDITIONAL LOCATION INFORMATION
OFFSHORE_COUNTY_NAME | VARCHAR2 | Offshore State waters - Nearest County/Parish | PART B – ADDITIONAL LOCATION INFORMATION
OCS_TYPE | VARCHAR2 | On which Outer Continental Shelf (OCS) (Alaska/Gulf of Mexico/Atlantic/Pacific) | PART B – ADDITIONAL LOCATION INFORMATION
OFF_OCS_AREA | VARCHAR2 | Offshore OCS - Area | PART B – ADDITIONAL LOCATION INFORMATION
OFF_OCS_BLOCK | VARCHAR2 | Offshore OCS - Block | PART B – ADDITIONAL LOCATION INFORMATION
OFF_AREA_ACCIDENT_TYPE | VARCHAR2 | Offshore - Area of Incident | PART B – ADDITIONAL LOCATION INFORMATION
PIPE_FACILITY_TYPE | VARCHAR2 | Pipeline/facility Interstate or Intrastate | PART C – ADDITIONAL FACILITY INFORMATION
SYSTEM_PART_INVOLVED | VARCHAR2 | Part of system involved in Incident | PART A – KEY REPORT INFORMATION
ITEM_INVOLVED | VARCHAR2 | Item involved in Incident | PART C – ADDITIONAL FACILITY INFORMATION
PIPE_TYPE | VARCHAR2 | Part of Pipe (Pipe Body, Pipe Seam) | PART C – ADDITIONAL FACILITY INFORMATION
PIPE_DIAMETER | NUMBER | Nominal diameter of Pipe (in) | PART C – ADDITIONAL FACILITY INFORMATION
PUDDLE_WELD_IND | VARCHAR2 | If Item involved in Incident is Pipe Body, was this a Puddle/Spot Weld? (Yes/No) | PART C – ADDITIONAL FACILITY INFORMATION
PIPE_WALL_THICKNESS | VARCHAR2 | Wall thickness (in) | PART C – ADDITIONAL FACILITY INFORMATION
PIPE_SMYS | VARCHAR2 | SMYS (Specified Minimum Yield Strength) of pipe (psi) | PART C – ADDITIONAL FACILITY INFORMATION
PIPE_SPECIFICATION | VARCHAR2 | Pipe specification | PART C – ADDITIONAL FACILITY INFORMATION
PIPE_SEAM_TYPE | VARCHAR2 | Type of Pipe Seam | PART C – ADDITIONAL FACILITY INFORMATION
PIPE_SEAM_DETAILS | VARCHAR2 | Type of Pipe Seam - Pipe Seam Other Details | PART C – ADDITIONAL FACILITY INFORMATION
PIPE_MANUFACTURER | VARCHAR2 | Type of Pipe Seam - Pipe manufacturer | PART C – ADDITIONAL FACILITY INFORMATION
PIPE_COATING_TYPE | VARCHAR2 | Pipeline coating type at point of Incident | PART C – ADDITIONAL FACILITY INFORMATION
PIPE_COATING_DETAILS | VARCHAR2 | Pipeline coating - Other pipeline coating type | PART C – ADDITIONAL FACILITY INFORMATION
COATING_APPLIED_IND | VARCHAR2 | Coating field applied? (Yes/No/Unknown) | PART C – ADDITIONAL FACILITY INFORMATION
PLASTIC_TYPE | VARCHAR2 | If Item involved in Incident is Plastic, specify type | PART C – ADDITIONAL FACILITY INFORMATION
PLASTIC_DETAILS | VARCHAR2 | If Item involved in Incident is Plastic, and type is "Other", specify | PART C – ADDITIONAL FACILITY INFORMATION
PLASTIC_SDR | VARCHAR2 | If Plastic, specify Standard Dimension Ratio (SDR) | PART C – ADDITIONAL FACILITY INFORMATION
WT_PLASTIC | NUMBER | If Plastic, what is wall thickness? | PART C – ADDITIONAL FACILITY INFORMATION
WT_PLASTIC_UNKNOWN_IND | VARCHAR2 | If Plastic, but SDR and wall thickness are "Unknown" | PART C – ADDITIONAL FACILITY INFORMATION
MATERIAL_PE_PIPE_CODE | VARCHAR2 | If Polyethylene (PE) is selected as the type of plastic, specify PE Pipe Material Designation Code | PART C – ADDITIONAL FACILITY INFORMATION
PLASTIC_PE_UNKNOWN_IND | VARCHAR2 | If Polyethylene (PE) is selected as the type of plastic, but PE is "Unknown" | PART C – ADDITIONAL FACILITY INFORMATION
WELD_SUBTYPE | VARCHAR2 | Weld Sub-type | PART C – ADDITIONAL FACILITY INFORMATION
WELD_DETAILS | VARCHAR2 | Other Weld Sub-type Details | PART C – ADDITIONAL FACILITY INFORMATION
DIFFERENT_GIRTH_WELD_IND | VARCHAR2 | Are any of PartC Question3.b through h values different on either side of the girth weld? (Yes/No) | PART C – ADDITIONAL FACILITY INFORMATION
DIFF_GIRTH_WELD_WALL_THICKNESS | NUMBER | PartC Q3.b-h values different, Wall thickness (in) | PART C – ADDITIONAL FACILITY INFORMATION
DIFF_GIRTH_WELD_SMYS | NUMBER | PartC Q3.b-h values different, SMYS (Specified Minimum Yield Strength) of pipe (psi) | PART C – ADDITIONAL FACILITY INFORMATION
DIFF_GIRTH_WELD_SPECIFICATION | VARCHAR2 | PartC Q3.b-h values different, Pipe specification | PART C – ADDITIONAL FACILITY INFORMATION
DIFF_GIRTH_WELD_SEAM_TYPE | VARCHAR2 | PartC Q3.b-h values different, Pipe Seam Type | PART C – ADDITIONAL FACILITY INFORMATION
DIFF_GIRTH_WELD_SEAM_DETAIL | VARCHAR2 | PartC Q3.b-h values different, Pipe Seam Type "Other", specify | PART C – ADDITIONAL FACILITY INFORMATION
DIFF_GIRTH_WELD_MANUFACTURER | VARCHAR2 | PartC Q3.b-h values different, Pipe manufacturer | PART C – ADDITIONAL FACILITY INFORMATION
DIFF_GIRTH_WELD_COATING_TYPE | VARCHAR2 | PartC Q3.b-h values different, Pipeline coating type at point of Accident | PART C – ADDITIONAL FACILITY INFORMATION
DIFF_GIRTH_WELD_COATING_DETAIL | VARCHAR2 | PartC Q3.b-h values different, Pipeline coating type at point of Accident "Other", specify | PART C – ADDITIONAL FACILITY INFORMATION
DIFF_GIRTH_WELD_CTNG_APPLD_IND | VARCHAR2 | PartC Q3.b-h values different, Wall thickness (in) | PART C – ADDITIONAL FACILITY INFORMATION
VALVE_TYPE | VARCHAR2 | Type of Valve | PART C – ADDITIONAL FACILITY INFORMATION
VALVE_MAINLINE_TYPE | VARCHAR2 | Type of Valve - Type of Mainline Valve | PART C – ADDITIONAL FACILITY INFORMATION
VALVE_MAINLINE_DETAILS | VARCHAR2 | Type of Valve - Other Mainline Valve Details | PART C – ADDITIONAL FACILITY INFORMATION
VALVE_MANUFACTURER | VARCHAR2 | Type of Valve - Mainline valve manufacturer | PART C – ADDITIONAL FACILITY INFORMATION
TUBING_MATERIAL | VARCHAR2 | If "Tubing, including Fittings", Tubing, including Fittings, material | PART C – ADDITIONAL FACILITY INFORMATION
TUBING_TYPE | VARCHAR2 | If "Tubing, including Fittings", Tubing, including Fittings, Type of Tubing | PART C – ADDITIONAL FACILITY INFORMATION
ITEM_INVOLVED_DETAILS | VARCHAR2 | Other Item Involved Details | PART C – ADDITIONAL FACILITY INFORMATION
INSTALLATION_YEAR | VARCHAR2 | Year item installed that involved in Incident | PART C – ADDITIONAL FACILITY INFORMATION
MANUFACTURED_YEAR | VARCHAR2 | Year item involved in Incident was manufactured | PART C – ADDITIONAL FACILITY INFORMATION
MATERIAL_INVOLVED | VARCHAR2 | Material involved in Incident | PART C – ADDITIONAL FACILITY INFORMATION
MATERIAL_DETAILS | VARCHAR2 | Material involved - Other Material than Carbon Steel Details | PART C – ADDITIONAL FACILITY INFORMATION
RELEASE_TYPE | VARCHAR2 | Type of Incident involved | PART C – ADDITIONAL FACILITY INFORMATION
PUNCTURE_AXIAL | NUMBER | Mechanical Puncture - Approx. size - Axial (in.) | PART C – ADDITIONAL FACILITY INFORMATION
PUNCTURE_CIRCUM | NUMBER | Mechanical Puncture - Approx. size - Circumferential (in.) | PART C – ADDITIONAL FACILITY INFORMATION
LEAK_TYPE | VARCHAR2 | Leak Type | PART C – ADDITIONAL FACILITY INFORMATION
LEAK_TYPE_OTHER | VARCHAR2 | Leak Type Other Details | PART C – ADDITIONAL FACILITY INFORMATION
RUPTURE_ORIENT | VARCHAR2 | Rupture Orientation (Circumferential, Longitudinal, Other) | PART C – ADDITIONAL FACILITY INFORMATION
RUPTURE_DETAILS | VARCHAR2 | Rupture Orientation Other Details | PART C – ADDITIONAL FACILITY INFORMATION
RUPTURE_LENGTH | NUMBER | Rupture - Approx. size (in.) (length circumferentially or axially) | PART C – ADDITIONAL FACILITY INFORMATION
RUPTURE_WIDTH | NUMBER | Rupture - Approx. size (in.) (widest opening) | PART C – ADDITIONAL FACILITY INFORMATION
RELEASE_TYPE_DETAILS | VARCHAR2 | Type of Incident Other Details | PART C – ADDITIONAL FACILITY INFORMATION
CLASS_LOCATION_TYPE | VARCHAR2 | Type of class location for incident | PART D – ADDITIONAL CONSEQUENCE INFORMATION
COULD_BE_HCA | VARCHAR2 | Incident occurred in High Consequence Area (HCA) (Yes, No) | PART D – ADDITIONAL CONSEQUENCE INFORMATION
DETERMINATION_METHOD | VARCHAR2 | Specific method used to identify the High Consequence Area (HCA) | PART D – ADDITIONAL CONSEQUENCE INFORMATION
PIR_RADIUS | NUMBER | What is the PIR (Potential Impact Radius) for the location of this Incident - Approx. size (feet) | PART D – ADDITIONAL CONSEQUENCE INFORMATION
NOT_FLAMMABLE_IND | VARCHAR2 | Not Flammable (Yes/No) | PART D – ADDITIONAL CONSEQUENCE INFORMATION
HEAT_DAMAGE_IND | VARCHAR2 | Were any structures outside the PIR impacted or otherwise damaged by heat/fire resulting from the Incident (Yes, No) | PART D – ADDITIONAL CONSEQUENCE INFORMATION
NON_HEAT_DAMAGE_IND | VARCHAR2 | Were any structures outside the PIR impacted or otherwise damaged NOT by heat/fire resulting from the Incident (Yes, No) | PART D – ADDITIONAL CONSEQUENCE INFORMATION
HCA_FATALITIES_IND | VARCHAR2 | Were any of the fatalities or injuries reported for persons located outside the PIR (Yes, No) | PART D – ADDITIONAL CONSEQUENCE INFORMATION
FATAL_INJURE_CAUSE | VARCHAR2 | If fatalities or injuries, describe the cause of the fatalities or injuries | PART D – ADDITIONAL CONSEQUENCE INFORMATION
EST_COST_OPER_PAID | NUMBER | Estimated Property Damage - Estimated cost of public and non-Operator private property damage paid/reimbursed by the Operator | PART D – ADDITIONAL CONSEQUENCE INFORMATION
EST_COST_OPER_PAID_CURRENT | NUMBER | Converted Property Damage to Current Year dollars | Not on the form
EST_COST_INTENT_REL | NUMBER | Cost of Gas Released - Estimated cost of gas released during intentional and controlled blowdown | PART D – ADDITIONAL CONSEQUENCE INFORMATION
EST_COST_INTENT_REL_CURRENT | NUMBER | Converted Property Damage to Current Year dollars | Not on the form
EST_COST_GAS_RELEASED | NUMBER | Cost of Gas Released - Estimated cost of gas released unintentionally | PART D – ADDITIONAL CONSEQUENCE INFORMATION
EST_COST_GAS_RELEASED_CURRENT | NUMBER | Converted Property Damage to Current Year dollars | Not on the form
EST_COST_PROP_DAMAGE | NUMBER | Estimated Property Damage - Estimated cost of Operator's property damage & repairs | PART D – ADDITIONAL CONSEQUENCE INFORMATION
EST_COST_PROP_DAMAGE_CURRENT | NUMBER | Converted Property Damage to Current Year dollars | Not on the form
EST_COST_EMERGENCY | NUMBER | Estimated Property Damage - Estimated cost of Operator's emergency response | PART D – ADDITIONAL CONSEQUENCE INFORMATION
EST_COST_EMERGENCY_CURRENT | NUMBER | Converted Property Damage to Current Year dollars | Not on the form
EST_COST_OTHER | NUMBER | Estimated Property Damage - Estimated other costs | PART D – ADDITIONAL CONSEQUENCE INFORMATION
EST_COST_OTHER_CURRENT | NUMBER | Converted Property Damage to Current Year dollars | Not on the form
EST_COST_OTHER_DETAILS | VARCHAR2 | Estimated Property Damage - Estimated other costs details | PART D – ADDITIONAL CONSEQUENCE INFORMATION
GAS_COST_IN_MCF | NUMBER | Cost of Gas Released, Cost of Gas in $ per thousand standard cubic feet (mcf) | PART D – ADDITIONAL CONSEQUENCE INFORMATION
TOTAL_COST | NUMBER | Total of all costs (Sum of EST_COST_OPER_PAID,EST_COST_GAS_RELEASED,EST_COST_INTENT_REL,EST_COST_PROP_DAMAGE,EST_COST_EMERGENC,EST_COST_OTHER) | PART D – ADDITIONAL CONSEQUENCE INFORMATION
TOTAL_COST_IN84 | Number | Converted Property Damage to 1984 dollars | Not on the form
TOTAL_COST_CURRENT | NUMBER | Converted Property Damage to Current Year dollars | Not on the form
NUM_PERSONS_HOSP_NOT_OVNGHT | NUMBER | Estimated number of persons with injuries requiring treatment in a medical facility but not requiring overnight in-patient hospitalization | PART D – ADDITIONAL CONSEQUENCE INFORMATION
NUM_INJURED_TREATED_BY_EMT | NUMBER | Estimated number of persons with injuries requiring treatment by EMTs at the site of incident: | PART D – ADDITIONAL CONSEQUENCE INFORMATION
NUM_RESIDENT_BUILDING_AFFCTD | NUMBER | Number of residential buildings affected (evacuated or required repair or gas service interrupted) | PART D – ADDITIONAL CONSEQUENCE INFORMATION
NUM_BUSINESS_BUILDING_AFFCTD | NUMBER | Number of business buildings affected (evacuated or required repair or gas service interrupted) | PART D – ADDITIONAL CONSEQUENCE INFORMATION
WILDLIFE_IMPACT_IND | VARCHAR2 | Wildlife impact (Yes/No) | PART D – ADDITIONAL CONSEQUENCE INFORMATION
FISH_AQUATIC_IMPACT_IND | VARCHAR2 | Wildlife impact, Fish/aquatic (Yes/No) | PART D – ADDITIONAL CONSEQUENCE INFORMATION
BIRDS_IMPACT_IND | VARCHAR2 | Wildlife impact, Birds (Yes/No) | PART D – ADDITIONAL CONSEQUENCE INFORMATION
TERRESTRIAL_IMPACT_IND | VARCHAR2 | Wildlife impact, Terrestrial (Yes/No) | PART D – ADDITIONAL CONSEQUENCE INFORMATION
ACCIDENT_PSIG | NUMBER | Estimated pressure at the point and time of the Incident (psig) | PART E – ADDITIONAL OPERATING INFORMATION
GAS_FLOW_IN_PIPE_IN_MCF | NUMBER | Estimated gas flow in pipe segment at the point and time of the incident (MSCF/D) | PART E – ADDITIONAL OPERATING INFORMATION
MOP_PSIG | NUMBER | Maximum Operating Pressure (MOP) at the point and time of the Incident (psig) | PART E – ADDITIONAL OPERATING INFORMATION
MOP_CFR_SECTION | VARCHAR2 | Maximum Operating Pressure (MOP) established by 49 CFR section | PART E – ADDITIONAL OPERATING INFORMATION
MOP_CFR_SECTION_DETAILS | VARCHAR2 | Maximum Operating Pressure (MOP) established by 49 CFR section other details | PART E – ADDITIONAL OPERATING INFORMATION
MAOP_ESTABLISHED_DATE | DATE | Date MAOP established | PART E – ADDITIONAL OPERATING INFORMATION
MAOP_REVERSAL_FLOW_IND | VARCHAR2 | Was the MAOP in E2a and b established in conjunction with a reversal of flow direction? (Yes/No/Bi-Directional) | PART E – ADDITIONAL OPERATING INFORMATION
ACCIDENT_PRESSURE | VARCHAR2 | Describe the pressure on the system or facility relating to the Incident (exceed MOP or not) | PART E – ADDITIONAL OPERATING INFORMATION
PRESSURE_RESTRICTION_IND | VARCHAR2 | System or facility relating to the Incident operating under an established pressure restriction with pressure limits below those normally allowed by the MOP (Yes, No, Null) | PART E – ADDITIONAL OPERATING INFORMATION
EXCEED_RESTRICTION_IND | VARCHAR2 | Pressure exceed established pressure restriction (Yes, No, Null) | PART E – ADDITIONAL OPERATING INFORMATION
PHMSA_RESTRICTION_IND | VARCHAR2 | Mandated by (PHMSA, State, Not mandated) | PART E – ADDITIONAL OPERATING INFORMATION
GAS_REQUIRED_ODORIZED_IND | VARCHAR2 | Was the gas at the point of failure required to be odorized in accordance with §192.625? (Yes/No) | PART E – ADDITIONAL OPERATING INFORMATION
GAS_ODORIZED_IND | VARCHAR2 | If the gas at the point of failure required to be odorized in accordance with §192.625, Was the gas at the point of failure odorized in accordance with §192.625? (Yes/No) | PART E – ADDITIONAL OPERATING INFORMATION
UPSTREAM_VALVE_TYPE_IND | VARCHAR2 | Type of upstream valve used to initially isolate release source | PART A – KEY REPORT INFORMATION
DOWNSTREAM_VALVE_TYPE_IND | VARCHAR2 | Type of downstream valve used to initially isolate release source | PART A – KEY REPORT INFORMATION
LENGTH_SEGMENT_ISOLATED | VARCHAR2 | Length of segment initially isolated between valves (ft) | PART E – ADDITIONAL OPERATING INFORMATION
INTERNAL_INSPECTION_IND | VARCHAR2 | Pipeline configured to accommodate internal inspection tools (Yes, No, Null) | PART E – ADDITIONAL OPERATING INFORMATION
DIAMETER_CHANGE_IND | VARCHAR2 | Physical features which limit tool accommodation - Changes in line pipe diameter (Yes, Null) | PART E – ADDITIONAL OPERATING INFORMATION
UNSUITABLE_MAINLINE_IND | VARCHAR2 | Physical features which limit tool accommodation - Presence of unsuitable mainline valves (Yes, Null) | PART E – ADDITIONAL OPERATING INFORMATION
TIGHT_MITERED_IND | VARCHAR2 | Physical features which limit tool accommodation - Tight or mitered pipe bends (Yes, Null) | PART E – ADDITIONAL OPERATING INFORMATION
OTHER_RESTRICTIONS_IND | VARCHAR2 | Physical features which limit tool accommodation - Other passage restrictions (Yes, Null) | PART E – ADDITIONAL OPERATING INFORMATION
EXTRA_THICK_WALL_IND | VARCHAR2 | Physical features which limit tool accommodation - Extra thick pipe wall (Yes, Null) | PART E – ADDITIONAL OPERATING INFORMATION
OTHER_INSPECTION_IND | VARCHAR2 | Physical features which limit tool accommodation - Other (Yes, Null) | PART E – ADDITIONAL OPERATING INFORMATION
INTERNAL_INSPECTION_DETAILS | VARCHAR2 | Physical features which limit tool accommodation - Other physical features Details | PART E – ADDITIONAL OPERATING INFORMATION
OPERATION_COMPLICATIONS_IND | VARCHAR2 | Operational factors which significantly complicate the execution of an internal inspection tool run (Yes, No, Null) | PART E – ADDITIONAL OPERATING INFORMATION
EXCESSIVE_DEBRIS_IND | VARCHAR2 | Operational factors complicate execution - Excessive debris or scale (Yes, Null) | PART E – ADDITIONAL OPERATING INFORMATION
LOW_OP_PRESSURE_IND | VARCHAR2 | Operational factors complicate execution - Low operating pressure(s) (Yes, Null) | PART E – ADDITIONAL OPERATING INFORMATION
LOW_FLOW_IND | VARCHAR2 | Operational factors complicate execution - Low flow or absence of flow (Yes, Null) | PART E – ADDITIONAL OPERATING INFORMATION
INCOMPAT_COMMOD_IND | VARCHAR2 | Operational factors complicate execution - Incompatible commodity (Yes, Null) | PART E – ADDITIONAL OPERATING INFORMATION
OTHER_COMPLICATIONS_IND | VARCHAR2 | Operational factors complicate execution - Other Complications (Yes, Null) | PART E – ADDITIONAL OPERATING INFORMATION
INSPECT_COMP_DETAILS | VARCHAR2 | Operational factors complicate execution - Other Operational factors Details | PART E – ADDITIONAL OPERATING INFORMATION
PIPELINE_FUNCTION | VARCHAR2 | Function of pipeline system | PART E – ADDITIONAL OPERATING INFORMATION
SCADA_IN_PLACE_IND | VARCHAR2 | Supervisory Control and Data Acquisition (SCADA)-based system in place on the pipeline or facility involved in the Incident (Yes, No, Null) | PART E – ADDITIONAL OPERATING INFORMATION
SCADA_OPERATING_IND | VARCHAR2 | SCADA operating at the time of the Incident (Yes, No, Null) | PART E – ADDITIONAL OPERATING INFORMATION
SCADA_FUNCTIONAL_IND | VARCHAR2 | SCADA fully functional at the time of the Incident (Yes, No, Null) | PART E – ADDITIONAL OPERATING INFORMATION
SCADA_DETECTION_IND | VARCHAR2 | SCADA -based information (such as alarm (s), event(s), and/or volume or pack calculations) assist with the detection of the Incident (Yes, No, Null) | PART E – ADDITIONAL OPERATING INFORMATION
SCADA_CONF_IND | VARCHAR2 | SCADA -based information (such as alarm (s), event(s), and/or volume or pack calculations) assist with the confirmation of the Incident (Yes, No, Null) | PART E – ADDITIONAL OPERATING INFORMATION
ACCIDENT_IDENTIFIER | VARCHAR2 | How Incident was identified for the Operator | PART A – KEY REPORT INFORMATION
ACCIDENT_DETAILS | VARCHAR2 | How Incident was identified for the Operator - Other Details | PART A – KEY REPORT INFORMATION
OPERATOR_TYPE | VARCHAR2 | Specify Type of Operator | PART A – KEY REPORT INFORMATION
INVESTIGATION_STATUS | VARCHAR2 | Investigation initiated into whether or not the controller(s) or control room issues were the cause of or a contributing factor to the Incident (Yes, No, Not necessary) | PART E – ADDITIONAL OPERATING INFORMATION
INVESTIGATION_STATUS_DETAILS | VARCHAR2 | Operator did not find that an investigation of the controller(s) actions or control room issues was necessary due to | PART E – ADDITIONAL OPERATING INFORMATION
INVEST_SCHEDULE_IND | VARCHAR2 | Investigation reviewed schedule rotations, continuous hours of service and other factors associated with fatigue (Yes, Null) | PART E – ADDITIONAL OPERATING INFORMATION
INVEST_NO_SCHEDULE_IND | VARCHAR2 | Investigation did NOT reviewed schedule rotations, continuous hours of service and other factors associated with fatigue (Yes, Null) | PART E – ADDITIONAL OPERATING INFORMATION
INVEST_NO_SCHEDULE_IND_DETAILS | VARCHAR2 | Details of Investigation did NOT reviewed schedule rotations, continuous hours of service and other factors associated with fatigue | PART E – ADDITIONAL OPERATING INFORMATION
INVEST_NO_CONTROL_ROOM_IND | VARCHAR2 | Investigation initiated - No control room issues (Yes, Null) | PART E – ADDITIONAL OPERATING INFORMATION
INVEST_NO_CONTROLLER_IND | VARCHAR2 | Investigation initiated - No controller issues (Yes, Null) | PART E – ADDITIONAL OPERATING INFORMATION
INVEST_INCORRECT_ACTION_IND | VARCHAR2 | Investigation initiated - Incorrect controller action or controller error (Yes, Null) | PART E – ADDITIONAL OPERATING INFORMATION
INVEST_FATIGUE_IND | VARCHAR2 | Investigation initiated - That fatigue may have affected the controller(s) involved or impacted the involved controller(s) response (Yes, Null) | PART E – ADDITIONAL OPERATING INFORMATION
INVEST_INCORRECT_PROCEDURE_IND | VARCHAR2 | Investigation initiated - Incorrect procedures (Yes, Null) | PART E – ADDITIONAL OPERATING INFORMATION
INVEST_INCORRECT_CONTROL_IND | VARCHAR2 | Investigation initiated - Incorrect control room equipment operation (Yes, Null) | PART E – ADDITIONAL OPERATING INFORMATION
INVEST_MAINT_IND | VARCHAR2 | Investigation initiated - Maintenance activities that affected control room operations, procedures, and/or controller response (Yes, Null) | PART E – ADDITIONAL OPERATING INFORMATION
INVEST_OTHER_IND | VARCHAR2 | Investigation initiated - Other areas (Yes, Null) | PART E – ADDITIONAL OPERATING INFORMATION
INVEST_OTHER_IND_DETAILS | VARCHAR2 | Investigation initiated - Other areas Details | PART E – ADDITIONAL OPERATING INFORMATION
EMPLOYEE_DRUG_TEST_IND | VARCHAR2 | Operator employees tested under the post-Incident drug and alcohol testing requirements of DOT’s Drug & Alcohol Testing regulations (Yes, No) | PART F – DRUG & ALCOHOL TESTING INFORMATION
NUM_EMPLOYEES_TESTED | NUMBER | Number of employees tested | PART F – DRUG & ALCOHOL TESTING INFORMATION
NUM_EMPLOYEES_FAILED | NUMBER | Number of employees failed | PART F – DRUG & ALCOHOL TESTING INFORMATION
CONTRACTOR_DRUG_TEST_IND | VARCHAR2 | Operator contractor employees tested under the post-Incident drug and alcohol testing requirements of DOT’s Drug & Alcohol Testing regulations (Yes, No) | PART F – DRUG & ALCOHOL TESTING INFORMATION
NUM_CONTRACTORS_TESTED | NUMBER | Number of contractors tested | PART F – DRUG & ALCOHOL TESTING INFORMATION
NUM_CONTRACTORS_FAILED | NUMBER | Number of contractors failed | PART F – DRUG & ALCOHOL TESTING INFORMATION
CAUSE | VARCHAR2 | Apparent Cause of the Incident | PART G – APPARENT CAUSE
CAUSE_DETAILS | VARCHAR2 | Detailed Cause of the Incident | PART G – APPARENT CAUSE
MAP_CAUSE | VARCHAR2 | Cause by PHMSA for 20 year incident trending | Not on the form
MAP_SUBCAUSE | VARCHAR2 | SubCause by PHMSA for 20 year incident trending | Not on the form
INTERNAL_EXTERNAL | VARCHAR2 | Corrosion Failure Sub-Cause (Internal, External) | PART G1 – Corrosion Failure
VISUAL_EXAM_RESULTS | VARCHAR2 | External Corrosion - Visual Examination | PART G1 – Corrosion Failure
VISUAL_EXAM_DETAILS | VARCHAR2 | External Corrosion - Other Visual Examination Details | PART G1 – Corrosion Failure
GALVANIC_CORROSION_IND | VARCHAR2 | External Corrosion Type - Galvanic | PART G1 – Corrosion Failure
ATMOSPHERE_CORROSION_IND | VARCHAR2 | External Corrosion Type - Atmosphere | PART G1 – Corrosion Failure
STRAY_CURRENT_CORROSION_IND | VARCHAR2 | External Corrosion Type - Stray Current | PART G1 – Corrosion Failure
MICROBIOLOGICAL_CORROSION_IND | VARCHAR2 | External Corrosion Type - Microbiological | PART G1 – Corrosion Failure
SELECTIVE_SEAM_CORROSION_IND | VARCHAR2 | External Corrosion Type - Selective Seam | PART G1 – Corrosion Failure
OTHER_CORROSION_IND | VARCHAR2 | External Corrosion Type - Other | PART G1 – Corrosion Failure
CORROSION_TYPE_DETAILS | VARCHAR2 | External Corrosion Type - Other Details | PART G1 – Corrosion Failure
STRAY_CURRENT_TYPE | VARCHAR2 | External Corrosion Type - Stray Current - Specify | PART G1 – Corrosion Failure
STRAY_CURRENT_DETAILS | VARCHAR2 | External Corrosion Type - Stray Current - Describe the stray current source | PART G1 – Corrosion Failure
FIELD_EXAM_BASIS_IND | VARCHAR2 | External Corrosion Type Based on - Field Examination | PART G1 – Corrosion Failure
METALLURGICAL_BASIS_IND | VARCHAR2 | External Corrosion Type Based on - Metallurgical Analysis | PART G1 – Corrosion Failure
OTHER_BASIS_IND | VARCHAR2 | External Corrosion Type Based on - Other Analysis | PART G1 – Corrosion Failure
CORROSION_BASIS_DETAILS | VARCHAR2 | External Corrosion Type Based on - Other Analysis Details | PART G1 – Corrosion Failure
UNDERGROUND_LOCATION | VARCHAR2 | External Corrosion - Failed item buried under the ground (Yes, No, Null) | PART G1 – Corrosion Failure
UNDER_CATHODIC_PROTECTION_IND | VARCHAR2 | Under Cathodic Protection (Yes, No, Null) | PART G1 – Corrosion Failure
CATHODIC_PRO_START_YEAR | VARCHAR2 | Year Cathodic Protection Started | PART G1 – Corrosion Failure
SHIELDING_EVIDENT | VARCHAR2 | Shielding, tenting, or disbonding of coating evident at the point of Incident (Yes, No, Null) | PART G1 – Corrosion Failure
CATHODIC_SURVEY_TYPE | VARCHAR2 | Cathodic Survey Type | PART G1 – Corrosion Failure
CP_ANNUAL_SURVEY_IND | VARCHAR2 | Cathodic Protection Annual Survey | PART G1 – Corrosion Failure
CLOSE_INTERVAL_SURVEY_IND | VARCHAR2 | Close Interval Survey | PART G1 – Corrosion Failure
OTHER_CP_SURVEY_IND | VARCHAR2 | Other Cathodic Protection Survey | PART G1 – Corrosion Failure
OTHER_CP_SURVEY_DETAILS | VARCHAR2 | If one or more Cathodic Protection Survey been conducted at the point of the incident is "Other", Describe other CP survey | PART G1 – Corrosion Failure
CP_ANNUAL_SURVEY_YEAR | NUMBER | the point of the incident? | PART G1 – Corrosion Failure
CLOSE_INTERVAL_SURVEY_YEAR | NUMBER | Close Interval Survey Year | PART G1 – Corrosion Failure
OTHER_CP_SURVEY_YEAR | NUMBER | Other Cathodic Protection Survey Year | PART G1 – Corrosion Failure
EXTERNALLY_COATED | VARCHAR2 | Failed item externally coated or painted | PART G1 – Corrosion Failure
PRIOR_DAMAGE | VARCHAR2 | External Corrosion - Observable damage to the coating or paint in the vicinity of the corrosion | PART G1 – Corrosion Failure
INT_VISUAL_EXAM_RESULTS | VARCHAR2 | Internal Corrosion - Visual Examination Results | PART G1 – Corrosion Failure
INT_VISUAL_EXAM_DETAILS | VARCHAR2 | Internal Corrosion - Other Visual Examination Results Details | PART G1 – Corrosion Failure
INT_CORROSIVE_COMMODITY_IND | VARCHAR2 | Internal Corrosion Cause - Corrosive Commodity | PART G1 – Corrosion Failure
INT_WATER_ACID_IND | VARCHAR2 | Internal Corrosion Cause - Water Acid | PART G1 – Corrosion Failure
INT_MICROBIOLOGICAL_IND | VARCHAR2 | Internal Corrosion Cause - Microbiological | PART G1 – Corrosion Failure
INT_EROSION_IND | VARCHAR2 | Internal Corrosion Cause - Erosion | PART G1 – Corrosion Failure
INT_OTHER_CORROSION_IND | VARCHAR2 | Internal Corrosion Cause - Other | PART G1 – Corrosion Failure
INT_CORROSION_TYPE_DETAILS | VARCHAR2 | Internal Corrosion Cause - Other Details | PART G1 – Corrosion Failure
INT_FIELD_EXAM_BASIS_IND | VARCHAR2 | Internal Corrosion Cause Based on - Field Examination | PART G1 – Corrosion Failure
INT_METALLURGICAL_BASIS_IND | VARCHAR2 | Internal Corrosion Cause Based on - Metallurgical Analysis | PART G1 – Corrosion Failure
INT_OTHER_BASIS_IND | VARCHAR2 | Internal Corrosion Cause Based on - Other Analysis | PART G1 – Corrosion Failure
INT_CORROSION_BASIS_DETAILS | VARCHAR2 | Internal Corrosion Cause Based on - Other Analysis Details | PART G1 – Corrosion Failure
INT_LOW_POINT_PIPE_LOC_IND | VARCHAR2 | Internal Corrosion Location - Low point in pipe | PART G1 – Corrosion Failure
INT_ELBOW_LOC_IND | VARCHAR2 | Internal Corrosion Location - Elbow | PART G1 – Corrosion Failure
INT_DROP_OUT_LOC_IND | VARCHAR2 | Internal Corrosion Location - Drop out | PART G1 – Corrosion Failure
INT_DEAD_LEG_LOC_IND | VARCHAR2 | Internal Corrosion Location - Dead-Leg | PART G1 – Corrosion Failure
INT_OTHER_LOC_IND | VARCHAR2 | Internal Corrosion Location - Other | PART G1 – Corrosion Failure
CORROSION_LOCATION_DETAILS | VARCHAR2 | Internal Corrosion Location - Other Details | PART G1 – Corrosion Failure
CORROSION_INHIBITORS | VARCHAR2 | Internal Corrosion - Commodity treated with corrosion inhibitors or biocides (Yes, No, Null) | PART G1 – Corrosion Failure
CORROSION_LINING | VARCHAR2 | Internal Corrosion - Interior coated or lined with protective coating (Yes, No, Null) | PART G1 – Corrosion Failure
CLEANING_DEWATERING | VARCHAR2 | Internal Corrosion - Cleaning/dewatering pigs (or other operations) routinely utilized (Yes, No, Not applicable) | PART G1 – Corrosion Failure
CORROSION_COUPONS | VARCHAR2 | Internal Corrosion - Corrosion coupons routinely utilized (Yes, No, Not applicable) | PART G1 – Corrosion Failure
NATURAL_FORCE_TYPE | VARCHAR2 | Natural Force Damage Sub-Cause | PART G2 – Natural Force Damage
EARTH_SUBTYPE | VARCHAR2 | Natural Force Damage - Sub-type of Earth Movement, NOT due to Heavy Rains/Floods | PART G2 – Natural Force Damage
HEAVY_RAINS_SUBTYPE | VARCHAR2 | Natural Force Damage - Sub-type of Heavy Rains/Floods | PART G2 – Natural Force Damage
LIGHTNING_SUBTYPE | VARCHAR2 | Natural Force Damage - Sub-type of Lightning | PART G2 – Natural Force Damage
TEMPERATURE_SUBTYPE | VARCHAR2 | Natural Force Damage - Sub-type of Temperature | PART G2 – Natural Force Damage
NF_OTHER_DETAILS | VARCHAR2 | Natural Force Damage - Other Natural Force Damage or Sub-type Details | PART G2 – Natural Force Damage
NF_EXTREME_WEATHER_IND | VARCHAR2 | Natural Force Damage - Natural forces causing incident generated in conjunction with an extreme weather event (Yes, No, Null) | PART G2 – Natural Force Damage
NF_HURRICANE_IND | VARCHAR2 | Extreme weather - Hurricane (Yes, Null) | PART G2 – Natural Force Damage
NF_TROPICAL_STORM_IND | VARCHAR2 | Extreme weather - Tropical Storm (Yes, Null) | PART G2 – Natural Force Damage
NF_TORNADO_IND | VARCHAR2 | Extreme weather - Tornado (Yes, Null) | PART G2 – Natural Force Damage
NF_OTHER_IND | VARCHAR2 | Extreme weather - Other type (Yes, Null) | PART G2 – Natural Force Damage
NF_EXTREME_WEATHER_DETAILS | VARCHAR2 | Extreme weather - Other type Details | PART G2 – Natural Force Damage
PARTY_TYPE | VARCHAR2 | Excavation Damage Sub-Cause | PART G3 – Excavation Damage
PRIOR_NOTIFICATION_IND | VARCHAR2 | Excavation Damage Third Party - Operator got prior notification of the excavation activity (Yes, No, Null) | PART G3 – Excavation Damage
ONE_CALL_SYSTEM_IND | VARCHAR2 | Notification received from One-Call System (Yes, Null) | PART G3 – Excavation Damage
EXCAVATOR_IND | VARCHAR2 | Notification received from Excavator (Yes, Null) | PART G3 – Excavation Damage
CONTRACTOR_IND | VARCHAR2 | Notification received from Contractor (Yes, Null) | PART G3 – Excavation Damage
LANDOWNER_IND | VARCHAR2 | Notification received from Landowner (Yes, Null) | PART G3 – Excavation Damage
STATE_LAW_EXEMPT_IND | VARCHAR2 | Per the primary Incident Investigator results, did State law exempt the excavator from notifying the one-call center? (Yes/No/Unknown) | PART G3 – Excavation Damage
STATE_LAW_EXEMPT_TYPE | VARCHAR2 | If State law exempt the excavator from notifying the one-call center, what was exempt | PART G3 – Excavation Damage
STATE_LAW_EXEMPT_DETAIL | VARCHAR2 | If State law exempt the excavator from notifying the one-call center, and "Other" exempt, specify | PART G3 – Excavation Damage
STATE_LAW_EXEMPT_AUTHORITY | VARCHAR2 | If State law exempt the excavator from notifying the one-call center, Exempting authority | PART G3 – Excavation Damage
STATE_LAW_EXEMPT_CRITERIA | VARCHAR2 | If State law exempt the excavator from notifying the one-call center, Exempting criteria | PART G3 – Excavation Damage
NOTIFY_CGA_DIRT | VARCHAR2 | Excavation Damage CGA-DIRT Program questions - Do you want PHMSA to upload CGA-DIRT Program questions to CGA-DIRT.com (Yes, No, Null) | PART G3 – Excavation Damage
PUBLIC_ROW_IND | VARCHAR2 | Excavation Damage CGA-DIRT Program questions Right-of-Way (RoW) - Public (Yes, Null) | PART G3 – Excavation Damage
PUBLIC_SUBTYPE | VARCHAR2 | Excavation Damage CGA-DIRT Program questions Right-of-Way (RoW) - Public Sub-type | PART G3 – Excavation Damage
PRIVATE_ROW_IND | VARCHAR2 | Excavation Damage CGA-DIRT Program questions Right-of-Way (RoW) - Private (Yes, Null) | PART G3 – Excavation Damage
PRIVATE_SUBTYPE | VARCHAR2 | Excavation Damage CGA-DIRT Program questions Right-of-Way (RoW) - Private Sub-type | PART G3 – Excavation Damage
PIPELINE_EASEMENT_ROW_IND | VARCHAR2 | Excavation Damage CGA-DIRT Program questions Right-of-Way (RoW) - Pipeline Property/Easement (Yes, Null) | PART G3 – Excavation Damage
POWER_TRANSMISSION_ROW_IND | VARCHAR2 | Excavation Damage CGA-DIRT Program questions Right-of-Way (RoW) - Power/Transmission Line (Yes, Null) | PART G3 – Excavation Damage
RAILROAD_ROW_IND | VARCHAR2 | Excavation Damage CGA-DIRT Program questions Right-of-Way (RoW) - Railroad (Yes, Null) | PART G3 – Excavation Damage
PUBLIC_UTIL_EASEMENT_ROW_IND | VARCHAR2 | Excavation Damage CGA-DIRT Program questions Right-of-Way (RoW) - Dedicated Public Utility Easement (Yes, Null) | PART G3 – Excavation Damage
FEDERAL_LAND_ROW_IND | VARCHAR2 | Excavation Damage CGA-DIRT Program questions Right-of-Way (RoW) - Federal Land (Yes, Null) | PART G3 – Excavation Damage
DATA_NOT_COLLECTED_ROW_IND | VARCHAR2 | Excavation Damage CGA-DIRT Program questions Right-of-Way (RoW) - Data not collected (Yes, Null) | PART G3 – Excavation Damage
UNKNOWN_ROW_IND | VARCHAR2 | Excavation Damage CGA-DIRT Program questions Right-of-Way (RoW) - Unknown/Other Row (Yes, Null) | PART G3 – Excavation Damage
EXCAVATOR_TYPE | VARCHAR2 | Excavation Damage CGA-DIRT Program questions - Type of Excavator | PART G3 – Excavation Damage
EXCAVATOR_EQUIPMENT | VARCHAR2 | Excavation Damage CGA-DIRT Program questions - Type of Excavation Equipment | PART G3 – Excavation Damage
WORK_PERFORMED | VARCHAR2 | Excavation Damage CGA-DIRT Program questions - Type of Work Performed | PART G3 – Excavation Damage
ONE_CALL_NOTIFIED_IND | VARCHAR2 | Excavation Damage CGA-DIRT Program questions - One-Call Center notified (Yes, No, Null) | PART G3 – Excavation Damage
ONE_CALL_TICKET_NUM | VARCHAR2 | Ticket Number of One-Call Center | PART G3 – Excavation Damage
ONE_CALL_CENTER_NAME | VARCHAR2 | State where more than a single One-Call Center exists, list name of One-Call Center notified | PART G3 – Excavation Damage
LOCATOR_TYPE | VARCHAR2 | Excavation Damage CGA-DIRT Program questions - Type of Locator | PART G3 – Excavation Damage
VISIBLE_MARKS | VARCHAR2 | Excavation Damage CGA-DIRT Program questions - Facilities marks visible | PART G3 – Excavation Damage
FACILITIES_MARKED | VARCHAR2 | Excavation Damage CGA-DIRT Program questions - Facilities marked correctly | PART G3 – Excavation Damage
SERVICE_INTERRUPTION | VARCHAR2 | Excavation Damage CGA-DIRT Program questions - Damage cause interruption in service | PART G3 – Excavation Damage
SERVICE_INTERRUPTION_HOURS | NUMBER | Duration of the interruption in service (hrs) | PART G3 – Excavation Damage
ROOT_CAUSE | VARCHAR2 | Excavation Damage CGA-DIRT Program questions - Root cause | PART G3 – Excavation Damage
ONE_CALL_SUBTYPE | VARCHAR2 | Excavation Damage CGA-DIRT Program questions - One-Call Notification Practices Not Sufficient Sub-type | PART G3 – Excavation Damage
LOCATING_SUBTYPE | VARCHAR2 | Excavation Damage CGA-DIRT Program questions - Locating Practices Not Sufficient Sub-type | PART G3 – Excavation Damage
EXCAVATION_SUBTYPE | VARCHAR2 | Excavation Damage CGA-DIRT Program questions - Excavation Practices Not Sufficient Sub-type | PART G3 – Excavation Damage
ROOT_CAUSE_OTHER | VARCHAR2 | Excavation Damage CGA-DIRT Program questions - Other Root Cause Details | PART G3 – Excavation Damage
OUTSIDE_FORCE_TYPE | VARCHAR2 | Other Outside Force Damage Sub-Cause | PART G4 – Other Outside Force Damage
VEHICLE_SUBTYPE | VARCHAR2 | Other Outside Force Damage - Vehicle Sub-type | PART G4 – Other Outside Force Damage
OSF_HURRICANE_IND | VARCHAR2 | Other Outside Force Damage Extreme weather - Hurricane (Yes, Null) | PART G4 – Other Outside Force Damage
OSF_TROPICAL_STORM_IND | VARCHAR2 | Other Outside Force Damage Extreme weather - Tropical Storm (Yes, Null) | PART G4 – Other Outside Force Damage
OSF_TORNADO_IND | VARCHAR2 | Other Outside Force Damage Extreme weather - Tornado (Yes, Null) | PART G4 – Other Outside Force Damage
OSF_HEAVY_RAINS_IND | VARCHAR2 | Other Outside Force Damage Extreme weather - Heavy Rains/Flood (Yes, Null) | PART G4 – Other Outside Force Damage
OSF_OTHER_WEATHER_IND | VARCHAR2 | Other Outside Force Damage Extreme weather - Other type (Yes, Null) | PART G4 – Other Outside Force Damage
OSF_OTHER_WEATHER_DETAILS | VARCHAR2 | Other Outside Force Damage Extreme weather - Other type Details | PART G4 – Other Outside Force Damage
INTENTIONAL_SUBTYPE | VARCHAR2 | Other Outside Force Damage - Intentional Damage Sub-type | PART G4 – Other Outside Force Damage
INTENTIONAL_DETAILS | VARCHAR2 | Other Outside Force Damage - Intentional Damage Other Details | PART G4 – Other Outside Force Damage
OSF_OTHER_DETAILS | VARCHAR2 | Other Outside Force Damage - Other Details | PART G4 – Other Outside Force Damage
DRIVER_ISSUED_CITATION_IND | VARCHAR2 | Other Outside Force Damage - Was the driver of the vehicle or equipment issued one or more citations related to the incident? (Yes/No) | PART G4 – Other Outside Force Damage
CITATION_SPEED_IND | VARCHAR2 | Other Outside Force Damage - The nature of the citations - "Excessive Speed" | PART G4 – Other Outside Force Damage
CITATION_RECKLESS_IND | VARCHAR2 | Other Outside Force Damage - The nature of the citations - "Reckless Driving" | PART G4 – Other Outside Force Damage
CITATION_DUI_IND | VARCHAR2 | Other Outside Force Damage - The nature of the citations - "Driving Under the Influence" | PART G4 – Other Outside Force Damage
CITATION_OTHER_IND | VARCHAR2 | Other Outside Force Damage - The nature of the citations - "Other" | PART G4 – Other Outside Force Damage
CITATION_OTHER_DETAIL | VARCHAR2 | Other Outside Force Damage - The nature of the citations - "Other", specify | PART G4 – Other Outside Force Damage
DRIVER_IN_CONTROL_IND | VARCHAR2 | Other Outside Force Damage - Was the driver under control of the vehicle at the time of the collision? (Yes/No/Unknown) | PART G4 – Other Outside Force Damage
ESTIMATED_SPEED | NUMBER | Other Outside Force Damage - Estimated speed of the vehicle at the time of impact (miles per hour) | PART G4 – Other Outside Force Damage
ESTIMATED_SPEED_UNKNOWN_IND | VARCHAR2 | Other Outside Force Damage - Estimated speed of the vehicle at the time of impact (miles per hour), "Unknown" | PART G4 – Other Outside Force Damage
VEHICLE_TYPE | VARCHAR2 | Other Outside Force Damage - Type of vehicle | PART G4 – Other Outside Force Damage
VEHICLE_TRAVEL_FROM | VARCHAR2 | Other Outside Force Damage - Where did the vehicle travel from to hit the pipeline facility? | PART G4 – Other Outside Force Damage
VEHICLE_TRAVEL_DISTANCE_FT | NUMBER | Other Outside Force Damage - Shortest distance from "traveling from" to the damaged pipeline facility (in feet) | PART G4 – Other Outside Force Damage
PROTECTIONS_INSTALLED_IND | VARCHAR2 | Other Outside Force Damage - At the time of the Incident, were protections installed to protect the damaged pipeline facility from vehicular damage? | PART G4 – Other Outside Force Damage
PROTECTION_BOLLARDS_POST_IND | VARCHAR2 | Other Outside Force Damage - Protections installed, type of protection "Bollards/Guard Posts" | PART G4 – Other Outside Force Damage
PROTECTION_BARRICADES_IND | VARCHAR2 | Other Outside Force Damage - Protections installed, type of protection "Barricades – include Jersey barriers and fences in instructions" | PART G4 – Other Outside Force Damage
PROTECTION_GUARD_RAILS_IND | VARCHAR2 | Other Outside Force Damage - Protections installed, type of protection "Guard Rails" | PART G4 – Other Outside Force Damage
PROTECTION_OTHER_IND | VARCHAR2 | Other Outside Force Damage - Protections installed, type of protection "Other" | PART G4 – Other Outside Force Damage
PROTECTION_OTHER_DETAIL | VARCHAR2 | Other Outside Force Damage - Protections installed, type of protection "Other", specify | PART G4 – Other Outside Force Damage
PWJF_FAILURE_TYPE | VARCHAR2 | Material Failure of Pipe or Weld Sub-Cause | PART G5 - Material Failure of Pipe or Weld
FIELD_EXAM_IND | VARCHAR2 | Material Failure of Pipe or Weld sub-cause Based on - Field Examination (Yes, Null) | PART G5 - Material Failure of Pipe or Weld
METALLURGICAL_IND | VARCHAR2 | Material Failure of Pipe or Weld sub-cause Based on - Metallurgical Analysis (Yes, Null) | PART G5 - Material Failure of Pipe or Weld
OTHER_ANALYSIS_IND | VARCHAR2 | Material Failure of Pipe or Weld sub-cause Based on - Other Analysis (Yes, Null) | PART G5 - Material Failure of Pipe or Weld
OTHER_ANALYSIS_DETAILS | VARCHAR2 | Material Failure of Pipe or Weld sub-cause Based on - Other Analysis Details | PART G5 - Material Failure of Pipe or Weld
STILL_UNDER_INVEST_IND | VARCHAR2 | Material Failure of Pipe or Weld - Sub-cause is Tentative or Suspected; Still Under Investigation (Yes, Null) | PART G5 - Material Failure of Pipe or Weld
FATIGUE_VIBR_RELATED_1 | VARCHAR2 | Construction/Installation/Fabrication related - Contributing factors | PART G5 - Material Failure of Pipe or Weld
FAILURE_SUBTYPE_1 | VARCHAR2 | Construction/Installation/Fabrication related - Contributing factors related to Fatigue/Vibration | PART G5 - Material Failure of Pipe or Weld
FATIGUE_VIBR_RELATED_OTHER_1 | VARCHAR2 | Construction/Installation/Fabrication related - Contributing factors related to Fatigue/Vibration Other Details | PART G5 - Material Failure of Pipe or Weld
MECHANICAL_STRESS_1 | VARCHAR2 | Construction/Installation/Fabrication related - Contributing factors related to Mechanical Stress | PART G5 - Material Failure of Pipe or Weld
OTHER_FACTOR_1 | VARCHAR2 | Construction/Installation/Fabrication related - Contributing factors related to Other factors | PART G5 - Material Failure of Pipe or Weld
OTHER_FACTOR_DETAILS_1 | VARCHAR2 | Construction/Installation/Fabrication related - Contributing factors related to Other factors Details | PART G5 - Material Failure of Pipe or Weld
FATIGUE_VIBR_RELATED_2 | VARCHAR2 | Original Manufacturing related (NOT girth weld or other welds formed in the field) - Contributing factors | PART G5 - Material Failure of Pipe or Weld
FAILURE_SUBTYPE_2 | VARCHAR2 | Original Manufacturing related (NOT girth weld or other welds formed in the field) - Contributing factors related to Fatigue/Vibration | PART G5 - Material Failure of Pipe or Weld
FATIGUE_VIBR_RELATED_OTHER_2 | VARCHAR2 | Original Manufacturing related (NOT girth weld or other welds formed in the field) - Contributing factors related to Fatigue/Vibration Other Details | PART G5 - Material Failure of Pipe or Weld
MECHANICAL_STRESS_2 | VARCHAR2 | Original Manufacturing related (NOT girth weld or other welds formed in the field) - Contributing factors related to Mechanical Stress | PART G5 - Material Failure of Pipe or Weld
OTHER_FACTOR_2 | VARCHAR2 | Original Manufacturing related (NOT girth weld or other welds formed in the field) - Contributing factors related to Other factors | PART G5 - Material Failure of Pipe or Weld
OTHER_FACTOR_DETAILS_2 | VARCHAR2 | Original Manufacturing related (NOT girth weld or other welds formed in the field) - Contributing factors related to Other factors Details | PART G5 - Material Failure of Pipe or Weld
STRESS_SUBTYPE | VARCHAR2 | Material Failure of Pipe or Weld related to Environmental Cracking - Stress Sub-type | PART G5 - Material Failure of Pipe or Weld
STRESS_DETAILS | VARCHAR2 | Material Failure of Pipe or Weld related to Environmental Cracking - Stress Sub-type Other Details | PART G5 - Material Failure of Pipe or Weld
ADDITIONAL_DENT_IND | VARCHAR2 | Material Failure of Pipe or Weld Additional factor - Dent | PART G5 - Material Failure of Pipe or Weld
ADDITIONAL_GOUGE_IND | VARCHAR2 | Material Failure of Pipe or Weld Additional factor - Gouge | PART G5 - Material Failure of Pipe or Weld
ADDITIONAL_PIPE_BEND_IND | VARCHAR2 | Material Failure of Pipe or Weld Additional factor - Pipe Bend | PART G5 - Material Failure of Pipe or Weld
ADDITIONAL_ARC_BURN_IND | VARCHAR2 | Material Failure of Pipe or Weld Additional factor - Arc Burn | PART G5 - Material Failure of Pipe or Weld
ADDITIONAL_CRACK_IND | VARCHAR2 | Material Failure of Pipe or Weld Additional factor - Crack | PART G5 - Material Failure of Pipe or Weld
ADDITIONAL_LACK_FUSION_IND | VARCHAR2 | Material Failure of Pipe or Weld Additional factor - Lack of Fusion | PART G5 - Material Failure of Pipe or Weld
ADDITIONAL_LAMINATION_IND | VARCHAR2 | Material Failure of Pipe or Weld Additional factor - Lamination | PART G5 - Material Failure of Pipe or Weld
ADDITIONAL_BUCKLE_IND | VARCHAR2 | Material Failure of Pipe or Weld Additional factor - Buckle | PART G5 - Material Failure of Pipe or Weld
ADDITIONAL_WRINKLE_IND | VARCHAR2 | Material Failure of Pipe or Weld Additional factor - Wrinkle | PART G5 - Material Failure of Pipe or Weld
PWF_ADDITIONAL_MISALIGN_IND | VARCHAR2 | Material Failure of Pipe or Weld Additional factor - Misalignment | PART G5 - Material Failure of Pipe or Weld
ADDITIONAL_BURNT_STEEL_IND | VARCHAR2 | Material Failure of Pipe or Weld Additional factor - Burnt Steel | PART G5 - Material Failure of Pipe or Weld
PWF_ADDITIONAL_OTHER_IND | VARCHAR2 | Material Failure of Pipe or Weld Additional factor - Other | PART G5 - Material Failure of Pipe or Weld
ADDITIONAL_OTHER_DETAILS | VARCHAR2 | Material Failure of Pipe or Weld Additional factor - Other details | PART G5 - Material Failure of Pipe or Weld
POST_CONSTR_PRESSURE_TEST_VAL | VARCHAR2 | Material Failure of Pipe or Weld Additional factor - Post-construction pressure test value (psig) | PART G5 - Material Failure of Pipe or Weld
EQ_FAILURE_TYPE | VARCHAR2 | Equipment Failure Sub-Cause | PART G6 – Equipment Failure
CONTROL_VALVE_IND | VARCHAR2 | Equipment Failure Malfunction of Control/Relief Equipment - Control Valve (Yes, Null) | PART G6 – Equipment Failure
INSTRUMENTATION_IND | VARCHAR2 | Equipment Failure Malfunction of Control/Relief Equipment - Instrumentation (Yes, Null) | PART G6 – Equipment Failure
SCADA_IND | VARCHAR2 | Equipment Failure Malfunction of Control/Relief Equipment - SCADA (Yes, Null) | PART G6 – Equipment Failure
COMMUNICATIONS_IND | VARCHAR2 | Equipment Failure Malfunction of Control/Relief Equipment - Communications (Yes, Null) | PART G6 – Equipment Failure
BLOCK_VALVE_IND | VARCHAR2 | Equipment Failure Malfunction of Control/Relief Equipment - Block Valve (Yes, Null) | PART G6 – Equipment Failure
CHECK_VALVE_IND | VARCHAR2 | Equipment Failure Malfunction of Control/Relief Equipment - Check Valve (Yes, Null) | PART G6 – Equipment Failure
RELIEF_VALVE_IND | VARCHAR2 | Equipment Failure Malfunction of Control/Relief Equipment - Relief Valve (Yes, Null) | PART G6 – Equipment Failure
POWER_FAILURE_IND | VARCHAR2 | Equipment Failure Malfunction of Control/Relief Equipment - Power Failure (Yes, Null) | PART G6 – Equipment Failure
STOPPLE_CONTROL_FITTING_IND | VARCHAR2 | Equipment Failure Malfunction of Control/Relief Equipment - Stopple/Control Fitting (Yes, Null) | PART G6 – Equipment Failure
PRESSURE_REGULATOR_IND | VARCHAR2 | Equipment Failure Malfunction of Control/Relief Equipment - Pressure Regulator (Yes, Null) | PART G6 – Equipment Failure
ESD_SYSTEM_FAILURE_IND | VARCHAR2 | Equipment Failure Malfunction of Control/Relief Equipment - ESD System Failure (Yes, Null) | PART G6 – Equipment Failure
OTHER_CONTROL_RELIEF_IND | VARCHAR2 | Equipment Failure Malfunction of Control/Relief Equipment -Other (Yes, Null) | PART G6 – Equipment Failure
OTHER_CONTROL_RELIEF_DETAILS | VARCHAR2 | Equipment Failure Malfunction of Control/Relief Equipment - Other details | PART G6 – Equipment Failure
OTHER_PUMP_IND | VARCHAR2 | Equipment Failure Pump or Pump-related Equipment - Other Pump (Yes, Null) | PART G6 – Equipment Failure
OTHER_PUMP_DETAILS | VARCHAR2 | Equipment Failure Pump or Pump-related Equipment - Other Pump Details | PART G6 – Equipment Failure
OTHER_STRIPPED_IND | VARCHAR2 | Equipment Failure Threaded Connection/Coupling Failure - Other Stripped (Yes, Null) | PART G6 – Equipment Failure
OTHER_STRIPPED_DETAILS | VARCHAR2 | Equipment Failure Threaded Connection/Coupling Failure - Other Stripped Details | PART G6 – Equipment Failure
OTHER_NON_THREADED_IND | VARCHAR2 | Equipment Failure Non-threaded Connection Failure - Other Non-threaded Connection (Yes, Null) | PART G6 – Equipment Failure
OTHER_NON_THREADED_DETAILS | VARCHAR2 | Equipment Failure Non-threaded Connection Failure - Other Non-threaded Connection Details | PART G6 – Equipment Failure
EQ_FAILURE_DETAILS | VARCHAR2 | Other Equipment Failure - Details | PART G6 – Equipment Failure
ADDITIONAL_VIBRATION_IND | VARCHAR2 | Equipment Failure Additional factor - Excessive vibration (Yes, Null) | PART G6 – Equipment Failure
ADDITIONAL_OVERPRESSURE_IND | VARCHAR2 | Equipment Failure Additional factor - Overpressurization (Yes, Null) | PART G6 – Equipment Failure
ADDITIONAL_SUPPORT_IND | VARCHAR2 | Equipment Failure Additional factor - No support or loss of support (Yes, Null) | PART G6 – Equipment Failure
ADDITIONAL_DEFECT_IND | VARCHAR2 | Equipment Failure Additional factor - Manufacturing defect (Yes, Null) | PART G6 – Equipment Failure
ADDITIONAL_ELECTRICITY_IND | VARCHAR2 | Equipment Failure Additional factor - Loss of electricity (Yes, Null) | PART G6 – Equipment Failure
ADDITIONAL_INSTALLATION_IND | VARCHAR2 | Equipment Failure Additional factor - Improper installation (Yes, Null) | PART G6 – Equipment Failure
ADDITIONAL_IMPROPER_MNTNCE_IND | VARCHAR2 | Equipment Failure Additional factor - Improper maintenance | PART G6 – Equipment Failure
ADDITIONAL_MISMATCH_IND | VARCHAR2 | Equipment Failure Additional factor - Mismatched items (Yes, Null) | PART G6 – Equipment Failure
ADDITIONAL_DISSIMILAR_IND | VARCHAR2 | Equipment Failure Additional factor - Dissimilar metals (Yes, Null) | PART G6 – Equipment Failure
ADDITIONAL_BREAKDOWN_IND | VARCHAR2 | Equipment Failure Additional factor - Breakdown of soft goods (Yes, Null) | PART G6 – Equipment Failure
ADDITIONAL_VALVE_IND | VARCHAR2 | Equipment Failure Additional factor - Valve vault (Yes, Null) | PART G6 – Equipment Failure
ADDITIONAL_ALARM_IND | VARCHAR2 | Equipment Failure Additional factor - Alarm/status failure (Yes, Null) | PART G6 – Equipment Failure
EQ_ADDITIONAL_MISALIGN_IND | VARCHAR2 | Equipment Failure Additional factor - Misalignment (Yes, Null) | PART G6 – Equipment Failure
EQ_ADDITIONAL_THERMAL_IND | VARCHAR2 | Equipment Failure Additional factor - Thermal stress (Yes, Null) | PART G6 – Equipment Failure
ADDITIONAL_EROSION_WEAR_IND | VARCHAR2 | Equipment Failure Additional factor - Erosion/abnormal wear | PART G6 – Equipment Failure
EQ_ADDITIONAL_OTHER_IND | VARCHAR2 | Equipment Failure Additional factor - Other failure (Yes, Null) | PART G6 – Equipment Failure
EQ_ADDITIONAL_OTHER_DETAILS | VARCHAR2 | Equipment Failure Additional factor - Other failure Details | PART G6 – Equipment Failure
OPERATION_TYPE | VARCHAR2 | Incorrect Operation Sub-Cause | PART G7 – Incorrect Operation
OVERFLOW_OTHER_IND | VARCHAR2 | Incorrect Operation - Specify Underground Gas Storage, Pressure Vessel, or Cavern Allowed or Caused to Overpressure | PART G7 – Incorrect Operation
OVERFLOW_OTHER_DETAILS | VARCHAR2 | Incorrect Operation - Other reason of overflow Details | PART G7 – Incorrect Operation
OPERATION_DETAILS | VARCHAR2 | Incorrect Operation - Other Sub-cause Details | PART G7 – Incorrect Operation
RELATED_INADEQUATE_PROC_IND | VARCHAR2 | Incorrect Operation Incident related to - Inadequate procedure (Yes, Null) | PART G7 – Incorrect Operation
RELATED_NO_PROC_IND | VARCHAR2 | Incorrect Operation Incident related to - No procedure established (Yes, Null) | PART G7 – Incorrect Operation
RELATED_FAILURE_FOLLOW_IND | VARCHAR2 | Incorrect Operation Incident related to - Failure to follow procedure (Yes, Null) | PART G7 – Incorrect Operation
RELATED_OTHER_IND | VARCHAR2 | Incorrect Operation Incident related to - Other (Yes, Null) | PART G7 – Incorrect Operation
OPERATION_RELATED_DETAILS | VARCHAR2 | Incorrect Operation Incident related to - Other Details | PART G7 – Incorrect Operation
CATEGORY_TYPE | VARCHAR2 | Incorrect Operation - Category type that caused Incident | PART G7 – Incorrect Operation
OPERATOR_QUALIFICATION_IND | VARCHAR2 | Incorrect Operation - Was the task(s) that led to the Incident identified as a covered task in your Operator Qualification Program (Yes, No, Null) | PART G7 – Incorrect Operation
QUALIFIED_INDIVIDUALS | VARCHAR2 | Individuals performing the task(s) qualified for the task(s) | PART G7 – Incorrect Operation
OTHER_TYPE | VARCHAR2 | Other Incident Cause Sub-Cause | PART G8 – Other Incident Cause
MISC_DETAILS | VARCHAR2 | Other Incident Cause - Miscellaneous Details | PART G8 – Other Incident Cause
UNKNOWN_SUBTYPE | VARCHAR2 | Other Incident Cause - Unknown Sub-type | PART G8 – Other Incident Cause
INCIDENT_UNKNOWN_COMMENTS | VARCHAR2 | Other Incident Cause - Investigation complete, cause of Incident unknown, specify | PART G8 – Other Incident Cause
COLLECTED_DATA_IND | VARCHAR2 | Integrity Inspections - Have internal inspection tools collected data at the point of the Incident? (Yes/No) | PART J – INTEGRITY INSPECTIONS
AXIAL_MAGNETIC_FLX_LKG_IND | VARCHAR2 | Integrity Inspections - Internal inspection tool, "Axial Magnetic Flux Leakage" | PART J – INTEGRITY INSPECTIONS
CIR_TRN_WAVE_MGN_FLX_LKG_IND | VARCHAR2 | Integrity Inspections - Internal inspection tool, "Circumferential/Transverse Wave Magnetic Flux Leakage" | PART J – INTEGRITY INSPECTIONS
ULTRASONIC_IND | VARCHAR2 | Integrity Inspections - Internal inspection tool, "Ultrasonic" | PART J – INTEGRITY INSPECTIONS
GEOMETRY_DEFORMATION_IND | VARCHAR2 | Integrity Inspections - Internal inspection tool, "Geometry/Deformation" | PART J – INTEGRITY INSPECTIONS
EMAT_IND | VARCHAR2 | Integrity Inspections - Internal inspection tool, "Electromagnetic Acoustic Transducer (EMAT)" | PART J – INTEGRITY INSPECTIONS
CPCM_IND | VARCHAR2 | Integrity Inspections - Internal inspection tool, "Cathodic Protection Current Measurement (CPCM)" | PART J – INTEGRITY INSPECTIONS
OTHER_TOOL_TECH_IND | VARCHAR2 | Integrity Inspections - Internal inspection tool, "Other" | PART J – INTEGRITY INSPECTIONS
AXIAL_RECENT_YEAR | NUMBER | Integrity Inspections - "Axial Magnetic Flux Leakage", Most recent run Year | PART J – INTEGRITY INSPECTIONS
AXIAL_RCNT_PROPUL_METHOD | VARCHAR2 | Integrity Inspections - "Axial Magnetic Flux Leakage", Most recent run Propulsion Method | PART J – INTEGRITY INSPECTIONS
AXIAL_RCNT_ATTUNED_DETECT | VARCHAR2 | Integrity Inspections - "Axial Magnetic Flux Leakage", Most recent run Attuned to Detect | PART J – INTEGRITY INSPECTIONS
AXIAL_RCNT_ATND_DTCT_DTLS | VARCHAR2 | Integrity Inspections - "Axial Magnetic Flux Leakage", Most recent run Attuned to Detect, "Other", specify | PART J – INTEGRITY INSPECTIONS
AXIAL_RCNT_ATND_DTCT_METAL | VARCHAR2 | Integrity Inspections - "Axial Magnetic Flux Leakage", Most recent run Attuned to Detect, "Metal Loss", specify | PART J – INTEGRITY INSPECTIONS
AXIAL_RCNT_ATT_DT_METAL_DTLS | VARCHAR2 | Integrity Inspections - "Axial Magnetic Flux Leakage", Most recent run Attuned to Detect, "Other Metal Loss", specify | PART J – INTEGRITY INSPECTIONS
AXIAL_PREVIOUS_YEAR | NUMBER | Integrity Inspections - "Axial Magnetic Flux Leakage", Previous run Year | PART J – INTEGRITY INSPECTIONS
AXIAL_PREV_PROPUL_METHOD | VARCHAR2 | Integrity Inspections - "Axial Magnetic Flux Leakage", Previous run Propulsion Method | PART J – INTEGRITY INSPECTIONS
AXIAL_PREV_ATTUNED_DETECT | VARCHAR2 | Integrity Inspections - "Axial Magnetic Flux Leakage", Previous run Attuned to Detect | PART J – INTEGRITY INSPECTIONS
AXIAL_PREV_ATND_DTCT_DTLS | VARCHAR2 | Integrity Inspections - "Axial Magnetic Flux Leakage", Previous run Attuned to Detect, "Other", specify | PART J – INTEGRITY INSPECTIONS
AXIAL_PREV_ATND_DTCT_METAL | VARCHAR2 | Integrity Inspections - "Axial Magnetic Flux Leakage", Previous run Attuned to Detect, "Metal Loss", specify | PART J – INTEGRITY INSPECTIONS
AXIAL_PREV_ATT_DT_METAL_DTLS | VARCHAR2 | Integrity Inspections - "Axial Magnetic Flux Leakage", Previous run Attuned to Detect, "Other Metal Loss", specify | PART J – INTEGRITY INSPECTIONS
CIRC_WAVE_RECENT_YEAR | NUMBER | Integrity Inspections - "Circumferential/Transverse Wave Magnetic Flux Leakage", Most recent run Year | PART J – INTEGRITY INSPECTIONS
CIRC_WV_RCNT_PROPUL_METHOD | VARCHAR2 | Integrity Inspections - "Circumferential/Transverse Wave Magnetic Flux Leakage", Most recent run Propulsion Method | PART J – INTEGRITY INSPECTIONS
CIRC_WV_RCNT_RESOLUTION | VARCHAR2 | Integrity Inspections - "Circumferential/Transverse Wave Magnetic Flux Leakage", Most recent run Resolution | PART J – INTEGRITY INSPECTIONS
CIRC_WV_RCNT_RESOLUTION_DTLS | VARCHAR2 | Integrity Inspections - "Circumferential/Transverse Wave Magnetic Flux Leakage", Most recent run Resolution, "Other", specify | PART J – INTEGRITY INSPECTIONS
CIRC_WV_PREVIOUS_YEAR | NUMBER | Integrity Inspections - "Circumferential/Transverse Wave Magnetic Flux Leakage", Previous run Year | PART J – INTEGRITY INSPECTIONS
CIRC_WV_PREV_PROPUL_METHOD | VARCHAR2 | Integrity Inspections - "Circumferential/Transverse Wave Magnetic Flux Leakage", Previous run Propulsion Method | PART J – INTEGRITY INSPECTIONS
CIRC_WV_PREV_RESOLUTION | VARCHAR2 | Integrity Inspections - "Circumferential/Transverse Wave Magnetic Flux Leakage", Previous run Resolution | PART J – INTEGRITY INSPECTIONS
CIRC_WV_PREV_RESOLUTION_DTLS | VARCHAR2 | Integrity Inspections - "Circumferential/Transverse Wave Magnetic Flux Leakage", Previous run Resolution, "Other", specify | PART J – INTEGRITY INSPECTIONS
ULTRASONIC_RECENT_YEAR | NUMBER | Integrity Inspections - "Ultrasonic", Most recent run Year | PART J – INTEGRITY INSPECTIONS
ULTRASONIC_RCNT_PROPUL_METHOD | VARCHAR2 | Integrity Inspections - "Ultrasonic", Most recent run Propulsion Method | PART J – INTEGRITY INSPECTIONS
ULTRASONIC_RCNT_ATTUNED | VARCHAR2 | Integrity Inspections - "Ultrasonic", Most recent run Attuned to Detect | PART J – INTEGRITY INSPECTIONS
ULTRA_RCNT_ATTUNEDD_DTLS | VARCHAR2 | Integrity Inspections - "Ultrasonic", Most recent run Attuned to Detect, "Other", specify | PART J – INTEGRITY INSPECTIONS
UTRA_RCNT_ATT_METL_RESOLUTION | VARCHAR2 | Integrity Inspections - "Ultrasonic", If Attuned to Wall Measurement, most recent run Metal Loss Resolution, specify | PART J – INTEGRITY INSPECTIONS
UTRA_RCNT_ATT_METL_RES_DTLS | VARCHAR2 | Integrity Inspections - "Ultrasonic", If Attuned to Wall Measurement, most recent run Metal Loss Resolution, "Other", specify | PART J – INTEGRITY INSPECTIONS
ULTR_PREVIOUS_YEAR | NUMBER | Integrity Inspections - "Ultrasonic", Previous run Year | PART J – INTEGRITY INSPECTIONS
ULTRA_PREV_PROPUL_METHOD | VARCHAR2 | Integrity Inspections - "Ultrasonic", Previous run Propulsion Method | PART J – INTEGRITY INSPECTIONS
ULTRA_PREV_ATTUNED | VARCHAR2 | Integrity Inspections - "Ultrasonic", Previous run Attuned to Detect | PART J – INTEGRITY INSPECTIONS
ULTRA_PREV_ATTUNED_DTLS | VARCHAR2 | Integrity Inspections - "Ultrasonic", Previous run Attuned to Detect, "Other", specify | PART J – INTEGRITY INSPECTIONS
UTRA_PREV_ATT_METL_RESOLUTION | VARCHAR2 | Integrity Inspections - "Ultrasonic", If Attuned to Wall Measurement, Previous run Metal Loss Resolution, specify | PART J – INTEGRITY INSPECTIONS
UTRA_PREV_ATT_METL_RES_DTLS | VARCHAR2 | Integrity Inspections - "Ultrasonic", If Attuned to Wall Measurement, Previous run Metal Loss Resolution, "Other", specify | PART J – INTEGRITY INSPECTIONS
GEOMETRY_RECENT_YEAR | NUMBER | Integrity Inspections - "Geometry/Deformation", Most recent run Year | PART J – INTEGRITY INSPECTIONS
GEOMETRY_RCNT_PROPUL_METHOD | VARCHAR2 | Integrity Inspections - "Geometry/Deformation", Most recent run Propulsion Method | PART J – INTEGRITY INSPECTIONS
GEOMETRY_RCNT_RESOLUTION | VARCHAR2 | Integrity Inspections - "Geometry/Deformation", Most recent run Resolution | PART J – INTEGRITY INSPECTIONS
GEOMETRY_RCNT_RESOLUTION_DTLS | VARCHAR2 | Integrity Inspections - "Geometry/Deformation", Most recent run Resolution, "Other", specify | PART J – INTEGRITY INSPECTIONS
GEOMETRT_RCNT_MEASUR_CUPS | VARCHAR2 | Integrity Inspections - "Geometry/Deformation", Most recent run Measurement Cups | PART J – INTEGRITY INSPECTIONS
GEOMETRY_PREVIOUS_YEAR | NUMBER | Integrity Inspections - "Geometry/Deformation", Previous run Year | PART J – INTEGRITY INSPECTIONS
GEOMETRY_PREV_PROPUL_METHOD | VARCHAR2 | Integrity Inspections - "Geometry/Deformation", Previous run Propulsion Method | PART J – INTEGRITY INSPECTIONS
GEOMETRY_PREV_RESOLUTION | VARCHAR2 | Integrity Inspections - "Geometry/Deformation", Previous run Resolution | PART J – INTEGRITY INSPECTIONS
GEOMETRY_PREV_RESOLUTION_DTLS | VARCHAR2 | Integrity Inspections - "Geometry/Deformation", Previous run Resolution, "Other", specify | PART J – INTEGRITY INSPECTIONS
GEOMETRT_PREV_MEASUR_CUPS | VARCHAR2 | Integrity Inspections - "Geometry/Deformation", Previous run Measurement Cups | PART J – INTEGRITY INSPECTIONS
EMAT_RECENT_YEAR | NUMBER | Integrity Inspections - "Electromagnetic Acoustic Transducer (EMAT)", Most recent run Year | PART J – INTEGRITY INSPECTIONS
EMAT_RCNT_PROPUL_METHOD | VARCHAR2 | Integrity Inspections - "Electromagnetic Acoustic Transducer (EMAT)", Most recent run Propulsion Method | PART J – INTEGRITY INSPECTIONS
EMAT_PREVIOUS_YEAR | NUMBER | Integrity Inspections - "Electromagnetic Acoustic Transducer (EMAT)", Previous run Year | PART J – INTEGRITY INSPECTIONS
EMAT_PREV_PROPUL_METHOD | VARCHAR2 | Integrity Inspections - "Electromagnetic Acoustic Transducer (EMAT)", Previous run Propulsion Method | PART J – INTEGRITY INSPECTIONS
CPCM_RECENT_YEAR | NUMBER | Integrity Inspections - "Cathodic Protection Current Measurement (CPCM)", Most recent run Year | PART J – INTEGRITY INSPECTIONS
CPCM_RCNT_PROPUL_METHOD | VARCHAR2 | Integrity Inspections - "Cathodic Protection Current Measurement (CPCM)", Most recent run Propulsion Method | PART J – INTEGRITY INSPECTIONS
CPCM_PREVIOUS_YEAR | NUMBER | Integrity Inspections - "Cathodic Protection Current Measurement (CPCM)", Previous run Year | PART J – INTEGRITY INSPECTIONS
CPCM_PREV_PROPUL_METHOD | VARCHAR2 | Integrity Inspections - "Cathodic Protection Current Measurement (CPCM)", Previous run Propulsion Method | PART J – INTEGRITY INSPECTIONS
OTHER_TOOL | VARCHAR2 | Integrity Inspections - "Other internal inspection tool", specify | PART J – INTEGRITY INSPECTIONS
OTHER_RECENT_YEAR | NUMBER | Integrity Inspections - "Other internal inspection tool", Most recent run Year | PART J – INTEGRITY INSPECTIONS
OTHER_RCNT_PROPUL_METHOD | VARCHAR2 | Integrity Inspections - "Other internal inspection tool", Most recent run Propulsion Method | PART J – INTEGRITY INSPECTIONS
OTHER_PREVIOUS_YEAR | NUMBER | Integrity Inspections - "Other internal inspection tool", Previous run Year | PART J – INTEGRITY INSPECTIONS
OTHER_PREV_PROPUL_METHOD | VARCHAR2 | Integrity Inspections - "Other internal inspection tool", Previous run Propulsion Method | PART J – INTEGRITY INSPECTIONS
INSP_COMPL_BEFORE_DAMAGE_IND | VARCHAR2 | Integrity Inspections - Do you have reason to believe that the internal inspection was completed BEFORE the damage was sustained? (Yes/No) | PART J – INTEGRITY INSPECTIONS
HAS_HYDRTST_CONDUC_BEFORE_IND | VARCHAR2 | Integrity Inspections - Has one or more hydrotest or other pressure test been conducted since original construction at the point of the Incident? (Yes/No) | PART J – INTEGRITY INSPECTIONS
HYDRTST_MOST_RCNT_YEAR | NUMBER | Integrity Inspections - Hydrotest or other pressure test, Most recent year tested | PART J – INTEGRITY INSPECTIONS
HYDRTST_MOST_RCNT_PRESSURE | NUMBER | Integrity Inspections - Hydrotest or other pressure test, Test pressure (psig) | PART J – INTEGRITY INSPECTIONS
DIRECT_ASMNT_CONDUCTED | VARCHAR2 | Integrity Inspections - Direct Assessment been conducted on the pipeline segment | PART J – INTEGRITY INSPECTIONS
DIRECT_ASMNT_AT_PNT_ACCDNT_YR | NUMBER | Integrity Inspections - Direct Assessment been conducted on the pipeline segment, and an investigative dig was conducted at the point of the Accident, Most recent year conducted | PART J – INTEGRITY INSPECTIONS
DIRECT_ASMNT_PNT_NOT_IDNTF_YR | NUMBER | Integrity Inspections - Direct Assessment been conducted on the pipeline segment, but the point of the Accident was not identified as a dig site, Most recent year conducted | PART J – INTEGRITY INSPECTIONS
ASMNT_ECDA_RCNT_YEAR | NUMBER | Integrity Inspections - The year of the most recent "External Corrosion Direct Assessment (ECDA)" | PART J – INTEGRITY INSPECTIONS
ASMNT_ICDA_RCNT_YEAR | NUMBER | Integrity Inspections - The year of the most recent "Internal Corrosion Direct Assessment (ICDA)" | PART J – INTEGRITY INSPECTIONS
ASMNT_SCCDA_RCNT_YEAR | NUMBER | Integrity Inspections - The year of the most recent "Stress Corrosion Cracking Direct Assessment (SCCDA)" | PART J – INTEGRITY INSPECTIONS
ASMNT_CONFIRMATORY_RCNT_YEAR | NUMBER | Integrity Inspections - The year of the most recent "Confirmatory Direct Assessment" | PART J – INTEGRITY INSPECTIONS
ASMNT_OTHER_TYPE | VARCHAR2 | Integrity Inspections - "Other Assessment", specify | PART J – INTEGRITY INSPECTIONS
ASMNT_OTHER_RCNT_YEAR | NUMBER | Integrity Inspections - The year of the most recent "Other Assessment" | PART J – INTEGRITY INSPECTIONS
ASMNT_ECDA_RCNT_IND | VARCHAR2 | Integrity Inspections - "External Corrosion Direct Assessment (ECDA)" | PART J – INTEGRITY INSPECTIONS
ASMNT_ICDA_RCNT_IND | VARCHAR2 | Integrity Inspections - "Internal Corrosion Direct Assessment (ICDA)" | PART J – INTEGRITY INSPECTIONS
ASMNT_SCCDA_RCNT_IND | VARCHAR2 | Integrity Inspections - "Stress Corrosion Cracking Direct Assessment (SCCDA)" | PART J – INTEGRITY INSPECTIONS
ASMNT_CONFIRMATORY_RCNT_IND | VARCHAR2 | Integrity Inspections - "Confirmatory Direct Assessment" | PART J – INTEGRITY INSPECTIONS
ASMNT_OTHER_RCNT_IND | VARCHAR2 | Integrity Inspections - "Other Assessment" | PART J – INTEGRITY INSPECTIONS
NON_DESTRUCTIVE_EXAM_IND | VARCHAR2 | Integrity Inspections - Has one or more non-destructive examination been conducted prior to the Incident at the point of the Incident since January 1, 2002? (Yes/No) | PART J – INTEGRITY INSPECTIONS
EXM_RADIOGRAPHY_RCNT_YEAR | NUMBER | Integrity Inspections - "Radiography" examination, most recent year the examination was conducted | PART J – INTEGRITY INSPECTIONS
EXM_WAVE_ULTRASONIC_RCNT_YEAR | NUMBER | Integrity Inspections - "Guided Wave Ultrasonic" examination, most recent year the examination was conducted | PART J – INTEGRITY INSPECTIONS
EXM_HANDL_ULTRASONIC_RCNT_YEAR | NUMBER | Integrity Inspections - "Handheld Ultrasonic Tool" examination, most recent year the examination was conducted | PART J – INTEGRITY INSPECTIONS
EXM_WET_MGNT_PARTCL_RCNT_YEAR | NUMBER | Integrity Inspections - "Wet Magnetic Particle Test" examination, most recent year the examination was conducted | PART J – INTEGRITY INSPECTIONS
EXM_DRY_MGNT_PARTCL_RCNT_YEAR | NUMBER | Integrity Inspections - "Dry Magnetic Particle Test" examination, most recent year the examination was conducted | PART J – INTEGRITY INSPECTIONS
EXM_OTHER_TYPE | VARCHAR2 | Integrity Inspections - "Other" type of examination, most recent year the examination was conducted | PART J – INTEGRITY INSPECTIONS
EXM_OTHER_RCNT_YEAR | NUMBER | Integrity Inspections - "Other" type of examination, specify | PART J – INTEGRITY INSPECTIONS
EXM_RADIOGRAPHY_RCNT_IND | VARCHAR2 | Integrity Inspections - "Radiography" examination (Yes/No) | PART J – INTEGRITY INSPECTIONS
EXM_WAVE_ULTRASONIC_RCNT_IND | VARCHAR2 | Integrity Inspections - "Guided Wave Ultrasonic" examination (Yes/No) | PART J – INTEGRITY INSPECTIONS
EXM_HANDL_ULTRASONIC_RCNT_IND | VARCHAR2 | Integrity Inspections - "Handheld Ultrasonic Tool" examination (Yes/No) | PART J – INTEGRITY INSPECTIONS
EXM_WET_MGNT_PARTCL_RCNT_IND | VARCHAR2 | Integrity Inspections - "Wet Magnetic Particle Test" examination (Yes/No) | PART J – INTEGRITY INSPECTIONS
EXM_DRY_MGNT_PARTCL_RCNT_IND | VARCHAR2 | Integrity Inspections - "Dry Magnetic Particle Test" examination (Yes/No) | PART J – INTEGRITY INSPECTIONS
EXM_OTHER_RCNT_IND | VARCHAR2 | Integrity Inspections - "Other" type of examination (Yes/No) | PART J – INTEGRITY INSPECTIONS
EXTRNL_COR_GALVANIC_IND | VARCHAR2 | Contributing Factors - External Corrosion, "Galvanic" | PART K – CONTRIBUTING FACTORS
EXTRNL_COR_ATMOSPHERIC_IND | VARCHAR2 | Contributing Factors - External Corrosion, "Atmospheric" | PART K – CONTRIBUTING FACTORS
EXTRNL_COR_STRAY_CURRENT_IND | VARCHAR2 | Contributing Factors - External Corrosion, "Stray Current Induced" | PART K – CONTRIBUTING FACTORS
EXTRNL_COR_MICROBIOLOGIC_IND | VARCHAR2 | Contributing Factors - External Corrosion, "Microbiologically Induced" | PART K – CONTRIBUTING FACTORS
EXTRNL_COR_SELECTIVE_SEAM_IND | VARCHAR2 | Contributing Factors - External Corrosion, "Selective Seam" | PART K – CONTRIBUTING FACTORS
INTRNL_COR_CORROSIVE_CMDTY_IND | VARCHAR2 | Contributing Factors - Internal Corrosion, "Corrosive Commodity" | PART K – CONTRIBUTING FACTORS
INTRNL_COR_WTR_DRPOUT_ACID_IND | VARCHAR2 | Contributing Factors - Internal Corrosion, "Water drop-out/Acid" | PART K – CONTRIBUTING FACTORS
INTRNL_COR_MICROBIOLOGIC_IND | VARCHAR2 | Contributing Factors - Internal Corrosion, "Microbiological" | PART K – CONTRIBUTING FACTORS
INTRNL_COR_EROSION_IND | VARCHAR2 | Contributing Factors - Internal Corrosion, "Erosion" | PART K – CONTRIBUTING FACTORS
NF_EARTH_MOVEMENT_IND | VARCHAR2 | Contributing Factors - Natural Forces, "Earth Movement, NOT due to Heavy Rains/Floods" | PART K – CONTRIBUTING FACTORS
NF_HEAVY_RAINS_IND | VARCHAR2 | Contributing Factors - Natural Forces, "Heavy Rains/Floods" | PART K – CONTRIBUTING FACTORS
NF_LIGHTNING_IND | VARCHAR2 | Contributing Factors - Natural Forces, "Lightning" | PART K – CONTRIBUTING FACTORS
NF_TEMPERATURE_IND | VARCHAR2 | Contributing Factors - Natural Forces, "Temperature" | PART K – CONTRIBUTING FACTORS
NF_HIGH_WINDS_IND | VARCHAR2 | Contributing Factors - Natural Forces, "High Winds" | PART K – CONTRIBUTING FACTORS
NF_VEGITATION_ROOT_IND | VARCHAR2 | Contributing Factors - Natural Forces, "Tree/Vegetation Root" | PART K – CONTRIBUTING FACTORS
EXCVTN_DMG_OPERATOR_IND | VARCHAR2 | Contributing Factors - "Excavation Damage by Operator (First Party)" | PART K – CONTRIBUTING FACTORS
EXCVTN_DMG_OP_CONTRACTOR_IND | VARCHAR2 | Contributing Factors - "Excavation Damage by Operator’s Contractor (Second Party)" | PART K – CONTRIBUTING FACTORS
EXCVTN_DMG_THIRD_PARTY_IND | VARCHAR2 | Contributing Factors - "Excavation Damage by Third Party" | PART K – CONTRIBUTING FACTORS
EXCVTN_DMG_PREVIOUS_DAMAGE_IND | VARCHAR2 | Contributing Factors - "Previous Damage due to Excavation Activit"y | PART K – CONTRIBUTING FACTORS
OSF_NEARBY_INDUSTRIAL_IND | VARCHAR2 | Contributing Factors - Other Outside Force, "Nearby Industrial, Man-made, or Other Fire/Explosion" | PART K – CONTRIBUTING FACTORS
OSF_VEHICLE_IND | VARCHAR2 | Contributing Factors - Other Outside Force, "Damage by Car, Truck, or Other Motorized Vehicle/Equipment NOT Engaged in Excavation" | PART K – CONTRIBUTING FACTORS
OSF_BOAT_IND | VARCHAR2 | Contributing Factors - Other Outside Force, "Damage by Boats, Barges, Drilling Rigs, or Other Adrift Maritime Equipment" | PART K – CONTRIBUTING FACTORS
OSF_OTHER_MARITIME_IND | VARCHAR2 | Contributing Factors - Other Outside Force, "Routine or Normal Fishing or Other Maritime Activity NOT Engaged in Excavation" | PART K – CONTRIBUTING FACTORS
OSF_ELECTRICAL_ARCING_IND | VARCHAR2 | Contributing Factors - Other Outside Force, "Electrical Arcing from Other Equipment or Facility" | PART K – CONTRIBUTING FACTORS
OSF_PREVOUS_MACHANICAL_IND | VARCHAR2 | Contributing Factors - Other Outside Force, "Previous Mechanical Damage NOT Related to Excavation" | PART K – CONTRIBUTING FACTORS
OSF_INTENTIONAL_IND | VARCHAR2 | Contributing Factors - Other Outside Force, "Intentional Damage" | PART K – CONTRIBUTING FACTORS
OSF_OTHER_UNDERGROUND_IND | VARCHAR2 | Contributing Factors - Other Outside Force, "Other underground facilities buried within 12 inches of the failure location" | PART K – CONTRIBUTING FACTORS
PWF_DESIGN_IND | VARCHAR2 | Contributing Factors - Pipe/Weld Failure, "Design-related" | PART K – CONTRIBUTING FACTORS
PWF_CONSTRUCTION_IND | VARCHAR2 | Contributing Factors - Pipe/Weld Failure, "Construction-related" | PART K – CONTRIBUTING FACTORS
PWF_INSTALLATION_IND | VARCHAR2 | Contributing Factors - Pipe/Weld Failure, "Installation-related" | PART K – CONTRIBUTING FACTORS
PWF_FABRICATION_IND | VARCHAR2 | Contributing Factors - Pipe/Weld Failure, "Fabrication-related" | PART K – CONTRIBUTING FACTORS
PWF_MANUFACTURING_IND | VARCHAR2 | Contributing Factors - Pipe/Weld Failure, "Original Manufacturing-related" | PART K – CONTRIBUTING FACTORS
PWF_ENV_STRESS_CORROSION_IND | VARCHAR2 | Contributing Factors - Pipe/Weld Failure, "Environmental Cracking-related, Stress Corrosion Cracking" | PART K – CONTRIBUTING FACTORS
PWF_ENV_SULFIDE_STRESS_IND | VARCHAR2 | Contributing Factors - Pipe/Weld Failure, "Environmental Cracking-related, Sulfide Stress Cracking" | PART K – CONTRIBUTING FACTORS
PWF_ENV_HYDROGEN_STRESS_IND | VARCHAR2 | Contributing Factors - Pipe/Weld Failure, "Environmental Cracking-related, Hydrogen Stress Cracking" | PART K – CONTRIBUTING FACTORS
PWF_ENV_HARD_SPOT_IND | VARCHAR2 | Contributing Factors - Pipe/Weld Failure, "Environmental Cracking-related, Hard Spot" | PART K – CONTRIBUTING FACTORS
EQF_CONTROL_RELEAF_IND | VARCHAR2 | Contributing Factors - Equipment Failure, "Malfunction of Control/Relief Equipment" | PART K – CONTRIBUTING FACTORS
EQF_COMPRESSOR_IND | VARCHAR2 | Contributing Factors - Equipment Failure, "Compressor or Compressor-related Equipment" | PART K – CONTRIBUTING FACTORS
EQF_THREADED_COUPLING_IND | VARCHAR2 | Contributing Factors - Equipment Failure, "Threaded Connection/Coupling Failure" | PART K – CONTRIBUTING FACTORS
EQF_NON_THREADED_IND | VARCHAR2 | Contributing Factors - Equipment Failure, "Non-threaded Connection Failure" | PART K – CONTRIBUTING FACTORS
EQF_DEFECTIVE_FITTING_IND | VARCHAR2 | Contributing Factors - Equipment Failure, "Defective or Loose Tubing or Fitting" | PART K – CONTRIBUTING FACTORS
EQF_EQUIPMENT_BODY_IND | VARCHAR2 | Contributing Factors - Equipment Failure, "Failure of Equipment Body (except Compressor), Vessel Plate, or other Material" | PART K – CONTRIBUTING FACTORS
IO_DAMAGE_BY_OPERATOR_IND | VARCHAR2 | Contributing Factors - Incorrect Operation, "Damage by Operator or Operator’s Contractor NOT Excavation and NOT Vehicle/Equipment Damage" | PART K – CONTRIBUTING FACTORS
IO_VALVE_POSITION_IND | VARCHAR2 | Contributing Factors - Incorrect Operation, "Valve Left or Placed in Wrong Position, but NOT Resulting in Overpressure" | PART K – CONTRIBUTING FACTORS
IO_EQUIPMENT_OVERPRESSURE_IND | VARCHAR2 | Contributing Factors - Incorrect Operation, "Pipeline or Equipment Overpressured" | PART K – CONTRIBUTING FACTORS
IO_NOT_INSTALLED_PROPERLY_IND | VARCHAR2 | Contributing Factors - Incorrect Operation, "Equipment Not Installed Properly" | PART K – CONTRIBUTING FACTORS
IO_WRONG_EQUIPMENT_IND | VARCHAR2 | Contributing Factors - Incorrect Operation, "Wrong Equipment Specified or Installed" | PART K – CONTRIBUTING FACTORS
IO_INADEQUATE_PROCEDURE_IND | VARCHAR2 | Contributing Factors - Incorrect Operation, "Inadequate Procedure" | PART K – CONTRIBUTING FACTORS
IO_NO_PROCEDURE_IND | VARCHAR2 | Contributing Factors - Incorrect Operation, "No procedure established" | PART K – CONTRIBUTING FACTORS
IO_FOLLOW_PROCEDURE_IND | VARCHAR2 | Contributing Factors - Incorrect Operation, "Failure to follow procedures" | PART K – CONTRIBUTING FACTORS
PREPARER_NAME | VARCHAR2 | Name of Operator's preparer | PART I – PREPARER AND AUTHORIZED PERSON
PREPARER_TITLE | VARCHAR2 | Title of Operator's preparer | PART I – PREPARER AND AUTHORIZED PERSON
PREPARER_EMAIL | VARCHAR2 | Email of Operator's preparer | PART I – PREPARER AND AUTHORIZED PERSON
PREPARER_TELEPHONE | VARCHAR2 | Telephone number of Operator's preparer | PART I – PREPARER AND AUTHORIZED PERSON
PREPARER_FAX | VARCHAR2 | Fax Number of Operator's preparer | PART I – PREPARER AND AUTHORIZED PERSON
LOCAL_CONTACT_NAME | VARCHAR2 | Local Contact Name | PART I – PREPARER AND AUTHORIZED PERSON
LOCAL_CONTACT_EMAIL | VARCHAR2 | Local Contact Email | PART I – PREPARER AND AUTHORIZED PERSON
LOCAL_CONTACT_TELEPHONE | VARCHAR2 | Local Contact Phone | PART I – PREPARER AND AUTHORIZED PERSON
AUTHORIZER_NAME | VARCHAR2 | Name of Operator's Authorizer | PART I – PREPARER AND AUTHORIZED PERSON
AUTHORIZER_TITLE | VARCHAR2 | Title of Operator's Authorizer | PART I – PREPARER AND AUTHORIZED PERSON
AUTHORIZER_TELEPHONE | VARCHAR2 | Telephone number of Operator's Authorizer | PART I – PREPARER AND AUTHORIZED PERSON
AUTHORIZER_EMAIL | VARCHAR2 | Email of Operator's Authorizer | PART I – PREPARER AND AUTHORIZED PERSON
NARRATIVE | VARCHAR2 | Narrative description of the incident | PART H – NARRATIVE DESCRIPTION OF THE INCIDENT

## gtggungs2010toPresent
DATAFILE_AS_OF | SIGNIFICANT | SERIOUS | SYSTEM_TYPE | REPORT_NUMBER | SUPPLEMENTAL_NUMBER | REPORT_RECEIVED_DATE | REPORT_TYPE | OPERATOR_ID | NAME | OPERATOR_STREET_ADDRESS | OPERATOR_CITY_NAME | OPERATOR_STATE_ABBREVIATION | OPERATOR_POSTAL_CODE | LOCAL_DATETIME | IYEAR | TIME_ZONE | DAYLIGHT_SAVINGS_IND | LOCATION_LATITUDE | LOCATION_LONGITUDE | NRC_RPT_NUM | NRC_RPT_DATETIME | ADDITIONAL_NRC_REPORT_NUMBERS | COMMODITY_RELEASED_TYPE | COMMODITY_DETAILS | UNINTENTIONAL_RELEASE | INTENTIONAL_RELEASE | ACCOMPANYING_LIQUID | FATALITY_IND | NUM_EMP_FATALITIES | NUM_CONTR_FATALITIES | NUM_ER_FATALITIES | NUM_WORKER_FATALITIES | NUM_GP_FATALITIES | FATAL | INJURY_IND | NUM_EMP_INJURIES | NUM_CONTR_INJURIES | NUM_ER_INJURIES | NUM_WORKER_INJURIES | NUM_GP_INJURIES | INJURE | STATUS_WHEN_IDENTIFIED | SHUTDOWN_DUE_ACCIDENT_IND | SHUTDOWN_EXPLAIN | SHUTDOWN_DATETIME | RESTART_DATETIME | STILL_SHUTDOWN_IND | COMMUNICATION_STATE_FED_IND | PARTY_INITIATED_COMMUNICATION | INITIAL_RESPONDER_COM_DATETIME | IGNITE_IND | IGNITE_DATETIME | HOW_EXTINGUISHED | HOW_EXTINGUISHED_OTHER_DETAIL | GAS_CONSUMED_BY_FIRE_IN_MCF | EXPLODE_IND | UPSTREAM_ACTION_TAKEN | UPSTREAM_OPRTNL_CNTRL_DETAIL | UPSTREAM_VALVE_CLOSE_DATETIME | DOWNSTREAM_ACTION_TAKEN | DOWNSTREAM_OPRTNL_CNTRL_DETAIL | DOWNSTREAM_VLV_CLOSE_DATETIME | NUM_PUB_EVACUATED | INCIDENT_IDENTIFIED_DATETIME | ON_SITE_DATETIME | ON_OFF_SHORE | ONSHORE_STATE_ABBREVIATION | ONSHORE_POSTAL_CODE | ONSHORE_CITY_NAME | ONSHORE_COUNTY_NAME | DESIGNATED_LOCATION | DESIGNATED_NAME | PIPE_FAC_NAME | SEGMENT_NAME | FEDERAL | LOCATION_TYPE | INCIDENT_AREA_TYPE | INCIDENT_AREA_SUBTYPE | INCIDENT_AREA_DETAILS | DEPTH_OF_COVER | OTHER_UNDERGROUND_FACILITIES | CROSSING | BRIDGE_CROSSING_IND | BRIDGE_TYPE | RAILROAD_CROSSING_IND | RAILROAD_TYPE | ROAD_CROSSING_IND | ROAD_TYPE | WATER_CROSSING_IND | WATER_TYPE | WATER_NAME | WATER_DEPTH | WATER_SUBTYPE | CROSSING_100_FEET | OFF_WATER_DEPTH | OFF_ACCIDENT_ORIGIN | OFFSHORE_STATE_ABBREVIATION | OFF_INSTATE_AREA | OFF_INSTATE_BLOCK | OFFSHORE_COUNTY_NAME | OCS_TYPE | OFF_OCS_AREA | OFF_OCS_BLOCK | OFF_AREA_ACCIDENT_TYPE | PIPE_FACILITY_TYPE | SYSTEM_PART_INVOLVED | ITEM_INVOLVED | PIPE_TYPE | PIPE_DIAMETER | PUDDLE_WELD_IND | PIPE_WALL_THICKNESS | PIPE_SMYS | PIPE_SPECIFICATION | PIPE_SEAM_TYPE | PIPE_SEAM_DETAILS | PIPE_MANUFACTURER | PIPE_COATING_TYPE | PIPE_COATING_DETAILS | COATING_APPLIED_IND | PLASTIC_TYPE | PLASTIC_DETAILS | PLASTIC_SDR | WT_PLASTIC | WT_PLASTIC_UNKNOWN_IND | MATERIAL_PE_PIPE_CODE | PLASTIC_PE_UNKNOWN_IND | WELD_SUBTYPE | WELD_DETAILS | DIFFERENT_GIRTH_WELD_IND | DIFF_GIRTH_WELD_WALL_THICKNESS | DIFF_GIRTH_WELD_SMYS | DIFF_GIRTH_WELD_SPECIFICATION | DIFF_GIRTH_WELD_SEAM_TYPE | DIFF_GIRTH_WELD_SEAM_DETAIL | DIFF_GIRTH_WELD_MANUFACTURER | DIFF_GIRTH_WELD_COATING_TYPE | DIFF_GIRTH_WELD_COATING_DETAIL | DIFF_GIRTH_WELD_CTNG_APPLD_IND | VALVE_TYPE | VALVE_MAINLINE_TYPE | VALVE_MAINLINE_DETAILS | VALVE_MANUFACTURER | TUBING_MATERIAL | TUBING_TYPE | ITEM_INVOLVED_DETAILS | INSTALLATION_YEAR | MANUFACTURED_YEAR | MATERIAL_INVOLVED | MATERIAL_DETAILS | RELEASE_TYPE | PUNCTURE_AXIAL | PUNCTURE_CIRCUM | LEAK_TYPE | LEAK_TYPE_OTHER | RUPTURE_ORIENT | RUPTURE_DETAILS | RUPTURE_LENGTH | RUPTURE_WIDTH | RELEASE_TYPE_DETAILS | CLASS_LOCATION_TYPE | COULD_BE_HCA | DETERMINATION_METHOD | PIR_RADIUS | NOT_FLAMMABLE_IND | HEAT_DAMAGE_IND | NON_HEAT_DAMAGE_IND | HCA_FATALITIES_IND | FATAL_INJURE_CAUSE | EST_COST_OPER_PAID | EST_COST_OPER_PAID_CURRENT | EST_COST_INTENT_REL | EST_COST_INTENT_REL_CURRENT | EST_COST_GAS_RELEASED | EST_COST_GAS_RELEASED_CURRENT | EST_COST_PROP_DAMAGE | EST_COST_PROP_DAMAGE_CURRENT | EST_COST_EMERGENCY | EST_COST_EMERGENCY_CURRENT | EST_COST_OTHER | EST_COST_OTHER_CURRENT | EST_COST_OTHER_DETAILS | GAS_COST_IN_MCF | TOTAL_COST | TOTAL_COST_IN84 | TOTAL_COST_CURRENT | NUM_PERSONS_HOSP_NOT_OVNGHT | NUM_INJURED_TREATED_BY_EMT | NUM_RESIDENT_BUILDING_AFFCTD | NUM_BUSINESS_BUILDING_AFFCTD | WILDLIFE_IMPACT_IND | FISH_AQUATIC_IMPACT_IND | BIRDS_IMPACT_IND | TERRESTRIAL_IMPACT_IND | ACCIDENT_PSIG | GAS_FLOW_IN_PIPE_IN_MCF | MOP_PSIG | MOP_CFR_SECTION | MOP_CFR_SECTION_DETAILS | MAOP_ESTABLISHED_DATE | MAOP_REVERSAL_FLOW_IND | ACCIDENT_PRESSURE | PRESSURE_RESTRICTION_IND | EXCEED_RESTRICTION_IND | PHMSA_RESTRICTION_IND | GAS_REQUIRED_ODORIZED_IND | GAS_ODORIZED_IND | UPSTREAM_VALVE_TYPE_IND | DOWNSTREAM_VALVE_TYPE_IND | LENGTH_SEGMENT_ISOLATED | INTERNAL_INSPECTION_IND | DIAMETER_CHANGE_IND | UNSUITABLE_MAINLINE_IND | TIGHT_MITERED_IND | OTHER_RESTRICTIONS_IND | EXTRA_THICK_WALL_IND | OTHER_INSPECTION_IND | INTERNAL_INSPECTION_DETAILS | OPERATION_COMPLICATIONS_IND | EXCESSIVE_DEBRIS_IND | LOW_OP_PRESSURE_IND | LOW_FLOW_IND | INCOMPAT_COMMOD_IND | OTHER_COMPLICATIONS_IND | INSPECT_COMP_DETAILS | PIPELINE_FUNCTION | SCADA_IN_PLACE_IND | SCADA_OPERATING_IND | SCADA_FUNCTIONAL_IND | SCADA_DETECTION_IND | SCADA_CONF_IND | ACCIDENT_IDENTIFIER | ACCIDENT_DETAILS | OPERATOR_TYPE | INVESTIGATION_STATUS | INVESTIGATION_STATUS_DETAILS | INVEST_SCHEDULE_IND | INVEST_NO_SCHEDULE_IND | INVEST_NO_SCHEDULE_IND_DETAILS | INVEST_NO_CONTROL_ROOM_IND | INVEST_NO_CONTROLLER_IND | INVEST_INCORRECT_ACTION_IND | INVEST_FATIGUE_IND | INVEST_INCORRECT_PROCEDURE_IND | INVEST_INCORRECT_CONTROL_IND | INVEST_MAINT_IND | INVEST_OTHER_IND | INVEST_OTHER_IND_DETAILS | EMPLOYEE_DRUG_TEST_IND | NUM_EMPLOYEES_TESTED | NUM_EMPLOYEES_FAILED | CONTRACTOR_DRUG_TEST_IND | NUM_CONTRACTORS_TESTED | NUM_CONTRACTORS_FAILED | CAUSE | CAUSE_DETAILS | MAP_CAUSE | MAP_SUBCAUSE | INTERNAL_EXTERNAL | VISUAL_EXAM_RESULTS | VISUAL_EXAM_DETAILS | GALVANIC_CORROSION_IND | ATMOSPHERE_CORROSION_IND | STRAY_CURRENT_CORROSION_IND | MICROBIOLOGICAL_CORROSION_IND | SELECTIVE_SEAM_CORROSION_IND | OTHER_CORROSION_IND | CORROSION_TYPE_DETAILS | STRAY_CURRENT_TYPE | STRAY_CURRENT_DETAILS | FIELD_EXAM_BASIS_IND | METALLURGICAL_BASIS_IND | OTHER_BASIS_IND | CORROSION_BASIS_DETAILS | UNDERGROUND_LOCATION | UNDER_CATHODIC_PROTECTION_IND | CATHODIC_PRO_START_YEAR | SHIELDING_EVIDENT | CATHODIC_SURVEY_TYPE | CP_ANNUAL_SURVEY_IND | CLOSE_INTERVAL_SURVEY_IND | OTHER_CP_SURVEY_IND | OTHER_CP_SURVEY_DETAILS | CP_ANNUAL_SURVEY_YEAR | CLOSE_INTERVAL_SURVEY_YEAR | OTHER_CP_SURVEY_YEAR | EXTERNALLY_COATED | PRIOR_DAMAGE | INT_VISUAL_EXAM_RESULTS | INT_VISUAL_EXAM_DETAILS | INT_CORROSIVE_COMMODITY_IND | INT_WATER_ACID_IND | INT_MICROBIOLOGICAL_IND | INT_EROSION_IND | INT_OTHER_CORROSION_IND | INT_CORROSION_TYPE_DETAILS | INT_FIELD_EXAM_BASIS_IND | INT_METALLURGICAL_BASIS_IND | INT_OTHER_BASIS_IND | INT_CORROSION_BASIS_DETAILS | INT_LOW_POINT_PIPE_LOC_IND | INT_ELBOW_LOC_IND | INT_DROP_OUT_LOC_IND | INT_DEAD_LEG_LOC_IND | INT_OTHER_LOC_IND | CORROSION_LOCATION_DETAILS | CORROSION_INHIBITORS | CORROSION_LINING | CLEANING_DEWATERING | CORROSION_COUPONS | NATURAL_FORCE_TYPE | EARTH_SUBTYPE | HEAVY_RAINS_SUBTYPE | LIGHTNING_SUBTYPE | TEMPERATURE_SUBTYPE | NF_OTHER_DETAILS | NF_EXTREME_WEATHER_IND | NF_HURRICANE_IND | NF_TROPICAL_STORM_IND | NF_TORNADO_IND | NF_OTHER_IND | NF_EXTREME_WEATHER_DETAILS | PARTY_TYPE | PRIOR_NOTIFICATION_IND | ONE_CALL_SYSTEM_IND | EXCAVATOR_IND | CONTRACTOR_IND | LANDOWNER_IND | STATE_LAW_EXEMPT_IND | STATE_LAW_EXEMPT_TYPE | STATE_LAW_EXEMPT_DETAIL | STATE_LAW_EXEMPT_AUTHORITY | STATE_LAW_EXEMPT_CRITERIA | NOTIFY_CGA_DIRT | PUBLIC_ROW_IND | PUBLIC_SUBTYPE | PRIVATE_ROW_IND | PRIVATE_SUBTYPE | PIPELINE_EASEMENT_ROW_IND | POWER_TRANSMISSION_ROW_IND | RAILROAD_ROW_IND | PUBLIC_UTIL_EASEMENT_ROW_IND | FEDERAL_LAND_ROW_IND | DATA_NOT_COLLECTED_ROW_IND | UNKNOWN_ROW_IND | EXCAVATOR_TYPE | EXCAVATOR_EQUIPMENT | WORK_PERFORMED | ONE_CALL_NOTIFIED_IND | ONE_CALL_TICKET_NUM | ONE_CALL_CENTER_NAME | LOCATOR_TYPE | VISIBLE_MARKS | FACILITIES_MARKED | SERVICE_INTERRUPTION | SERVICE_INTERRUPTION_HOURS | ROOT_CAUSE | ONE_CALL_SUBTYPE | LOCATING_SUBTYPE | EXCAVATION_SUBTYPE | ROOT_CAUSE_OTHER | OUTSIDE_FORCE_TYPE | VEHICLE_SUBTYPE | OSF_HURRICANE_IND | OSF_TROPICAL_STORM_IND | OSF_TORNADO_IND | OSF_HEAVY_RAINS_IND | OSF_OTHER_WEATHER_IND | OSF_OTHER_WEATHER_DETAILS | INTENTIONAL_SUBTYPE | INTENTIONAL_DETAILS | OSF_OTHER_DETAILS | DRIVER_ISSUED_CITATION_IND | CITATION_SPEED_IND | CITATION_RECKLESS_IND | CITATION_DUI_IND | CITATION_OTHER_IND | CITATION_OTHER_DETAIL | DRIVER_IN_CONTROL_IND | ESTIMATED_SPEED | ESTIMATED_SPEED_UNKNOWN_IND | VEHICLE_TYPE | VEHICLE_TRAVEL_FROM | VEHICLE_TRAVEL_DISTANCE_FT | PROTECTIONS_INSTALLED_IND | PROTECTION_BOLLARDS_POST_IND | PROTECTION_BARRICADES_IND | PROTECTION_GUARD_RAILS_IND | PROTECTION_OTHER_IND | PROTECTION_OTHER_DETAIL | PWJF_FAILURE_TYPE | FIELD_EXAM_IND | METALLURGICAL_IND | OTHER_ANALYSIS_IND | OTHER_ANALYSIS_DETAILS | STILL_UNDER_INVEST_IND | FATIGUE_VIBR_RELATED_1 | FAILURE_SUBTYPE_1 | FATIGUE_VIBR_RELATED_OTHER_1 | MECHANICAL_STRESS_1 | OTHER_FACTOR_1 | OTHER_FACTOR_DETAILS_1 | FATIGUE_VIBR_RELATED_2 | FAILURE_SUBTYPE_2 | FATIGUE_VIBR_RELATED_OTHER_2 | MECHANICAL_STRESS_2 | OTHER_FACTOR_2 | OTHER_FACTOR_DETAILS_2 | STRESS_SUBTYPE | STRESS_DETAILS | ADDITIONAL_DENT_IND | ADDITIONAL_GOUGE_IND | ADDITIONAL_PIPE_BEND_IND | ADDITIONAL_ARC_BURN_IND | ADDITIONAL_CRACK_IND | ADDITIONAL_LACK_FUSION_IND | ADDITIONAL_LAMINATION_IND | ADDITIONAL_BUCKLE_IND | ADDITIONAL_WRINKLE_IND | PWF_ADDITIONAL_MISALIGN_IND | ADDITIONAL_BURNT_STEEL_IND | PWF_ADDITIONAL_OTHER_IND | ADDITIONAL_OTHER_DETAILS | POST_CONSTR_PRESSURE_TEST_VAL | EQ_FAILURE_TYPE | CONTROL_VALVE_IND | INSTRUMENTATION_IND | SCADA_IND | COMMUNICATIONS_IND | BLOCK_VALVE_IND | CHECK_VALVE_IND | RELIEF_VALVE_IND | POWER_FAILURE_IND | STOPPLE_CONTROL_FITTING_IND | PRESSURE_REGULATOR_IND | ESD_SYSTEM_FAILURE_IND | OTHER_CONTROL_RELIEF_IND | OTHER_CONTROL_RELIEF_DETAILS | OTHER_PUMP_IND | OTHER_PUMP_DETAILS | OTHER_STRIPPED_IND | OTHER_STRIPPED_DETAILS | OTHER_NON_THREADED_IND | OTHER_NON_THREADED_DETAILS | EQ_FAILURE_DETAILS | ADDITIONAL_VIBRATION_IND | ADDITIONAL_OVERPRESSURE_IND | ADDITIONAL_SUPPORT_IND | ADDITIONAL_DEFECT_IND | ADDITIONAL_ELECTRICITY_IND | ADDITIONAL_INSTALLATION_IND | ADDITIONAL_IMPROPER_MNTNCE_IND | ADDITIONAL_MISMATCH_IND | ADDITIONAL_DISSIMILAR_IND | ADDITIONAL_BREAKDOWN_IND | ADDITIONAL_VALVE_IND | ADDITIONAL_ALARM_IND | EQ_ADDITIONAL_MISALIGN_IND | EQ_ADDITIONAL_THERMAL_IND | ADDITIONAL_EROSION_WEAR_IND | EQ_ADDITIONAL_OTHER_IND | EQ_ADDITIONAL_OTHER_DETAILS | OPERATION_TYPE | OVERFLOW_OTHER_IND | OVERFLOW_OTHER_DETAILS | OPERATION_DETAILS | RELATED_INADEQUATE_PROC_IND | RELATED_NO_PROC_IND | RELATED_FAILURE_FOLLOW_IND | RELATED_OTHER_IND | OPERATION_RELATED_DETAILS | CATEGORY_TYPE | OPERATOR_QUALIFICATION_IND | QUALIFIED_INDIVIDUALS | OTHER_TYPE | MISC_DETAILS | UNKNOWN_SUBTYPE | INCIDENT_UNKNOWN_COMMENTS | COLLECTED_DATA_IND | AXIAL_MAGNETIC_FLX_LKG_IND | CIR_TRN_WAVE_MGN_FLX_LKG_IND | ULTRASONIC_IND | GEOMETRY_DEFORMATION_IND | EMAT_IND | CPCM_IND | OTHER_TOOL_TECH_IND | AXIAL_RECENT_YEAR | AXIAL_RCNT_PROPUL_METHOD | AXIAL_RCNT_ATTUNED_DETECT | AXIAL_RCNT_ATND_DTCT_DTLS | AXIAL_RCNT_ATND_DTCT_METAL | AXIAL_RCNT_ATT_DT_METAL_DTLS | AXIAL_PREVIOUS_YEAR | AXIAL_PREV_PROPUL_METHOD | AXIAL_PREV_ATTUNED_DETECT | AXIAL_PREV_ATND_DTCT_DTLS | AXIAL_PREV_ATND_DTCT_METAL | AXIAL_PREV_ATT_DT_METAL_DTLS | CIRC_WAVE_RECENT_YEAR | CIRC_WV_RCNT_PROPUL_METHOD | CIRC_WV_RCNT_RESOLUTION | CIRC_WV_RCNT_RESOLUTION_DTLS | CIRC_WV_PREVIOUS_YEAR | CIRC_WV_PREV_PROPUL_METHOD | CIRC_WV_PREV_RESOLUTION | CIRC_WV_PREV_RESOLUTION_DTLS | ULTRASONIC_RECENT_YEAR | ULTRASONIC_RCNT_PROPUL_METHOD | ULTRASONIC_RCNT_ATTUNED | ULTRA_RCNT_ATTUNEDD_DTLS | UTRA_RCNT_ATT_METL_RESOLUTION | UTRA_RCNT_ATT_METL_RES_DTLS | ULTR_PREVIOUS_YEAR | ULTRA_PREV_PROPUL_METHOD | ULTRA_PREV_ATTUNED | ULTRA_PREV_ATTUNED_DTLS | UTRA_PREV_ATT_METL_RESOLUTION | UTRA_PREV_ATT_METL_RES_DTLS | GEOMETRY_RECENT_YEAR | GEOMETRY_RCNT_PROPUL_METHOD | GEOMETRY_RCNT_RESOLUTION | GEOMETRY_RCNT_RESOLUTION_DTLS | GEOMETRT_RCNT_MEASUR_CUPS | GEOMETRY_PREVIOUS_YEAR | GEOMETRY_PREV_PROPUL_METHOD | GEOMETRY_PREV_RESOLUTION | GEOMETRY_PREV_RESOLUTION_DTLS | GEOMETRT_PREV_MEASUR_CUPS | EMAT_RECENT_YEAR | EMAT_RCNT_PROPUL_METHOD | EMAT_PREVIOUS_YEAR | EMAT_PREV_PROPUL_METHOD | CPCM_RECENT_YEAR | CPCM_RCNT_PROPUL_METHOD | CPCM_PREVIOUS_YEAR | CPCM_PREV_PROPUL_METHOD | OTHER_TOOL | OTHER_RECENT_YEAR | OTHER_RCNT_PROPUL_METHOD | OTHER_PREVIOUS_YEAR | OTHER_PREV_PROPUL_METHOD | INSP_COMPL_BEFORE_DAMAGE_IND | HAS_HYDRTST_CONDUC_BEFORE_IND | HYDRTST_MOST_RCNT_YEAR | HYDRTST_MOST_RCNT_PRESSURE | DIRECT_ASMNT_CONDUCTED | DIRECT_ASMNT_AT_PNT_ACCDNT_YR | DIRECT_ASMNT_PNT_NOT_IDNTF_YR | ASMNT_ECDA_RCNT_YEAR | ASMNT_ICDA_RCNT_YEAR | ASMNT_SCCDA_RCNT_YEAR | ASMNT_CONFIRMATORY_RCNT_YEAR | ASMNT_OTHER_TYPE | ASMNT_OTHER_RCNT_YEAR | ASMNT_ECDA_RCNT_IND | ASMNT_ICDA_RCNT_IND | ASMNT_SCCDA_RCNT_IND | ASMNT_CONFIRMATORY_RCNT_IND | ASMNT_OTHER_RCNT_IND | NON_DESTRUCTIVE_EXAM_IND | EXM_RADIOGRAPHY_RCNT_YEAR | EXM_WAVE_ULTRASONIC_RCNT_YEAR | EXM_HANDL_ULTRASONIC_RCNT_YEAR | EXM_WET_MGNT_PARTCL_RCNT_YEAR | EXM_DRY_MGNT_PARTCL_RCNT_YEAR | EXM_OTHER_TYPE | EXM_OTHER_RCNT_YEAR | EXM_RADIOGRAPHY_RCNT_IND | EXM_WAVE_ULTRASONIC_RCNT_IND | EXM_HANDL_ULTRASONIC_RCNT_IND | EXM_WET_MGNT_PARTCL_RCNT_IND | EXM_DRY_MGNT_PARTCL_RCNT_IND | EXM_OTHER_RCNT_IND | EXTRNL_COR_GALVANIC_IND | EXTRNL_COR_ATMOSPHERIC_IND | EXTRNL_COR_STRAY_CURRENT_IND | EXTRNL_COR_MICROBIOLOGIC_IND | EXTRNL_COR_SELECTIVE_SEAM_IND | INTRNL_COR_CORROSIVE_CMDTY_IND | INTRNL_COR_WTR_DRPOUT_ACID_IND | INTRNL_COR_MICROBIOLOGIC_IND | INTRNL_COR_EROSION_IND | NF_EARTH_MOVEMENT_IND | NF_HEAVY_RAINS_IND | NF_LIGHTNING_IND | NF_TEMPERATURE_IND | NF_HIGH_WINDS_IND | NF_VEGITATION_ROOT_IND | EXCVTN_DMG_OPERATOR_IND | EXCVTN_DMG_OP_CONTRACTOR_IND | EXCVTN_DMG_THIRD_PARTY_IND | EXCVTN_DMG_PREVIOUS_DAMAGE_IND | OSF_NEARBY_INDUSTRIAL_IND | OSF_VEHICLE_IND | OSF_BOAT_IND | OSF_OTHER_MARITIME_IND | OSF_ELECTRICAL_ARCING_IND | OSF_PREVOUS_MACHANICAL_IND | OSF_INTENTIONAL_IND | OSF_OTHER_UNDERGROUND_IND | PWF_DESIGN_IND | PWF_CONSTRUCTION_IND | PWF_INSTALLATION_IND | PWF_FABRICATION_IND | PWF_MANUFACTURING_IND | PWF_ENV_STRESS_CORROSION_IND | PWF_ENV_SULFIDE_STRESS_IND | PWF_ENV_HYDROGEN_STRESS_IND | PWF_ENV_HARD_SPOT_IND | EQF_CONTROL_RELEAF_IND | EQF_COMPRESSOR_IND | EQF_THREADED_COUPLING_IND | EQF_NON_THREADED_IND | EQF_DEFECTIVE_FITTING_IND | EQF_EQUIPMENT_BODY_IND | IO_DAMAGE_BY_OPERATOR_IND | IO_VALVE_POSITION_IND | IO_EQUIPMENT_OVERPRESSURE_IND | IO_NOT_INSTALLED_PROPERLY_IND | IO_WRONG_EQUIPMENT_IND | IO_INADEQUATE_PROCEDURE_IND | IO_NO_PROCEDURE_IND | IO_FOLLOW_PROCEDURE_IND | PREPARER_NAME | PREPARER_TITLE | PREPARER_EMAIL | PREPARER_TELEPHONE | PREPARER_FAX | LOCAL_CONTACT_NAME | LOCAL_CONTACT_EMAIL | LOCAL_CONTACT_TELEPHONE | AUTHORIZER_NAME | AUTHORIZER_TITLE | AUTHORIZER_TELEPHONE | AUTHORIZER_EMAIL | NARRATIVE
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100001 | 15951 | 2010-03-10 20:09 | SUPPLEMENTAL FINAL | 602 | CENTERPOINT ENERGY GAS TRANSMISSION | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2010-02-09 01:32 | 2010 |  |  | 35.6724 | -99.272 | 930880 | 2010-02-10 14:08 |  | NATURAL GAS |  | 30142 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | [7 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-02-09 01:32 | 2010-02-09 01:43 | ONSHORE | OK | 73650 | HAMMOND | CUSTER | SURVEY STATION NO. | 4515+67 | CEGT AD-WEST | RED MOON CMPR ST. | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1990 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | TEFLON SEAT | OTHER | [8 empty] | REGULATOR ON PNEUMATIC ACTUATOR | CLASS 1 LOCATION | NO |  | 524 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 172714 | 106479.019417476 | 775 | 924.893473290376 | 400 | 477.364373311162 | 0 | 0 |  |  | 173889 | 111035.30765694 | 107881.277264077 | [8 empty] | 855 |  | 1000 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO INDICATION OF ANY ACTIONS BY CONTROL PRIOR TO THE INCIDENT | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | YES |  |  |  | YES | ICE STORM | [301 empty] | JOHNNY L. CAVITT | DOT COMPLIANCE MANAGER | johnny.cavitt@centerpointenergy.com | 318-429-3606 | 318-429-3927 |  |  |  | JOHNNY L. CAVITT | DOT COMPLIANCE MANAGER | 318-429-3606 | johnny.cavitt@centerpointenergy.com | THE REGULATOR FOR THE PNEUMATIC ACTUATOR FROZEN UP AND CAUSE PRESSURE TO DROP BELOW WHAT WAS NEEDED TO KEEP THE ACTUATOR CLOSED AND IT FAILED OPEN RELEASING GAS THROUGH THE BLOW DOWN VALVE ON THE ESD DISCHARGE BLOWDOWN VALVE(3") ON 16" HEADERS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100002 | 15077 | 2010-03-12 14:43 | SUPPLEMENTAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 569 BROOKWOOD VILLAGE | BIRMINGHAM | AL | 35209 | 2010-01-06 04:32 | 2010 |  |  | 33.1076 | -89.1528 | 927803 | 2010-01-06 06:25 |  | NATURAL GAS |  | 41176 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-01-06 04:58 | 2010-01-20 16:16 |  |  |  |  | NO |  |  |  |  | NO | [7 empty] | 2010-01-06 04:32 | 2010-01-06 04:44 | ONSHORE | MS | 39339 | LOUISVILLE | WINSTON | MILEPOST | 50.785 | 2ND NORTH MAIN | CENTER RIDGE GATE TO LOUISVILLE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 |  | 0.25 | 52000 | API 5L OR EQUIVALENT | DSAW |  | REPUBLIC | COAL TAR | [28 empty] | 1952 | 1952 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 640 | 75.4 |  | CLASS 2 LOCATION | NO |  | 454 |  | NO | NO | NO |  | 4000 | 4773.64373311162 |  | 0 | 242699 | 149625.111650485 | 140000 | 167077.530658907 | 20000 | 23868.2186655581 |  | 0 |  |  | 406699 | 244963.513077501 | 345344.504708062 | [8 empty] | 740 |  | 750 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 54458 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LOW ALARM AND PHONE CALL FROM FIELD PERSONNEL OCCURRED SIMULTANEOUSLY | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES |  |  |  |  | YES | NEAR NEUTRAL PH SCC AS SECONDARY FAILURE MECHANISM. |  |  | YES | YES |  |  | YES | YES | 1963 | NO | YES | YES |  |  |  | 2009 |  |  |  | NO | [190 empty] | YES | YES |  |  | YES |  |  |  | 2009 | [31 empty] | 2009 | [23 empty] | YES | 1994 | 990 | NO | [13 empty] | NO | [63 empty] | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | ken.peters@elpaso.com | 2053257554 | 2053253729 |  |  |  | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | 2053257554 | ken.peters@elpaso.com | ON JANUARY 6 2010 SOUTHERN NATURAL GAS (SNG) COMPANY OPERATIONS PERSONNEL AT THE LOUISVILLE (MS) COMPRESSOR STATION ADVISED SNG GAS CONTROL THAT MEMBERS OF THE GENERAL PUBLIC HAD REPORTED A LOUD NOISE NEAR HIGHWAY 14 WEST OF LOUISVILLE MS. GAS CONTROL SAW A CORRESPONDING PRESSURE DROP VIA THE SCADA SYSTEM. A FAILURE HAD OCCURED ON SNG'S 24 INCH 2ND NORTH MAIN PIPELINE. SNG FIELD PERSONNEL WERE DISPATCHED TO CLOSE VALVES FOR ISOLATION OF THE FAILURE SITE AND TAKE THE AFFECTED SEGMENT OF PIPELINE OUT OF SERVICE. THE FAILURE WAS CAUSED BY A CLUSTER OF EXTERNAL CORROSION PITS WITH SUBSEQUENT NEAR-NEUTRAL PH STRESS CORROSION CRACKING (SCC) CONFINED WITHIN A LOCALIZED AREA OF THE MOST SEVERE CORROSION. THE EVIDENCE GATHERED DURING THE INVESTIGATION CONCLUDED THAT THE EXTERNAL CORROSION WHICH INITIATED THIS FAILURE ALLOWED ELECTROCHEMICAL CORROSION TO THIN THE PIPE WALL, INCREASING THE LOCALIZED STRESSES, WHICH CROSSED THE THRESHOLD FOR SCC TO INITIATE AND PROPAGATE UNTIL THE REMAINING PIPE WALL COULD NO LONGER SUPPORT NORMAL OPERATING PRESSURE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20100003 | 15054 | 2010-03-16 17:05 | SUPPLEMENTAL FINAL | 602 | CENTERPOINT ENERGY GAS TRANSMISSION | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2010-02-16 08:18 | 2010 |  |  | 35.7084 | -99.907 | 931392 | 2010-02-16 11:42 |  | NATURAL GAS |  | 1213 | 12427 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-02-16 12:50 | 2010-02-16 23:20 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-02-16 08:18 | 2010-02-16 08:18 | ONSHORE | OK | 73660 | REYDON | ROFER MILLS COUNTY | SURVEY STATION NO. | 6428+12 | CEGT AD-WEST |  | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1974 |  | CARBON STEEL |  | OTHER | [8 empty] | 1"X1/2" SWEDGE UNDER VALVE CRACKED | CLASS 1 LOCATION | NO |  | 524 |  | NO | NO | NO |  | 0 | 0 | 65863 | 78601.6242984826 | 6429 | 3963.50970873786 | 3838 | 4580.3111619206 | 0 | 0 | 0 | 0 |  |  | 76130 | 42291.8537695774 | 87145.4451691411 | [8 empty] | 904 |  | 1000 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | AUTOMATIC | 79801 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | BECAUSE FIELD OPERATOR WAS INVOLVE WITH INCIDENT | [12 empty] | YES | 1 | 0 | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | OTHER | 1"X1/2" SWEDGE TOP THREADS BROKE IN 1/2" VALVE | [18 empty] | YES | AGE OF SWEDGE CONNECTION | [161 empty] | JOHNNY L. CAVITT | DOT COMPLIANCE MANAGER | johnny.cavitt@centerpointenergy.com | 318-429-3606 | 318-429-3927 |  |  |  | JOHNNY L. CAVITT | DOT COMPLIANCE MANAGER | 318-429-3606 | johnny.cavitt@centerpointenergy.com | AT APPROXIMATELY 08:18 HRS ON FEBRUARY 22, A FIELD EMPLOYEE WAS PERFORMING ANNUAL VALVE MAINTENANCE ON AUXILIARY VALVE ON CEGT LINE AD-WEST. HE CONNECTED A CRESCENT WRENCH TO A 1'X 1/2 ' SWEDGE CONNECTION FOR THE 1/2 ' BALL VALVE AND IMMEDIATELY STARTED HEARING GAS LEAKING. HE NOTIFIED SYSTEM CONTROL AT 08:25 HRS. IT WAS FIRST THOUGHT THAT THE EVENT WOULD BE CORRECTED WITH MINOR COMPLICATIONS. HOWEVER, AFTER EVALUATING THE SITUATION ALONG WITH FIELD EMPLOYEES, MANAGEMENT AND SYSTEM CONTROL IT WAS DECIDED THAT LINE AD-WEST WOULD HAVE TO BE BLOWN DOWN TO COMPLETE THE REPAIRS (APPROXIMATELY 10:18 HRS). SYSTEM CONTROL CALCULATED THE LINE FILL AND IT WAS DETERMINED THAT THE BLOW DOWN WOULD BE @ 12,427 MCF VALUED AT $65,863. SYSTEM CONTROL THEN NOTIFIED THE NRC AT 11:42. THE LINE WAS BLOWN DOWN REPAIRS MADE AND THE LINE WAS BACK IN SERVICE BY 23:20 HRS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100004 | 15829 | 2010-03-17 14:05 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2010-02-17 04:40 | 2010 |  |  | 33.13 | -97.4958 | 931516 | 2010-02-17 15:00 |  | NATURAL GAS |  | 35192 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE VALVE WAS ABLE TO BE CLOSED WITHOUT SHUTTING DOWN THE PIPELINE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-02-17 06:50 | 2010-02-17 06:51 | ONSHORE | TX | 76078 | RHOME | WISE | MILEPOST | 78 | 225-21 SHERMAN EXTENSION | WISE COUNTY COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | OTHER | COMPRESSOR VENT VALVE |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2009 |  | CARBON STEEL |  | LEAK |  |  | OTHER | SOLENOID FAILURE ON VENT VALVE | [5 empty] | CLASS 1 LOCATION | NO |  | 861 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 189000 | 116519.417475728 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 189000 | 120800.970873786 | 116519.417475728 | [8 empty] | 1033 |  | 1200 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [5 empty] | YES | ALARM WAS NEEDED WHEN VALVE CHANGES POSITION | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | SOLENIOD FAILED ON THE VALVE | [161 empty] | MATTHEW STRATMANN | PIPELINE COMPLIANCE SPECIALIST | mstratmann@eprod.com | 713-381-8209 |  |  |  |  | MATTHEW STRATMANN | PIPELINE COMPLIANCE SPECIALIST | 713-381-8209 | mstratmann@eprod.com | ON FEBRUARY 17, 2010 THE WISE COUNTY COMPRESSOR STATION DISCHARGE VENT VALVE SOLENOID FAILED, CAUSING THE COMPRESSOR DISCHARGE VENT VALVE TO OPEN. THE PLC FAILED TO CLOSE THE SUCTION AND DISCHARGE VALVES ON THE COMPRESSOR AND INITIATE A COMPRESSOR STATION SHUTDOWN. THE INCIDENT WAS DISCOVERED BY LOCAL OPERATIONS AT 06:50. AFTER REVIEW OF THE INCIDENT, IT WAS DISCOVERED THAT A SEQUENCE BYPASS HAD BEEN INSTALLED DURING THE INTIAL COMMISSIONING OF THE STATION TO HELP PURGE THE STATION. THE BYPASS WAS NOT REMOVED AFTER COMMISSIONING. THIS ALLOWED THE COMPRESSOR SUCTION AND DISCHARGE VALVES TO STAY OPEN WHEN THE SOLENIOD FAILED ON THE COMPRESSOR VENT VALVE CAUSING IT TO OPEN.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20100005 | 15784 | 2010-03-18 16:01 | SUPPLEMENTAL FINAL | 26330 | ENOGEX LLC | P.O. BOX 24300 | OKLAHOMA CITY | OK | 73124 | 2010-02-19 10:03 | 2010 |  |  | 35.2981 | -98.8345 |  |  |  | NATURAL GAS |  | 2013 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-02-19 10:03 | 2010-02-19 10:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-02-19 10:03 | 2010-02-19 10:04 | ONSHORE | OK | 73632 | CORDELL | OKLAHOMA |  |  | CORDELL COMPRESSOR |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | ESD SYSTEM | 1983 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | NOT APPLICABLE | OTHER | [8 empty] | UNINTENDED GAS RELEASE | CLASS 1 LOCATION | NO |  | 1 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 10850 | 6689.07766990291 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 10850 | 6934.87055016181 | 6689.07766990291 | [8 empty] | 850 |  | 1223 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER'S ACTION DID NOT CONTRIBUTE TO INCIDENT | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | MALFUNCTION OF ESD PILOT GAS PRESSURE REGULATOR | [161 empty] | MIKE REED | MANAGER EHS ASSESSMENT AND COMPLIANCE | reedmd@oge.com | 405 558-4685 | 405 557-8618 |  |  |  | PAUL M BREWER | VP OPERATIONS | 405 525-7788 | brewerpm@oge.com | AT 10:03 AM AN I&E TECHNICIAN WAS WORKING INSIDE THE COMPRESSOR STATION OFFICE/MCC WHEN HE OVERHEARD GAS BLOWING OUTSIDE OF THE BUILDING. THE TECHNICIAN WENT OUTSIDE TO DISCOVER AN ESD SYSTEM VENT VALVE, ESV-303, 100% OPEN. THE TECHNICIAN THEN VERIFIED THERE WAS NOT AN ACTIVE ESD CONDITION ON THE STATION CONTROL COMPUTER. THE TECHNICIAN THEN PHONED A STATION OPERATOR TO ASSIST. THE STATION OPERATOR ARRIVED AT APPROXIMATELY 10:20 AM AND CLOSED A 12 INCH VALVE TO ISOLATE THE STATION FROM L-25. THE GAS RELEASE THROUGH ESV-303 IMMEDIATELY BEGAN TO DECREASE. AS THE NOISE GENERATED BY THE VENTING GAS SUBSIDED, THE OPERATOR THEN HEARD GAS BLOWING FROM A SECOND VENT VALVE, ESV-193, WITHIN THE COMPRESSOR YARD. THE OPERATOR THEN CLOSED A 16 INCH VALVE TO ISOLATE THE STATION FROM L-127. WITH THE STATION COMPLETELY ISOLATED FROM ALL CONNECTING PIPELINES, THE STATION PIPING QUICKLY VENTED TO ATMOSPHERE AND WAS FULLY DEPRESSURED AT 10:26 AM. THE I&E TECHNICIAN RETURNED TO THE CONTROL COMPUTER TO FIND AN ACTIVE ESD ALARM AND A UNIT 1056 COMPRESSOR SHUTDOWN ALARM HAD OCCURRED WHILE HE WAS OUTSIDE OF THE OFFICE. AN INVESTIGATION WAS CONDUCTED FOLLOWING THIS INCIDENT. THE INVESTIGATION CONCLUDED THAT THE INADVERTENT GAS RELEASE WAS CAUSED BY THE UNPLANNED OPENING OF TWO ACTUATED EMERGENCY SHUTDOWN VENT VALVES DUE TO INADEQUATE PILOT GAS PRESSURE. AN INSPECTION OF PILOT GAS SYSTEM TO DETERMINE THE PRESENCE OF FOREIGN MATTER SUCH AS PIPE SCALE, PIPELINE CONTAMINANTS, ETC. WILL BE PERFORMED. IN ADDITION, THE CONTINUED USE OF THE VALVE OPERATORS CURRENTLY INSTALLED ON THE EMERGENCY VENT VALVES WILL BE EVALUATED. UPDATE JULY 30, 2010: AN INSPECTION OF THE PILOT GAS SYSTEM REVEALED THAT NO FOREIGN MATTER WAS PRESENT IN THE PILOT GAS FILTRATION ASSEMBLY OR THE PILOT GAS REGULATORS. THE REGULATORS WERE REPLACED WITH NEW LIKE KIND. FINANCES HAVE BEEN APPROPRIATED FOR THE REPLACEMENT OF ALL EXISTING ESD VENT VALVE ACTUATORS. MATERIALS HAVE BEEN ORDERED AND INSTALLATION HAS BEGUN. UPDATE MAY 26, 2011: REPLACEMENT OF ESD VENT VALE ACTUATORS IS COMPLETE. UPDATE MARCH 5, 2013: COMPLETED SECTION E.5.F.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100006 | 17108 | 2010-03-26 09:36 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2010-03-02 04:20 | 2010 |  |  | 37.9422 | -98.2588 | 932729 | 2010-03-02 08:00 |  | NATURAL GAS |  | 91089 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-03-02 08:00 | 2011-12-10 08:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 20 | 2010-03-02 04:20 | 2010-03-02 06:03 | ONSHORE | KS | 67510 | ABBYVILLE | RENO | SURVEY STATION NO. | 140/26053 | HUGOTON 26" LOOP | RA | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 40 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 26 |  | 0.281 | 60000 | API - 5LX 60 | LONGITUDINAL ERW - HIGH FREQUENCY |  | NATIONAL TUBE DIV., U.S. STEEL CORP | COAL TAR | [9 empty] | PIPE GIRTH WELD | [18 empty] | 1968 | 1967 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 81.6 | 1 |  | CLASS 1 LOCATION | NO |  | 538 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 313880 | 193508.54368932 | 638025 | 761426.010704635 | 2000 | 2386.82186655581 | 0 | 0 |  |  | 953905 | 551229.338602744 | 957321.376260512 | [8 empty] | 833 |  | 900 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 128139 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS NOT IDENTIFIED AS A CONTROLLER FAILURE POSSIBILITY. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | YES | [6 empty] | YES | [14 empty] | YES | [63 empty] | YES | YES |  |  | YES |  |  |  | 2008 | [31 empty] | 2008 | [23 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DAVID COOMES | PIPELINE COMPLIANCE ENGINEER | david.coomes@sscgp.com | 270-852-4391 |  |  |  |  | DAVID L. SINCLAIR | MANAGER OF PIPELINE COMPLIANCE | 270-852-4434 | david.l.sinclair@sscgp.com | AT 4:20AM THE GAS CONTROLLER NOTICED A PRESSURE DROP AT THE STAFFORD STATION OF APPROX. 100 PSI. IN APPROX. 30 MIN. AT 4:30AM THE GAS CONTROLLER CONTACTED THE ON CALL OPERATOR TO GO TO HESSTON STATION TO SEE IF HE CAN INDENTIFY ANY PROBLEMS THERE. ASLO,THE GAS CONTROLLERCONTACTED A SECOND OPERATOR ON CALLTO GO TO STAFFORD STATION AND SEE IF HE CAN IDENTIFY ANY PROBLEMS THERE. A PINCH WAS ENABLED AT STAFFORD STATION TO HOLD UPSTREAM PRESSURE FOR POWER PLANTS. AT 5:08AM THE GAS CONTROLLER RECEIVED A CALL FROM RENO COUNTY 911 DISPATCH ABOUT A LEAK AT RED ROCK ROAD AND ANDRE ROAD IN RENO COUNTY KANSAS. THE GAS CONTROLLER WAS INFORMED BY THE DISPATCHER THAT RENO COUNTY EMERGENCY CREWS WERE ON SITE. AT 6:03AM THE SOUTHERN STAR LYONS DISTRICT MANAGER ARRIVED ON SITE. AT 6:06AM SOUTHERN STAR PERSONNEL ON SITE CALLED GAS CONTROL TO INFORM THEM THAT HE WAS SHUTTING IN THE RA LINE. AT 7:22 KGS ARK RIVER IS FLOWING TO ASSIST SSCGP. AT 8:00AM RA WAS ISOLATED. AT 8:40AM SOUTHERN STAR PERSONNEL ON SITE CALLED GAS CONTROL TO INFORM HIM THAT ARK RIVER IS PHYSICALLY SHUT IN TO MAKE SURE NO GAS FLOWS INTO RA LINE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20100007 | 15818 | 2010-03-26 14:30 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2010-03-05 12:30 | 2010 |  |  | 38.1558 | -121.6913 |  |  |  | NATURAL GAS |  | 1 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | [9 empty] | YES |  |  |  |  | NO | [6 empty] | 0 | 2010-03-05 13:00 | 2010-03-05 13:30 | ONSHORE | CA | 94571 | RIO VISTA | SOLANO |  |  | L114 DEHYDRATOR |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | DEHYDRATOR/DRIER/TREATER/SCRUBBER | [40 empty] | CARBON STEEL |  | OTHER | [8 empty] | REBOILER FIRE | CLASS 1 LOCATION | NO |  | 30 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 59670.5466638952 | 5000 | 5967.05466638952 | 0 | 0 |  |  | 55000 | 30129.3909790064 | 65637.6013302848 | [8 empty] | 10 |  | 15 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [103 empty] | OTHER OUTSIDE FORCE DAMAGE | [9 empty] | REBOILER WAS OVERWHELMED WITH PIPELINE LIQUIDS FROM UPSTREAM SUPPLIER CAUSING A FIRE. | [251 empty] | LAURENCE DENISTON | INTERIM MANAGER | lcd1@pge.com | [5 empty] | FRANCESS YEE | SR. PROGRAM MANAGER | 925-974-4316 | fsc2@pge.com | A FIRE OCCURRED AT APPROXIMATELY 1230 HOURS ON 3/5/10 AT THE LINE 114 DEHYDRATOR STATION NEAR RIO VISTA. DUE TO A DEHYDRATOR UPSET FROM AN UPSTREAM GAS SUPPLIER (VENOCO) LARGER THAN NORMAL QUANTITIES OF FLAMMABLE PIPELINE LIQUIDS WERE INTRODUCED INTO THE PG&E DEHYDRATOR. THE EXTRA LIQUIDS TRAVELED THROUGH THE CONTACT TOWER, OVERWHELMING THE VAPOR RECOVERY SYSTEM AND EVENTUALLY REACHED THE REBOILER NATURAL GAS FIRED BURNER WHERE THE LIQUIDS IGNITED. PROPERTY DAMAGES WERE APPROXIMATELY $50,000. THERE WERE NO FATALITIES AND NO INJURIES. SACRAMENTO TV CHANNEL 10 REPORTED THE STORY ON MONDAY MORNING 3/9/10; PG&E DID NOT BECOME AWARE OF THE REPORT UNTIL THE AFTERNOON OF 3/9/10.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100008 | 15033 | 2010-03-31 13:10 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2010-03-01 14:00 | 2010 |  |  | 35.1824 | -113.4715 | 932691 | 2010-03-01 14:45 |  | NATURAL GAS |  | 0 | 21050 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RESULT OF A PLANNED PROJECT DUE TO ILI. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-03-01 14:00 | 2010-03-01 14:00 | ONSHORE | AZ | 86401 | KINGMAN | MOJAVE | MILEPOST | 361+2181.6 |  | LINE NO. 1201 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 300 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 |  | 0.438 | 52000 | API 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | A.O. SMITH | COAL TAR | [28 empty] | 1969 | 1969 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 602 | [6 empty] | 0 | 99567 | 118824.346393681 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 99567 | 54543.5103928497 | 118824.346393681 | [8 empty] | 626 |  | 845 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 96710 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | DURING ILI ANOMALY DIG |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ACTIVITY WAS IN RESPONSE TO AN ILI INDICATION. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [7 empty] | YES | [14 empty] | YES | [63 empty] | YES | YES | [6 empty] | 2008 | [55 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | ken.peters@elpaso.com | 2053257554 | 2053253729 |  |  |  | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | 2053257554 | ken.peters@elpaso.com | AN ANOMALY INDICATION FROM AN ILI RUN WAS BEING INVESTIGATED ON EL PASO NATURAL GAS COMPANY'S LINE NO. 1201. A VERY MINUTE AMOUNT OF GAS WAS DISCOVERED TO BE LEAKING FOLLOWING EXCAVATION OF THE ANOMALY. THE PIPELINE WAS BLOWN DOWN TO ATMOSHERIC PRESSURE FOR FURTHER IN SITU INVESTIGATION. A ROCK WAS FOUND IMPINGING ON THE PIPE SURFACE AT THE 6:30 O'CLOCK POSITION RESULTING IN A SMALL CRACK THROUGH WHICH THE GAS IS BELIEVED TO HAVE BEEN ESCAPING. THIS OCCURRENCE WAS DEEMED TO BE A REPORTABLE INCIDENT ONLY BECAUSE OF THE AMOUNT OF GAS BLOWN DOWN.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100009 | 15342 | 2010-04-01 16:33 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 569 BROOKWOOD CENTER | BIRMINGHAM | AL | 35209 | 2010-03-06 15:30 | 2010 |  |  | 28.3167 | -91.4002 | 933178 | 2010-03-06 16:20 |  | NATURAL GAS |  | 0 | 1600 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-03-07 08:00 | 2010-03-11 10:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-03-06 15:30 | 2010-03-07 08:00 | OFFSHORE | [28 empty] | 270 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EUGENE ISLAND | 302 | BELOW WATER, PIPE ON OR ABOVE SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | REPAIR SLEEVE OR CLAMP | [38 empty] | 2009 |  | CARBON STEEL |  | OTHER | [8 empty] | A 2" VALVE AND NIPPLE ON AN EXISTING REPAIR CLAMP HAD BEEN DISLOCATED RESULTING IN A LEAK. | CLASS 1 LOCATION | NO |  | 635 |  | NO | NO | NO |  | 0 | 0 | 64338 | 76781.6726252339 | 0 | 0 | 376868 | 449758.391602578 | 2400 | 2864.18623986697 | 0 | 0 |  |  | 443606 | 243010.520266057 | 529404.250467678 | [8 empty] | 810 |  | 1250 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 204619 | NO |  |  |  | YES |  |  |  | YES |  |  | YES |  | YES | IT IS OFFSHORE. | TRANSMISSION SYSTEM | YES | YES | NO | NO | NO | OTHER | AIR PATROL BY 3RD PARTY |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | UNKNOWN DAMAGE CAUSED DISLOCATION OF VALVE AND NIPPLE. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | A 2" VALVE AND NIPPLE WAS FOUND TO BE DISLOCATED FROM A REPAIR CLAMP ON TENNESSEE GAS PIPELINE'S 523M-2300 PIPELINE BUT THE DISLOCATION WAS OF UNKNOWN ORIGIN AND THE ORIGIN IS EXPECTED TO REMAIN INDETERMINATE. | [147 empty] | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | ken.peters@elpaso.com | 2053257554 | 2053253729 |  |  |  | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | 2053257554 | ken.peters@elpaso.com | ON MARCH 6, 2010, A 15 FEET DIAMETER GAS BUBBLE WAS REPORTED IN THE VICINITY OF TENNESSEE GAS PIPELINE'S 523M-2300 PIPELINE. IT WAS ACCOMPANIED BY A SHEEN ABOUT 20 FEET WIDE BY 1 MILE LONG. COMPANY'S GAS CONTROL BEGAN SHUTTING IN PRODUCTION INTO THE PIPELINE AND PERSONNEL WERE MOBILIZED TO SHUT IN THE SUBSEA VALVES FOR SEGMENT ISOLATION. INVESTIGATION REVEALED THAT A 2-INCH VALVE AND NIPPLE HAD BEEN DISLOCATED BY AN UNKNOWN AND INDERTIMINATE CAUSE, RESULTING IN THE LEAK. REPAIR WAS EFFECTED BY INSTALLING A NEW VALVE AND NIPPLE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100010 | 16350 | 2010-04-05 10:49 | SUPPLEMENTAL FINAL | 32341 | SOUTHEAST SUPPLY HEADER, LLC | 1111 LOUISIANA | HOUSTON | TX | 77002 | 2010-01-21 12:29 | 2010 |  |  | 31.8595 | -90.3313 | 929301 | 2010-01-21 21:09 |  | NATURAL GAS |  | 239 | 29184 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | PINHOLE LEAK PRESSURE WAS LOWERED 20% | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-01-21 12:30 | 2010-01-21 13:00 | ONSHORE | MS | 39083 | HAZLEHURST | COPIAH | SURVEY STATION NO. | 4616+82 | SOUTHEAST SUPPLY HEADER (SESH) | BETWEEN BV#65714 & BV#65707 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 108 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 42 |  | 1 | 70000 | API 5L GRADE X70 | DSAW |  | JFE | EPOXY | [9 empty] | PIPE GIRTH WELD | [18 empty] | 2008 | 2007 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 1045 |  | NO | NO | NO |  | 0 | 0 | 159931 | 190863.403970069 | 1310 | 807.621359223301 | 400322 | 477748.651631677 | 0 | 0 | 0 | 0 |  |  | 561563 | 307747.873810288 | 669419.676960969 | [8 empty] | 1005 |  | 1200 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 51216 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIN HOLE LEAK IN GIRTH WELD | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES | [7 empty] | YES | THE LEAK WAS CAUSED BY HYDROGEN-ASSISTED CRACKING (HAC). | [12 empty] | YES | [63 empty] | YES |  |  |  | YES | [35 empty] | 2008 | [23 empty] | NO |  |  | NO | [13 empty] | YES | 2010 |  | 2010 |  | 2010 |  |  | YES |  | YES |  | YES | [51 empty] | JOHNNY L. CAVITT | DOT COMPLIANCE MANAGER | johnny.cavitt@centerpointenergy.com | 318-429-3606 | 318-429-3927 |  |  |  | JOHNNY L. CAVITT | DOT COMPLIANCE MANAGER | 318-429-3606 | johnny.cavitt@centerpointenergy.com | ON JANUARY 21, 2010, A SOUTHERN PINES ELECTRIC (SPE) EMPLOYEE RESPONDING TO POTENTIAL TORNADO DAMAGE TO THEIR POWER LINES WAS WALKING DOWN OUR RIGHT-OF-WAY AND SAW BUBBLES IN WATER THAT HAD POOLED ALONG THE RIGHT-OF-WAY. THE SPE EMPLOYEE CALLED THE SESH SYSTEM CONTROL CENTER AT 12:30 HRS. TO REPORT WHAT HE SUSPECTED TO BE A PIPELINE LEAK. SYSTEM CONTROL DISPATCHED AN SESH EMPLOYEE WHO ARRIVED ON SITE AT 13:30 HRS. AND SUSPECT THAT OUR PIPELINE MAY HAVE A PINHOLE LEAK. THE LOCATED WAS AT CONSTRUCTION STATION 4583+53, IN COPIAH COUNTY, MS. THE LOCATION WAS EXCAVATED AND AT 19:25 HRS. THE LEAK WAS CONFIRMED AS A GIRTH WELD LEAK. ON JANUARY 22, 2010 THE LINE WAS BLOWN DOWN AND A SLEEVE WAS PLACE ON THE LINE UNTIL PERMANENT REPAIRS COULD BE MADE. ON FEBRUARY 7, 2010 PERMANENT REPAIRS WERE MADE TO THE LINE BY PIPE REPLACEMENT. FACTS, CIRCUMSTANCES, AND CONDITIONS THAT MAY HAVE CONTRIBUTED DIRECTLY OR INDIRECTLY TO CAUSING THE INCIDENT THE LEAK WAS THE RESULT OF A THOUGH-WALL CRACK IN THE GIRTH WELD JOINING THE 1.000' WT INDUCTION BEND TO 0.600' WT PIPE TRANSITION PIPE. THE CRACK WAS THE RESULT OF HYDROGEN-ASSISTED CRACKING (HAC). HAC MOST LIKELY THE RESULT OF MARGINAL HEAT INPUT OR PRE-HEAT AT THE 6 O'CLOCK POSITION WHICH PROMOTED RETENTION OF DIFFUSIBLE HYDROGEN WITHIN THE WELD. MARGINAL HEAT INPUT WAS LIKELY THE RESULT OF COLD AND WINDY CONDITIONS PRESENT DURING THE DAY OF WELDING. THERE WAS NO EVIDENCE OF CRACKING ELSEWHERE IN THE WELD. THE CRACK OCCURRED ON THE FACTORY END OF AN INDUCTION BEND AT A LOCATION WITH OPTIMUM WELD FIT-UP. IT WAS CONCLUDED THAT WELD FIT-UP DID NOT PLAY ANY ROLE IN THE INITIATION OF THE HYDROGEN CRACK. THE PIPELINE HAD BEEN HYDROSTATICALLY TESTED FOR 24 HOURS AT A MINIMUM PRESSURE CORRESPONDING TO A HOOP STRESS IN EXCESS OF 100% OF SMYS. PART C ADDITION THE PIPED JOINTED AT THE GIRTH WELD WERE OF TWO DIFFERENT WT. PART C HAD THE DATA FOR THE BEND, 42 " DIAMETER 1" WT PIPE. THE FOLLOWING IS THE DATA FOR THE PUP, 42 " DIAMETER .600 " WT. API 5L GRADE X70, PSL 2, 42' OD X .600' WT HELICAL WELDED LINE PIPE MANUFACTURED BY CORINTH PIPEWORKS IN 2007. 70,000 SMYS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100011 | 15871 | 2010-04-05 12:11 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2010-01-05 10:35 | 2010 |  |  | 32.3012 | -90.0946 | 927744 | 2010-01-05 10:42 |  | NATURAL GAS |  | 1523 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-01-05 10:45 | 2010-01-14 16:48 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 0 | 2010-01-05 10:35 | 2010-01-05 10:35 | ONSHORE | MS | 39232 | FLOWOOD | RANKIN |  |  | JACKSON COMPRESSOR STATION | DEHYDRATION AREA | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | DEHYDRATOR/DRIER/TREATER/SCRUBBER | [38 empty] | 1999 |  | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 3 | 2.5 |  | CLASS 1 LOCATION | NO |  | 44 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 6908 | 4258.81553398058 | 1390855 | 1659861.56360424 | 3163 | 3774.75878195801 | 0 | 0 |  |  | 1400926 | 768068.277511958 | 1667895.13792018 | [8 empty] | 780 |  | 1020 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [313 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 270-688-6357 | 270-688-5871 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 270-688-6361 | jeff.mcmaine@bwpmlp.com | THE PROCESS COIL IN INDIRECT BATH HEATER RUPTURED (CAUSE UNDETERMINED AT THIS TIME) RELEASING NATURAL GAS INTO BATH SOLUTION CHAMBER. THE GAS IN THE CHAMBER IGNITED RESULTING IN AN EXPLOSION OCCURING IN THE VESSEL. FINAL REPORT UPDATE: CAUSE WAS INTERNAL CORROSION.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20100012 | 15129 | 2010-04-07 11:27 | SUPPLEMENTAL FINAL | 1007 | KM INTERSTATE GAS TRANSMISSION CO | 500 DALLAS ST. (ONE ALLEN CENTER) | HOUSTON | TX | 77002 | 2010-03-09 16:02 | 2010 |  |  | 40.4877 | -98.5519 | 933460 | 2010-03-09 17:26 |  | NATURAL GAS |  | 2535 | 3352 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-03-09 16:20 | 2010-03-23 18:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-03-09 16:02 | 2010-03-09 16:02 | ONSHORE | NE | 68973 | ROSELAND | ADAMS | SURVEY STATION NO. | 3389+75 | 16" FRANKLIN TO HASTINGS | 710-005-00-00 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 41 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.25 | 35000 | API 5L - GRADE B | OTHER | ELECTRIC WELDED | UNKNOWN | COAL TAR | [28 empty] | 1946 | 1929 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 21.5 | 0.2 |  | CLASS 1 LOCATION | NO |  | 296 |  | NO | NO | NO |  | 0 | 0 | 19107 | 22802.5027021409 | 14450 | 8908.49514563107 | 21200 | 25300.3117854916 | 540 | 644.441903970069 | 0 | 0 |  |  | 55297 | 31612.1183933932 | 57655.7515372337 | [8 empty] | 644 |  | 720 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 56726 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA SYSTEM WAS FUNCTIONING NORMALLY AT THE TIME OF THE INCIDENT. LINE PRESSURE WAS WITHIN NORMAL OPERATING RANGE AT THE TIME OF THE INCIDENT. GAS CONTROLLER RESPONDED APPROPRIATELY. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES | [7 empty] | YES | LONG SEAM WELD DEFECT AT WRINKLE BEND AND SOIL HEAVING. | [16 empty] | YES | [59 empty] | YES |  |  |  | YES | [35 empty] | 2001 | [23 empty] | YES | 1976 | 902 | NO | [13 empty] | NO | [63 empty] | LARRY KEPPLER | SR. COMPLIANCE ENGINEER | larry_keppler@kindermorgan.com | 713-369-9707 | 713-336-4041 |  |  |  | BRUCE HANCOCK | DIRECTOR COMPLIANCE CODES AND STANDARDS | 303-914-7959 | bruce_hancock@kindermorgan.com | A METALLURGICAL ANALYSIS OF THE FAILURE WAS CONDUCTED. THE CONCLUSION OF THAT ANALYSIS IS THAT THIS REPORT IS SELF CONTAINED AND NO FURTHER INFORMATION IS REQUIRED TO COMPLETE THIS REPORT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100013 | 15036 | 2010-04-08 11:26 | SUPPLEMENTAL FINAL | 12696 | CYPRESS GAS PIPELINE COMPANY | 338 WAVERLY RD | THIBODAUX | LA | 70302 | 2010-03-22 14:59 | 2010 |  |  | 29 | -91 | 934772 | 2010-03-22 16:14 |  | NATURAL GAS |  | 4101 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-03-22 15:46 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-03-22 14:59 | 2010-03-22 15:46 | ONSHORE | LA | 70342 | BERWICK | ST. MARY | SURVEY STATION NO. | 7727 - 7659 | BR-S #001 | 580-200 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 2 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.344 | 42000 | API 5LX | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | YOUNGSTOWN | OTHER | ASPHALT, 9/16" SOMASTIC, W/ 1 1/2" CONCRETE | [27 empty] | 1959 | 1952 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 816 | 16 |  | CLASS 1 LOCATION | NO |  | 332 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 15953 | 9835.10194174757 | 226466 | 270267.000415714 | 308811 | 368538.423716483 | 0 | 0 |  |  | 551230 | 303425.042492293 | 648640.526073945 | [8 empty] | 783 |  | 903 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | CHECK VALVE | 11880 | NO |  | YES |  |  |  | YES | LACK OF ILI LAUNCHERS AND RECEIVERS AND FITTING REQUIREMENTS. | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ALTHOUGH BEING MONITORED BY SCADA, PIPELINE WAS PRESSURED BUT NOT FLOWING AT TIME OF RELEASE. CONTROLLERS ACTIONS WERE NOT AFFECTING THE SEGEMNT AND DID NOT CONTRIBUTE TO THE RELEASE. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION | [6 empty] | YES | EXTERNAL CORROSION DUE TO COATING DISBONDMENT AND SHIELDING. |  |  | YES | YES |  |  | YES | YES | 1953 | YES | YES | YES |  |  |  | 2009 |  |  |  | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | NATHAN L. GRAY JR. | PIPELINE COMPLIANCE SPECIALIST | ngray@eprod.com | 9858041376 |  |  |  |  | NATHAN L. GRAY JR. | PIPELINE COMPLIANCE SPECIALIST | 9858041376 | ngray@eprod.com | ON MARCH 22, 2010, LOCAL OPERATING PERSONNEL WAS NOTIFIED BY OPERATIONS CONTROL THAT THERE WAS A PRESSURE LOSS ON THE BR-S #001 16" PIPELINE NEAR BERWICK, LA IN ST. MARY PARISH. THE LINE WAS PRESSURED, HOWEVER WAS NOT FLOWING. IN ADDITION, OPERATIONS CONTROL RECEIVED A CALL FROM THE BERWICK POLICE DEPARTMENT INDICATING THAT A PIPELINE HAD RUPTURED BEHIND THE LANDFILL APPROXIMATELY 2 MILES WEST OF THE ATCHAFALAYA RIVER BRIDGE ON HWY 49. LOCAL OPERATING PERSONNEL ARRIVED ON THE SCENE TO FIND THAT A PIPE RUPTURE HAD OCCURRED RELEASING PIPE AND NATURAL GAS FROM THE BR-S #001 PIPELINE ROW. THE LINE WAS IMMEDIATELY ISOLATED. ACTIONS WERE TAKEN IMMEDIATELY TO SECURE THE SITE AND PERFORM A FIELD INVESTIGATION. PIPE SPECIMENS AND SOIL SAMPLES WERE TAKEN AND SECURED IN ACCORDANCE WITH REGULATORY REQUIREMENTS. THE PIPE SAMPLES WERE SUBMITTED TO WELDING AND TESTING LABORATORIES IN BATON ROUGE, LA FOR A METALLURGY EXAMINATION. TESTING IS PRESENTLY BEING CONDUCTED. FINAL LAB REPORT HAS BEEN COMPLETED. A REVIEW OF THE WELDING AND TESTING LABAROTORIES FINAL REPORT IS BEING REVIEWED BY COMPANY INTEGRITY MANAGEMENT GROUP TO DETERMINE ASSESSMENT OPTIONS BEFORE PUTTING PIPELINE BACK IN SERVICE. NOTE: PART C-4: THE VALUE DEFAULTED TO 1959 WHEN ACTUAL INSTALLATION OCCURRED IN 1953. ALSO, PART A (5) WOULD NOT TAKE LATITUDE 29.673 OR LONGITUDE -91.251.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100014 | 17098 | 2010-04-09 17:55 | SUPPLEMENTAL FINAL | 31286 | ONEOK GAS TRANSPORTATION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2010-03-11 15:20 | 2010 |  |  | 35.6831 | -96.952 | 933684 | 2010-03-11 18:34 |  | NATURAL GAS |  | 42800 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-03-11 15:20 | 2010-03-27 11:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2010-03-11 15:20 | 2010-03-11 15:45 | ONSHORE | OK | 74834-9675 | CHANDLER | LINCOLN | MILEPOST | 1471+73 | A-26 | WELLSTON / CHANDLER | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 26 |  | 0.25 | 52000 | X-52 | FLASH WELDED |  | A. O. SMITH | COAL TAR | [28 empty] | 1951 | 1950 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 552 | 26 |  | CLASS 1 LOCATION | NO |  | 539 |  | NO | NO | NO |  | 10000 | 11934.109332779 | 0 | 0 | 210000 | 129466.019417476 | 50000 | 59670.5466638952 | 200000 | 238682.186655581 | 315379 | 376376.746726252 | PIPE REPLACEMENTS, TESTING |  | 785379 | 449420.007372869 | 816129.608795983 | [8 empty] | 549 |  | 600 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 52776 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE RUPTURE WAS DUE TO EXTERNAL CORROSION | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | OTHER | THIRD PARTY FAILURE ANALYSIS INDICATED SHALLOW PIT CORROSION ON OUTSIDE DIAMETER | [5 empty] | YES | THIRD PARTY FAILURE ANALYSIS INDICATED SHALLOW PIT CORROSION ON OUTSIDE DIAMETER |  |  |  |  | YES | THIRD PARTY FAILURE ANALYSIS | YES | YES | 1951 | NO | YES | YES |  |  |  | 2009 |  |  |  | NO | [190 empty] | YES | YES |  |  | YES |  |  |  | 2003 | [31 empty] | 2003 | [23 empty] | NO |  |  | Yes, but the point of the Accident was not identified as a dig site |  | 2003 | [11 empty] | NO | [63 empty] | PATTI FORD | SENIOR ENGINEER | patti.ford@oneok.com | 918 588 7131 | 918 732 1311 |  |  |  | WESLEY R DUNBAR | VICE PRESIDENT | 918 588 7424 | wesley.dunbar@oneok.com | ONEOK GAS TRANPORTATION A-26 26INCH PIPELINE RUPTURED AND IGNITED 4 MILES WEST OF CHANDLER, OKLAHOMA AT APPROXIMATELY 1520 HOURS ON THURSDAY MARCH 11, 2010. OPERATIONS PERSONNEL WERE DISPATCHED TO THE SITE AND NEAREST MAIN LINE VALVES. THERE WERE NO INJURIES. LOCAL EMERGENCY SERVICES PERSONNEL WERE ALSO PRESENT. MAIN LINE VALVES AT WELLSTON AND CHANDLER WERE CLOSED AND LOCKED OUT BY APPROXIMATELY 1600 HOURS WITH THE FIRE OUT BY APPROXIMATELY 1700 HOURS. THE OKLAHOMA CORPORATION COMMISSION WAS CONTACTED AT 1610 HOURS ON MARCH 11, 2010. THE NRC WAS CONTACTED AT 1834 HOURS ON MARCH 11, 2010 AND THE INCIDENT NUMBER IS 933684. PIPELINE REPAIRS WERE MADE AND THE 10 MILE SEGMENT OF PIPELINE FROM WELLSTON TO CHANDLER WAS SUCCESSFULLY HYDROTESTED. THE LINE WAS PUT BACK IN FULL SERVICE BY 1100 HOURS ON MARCH 27, 2010. FAILURE ANALYSIS WAS CONDUCTED ON THE RUPTURED PIPE SEGMENTS BY SHERRY LABORATORIES IN BROKEN ARROW, OKLAHOMA. THE PIPE RUPTURED DUE TO SHALLOW PIT CORROSION LOCATED ON THE OUTSIDE DIAMETER OF THE PIPE. A LONG SEAM CLOSE TO THE RUPTURE INITIATION SITE DID NOT CONTRIBUTE TO THE INCIDENT. UPDATE FOR APRIL 21, 2015 - ADDED YEAR OF PIPE MANUFACTURE IN PART C PER PHMSA REQUEST. ALSO, DUE TO UPDATES IN THE REQUIRED PARTS OF THE FORM, PART E 2(A) ON HOW MAOP WAS DETERMINED AND PART B 6 ON MILEPOST FOR THE INCIDENT SITE. THIS SUPPLEMENTAL IS TO FINALIZE THE REPORT. NO ADDITIONAL INFORMATION HAS BEEN ADDED. PAT VAUGHAN 5/24/2016.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100015 | 15783 | 2010-04-13 11:02 | SUPPLEMENTAL FINAL | 19570 | WILLIAMS GAS PIPELINE - TRANSCO | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2010-02-10 03:58 | 2010 |  |  | 29.4609 | -93.387 | 930948 | 2010-02-10 11:00 |  | NATURAL GAS |  | 18 | 0 | 300 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | DID NOT AFFECT GAS FLOW | [6 empty] | NO |  |  |  |  | NO | [7 empty] | 2010-02-10 03:58 | 2010-02-10 04:14 | ONSHORE | LA | 70631-4206 | JOHNSON BAYOU | CAMERON |  |  | STATION 44 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ABOVEGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | FILTER/STRAINER/SEPARATOR | [40 empty] | CARBON STEEL |  | OTHER | [8 empty] | 6" STRAINER LID FAILED (CAME OFF) | CLASS 1 LOCATION | NO |  | 49 |  | NO | NO | NO |  | 0 | 0 | 1000 | 1193.41093327791 | 1200 | 739.805825242718 | 5000 | 5967.05466638952 | 250000 | 298352.733319476 | 0 | 0 |  |  | 257200 | 141005.610120819 | 306253.004744386 | [8 empty] | 845 |  | 1250 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT CAUSED BY CONNECTION FAILURE UNRELATED TO CONTROLLER ACTIONS | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | OTHER | YALE CLOSURE ON STRAINER | [15 empty] | YES |  |  | YES | LOSS OF FIT UP FROM CORROSION, WEAR & MECHANICAL DAMAGE | [161 empty] | EDGAR RODRIGUEZ | PIPELINE SAFETY SPECIALIST II | edgar.x.rodriguez@williams.com | 713-215-2846 |  |  |  |  | MARIE SOTAK | PIPELINE SAFETY MANAGER | 713-215-2111 | marie.sotak@williams.com | 6" STRINER LID (YALE CAP CLOSURE) FAILED ALLOWING CONDENSATE AND GAS TO ESCAPE TO THE ATMOSPHERE. OPERATOR ON DUTY ISOLATED STRAINER POT WITH VALVING UPSTREAM AND DOWNSTREAM. GAS LOSS WITH CONDENSATE/SALTWATER WAS RELEASED. METALURGICAL REPORT REVEALED THE FOLLOWING FINDINGS: SEVERAL CIRCUMSTANCES WORKED IN COMBINATION TO ALLOW THE CAP TO FAIL AND COME OFF OF THE BARREL. THERE WAS A LOSS OF FIT-UP BETWEEN THE MATING THREADS ON THE CAP AND BARREL AS A RESULT OF CORROSION, WEAR, AND PRIOR MECHANICAL DAMAGE (POSSIBLE OVER-TIGHTENING AND/OR CROSSTHREADING). · THE CAP WAS TIGHTENED BY HAMMER BLOWS TO ITS DAMAGED EARS, WHICH RESULTED IN THE CAP BEING INSTALLED OFF-CENTER RELATIVE TO THE BARREL. · THE NUMBER OF THREADS CAPABLE OF CARING LOADS WAS REDUCED BY PRIOR DAMAGE TO NO MORE THAN TWO. · THE THREADS ON ONE SIDE OF THE CONNECTION WERE FULLY ENGAGED AND THE TRHEADS ON THE OPPOSITE SIDE WERE ONLY SLIGHTLY ENGAGED. · THE THREADS LOCATED 90° RELATIVE TO THE ENGAGED THREADS WERE ONLY PARTIALLY ENGAGED; THESE WERE OVERLOADED AND SHEARED OFF AT THE TIME OF FAILURE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20100016 | 16027 | 2010-04-23 13:20 | SUPPLEMENTAL FINAL | 19610 | TRANSWESTERN PIPELINE COMPANY LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2010-03-27 10:22 | 2010 |  |  | 35.4727 | -101.2038 | 935301 | 2010-03-27 14:50 |  | NATURAL GAS |  | 1 | 10801 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-03-27 11:25 | 2010-03-27 14:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-03-27 10:22 | 2010-03-27 10:28 | ONSHORE | TX | 79097 | WHITE DEER | CARSON | SURVEY STATION NO. | 3641+28 | PANHANDLE LATERAL | P3 TO V308 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 50 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 |  | 0.312 | 56000 | API 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | A. O. SMITH | COAL TAR | [28 empty] | 1960 | 1960 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 526 |  | NO | NO | NO |  | 0 | 0 | 45148 | 53880.1168156309 | 5 | 3.08252427184466 | 45852 | 54720.2781126585 | 0 | 0 | 0 | 0 |  |  | 91005 | 49853.6426854182 | 108603.477452561 | [8 empty] | 550 |  | 1008 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | REMOTELY CONTROLLED | 103917 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A PINHOLE LEAK WELL BELOW THE MINIMUM THRESHOLD TO BE IDENTIFIED BY ANY CONTROLLER AND WELL BELOW THE STATE OF THE ART LIMITATIONS OF ANY SCADA TECHNOLOGY | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [52 empty] | LIGHTNING |  |  | DIRECT HIT |  |  | NO | [306 empty] | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | AN ILI TOOL WAS RUN ON THE PANHANDLE LATERAL (TXBP132) ON MARCH 9, 2010. THE ILI COMPANY NOTED DURING THE INITIAL EVALUATION OF THE DATA FROM THE ILI TOOL, THAT AN ANOMALY WAS DETECTED AND MAY HAVE A WALL LOSS GREATER THAN 70% OF THE WALL THICKNESS OF THE PIPE. WITHIN A FEW HOURS OF NOTIFICATION TO TW, THE PIPELINE WAS REDUCED IN PRESSURE AND AN EXCAVATION CREW WAS SENT OUT TO THE SITE. DURING THE BELL HOLE INVESTIGATION GAS DRIED SOIL WAS NOTED, SO THE EXCAVATION WAS TEMPORARILY STOPPED UNTIL A GAS DETECTOR HAD "SNIFFED" THE AREA FOR GAS. THE GAS DETECTOR INDICATED A HIGH PPM OF METHANE GAS SO ALL CONSTRUCTION WAS STOPPED UNTIL THE PIPELINE WAS BLOWN DOWN TO ATMOSPHERE. CONTINUED INVESTIGATION FOUND A PIN HOLE LEAK UNDER A THERMITE WELD THAT WAS PARTIALLY BONDED TO THE PIPE. THE THERMITE WELD CONNECTED BOTH THE NEGATIVE HEADER CABLE THAT GOES TO THE RECTIFIER AND THE TEST LEAD WIRE THAT GOES TO THE CP TEST STAND. THE THERMITE WELD WAS EASILY REMOVED WITH JUST A SMALL PULL ON THE WIRING. THE NEGATIVE HEADER CABLE LEAD WAS A TRIANGLE PWC, INC S N-A 1-AWG TYPE THHN/THWN, GASOLINE AND OIL RESISTANT WIRE. THE INSULATION ON THE WIRE HAD BEEN HEATED AND HAD MELTED THE INSULATION BACK APPROXIMATELY 3.5 INCHES FROM THE THERMITE CONNECTION. SOME OF THE METAL CABLE STRANDS WHERE THE INSULATION HAD MELTED BACK SHOWED DISCOLORATION. ADDITIONALLY THERE WAS A SMALL AMOUNT OF DISCOLORATION ON THE SURFACE OF THE PIPE SURROUNDING THE LEAK. NO CORROSION, DENTS, CRACKS OR GOUGES WERE FOUND ON THE SURFACE OF THE PIPE. THE LEAK WAS THE SIZE OF A PIN HOLE AND APPEARS TO HAVE OCCURRED DUE TO ELECTRICAL ARCING FROM THE NEGATIVE HEADER CABLE TO THE PIPE SURFACE. CORROSION TECHNICIAN REPORTS THE CPU UNIT "SIMMS" WAS INSTALLED IN AUGUST 1990, AND IS SUBJECT TO HIGH LIGHTNING STRIKES AND POWER SURGES. THE RECTIFIER HAS BEEN STRUCK BY LIGHTING A NUMBER OF TIMES BLACKING THE INSIDE OF THE RECTIFIER CASE. ON ONE OCCURRENCE, A LIGHTING STRIKE DISLODGED THE CONNECTION BLOCK FROM THE CASE OF THE RECTIFIER. THE CORROSION TECHNICIAN INSTALLED A SURGEX UNIT IN JUNE 2000 TO HELP REDUCE THE NUMBER OF REPAIRS TO THE RECTIFIER AND MINIMIZE DAMAGE FROM LIGHTING STRIKES. THE RECTIFIER UNIT IS LOCATED WITHIN 30 FT FROM WHERE THE LEAK OCCURRED. TRANSWESTERN DID A THROUGH REVIEW OF CP RECORDS FROM 2003 AND FOUND NO INDICATION OF THE CP PROBLEMS OR A CHANGE IN THE CP SYSTEMS CIRCUIT RESISTANCE. THE OVER ALL CIRCUIT RESISTANCE WAS FROM 0.47 OHMS TO 0.85 OHMS. THE PIPE TO SOIL POTENTIALS ARE BETWEEN -3 TO -4 VOLTS, WITH INSTANT OFF READINGS BETWEEN -1 TO -1.25 VOLTS. THE HIGH VOLTAGE POTENTIALS ARE ASSOCIATED WITH THE CP GROUND BED BEING LOCATED WITHIN 30 FT. OF THE PIPELINE. CONCLUSION ' THE CAUSE OF THE LEAK IS ATTRIBUTED TO METAL LOSS FROM ELECTRICAL ARCING BETWEEN THE NEGATIVE HEADER CABLE AND THE PIPE SURFACE FROM LIGHTING STRIKES. A PREVIOUS ILI TOOL RUN THAT WAS CONDUCTED MARCH 2003 SHOWED NO WALL LOSS ANOMALY'S AT THIS LOCATION. **THIS REPORT IS BEING SUBMITTED IN RESPONSE TO PHMSA'S REQUEST, (DOCKET ID PHMSA-2013-0028), FOR SUPPLEMENTAL REPORTS FROM OPERATORS WHO SUBMITTED REPORTS FOR INCIDENTS OCCURRING AFTER JANUARY 1, 2010, WITH ANY OF THE FOLLOWING: (1) ``PIPE GIRTH WELD'' WAS SELECTED AS THE ``ITEM INVOLVED IN INCIDENT'' IN PART C3 OF THE REPORT. THE REVISED REPORT COLLECTS DATA ABOUT THE PIPE ADJACENT TO THE GIRTH WELD. (2) ``FUNCTION OF PIPELINE SYSTEM'' IS NULL IN PART E5F OF THE REPORT. THE REVISED REPORT COLLECTS THE FUNCTION OF THE PIPELINE SYSTEM FOR ALL INCIDENTS.** THIS SUPPLEMENTAL REPORT IS TO ACKNOWLEDGE THAT THE TWO RELEVANT SECTIONS IN PHMSA'S REQUEST HAVE BEEN REVIEWED AND NO FURTHER ACTIONS WERE NEEDED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100017 | 17580 | 2010-04-26 12:03 | SUPPLEMENTAL FINAL | 4070 | EAST TENNESSEE NATURAL GAS CO | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2010-03-25 09:05 | 2010 |  |  | 36.4785 | -82.5514 | 935074 | 2010-03-25 12:47 |  | NATURAL GAS |  | 100 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | TEMPORARY BYPASS INSTALLED USING STOPPLES | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-03-25 10:05 | 2010-03-25 10:05 | ONSHORE | TN | 37660 | KINGSPORT | SULLIVAN | MILEPOST | 2.2 | EAST TENNESSEE NATURAL GAS | 12" KINGSPORT LATERAL 3307B-100 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 |  | 0.25 | 42000 | API-5L | LONGITUDINAL ERW - LOW FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | UNKNOWN | 1953 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 2 LOCATION | NO |  | 256 |  | NO | NO | NO |  | 5000 | 5967.05466638952 | 0 | 0 | 500 | 308.252427184466 | 114000 | 136048.846393681 | 0 | 0 | 0 | 0 |  |  | 119500 | 65508.6252244216 | 142324.153487255 | [8 empty] | 590 |  | 706 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 36590 | NO |  | YES | [5 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS TOO SMALL TO BE IDENTIFIED BY CONTROL ROOM PERSONNEL. THE LEAK WAS CAUSED BY OLD MECHANICAL DAMAGE. A REVIEW OF OPERATING RECORDS FOUND ABNORMAL OPERATING CONDITIONS DID NOT CAUSE OR CONTRIBUTE TO THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [64 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | [10 empty] | NO |  |  | YES | PRIVATE EASEMENT | [7 empty] | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO |  |  | UNKNOWN/OTHER | YES | YES |  |  | DATA NOT COLLECTED | [121 empty] | NO | [62 empty] | NO | NO |  |  | NO | [13 empty] | NO | [63 empty] | DWAYNE TESCHENDORF | ENGINEER SPECIALIST | dwayne.teschendorf@enbridge.com | 7136275573 |  |  |  |  | RICK W KIVELA | MANAGER | 7136276388 | rick.kivela@enbridge.com | ON THE MARCH 25, 2010 DAMAGE TO THE 12-INCH EAST TENNESSEE NATURAL GAS (OPID #04070) LINE 3307B-100 NEAR KINGSPORT, TENNESSEE (NATIONAL RESPONSE CENTER REPORT #935074) WAS DISCOVERED. THE APPARENT CAUSE OF THE INCIDENT WAS EXCAVATION DAMAGE THAT CAUSED A CRACK IN THE 12-INCH DIAMETER PIPELINE RESULTING IN THE LEAK. THE PIPE WAS REPLACED AND THE PIPELINE RETURNED TO SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100018 | 16953 | 2010-05-04 15:25 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2010-04-16 16:40 | 2010 |  |  | 31.9162 | -104.4309 | 936330 | 2010-04-16 16:50 |  | NATURAL GAS |  | 9 | 17710 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-04-16 16:40 | 2010-04-17 13:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-04-16 16:40 | 2010-04-16 16:40 | ONSHORE | TX | 88268 | Not Within a Municipality | CULBERSON | MILEPOST | 1100MP79+2825 | LINE 1100 | MP 79 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 26 |  | 0.281 | 52000 | API 5L OR EQUIV | DSAW |  | A.O. SMITH | COAL TAR | [28 empty] | 1947 | 1947 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 515 |  | NO | NO | NO |  | 0 | 0 | 97750 | 116655.918727915 | 50 | 30.8252427184466 | 9250 | 11039.0511328206 | 0 | 0 | 0 | 0 |  |  | 107050 | 58647.3185606878 | 127725.795103454 | [8 empty] | 562 |  | 825 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 132000 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE BEING NO ALARMS OR SIGNIFICANT PRESSURE DROP SEEN BY GAS CONTROL; SIMPLY A MINOR LOCAL CORROSION PINHOLE LEAK. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1970 | YES | YES | YES |  |  |  | 2009 |  |  |  | YES | [190 empty] | YES | YES | [6 empty] | 2009 | [55 empty] | YES | 1986 | 1131 | NO | [13 empty] | NO | [63 empty] | MERLIN MOSEMAN | CODES AND STANDARDS ENGINEER | merlin_moseman@kindermorgan.com | 7134204614 | 7134207464 |  |  |  | MERLIN MOSEMAN | CODES AND STANDARDS ENGINEER | 7134204614 | merlin_moseman@kindermorgan.com | FOLLOWING A RUN OF AN INSTRUMENTED INSPECTION DEVICE, EXCAVATION OF EL PASO NATURAL GAS COMPANY'S LINE 1100 WAS BEING PERFORMED PURSUANT TO THE COMPANY INTEGRITY MANAGEMENT PLAN. DURING THIS EXCAVATION, A SMALL CORROSION PIT WAS DISCOVERED IN THE PIPE WALL ALONG WITH AN INDICATION OF LEAKING NATURAL GAS. THE PIPELINE WAS BLOWN DOWN TO ATMOSPHERIC PRESSURE AND REPAIRED BY REPLACING A 40' SECTION OF PIPE. INCIDENT LOCATION, PIPE WALL THICKNESS AND YEAR OF INSTALLATION INFORMATION UPDATED ON 12/15/2015.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100019 | 15761 | 2010-05-04 16:12 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2010-01-10 21:24 | 2010 |  |  | 41.6695 | -94.1691 | 928196 | 2010-01-10 23:50 |  | NATURAL GAS |  | 1970 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-01-11 | 2010-01-11 12:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2010-01-10 21:24 | 2010-01-10 21:40 | ONSHORE | IA | 50233 | REDFIELD | DALLAS | SURVEY STATION NO. | SEC12T79NR29W | REDFIELD MAHER #3 WELL SITE | ST. PETER UNDERGROUND STORAGE FID SYSTEM | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTERSTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | DRAIN LINES | [38 empty] | 2006 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 75 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 11600 | 7151.45631067961 | 464000 | 553742.673040948 | 3500 | 4176.93826647267 | 0 | 0 |  |  | 479100 | 263514.062803755 | 565071.0676181 | [8 empty] | 420 |  | 960 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A NORTHERN NATURAL GAS COMPANY POST INCIDENT INVESTIGATION DETERMINED THAT THE PRIMARY CAUSE OF THE INCIDENT WAS GAS LEAKING FROM A 1-LNCH UNION OF WHICH CONTROLLER'S DID NOT HAVE ANY MONITORING CAPABILITY OR CONTROL OVER. THE CONTROLLER DID INDICATE THAT THE MAHER #3 WELL SITE HAD AN INDICATION OF A PRESSURE DROP THEN A LOSS OF COMMUNICATIONS ALARM AT THE LOCATION, WHICH THE ON-SITE GROUND PATROL WAS CHECKING ON DURING THE FIELD FACILITIES CHECK. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | MECHANICAL COUPLING | [17 empty] | YES | [164 empty] | BYRON H. WOOD | SR. PIPELINE SAFETY SPECIALIST | byron.wood@nngco.com | 402-398-7396 | 402-398-7606 |  |  |  | THOMAS G. CORRELL | DIRECTOR. PIPELINE SAFETY AND INTEGRITY | 402-398-7715 | thomas.correll@nnqco.com | ON JANUARY 10, 2010, AT APPROXIMATELY 21:24 P.M. A FIRE WAS DISCOVERED, BY A NORTHERN NATURAL GAS COMPANY EMPLOYEE, AT THE REDFIELD UNDERGROUND STORAGE FIELD, LOCATED NEAR REDFIELD, IOWA, IN THE SL PETER UNDERGROUND STORAGE FORMATION AT WHAT IS CALLED THE MAHER #3 WELL SITE IN SECTION 12, T19N, R29W, DALLAS COUNTY, IOWA. THERE WAS NO EXPLOSION, NO INJURIES, NO EVACUATIONS AND NO LOSS OF SERVICE TO CUSTOMERS. AT APPROXIMATELY 24:00 HOURS THE ST PETER FORMATION PIPELINE SYSTEM PORTION, OF THE STORAGE FIELD, WAS ISOLATED AND PRESSURE WAS BLOWN DOWN ON THE PIPING TO 5 PSIG TO ENABLE SAFE CLOSURE OF THE MAHER #3 WELL HEAD VALVE (SEE PAGE 2, ITEM 15A). THE FIRE WAS EXTINGUISHED BY 01:50 A.M. THE FIRE DESTROYED THE WELL HOUSE BUILDING AND ALL OF THE COMPONENTS WITHIN THE BUILDING BUT THE WELL HEAD VALVE AND PIPING WERE UNAFFECTED. THE PORTION OF THE ST. PETER PIPING, THAT WAS ISOLATED IN ORDER TO FACILITATE REDUCTION IN PRESSURE FOR THE CLOSURE OF THE MAHER #3 WELL HEAD VALVE, WAS RETURN TO NORMAL OPERATION PRESSURES AT APPROXIMATELY 12:00 A.M. ON MONDAY, JANUARY 11TH (SEE PAGE 2, ITEM 15B). PRELIMINARY RESULTS OF A POST INCIDENT INVESTIGATION IDENTIFIED THAT THE GAS LEAKAGE APPEARED TO BE FROM A BROKEN ONE-INCH UNION ON THE WELL SEPARATOR DRAIN LINE. THE UNION'S THREADS APPEARED TO BE STRIPPED OR PULLED. AT THE TIME OF THE EVENT THE AMBIENT TEMPERATURE WAS 21 DEGREES FAHRENHEIT AND THE WIND WAS OUT OF THE WEST AT APPROXIMATELY 14 MILES PER HOUR. IT IS POSSIBLE THAT FREEZING AND HEAVING MAY HAVE CREATING SUFFICIENT THERMAL STRESS WHICH CONTRIBUTED TO THE SEPARATION OF THE THREADS ON THE ONE-INCH UNION. THE NIGHT BEFORE THE FAILURE THERE WAS AN APPROXIMATE LOW TEMPERATURE OF - 19 DEGREES FAHRENHEIT IN THE AREA. ADDITIONAL METALLURGICAL FAILURE ANALYSIS IS BEING CONDUCTED TO ASSIST WITH DETERMINING WHETHER THERMAL STRESS FROM THE COLD TEMPERATURES COULD BE A ROOT CAUSE FOR STRIPPING OF THE THREADS AND THE UNION'S FAILURE. FINAL REPORT: A METALLURGICAL EXAMINATION OF THE FAILED ONE-INCH UNION INDICATED THAT TWO PORTIONS OF THE UNION'S THREADS DEMONSTRATED ROLLED DAMAGE TO THE TOP OF THE THREADS, WHICH INDICATES THE COMPONENT PULLED OVER THE PEAK OF THE THREAD AS IT DISENGAGED. AN EXAMINATION OF THE THREADS ALSO INDICATES ONE FLATTENED/ROUNDED LOCATION THAT MAY HAVE BEEN DAMAGED OR IMPROPERLY MACHINED PREVIOUS TO THE FAILURE. THE FITTING WAS INSTALLED IN 2006, AND MAY HAVE BEEN FAULTY AND THE FROZEN CONDITION OF THE DRAIN LINE, ON DECEMBER 10, 2010, MOST LIKELY CREATED THERMAL STRESS, WHICH RESULTED IN FAILURE OF THE FITTING. AS A MEASURE TO PREVENT RECURRENCE, ALL WELL SEPARATOR DRAIN LINES AT THE REDFIELD, IOWA UNDERGROUND STORAGE FACILITY WERE DISSEMBLED AND INSPECTED. NO OTHER ISSUES OR PROBLEMS WERE FOUND. THE FIRE APPEARS TO HAVE STARTED IMMEDIATELY AS THERE WAS NO INDICATION OF AN EXPLOSION. THE WIRING IN THE CONDUIT, STATIC ELECTRICITY OR SPARKS FROM THE BUILDING STRUCTURE OR THE ONE-INCH PIPE STRIKING OTHER PIPING WHEN IT SEPARATED WAS THE LIKELY IGNITION SOURCE. THIS EVENT IS CONSIDERED COMPLETE AND CLOSED. SUPPLEMENTAL/FINAL TO REPORT 20100019 PER PHMSA REQUEST IDENTIFIED PART E5F AS TRANSMISSION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100020 | 16354 | 2010-05-07 11:54 | SUPPLEMENTAL FINAL | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 800 GASTON ROAD | GASTONIA | NC | 28056 | 2010-04-08 18:42 | 2010 |  |  | 35.3034 | -82.1747 | 936559 | 2010-04-09 00:54 |  | NATURAL GAS |  | 7240 | 513 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-04-08 21:35 | 2010-04-09 02:47 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2010-04-08 18:42 | 2010-04-08 19:00 | ONSHORE | NC | 28756 | MILL SPRING | POLK |  |  | MILL SPRING TAKE OFF | RSO1972 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | TUBING | [38 empty] | 1990 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | ALUMINUM | OTHER | [8 empty] | LIGHTNING STRIKE | CLASS 2 LOCATION | NO |  | 312 |  | NO | NO | NO |  | 0 | 0 | 3000 | 3580.23279983372 | 41700 | 25708.2524271845 | 300000 | 358023.279983372 | 16000 | 19094.5749324465 | 0 | 0 |  |  | 360700 | 201403.380299597 | 406406.340142836 | [8 empty] | 530 |  | 500 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE EXCEEDED MAOP, BUT DID NOT EXCEED THE APPLICABLE ALLOWANCE IN 192.201 | NO | [22 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CAUSE OF THE INCIDENT NOT INVOLVING THE CONTROLLER OR THE CONTROL ROOM. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [52 empty] | LIGHTNING |  |  | DIRECT HIT |  |  | YES |  |  |  | YES | SEVERE THUNDERSTORM WARNING | [301 empty] | MARC WORTH | REGIONAL MANAGER - OPERATIONS | mworth@scana.com | 828-670-3520 | 828-670-3513 |  |  |  | BILL RAYNER | GENERAL MANAGER SYSTEM OPERATIONS AND MAINTENANCE | 704-810-3200 | frayner@scana.com | PSNC ENERGY'S MILL SPRING TAKE-OFF STATION IS LOCATED ON A SITE OWNED AND OPERATED BY WILLIAMS-TRANSCO IN MILL SPRING, NORTH CAROLINA. ON APRIL 8, 2010, PSNC ENERGY'S SCADA SYSTEM INDICATED A LOW PRESSURE ALARM FROM THE MILL SPRING TAKE-OFF STATION AT 6:42 P.M. FOLLOWED BY A HIGH FLOW ALARM AT 6:47 P.M. PSNC ENERGY'S GAS CONTROL DISPATCHED COMPANY PERSONNEL TO THIS SITE TO INVESTIGATE THE ALARM NOTIFICATIONS. ABOUT THE SAME TIME, RESIDENTS IN THE VICINITY OF THE MILL SPRING TAKE-OFF STATION REPORTED SEEING BRIGHT LIGHTNING AND IMMEDIATE THUNDER. SIMULTANEOUS WITH THE SCADA ALARMS, AT APPROXIMATELY 6:40 P.M., A LOCAL PSNC ENERGY EMPLOYEE RECEIVED CALLS FROM THE POLK COUNTY SHERRIFF'S DEPARTMENT AND POLK COUNTY EMS INDICATING A FIRE AT THE MILL SPRING TAKE-OFF STATION. THIS EMPLOYEE IMMEDIATELY RESPONDED TO THE CALL AND ARRIVED AT THE MILL SPRING TAKE-OFF STATION AT 7:00 P.M. THE PSNC ENERGY TAKE-OFF STATION WAS ON FIRE. THE FIRE WAS OF A MAGNITUDE AND IN A LOCATION THAT THE PSNC ENERGY STATION VALVES COULD NOT BE REACHED. PSNC ENERGY ENGINEERING AND OPERATIONS PERSONNEL DEVELOPED A PLAN TO ISOLATE THE TAKE-OFF STATION UTILIZING OTHER REMOTE PIPELINE BLOCK VALVES. FIRE FIGHTERS USED WATER BLANKETS TO KEEP OTHER EQUIPMENT, SURROUNDING MATERIALS, AND VEGETATION FROM COMBUSTING. AT 9:55 P.M. THE TAKE-OFF STATION WAS ISOLATED AND THE FIRE WAS EXTINGUISHED. BASED UPON THE LOCAL SEVERE WEATHER CONDITIONS AND FIRST-HAND ACCOUNTS, PSNC ENERGY'S SCADA SYSTEM ALARMS, AND POST-INCIDENT SITE EVALUATIONS, IT IS BELIEVED THAT LIGHTNING CAUSED A TUBING FAILURE WHICH SUBSEQUENTLY RESULTED IN A STATION FIRE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20100021 | 15785 | 2010-05-12 09:34 | SUPPLEMENTAL FINAL | 26330 | ENOGEX LLC | P.O. BOX 24300 | OKLAHOMA CITY | OK | 73124 | 2010-04-19 09:49 | 2010 |  |  | 35.1177 | -96.2016 |  |  |  | NATURAL GAS |  | 6 | 6 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-04-19 09:55 | 2010-05-10 13:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-04-19 09:49 | 2010-04-19 09:49 | ONSHORE | OK | 74883 | WETUMKA | HUGHES |  |  | WETUMKA STORAGE FIELD | IW-3 LATERAL/L-256 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 42 |  | NO | [22 empty] | INTRASTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | PIPE | PIPE BODY | 8.625 |  | 0.188 | 42000 | API 5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1981 | 1981 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 171 |  | NO | NO | NO |  | 0 | 0 | 25 | 29.8352733319476 | 25 | 15.4126213592233 | 11500 | 13724.2257326959 | 0 | 0 | 0 | 0 |  |  | 11550 | 6329.45589227492 | 13769.4736273871 | [8 empty] | 485 |  | 827 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS A PIN HOLE WITH NOT ENOUGH VOLUME OF GAS LEAKING TO BE DETECTED BY SCADA. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | MIKE REED | MANAGER ASSESSMENT DOT COMPLIANCE | reedmd@oge.com | 405 558-4685 | 405 557-8618 |  |  |  | PAUL M BREWER | VP OPERATIONS | 4055257788 | brewerpm@oge.com | AN ENOGEX EMPLOYEE WAS ON LOCATION AT THE WETUMKA STORAGE FIELD IW-3 SITE. HE HEARD BUBBLING IN A PUDDLE OF WATER THAT WAS ON THE RIGHT OF WAY ADJACENT TO THE IW-3 WELL PAD. HE SHUT IN THE WELL AND ISOLATED THE LINE. THE LINE REMAINED ISOLATED UNTIL REPAIR COMPLETED ON MAY 5, 2010 . LOCALIZED CORROSION PITTING WAS DISCOVERED ON THE INTERNAL WALL OF THE PIPE. MEASUREMENTS INDICATE MINIMAL (.004 INCHES) WALL LOSS OF REMAINING PIPE. 12' 9" OF PIPE WAS REPLACED. UPDATE MARCH 5, 2013: COMPLETED SECTION E.5.F.
2021-02-26 10:37 | YES | YES | GT (Gas Transmission) | 20100022 | 15786 | 2010-05-12 09:44 | SUPPLEMENTAL | 26330 | ENOGEX LLC | P.O. BOX 24300 | OKLAHOMA CITY | OK | 73124 | 2010-04-14 14:30 | 2010 |  |  | 33.979 | -96.008 |  |  |  | OTHER GAS | HYDROCARBONS | 0 | 0 | 0 | NO | [5 empty] | 0 | YES | 0 | 1 | 0 | 0 | 0 | 1 |  | NO | FACILITY WAS SHUTDOWN FOR CONSTRUCTION TIE-INS PRIOR TO INCIDENT TIME. | [6 empty] | YES |  |  |  |  | NO | [6 empty] | 0 | 2010-04-14 14:30 | 2010-04-14 14:30 | ONSHORE | OK | 74723 | BENNINGTON | BRYAN |  |  | BENNINGTON COMPRESSOR STATION |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | FLANGE ASSEMBLY | [38 empty] | 2008 |  | CARBON STEEL |  | OTHER | [8 empty] | CONTRACT EMPLOYEE INJURY REQUIRING IN-PATIENT HOSPITALIZATION | CLASS 1 LOCATION | NO |  | 1 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | [8 empty] | 0 |  | 1440 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | NO | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | FACILITY WAS ISOLATED AND ALL GAS VENTED FROM STATION PIPING AT THE TIME OF THE INCIDENT. SCADA SYSTEM WAS OPERATIONAL; HOWEVER GAS CONTROLLERS WERE NOT MONITORING OR CONTROLLING STATION PARAMETERS ON APRIL 14, 2010. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | IGNITION OF FLAMMABLES/COMBUSTIBLES INSIDE PIPING MANIFOLD DURING HOT WORK (FLAME CUTTING) OF PIPING MANIFOLD. | [147 empty] | MIKE REED | MANAGER EHS ASSESSMENT AND COMPLIANCE | reedmd@oge.com | 405 558-4685 | 405 557-8618 |  |  |  | PAUL M BREWER | VP OPERATIONS | 405 525-7788 | brewerpm@oge.com | COMPRESSOR STATION WAS ISOLATED AND VENTED TO ATMOSPHERE FOR CONSTRUCTION TIE-INS RELATED TO EXPANSION PROJECT. A SHORT SECTION (APPROXIMATELY 12-18 INCHES) OF A 16 INCH RECYCLE PIPING SYSTEM WAS TO BE REMOVED AND A 16 X 8 REDUCING TEE ADDED TO CONNECT A NEW RECYCLE PIPING SYSTEM TO THE EXISTING RECYCLE PIPING SYSTEM. A LOCK-OUT/TAG-OUT PROCEDURE AND AN AIR MOVER WERE IN PLACE TO ELIMINATE OR MITIGATE HAZARDS DURING THE HOT WORK OPERATION. MEANWHILE, WORKERS WERE INSTALLING A NEW METER TUBE ON AN ADJACENT PIPING MANIFOLD THAT WAS CONNECTED TO THE RECYCLE PIPING SYSTEM. A 12" BLIND FLANGE WAS REMOVED FROM THE PIPING MANIFOLD TO INSTALL AN ISOLATION VALVE BETWEEN THE NEW METER TUBE AND THE EXISTING PIPING MANIFOLD. A CONTRACT EMPLOYEE WAS STANDING BESIDE THE OPEN ENDED PIPE FLANGE AT THE SAME TIME THE NEARBY HOT WORK IGNITED VAPORS INSIDE THE PIPING SYSTEM. CONTRACT EMPLOYEE WAS INJURED AS A RESULT OF A FLASH FIRE WHICH IMMEDIATELY EXTINGUISHED ITSELF. CONTRACT EMPLOYEE'S INJURIES REQUIRED IN-PATIENT HOSPITALIZATION. UPDATE NOVEMBER 23, 2010 AN INVESTIGATION TEAM WAS ASSEMBLED IMMEDIATELY FOLLOWING THE INCIDENT AND AN INVESTIGATION WAS CONDUCTED TO DETERMINE THE CAUSE OR CAUSES OF THE INCIDENT. THE FOLLOWING CAUSAL FACTORS WERE IDENTIFIED: 1. TWO INDEPENDENT JOBS WERE ON-GOING AT THE SAME TIME WHICH IMPACTED ONE ANOTHER AND EFFECTIVE COMMUNICATION BETWEEN THESE JOBS WAS NOT ADEQUATE TO CONSIDER THE IMPACT OF INDEPENDENT ACTIONS TAKEN. 2. THREE VALVES (XV #853, XV # 861, AND XV # 871) FAILED OPEN WHEN THE INSTRUMENT AIR BLED OFF FOLLOWING THE INITIAL ESD. THIS CONDITION MAY HAVE UNKNOWINGLY INCREASED THE VOLUME OF VAPORS WITHIN THE PIPING REQUIRED TO BE PURGED PRIOR TO THE HOT WORK BEING CONDUCTED THEREBY DECREASING THE EFFECTIVENESS OF THE AIR MOVER. 3. A12-INCH BLIND FLANGE WAS REMOVED, POTENTIALLY CHANGING THE AIR FLOW DYNAMICS WITHIN THE PIPE AND POSSIBLY LIMITING THE EFFECTIVENESS OF THE AIR MOVER IN THE LOCATION OF THE 16-INCH TEE ON THE UPSTREAM SIDE OF THE EXISTING RECYCLE METER RUN. 4. THE SCOPE OF THE SAFE WORK PERMIT (WRITTEN PRIOR TO WORK BEING PERFORMED), WHICH INCLUDED MULTIPLE CONTRACTORS OVER AN ENTIRE SHIFT, WAS LIKELY TOO BROAD TO BE EFFECTIVE IN CONTROLLING MULTIPLE TASKS. THE FOLLOWING ROOT CAUSE(S) WERE IDENTIFIED: 1. THE POTENTIAL HAZARDS ASSOCIATED WITH MULTIPLE ONGOING AND SEEMINGLY UNRELATED JOBS WITHIN THE SAME GENERAL WORK AREA WERE NOT SUFFICIENTLY ANALYZED TO CONSIDER THE POTENTIAL IMPACTS OF ONE JOB ON THE OTHER. 2. THREE VALVES THAT WERE CLOSED DURING LO/TO FAILED OPEN DUE TO THE LOSS OF INSTRUMENT GAS AFTER THE ESD. THIS CONDITION WAS EITHER NOT ANTICIPATED OR NOT CONSIDERED TO BE RELEVANT DURING JOB PLANNING. 3. AN UNDETECTED FLAMMABLE ATMOSPHERE EXISTED WITHIN THE PIPING DURING AUTHORIZED HOT WORK ACTIVITIES. RECOMMENDATIONS ARE BEING IMPLEMENTED TO ADDRESS THE FINDINGS ABOVE TO PREVENT A RECURRENCE. UPDATE MARCH 5, 2013: COMPLETED SECTION E.5.F.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20100023 | 15038 | 2010-05-13 14:30 | SUPPLEMENTAL FINAL | 19570 | WILLIAMS GAS PIPELINE - TRANSCO | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2010-04-26 06:08 | 2010 |  |  | 27.5117 | -97.9847 | 938267 | 2010-04-26 09:00 |  | NATURAL GAS |  | 4 | 6819 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-04-26 07:15 | 2010-04-29 11:05 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-04-26 06:15 | 2010-04-26 07:15 | ONSHORE | TX | 78363 | KINGSVILLE | KLEBERG | MILEPOST | 97.457 | MAINLINE A |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 65 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 |  | 0.281 | 52000 | TGTC-1A | DSAW |  | CONSOLIDATED WESTERN | COAL TAR | [29 empty] | 1950 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 491 |  | NO | NO | NO |  | 5000 | 5967.05466638952 | 26069 | 31111.0296196217 | 15 | 9.24757281553398 | 25000 | 29835.2733319476 | 1000 | 1193.41093327791 | 0 | 0 |  |  | 57084 | 31272.3912655666 | 68116.0161240523 | [8 empty] | 518 |  | 878 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 53118 | NO |  | YES | [5 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS MATERIAL FAILURE. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  |  |  |  | YES | [5 empty] | YES |  |  |  | YES | YES | 1950 | YES | YES | YES |  |  |  | 2009 |  |  |  | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | EDGAR RODRIGUEZ | PIPELINE SAFETY SPECIALIST II | edgar.x.rodriguez@williams.com | 7132152846 | 7132152222 |  |  |  | MARIE SOTAK | PIPELINE SAFETY MANAGER | 7132152111 | marie.sotak@williams.com | A CALL FROM A WILLIAMS EMPLOYEE WAS RECEIVED AT 6:15PM STATING THAT A LEAK ON 24" MAINLINE A HAS BEEN DISCOVERED. AFTER HAVING NOTIFIED GAS CONTROL IN HOUSTON, SEVERAL SOUTH TEXAS DISTRICT EMPLOYEES WERE CONTACTED AND REQUESTED THAT THEY CLOSE BOTH BLOCK VALVES 10-A-70 AND 10-A 80, WHICH WOULD ISOLATE THE SECTION OF PIPELINE WHERE THE LEAK WAS LOCATED. THE PIPELINE WAS ISOLATED AND HAD BEEN MADE SECURE BY 7:15 PM. NRC WAS CONTACTED AT 7:37 PM AND ANY OTHER AGENCIES THAT WOULD NORMALLY BE INCLUDED IN THE NOTIFICATION PROCESS. THESE NOTIFICATIONS WERE COMPLETED BY 8:00 PM THAT EVENING.. A GAS HANDLING PLAN AND A WORK PLAN WERE GENERATED EARLY ON TUESDAY MORNING AND THE SECTION OF PIPELINE BETWEEN THE TWO BLOCK VALVE SETTINGS WAS BLOWN DOWN. A CONTRACTOR WAS DISPATCHED TO THE LOCATION AND ONCE THE PIPELINE WAS MADE SAFE, STARTED EXCAVATING THE LINE TO EXPOSE THE AREA OF THE LEAK. DURING THE EXCAVATION PROCESS, AN OLD AND MOSTLY CORRODED 2" PIPELINE WHICH WAS ALREADY IN PIECES WAS UNCOVERED. THIS 2" PIPELINE WAS LOCATED APPROXIMATELY 2 1/2" ABOVE OUR 24" PIPELINE. THIS 2" PIPE WAS ABANDONED AND BEEN OUT OF SERVICE FOR SOME TIME. THE SOIL AROUND THE 2" PIPELINE AND DOWN TO OUR PINHOLE LEAK WAS SATURATED WITH SOME TYPE OF PRODUCT THAT SMELLED VERY MUCH LIKE CONDENSATE. THE PINHOLE LEAK WAS LOCATED AND AFTER CLOSE INSPECTION, A 30' SECTION OF PIPE WAS CUT OUT AND REPLACED WITH NEW PRETESTED PIPE. THE ORIGINAL 24" PIPE AT BOTH ENDS OF THE 30' SECTION WAS IN EXCELLENT CONDITION BOTH INTERNALLY AND EXTERNALLY. SOIL SAMPLES WERE TAKEN OF THE IMMEDIATE AREA AND WERE SHIPPED OVERNIGHT TO A LAB FOR FURTHER ANALYSIS. WILLIAMS HAD A METALLURGICAL TEST OF THE PIPE THAT WAS CUT OUT IN ORDER THAT IT CAN IDENTIFY THE ROOT CAUSE OF THE CORROSION AT THAT PARTICULAR SITE. THE 24" PIPELINE WAS PURGED, PACKED AND PLACED BACK IN SERVICE AT 11:00 AM ON THURSDAY, APRIL 29TH, 2010. METALLURGICAL ANALYSIS CONFIRMED THAT THE REASON FOR THE LEAS WAS MICROBIOLOGICAL ON 6/2/2010. THE METALLURGICAL REPORT FOUND THE FOLLOWING; THE COAL TAR CORROSION PROTECTION THAT COATED THE PIPELINE WHEN IT WAS ORIGINALLY INSTALLED HAD BEEN SEVERELY DEGRADED IN THE AREA AROUND THE LEAK, PROBABLY BY A CHEMICAL SUBSTANCE THAT HAD APPARENTLY LEAKED FROM THE 2-INCH PIPELINE INSTALLED OVER THE 24-INCH LINE. VISUAL EXAMINATION OF THE LEAK SHOWED CORROSION PITTING ON THE OUTSIDE SURFACE. SOME OF THE PITS HAD A FIBROUS APPEARANCE INDICATING PREFERENTIAL ATTACK FOLLOWING THE PIPE AXIS. THE FIBROUS APPEARANCE WAS CHARACTERISTIC OF MICROBIOLOGICALLY-INFLUENCED CORROSION (MIC). METALLOGRAPHIC ANALYSIS OF THE CORROSION PITS SHOWED UNDERCUTTING AND PITS WITHIN PITS, WHICH ARE ALSO UNIQUE CHARACTERISTICS OF MIC. THE LEAK WAS CAUSED BY MIC, WHICH OCCURED AFTER THE COAL TAR COATING HAD BEEN DEGRADED EXPOSING THE BARE PIPE. THE PRESENCE OF SULFUR AND MOISTURE IN THE SOIL AROUND THE LEAK CREATED AN IDEAL ENVIRONMENT FOR MIC TO OCCUR.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100024 | 15025 | 2010-05-14 21:06 | ORIGINAL FINAL | 602 | CENTERPOINT ENERGY GAS TRANSMISSION | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2010-04-15 17:30 | 2010 |  |  | 34.9276 | -91.0532 | 937186 | 2010-04-15 19:06 |  | NATURAL GAS |  | 27187.5 | 1125 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-04-15 18:18 | 2010-04-16 15:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-04-15 17:30 | 2010-04-15 18:15 | ONSHORE | AR | 72392 | 1 MILE EAST OF WHEATLEY | ST. FRANCIS COUNTY |  |  | CENTERPOINT GAS TRANSMISSION PIPELINE | JM-20 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 4 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 4 |  | 0.237 | 35000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1959 | 1953 | CARBON STEEL |  | OTHER | [8 empty] | FARMER PULLING LEVEE PLOW SEVERED THE PIPELINE COMPLETELY IN HALF | CLASS 1 LOCATION | NO |  | 72 |  | NO | NO | NO |  | 0 | 0 | 4680 | 5585.1631677406 | 113100 | 69726.6990291262 | 1000 | 1193.41093327791 | 18000 | 21481.3967990023 | 25000 | 29835.2733319476 | COST FOR RE-LIGHT TO DISTRIBUTION CUSTOMERS |  | 161780 | 98956.0850034206 | 127821.943261095 | [8 empty] | 615 |  | 685 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 97680 | [8 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | DISTRIBUTION EMPLOYEE NOTIFIED ONE OF OUR FIELD EMPLOYEES |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT CAUSED BY THIRD PARTY | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [7 empty] | FARMER | FARM EQUIPMENT | AGRICULTURE | NO |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | YES | 22 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | JOHNNY L. CAVITT | DOT COMPLIANCE MANAGER | johnny.cavitt@centerpointenergy.com | 318-429-3606 | 318-429-3927 |  |  |  | JOHNNY L. CAVITT | DOT COMPLIANCE MANAGER | 318-429-3606 | johnny.cavitt@centerpointenergy.com | ON APRIL 15 A FARMER PULLING LEVEES ON HIS FIELD IN ST. FRANCIS COUNTY BETWEEN GOODWIN AND WHEATLEY ARKANSAS, SEVERED CEGT/S 4" JM-20 PIPELINE AT STATIONING 590+36. CEGT WAS NOTIFIED AT 17:30 HRS. AND ARRIVED ON SITE AT 18:15 HRS. EMERGENCY RESPONDERS CLOSED HIGHWAY 70 THAT WAS WITHIN 100 YARDS OF THE LEAK SITE AT 18:57 HRS. HIGHWAY 70 WAS REOPENED AT 20:37 BY EMERGENCY RESPONDERS. REPAIRS WERE COMPLETED ON APRIL 16 AT 03:37 HRS. AT 15:45 JM-20 WAS LOADED AND ALL CEGT MEASUREMENT FACILITIES WERE PURGED AND LOADED SO THE DISTRIBUTION COMPANY COULD BEGIN TO RELIGHT CUSTOMERS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100025 | 15026 | 2010-05-19 09:30 | ORIGINAL FINAL | 3 | ACADIAN GAS PIPELINE SYSTEM | 1100 LOUISIANA ST. | HOUSTON | TX | 77002 | 2010-04-19 09:27 | 2010 |  |  | 29.9242 | -91.1239 | 937511 | 2010-04-19 16:00 |  | NATURAL GAS |  | 6838 | 2234 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-04-19 14:41 | 2010-05-03 11:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-04-19 09:27 | 2010-04-19 11:58 | ONSHORE | LA | 70339 | PEIRRE PART | ASSUMPTION | SURVEY STATION NO. | 250+20 | 12" LAKE VERRET PIPELINE | 307-0308 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | YES | [6 empty] | YES | UNCASED |  | 7 | BELOW WATER, PIPE BURIED BELOW BOTTOM (NOT IN BORED/DRILLED CROSSING) | [11 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12.75 |  | 0.25 | 42000 | API 5LX | LONGITUDINAL ERW - HIGH FREQUENCY |  | LONESTAR | OTHER | SOMASTIC, WITH CONCRETE | [27 empty] | 1964 | 1964 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 277 |  | NO | NO | NO |  | 0 | 0 | 8579 | 10238.2723965911 | 26258 | 16188.1844660194 | 322826 | 385264.077946373 | 0 | 0 | 0 | 0 |  |  | 357663 | 198329.040751743 | 411690.534808983 | [8 empty] | 808 |  | 909 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 47505 | NO | [5 empty] | YES | PIG TRAPS NOT INSTALLED DURING PIPELINE INSTALLATION. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS UNDETECTABLE DUE TO THE SMALL AMOUNT OF LEAKAGE. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [146 empty] | NATHAN L. GRAY JR. | PIPELINE COMPLIANCE SPECIALIST | ngray@eprod.com | 9858041376 |  |  |  |  | NATHAN L. GRAY JR. | PIPELINE COMPLIANCE SPECIALIST | 9858041376 | ngray@eprod.com | PUBLIC NOTIFIED GAS CONTROL CENTER OF A LEAKING PIPELINE NEAR EAST LAKE VERRET AREA. CONTROL CENTER NOTIFIED OPERATIONS OF A POSSIBLE LEAK ON OUR 12" LAKE VERRET PIPELINE. OPERATIONS INVESTIGATED AND CONFIRMED LEAK ON THE 12" LAKE VERRET PIPELINE. OPERATIONS ISOLATED AND DEPRESSURED PIPELINE SEGMENT, INSTALLED 18" WELD SLEEVE OVER LEAK AREA. PURGED PIPELINE AND RETURNED TO SERVICE. NOTE: PART A, STREET ADDRESS SHOULD BE 338 NOT 514.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20100026 | 15879 | 2010-05-28 15:30 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2010-05-06 15:15 | 2010 |  |  | 41.8019 | -85.5865 | 939431 | 2010-05-07 08:48 |  | NATURAL GAS |  | 114.5 | 5414.5 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-05-06 15:40 | 2010-05-08 13:30 |  |  |  |  | NO |  |  |  |  | NO | [7 empty] | 2010-05-06 15:15 | 2010-05-06 15:15 | ONSHORE | MI | 49099 | WHITE PIGEON | SAINT JOSEPH |  |  | WHITE PIGEON COMPRESSOR STATION |  | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [8 empty] | CARBON STEEL |  | OTHER | [8 empty] | VALVE STEM TOP PLATE BROKE, ALLOWING VALVE TO BE TURNED MORE THAN 1/4 TURN. VALVE STEM CAME OUT OF VALVE. | CLASS 1 LOCATION | NO |  | 621 |  | NO | NO | NO |  | 0 | 0 | 31723 | 37858.575036375 | 687 | 423.538834951456 | 18600 | 22197.443358969 | 0 | 0 | 0 | 0 |  |  | 51010 | 28006.399073321 | 60479.5572302955 | [8 empty] | 595 |  | 900 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LOCAL OPERATING PERSONNEL WERE EXECUTING A LOCAL WORK ORDER TO CHANGE THE POSITION OF THE EMERGENCY FUEL LINE VALVE AND MAKE A TIE-IN TO A NEW COMPRESSOR UNIT UNDER CONSTRUCTION. THE INCIDENT WAS NOT CAUSED BY AND THERE WAS NO CONTRIBUTION TO THE INCIDENT BY CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES. | [12 empty] | YES | 4 | 0 | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | VALVE STEM TOP PLATE BROKE, ALLOWING VALVE TO BE TURNED MORE THAN 1/4 TURN. VALVE STEM CAME OUT OF VALVE. | [15 empty] | YES | VALVE STEM TOP PLATE BROKE, ALLOWING VALVE STEM TO COME OUT OF VALVE. | [161 empty] | ALAN M. CHICHESTER | GAS REGULATORY SERVICES ENGINEER | alan.chichester@cmsenergy.com | 989-791-5841 |  |  |  |  | TRACY A. GOBLE | REGULATORY AND COMPLIANCE MANAGER | 517-768-3187 | tracy.goble@cmsenergy.com | ON MAY 6, 2010, DURING TIE-IN OF THE EMERGENCY FUEL LINE TO A NEW COMPRESSOR UNIT THE 2 INCH VALVE ON THE EMERGENCY FUEL LINE EXPERIENCED AN EQUIPMENT FAILURE. THE 2 INCH VALVE'S TOP PLATE BROKE, ALLOWING THE VALVE STEM TO BE ROTATED PAST THE 1/4 STOP POSITION. THIS IN TURN ALLOWED THE VALVE STEM TO COME OUT OF THE VALVE. TO MAKE THE REPAIR IT WAS NECESSARY TO ISOLATE AND BLOW DOWN APPROXIMATELY 5 MILES OF 30 INCH TRANSMISSION LINE THAT WAS OPERATING AT 595 PSIG. THE REPAIRS WERE COMPLETED ON MAY 8, 2010 AND THE UNIT WAS RETURNED TO SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100027 | 15956 | 2010-06-02 16:49 | SUPPLEMENTAL FINAL | 6660 | GREAT LAKES GAS TRANSMISSION CO | 700 LOUISIANA STREET | HOUSTON | TX | 77002 | 2010-05-03 10:15 | 2010 |  |  | 47.5853 | -95.2051 | 939772 | 2010-05-10 17:43 |  | NATURAL GAS |  | 25 | 100 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | COMPRESSOR UNIT WAS SHUTDOWN. STATION AND PIPELINE REMAINED OPERATIONAL. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-05-03 10:15 | 2010-05-03 10:15 | ONSHORE | MN | 56676 | SHEVLIN | CLEARWATER | MILEPOST | 131.4 | SHEVLIN COMPRESSOR STATION (CS 3) |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | WELD/FUSION | [19 empty] | FILLET WELD | [18 empty] | 1992 |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 800 |  | NO | NO | NO |  | 0 | 0 | 400 | 477.364373311162 | 100 | 61.6504854368932 | 96000 | 114567.449594679 | 0 | 0 | 0 | 0 |  |  | 96500 | 52872.5211371728 | 115106.464453427 | [8 empty] | 974 |  | 1000 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS MINOR AND THE CONCENTRATION OF GAS IN AIR WAS NOT AT A LEVEL DETECTABLE BY THE COMPRESSOR BUILDING GAS MONITORS. THUS, NO ALARMS SETPOINTS WERE REACHED. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | YES |  |  |  | YES | MECHANICAL VIBRATION |  | YES | [14 empty] | YES | [63 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | ROBERT CADORIN | REGIONAL COMPLIANCE SPECIALIST | robert_cadorin@transcanada.com | 248-205-7669 | 248-205-5369 |  |  |  | ROBERT CADORIN |  | 248-205-7669 | No Email Address | DURING A ROUTINE WALK-THROUGH OF THE COMPRESSOR UNIT 303 BUILDING, A STATION TECHNICIAN WAS ABLE TO SMELL GAS IN THE COMPRESSOR BUILDING. THE TECHNICIAN HAD THE UNIT SHUTDOWN AND UNIT PIPING EVACUATED OF GAS. THE PIPING WAS THEN REPRESSURIZED TO A POINT WHERE THE GAS LEAK COULD BE HEARD AND DETECTED USING A PORTABLE LEAK DETECTOR. THE LEAK WAS EMANATING AT A FILLET WELD THAT CONNECTED A WELD-O-LET TO THE DISCHARGE HORN PIPING OF THE UNIT GAS COMPRESSOR. THE PIPING WAS THEN DEPRESSURIZED TO ALLOW FOR FURTHER ANALYSIS. A MAGNETIC PARTICLE EXAMINATION OF THE FILLET WELD REVEALED A CIRCUMFERENTIAL CRACK AROUND PART OF THE BASE OF THE WELD. DUE TO UNCERTAINTY OF THE INTEGRITY OF THE PIPE (CONTAINING THE WELD-O-LET) AND AN ASSOCIATED FLANGE, IT WAS DECIDED TO REMOVE AND REPLACE THE AFFECTED PIPE SEGMENT AND FLANGE. THE REMOVED MATERIAL WAS SENT TO A LABORATORY FOR ANALYSIS, WHICH DETERMINED THAT THE FRACTURE MECHANISM CAUSING THE THROUGH-WALL CRACK ON THE 30-INCH HEADER PIPE (DISCHARGE HORN) WAS HIGH CYCLE, LOW STRESS FATIGUE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100028 | 15926 | 2010-06-02 18:03 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | TX | 77002 | 2010-05-06 14:46 | 2010 |  |  | 28.32 | -91.59 | 939401 | 2010-05-06 14:46 |  | NATURAL GAS |  | 1507 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | COMPANY HAS TO RECON LINE IN ORDER TO CONFIRM LEAK ON FACILITIES | [6 empty] | NO |  |  |  |  | NO | [9 empty] | OFFSHORE | [28 empty] | 225 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EUGENE ISLAND | 307 | BELOW WATER, PIPE ON OR ABOVE SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 |  | 0.375 | 52000 | API | OTHER | UNKNOWN | KAISER | OTHER | UNKNOWN | [27 empty] | 1978 | 1978 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 398 |  | NO | NO | NO |  | 0 | 0 | 10000 | 11934.109332779 | 10000 | 6165.04854368932 | 390000 | 465430.263978383 | 0 | 0 | 0 | 0 |  |  | 410000 | 225514.429244201 | 483529.421854851 | [8 empty] | 950 |  | 1300 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 23000 | NO |  | YES |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | AIR PATROL |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  | YES |  |  |  |  | YES | [5 empty] | YES |  |  |  | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | LOUIS SALINAS | REGULATORY COMPLIANCE | louis_salinas@transcanada.com | 832-320-5305 | 832-320-6305 |  |  |  | LOUIS SALINAS |  | 832-320-5305 | No Email Address | A LEAK WAS SUSPECTED AFTER BUBBLES WERE SPOTTED IN THE EI 307A AREA. THE PRODUCER (DYNAMIC) SHUT IN AND THE BUBBLES STOPPED. THE LEAK WAS IN THE AREA OF THE ANR 16-IN LINE 607 LINE, FROM EI BLK. 307A TO EI BLK. 305. A DIVING BOAT WAS MOBILIZED TO INSPECT THE AREA AND ASSESS THE PIPELINE CONDITION FOR A REPAIR METHOD. FOLLOWING A DIVER INSPECTION, THE PIPELINE WAS REPAIRED, USING A BOLT-ON REPAIR CLAMP. THE REPAIRED SECTION WAS LEAK TESTED AND THE LINE WAS PLACED BACK INTO SERVICE ON JUNE 23. 2010.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100029 | 15030 | 2010-06-03 16:11 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 569 BROOKWOOD CENTER | BIRMINGHAM | AL | 35209 | 2010-03-08 10:00 | 2010 |  |  | 28.6 | -92.5834 | 937446 | 2010-04-19 09:31 |  | NATURAL GAS |  | 4266 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-03-09 08:45 | 2010-04-24 08:00 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 0 | 2010-03-08 10:00 | 2010-03-08 15:00 | OFFSHORE | [28 empty] | 150 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | VERMILLIION | 241 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 20 |  | 0.6 | 60000 | API 5L | OTHER | UNKNOWN |  | OTHER | ASPHALT WITH CONCRETE OVERLAY | [27 empty] | 1970 | 1969 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 560 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 23760 | 14648.1553398058 | 271000 | 323414.362918312 | 0 | 0 | 0 | 0 |  |  | 294760 | 163642.134227186 | 338062.518258118 | [8 empty] | 740 |  | 1250 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 31680 | NO |  |  | YES | YES |  | YES | OFFSHORE PIPELINE | YES |  |  |  |  | YES | OFFSHORE PIPELINE | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | AIR PATROL |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAKING FACILITY WAS 65 MILES OFFSHORE AND IN 150 FEET OF WATER, GOM. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  | YES |  |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KENNETH C. PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | ken.peters@elpaso.com | 2053257554 | 2053253729 |  |  |  | KENNETH C. PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | 2053257554 | ken.peters@elpaso.com | DUE TO POOR 3RD PARTY REPORTING OF LEAK COORDINATES, WEATHER CONDITIONS AND CLOSE PROXIMITY TO THE SUBSEA CONNECTION, CONFIRMATION OF A REPORTABLE LEAK WAS DELAYED. THE INITIAL REPORT WAS RECEIVED MARCH 8, 2010 AT 10:00 AM CST. TGP BEGAN TRYING TO LOCATE THE LEAK BUT ISOLATED THE SUSPECTED 20" 509A-1100 PIPELINE EVEN THOUGH A LEAK WAS NOT CONFIRMED. THE LEAK WAS EXTREMELY SMALL WITH THE PIPELINE LOSING APPX. 10 PSI PER DAY. ON MARCH 12, 2010 A LEAK WAS LOCATED IN CLOSE PROXIMITY TO A SUBSEA CONNECTION AND A MAINTENANCE (TIGHTNESS TYPE) LEAK WAS SUSPECTED. SEVERAL ATTEMPTS WERE MADE TO DIVE ON THE LOCATION WITH ULTIMALTE SUCCESS TO REPAIR IT BY APRIL 19, 2010. A PIN HOLE IN THE 6:00 POSITION WAS IDENTIFIED VERY CLOSE TO THE SUBSEA CONNECTION MOST LIKELY CAUSED BY INTERNAL CORROSION. PROBLEMS ENCOUNTERED IN ATTEMPTING TO MAKE A SUCCESSFUL DIVE INCLUDED INCLEMENT WEATHER AND DIFFICULTY IN OBTAINING PRODUCER PLATFORM BOARDING AGREEMENTS.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20100030 | 16724 | 2010-06-04 15:34 | SUPPLEMENTAL FINAL | 18646 | ENBRIDGE OFFSHORE (GAS TRANSMISSION) LLC | 1100 LOUISIANA ST. SUITE 3300 | HOUSTON | TX | 77002 | 2010-05-07 15:45 | 2010 |  |  | 28.2859 | -92.5686 | 939515 | 2010-05-07 16:15 |  | NATURAL GAS |  | 45035 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-05-07 18:00 | 2010-05-11 17:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-05-07 15:45 | 2010-05-10 13:45 | OFFSHORE | [28 empty] | 215 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | VERMILION | 321 | BELOW WATER, PIPE ON OR ABOVE SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 6.625 |  | 0.28 | 42000 | API 5L | SEAMLESS |  | HENGYANG VALIN STEEL TUBE CO., LTD | EPOXY | [28 empty] | 2009 | 2008 | CARBON STEEL |  | OTHER | [8 empty] | SEPERATION DUE TO THIRD PARTY DAMAGE | CLASS 1 LOCATION | NO |  | 20 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 180000 | 110970.873786408 | 0 | 0 | 137000 | 163497.297859073 | 144000 | 171851.174392018 | $17000 ADMINISTATIVE COST, $127000 LOST REVENUE |  | 461000 | 268982.341236608 | 446319.346037499 | [8 empty] | 800 |  | 1200 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 153352 | NO | YES |  |  |  |  | YES | 6" TO 22" PIPE DIAMETER CHANGE | NO | [6 empty] | OFFSHORE GATHERING | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY DAMAGE | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [103 empty] | OTHER OUTSIDE FORCE DAMAGE | [9 empty] | THIRD PARTY VESSEL CLEANING UP SEA FLOOR ASSOCIATED WITH PLATFORM ABANDONDMENT SCOPE CLEAN UP REQUIRED BY MMS. DRAGGING METAL MESH NETS TO INSURE CLEAN FLOOR. | [251 empty] | CHRISTINE STORM | WESTERN GULF OPERATIONS MANAGER | christine.storm@enbridge.com | 337-569-2286 |  |  |  |  | GREGG JOHNSON | COMPLIANCE MANAGER | 713-353-6369 | gregg.johnson@enbridge.com | W&T (THE VR320 PLATFORM PRODUCER) HIRED A VESSEL THE 'LIA JANE' TO DRAG METAL "GORILLA" NETS IN A 1300' RADIUS AROUND THE ABANDONED VR320 PLATFORM SITE. WHILE DRAGGING THE METAL NETS, SOMETHING WAS SNAGGED. WHILE THE VESSEL CREW WORKED TO "UN-SNAG" THE NET, THEY OBSERVED A LARGE GAS RELEASE, APPROXIMATELY 1/2 MILE TO THE WEST OF THEIR LOCATION. THE GAS RELEASE WAS 50' HIGH BY 100' WIDE BUT THERE WAS NO SHEEN. THE ENBRIDGE GAS CONTROL CENTER IMMEDIATELY NOTICED THE DROP IN PRESSURE ON THE STINGRAY 22" PIPELINE AND SUBSEQUENTLY INITIATED THE INCIDENT COMMAND PROCEDURE WHICH RESULTED IN THE IMMEDIATE SHUT-IN OF PRODUCTION INTO THE 22" AND BLOW-DOWN OF THE 22" PIPELINE (FROM THE INCIDENT LOCATION TO THE TERMINATION OF THE 22" PIPELINE AT WC509 COMPRESSOR STATION). DIVERS LATER CONFIRMED THE DAMAGE WAS ON A 6" PIPELINE THAT GOES OUT TO THE VERMILION 326 PLATFORM.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100031 | 15377 | 2010-06-04 17:49 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | TX | 77002 | 2010-05-10 07:47 | 2010 |  |  | 28.3207 | -91.591 | 939668 |  |  | NATURAL GAS |  | 1000 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | COMPANY FLEW RECON FLIGHT IN ORDER TO CONFIRM LEAK ON FACILITIES | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 |  |  | OFFSHORE | [28 empty] | 225 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EUGENE ISLAND | 307A | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 |  | 0.375 | 52000 | API | OTHER | UNKNOWN | KAISER | OTHER | [28 empty] | 1978 | 1978 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 398 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 10000 | 6165.04854368932 | 200000 | 238682.186655581 | 125000 | 149176.366659738 | 100000 | 119341.09332779 | INVESTIGATION |  | 435000 | 239209.606961931 | 513364.695186799 | [8 empty] | 950 |  | 1300 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 23200 | NO |  | YES |  | YES |  | YES | 10-IN. PLATFORM PIPING INTO A 16-IN. RISER AT THE +40 FT. LEVEL INTO A 16-IN CAMERON COLLET CONNECTOR. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | AIR PATROL |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  | YES |  |  |  |  | YES | [5 empty] | YES |  |  |  | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | LOUIS SALINAS |  | louis_salinas@transcanada.com | [5 empty] | LOUIS SALINAS |  | 832-320-5305 | No Email Address | A SECOND LEAK WAS SUSPECTED AFTER BUBBLES WERE SPOTTED IN THE EI 307A AREA. THE LEAK WAS IN THE AREA OF THE ANR 16-IN LINE 607 LINE, FROM EI BLK. 307A TO EI BLK. 305. THE BUBBLES WERE IN CLOSE PROXIMITY TO A PREVIOUS REPAIR AND CLAMP LOCATION OCCURRING IN 2009. A DIVING BOAT WAS MOBILIZED TO INSPECT THE AREA AND ASSESS THE PIPELINE CONDITION FOR A REPAIR METHOD. THE REPAIR OF THE LINE WAS COMPLETED ON JUNE 23, 2010 WHEN A REPAIR CLAMP WAS INSTALLED. THE LINE WAS CHECKED FOR LEAKS AND PLACED BACK INTO SERVICE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20100032 | 15952 | 2010-06-10 18:27 | SUPPLEMENTAL FINAL | 12576 | MISSISSIPPI RIVER TRANSMISSION CORP | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2010-05-10 02:00 | 2010 |  |  | 35.8292 | -91.1391 | 939750 | 2010-05-10 14:45 |  | NATURAL GAS |  | 2896 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | DUAL REGULATING METER RUN, ONE SIDE WAS SHUT DOWN THE OTHER KEEP WORKING | [6 empty] | YES |  |  |  |  | NO | [6 empty] | 0 | 2010-05-10 12:30 | 2010-05-10 12:30 | ONSHORE | AR | 72471 | SWIFTON | JACKSON | SURVEY STATION NO. | 17+53 | SWIFTON TB METER # 90023 | MRT LINE A-45-A | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 2008 |  | CARBON STEEL |  | LEAK | [9 empty] | CLASS 1 LOCATION | NO |  | 37 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 11585 | 7142.20873786408 | 2750 | 3281.88006651424 | 0 | 0 | 0 | 0 |  |  | 14335 | 8911.12165251019 | 10424.0888043783 | [8 empty] | 481 |  | 1000 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [52 empty] | LIGHTNING |  |  | DIRECT HIT |  |  | NO | [306 empty] | JOHNNY L. CAVITT | DOT COMPLIANCE MANAGER | johnny.cavitt@centerpointenergy.com | 318-429-3606 | 318-429-3927 |  |  |  | JOHNNY L. CAVITT | DOT COMPLIANCE MANAGER | 318-429-3606 | johnny.cavitt@centerpointenergy.com | THIS EVENT WAS REPORTED BECAUSE IT WAS CONSIDERED SIGNIFICANT IN THE JUDGMENT OF THE OPERATOR, EVEN THOUGH THIS EVENT DID NOT MEET THE CRITERIA OF THE DEFINITION OF AN INCIDENT IN §191.3 PARAGRAPHS (1)(I) OR (1)(II), IT WAS REPORTED BECAUSE IT WAS CONSIDERED SIGNIFICANT IN THE JUDGMENT OF THE OPERATOR SINCE WE EXPERIENCED AN IGNITION OF LEAKING GAS. AT 1230 ON MAY 10, 2010 AN MRT EMPLOYEE ARRIVED AT THE SWIFTON M&R STATION ON LINE A-45-A TO REPLACE A LOCK AND DISCOVERED THE RELIEF VALVE VENTING. HE FOUND UPON ENTERING THE BUILDING THAT THE CONTROLLER FOR THE PRIMARY REGULATOR WAS ENGULFED IN FLAMES. FIRE WAS EXTINGUISHED AND REGULATOR WAS ISOLATED. THE SECOND CUT REGULATOR BEGAN TO REGULATE AND THE RELIEF VALVE STOPPED VENTING. THE SUPPLY LINE TO THE CONTROLLER FOR THE PRIMARY REGULATOR HAD A HOLE IN IT, APPARENTLY FROM HIGH VOLTAGE (LIGHTNING) ARCING BETWEEN IT AND THE PIPING TO THE REGULATOR RESULTING IN A FIRE THAT ENGULFED THE CONSTANT BLEED CONTROLLER CAUSING IT TO FAIL. ALL TUBING AND PIPING IN THIS FACILITY WERE INSULATED FOR CP REASONS. THE INSULATOR FOR THE SUPPLY TUBING THAT DEVELOPED A HOLE WAS DOWNSTREAM OF THE INSULATOR FOR THE MAIN GAS PIPING. WHEN THE HIGH VOLTAGE INTRODUCED INTO THE PIPING AND TUBING THERE WAS A LARGE POTENTIAL DIFFERENCE BETWEEN THE TWO RESULTING IN THE ARCING. THE PRIMARY REGULATOR WAS REPLACED WITH A FISHER 627 (SPRING OPERATED), ELIMINATING NEED FOR SUPPLY TUBING.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20100033 | 16021 | 2010-06-15 11:56 | SUPPLEMENTAL FINAL | 5304 | FLORIDA GAS TRANSMISSION CO | 5444 WESTHEIMER ROAD | HOUSTON | TX | 77056 | 2010-05-18 00:34 | 2010 |  |  | 26.8387 | -80.1271 | 940633 | 2010-05-18 09:00 |  | NATURAL GAS |  | 3 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-05-18 06:40 | 2010-05-19 12:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-05-18 05:48 | 2010-05-18 06:40 | ONSHORE | FL | 33418 | PALM BEACH GARDENS | PALM BEACH | MILEPOST | 828.3 | PALM BEACH COUNTY (GARDENS) | 030065 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1991 |  | CARBON STEEL |  | OTHER | [8 empty] | GAS SERVICE LOST TO CUSTOMER | CLASS 2 LOCATION | NO |  | 73 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 12 | 7.39805825242718 | 0 | 0 | 8000 | 9547.28746622324 | 0 | 0 |  |  | 8012 | 4390.12677258629 | 9554.68552447567 | [8 empty] | 100 |  | 700 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | OTHER | NOTIFICATION FROM CUSTOMER |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  | YES | CONTROLLERS ACTIONS WERE NOT CONSIDERED TO BE EFFECTED BY FATIGUE. | YES | YES |  |  |  |  | YES |  |  | YES | 6 | 0 | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [204 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE |  |  |  | YES |  |  |  |  | OTHER MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | INCIDENT DID NOT MEET REPORTING THRESHOLDS, HOWEVER WAS SIGNIFICANT IN THE JUDGMENT OF THE OPERATOR BECAUSE IT RESULTED IN THE LOSS OF NATURAL GAS SERVICE TO APPROXIMATELY 10,000 TAMPA ELECTRIC COMPANY CUSTOMERS. SUPPLEMENTAL REPORT TO FOLLOW. THIS INCIDENT IS BEING CLOSED BECAUSE IT DID NOT MEET THE REPORTING THRESHOLD. THERE ARE NO UPDATES TO ADD. **THIS REPORT IS BEING SUBMITTED IN RESPONSE TO PHMSA'S REQUEST, (DOCKET ID PHMSA-2013-0028), FOR SUPPLEMENTAL REPORTS FROM OPERATORS WHO SUBMITTED REPORTS FOR INCIDENTS OCCURRING AFTER JANUARY 1, 2010, WITH ANY OF THE FOLLOWING: (1) ``PIPE GIRTH WELD'' WAS SELECTED AS THE ``ITEM INVOLVED IN INCIDENT'' IN PART C3 OF THE REPORT. THE REVISED REPORT COLLECTS DATA ABOUT THE PIPE ADJACENT TO THE GIRTH WELD. (2) ``FUNCTION OF PIPELINE SYSTEM'' IS NULL IN PART E5F OF THE REPORT. THE REVISED REPORT COLLECTS THE FUNCTION OF THE PIPELINE SYSTEM FOR ALL INCIDENTS.** THIS SUPPLEMENTAL REPORT IS TO ACKNOWLEDGE THAT THE TWO RELEVANT SECTIONS IN PHMSA'S REQUEST HAVE BEEN REVIEWED AND NO FURTHER ACTIONS WERE NEEDED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100034 | 16833 | 2010-06-25 16:11 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2010-05-29 10:35 | 2010 |  |  | 29.0579 | -90.2849 | 942098 | 2010-05-29 10:55 |  | NATURAL GAS |  | 897 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-05-29 15:00 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-05-29 10:10 | 2010-05-29 10:10 | OFFSHORE | [28 empty] | 20 | IN STATE WATERS | LA | SOUTH TIMBALIER | UNKNOWN | LAFOURCHE |  |  |  | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12.75 |  | 0.375 | 42000 | API 5L OR EQUIVALENT | SEAMLESS |  | US STEEL | COMPOSITE | [28 empty] | 1973 | 1973 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 314 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 3592 | 2214.4854368932 | 219166 | 261555.100602785 | 50000 | 59670.5466638952 | 1781437 | 2125986.39274579 | PROJECTED COST FOR ABANDONMENT |  | 2054195 | 1125630.75814561 | 2449426.52544936 | [8 empty] | 750 |  | 1440 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 24311 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE WAS BEING MANUALLY CONTROLLED AT THE TIME FOR GAS DIVERSION. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ROUTINE OR NORMAL FISHING OR OTHER MARITIME ACTIVITY NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | FISHING OR MARITIME ACTIVITY | [103 empty] | ROUTINE OR NORMAL FISHING OR OTHER MARITIME ACTIVITY NOT ENGAGED IN EXCAVATION | [261 empty] | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | ken.peters@elpaso.com | 2053257554 | 2053253729 |  |  |  | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | 2053257554 | ken.peters@elpaso.com | FOR OPERATIONAL FLEXIBILITY, GAS WAS DIVERTED FROM ONE PIPELINE INTO TENNESSEE GAS PIPELINE COMPANY'S 12" 524C-900 LINE LOCATED IN THE SOUTH TIMBALIER AREA OF THE GULF OF MEXICO, STATE WATERS. AFTER DIVERSION WAS COMPLETE, BUBBLES WERE NOTED IN THE WATER INDICATING A POSSIBLE LEAK COMING FROM THE 524C-900 PIPELINE. THE LINE WAS SHUT IN AND VACATED OF GAS. INVESTIGATION BY DIVERS REVEALED THE CAUSE OF THE INCIDENT TO LIKELY BE DAMAGE FROM FISHING ACTIVITIES DUE TO THE PRESENCE OF SHRIMP NETS AND VISUAL DAMAGE TO THE COATING THAT COULD HAVE BEEN CAUSED BY AN ANCHOR OR ANOTHER BLUNT DEVICE POSSIBLY USED BY FISHERMEN TO RETRIEVE A NET. THE PIPELINE WILL REMAIN OUT OF SERVICE AND IS SLATED FOR ABANDONMENT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100035 | 15174 | 2010-06-30 16:38 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 2 BRENTWOOD COMMONS, SUITE 190 | BRENTWOOD | TN | 37027 | 2010-06-06 16:30 | 2010 |  |  | 28.973 | -91.9116 | 943022 | 2010-06-06 17:00 |  | NATURAL GAS |  | 4000 | 1000 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE PIPELINE WAS SHUT IN AT THE PRODUCER PLATFORM. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 |  |  | OFFSHORE | [28 empty] | 65 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SOUTH MARSH ISLAND | 9 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12.75 |  | 0.375 | 46000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | AMERICAN STEEL | OTHER | UNKNOWN | [27 empty] | 1968 | 1968 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 284 |  | NO | NO | NO |  | 0 | 0 | 10000 | 11934.109332779 | 30000 | 18495.145631068 | 225000 | 268517.459987529 | 0 | 0 | 0 | 0 |  |  | 265000 | 147909.427828217 | 298946.714951376 | [8 empty] | 970 |  | 1300 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 93825 | NO |  |  |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | AIR PATROL |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  | YES |  |  |  |  | YES |  |  |  | YES | [5 empty] | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [168 empty] | NO | [63 empty] | YES | 1968 | 2660 | NO | [77 empty] | LOUIS SALINAS | REGULATORY COMPLIANCE | louis_salinas@transcanada.com | 832-320-5305 | 832-320-6305 |  |  |  | LOUIS SALINAS |  | 832-320-5305 | No Email Address | A GAS BOIL WAS REPORTED AT SMI BLOCK 9, LOCATION AT 28 58.4 AND 91 54.7 BY CHEVRON. THE MMS SN IS 2308 AND IS A 12" GAS LINE FROM SM 10, LOCATED ON A PLATFORM THAT BELONGS TO MARINER. THE SUSPECTED LEAK WAS REPORTED BY CHEVRON TO BE 3 MI SW OF SM 288. UPON FURTHER INVESTIGATION, THE LEAK WAS FOUND TO BE ON TRANSCANADA'S LINE NO. 747 IN SOUTH MARSH ISLAND BLOCK 9/287. STEPS WERE TAKEN TO ISOLATE AND DEPRESSURIZE THE PIPELINE, IN ORDER TO BEGIN AN INSPECTION OF THE DAMGE AND PLAN FOR REPAIRS. THE PIPELINE WAS REPAIRED, USING A BOLT-ON REPAIR CLAMP. THE REPAIRED SECTION WAS LEAK TESTED AND THE LINE WAS PLACED BACK INTO SERVICE ON AUGUST 1. 2010.
2021-02-26 10:37 | YES | YES | GT (Gas Transmission) | 20100036 | 16151 | 2010-07-08 07:49 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2010-06-07 14:39 | 2010 |  |  | 32.3147 | -97.6145 | 943140 | 2010-06-07 16:45 |  | NATURAL GAS |  | 172000 |  |  | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES | 0 | 0 | 0 | 7 | 0 | 7 |  | YES |  | 2010-06-07 14:40 | 2010-06-12 17:45 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 0 | 2010-06-07 14:45 | 2010-06-07 15:15 | ONSHORE | TX | 76003 | CLEBURNE | JOHNSON | MILEPOST | 360+00-370+00 | NORTH TEXAS 36" | 225 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 36 |  | 0.406 | 65000 | API5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | FIELD APPLIED EPOXY | [28 empty] | 1970 | 1970 | CARBON STEEL |  | MECHANICAL PUNCTURE | [9 empty] | CLASS 1 LOCATION | NO |  | 805 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 741422 | 457090.262135922 | 287578 | 343198.729370193 | 0 | 0 | 0 | 0 |  |  | 1029000 | 631423.502481839 | 800288.991506116 | [8 empty] | 950 |  | 1051 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | AUTOMATIC | 105600 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | OTHER | NOTIFICATION FROM A PRODUCER ON THE LINE |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 2 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | NO |  |  |  |  | YES | [6 empty] | UTILITY | AUGER | POLE | YES | 101525391 | TEXAS EXCAVATION SAFETY SYSTEMS, INC. | UTILITY OWNER | NO | NO | YES | 123 | OTHER |  |  |  | SEE NARRATIVE IN PART H | [262 empty] | JOEL E. KOHLER | SR STAFF ENGINEER | jkohler@eprod.com | 713-381-4830 | 713-381-6660 |  |  |  | JOEL E. KOHLER | SR STAFF ENGINEER | 713-381-4830 | jkohler@eprod.com | NARRATIVE EXPLANATION FOR PART G3, QUESTION 17: SUBSURFACE UTILITY ENGINEERING PERFORMED BY SURVEY AND MAPPING, INC. FOR A BRAZOS ELECTRIC COOPERATIVE ELECTRIC LINE INSTALLATION PROJECT WAS INADEQUATE, RESULTING IN INACCURATE MAPS USED TO DESIGN THE ELECTRIC LINE PROJECT. EXCAVATOR PLACED ONE CALLS CONTAINING INACCURACIES IN BOTH THE DRIVING DIRECTIONS AND LAT./LONG. DESCRIPTIONS (TICKETS 10152391 AND 101525432). THESE INACCURACIES WERE COMPOUNDED BY MISCOMMUNICATION BETWEEN THE EXCAVATOR AND THE LOCATOR ON JUNE 7, 2010. THE LOCATOR CLOSED THE TICKET WITH NOTATION OF "NO CONFLICT" BASED ON HIS UNDERSTANDING THAT THE WORK WAS IN A DIFFERENT LOCATION AND SPECIFICALLY NOT ON THE "GEORGE'S CREEK RANCH" WHERE THE INCIDENT LATER OCCURRED. THE EXCAVATOR'S ON-SITE REPRESENTATIVE WAS INADEQUATELY TRAINED. THE EXCAVATOR COMMENCED EXCAVATION WITHOUT POSITIVE RESPONSES FOR BOTH TICKETS AND FAILED TO MAKE THE SHORT NOTICE ONE-CALL REQUIRED BY STATUTE.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20100038 | 16099 | 2010-07-08 07:51 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2010-05-04 15:20 | 2010 |  |  | 28.1524 | -96.1931 | 935981 | 2010-05-04 16:00 |  | NATURAL GAS |  | 3000 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-05-04 15:50 | 2010-05-05 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-05-04 15:20 | 2010-05-05 09:00 | OFFSHORE | [28 empty] | 50 | IN STATE WATERS | TX | MATAGORDA BAY | 560 | MATAGORDA |  |  |  | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12.75 |  | 0.375 | 42000 | API5L | OTHER | UNKNOWN | UNKNOWN | OTHER | CONCRETE UNDERWATER | [27 empty] | 1983 | 1983 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 293 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 298352.733319476 | 0 | 0 | 0 | 0 |  |  | 250000 | 136951.777177302 | 298352.733319476 | [8 empty] | 850 |  | 1250 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 31680 | YES | [7 empty] | NO | [6 empty] | TYPE A GATHERING | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A MINOR LEAK CAUSE CORROSION | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | THE SECTION PIPELINE IS IN THE GULF OF MEXICO AND HAS BEEN ABANDONED IN PLACE. THE SUSPECTED CAUSE WAS INTERNAL CORROSION BECAUSE THIS WAS A STAGNANT SECTION |  | YES | [6 empty] | YES | BECAUSE THIS IS A STAGNANT SECTION, WE ARE TAKING THE ASSUMPTION THAT LIQUID BUILDUP CAUSE THE CORROSION. THE SECTION WAS ABANDONED IN PLACE. |  |  |  |  | YES | END SECTION OF A LINE UPSTREAM FROM THE ACTIVE PRODUCER TIES. | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | NATHAN L. GRAY JR. | SENIOR PIPELINE COMPLIANCE SPECIALIST | ngray@eprod.com | 9858041376 |  |  |  |  | NATHAN L. GRAY JR. | SENIOR PIPELINE COMPLIANCE SPECIALIST | 9858041376 | ngray@eprod.com | A PIPELINE TECHNICIAN DISCOVERED AN OFFSHORE NATURAL GAS RELEASE ON ENTERPRISE PIPELINE X1-300, A NATURAL GAS GATHERING PIPELINE. THE TECHNICIAN NOTICED BUBBLES COMING TO THE SURFACE. THIS WAS DRY GAS WITH NO SHEEN NOTICEABLE. THE LEAK OCCURRED ON A STAGNANT PORTION OF THE PIPELINE. THE PIPELINE WAS ISOLATED AND THE STAGNANT PORTION OF LINE WITH THE LEAK WAS ABANDONED. THIS SECTION WAS ALREADY SCHEDULED TO BE ABANDONED IN LATE 2010. THE SUSPECTED CAUSE IS INTERAL CORROSION. THE ABANDONMENT OPERATIONS WERE FINALIZED ON SEPTEMBER 20, 2012.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100039 | 16807 | 2010-07-14 16:51 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2010-06-23 09:22 | 2010 |  |  | 44.4866 | -93.2223 | 945138 | 2010-06-23 10:45 |  | NATURAL GAS |  | 1000 | 17933 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-06-24 08:00 | 2010-06-25 19:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 5 | 2010-06-23 09:28 | 2010-06-23 10:05 | ONSHORE | MN | 55057 | NORTHFIELD | DAKOTA | MILEPOST | 95.89 | 30-INCH D LINE | MNM80104 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 84 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 |  | 0.375 | 75000 | API 5L | SINGLE SAW |  | BERG STEEL PIPE CO. | EPOXY | [28 empty] | 2009 | 2008 | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | 9000 SERIES GARLOCK FLANGE GASKET | LEAK |  |  | OTHER | FLANGE GASKET | [5 empty] | CLASS 1 LOCATION | NO |  | 563 |  | NO | NO | NO |  | 0 | 0 | 89665 | 107007.191332363 | 5295 | 3264.3932038835 | 25335 | 30235.0659945957 | 10000 | 11934.109332779 | 0 | 0 |  |  | 130295 | 71860.2332488452 | 152440.759863622 | [8 empty] | 739 |  | 1000 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 100320 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS FROM AN UNDERGROUND MANUALLY OPERATED VALVE'S FLANGE GASKET. CONTROLLERS DO NOT HAVE ANY REMOTE CONTROL OF THIS PART OF PIPELINES OPERATION. LEAK WAS NOT SIGNIFICANT ENOUGH, WHEN FOUND THAT IT WOULD TYPICALLY BE DETECTED BY ANY CHANGE IN SCADA PRESSURES. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | [204 empty] | EQUIPMENT NOT INSTALLED PROPERLY | [6 empty] | YES | IT APPEARS THAT ENGINEERING STANDARD 7570 JOINING OF PIPE & PIPING COMPONENTS OTHER THAN BY WELDING WAS NOT ADEQUATELY AND SUCCESSFULLY FOLLOWED AS ALL INDICATIONS ARE THAT THE FLANGE, IN WHICH THE GASKET FAILED, WAS NOT CONSISTENTLY TORQUED ON ALL BOLTS AROUND THE FLANGE. | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | BYRON WOOD | SR. PIPELINE SAFETY SPECIALIST | byron.wood@nngco.com | 402-398-7396 | 402-398-7706 |  |  |  | THOMAS CORRELL | DIRECTOR OF PIPELINE SAFETY AND INTEGRITY | 402-398-7715 | thomas.correll@nngco.com | ON JUNE 23, 2010, A LANDOWNER, EUGENE MULLIGAN, CALLED NORTHERN NATURAL GAS COMPANY'S OPERATIONS COMMUNICATION CENTER TO REPORT BLOWING GAS TO ATMOSPHERE AT A VALVE SITE NEAR WHERE HE LIVED. NORTHERN EMPLOYEES IMMEDIATELY RESPONDED. IT WAS DETERMINED THAT IT WAS NATURAL GAS BLOWING FROM NORTHERN'S MNM80104-M500D MAINLINE AT A VALVE SITE AT APPROXIMATE MILEPOST 95.89. PIPELINE PRESSURE ON THE LINE WAS 739 PSIG. THE LINE HAS AN MAOP OF 1,000 PSIG. A PIR OF 563 FEET WAS CALCULATED. LOCAL POLICE ASSISTED WITH BARRICADING OFF 320TH STREET WHICH PASSES BY THE VALVE SITE. THERE WAS NO FIRE, NO EXPLOSION AND NO INJURIES. AS A PRECAUTION 5 PEOPLE WERE EVACUATED FROM RESIDENCES IN THE NEAR AREA. APPROXIMATELY 13 MILES OF C LINE AND 6 MILES OF D LINE WERE SHUT IN TO ENABLE ISOLATION OF THE LINE SEGMENT. AN ATTEMPT WAS MADE TO DRAW GAS PRESSURE DOWN WITH COMPRESSION HORSEPOWER @ THE FARMINGTON COMPRESSOR STATION. AT 490 PSIG COMPRESSION WAS SHUT DOWN DUE TO HIGH ROD LOAD ON UNITS. AN EMERGENCY 1-CALL WAS MADE AND CONTRACTOR PERSONNEL WERE CALLED TO ASSIST WITH REPAIRS. IT WAS DETERMINE THAT LINE WOULD BE BLOWN DOWN TO 50 PSIG FOR OVERNIGHT, ONE PERSON WOULD MAN SITE THRU THE NIGHT. ON JUNE 24 THE LINE WAS BLOWN DOWN TO ZERO PRESSURE. FOUR FARMTAP CUSTOMERS WERE IMPACTED. EXCAVATION WAS COMMENCED AND IT WAS FOUND THAT THERE WAS A SIGNIFICANT FROST BALL. A HOT WATER HYDRO VAC WAS UTILIZED TO REMOVE FROST. INVESTIGATION INDICATED THAT THERE WAS A PORTION OF THE FLANGE GASKET BLOWN OUT, WHICH ALLOWED GAS LEAKAGE. THE FLANGE WAS DISASSEMBLED AND A NEW LAMONS 30" 600 ASME B16 47A, ASME B1620, 304IR GASKET WAS INSTALLED. THE FLANGE BOLTS WERE RE-INSTALLED AND RETORQUED. ADDITIONAL CONCRETE SUPPORT BLOCKS WERE INSTALLED AND ALLOWED TO CURE. ON JUNE 28TH THE LINE WAS PURGED AND SLOWLY RELOADED TO OPERATIONAL PRESSURE, LEAK CHECKED, COATED AND BACKFILLED. A SUPPLEMENTAL FINAL REPORT WILL BE FILED WHEN ALL COST OF REPAIRS IS CALCULATED. FINAL COST WERE CALCULATED AND INITIAL COSTS WERE CHANGED/UPDATED. ON APRIL18,2011 A SUPPLEMENTAL FINAL REPORT WAS FILED AS PHMSA REQUESTED TO PROVIDE ADDITIONAL INFORMATION ON PIPE SPEC'S, PART C, ITEM 3 OF THE REPORT AND COST OF GAS RELEASED UNINTENTIONALLY IN PART D, ITEM 7B. THIS INFORMATION HAS BEEN ADDED TO THIS SUPPLEMENTAL FINAL REPORT AS REQUESTED. SUPPLEMENTAL/FINAL REPORT - THIS REPORT IS BEING FILED AS A SUPPLEMENTAL/FINAL REPORT TO REPORT # 20100039-15215 DATED 08/31/2010 AS A FOLLOW UP TO DISCUSSION WITH PHMSA REPRESENTATIVES. PART A ITEM 7 WAS CHANGED TO MATCH TIME ON THE NRC FORM, THE CAUSE OF THE EVENT WAS CHANGED FROM EQUIPMENT FAILURE TO INCORRECT OPERATIONS. AN ANALYSIS OF THE EVENT INDICATES THAT THERE WAS ADEQUATE, PROPER SUPPORT FOR THE PIPING, NO INDICATION OF SUBSIDENCE AND ALTHOUGH THE GASKET MATERIAL WAS NOT ANALYZED DUE TO IT'S DAMAGED CONDITION, THERE ARE TWO OTHER SIMILAR 30-INCH VALVES WITH THE SAME TYPE OF GASKETS INSTALLED ON THIS PIPING AND NEITHER OF THOSE HAVE HAD ANY PROBLEMS OR LEAKS, THIS IS A VERY GOOD, HIGH QUALITY GASKET. THE LEAKAGE APPEARS TO HAVE BEEN BETWEEN THE 6 O'CLOCK AND 9 O'CLOCK POSITION ONLY. NORTHERN BELIEVES THAT THE ROOT CAUSE OF THIS EVENT IS MOST LIKELY THAT ALL OF THE BOLTS ON THE FLANGE WERE NOT CONSISTENTLY TORQUED WHICH LED TO LEAKAGE, WHICH ULTIMATELY LED TO THE GASKET FAILURE. NORTHERN IS ISSUING A TECHNICAL BULLETIN TO ALL EMPLOYEES, INSPECTORS AND CONSTRUCTION PERSONNEL RE-EMPHASIZING THE IMPORTANCE OF PROPER TORQUEING AND THE REQUIREMENTS OF ENGINEERING STANDARD 7570 WHEN JOINING OF PIPE & PIPING COMPONENTS OTHER THAN BY WELDING. SHOULD THERE BE AN EVENT OF THIS NATURE IN THE FUTURE EVERY EFFORT WILL BE MADE TO ENSURE THAT EVEN THOUGH THE GASKET MATERIAL MAY BE DAMAGED IT WILL BE SENT TO A LABORATORY FOR ANALYSIS TO DETERMINE IF THE QUALITY OF THE GASKET WAS OR IS A FACTOR IN THE EVENT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100040 | 15044 | 2010-07-19 11:43 | ORIGINAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2010-02-21 12:31 | 2010 |  |  | 29.8037 | -91.326 | 931827 | 2010-02-21 13:52 |  | NATURAL GAS |  | 188 | 1365 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | LEAK IS IN REMOTE LOCATION. PIPELINE PRESSURE HAS BEEN REDUCED MORE THAN 20% UNT | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-02-21 16:15 | 2010-02-21 16:15 | ONSHORE | LA | 70522 | CENTERVILLE | ST MARTIN | MILEPOST | 39.17 | INDEX 130 |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 72 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 |  | 0.5 | 52000 | API 5L | FLASH WELDED |  | A O SMITH | ASPHALT | [28 empty] | 1951 | 1951 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 640 |  | NO | NO | NO |  | 0 | 0 | 6744 | 8048.36333402619 | 929 | 572.733009708738 | 335074 | 399880.975057161 | 0 | 0 | 0 | 0 | INITIAL INVESTIGATION: BOATS, DIVERS, EMPLOYEE EXPENSE |  | 342747 | 187844.108601916 | 408502.071400896 | [8 empty] | 780 |  | 936 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 76243 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO NOTICEABLE FLUCTUATION IN PRESSURE OF VOLUMES WAS NOT CAPTURED BY SCADA PARAMETERS. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES |  |  |  |  | YES | OTHER | BRACE WELDED TO PIPE MOVED BACK & FORTH, FROM WEAR ACTION. | [15 empty] | YES | [63 empty] | YES | [6 empty] | YES | [50 empty] | COMBINATION TOOL | 2009 |  |  |  |  | NO |  |  | NO | [13 empty] | NO | [63 empty] | GLENN FLOYD | TECHNICAL SPECIALIST II | glenn.floyd@bwpmlp.com | 9016853471 | 9016853475 |  |  |  | JACK L ADAMS | DIR DOT COMPLIANCE AND SECURITY | 7134798099 | jack.adams@bwpmlp.com | LEAK UNDER 3 FEET OF WATER AND 6 FEET OF MUD. INITIAL INSPECTION FOUND LEAK TO BE UNDER A BRACE. LEAK OCCURRED IN ST MARTIN PARISH. HOWEVER NEAREST CITY/TOWN IS CENTERVILLE LA ST MARY PARISH.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20100041 | 15050 | 2010-07-19 15:32 | SUPPLEMENTAL FINAL | 19570 | WILLIAMS GAS PIPELINE - TRANSCO | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2010-06-21 09:24 | 2010 |  |  | 28.4661 | -95.7281 | 944879 | 2010-06-21 12:30 |  | NATURAL GAS |  | 2305 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-06-21 13:45 | [5 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-06-21 09:24 | 2010-06-23 09:30 | OFFSHORE | [28 empty] | 68 | IN STATE WATERS | TX | BRAZOS | 474 |  |  |  |  | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [5 empty] | SUB SEA TIE IN | 1995 |  | CARBON STEEL |  | LEAK |  |  | OTHER | GREASE CERT BECAME LOOSE | [5 empty] | CLASS 1 LOCATION | NO |  | 98 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 10574 | 6518.92233009709 | 10000 | 11934.109332779 | 90000 | 107406.983995011 | 0 | 0 |  |  | 110574 | 61539.1736540923 | 125860.015657888 | [8 empty] | 1003 |  | 1248 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 145939 | NO | YES | [6 empty] | YES |  |  |  |  | YES | NON-PIGGABLE DUE TO UNDER WATER TIE IN. | TYPE A GATHERING | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS NOT OF A MAGNITUDE TO BE DETECTED BY AUTOMATED EQUIPMENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [6 empty] | YES | GREASE CERT LOOSENED. | [22 empty] | YES | GREASE CERT LOOSENED. | [161 empty] | EDGAR RODRIGUEZ JAMES M HARRISON | P.S.S. PIPELINE INTEGRITY MANAGER | edgar.x.rodriguez@williams.com | 713-215-2846 | 713-215-2222 |  |  |  | MARIE SOTAK | PIPELINE SAFETY MANAGER | 713-215-2111 | marie.sotak@williams.com | FACTUAL INFORMATION LEAK WAS REPORTED TO OPERATOR AT 8:28 A.M. JUNE 21, 2010. IT WAS REPORTED TO HIM BY DISTRICT TEAM IN ROUTE TO PLATFORM. THE LEAK SOURCE WAS FOUND TO BE FROM A GREASE FITTING ON A 4" VALVE IN SSTI OF STUB OF SUB SEA TIE-IN ASSEMBLY THAT WAS LEFT IN PLACE AFTER THE PIPELINE WAS PREVIOUSLY ABANDONED. THERE WAS NO SHEEN ASSOCIATED WITH THE LEAK. THE SSTI IS CONNECTED TO WILLIAMS 30" LINE THAT RUNS FROM BA 538 TO SHORE LINE. NOTIFICATIONS OF THE LEAK WERE MADE TO WGP MANAGEMENT, NRC (NO. 944879 WAS ASSIGNED), COAST GUARD, AND MMS. WGP EMPLOYEES CONTRACTED A DIVING COMPANY, THAT REPAIRED THE LEAK BY INSTALLING BLIND FLANGE BETWEEN LEAKING PLUG AND 30" PIPELINE ON JUNE 24TH, 2010. ROOT CAUSE ANALYSIS WAS PERFORMED & ATTACHED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100042 | 15047 | 2010-07-19 17:22 | ORIGINAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION LP (SPECTRA ENERGY CORP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2010-06-20 12:00 | 2010 |  |  | 28.4419 | -93.195 | 944805 | 2010-06-20 17:49 |  | NATURAL GAS |  | 424 | 22615 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-06-20 12:00 | 2010-06-29 10:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-06-20 12:00 | 2010-06-20 12:00 | OFFSHORE | [28 empty] | 165 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST CAMERON | 513 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 20 |  | 0.406 | 52000 | GIRTH WELD SMAW | SEAMLESS |  | U S STEEL | OTHER | CONCRETE AND SOMASTIC | [27 empty] | 1975 | 1975 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 524 |  | NO | NO | NO |  | 0 | 0 | 158300 | 188916.950737892 | 2968 | 1829.78640776699 | 700000 | 835387.653294534 | 0 | 0 | 0 | 0 |  |  | 861268 | 472079.864058835 | 1026134.39044019 | [8 empty] | 899 |  | 1440 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 81629 | NO | [5 empty] | YES | NO PLATFORMS FROM WHICH TO LAUNCH AND RECEIVE TOOLS | YES |  |  |  |  | YES | NO PLATFORMS FROM WHICH TO LAUNCH/RECEIV | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | THIRD PARTY (PLATFORM OPERATOR) OBSERVATION |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS TOO SMALL TO BE IDENTIFIED BY CONTROL ROOM PERSONNEL. A REVIEW OF OPERATING RECORDS FOUND ABNORMAL OPERATING CONDITIONS DID NOT CAUSE OR CONTRIBUTE TO THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  | YES |  |  |  |  | YES | [7 empty] | YES | ADJACENT TO GIRTH WELD | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DWAYNE TESCHENDORF | PRINCIPAL ENGINEER | deteschendorf@spectraenergy.com | 713-627-5573 | 713-386-4468 |  |  |  | RICK KIVELA | DIRECTOR - OPERATIONAL COMPLIANCE | 713-627-6388 | rwkivela@spectraenergy.com | A THIRD PARTY PLATFORM OPERATOR OBSERVED BUBBLES ON THE SURFACE IN THE GULF OF MEXICO IN WEST CAMERON BLOCK 513 ABOUT 100 MILES SOUTH OF CAMERON, LOUISIANA. ON JUNE 20, 2010, SPECTRA ENERGY PERSONNEL CONFIRMED THE NATURAL GAS LEAK WAS ON THE TEXAS EASTERN TRANSMISSION, LP 20-INCH LINE 41-A-6. THE WATER DEPTH AT THE LEAK SITE WAS APPROXIMATELY 165 FEET. AFTER CONCRETE COATING WAS REMOVED, THE SOURCE OF THE LEAK WAS DETERMINED TO BE A PIN HOLE IN THE PIPE WALL. ULTRASONIC TESTING RESULTS SHOWED NO WALL LOSS OUTSIDE THE IMMEDIATE AREA OF THE PIN HOLE. THE MOST LIKELY CAUSE OF THE LEAK WAS DETERMINED TO BE INTERNAL CORROSION NEAR A GIRTH WELD.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20100043 | 16039 | 2010-07-20 10:57 | SUPPLEMENTAL FINAL | 15105 | PANHANDLE EASTERN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2010-06-22 02:00 | 2010 |  |  | 39.8041 | -87.3486 | 944992 | 2010-06-22 09:00 |  | NATURAL GAS |  | 14800 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | [7 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-06-22 02:16 | 2010-06-22 02:55 | ONSHORE | IN | 47862-8087 | MONTEZUMA | PARKE | MILEPOST | MP 869.4 | MONTEZUMA COMPRESSOR STATION | 200 LINE DISCHARGE RELIEF VALVE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | INSTRUMENTATION | [38 empty] | 2006 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | ELECTRONIC COMPONENT | OTHER | [8 empty] | ELECTRONIC COMPONENT FAILURE RESULTED IN GAS BEING VENTED FROM RELIEF VALVE | CLASS 1 LOCATION | NO |  | 507 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 64495 | 39761.4805825243 | 1600 | 1909.45749324465 | 756 | 902.218665558096 | 0 | 0 |  |  | 66851 | 42513.1659105784 | 42573.156741327 | [8 empty] | 738 |  | 800 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | YES | YES | PHMSA | [20 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EQUIPMENT FAILURE AT A FIELD LOCATION - PROMPT ACTION BY THE CONTROLLER TO DISPATCH PERSONNEL | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [52 empty] | LIGHTNING |  |  | SECONDARY IMPACT SUCH AS RESULTING NEARBY FIRES |  |  | YES |  |  |  | YES | UNPRECEDENTED LIGHTNING PRODUCING STORM | [301 empty] | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | A LIGHTNING STRIKE CAUSED A TRANSDUCER SIGNAL TO SPIKE RESULTING IN A CROSS-BLEED VALVE 1386-4 THAT IT WAS PROVIDING THE SIGNAL FOR TO GO CLOSED. THIS VALVE CLOSURE CAUSED A PRESSURE REDUCTION THAT RESULTED IN ANOTHER DIFFERENT CROSS-BLEED VALVE 1328 3D-2D TO OPEN FULLY IN AN ATTEMPT TO MAINTAIN PRESSURE SET-POINT. WHEN THE TRANSDUCER FOR VALVE 1386-4 RECOVERED AND STARTED PROVIDING A TRUE SIGNAL, CROSS-BLEED VALVE 1386-4 OPENED INCREASING PRESSURE. THE PRESSURE INCREASE WAS TOO FAST FOR CROSS-BLEED VALVE 1328 3D-2D TO RECOVER AND CLOSE, BEFORE THE PRESSURE ROSE TO THE SET-POINT OF THE RELIEF VALVE, RESULTING IN THE RELIEF VALVE OPERATING TO BLEED OFF THE EXCESS PRESSURE. RECORDS INDICATE THAT THE RELIEF VALVE CYCLED OPEN AND CLOSED IN CONJUNCTION WITH THE CROSS-BLEED VALVE, UNTIL EQUILIBRIUM WAS REACHED AND ALL CONTROLS RETURNED TO NORMAL. THE RELIEF VALVE DISPELLED SUFFICIENT GAS TO MAKE THE EVENT REPORTABLE, ONLY BECAUSE OF GAS LOSS. **THIS REPORT IS BEING SUBMITTED IN RESPONSE TO PHMSA'S REQUEST, (DOCKET ID PHMSA-2013-0028), FOR SUPPLEMENTAL REPORTS FROM OPERATORS WHO SUBMITTED REPORTS FOR INCIDENTS OCCURRING AFTER JANUARY 1, 2010, WITH ANY OF THE FOLLOWING: (1) ``PIPE GIRTH WELD'' WAS SELECTED AS THE ``ITEM INVOLVED IN INCIDENT'' IN PART C3 OF THE REPORT. THE REVISED REPORT COLLECTS DATA ABOUT THE PIPE ADJACENT TO THE GIRTH WELD. (2) ``FUNCTION OF PIPELINE SYSTEM'' IS NULL IN PART E5F OF THE REPORT. THE REVISED REPORT COLLECTS THE FUNCTION OF THE PIPELINE SYSTEM FOR ALL INCIDENTS.** PART E5F OF THIS REPORT HAS BEEN COMPLETED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20100044 | 15927 | 2010-07-23 15:35 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2010-06-24 14:00 | 2010 |  |  | 29.8445 | -93.0488 | 945796 | 2010-06-28 12:00 |  | NATURAL GAS |  | 0.01 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | [9 empty] | NO |  |  |  |  | NO | [6 empty] | 0 |  |  | ONSHORE | LA | 70631 | CAMERON | CAMERON |  |  | CHENIERE PERDUE METER STATION |  | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 6.625 |  | 0.28 | 35000 | API | OTHER | UNKNOWN | UNKNOWN | COAL TAR | [28 empty] | 1956 | 1955 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 135 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 1000 | 616.504854368932 | 45000 | 53703.4919975057 | 3000 | 3580.23279983372 | 2000 | 2386.82186655581 | 0 |  | 51000 | 28029.5140115122 | 60287.0515182642 | [8 empty] | 195 |  | 1090 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | PRODUCER CALLED TRANSCANADA TO NOTIFY OF A SUSPECTED LEAK. |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  | YES | [5 empty] | YES | [7 empty] | YES | THE CORROSION IS LOCATED ON A SECTION OF PIPE NEAR A TEE FITTING. | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | LOUIS SALINAS |  | louis_salinas@transcanada.com | 832-320-5305 | 832-320-6305 |  |  |  | LOUIS SALINAS |  | 832-320-5305 | No Email Address | A SUSPECTED LEAK ON ANR'S CHENIER PERDUE METER STATION PIPING WAS APPARENTLY NOTICED FIRST BY THE PRODUCER WHO SUPPLIES THE GAS TO THE METER STATION. THE LEAK WAS LOCATED NEAR THE SOUTH FENCE LINE IN ANR'S METER STATION YARD. UPON EXCAVATING THE PIPE, THE LEAK WAS CONFIRMED. A REPAIR CLAMP WAS INSTALLED ON SEPTEMBER 15, 2010, ON THE DAMAGED AREA OF PIPE, COMPLETING THE REPAIR OPERATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100045 | 15052 | 2010-07-28 16:48 | ORIGINAL FINAL | 31613 | ENBRIDGE PIPELINES (EAST TEXAS) L.P. | 1501 MCKINNEY SUITE 600 | HOUSTON | TX | 77010 | 2010-06-28 11:15 | 2010 |  |  | 30.8905 | -95.0764 | 945772 | 2010-06-28 12:42 |  | NATURAL GAS |  | 0 | 13619 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-06-28 11:15 | 2010-07-08 15:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-06-28 11:15 | 2010-06-28 11:15 | ONSHORE | TX | 77360 | ONALASKA | POLK |  |  |  |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 96 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | PLIDCO SADDLE | 1985 |  | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  |  |  | NO | NO | NO |  | 0 | 0 | 63056 | 75251.7198087716 | 0 | 0 | 65077 | 77663.6033049262 | 0 | 0 | 0 | 0 |  |  | 128133 | 70192.168260237 | 152915.323113698 | [8 empty] | 810 |  | 1050 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 19 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | WHILE EXCAVATING TO VERIFIY EXISTING VALVE TYPE AND SIZE A PLIDCO SADDLE SHIFTED RESULTED IN A MINOR LEAK. DECISIONS WERE MADE TO BLOCK IN AND BLOW DOWN SECTION OF 20.0" PIPELINE AND REPLACE SADDLE WITH NEW PIPE. | [147 empty] | JERRY HILL | COMPLIANCE COORDINATOR | jerry.hill@enbridge.com | 903-323-4330 |  |  |  |  | JERRY HILL | COMPLIANCE COORDINATOR | 903-323-4330 | jerry.hill@enbridge.com | WHILE EXCAVATING TO VERIFIY EXISTING VALVE TYPE AND SIZE A PLIDCO SADDLE SHIFTED RESULTED IN A MINOR LEAK. DECISIONS WERE MADE TO BLOCK IN AND BLOW DOWN SECTION OF 20.0" PIPELINE AND REPLACE SADDLE WITH NEW PIPE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100046 | 17254 | 2010-07-29 17:23 | SUPPLEMENTAL FINAL | 15931 | PUBLIC SERVICE CO OF COLORADO | 1800 LARIMER STREET | DENVER | CO | 80202 | 2010-06-29 10:00 | 2010 |  |  | 39.5529 | -106.3909 | 946219 | 2010-07-01 12:17 |  | NATURAL GAS |  | 250000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-06-29 18:30 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-06-29 11:00 | 2010-06-29 15:15 | ONSHORE | CO | 81645 | Not Within a Municipality | EAGLE | SURVEY STATION NO. | 105262 | 4'' BATTLE MOUNTAIN TO MINTURN | GIS ID 52750643 | YES | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 4 |  | 0.188 | 35000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COLD APPLIED TAPE | [28 empty] | 1965 | 1965 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 82 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 945000 | 582597.087378641 | 3500 | 4176.93826647267 | 6500 | 7757.17106630638 | 0 | 0 |  |  | 955000 | 609482.925456024 | 594531.19671142 | [8 empty] | 450 |  | 691 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 23496 | NO |  |  | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | AIR PATROL |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  | YES | DID NOT REVIEW SINCE THERE WERE NO CONTROLLER ISSUES. | YES | YES | [7 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED | YES | YES | [15 empty] | STRESS CORROSION CRACKING | [5 empty] | YES | [63 empty] | NO | [63 empty] | YES | 1965 | 760 | NO | [13 empty] | NO | [63 empty] | MARK NOLAN | PRINCIPAL ENGINEER | mark.nolan@xcelenergy.com | 303-571-3931 |  |  |  |  | MARK NOLAN | PRINCIPAL ENGINEER | 303-571-3931 | mark.nolan@xcelenergy.com | AN AERIAL LEAK SURVEY WAS BEING CONDUCTED ON JUNE 29, 2010. A LEAK WAS DETECTED IN A REMOTE AREA OF THE WHITE RIVER NATIONAL FOREST SOUTH OF MINTURN COLORADO. CREWS WERE DISPATCHED AND ISOLATED THE SUBJECT SECTION OF THE 4 INCH TRANSMISSION PIPELINE. THE FAILURE WAS ATTRIBUTABLE TO STRESS-CORROSION CRACKING (SCC). A COLONY OF SCC DEVELOPED ON THE EXTERNAL PIPE SURFACE BENEATH A LAP IN THE TAPE WRAP COATING THAT HAD DISBONDED. THE INTACT BUT DISBONDED COATING ALLOWED MOISTURE TO COME IN CONTACT WITH THE PIPE SURFACE AND THE HIGH DIELECTRIC STRENGTH OF THE TAPE COATING EFFECTIVELY SHIELDED THAT AREA OF THE PIPE SURFACE FROM CATHODIC PROTECTION. INDIVIDUAL SCC GREW IN LENGTH AND DEPTH COALESCED TO FORM ONE LARGE CRACK THAT EXCEEDED THE RESISTANCE OF THE MATERIAL AND CAUSED THE FAILURE. THE FACT THAT THE SCC WAS CIRCUMFERENTIALLY-ORIENTED INDICATES THAT THE PRIMARY LOAD ON THE PIPELINE WAS AXIAL TENSION RATHER THAN HOOP STRESS. THE SOURCE OF THE BENDING STRESS WAS BELIEVED TO BE SOIL SETTLEMENT IN THE RIGHT OF WAY.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20100047 | 15787 | 2010-08-03 15:25 | SUPPLEMENTAL FINAL | 26330 | ENOGEX LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2010-07-07 22:00 | 2010 |  |  | 35.9998 | -95.9578 | 946970 | 2010-07-07 23:20 |  | NATURAL GAS |  | 15117 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-07-07 23:20 | 2010-07-08 01:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 70 | 2010-07-07 22:00 | 2010-07-07 22:40 | ONSHORE | OK | 74037 | JENKS | TULSA | MILEPOST | RIVERSIDE PS | AEP RIVERSIDE POWER STATION |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | INSTRUMENTATION | [38 empty] | 2009 |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENDED RELEASE OF NATURAL GAS | CLASS 1 LOCATION | NO |  | 72 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 67875 | 41845.2669902913 | 2 | 2.38682186655581 | 300 | 358.023279983371 | 0 | 0 |  |  | 68177 | 43548.3260963447 | 42205.6770921412 | [8 empty] | 160 |  | 275 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE SCADA SYSTEM PROVIDES MONITORING CAPABILITY ONLY, THEREFORE, THE GAS CONTROLLER REACTED EXACTLY AS TRAINED TO REPSOND TO A HIGH PRESSURE ALARM AND DISPATCH ON-CALL PERSONNEL TO RESPOND. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | PIPE NIPPLE |  |  |  |  | YES | [177 empty] | MIKE REED | MANAGER EHS ASSESSMENT AND COMPLIANCE | reedmd@oge.com | 405 558-4685 | 405 557-8618 |  |  |  | PAUL M BREWER | VP OPERATIONS | 405 525-7788 | brewerpm@oge.com | ON WEDNESDAY JULY 7, 2010 AT APPROX 10:00 PM ENOGEX GAS CONTROL RECEIVED A HIGH PRESSURE ALARM AT THE AEP RIVERSIDE POWER STATION LOCATED IN JENKS, OKLAHOMA. AT 10:40 PM AN ENOGEX EMPLOYEE ARRIVED AT THE POWER STATION TO ASSESS THE SITUATION. THE EMPLOYEE WAS GREETED AT THE MAIN FACILITY ENTRANCE BY AN AEP INCIDENT COMMANDER. LOCAL EMERGENCY RESPONDERS FROM THE JENKS FIRE AND POLICE DEPARTMENTS VOLUNTARILY EVACUATED 70 PEOPLE FROM NEARBY HOMES PRIOR TO THE ARRIVAL OF ENOGEX PERSONNEL. AT 10:48 PM THE ENOGEX EMPLOYEE WAS ESCORTED TO THE LOW PRESSURE GAS YARD BY THE AEP INCIDENT COMMANDER. THE ENOGEX EMPLOYEE DISCOVERED NATURAL GAS RELIEVING TO ATMOSPHERE FROM TWO (2) 4 INCH BY 6 INCH PRESSURE SAFETY VALVES (PSV) AND TWO (2) 6 INCH BY 8 INCH PRESSURE SAFETY VALVES (PSV). UPON ENTERING THE GAS YARD, THE EMPLOYEE SMELLED AN ODOR OF MERCAPTAN AND HIS PERSONAL GAS MONITOR ALARM ACTIVATED, WHICH INDICATED THE PRESENCE OF A FLAMMABLE MIXTURE OF NATURAL GAS IN AIR. THE EMPLOYEE SAW THAT A 3/4 INCH PIPE NIPPLE, WHICH WAS A PORTION OF THE PRESSURE REGULATOR SENSING ASSEMBLY, HAD BROKEN RESULTING IN TWO (2) DEMAND REGULATORS TRAVELING TO THE FULLY OPEN POSITION, THUS INCREASING THE OPERATING PRESSURE DOWNSTREAM OF THE REGULATORS TO EQUAL THE 150 PSIG SET POINT OF THE FOUR (4) PSVS. AT 11:08 PM ENOGEX GAS CONTROL CLOSED AN AUTOMATED PIPELINE VALVE LOCATED UPSTREAM OF THE LOW PRESSURE GAS YARD TO ISOLATE THE GAS YARD FROM THE PIPELINE. NATURAL GAS CONTINUED TO ESCAPE TO ATMOSPHERE THROUGH A 3/4 INCH PIPE FITTING. AT 11:14 PM ENOGEX EMPLOYEES ISOLATED THE REGULATOR PIPING TO END THE RELEASE OF NATURAL GAS. THE NIPPLE WAS REPLACED AND THE PRIMARY GAS LOAD TO THE POWER STATION RESUMED AT 1:05 AM. AN INTERNAL INCIDENT INVESTIGATION WAS PERFORMED TO DETERMINE THE ROOT CAUSE AND CAUSAL FACTORS OF THE INCIDENT. IT WAS DETERMINED THAT A 3/4 INCH THREADED PIPE NIPPLE BROKE AT THE THREADED CONNECTION TO A 3/4 INCH THREAD-O-LET WELDED TO THE PIPING IMMEDIATELY DOWNSTREAM OF ONE OF THE REGULATORS. THE FAILURE IS BELIEVED TO HAVE BEEN CAUSED BY EXCESSIVE VIBRATION AND/OR METAL FATIGUE. TO PROVIDE THE NECESSARY FINAL DEMAND PRESSURE TO THE CUSTOMER DURING A WIDE RANGE OF POWER STATION LOAD CONDITIONS, THE REGULATOR STATION DESIGN CONSISTS OF TWO REGULATORS, I.E. REGULATOR 1 AND REGULATOR 2, PLACED IN PARALLEL TO ONE ANOTHER. A SINGLE PNEUMATIC PRESSURE CONTROLLER PROVIDES THE NECESSARY LOADING PRESSURE TO EACH REGULATOR. A LOADING PRESSURE OF 3 TO 9 PSIG CONTROLS REGULATOR1 AND A LOADING PRESSURE OF 9 TO 15 PSIG CONTROLS REGULATOR 2. THE FAILURE OF THE PIPE NIPPLE IN THE PRESSURE SENSING LINE AND SUBSEQUENT LOSS OF PROCESS VARIABLE CAUSED REGULATOR 1 TO TRAVEL TO THE FULLY OPEN POSITION FOLLOWED BY REGULATOR 2. THIS CREATED AN INCREASE IN THE DOWNSTREAM FINAL DEMAND PRESSURE TO A PRESSURE EQUAL TO THE 150 PSIG SETPOINT OF FOUR PRESSURE SAFETY VALVES (PSVS) INSTALLED TO PROTECT THE DOWNSTREAM PIPING FROM ACCIDENTAL OVERPRESSURE. IT WAS DETERMINED THAT THE RESULTING ACTION OF THE TWO REGULATORS, ALONG WITH THE ACTIVATION OF THE FOUR PSVS DOWNSTREAM OF THE REGULATORS RESULTED IN THE UNCONTROLLED GAS RELEASE TO ATMOSPHERE. IT WAS DETERMINED THAT THE TIMELY RESPONSE BY ENOGEX PERSONNEL TO CONTROL THE GAS RELEASE WAS HINDERED BY THE FOLLOWING: 1)A MISCOMMUNICATION BETWEEN AEP PERSONNEL AND THE JENKS FIRE AND POLICE DEPARTMENTS. THE EMERGENCY RESPONSE PERSONNEL ARRIVED ON SCENE (AT MAIN GATE) WELL AHEAD OF ENOGEX PERSONNEL. TO PREVENT THE EMERGENCY RESPONSE PERSONNEL FROM ENTERING THE FACILITY, AEP WOULD NOT OPEN THE MAIN GATE FOR ENOGEX AS QUICKLY AS DESIRED. 2) A POTENTIALLY HAZARDOUS CONDITION INSIDE THE LOW PRESSURE GAS YARD, WHEREAS THE PRESENCE OF A FLAMMABLE GAS MIXTURE IN THE ATMOSPHERE PREVENTED ENTRY. DUE TO THE PRESENCE OF NATURAL GAS IN THE ATMOSPHERE, THE ENOGEX RESPONDER COULD NOT SAFELY ENTER THE LOW PRESSURE GAS YARD TO MANUALLY CLOSE ISOLATION VALVES. UPDATE MARCH 5, 2013: COMPLETED SECTION E.5.F.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100048 | 15319 | 2010-08-04 16:56 | SUPPLEMENTAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2010-07-07 19:42 | 2010 |  |  | 31.101 | -94.4863 | 946956 | 2010-07-08 12:10 |  | NATURAL GAS |  | 2000 | 11833 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-07-07 22:50 | 2010-07-09 03:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-07-07 19:42 | 2010-07-07 19:42 | ONSHORE | TX | 75980 | ZAVALLA | ANGELINA COUNTY | SURVEY STATION NO. | 4436+52 | TEXOMA, 30" | ACCOUNT 3080 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 38 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION | [19 empty] | FILLET WELD | [18 empty] | 1996 |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 682 |  | NO | NO | NO |  | 0 | 0 | 55615 | 66371.5490542507 | 9000 | 5548.54368932039 | 0 | 0 | 0 | 0 | 53700 | 64086.1671170235 | OTHER COSTS INCLUDED PIPE & MATERIAL REPLACEMENT, CONTRACT LABOR AND INSPECTION |  | 118315 | 65635.9612730131 | 136006.259860595 | [8 empty] | 926 |  | 970 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 67780 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | BASED ON THE VOLUME OF THE LEAK, AND PRESSURE DIFFERENTIAL, CONTROLLERS COULD NOT HAVE DETECTED THIS LEAK. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | CONSTRUCTION DEFECT: UNSUPPORTED TAP VALVE | [147 empty] | DANNY NICHOLS | DIRECTOR OF REGULATORY COMPLIANCE | danny.nichols@energytransfer.com | 832.668.1006 | 832.668.1129 |  |  |  | DANNY NICHOLS | DIRECTOR OF REGULATORY COMPLIANCE | 832.668.1006 | danny.nichols@energytransfer.com | LEAK WAS DISCOVERED ON THE EVENING OF 07/07/2010 ON AN INACTIVE 2" BRANCH CONNECTION OFF THE 30" TEXOMA INTRASTATE PIPELINE. LEAK WAS DUE TO A FAILED FILLET WELD ON THE TAP. THE LEAK WAS BELIEVED TO HAVE RECENTLY OCCURRED BY OBSERVATION OF THE GROUND CONDITIONS AND THAT IT HAD NOT BEEN IDENTIFIED BY RECENT AERIAL PATROLS. DUE TO THE LOCATION AND AMOUNT OF LEAKAGE, THE INCIDENT WAS NOT DEEMED "REPORTABLE" UNTIL THE NEXT DAY (07/08/2010), DUE TO THE CALCULATION OF CONTROLLED BLOW DOWN VOLUME. THE 2" BRANCH CONNECTION WAS A SIDE TAP THAT WAS PERFORMED IN 1996 FOR A WELL TIE-IN AND HAS SUBSEQUENTLY BEEN OUT OF SERVICE FOR APPROXIMATELY THE LAST FIVE YEARS. VISUAL INSPECTION OF THE BRANCH REVEALED A CRACK IN THE TOE OF THE FILLET WELD OF THE SADDLE PAD FROM THE 10 TO 2 O'CLOCK POSITION. DURING THE EXCAVATION THE BLOCK VALVE WAS FOUND TO BE UNSUPPORTED AND THE PIPING TO BE IN A BIND DUE TO SETTLEMENT OF THE AREA WHICH IS INDICATIVE WITH THE TYPE OF FAILURE THAT OCCURRED. CURRENT OPERATING PROCEDURES HAVE BEEN REVISED, FROM THE PREVIOUS OPERATOR, PREVENTING FUTURE SIMILAR OCCURRENCES. A 40' SECTION OF 30" LINE PIPE WAS CUT OUT AND REPLACED, REMOVING THE LEAKING TAP. THE ONLY COST ASSOCIATED WITH THIS REPORT WAS GAS LOSS, PIPE REPLACEMENT AND LABOR COSTS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100049 | 15061 | 2010-08-13 10:03 | ORIGINAL FINAL | 31286 | ONEOK GAS TRANSPORTATION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2010-07-15 23:20 | 2010 |  |  | 35.2082 | -97.1803 | 947893 | 2010-07-16 02:57 |  | NATURAL GAS |  | 10300 | 9900 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-07-16 02:27 | 2010-07-17 15:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-07-15 23:30 | 2010-07-15 23:55 | ONSHORE | OK | 73026 | NORMAN | CLEVELAND |  |  | A-1300 | HWY 102 / LEXINGTON | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 66 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1975 |  | CARBON STEEL |  | OTHER | [8 empty] | BALON VALVE / VALVE BOLT FAILURE | CLASS 1 LOCATION | NO |  | 580 |  | NO | NO | NO |  | 1300 | 1551.43421326128 | 45853 | 54721.4715235918 | 47545 | 29311.7233009709 | 51502 | 61463.0498856787 | 1000 | 1193.41093327791 | 3000 | 3580.23279983372 | COMPANY LABOR FOR REPAIR |  | 150200 | 86623.9332429256 | 151821.322656614 | [8 empty] | 565 |  | 843 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 70418 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS INCIDENT WAS EQUIPMENT FAILURE ONLY, CONTROL ROOM ISSUES WERE NOT A FACTOR | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | FAILURE OF EQUIPMENT BODY (EXCEPT COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL | MATERIAL/WELD/EQUIP FAILURE | FAILURE OF EQUIPMENT BODY | [166 empty] | FAILURE OF EQUIPMENT BODY (EXCEPT COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL | [35 empty] | YES | UNDERGROUND SERVICE LED TO BALON VALVE CORROSION ISSUES RESULTING IN FAILURE | [161 empty] | PATTI FORD | SENIOR PIPELINE SAFETY ENGINEER | patti.ford@oneok.com | 918 588 7131 | 918 732 1311 |  |  |  | MICHEL E NELSON | SENIOR VICE PRESIDENT - NATURAL GAS PIPELINES | 918 588 7944 | michel.nelson@oneok.com | A LANDOWNER CALLED ONEOK GAS TRANSPORTATION GAS CONTROL TO REPORT A NATURAL GAS LEAK ON THE 24 INCH A-1300 NATURAL GAS PIPELINE NEAR THE LITTLE RIVER IN CLEVELAND COUNTY OKLAHOMA AT APPROXIMATELY 2330 HOURS ON THURSDAY JULY 15, 2010. ONEOK GAS TRANSPORTATION FIELD PERSONNEL WERE CONTACTED AND WERE ON THE SCENE BY 2355 HOURS. THERE WAS NO EXPLOSION, NO FIRE, NO INJURIES, AND NO DEATHS. THE LOCAL FIRE DEPARTMENT DID COME OUT TO THE SITE BUT DID NOT REMAIN ON SCENE. THE OKLAHOMA CORPORATION COMMISSION WAS NOTIFIED VIA TELEPHONE AT 0155 HOURS ON FRIDAY JULY 16, 2010. THE NATIONAL RESPONSE CENTER WAS CONTACTED AT 0257 HOURS ON FRIDAY JULY 16, 2010. THE NRC INCIDENT NUMBER IS 947893. THE A-1300 SEGMENT WHERE THE LEAK WAS LOCATED WAS ISOLATED BY CLOSING THE HIGHWAY 102 BLOCK VALVE AND THE LEXINGTON TAKE OFF VALVE. THE 13.3 MILES OF PIPELINE AROUND THE LEAK WAS ISOLATED BY 0227 HOURS ON FRIDAY JULY 16, 2010. THE LINE WAS ALLOWED TO BLOW DOWN AND THE SITE SECURED BY 0630 HOURS. THREE TV STATION CREWS WERE IN THE AREA FOR A SHORT PERIOD OF TIME AND THEY WERE BRIEFED ON THE SITUATION. APPROXIMATELY 10 FARM TAP CUSTOMERS WERE IMPACTED AND SERVICE TO THE TOWN OF LITTLE AXE, OKLAHOMA WAS PUT ON A CASCADE SYSTEM BY OKLAHOMA NATURAL GAS. CLOSER EXAMINATION OF THE INCIDENT SITE REVEALED A 30 FOOT DIAMETER CRATER WHERE A DRIP WAS LOCATED. REPAIR CONSISTED OF REPLACING 63 FEET OF A-1300 PIPELINE INCLUDING REMOVAL OF THE DRIP WITH 24 INCH 0.375 WALL THICKNESS X-60 GRADE PRETESTED PIPE. THE PIPELINE WAS PUT BACK INTO NORMAL SERVICE AT 1530 HOURS ON SATURDAY JULY 17, 2010. FIELD ASSESSMENT INDICATES A MATERIAL FAILURE OF THE 2 INCH BALON VALVE(S) LOCATED ON THE DRIP AS THE CAUSE OF THE INCIDENT. THESE VALVES WERE IN SERVICE IN A DAMP AND / OR WET ENVIRONMENT. IT APPEARS VALVE BODY AND / OR BOLT HAD CORROSION ISSUES WHICH LEAD TO VALVE FAILURE. THERE WAS ADEQUATE CATHODIC PROTECTION ON THE PIPELINE AND DRIP.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100050 | 16095 | 2010-08-27 11:42 | SUPPLEMENTAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2010-07-28 07:04 | 2010 |  |  | 29.8601 | -97.2242 | 949134 | 2010-07-28 08:45 |  | NATURAL GAS |  | 208458 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-07-28 08:05 | 2010-09-01 11:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 15 | 2010-07-28 07:10 | 2010-07-28 07:59 | ONSHORE | TX | 77474 | SEALY | AUSTIN | SURVEY STATION NO. | 3312+92 | OASIS / PRAIRIE LEA TO KATY | ACCOUNT 3900 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 42 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 36 |  | 0.438 | 60000 | API 5L | DSAW |  | MANNESMANN | ASPHALT | [28 empty] | 1970 | 1969 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 960 | 113 |  | CLASS 1 LOCATION | NO |  | 852 |  | NO | NO | NO |  | 60326 | 71993.7079609229 | 0 | 0 | 987151 | 608583.383495146 | 822854 | 982002.960091457 | 8855 | 10567.6538141758 | 0 | 0 |  |  | 1879186 | 1119609.14172551 | 1673147.7053617 | [8 empty] | 958 |  | 1050 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 105072 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INITIAL DETERMINATION IDENTIFIED THAT THE PIPELINE WAS OPERATING WITHIN IT'S PRESSURE LIMITATIONS, PRIOR TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | STRESS CORROSION CRACKING (SCC) | [147 empty] | DANNY NICHOLS | DIRECTOR OF REGULATORY COMPLIANCE | danny.nichols@energytransfer.com | 832.668.1006 | 832.668.1129 |  |  |  | DANNY NICHOLS | DIRECTOR OF REGULATORY COMPLIANCE | 832.668.1006 | danny.nichols@energytransfer.com | ETC EXPERIENCED A RUPTURE ON THE 36" OASIS PIPELINE IN A RURAL (CLASS I) AREA IN AUSTIN COUNTY, TX ON JULY 28, 2010. THE LINE IS AN INTRASTATE NATURAL GAS TRANSMISSION PIPELINE UNDER THE JURISDICTION OF THE TEXAS RAILROAD COMMISSION. THE INCIDENT WAS REPORTED TO THE TRRC UNDER INCIDENT ID: 551 AND ALSO TO THE NRC UNDER ID: 949134. THROUGH A THOROUGH EXAMINATION, BY THIRD PARTY, KIEFNER & ASSOCIATES, AND THROUGH MAG-PARTICLE TESTING, STRESS CORROSION CRACKING (SCC) WAS DETERMINED TO HAVE BEEN INVOLVED. METALURGICAL LAB ANALYSIS WILL BE PERFORMED ON THE FAILED SECTION OF PIPE AND WILL PROVIDE FURTHER DETAILED INFORMATION. TO DATE, ETC HAS COMPLETED HYDROSTATIC TESTING OF APPROXIMATELY 30.5 MILES WITHIN THE AREA OF THE INITIAL IN SERVICE FAILURE. THE TESTING CONSISTED OF FOUR TEST SECTIONS RUNNING EAST TO WEST FROM THE BRAZOS RIVER (STA. 2950+00) TO 4.5 MILES WEST OF MLV2 (STA. 4560+00). EACH TEST SECTION WAS TESTED TO A MINIMUM OF 100% SMYS FOR ONE HOUR AND THEN A SUBSEQUENT LEAK TEST AT 90% SMYS FOR A MINIMUM OF 8 HRS WITHOUT PRESSURE LOSS. SECTION 1 AND 4 SUCCESSFULLY PASSED THEIR INITIAL TESTS, SECTION 2 HAD TWO FAILURES AND SECTION 3 HAD 3 FAILURES BEFORE ACHIEVING A SUCCESSFUL TEST. IT SHOULD BE NOTED, THAT OF THE 5 FAILURES THAT OCCURRED DURING THE TESTING, THE MINIMUM FAILURE PRESSURE OCCURRED AT 84% OF SMYS INDICATING THERE WERE NO OTHER CRITICAL CRACKS THAT WOULD HAVE FAILED AT OPERATING PRESSURE. BASED ON THE RESULTS OF THE HYDROSTATIC TESTING, AND INTEGRATION OF INFORMATION OBTAINED FROM THE RUPTURE SITE, SOIL RESISTIVITY SURVEYS AND SUBSEQUENT EXCAVATIONS, ETC FEELS THAT ALL OF THE SCC COLONIES OF A CRITICAL SIZE WERE LOCATED WITHIN THE SECTION OF LINE BETWEEN MLV1 TO MLV2. PLANS ARE TO REINSTORE SERVICE ON OR AROUND SEPTEMBER 1, 2010 AND SUBSEQUENTLY RUNNING THE EMAT CRACK DETECTION TOOL FROM OUR PRAIRIE LEE COMPRESSOR STATION TO KATY, APPROXIMATELY 113 MILES, TO FURTHER CONFIRM OUR FINDINGS AND FURTHER DEVELOP OUR OVERALL MITIGATION PLAN FOR THIS THREAT. FINAL UPDATE 08/26/2013: AFTER A THOROUGH METALLURGICAL EXAMINATION, PERFORMED BY KIEFNER AND ASSOCIATES, INC, THE FAILURE WAS MOST LIKELY DETERMINED TO BE CAUSED BY HIGH PH TYPE SCC IN THE BODY OF THE PIPE. THIS DETERMINATION WAS BASED UPON PIPE-TO-SOIL POTENTIAL, SOIL RESISTIVITY, AND PH MEASUREMENTS AS WELL AS METALLOGRAPHIC SECTIONS THROUGH ADJACENT IN THE COLONY
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100051 | 15063 | 2010-08-27 15:52 | ORIGINAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2010-07-31 01:15 | 2010 |  |  | 30.0126 | -92.0812 | 949470 | 2010-07-31 02:20 |  | NATURAL GAS |  | 3110 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-07-31 02:20 | 2010-08-01 20:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-07-31 01:15 | 2010-07-31 01:50 | ONSHORE | LA | 70511 | ABBEVILLE | VERMILLIAN | MILEPOST | 3.78 | ABBEVILLE 8" | INDEX-207-7-6 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 |  | 0.259 | 24000 | API-5L | OTHER | FURNACE LAP WELD | YOUNGSTOWN | OTHER | GREASE OR WAX - CONSIDERED BARE | [27 empty] | 1940 | 1940 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 13.5 | 8.5 |  | CLASS 1 LOCATION | NO |  | 192 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 15000 | 9247.57281553398 | 83000 | 99053.1074620661 | 4925 | 5877.54884639368 | 0 | 0 |  |  | 102925 | 57753.3186740338 | 114178.229123994 | [8 empty] | 528 |  | 577 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 25449 | NO | [5 empty] | YES | NO PIGTRAPS | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS CAUSED BY THIRD PARTY DAMAGE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [260 empty] | GLENN FLOYD | TECHNICAL SPECIALIST | glenn.floyd@bwpmlp.com | 9016853471 | 9016853475 |  |  |  | JACK ADAMS | DIRECTOR COMPLIANCE DOT AND SECURITY | 7134798099 | jack.adams@bwpmlp.com | THE PIPELINE CROSSES PROPERTY USED AS A LANDFILL. THE NORMAL LANDFILL ACTIVITY WAS NOT ON THE PIPELINE RIGHTS-OF-WAY. PIPELINE IS MARKED AND PROPERTY OWNERS ARE AWARE OF IT'S LOCATION. PROPERTY OWNERS HAD STACKED TREE TRUNKS AND LIMBS ON THE ROW. LANDOWNERS WERE MOVING THE DEBRIS OFF THE ROW USING BULLDOZERS. PIPE COVER WAS REMOVED WHILE THE DEBRIS WAS BEING PUSHED INTO PILES. BECAUSE OF THE REDUCED COVER, THE PIPE WAS FLATTENED BY THE DOZER TRACKS. A NEIGHBOR HEARD THE RUPTURE AND CALLED A BWP EMPLOYEE, WHO DETERMINED THE RUPTURE WAS ON THE GULF SOUTH SYSTEM.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100052 | 16804 | 2010-08-31 09:48 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2010-08-06 06:00 | 2010 |  |  | 42.6404 | -92.0275 | 950103 | 2010-08-06 08:41 |  | NATURAL GAS |  | 271 | 456 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-08-06 09:08 | 2010-08-06 16:40 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-08-06 06:00 | 2010-08-06 06:40 | ONSHORE | IA | 50629 | FAIRBANK | BUCHANAN | MILEPOST | MILEPOST 7.29 | HAWKEYE/MENLO ETHANOL TOWN BORDER STATION | HAWKEYE/MENLO ETHANOL BRANCH LINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE OTHER ENCLOSED SPACE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 6 |  | 0.28 | 35000 | 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | TENARIS | PAINT | [28 empty] | 2008 | 2005 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 131 |  | NO | NO | NO |  | 0 | 0 | 2006 | 2393.98233215548 | 1192 | 734.873786407767 | 13371 | 15957.0975888589 | 7431 | 8868.23664518811 | 69372 | 82789.3032633548 | CONTRACTOR LABOR, EQUIPMENT, SANDBLASTING, X-RAY, ETC. |  | 93372 | 51258.7363034685 | 110743.493615965 | [8 empty] | 740 |  | 1000 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS CAUSED BY AN OUTSIDE PARTY LOOSING CONTROL OF A VEHICLE, ROLLING AND ENDING UP INSIDE THE TOWN BORDER STATION FACILITY. CONTROLLER(S) HAD NO KNOWLEDGE OR CONTROL OF ANY OF THE AFOREMENTIONED CIRCUMSTANCES. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [260 empty] | BYRON WOOD | SR. PIPELINE SAFETY SPECIALIST | byron.wood@nngco.com | 402-398-7396 | 402-398-7606 |  |  |  | THOMAS CORRELL | DIRECTOR PIPELINE SAFETY AND INTEGRITY | 402-398-7715 | thomas.correll@nngco.com | IN THE EARLY MORNING HOURS OF AUGUST 6, 2010, A LOCAL RESIDENT LOST CONTROL OF HIS VEHICLE. THE VEHICLE LEFT THE ROAD, ROLLED NUMEROUS TIMES AND FINALLY ENDED UP INSIDE THE FENCING OF THE HAWKEYE/MENLO RENEWABLES ETHANOL PLANT TOWN BORDER STATION, WHICH IS OWNED AN OPERATED BY NORTHERN NATURAL GAS COMPANY AND SUPPLIES NATURAL GAS TO THE ETHANOL PLANT. ONE INDIVIDUAL WAS DEAD AT THE SITE AND ONE WAS TRANSPORTED BY LIFE FLIGHT TO A HOSPITAL AND DIED SHORTLY THEREAFTER. THE VEHICLE STRUCK AND DAMAGED HIGH-PRESSURE NATURAL GAS PIPING IN SEVERAL PLACES IN THE TOWN BORDER STATION. A 1/4-INCH DIAMETER PIPE FITTING, BETWEEN THE STATION INLET FILTER AND THE FILTER INLET GAUGE ISOLATION VALVE WAS BROKEN, CAUSING THE RELEASE OF HIGH PRESSURE GAS. THE STATION PIPING WAS ISOLATED AND BLOWN DOWN TO ZERO PRESSURE AND UPON CLOSER OBSERVATION IT WAS DECIDED THAT THE 7.5 MILE LONG, 6-INCH BRANCH LINE TO THE STATION NEEDED TO BE ISOLATED AND BLOWN DOWN IN ORDER TO ENSURE SAFETY FOR ALL PERSONNEL WHILE INSPECTING FOR DAMAGE AND REPAIRING PIPING WITHIN THE TOWN BORDER STATION. THERE WERE NO DEFECTS FOUND BUT THE 6-INCH DIAMETER IN-LINE INSPECTION TOOL RECEIVER INLET AND THE 4-INCH DIAMETER STATION INLET VALVES WERE FOUND TO BE DAMAGED. BOTH THE 6 AND 4-INCH VALVES WERE REPLACED AS WELL AS THREE FITTINGS AND VARIOUS SMALL LENGHTS OF PIPE TO FACILITIATE REPLACEMENT OF THE VALVES. THERE WAS NO FIRE, EXPLOSION OR EVACUATIONS BECAUSE OF THE INCIDENT. UPON COMPLETION OF REPAIRS THE BRANCH LINE AND THE TOWN BORDER STATION WERE PURGED, RE-PRESSURIZED WITH NATURAL GAS AND SERVICE WAS RESTORED TO THE ETHANOL PLANT. THE VEHICLE CRASH WAS INVESTIGATED BY THE IOWA STATE HIGHWAY PATROL AND LOCAL COUNTY LAW ENFORCEMENT OFFICIALS. FINAL REPORT: THE TOTAL COST OF REPAIRS WAS REVISED TO CALCULATE THE FINAL TOTAL OF $93,372. THIS REPORT IS CONSIDERED COMPLETE WITH NO FURTHER ACTIONS PENDING. SUPPLEMENTAL/FINAL: UPDATE PART E5F WITH TRANSMISSION PER PHMSA REQUEST ON REPORT 20100052 DATED 8/31/2010. SUPPLEMENTAL/FINAL: UPDATE ON TIMELINE OF EVENTS. THE INDIVIDUALS CRASHED INTO THE TOWN BORDER STATION AROUND 01:30. LOCAL POLICE DID NOT ARRIVE AT THE STATION UNTIL 05:35 THE SAME MORNING. NORTHERN WAS NOT NOTIFIED UNTIL 06:00 AS SHOWN IN PART A4.
2021-02-26 10:37 | NO | NO | GG (Gas Gathering) | 20100053 | 15295 | 2010-09-01 11:26 | SUPPLEMENTAL FINAL | 19410 | THUMS LONG BEACH CO | 111 WEST OCEAN BLVD, STE. 800 | LONG BEACH | CA | 90802 | 2010-08-06 10:38 | 2010 |  |  | 33.7586 | -118.1819 | 950179 | 2010-08-06 16:15 |  | OTHER GAS | PRODUCED GAS (WET) | 0 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-08-06 10:48 | 2011-01-15 16:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-08-06 10:38 | 2010-08-06 10:38 | ONSHORE | CA | 90802 | LONG BEACH | LOS ANGELES |  |  | ISLAND GRISSOM | GJ4 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | OTHER | EMBEDDED IN CONCRETE | 12 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12.75 |  | 0.375 | 35000 | API 5L GRB | SEAMLESS |  | UNKNOWN | OTHER | CONCRETE MASTIC | [27 empty] | 1966 | 1965 | CARBON STEEL |  | MECHANICAL PUNCTURE | 0.4 | 1.2 | [7 empty] | CLASS 1 LOCATION | NO |  | 176 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 75000 | 89505.8199958429 | 0 | 0 | 0 | 0 |  |  | 75000 | 41085.5331531906 | 89505.8199958429 | [8 empty] | 35 |  | 400 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 6095 | YES | [7 empty] | NO | [6 empty] | TYPE B GATHERING | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS JOB DID NOT REQUIRE CONTROLLER ACTION | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [10 empty] | NO |  |  | YES | PRIVATE BUSINESS | [7 empty] | CONTRACTOR | HAND TOOLS | UNKNOWN/OTHER | NO |  |  | CONTRACT LOCATOR | DATA NOT COLLECTED | YES | NO |  | LOCATING PRACTICES NOT SUFFICIENT |  | FACILITY MARKING OR LOCATION NOT SUFFICIENT | [264 empty] | HAIDONG ZHANG | SR. FACILITIES ENGINEER | haidong_zhang@oxy.com | 562.624.3129 | 562.624.3498 |  |  |  | CHARLIE PLANT | VICE PRESIDENT - OPERATION | 562.624.3202 | charlie_plant@oxy.com | CONTRACT WORK CREW WAS IN THE PROCESS OF BREAKING OUT THE CONCRETE AROUND THE GJ5 LINE IN PREPARATION TO CUT AND REPAIR OF THE GJ5 LINE. THE PIPELINES WERE ENCASED IN CONCRETE IN THE WORK AREA. THE CONSTRUCTION CREW WAS USING A JACK HAMMER TO EXPOSE GJ5 AND PUNCTURED GJ4. THE GJ 4 (12-IN PIPE) AND GJ5 (14-IN PIPE) ARE APPROXIMATELY 20-IN C/L TO C/L (APPROXIMATELY 6-IN APART EDGE PIPE TO EDGE OF PIPE) IN THE WORK AREA. GJ4 WAS AN ACTIVE GAS LINE AT THE TIME OF INCIDENT. GJ4 WAS SHUT DOWN AND BLED OFF IMMEDIATELY. GAS WAS SWITCHED TO THE GJ2 PIPELINE. JACK HAMMER BEAD WAS LEFT IN THE PUNCTURE. NO GAS IGNITION OR HUMAN INJURY OCCURRED DURING THIS INCIDENT. ESTIMATED VOLUME OF GAS RELEASED UNINTENTIONALLY IS 0.098 MCF (ENTRY NOT ACCEPTED IN PART A) DAMAGED SECTION REPLACED ON NOVEMBER 23, 2010 RESEARCH TO IDENTIFY COATING COMPATIBLE WITH THE ORIGINAL CONCRETE MASTIC COATING COATING AND INSPECTION COMPLETED ON APRIL 11, 2011 BACKFILL AND CONCRETE ENCASEMENT COMPLETED ON JUNE 26, 2011
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100054 | 15080 | 2010-09-02 16:52 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2010-08-07 19:00 | 2010 |  |  | 35.6403 | -119.8307 | 950266 | 2010-08-08 01:09 |  | NATURAL GAS |  | 63410 | 3790 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-08-08 02:15 | 2010-08-09 02:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-08-07 19:00 | 2010-08-07 20:30 | ONSHORE | CA | 93249 | LOST HILLS | KERN | MILEPOST | 30.22 | LINE 85 | NA | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 26 |  | 0.25 | 41000 | UNKNOWN | FLASH WELDED |  | A O SMITH | COAL TAR | [28 empty] | 1931 | 1931 | CARBON STEEL |  | MECHANICAL PUNCTURE | 4 | 4 | [7 empty] | CLASS 1 LOCATION | NO |  | 359 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 285000 | 175703.883495146 | 150000 | 179011.639991686 | 10000 | 11934.109332779 | 0 | 0 |  |  | 445000 | 269809.331568231 | 366649.63281961 | [8 empty] | 376 |  | 400 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 40286 | NO | [5 empty] | YES | WELD STYLE | NO | [6 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE REPORTED BY THIRD PARTY | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [7 empty] | FARMER | FARM EQUIPMENT | AGRICULTURE | NO |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO |  | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | W. JEFF KOSKIE | PIPELINE SAFETY ADVISOR | wkoskie@semprautilities.com | (213)305-8660 | (213)244-8155 |  |  |  | W. JEFF KOSKIE | PIPELINE SAFETY ADVISOR | (213)305-8660 | wkoskie@semprautilities.com | ON AUGUST 7, 2010 A 26' NATURAL GAS TRANSMISSION PIPELINE OPERATING AT APPROXIMATELY 375 POUNDS WAS DAMAGED BY A FARMER PERFORMING GRADING WORK. WHILE GRADING FIELDS, THE FARMER STRUCK AND DAMAGED THE MAIN. NO INJURIES OR PUBLIC PROPERTY DAMAGE RESULTED FROM THIS INCIDENT. ALL REPAIRS HAVE BEEN COMPLETED, AND PIPELINE HAS BEEN PUT BACK INTO SERVICE. INVESTIGATION OF THE INCIDENT SHOWED THAT THE EXCAVATOR DID NOT HAVE A USA TICKET, BUT WAS AWARE OF PIPING FROM A PREVIOUS LOCATE REQUEST PERFORMED YEARS AGO. THIS INCIDENT WAS REPORTED TO PHMSA UNDER INCIDENT # 95266, BASED UPON DAMAGE TO COMPANY FACILITIES EXCEEDING $50K. NOTE: DAMAGE AMOUNT AND GAS LOST COSTS ARE OFF BY A FACTOR OF 10X STATED VALUE. FORM WOULD NOT ACCEPT 6 FGURE NUMBERS. DISCUSSED WITH PETER KATCHMAR, AGREED WE WILL SUBMIT THIS ORIGINAL AND SUBMIT A REVISED FINAL WHEN ISSUE RESOLVED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100055 | 15279 | 2010-09-10 16:06 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2010-08-17 09:15 | 2010 |  |  | 28.8136 | -89.3807 | 951219 | 2010-08-17 10:00 |  | NATURAL GAS |  | 1570 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-08-17 09:30 | 2011-01-10 15:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-08-17 09:15 |  | OFFSHORE | [28 empty] | 250 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SOUTH PASS | 77 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | OTHER | [37 empty] | BREAK AWAY CONNECTOR | 2006 |  | CARBON STEEL |  | OTHER | [8 empty] | MUD SLIDE BROKE PIPELINE AT BREAK AWAY CONNECTOR. | CLASS 1 LOCATION | NO |  | 334 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 6280 | 3871.65048543689 | 262061 | 312746.462585741 | 0 | 0 | 0 | 0 |  |  | 268341 | 147572.794573049 | 316618.113071178 | [8 empty] | 834 |  | 1440 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 31680 | NO |  | YES | [5 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | AIR PATROL |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE OPERATING UNDER MAOP AND BREAK WAS DUE TO NATURAL FORCES OFFSHORE. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [52 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | OFFSHORE MUDSLIDE. | NO | [306 empty] | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | ken.peters@elpaso.com | 2053257554 | 2053257329 |  |  |  | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | 2053257554 | ken.peters@elpaso.com | A PRODUCER REPORTED THAT AN AIRCRAFT PERFORMING PATROL REPORTED SEEING BUBBLES IN THE VICINITY OF TENNESSEE GAS PIPELINE (TGP)COMPANY'S 12" 527A-801 PIPELINE IN THE GULF OF MEXICO, OFFSHORE LOUISIANA, IN SOUTH PASS BLOCK 77. TGP'S GAS CONTROL CONFIRMED SEEING A PRESSURE DROP VIA SCADA. SINCE THIS PIPELINE HAS BEEN AFFECTED BY OFFSHORE MUDSLIDES IN THE PAST, SUCH AN OCCURRENCE WAS SUSPECTED TO BE THE CAUSE OF THIS EVENT, LIKELY SEPARATING THE PIPELINE AT A DESIGNED BREAK AWAY JOINT. FIELD INVESTIGATION CONFIRMED THIS TO BE THE CASE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100056 | 15928 | 2010-09-13 12:03 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2010-08-25 09:00 | 2010 |  |  | 28.7613 | -91.4032 | 952131 | 2010-08-25 20:05 |  | NATURAL GAS |  | 10000 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | [9 empty] | NO |  |  |  |  | NO | [9 empty] | OFFSHORE | [28 empty] | 100 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EUGENE ISLAND | 188 | PLATFORM | INTERSTATE | OFFSHORE PLATFORM, INCLUDING PLATFORM-MOUNTED EQUIPMENT AND PIPING | PIPE | PIPE BODY | 12.75 |  | 0.375 | 46000 | API | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | AMERICAN | COAL TAR | [29 empty] | 1968 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 317 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 55000 | 33907.7669902913 | 75000 | 89505.8199958429 | 20000 | 23868.2186655581 | 0 | 0 | 0 |  | 150000 | 87195.3970102227 | 147281.805651692 | [8 empty] | 895 |  | 1300 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  | YES |  |  |  |  | YES | [5 empty] | YES |  |  |  | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [168 empty] | NO | [63 empty] | NO | [16 empty] | NO | [63 empty] | LOUIS SALINAS | COMPLIANCE ENGINEER | louis_salinas@transcanada.com | 832-320-5305 | 832-320-6305 |  |  |  | LOUIS SALINAS |  | 832-320-5305 | No Email Address | DURING ROUTINE SANDBLASTING OPERATIONS, A PIN HOLE LEAK WAS DISCOVERED. THE 12" PIPELINE WAS ISOLATED AND BLOWN DOWN. THERE WERE NO ENVIRONMENTAL OR SAFETY ISSUES.
2021-02-26 10:37 | NO | NO | GG (Gas Gathering) | 20100057 | 15903 | 2010-09-14 08:34 | SUPPLEMENTAL | 32118 | CROSSTEX NORTH TEXAS GATHERING, L.P. | 1722 ROUTH STREET SUITE 1300 | DALLAS | TX | 75201 | 2010-08-26 09:35 | 2010 |  |  | 29.6413 | -90.9669 | 952182 | 2010-08-26 11:45 |  | OTHER GAS | LIQUID COOLANT FOR ENGINE | 0 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | LIQUID COOLANT LEAK ON UNIT # 10 @ CROUCH COMPRESSOR | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-08-26 09:35 | 2010-08-26 09:35 | ONSHORE | TX | 76058 | JOSHUA | JOHNSON | MILEPOST | CROUCH STA | CROUCH COMPRESSOR UNIT # 10 | GATHERING COMPRESSOR AT CROUCH STA UNIT # 10 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | TUBING | [38 empty] | 2008 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | NO |  | 595 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 1193.41093327791 | 0 | 0 | 0 | 0 |  |  | 1000 | 547.807108709208 | 1193.41093327791 | [8 empty] | 980 |  | 1176 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TYPE A GATHERING | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LOCAL UNIT LEAK OF TURBO COOLANT LEAK ON HOT EXAUST OF ENGINE CREATE A FIRE. NO SCADA INVOLVED IN INCIDENT | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | LIQUID ENGINE COOLANT DEVELOPED A LEAK AT A FITTING THAT DRIPPED ONTO EXHAUST PIPING CREATING A SMALL FIRE ON THE TURBO CHARGER OF ENGINE #10 | [147 empty] | WILLIAM WORLEY | DOT COMPLIANCE MANAGER | bill.worley@crosstexenergy.com | 214 721 9449 | 214 953 9501 |  |  |  | WILLIAM WORLEY | DOT COMPLIANCE MANAGER | 214 721 9449 | bill.worley@crosstexenergy.com | TUBING FITTING BECAME LOOSE ALLOWING COOLANT TO DRIP ONTO TURBO AND EXHAUST PIPING RESULTING IN A SMALL FIRE. THE FIRE WAS IMMEDIATELY EXTENGUISHED BY LOCAL EMPLOYEE AND SHUT DOWN ENGINE. LEAKING FITTING WAS REPAIRED AND UNIT # 10 WAS RETURNED TO SERVICE WITHIN 3 HOURS OF SHUTTING DOWN UNIT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100058 | 16738 | 2010-09-14 15:11 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2010-07-26 11:40 | 2010 |  |  | 29.137 | -90.7322 | 948908 | 2010-07-26 12:41 |  | NATURAL GAS |  | 6 | 28283 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-07-27 07:30 | 2010-08-04 15:10 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-07-26 12:05 | 2010-07-26 13:40 | OFFSHORE | [28 empty] | 5 | IN STATE WATERS | LA | LAKE PELTO | 0 | TERRABORNE PARISH |  |  |  | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 26 |  | 0.417 | 52000 | API 5L OR EQUIVALENT | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | US STEEL | OTHER | CONCRETE OVER ENAMEL | [27 empty] | 1990 | 1990 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 622 |  | NO | NO | NO |  | 0 | 0 | 113132 | 135012.965703596 | 24 | 14.7961165048544 | 694000 | 828227.187694866 | 0 | 0 | 0 | 0 |  |  | 807156 | 442167.987072506 | 963254.949514967 | [8 empty] | 740 |  | 1200 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 216480 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SINCE LEAK WAS OF PINHOLE SIZE, IT WAS NOT DETECTABLE BY PRESSURE DROP. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN | [5 empty] | YES | NOT DETERMINED DUE TO LACK OF VISIBILITY UNDERWATER AND BECAUSE REPAIR WAS MADE BY CLAMP INSTALLATON. NO PIPE CUT OUT. |  |  | YES | SUSPECTED DUE TO PINHOLD NATURE OF LEAK AND LOCATION ON BOTTOM OF PIPE. | YES | [5 empty] | YES | NO | YES | NO | [168 empty] | NO | [63 empty] | YES | 1968 | 1940 | NO | [13 empty] | NO | [63 empty] | KENNETH C PETERS | SENIOR ENGINEER | ken.peters@elpaso.com | 2053257554 | 2053253508 |  |  |  | KENNETH C PETERS | SENIOR ENGINEER | 2053257554 | ken.peters@elpaso.com | TERRABORNE PARRISH SHERIFF DEPARTMENT PERSONNEL NOTICED BUBBLES IN LAKE PELTO AND REPORTED SAME TO TENNESSEE GAS PIPELINE (TGP). TGP DETERMINED THAT A SMALL LEAK WAS OCCURRING ON ITS 26" 523M-100 PIPELINE. DIVER INVESTIGATION REVEALED A PINHOLE LEAK IN A GIRTH WELD AT APPROXIMATELY THE 6 O'CLOCK POSITION ON THE BOTTOM OF THE PIPE. REPAIRS WERE MADE BY INSTALLING A LEAK CLAMP AND THE PIPELINE WAS PLACED BACK INTO SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100059 | 15190 | 2010-09-15 14:21 | SUPPLEMENTAL FINAL | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | ONE ENERGY PLAZA | DETROIT | MI | 48226 | 2010-08-16 17:30 | 2010 |  |  | 42.2905 | -83.1597 | 951156 | 2010-08-16 18:25 |  | NATURAL GAS |  | 2162 | 56 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | PRESSURE REDUCED 150 PSIG TO 45 PSIG FROM 8/16 TO 9/3 THEN SHUT DOWN | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-08-16 18:25 | 2010-08-16 18:25 | ONSHORE | MI | 48217-1354 | DETROIT | WAYNE | SURVEY STATION NO. | 13700 MELLON | FORT STREET 150 PSIG | MELLON STREET SECTION | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 72 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PULSATION BOTTLE OR DRIP/DRIP COLLECTION DEVICE | [38 empty] | 1951 |  | CARBON STEEL |  | LEAK | 0.4 | 0.2 | PINHOLE | CORROSION | OTHER | EVIDENCE REVEALED THAT THE APPARENT CONCENTRATION CELL CORROSION WAS CAUSED BY THE BUILD-UP OF INTERNAL PIPELINE DEBRIS AND CONTAMINATNTS. |  |  |  | CLASS 3 LOCATION | YES |  | 203 |  | NO | NO | NO |  | 0 | 0 | 384 | 458.269798378716 | 14810 | 9130.43689320388 | 158570 | 189239.171689877 | 24806 | 29603.7516108917 | 0 | 0 |  |  | 198570 | 110130.972807731 | 228431.629992352 | [8 empty] | 150 |  | 150 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 10560 | NO |  | YES |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING | [5 empty] | YES | DEBRIS AND CONTAMINANTS |  | YES | [6 empty] | YES | DRIP TANK ASSEMBLY | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [313 empty] | MICHAEL LASKOWSKI | STAFF ENGINEER | laskowskim@dteenergy.com | 313-389-7762 | 313-389-7757 |  |  |  | ROBERT FRECKELTON | MANAGER | 313-389-7755 | freckeltonr@dteenergy.com | AT 15:30 ON AUGUST 16, 2010 MICHCON RECEIVED A REPORT OF LEAKING GAS ON MELLON STREET WEST OF DIX ROAD IN THE CITY OF DETROIT, WAYNE COUNTY, MI. MICHCON REPAIR CREWS CONDUCTED LEAK POLICY CHECKS AND DETERMINED THE LEAK WAS ON THE 24" 150 PSIG TRANSMISSION PIPELINE (FORT STREET 150 PSIG SYSTEM). ENGINEERING DETERMINED THAT THE PRESSURE MUST BE REDUCED TO 45 PSIG PRIOR TO EXCAVATING OF THE 24" PIPELINE. AT 17:30 REPAIR CREWS REPORTED THAT A 24" VESSEL (DRIP POT) WAS LEAKING BELOW THE 24" PIPELINE AND WOULD BE UNABLE TO MAKE PERMANENT REPAIRS. ON AUGUST 17, 2010, ENGINEERING DETERMINED THAT A 24" STOPPLE FITTING AND VALVE SHUTDOWN WOULD BE REQUIRED TO ELIMINATED THE LEAK. ON SEPTEMBER 2, 2010 THE 24" STOPPLE FITTING WAS INSTALLED. AT 14:00 ON SEPTEMBER 3, 2010 THE PIPELINE WAS VALVED OFF AT THE RIVER ROUGE GATE STATION (APPROXIMATELY 1 MILE AWAY). AT 15:00 THE PIPELINE WAS BLOWN DOWN AND CLEARED. AT 21:00 A 24" VALVE WITH A PUP AND CAP WERE INSTALLED AND THE PIPELINE WAS PHYSICALLY SEPARATED ELIMINATING THE LEAK. MICHCON PERSONNEL MONITORED THE LEAK LOCATION ONCE PER SHIFT UNTIL THE LEAK WAS ELIMINATED ON SEPTEMBER 3, 2010. AS OF 9/15, ENGINEERING IS COMPLETING PLANS TO REMOVE AND REPLACE A 185 FOOT SECTION OF PIPELINE. MICHCON INSTALLED 60' OF 24" PIPE TO COMPLETE THE LEAK REPAIR. AN ADDITIONAL 162' OF 24" PIPE WAS INSTALLED TO PREPARE THE PIPELINE FOR FUTURE IN-LINE INSPECTION. THE PIPELINE WAS PUT BACK IN OPERATION ON OCTOBER 8, 2010.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100060 | 16074 | 2010-09-17 13:02 | SUPPLEMENTAL FINAL | 13845 | NORTHWEST PIPELINE CORP (WGP) | 295 CHIPETA WAY | SALT LAKE CITY | UT | 84108 | 2010-09-02 17:49 | 2010 |  |  | 48.4224 | -122.216 | 953022 | 2010-09-03 13:38 |  | NATURAL GAS |  | 82000 | 0.3 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | ISOLATING VALVE NOT CLOSE ALL THE WAY. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-09-03 06:40 | 2010-09-03 07:42 | ONSHORE | WA | 98273 | MOUNT VERNON | SKAGIT | MILEPOST | 1440 | MOUNT VERNON COMPRESSOR STATION | B PLANT SUCTION VALVE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | OTHER | INPROPER VALVE CLOSURE IN COMP. |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | MAINLINE | BALL | [7 empty] | CARBON STEEL |  | OTHER | [8 empty] | THIS WAS AN UNINTENTIONAL GAS RELEASE THROUGH A GAS VENTING SYSTEM FOLLOWING NORMAL COMPRESSOR SHUT DOWN SEQUENCE. MAINLINE ISOLATING VALVE DID NOT CLOSE FULLY. | CLASS 1 LOCATION | NO |  | 428 |  | NO | NO | NO |  | 0 | 0 | 100 | 119.341093327791 | 300000 | 184951.45631068 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 300100 | 191802.353526405 | 185070.797404007 | [8 empty] | 224 |  | 960 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | OTHER | WILLIAMS EMPLOYEE PULLING INTO FACILITY THE FOLLOWING MORNING. |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | YES |  |  |  | YES |  |  | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [204 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | [6 empty] | YES | WESTLOCK LIMIT SWITCH SHOWED VALVE CLOSED WHEN IT WAS STILL 10% ~ OPEN. LIMIT SWITCH ADJUSTED AFTER INCIDENT AND TESTED. OPERATED CORRECTLY | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | DUSTIN WALLIS | ENGINEER | dustin.wallis@williams.com | 801-584-6599 |  |  |  |  | DUSTIN WALLIS | ENGINEER | 801-584-6599 | dustin.wallis@williams.com | UNIT SUCTION VALVE WAS NOT FULLY CLOSED AGAINST THE MECHANICAL STOP EVEN THOUGH THE WESTLOCK INDICATOR SHOWED CLOSED. WHEN UNIT PRESSURIZED HOLD STATUS TIMED OUT THE UNIT VENT VALVE OPENED ALLOWING GAS TO FLOW THROUGH UNIT SUCTION VALVE. WHILE SETTING THE LIMIT SWITCHES ON THE NEW SUCTION VALVE THE VALVE OPERATOR SOLENOIDS WERE ENERGIZED LOCALLY WITH A PORTABLE POWER SUPPLY INSTEAD OF USING THE HMI. THE LIMIT SWITCHES WERE CHECKED WITH A FLUKE TO VERIFY THEY WERE GETTING A CLOSED CONTACT STATUS. WHILE THIS WAS BEING DONE THE VALVE WAS ALSO CHECKED TO VERIFY THE VALVE WAS TRAVELING ALL THE WAY TO THE MECHANICAL STOPS. THE VALVE WAS COMMISSIONED WITH ZERO GAS PRESSURE. THE VALVE STATUS WAS NOT VERIFIED USING THE UNIT HMI TO SEND OPEN AND CLOSED COMMANDS AFTER THE UNIT WAS PURGED AND PACKED. DISTRICT: WESTLOCK LIMIT SWITCH SHOWED VALVE CLOSED WHEN IT WAS STILL 10% ~ OPEN. LIMIT SWITCH ADJUSTED AND TESTED. OPERATES CORRECTLY GAS CONTROL ACTIONS: IT WAS CONCLUDED THAT THE CONTROLLERS FAILURE TO RESPOND TO A LOW-LUBE OIL & A UNIT COOL DOWN LOCKOUT ALARM IS OF GREAT CONCERN & IS CLEARLY A BREACH OF GAS CONTROLS PROTOCOL. THESE ALARMS WERE SECONDARY TO GAS BEING VENTED BUT FOLLOWING PROTOCOL REGARDING THESE ALARMS MAY HAVE FOUND THE PROBLEM MUCH SOONER.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100061 | 15929 | 2010-09-17 15:13 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | TX | 77002 | 2010-08-27 12:30 | 2010 |  |  | 28.5843 | -91.5724 | 952308 | 2010-08-27 14:30 |  | NATURAL GAS |  | 50000 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-08-28 15:30 | 2012-09-15 12:00 |  |  |  |  | NO |  |  |  |  | NO | [9 empty] | OFFSHORE | [28 empty] | 100 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SOUTH MARSH ISLAND | 10 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12.75 |  | 0.375 | 46000 | API | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | AMERICAN STEEL | COAL TAR | [28 empty] | 1968 | 1968 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 323 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 200000 | 123300.970873786 | 800000 | 954728.746622324 | 50000 | 59670.5466638952 | 0 | 0 |  |  | 1050000 | 593467.757613183 | 1137700.26416001 | [8 empty] | 944 |  | 1300 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  | YES | [6 empty] | YES | INITIAL DETERMINATION IS BASED ON PREVIOUS HISTORYOF FAILURE |  |  | YES |  |  |  | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [313 empty] | LOUIS SALINAS | COMPLIANCE ENGINEER | louis_salinas@transcanada.com | 832-320-5305 | 832-320-6305 |  |  |  | LOUIS SALINAS |  | 832-320-5305 | No Email Address | AN OFFSHORE PIPELINE LEAK WAS REPORTED AT 12:30 PM ON THE 12-IN ANR LINE 747 ON 8-27-10. IT WAS DISCOVERED IN THE SMI 10 AREA IN CLOSE PROXIMITY TO ANOTHER ANR PIPELINE AND TWO MARINER ENERGY PIPELINES BY A THIRD PARTY. THE PIPELINE WAS ISOLATED BY CLOSING THE BLOCK VALVE ON MARINER SMI BLK. 10 PLATFORM AND THE SIDE VALVE AT EI BLK. 115. A REPAIR CLAMP WAS INSTALLED, AND A PORTION OF THE PIPELINE WAS ABANDONED IN SEPTEMBER 2012.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100062 | 16737 | 2010-09-21 12:39 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2010-09-01 20:45 | 2010 |  |  | 28.9635 | -89.4027 | 952827 | 2010-09-01 21:40 |  | NATURAL GAS |  | 1375 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-09-02 10:30 |  | YES |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2010-09-01 20:50 | 2010-09-02 08:00 | OFFSHORE | [28 empty] | 4 | IN STATE WATERS | LA | WEST DELTA | 83 | PLAQUEMINES |  |  |  | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 10.75 |  | 0.25 | 46000 | API 5L OR EQUIVALENT | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | LONESTAR | OTHER | COAL TAR ENAMEL & CONCRETE | [27 empty] | 1959 | 1959 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 406 | 18 |  | CLASS 1 LOCATION | NO |  | 244 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 5500 | 3390.77669902913 | 500000 | 596705.466638952 | 0 | 0 | 0 | 0 |  |  | 505500 | 277418.926522889 | 600096.243337982 | [8 empty] | 830 |  | 1076 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 41712 | YES | [7 empty] | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | OTHER | NOTIFICATION FROM ANOTHER OPERATOR |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LINE OPERATING UNDER MAOP SO THAT ALARMS OR ALERTS WERE NOT ACTIVE AND WE WERE NOTIFIED BY AN EYE WITNESS ON A PLATFORM SOME DISTANCE AWAY. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) |  | YES | [13 empty] | YES | PRESSURE FLUCTUATIONS INDUCED DUCTILE TEARING MECHANISM IN THE WELD. | [7 empty] | YES | [62 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KENNETH C PETERS | SENIOR ENGINEER | ken.peters@elpaso.com | 2053257554 | 2053253508 |  |  |  | KENNETH C PETERS | SENIOR ENGINEER | 2053257554 | ken_peters@kindermorgan.com | TENNESSEE GAS PIPELINE (TGP) COMPANY'S 10" 526A-1200 PIPELINE RUPTURED SEPTEMBER 1, 2010. THE GAS IGNITED AND THE FIRE WAS WITNESSED BY ANOTHER OPERATOR ON A PLATFORM SOME DISTANCE AWAY. THE RUPTURE WAS IN THE GULF OF MEXICO NEAR PLAQUEMINES PARISH, LA. BLOCK VALVES WERE CLOSED AND THE PIPELINE WAS BEEN SHUT IN. INVESTIGATION REVEALED THAT THE PIPE HAD RUPTURED IN THE PIPE'S LONGITUDINAL SEAM. PIECES WERE REMOVED AND A METALLURGICAL ANALYSIS WAS PERFORMED. THIS ANALYSIS SHOWED PRE-EXISITNG WELD DEFECTS (LACK OF FUSION) THAT ARE LIKELY THE CAUSE OF THE RUPTURE. THE PIPELINE CONTINUES TO REMAIN DORMANT AS THE COMMERCIAL SIDE OF THE BUSINESS WEIGHS OPTIONS FOR THE FUTURE OF THE LINE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100063 | 16044 | 2010-09-22 16:17 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | TX | 77002 | 2010-09-02 14:00 | 2010 |  |  | 28.522 | -91.6451 | 952927 |  |  | NATURAL GAS |  | 1000 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES | [7 empty] | NO |  |  |  |  | NO | [9 empty] | OFFSHORE | [28 empty] | 160 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EUGENE ISLAND | 250 | PORTION OF RISER OUTSIDE OF SPLASH ZONE, INCLUDING RISER BEND | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 |  | 0.5 | 42000 | API | OTHER | UNKNOWN | UNKNOWN | OTHER | UNKNOWN | [27 empty] | 1970 | 1970 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 392 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 20000 | 12330.0970873786 | 125000 | 149176.366659738 | 10000 | 11934.109332779 | 0 | 0 |  |  | 155000 | 86737.1311967787 | 173440.573079896 | [8 empty] | 900 |  | 1250 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 2165 | NO |  | YES |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | OTHER | A SMALL PINHOLE DEFECT. |  | YES | [7 empty] | YES |  |  |  | NO | [11 empty] | YES | NO | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | LOUIS SALINAS |  | louis_salinas@transcanada.com | 832-320-5305 | 832-320-6305 |  |  |  | LOUIS SALINAS |  | 832-320-5305 | No Email Address | PAINT CONTRACTOR BEGAN TO SANDBLAST AND PAINT ON THE 16 " ANR LINE # 678, ON THE EUGENE ISLAND BLK. 250 PLATFORM (AN EL PASO FACILITY). A LEAK WAS DISCOVERED IN AN AREA UNDER A PIPE SUPPORT. NATURAL GAS WAS RELEASED. SUBSEQUENTLY, ALL WORK WAS STOPPED AND THE SANDBLASTERS LEFT THE PLATFORM AND CALLED IN, NOTIFYING OPERATIONS PERSONNEL OF THE LEAK. THE LEAK WAS CHECKED OUT BY ONE OF THE MEASUREMENT TEAMS; ALL VALVES WERE SHUT-IN AND NOTIFICATIONS TO THE MANAGER WERE MADE. A REPAIR PLAN IS BEING DEVELOPED, WHILE THE LINE IS OUT OF SERVICE. A REPAIR WAS COMPLETED IN LATE 2012. A BOLT-ON REPAIR CLAMP WAS USED. THE WAS PLACED BACK INTO SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100064 | 15112 | 2010-09-30 18:10 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION LP (SPECTRA ENERGY CORP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2010-09-02 11:10 | 2010 |  |  | 29.6147 | -88.7752 | 952891 | 2010-09-02 12:41 |  | NATURAL GAS |  | 8040 | 165 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-09-02 14:00 | 2010-09-11 19:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-09-02 11:10 | 2010-09-02 14:00 | OFFSHORE | [28 empty] | 50 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | MAIN PASS | 94 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 |  | 0.375 | 46000 | API-5LX-46 | SEAMLESS |  | US STEEL | EPOXY | [28 empty] | 1970 | 1970 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 419 |  | NO | NO | NO |  | 0 | 0 | 660 | 787.651215963417 | 32160 | 19826.7961165049 | 400000 | 477364.373311162 | 0 | 0 |  | 0 |  |  | 432820 | 240039.735981257 | 497978.82064363 | [8 empty] | 950 |  | 1440 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 58978 | NO |  | YES |  |  |  | YES | NO LAUNCHER OR RECEIVER BARRELS. | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE GAS LOSS WAS SO INSIGNIFICANT THAT SCADA WOULD NO BE ABLE TO DETECT IT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DWAYNE TESCHENDORF | PRINCIPAL ENGINEER | deteschendorf@spectraenergy.com | 713-627-5573 | 713-386-4468 |  |  |  | RICK KIVELA | DIRECTOR OF OPERATIONAL COMPLIANCE | 713-627-6388 | rwkivela@spectraenergy.com | INDICATIONS OF BUBBLES ON THE WATER'S SURFACE IN MAIN PASS BLOCK 94 WERE REPORTED BY A THIRD PARTY AT 11:10AM ON SEPTEMBER 2, 2010. UPON INVESTIGATION, IT WAS DETERMINED THE LEAK WAS THE CAUSED BY A PINHOLE RESULTING FROM INTERNAL CORROSION. A LEAK CLAMP WAS INSTALLED AS A PERMANENT REPAIR. INSTALLATION OF THE LEAK CLAMP COST $400,000.
2021-02-26 10:37 | YES | YES | GT (Gas Transmission) | 20100065 | 16433 | 2010-10-04 16:36 | SUPPLEMENTAL FINAL | 31451 | KINDER MORGAN TEXAS PIPELINE CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2010-09-17 09:49 | 2010 |  |  | 30.1045 | -94.9953 | 954358 | 2010-09-17 10:30 |  | NATURAL GAS |  | 1 | 0 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 |  | NO | TUBING FAILURE WAS UNRELATED TO TRANSPORTAION | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-09-17 09:49 | 2010-09-17 09:50 | ONSHORE | TX | 77535 | DAYTON | LIBERTY |  |  | DAYTON STORAGE FIELD |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | TUBING | [38 empty] | 2010 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL | OTHER | [8 empty] | TUBING COMPRESSION CONECTION FAILURE | CLASS 1 LOCATION | NO |  | 65 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 1 | 0.616504854368932 | 100 | 119.341093327791 | 10000 | 11934.109332779 | 0 | 0 |  |  | 10101 | 5533.49095653905 | 12054.0669309612 | [8 empty] | 2000 |  | 2300 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | TUBING CONNECTION FAILURE WAS UNRELATED TO THE SCADA SYSTEM. | [12 empty] | YES | 2 | 0 | YES | 2 | 0 | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | OTHER | COMPRESSION NUT | [6 empty] | YES | [172 empty] | MARTIN MULLER | COMPLIANCE | martin_muller@kindermorgan.com | 205-325-3863 | 2053253863 |  |  |  | MERLIN MOSEMAN | COMPLIANCE | 713-420-4614 | merlin_moseman@kindermorgan.com | ON SEPTEMBER 17, 2010 THE KINDER MORGAN TEXAS PIPELINE (KMTP) EMPLOYEE WAS ASSIGNED THE TASK OF REMOVING 1/2" TUBING THAT WAS INSTALLED ON SEPTEMBER 14, 2010. THE TUBING CONTAINED PRESSURIZED NATURAL GAS AND DURING THE REMOVAL IT PULLED OUT FROM THE COMPRESSION NUT. THE TUBING STRUCK THE EMPLOYEE IN THE LEGS. THE EMPLOYEE SUSTAINED INJURIES TO BOTH LEGS AND HIS RIGHT HAND. THE FERRULE ON THE CONNECTION THAT PARTED WAS NOT PROPERLY SEATED DURING INSTALLATION BY THE SUBCONTRACTOR.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20100066 | 15948 | 2010-10-05 00:40 | SUPPLEMENTAL FINAL | 602 | CENTERPOINT ENERGY GAS TRANSMISSION | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2010-08-31 16:20 | 2010 |  |  | 33.3493 | -93.9654 | 952701 | 2010-08-31 17:32 |  | NATURAL GAS |  | 20 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-08-31 17:03 | 2010-08-31 18:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2010-08-31 16:26 | 2010-08-31 16:26 | ONSHORE | AR | 71837 | FOUKE | MILLER | SURVEY STATION NO. | 484+55 | FOUKE TOWN BORDER MS 080772 | AM-129 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | TUBING | [38 empty] | 2006 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 100 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 60 | 36.9902912621359 | 1700 | 2028.79858657244 | 300 | 358.023279983371 | 0 | 0 | N/A |  | 2060 | 1133.96373198152 | 2423.81215781795 | [8 empty] | 50 |  | 65 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [52 empty] | LIGHTNING |  |  | DIRECT HIT |  |  | NO | [306 empty] | JOHNNY L. CAVITT | DOT COMPLIANCE MANAGER | johnny.cavitt@centerpointenergy.com | 318-429-3606 |  |  |  |  | JOHNNY L. CAVITT | DOT COMPLIANCE MANAGER | 318-429-3606 | johnny.cavitt@centerpointenergy.com | ON AUGUST 31, 2010 AT APPROXIMATELY 16:20 AN OPERATOR EMPLOYEE ARRIVED AT THE FOUKE TB STATION ON CEGT LINE AM-129 IN RESPONSE TO A COMMUNICATION FAILURE TICKET. AT 16:26 THE EMPLOYEE NOTICE AN ABNORMAL SOUND COMING FROM THE BUILDING WHERE THE STATION METER IS LOCATED. WHEN THEY OPENED THE DOOR TO THE BUILDING THEY DISCOVERED THAT THE EGM WAS ON FIRE AND THAT BURNING GAS WAS BLOWING OUT OF THE PRESSURE TRANSMITTER SENSING LINE. THE FIELD EMPLOYEE CONTACT SYSTEM CONTROL AT APPROXIMATELY 16:48 INFORMING THEM OF THE INCIDENT AND THAT HE WOULD ISOLATE THE METER BY CLOSING THE INLET AND OUTLET VALVES TO THE METER TO LET THE FIRE BURN ITSELF OUT. THE FIELD EMPLOYEE CALLED BACK TO SYSTEM CONTROL REQUESTING THAT THEY NOTIFY OTHER EMPLOYEES ON HIS FIELD TEAM THAT HE WOULD NEED A ASSISTANCE IN THE REPAIR OF THE METER. HELP ARRIVED AT 17:03 AND THEY WERE ABLE TO TURN OFF THE 1/4 INCH VALVE THAT FED THE SENSING LINE THAT STILL BURNING. AT APPROXIMATELY 17:22 SYSTEM CONTROL WAS NOTIFIED THAT THE FIRE WAS OUT. THE MELTED EGM WAS REMOVED, AND THE 1/4 INCH BALL VALVE WAS REPLACED AND PLUGGED. THE METER WAS INSPECTED AND NO DAMAGE WAS FOUND. THE STATION WAS PUT BACK IN SERVICE AT 18:00. IT WAS DETERMINED THAT LIGHTENING HAD HIT THE PRESSURE TRANSMITTER SENSING LINE CAUSING THE LEAK AND FIRE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100067 | 16088 | 2010-10-05 10:23 | SUPPLEMENTAL FINAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2010-10-02 12:43 | 2010 |  |  | 37.0031 | -100.4828 | 955856 | 2010-10-02 14:22 |  | NATURAL GAS |  | 1 | 11554.3 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-10-02 13:00 | 2010-10-05 12:55 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-10-02 12:43 | 2010-10-02 12:47 | ONSHORE | KS | 67864 | MEADE | MEADE | MILEPOST | MP 55 |  | AMARILLO #2 LINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 26 |  | 0.25 | 52000 | AO SMITH SPECIFICATION #2030-C | OTHER | ELECTRIC FUSION WELDED | AO SMITH | COAL TAR | [9 empty] | PIPE GIRTH WELD | [18 empty] | 1948 | 1948 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 479 |  | NO | NO | NO |  | 2500 | 2983.52733319476 | 63394 | 75655.0927042195 | 5 | 3.08252427184466 | 81469 | 97225.9953232177 | 1063 | 1268.59582207441 | 0 | 0 |  |  | 148431 | 81312.0137101532 | 177136.293706978 | [8 empty] | 629 |  | 712 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 86344 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DEAD VEGETATION LEAD TO DISCOVERY OF LEAK; NOT DETECTABLE BY CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES | [7 empty] | YES | CRACK IN WELD FROM ORIGINAL CONSTRUCTION | [12 empty] | YES | [63 empty] | YES | YES | [6 empty] | 2005 | [55 empty] | YES | 1975 | 925 | NO | [13 empty] | NO | [63 empty] | KRISTIN VAN DER LAAN | ENGINEER III COMPLIANCE CODES AND STANDARDS | kristin_vanderlaan@kindermorgan.com | 303-914-7752 | 303-984-3303 |  |  |  | REJI GEORGE | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713-420-5433 | reji_george@kindermorgan.com | DEAD VEGETATION WAS DISCOVERED ON THE ROW. KANSAS ONE-CALL CONTACTED AND PRESSURE REDUCTION INITIATED IN PREPARATION FOR EXCAVATION. LEAKING CRACK IN GIRTH WELD DISCOVERED AFTER EXCAVATION OF THE PIPELINE. PERSONNEL MOVED AWAY TO A SAFE DISTANCE. REMEDIATION PLAN MADE TO BLOWDOWN THE PIPELINE SEGMENT AND REPLACE THE PIPE. ESTIMATED COST OF REPAIRS AND GAS LOSS DUE TO BLOWDOWN DETERMINED TO BE $50,000 OR MORE. NRC CONTACTED. PIPELINE BLOWNDOWN AND REPAIRS MADE, SYSTEM RETURNED TO SERVICE. METALLURGICAL REPORT CONFIRMED THAT THE LEAK WAS CAUSED BY A CRACKED GIRTH WELD
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100068 | 15248 | 2010-10-07 12:38 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION CORP | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2010-09-09 05:30 | 2010 |  |  | 37.9384 | -82.6356 | 953483 | 2010-09-09 09:35 |  | NATURAL GAS |  | 23500 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-09-09 08:50 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-09-09 08:00 | 2010-09-09 08:00 | ONSHORE | KY | 41230 | RICHARDSON (NEAR) | LAWRENCE | SURVEY STATION NO. | 1741+68 | LINE P | VS-7087 - CHESTNUT CREEK TO PEACH ORCHARD BRANCH | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.25 | 24000 | UNKNOWN | SEAMLESS |  | UNKNOWN | NONE | [28 empty] | 1928 | 1928 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 24 | 20 |  | CLASS 1 LOCATION | NO |  | 234 |  | NO | NO | NO |  | 1000 | 1193.41093327791 | 0 | 0 | 91297 | 56285.0436893204 | 234864 | 280289.265433382 | 2800 | 3341.55061317813 | 55862 | 66666.3215547703 | INCLUDES MEASUREMENT EQUIPMENT FOR LINE P TO OPERATE AT REDUCED PRESSURE. |  | 385823 | 219696.697017488 | 407775.592223929 | [8 empty] | 284 |  | 288 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 38367 | NO | [5 empty] | YES | PIPELINE CONTAINS SECTIONS OF COUPLED PIPELINE. PIPELINE OPERATES AT LOW PRESSURE. | YES |  | YES |  |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | [8 empty] | YES | 1 | 0 | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [8 empty] | YES | YES |  |  | YES | NO |  | NO | NO | [8 empty] | NO | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | GREGORY LAGO | ENGINEER | glago@nisource.com | (304) 357-2465 | (304) 357-3804 |  |  |  | MICHAEL HOFFMAN | MANAGER | (304) 357-2548 | mikehoffman@nisource.com | RUPTURE OCCURRED ON LINE P IN A REMOTE CLASS 1 AREA APPROXIMATELY 850 FEET SOUTH OF STATE ROUTE 645 IN LAWRENCE COUNTY, KENTUCKY. THERE WERE NO INJURIES AND NO GAS IGNITION. THE PIPE IN THE AREA IS 20" OD, UNCOATED, COUPLED AND CATHODICALLY UNPROTECTED PIPE. THE CAUSE, BASED UPON VISUAL EXAMINATION OF THE RUTURED PIPE AND METALLURGICAL FAILURE ANALYSIS WAS DETERMINED TO BE EXTERNAL CORROSION. METALLURGICAL TESTING AND FAILURE ANALYSIS WAS COMPLETED BY DNV COLUMBUS INC.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100069 | 15772 | 2010-10-07 14:30 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION CORP | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2010-09-07 09:35 | 2010 |  |  | 40.8247 | -80.7564 | 953292 | 2010-09-07 12:50 |  | NATURAL GAS |  | 0 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | COMPRESSOR STATION UNIT NO. 2 WAS ISOLATED AS OF MARCH 2010 | [6 empty] | NO |  |  |  |  | YES | [6 empty] | 0 | 2010-09-07 09:36 | 2010-09-07 09:40 | ONSHORE | OH | 44431 | LEETONIA | COLUMBIANA |  |  | BRINKER COMPRESSOR STATION |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 1955 |  | CARBON STEEL |  | OTHER | [8 empty] | COMPRESSOR STATION CRANKCASE FAILURE. | CLASS 1 LOCATION | NO |  | 50 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 80 | 49.3203883495146 | 490000 | 584771.357306173 | 0 | 0 | 0 | 0 |  |  | 490080 | 268476.615953596 | 584820.677694523 | [8 empty] | 0 |  | 0 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE UNIT WAS SHUT DOWN SEVERAL MONTHS BEFORE THIS EVENT TOOK PLACE DUE TO CONSTRUCTION PROJECT. | [12 empty] | NO |  |  | YES | 2 | 0 | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | LOCK-OUT/TAG-OUT PROCEDURE AND LEAK SURVEY FOR GAS LEAK WERE NOT FOLLOWED AS PUBLISHED ON COMPANY'S PLANS AND PROCEDURES DOCUMENTS. |  |  |  | YES | SHUTOFF VALVES ON THE COMMON OIL DRAIN LINE THAT SERVE TO ISOLATE EACH UNIT WERE LEFT OPEN AND WERE NOT INCLUDED AS PART OF THE LOCKOUT/TAGOUT (LOTO) PROCEDURE BEING USED AT THE TIME OF THE INCIDENT. | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | GEORGE HAMATY | ENGINEER | ghamaty@nisource.com | (304) 357-3728 | (034) 357-3804 |  |  |  | PERRY MICHAEL HOFFMAN | MANAGER | (304) 357-2465 | mikehoffman@nisource.com | TWO CONTRACT EMPLOYEES WERE WELDING OUTSIDE THE COMPRESSOR STATION BUILDING AT THE MANIFOLD OF THE EXHAUST PIPING FOR COMPRESSOR UNIT NO. 2. ALL NECESSARY HOT WORK PERMITS WERE IN PLACE AT THE TIME. THE COMPRESSOR STATION HAS THREE UNITS, NONE OF WHICH WERE OPERATIONAL AT THE TIME OF THIS EVENT. UNITS NO. 1 & 2 WERE ISOLATED WITH PROPER LOCK-OUT TAG-OUT IN PLACE PER THE COMPANY'S OPERATIONS & MAINTENANCE MANUAL. UNIT NO. 3 WAS NOT RUNNING AT THE TIME OF THE INCIDENT. THE COMPANY HAS INITIATED A ROOT CAUSE ANALYSIS (RCA) INVESTIGATION TO DETERMINE THE CAUSE OF THE INCIDENT. THE COMPRESSOR MANUFACTURER ALONG WITH A FAILURE ANALYSIS INVESTIGATIVE EXPERT (CONSULTANT) CONDUCTED THEIR INVESTIGATIONS INTO THIS INCIDENT. THE RCA REPORT IDENTIFIED THAT THE SOURCE OF IGNITION WAS ARC WELDING BEING PERFORMED ON THE EXHAUST FLANGE LOCATED OUTSIDE OF THE COMPRESSOR BUILDING. NATURAL GAS WAS PRESENT IN THE CRANKCASE VENT DUE TO A PACKING LEAK IN THE COMPRESSOR CYLINDERS OF UNIT #3. THE PACKING LEAK ON UNIT NO. 3 TRAVELED VIA A COMMON OIL DRAIN TO THE UNIT NO. 2 COMPRESSOR CYLINDER DISTANCE PIECES AND THUS INTO THE UNIT NO.2 CRANKCASE AND VENT. GAS MONITORING WAS PERFORMED USING A GAS DETECTOR AT THE VENTS, EXHAUST, STARTERS, AND SURROUNDING AREA PRIOR TO THE WELDING AND THERE WAS NO INDICATION OF A COMBUSTIBLE ATMOSPHERE. IT APPEARS THAT THE GAS MONITOR WAS NOT EXPOSED TO THE COMBUSTIBLE MIXTURE LONG ENOUGH TO PROVIDE AN ALARM TO THE OPERATOR. SHUTOFF VALVES ON THE COMMON OIL DRAIN LINE THAT SERVE TO ISOLATE EACH UNIT WERE LEFT OPEN AND WERE NOT INCLUDED AS PART OF THE LOCKOUT/TAGOUT (LOTO) PROCEDURE BEING USED AT THE TIME OF THE INCIDENT. RECOMMENDATIONS WERE NOTED AND SHARED VIA A SAFETY ALERT BROADCAST THROUGHOUT THE ENTIRE COMPANY NOTIFICATION SYSTEM. AMONG THESE RECOMMENDATIONS WERE: MANDATORY INSPECTION OF ALL UNITS AND FACILITIES COMPANY-WIDE FOR SIMILAR COMMON VENT/PIPING SYSTEMS THAT WERE FOUND AT THE INCIDENT SITE. ENGINEERING SHALL REVIEW INSPECTION RESULTS, DOCUMENTATION AND ASSURE THE NECESSARY FOLLOW-UP ACTIVITIES ARE PLANNED AND COMPLETED. REVIEW AND PERFORM MODIFICATIONS TO STATION ISOLATION LOCK-OUT/TAG-OUT PROCEDURES TO INCLUDE DRAIN AND VENT VALVES THAT ARE COMMON WITHIN A STATION THAT COULD POTENTIALLY LEAD TO A COMBUSTIBLE MIXTURE. WHEN PERFORMING "HOT WORK" ON A COMPRESSOR UNIT, CONSIDERATIONS SHALL BE MADE FOR EVACUATING GAS FROM ALL UNITS WITHIN THE COMPRESSOR BUILDING. IDEALLY, ANY WELDING, BURNING, OPEN FLAME OR GRINDING TASKS SHOULD BE PERFORMED IN SAFE AREAS OUTSIDE THE BOUNDARIES OF THE COMPRESSOR BUILDING. WHEN HOT WORK IS NECESSARY IN BUILDINGS WITH PRESSURIZED UNITS, IT IS CRITICAL TO ENSURE EQUIPMENT SPECIFIC ISOLATION AND LOTO PLANS ARE IN PLACE AND THAT HOT WORK PERMITS ARE EXECUTED TO ENSURE ABSENCE OF ANY FLAMMABLE/EXPLOSIVE ATMOSPHERE. LOTO PLANS SHOULD BE CHALLENGED AND REVIEWED BY OPERATIONS, ENGINEERING AND CONTRACTORS PERFORMING THE WORK BEFORE BEGINNING ANY WORK ON COMPRESSION UNITS TO IDENTIFY POTENTIAL PATHS FOR A FLAMMABLE/EXPLOSIVE MIXTURE TO OCCUR.
2021-02-26 10:37 | YES | YES | GT (Gas Transmission) | 20100070 | 17044 | 2010-10-13 10:40 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2010-09-09 18:11 | 2010 |  |  | 37.6225 | -122.4419 | 95380 | 2010-09-09 19:30 |  | NATURAL GAS |  | 47600 | 0 | 0 | YES | 0 | 0 | 0 | 0 | 8 | 8 | YES | 0 | 0 | 0 | 0 | 51 | 51 |  | YES |  | 2010-09-09 19:30 |  | YES |  |  |  | YES |  |  |  |  | YES | [6 empty] | 108 | 2010-09-09 18:13 | 2010-09-09 18:41 | ONSHORE | CA | 94066 | SAN BRUNO | SAN MATEO | MILEPOST | MP 39.28 | L132 | 180 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 |  | 0.375 | 32000 | NA | DSAW |  | NA | ASPHALT | [28 empty] | 1956 | 1949 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 216 | 60 |  | CLASS 3 LOCATION | YES | METHOD2 | 414 |  | YES | NO | NO |  | 50000000 | 59670546.6638952 | 0 | 0 | 263000 | 162140.776699029 | 100000 | 119341.09332779 | 0 | 0 | 508000000 | 606252754.105176 | PAID TO SETTLE PERSONAL INJURY, PROPERTY DAMAGE AND OTHER CLAIMS |  | 558363000 | 305899246.076111 | 666204782.639098 | [8 empty] | 386 |  | 400 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 8237 | NO | YES | YES |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | NO | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) | [11 empty] | YES | SEE ATTACHED FINAL NTSB REPORT | YES | 3 | 0 | YES | 1 | 0 | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) |  | YES | [13 empty] | YES | SEE ATTACHED NTSB REPORT | [13 empty] | YES | SEE ATTACHED FINAL NTSB REPORT. | [55 empty] | NO | [63 empty] | NO |  |  | Yes, but the point of the Accident was not identified as a dig site |  | 2009 | [11 empty] | NO | [63 empty] | LAURENCE DENISTON | PRINCIPAL | lcd1@pge.com | 925-328-5756 |  |  |  |  | MIKE FALK | DIRECTOR | 925-244-3276 | mdfl@pge.com | AT APPROXIMATELY 1811 HOURS ON SEPTEMBER 9, 2010 LINE 132 RUPTURED AT MP 39.28 NEAR GLENVIEW DRIVE AND EARL AVENUE IN SAN BRUNO CAUSING A FIRE. THE L132 PIPELINE WAS ISOLATED AT APPROXIMATELY 1930 HOURS BETWEEN L132 MP 38.49 AND MP 40.05. THERE WERE EIGHT FATALITIES AND FIFTY-ONE OTHER INJURIES. THIRTY-EIGHT HOMES WERE DESTROYED, SEVEN OTHERS SIGNIFICANTLY DAMAGED WITH DOZENS OF OTHERS SUSTAINING SOME DAMAGE. SEE ATTACHED FINAL NTSB REPORT.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20100072 | 16313 | 2010-10-13 12:19 | SUPPLEMENTAL FINAL | 18646 | ENBRIDGE OFFSHORE (GAS TRANSMISSION) LLC | 1100 LOUISIANA SUITE 3300 | HOUSTON | TX | 77002 | 2010-09-16 13:45 | 2010 |  |  | 28.3102 | -92.3326 | 954260 | 2010-09-16 15:38 |  | NATURAL GAS |  | 259 | 20796 | 1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-09-16 22:00 | 2010-09-27 03:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-09-16 13:45 | 2010-09-16 14:52 | OFFSHORE | [28 empty] | 51 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | VERMILLIION | 263 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTRASTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | WELD/FUSION | [19 empty] | OTHER BUTT WELD | [18 empty] | 1974 |  | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 20 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 583000 | 695758.574101019 | 0 | 0 | 0 | 0 | AFE FOR THE REPAIR WAS $583000 |  | 583000 | 319371.544377468 | 695758.574101019 | [8 empty] | 780 |  | 1200 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | AUTOMATIC | 271661 | NO | [5 empty] | YES | ORIGINATION PLATFORM ABANDONED | NO | [6 empty] | OFFSHORE GATHERING | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIN HOLE LEAK DETECTED BY OUTSIDE COMPANY FLYING OVER THE AREA. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING | [5 empty] | YES | UNABLE TO DETERMINE | YES | [7 empty] | YES | PIN HOLE IN WELD | YES | NO | NO | YES | [168 empty] | NO | [80 empty] | NO | [63 empty] | LESLIE B STEVENS | COMPLIANCE COORDIANTOR | leslie.stevens@enbridge.com | 832-214-1649 | 985-851-4126 |  |  |  | LESLIE B STEVENS | COMPLIANCE COORDINATOR | 832-214-1649 | leslie.stevens@enbridge.com | BUBBLES IN THE WATER IN THE VERMILLION BLOCK 263 WERE SPOTTED BY AN OUTSIDE COMPANY FLYING OVER THE AREA ON SEPEMBER 16, 2010. THE PIPELINE WAS SHUT DOWN AND ISOLATED AT EACH END. A DIVE BOAT WAS HIRED TO INVESTIGATE THE SOURCE OF THE LEAK. THE LEAK WAS CONFIRMED TO BE A PINHOLE LEAK IN OUR PIPLINE IN VERMILLION BLOCK 263. A PIPELINE CLAMP WAS INSTALLED AND THE PIPELINE PUT BACK IN SERVICE ON SEPTEMBER 27TH 2010.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100073 | 15113 | 2010-10-14 09:29 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION LP (SPECTRA ENERGY CORP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2010-09-16 11:00 | 2010 |  |  | 28.9212 | -93.0323 | 954233 | 2010-09-16 11:40 |  | NATURAL GAS |  | 400 | 12700 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-09-16 11:30 | 2010-09-21 12:40 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-09-16 11:00 | 2010-09-16 16:00 | OFFSHORE | [28 empty] | 150 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST CAMERON | 272 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 20 |  | 0.406 | 52000 | API-5L X-52 | SEAMLESS |  | U.S. STEEL | OTHER | CONCRETE COATED | [27 empty] | 1969 | 1969 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 524 |  | NO | NO | NO |  | 0 | 0 | 50800 | 60625.2754105176 | 1600 | 986.407766990291 | 250000 | 298352.733319476 | 0 | 0 | 0 | 0 |  |  | 302400 | 165803.032021413 | 359964.416496984 | [8 empty] | 900 |  | 1440 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 91608 | NO |  |  |  | YES |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | NOTIFICATION FROM PLATFORM OPERATOR |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE GAS LOSS WAS SO INSIGNIFICANT THAT SCADA WOULD NOT BE ABLE TO DETECT IT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DWAYNE TESCHENDORF | PRINCIPAL ENGINEER | deteschendorf@spectraenergy.com | 713-627-5573 | 713-386-4468 |  |  |  | RICK KIVELA | DIRECTOR OF OPERATIONAL COMPLIANCE | 713-627-6388 | rwkivela@spectraenergy.com | INDICATIONS OF BUBBLES ON THE SURFACE OF THE WATER IN WEST CAMERON BLOCK 272 WERE REPORTED BY A NEARBY PLATFORM OPERATOR AT 11:00 AM ON SEPTEMBER 16, 2010. UPON INVESTIGATION, IT WAS DETERMINED THE LEAK WAS CAUSED BY A PINHOLE RESULTING FROM INTERNAL CORROSION. A LEAK CLAMP WAS INSTALLED AS A PERMANENT REPAIR AT A COST OF $250,000.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20100074 | 15219 | 2010-10-14 20:24 | SUPPLEMENTAL FINAL | 602 | CENTERPOINT ENERGY GAS TRANSMISSION | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2010-09-14 14:00 | 2010 |  |  | 35.0852 | -92.4898 | 953986 | 2010-09-14 14:28 |  | NATURAL GAS |  | 168 | 168 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | LINE WAS ISOLATED AND PRESSURE REDUCED TO 100 PSI | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 80 | 2010-09-14 14:00 | 2010-09-14 14:00 | ONSHORE | AR | 72032 | CONWAY | FAULKNER | SURVEY STATION NO. | 1272+39 | CEGT | LINE B | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | ABANDON TAP | 1949 |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | YES | METHOD2 | 154 |  | NO | NO | NO |  | 0 | 0 | 638 | 761.396175431303 | 638 | 393.330097087379 | 1840 | 2195.87611723135 | 7008 | 8363.42382041156 | 8835 | 10543.7855955103 | EVACUATION OF NURSING HOME AND LOCAL BUSINESS |  | 18959 | 10444.1572101824 | 22257.8118056719 | [8 empty] | 413 |  | 500 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 27848 | NO |  |  |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS CAUSED BY 2ND PARTY DAMAGE AND REPORTED ALMOST IMMEDIATELY SO THERE WAS NO CONTROL ROOM ACTIONS THAT CAUSED OR CONTRIBUTED TO THE INCIDENT | [12 empty] | YES | 1 | 0 | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [10 empty] | NO | YES | CITY STREET |  |  | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 1009090334 | ARKANSAS ONE CALL | UTILITY OWNER | YES | YES |  |  | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO MAINTAIN CLEARANCE | [263 empty] | JOHNNY L. CAVITT | DOT COMPLIANCE MANAGER | johnny.cavitt@centerpointenergy.com | 318-429-3606 | 318-429-3927 |  |  |  | JOHNNY L. CAVITT | DOT COMPLIANCE MANAGER | 318-429-3606 | johnny.cavitt@centerpointenergy.com | ON SEPTEMBER 14, 2010 AT APPROXIMATELY 1400 HRS, CEGT PERSONNEL REPORTS TO CEGT SYSTEM CONTROL THAT AN UNDERGROUND ABANDONED TAP WAS STRUCK, AND WAS LEAKING GAS AT THE CONNECTION OF A 1" VALVE TO A 1" PIPE CONNECTED TO LINE B AT THE CORNER OF COLLEGE AND REEDY STREET IN CONWAY, AR. A CALL WAS MADE TO 911 TO REQUEST INCIDENT ASSISTANCE FROM THE CITY OF CONWAY POLICE AND FIRE DEPARTMENTS. LOCAL TRAFFIC WAS BLOCKED AND ROUTED AROUND THE IMMEDIATE AREA. ST ANDREWS NURSING HOME WAS EVACUATED TO A LOCAL CHURCH AND THE LOCAL HOSPITAL. DURING THE INCIDENT GAS DETECTION EQUIPMENT WAS USED TO MONITOR FOR ANY MIGRATION OF THE ESCAPING GAS. AT APPROXIMATELY 1740 HRS THE PLUG WAS REMOVED FROM THE TOP OF THE VALVE AND THE DAMAGED VALVE WAS OPENED TO VENT TO THE ATMOSPHERE. THE VALVE AND A SECTION OF THE ONE INCH PIPE WERE REMOVED USING A FOUR DISC CUTTER. THE REMAINING PIPE WAS THEN THREADED AND A NEW ONE INCH VALVE WAS INSTALLED. THE VALVE WAS SHUT OFF AT APPROXIMATELY 1807 HRS.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20100075 | 15950 | 2010-10-14 22:09 | SUPPLEMENTAL FINAL | 602 | CENTERPOINT ENERGY GAS TRANSMISSION | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2010-09-14 08:20 | 2010 |  |  | 35.3101 | -92.3492 | 953938 | 2010-09-14 09:05 |  | NATURAL GAS |  | 60.5 | 60.5 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | PIPELINE PERSONNEL WERE THEN ABLE TO ACCESS THE BELOW GROUND VALVE AND SHUT IT I | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 2 | 2010-09-14 08:20 | 2010-09-14 08:20 | ONSHORE | AR | 72061 | GUY | FAULKNER | SURVEY STATION NO. | 954+48 | CEGT LINE BM-21 | LINE BM-21 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | METER | [38 empty] | 1985 |  | CARBON STEEL |  | OTHER | [8 empty] | VEHICLE RAN OVER TAP | CLASS 2 LOCATION | NO |  | 55 |  | NO | NO | NO |  | 0 | 0 | 230 | 274.484514653918 | 0 | 0 | 0 | 0 | 3701 | 4416.81386406153 | 0 | 0 | N/A |  | 3931 | 2153.4297443359 | 4691.29837871544 | [8 empty] | 325 |  | 400 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OUTSIDE FORCE - VEHICLE RAN OVER TAP, CONTROLLER ACTION WAS NOT THE CAUSE OR OR A CONTRIBUTING FACTOR TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [260 empty] | JOHNNY L. CAVITT | DOT COMPLIANCE MANAGER | johnny.cavitt@centerpointenergy.com | 318-429-3606 | 318-429-3927 |  |  |  | JOHNNY L. CAVITT | DOT COMPLIANCE MANAGER | 318-429-3606 | johnny.cavitt@centerpointenergy.com | AT APPROXIMATELY 08:20 HRS ON SEPTEMBER 14, A VEHICLE LEFT THE ROAD STRIKING AN ABOVEGROUND TAP ON CEGT BM-21 NEAR GUY, AR. THE VEHICLE PROCEEDED THROUGH THE SETTING AND STRUCK A POWER POLE APPROXIMATELY 40 FEET FROM THE CEGT TAP. PERSONS IN THE VEHICLE WERE REMOVED FROM THE SITE BY EMERGENCY RESPONSE PERSONNEL. TRAFFIC WAS BLOCKED BOTH DIRECTIONS ON HWY 25 A MINIMUM 1/4 MILE FROM INCIDENT SITE. FIRE DEPARTMENT EVACUATED 2 PERSONS FROM A HOME THAT WAS WITHIN THE 1/4 MILE AREA. CEGT WORKED WITH POWER COMPANY ON-SITE TO ISOLATE POWER, ELIMINATING IGNITION SOURCE. PIPELINE PERSONNEL WERE THEN ABLE TO ACCESS THE BELOW GROUND VALVE AND SHUT IT IN AT 10:30 HRS. HIGHWAY WAS REOPENED AT 10:35, AND HOMEOWNERS WERE ALLOWED BACK INTO THEIR HOME AT 11:00. THE TAP WAS REPAIRED AND PUT BACK IN SERVICE AT 13:10 HRS.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20100076 | 15102 | 2010-10-18 11:55 | SUPPLEMENTAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 569 BROOKWOOD VILLAGE, ROOM 798 | BIRMINGHAM | AL | 35209 | 2010-09-21 08:13 | 2010 |  |  | 30.7572 | -84.2843 | 954697 | 2010-09-21 10:11 |  | NATURAL GAS |  | 7153 | 135 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-09-21 09:00 | 2010-09-21 19:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-09-21 08:13 | 2010-09-21 08:55 | ONSHORE | GA | 39827 | CAIRO | GRADY | MILEPOST | 14.279 | SOUTH GRADY LINE 4 |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 11 |  | YES |  |  |  |  | YES | UNCASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6.625 |  | 0.188 | 35000 | API 5L OR EQUIVALENT | LONGITUDINAL ERW - LOW FREQUENCY |  | ACME NEWPORT STEEL | COAL TAR | [28 empty] | 1955 | 1955 | CARBON STEEL |  | MECHANICAL PUNCTURE | 2 | 6 | [7 empty] | CLASS 1 LOCATION | NO |  | 79 |  | NO | NO | NO |  | 0 | 0 | 523 | 624.153918104344 | 27734 | 17098.145631068 | 19934 | 23789.4535439618 |  | 0 | 2396 | 2859.41259613386 | PURGE GAS |  | 50587 | 30245.4598035516 | 44371.1656892679 | [8 empty] | 811 |  | 990 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 50836 | NO |  | YES |  |  |  | YES | NO PERMANENTLY INSTALLED LAUNCHER OR RECEIVER. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | 3RD PARTY DAMAGE NEGATED THE NEED FOR CONTROL ROOM CONSIDERATION. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES | YES | COUNTY ROAD |  |  | YES | [6 empty] | COUNTY | GRADER/SCRAPER | GRADING | NO |  |  | DATA NOT COLLECTED | DATA NOT COLLECTED | DATA NOT COLLECTED | YES | 11 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | ken.peters@elpaso.com | 2053247554 | 2053253729 |  |  |  | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | 2053257554 | ken.peters@elpaso.com | ON SEPTEMBER 21, 2010, A GRADY COUNTY PUBLIC WORKS MOTOR GRADER DAMAGED SOUTHERN NATURAL GAS COMPANY'S 6' SOUTH GRADY PIPELINE CAUSING A GAS RELEASE AT 811 PSIG. THE LOCATION WAS AT A DIRT ROAD, HOPKINS ROAD, IN GRADY COUNTY, GA. THE MOTOR GRADER OPERATOR WAS INJURED ON HIS RIGHT SIDE DUE TO DEBRIS FROM THE GAS RELEASE. HE WAS TREATED AT THE GRADY COUNTY HOSPITAL AND RELEASED WITHIN 4 HOURS. NO FIRE OCCURRED. 911 EMERGENCY RESPONDERS INCLUDED THE GRADY COUNTY EMA AND THE CALVARY VOLUNTEER FIRE DEPARTMENT WHO SECURED THE AREA. 9.628 MILES OF PIPELINE WAS ISOLATED AND DEPRESSURIZED. EVALUATION OF THE DAMAGE TO THE PIPELINE REVEALED A 6' X 2' CUT INTO THE PIPE. A 2' SECTION OF PIPE WAS REPLACED AND THE LINE WAS RETURNED TO SERVICE AT 7:00 P.M. EDT THE SAME DAY. THE MOTOR GRADER OPERATOR DID NOT CONTACT THE ONE CALL CENTER PRIOR TO THE GRADING ACTIVITY. THE PIPELINE WAS MARKED WITH 49 CFR 192 MARKERS ON BOTH SIDES OF THE DIRT ROAD. THE OPERATOR WAS PULLING THE DITCHES ON THE NORTH SIDE OF THE ROAD, WHICH IS THE ONLY SIDE OF THE ROAD THAT THE COUNTY MAINTAINS IN THIS AREA. THE GRADER OPERATOR STATED THAT HE LIFTED HIS BLADE AND THOUGHT HE WAS PAST THE PIPELINE WHEN HE LOWERED HIS BLADE. THE BLADE WAS LOWERED DIRECTLY ON TOP OF THE PIPELINE, NEAR THE NORTH SIDE MARKER, RESULTING IN THE DAMAGE TO THE PIPE AND THE SUBSEQUENT GAS RELEASE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100077 | 15207 | 2010-10-18 17:49 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | TX | 77002 | 2010-09-28 15:30 | 2010 |  |  | 28.3193 | -91.6043 | 955427 | 2010-09-28 17:00 |  | NATURAL GAS |  | 2000 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | COMPANY FLEW RECON OVER AREA TO CONFIRM LEAK ON ITS FACILITIES. | [6 empty] | NO |  |  |  |  | NO | [9 empty] | OFFSHORE | [28 empty] | 226 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EUGENE ISLAND | 307 | BELOW WATER, PIPE ON OR ABOVE SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 |  | 0.375 | 52000 | API | OTHER | UNKNOWN | KAISER | OTHER | UNKNOWN | [27 empty] | 1978 | 1978 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 398 |  | NO | NO | NO |  | 0 | 0 | 20000 | 23868.2186655581 | 20000 | 12330.0970873786 | 99000 | 118147.682394513 | 75000 | 89505.8199958429 | 0 | 0 |  |  | 214000 | 119057.750610622 | 243851.818143292 | [8 empty] | 875 |  | 1300 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 23000 | NO |  | YES | [5 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | AIR PATROL |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | PIPE HAS NOT BEEN INSPECTED - IC IS SUSPECTED CAUSE. |  |  |  |  | YES | UNDETERMINED AT THIS TIME. |  |  | YES | THE CAUSE OF THE IC HAS NOT BEEN DETERMINED TO DATE. |  |  | YES |  |  |  | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [313 empty] | LOUIS SALINAS |  | louis_salinas@transcanada.com | 832-320-5305 | 832-320-6305 |  |  |  | LOUIS SALINAS | COMPLIANCE ENGINEER | 832-320-5305 | No Email Address | A LEAK WAS LOCATED ON THE EUGENE ISLAND BLOCK 307 LINE (TRANSCANADA-ANR LINE 607) AFTER THE PRODUCER SIGHTED AN APPROXIMATE 20 FT. DIAMETER BUBBLE CIRCLE WITH NO SHEEN. THE ANR 16-IN. LINE TRAVERSES FROM EI BLK. 307A TO EI BLK. 305. AFTER THE LINE WAS SHUT-IN (ONE PRODUCER) AND THE SIDE VALVE AT EI BLK. 305 WAS CLOSED, THE LINE WAS BLOWN DOWN. A DIVE BOAT WAS MOBILIZED TO ASSESS THE PIPE CONDTION, LOCATE THE SOURCE OF THE LEAK, AND RECOMMEND A REPAIR METHOD. IN LATE, 2010, THE PIPELINE WAS SOLD TO DYNAMIC OFFSHORE, INC. OPERATIONAL RESPONSIBILITY WAS TRANSFERRED TO DYNAMIC.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20100078 | 15157 | 2010-10-20 08:54 | SUPPLEMENTAL FINAL | 4070 | EAST TENNESSEE NATURAL GAS CO | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2010-09-25 20:00 | 2010 |  |  | 35.0882 | -85.2114 | 955164 | 2010-09-25 21:15 |  | NATURAL GAS |  | 50 | 1383 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-09-25 20:00 | 2010-09-26 19:58 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-09-25 20:00 | 2010-09-25 20:00 | ONSHORE | TN | 37416 | CHATTANOOGA | HAMILTON | SURVEY STATION NO. | 304+27 | 3200-1 |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 12.75 |  | 0.25 | 42000 | API-5L X-42 | LONGITUDINAL ERW - LOW FREQUENCY |  | REPUBLIC | COMPOSITE | [28 empty] | 1950 | 1950 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | NO |  | 253 |  | NO | NO | NO |  | 2500 | 2983.52733319476 | 5532 | 6601.94928289337 | 200 | 123.300970873786 | 50000 | 59670.5466638952 | 0 | 0 | 0 | 0 |  |  | 58232 | 31918.1738478231 | 69379.3242508572 | [8 empty] | 744 |  | 823 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 28224 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE GAS LOSS WAS SO INSIGNIFICANT THAT SCADA WOULD NOT BE ABLE TO DETECT IT. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | YES | YES | [13 empty] | YES | UNDETERMINED | [7 empty] | YES | [62 empty] | YES | YES | [6 empty] | 2004 | [55 empty] | YES | 1994 | 1260 | NO | [13 empty] | NO | [63 empty] | DWAYNE TESCHENDORF | PRINCIPAL ENGINEER | deteschendorf@spectraenergy.com | 713-627-5573 | 713-386-4468 |  |  |  | RICK KIVELA | DIRECTOR OF OPERATIONAL COMPLIANCE | 713-627-6388 | rwkivela@spectraenergy.com | A SMALL LEAK WAS DETECTED ON EAST TENNESSEE NATURAL GAS LINE 3200-1 DURING A ROUTINE INSTRUMENTED LEAK SURVEY. THE LEAK ORIGINATED AT THE PIPE WELD SEAM. THE LEAKING PIPE WAS REMOVED AND A METALLURGICAL ANALYSIS WAS PERFORMED. THE METALLURGICAL ANALYSIS DETERMINED THE LEAK WAS THE RESULT OF LACK OF FUSION IN THE PIPE WELD SEAM.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20100079 | 15156 | 2010-10-20 08:55 | SUPPLEMENTAL FINAL | 4070 | EAST TENNESSEE NATURAL GAS CO | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2010-09-24 12:00 | 2010 |  |  | 35.1051 | -85.1679 | 955034 | 2010-09-24 13:00 |  | NATURAL GAS |  | 50 | 1383 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-09-25 14:00 | 2010-09-26 19:58 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-09-24 12:00 | 2010-09-24 12:00 | ONSHORE | TN | 37416 | CHATTANOOGA | HAMILTON | SURVEY STATION NO. | 453+20 | 3200-1 |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 12.75 |  | 0.25 | 42000 | API-5L X-42 | LONGITUDINAL ERW - LOW FREQUENCY |  | REPUBLIC | COMPOSITE | [28 empty] | 1950 | 1950 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 253 |  | NO | NO | NO |  | 5000 | 5967.05466638952 | 5532 | 6601.94928289337 | 200 | 123.300970873786 | 50000 | 59670.5466638952 | 0 | 0 | 0 | 0 |  |  | 60732 | 33287.6916195961 | 72362.8515840519 | [8 empty] | 744 |  | 823 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 28224 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE GAS LOSS WAS SO INSIGNIFICANT THAT SCADA WOULD NOT BE ABLE TO DETECT IT. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | YES | YES | [13 empty] | YES | UNDETERMINED | [7 empty] | YES | [62 empty] | YES | YES | [6 empty] | 2004 | [55 empty] | YES | 1994 | 1260 | NO | [13 empty] | NO | [63 empty] | DWAYNE TESCHENDORF | PRINCIPAL ENGINEER | deteschendorf@spectraenergy.com | 713-627-5573 | 713-386-4468 |  |  |  | RICK KIVELA | DIRECTOR OF OPERATIONAL COMPLIANCE | 713-627-6388 | rwkivela@spectraenergy.com | A SMALL LEAK WAS DETECTED ON EAST TENNESSEE NATURAL GAS LINE 3200-1 DURING A ROUTINE INSTRUMENTED LEAK SURVEY. THE LEAK ORIGINATED AT THE PIPE WELD SEAM. THE LEAKING PIPE WAS REMOVED AND A METALLURGICAL ANALYSIS WAS PERFORMED. THE METALLURGICAL ANALYSIS DETERMINED THE LEAK WAS THE RESULT OF LACK OF FUSION IN THE PIPE WELD SEAM.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20100080 | 15944 | 2010-10-20 20:16 | SUPPLEMENTAL FINAL | 602 | CENTERPOINT ENERGY GAS TRANSMISSION | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2010-09-20 15:44 | 2010 |  |  | 32.8745 | -92.7815 | 954646 | 2010-09-20 16:38 |  | NATURAL GAS |  | 1029 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-09-20 18:43 | 2010-09-21 02:43 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-09-20 15:44 | 2010-09-20 16:14 | ONSHORE | LA | 71222 | SUMMERFIELD | CLAIBORNE | SURVEY STATION NO. | 146+35 | RE#319 MS244705 | CEGT LINE KM-48 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | M&R STATION | 1991 |  | CARBON STEEL |  | OTHER | [8 empty] | LOG TRUCK RAN OFF ROAD, ROLLED OVER AND LOGS CAME OFF OF TRAILOR AND DAMAGED M&R STATION. | CLASS 1 LOCATION | NO |  | 46 |  | NO | NO | NO |  | 10000 | 11934.109332779 | 0 | 0 | 3962 | 2442.59223300971 | 26237 | 31311.5226564124 | 200 | 238.682186655581 | 0 | 0 |  |  | 40399 | 22492.7938983546 | 45926.9064088567 | [8 empty] | 305 |  | 500 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS AN OUTSIDE FORCE DAMAGE EVENT AND THE CONTROLLER ACTIONS WERE NOT THE CAUSE OR A CONTRIBUTING FACTOR. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [103 empty] | OTHER OUTSIDE FORCE DAMAGE | [9 empty] | LOG TRUCK RAN OFF ROAD, TURNED OVER AND LOGS CAME OFF OF TRAILOR AND DAMAGED M&R STATION | [251 empty] | JOHNNY L. CAVITT | DOT COMPLIANCE MANAGER | johnny.cavitt@centerpointenergy.com | 318-429-3606 | 318-429-3927 |  |  |  | JOHNNY L. CAVITT | DOT COMPLIANCE MANAGER | 318-429-3606 | johnny.cavitt@centerpointenergy.com | EVEN THOUGH THIS EVENT DID NOT MEET THE CRITERIA OF THE DEFINITION OF AN INCIDENT IN §191.3 PARAGRAPHS (1)(I) OR (1)(II), IT WAS REPORTED BECAUSE IT WAS CONSIDERED SIGNIFICANT IN THE JUDGMENT OF THE OPERATOR SINCE EMERGENCY RESPONDERSL CLOSED LA HIGHWAY ALT 2, AND THURMAN SCHOOL ROAD.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100081 | 15103 | 2010-10-28 08:51 | ORIGINAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION LP (SPECTRA ENERGY CORP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2010-09-29 14:30 | 2010 |  |  | 28.4367 | -93.19 | 955523 | 2010-09-29 15:00 |  | NATURAL GAS |  | 400 | 11995 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-09-29 14:30 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-09-29 14:30 | 2010-09-29 14:30 | OFFSHORE | [28 empty] | 180 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST CAMERON | 513 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 20 |  | 0.406 | 52000 | API-5L X-52 | SEAMLESS |  | U.S.STEEL | OTHER | CONCRETE AND SOMASTIC | [27 empty] | 1975 | 1975 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 52 |  | NO | NO | NO |  | 0 | 0 | 47980 | 57259.8565786739 | 1600 | 986.407766990291 | 600000 | 716046.559966743 | 0 | 0 | 0 | 0 |  |  | 649580 | 355990.704023075 | 774292.824312407 | [8 empty] | 960 |  | 1440 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 179520 | NO | [5 empty] | YES | NO PLATFORM FROM WHICH TO LAUNCH AND RECEIVE TOOLS. | YES |  |  |  |  | YES | NO PLATFORMS FROM WHICH TO LAUNCH/RECEIV | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | THIRD PARTY (PLATFORM OPERATOR) OBSERVATION |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS TOO SMALL TO BE IDENTIFIED BY CONTROL ROOM PERSONNEL. A REVIEW OF OPERATING RECORDS FOUND ABNORMAL OPERATING CONDITIONS DID NOT CAUSE OR CONTRIBUTE TO THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DWAYNE TESCHENDORF | PRINCIPAL ENGINEER | deteschendorf@spectraenergy.com | 713-627-5573 | 713-386-4468 |  |  |  | RICK KIVELA | DIRECTOR OF OPERATIONAL COMPLIANCE | 713-627-6388 | rwkivela@spectraenergy.com | INDICATIONS OF BUBBLES ON THE WATER SURFACE IN WEST CAMERON 513 WERE REPORTED BY A PLATFORM OPERATOR AT 2:30 PM ON SEPTEMBER 29, 2010. UPON INVETIGATION IT WAS DETERMINED THE LEAK WAS CAUSED BY A PINHOLE LEAK RESULTING FOM INTERNAL CORROSION. A LEAK CLAMP WAS INSTALLED AS A PERMANENT REPAIR.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100082 | 15854 | 2010-10-28 15:11 | SUPPLEMENTAL FINAL | 19570 | WILLIAMS GAS PIPELINE - TRANSCO | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2010-10-19 15:45 | 2010 |  |  | 29.4884 | -90.9775 | 957444 | 2010-10-19 16:40 |  | NATURAL GAS |  | 10 | 4541 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-10-19 16:30 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-10-19 15:45 | 2010-10-19 15:47 | ONSHORE | LA | 70360 | HOUMA | TERREBONNE | MILEPOST | 111.579 | 20" SELA GATHERING LINE | SELA-A | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | UNDER WATER - MARSH ENVIRONMENT | 18 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 20 |  | 0.312 | 52000 | API 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | YOUNGSTOWN | ASPHALT | [28 empty] | 1959 | 1958 | CARBON STEEL |  | LEAK |  |  | OTHER | LONGITUDINAL TEAR/CRACK .437" | [5 empty] | CLASS 1 LOCATION | NO |  | 428 |  | NO | NO | NO |  | 50000 | 59670.5466638952 | 190000 | 226748.077322802 | 1 | 0.616504854368932 | 350000 | 417693.826647267 | 5000 | 5967.05466638952 | 0 | 0 |  |  | 595001 | 325945.868840555 | 710080.121805208 | [8 empty] | 810 |  | 1170 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 54542 | NO | [5 empty] | YES | PIG TRAPS ON EACH END OF SEGMENT WILL NOT ACCOMODATE A SMART PIG | YES |  |  |  |  | YES | PIG TRAPS | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | LANDOWNER REPORT |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PRESSURE DROP DUE TO THE MINIMAL LEAK COULD NOT BE DETECTED. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | YES | YES | YES | MPI, TOFD, PAUT, ZERO DEGREE ULTRASONIC | [11 empty] | YES | ANOMALLY DURING THE MANUFACTURING PROCESS | [7 empty] | YES | [62 empty] | NO | [63 empty] | YES | 1995 | 1182 | NO | [13 empty] | NO | [63 empty] | EDGAR RODRIGUEZ | PIPELINE SAFETY SPECIALIST II | edgar.x.rodriguez@williams.com | 713-215-2846 | 713-215-2222 |  |  |  | MARIE SOTAK | PIPELINE SAFETY MANAGER | 713-215-2111 | marie.sotak@williams.com | PIPE WAS EXCAVATED AND EXAMINED ON NOVEMBER 7TH AND 8TH OF 2011. A LACK OF FUSION MANUFACTURING ANOMALY WAS LOCATED IN THE CENTER OF THE ERW LONG SEAM. THE LENGTH OF THE ANOMALY WAS FOUND TO BE 0.45 INCHES. A 24" PRESSURE CONTAINING TYPE "B" STEEL SLEEVE, CENTERED AT THE ANOMALY LOCATION WAS INSTALLED AS A PERMANENT REPAIR.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100083 | 15106 | 2010-10-29 15:24 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2010-10-02 13:15 | 2010 |  |  | 36.723 | -121.7114 | 955875 | 2010-10-02 17:05 |  | NATURAL GAS |  | 12000 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-10-02 18:55 | 2010-10-03 05:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-10-02 13:35 | 2010-10-02 13:50 | ONSHORE | CA | 93901 | SALINAS | MONTEREY | MILEPOST | MP 5.61 | LINE 301B |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 29 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 |  | 0.281 | 35000 | GR. B SEAMLESS | SEAMLESS |  |  | COAL TAR | [28 empty] | 1952 |  | CARBON STEEL |  | MECHANICAL PUNCTURE | 2.5 | 5 | [7 empty] | CLASS 1 LOCATION | NO |  | 167 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 42892 | 26443.1262135922 | 47000 | 56090.3138640615 | 620 | 739.914778632301 | 0 | 0 |  |  | 90512 | 53501.3641607454 | 83273.3548562861 | [8 empty] | 402 |  | 408 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 21650 | NO |  | YES | [5 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA DETECTED PRESSURE DROP AMD CONTROL ROOM PERSONNEL NOTIFIED LOCAL PERSONNEL. LOCAL PERSONNEL BECAME AWARE OF INCIDENT BY MONITORING POLICE SCANNER PRIOR TO RECEIVING CALL FROM CONTROL ROOM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  | YES | PRIVATE EASEMENT | YES | [6 empty] | FARMER | FARM EQUIPMENT | AGRICULTURE | NO |  |  | DATA NOT COLLECTED | NO | YES | YES | 10 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | LAWRENCE BERG | SENIOR GAS ENGINEER | lmb5@pge.com | 925-974-4084 | 925-974-4220 |  |  |  | GLEN CARTER | SENIOR DIRECTOR | 925-974-4231 | gecj@pge.com | AT APPROXIMATELY 13:15 HOURS ON 10/2/10 A FARMER RIPPING HIS FIELD STRUCK LINE 301B, A 12-INCH STEEL GAS TRANSMISSION PIPELINE, WHICH RELEASED GAS TO THE ATMOSPHERE. THE FARMER DID NOT CALL UNDERGROUND SERVICE ALERT (USA) PRIOR TO STARTING THE FIELD RIPPING, AND THEREFORE DID NOT HAVE A VALID USA TICKET. THE LOCATION OF THE GAS INCIDENT IS APPROXIMATELY ONE MILE EAST OF COOPER ROAD AND HIGHWAY 183. PG&E ARRIVED ON SCENE AT 13:50 HOURS AFTER HEARING A 911 CALL ON A SCANNER ABOUT THIS INCIDENT. THE SALINAS FIRE DEPARTMENT ARRIVED SHORTLY THEREAFTER. PG&E CREWS CLOSED VALVES AT TWO LOCATIONS AT APPROXIMATELY 18:55 HOURS AND THE PIPE WENT FLAT AND GAS FLOW STOPPED AT 19:40 HOURS. THE GAS CREW REPLACED A THREE-FOOT SECTION OF THE DAMAGED PIPE. THIS SECTION OF LINE 301B WAS REPRESSURIZED AND RETURNED TO SERVICE AT 05:15 HOURS ON 10/03/10. THERE WERE NO FATALITIES OR INJURIES AND NO MAJOR MEDIA PRESENT. SIX CUSTOMERS LOST SERVICE LOST SERVICE AS A RESULT OF THIS INCIDENT. THIS INCIDENT IS REPORTABLE TO THE CPUC AND DOT DUE TOTAL COSTS, INCLUDING THE LOSS OF GAS, EXCEED $50,000.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100084 | 15930 | 2010-11-01 17:13 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | TX | 77002 | 2010-10-11 16:00 | 2010 |  |  | 28.7613 | -91.4032 | 956652 | 2010-10-11 16:00 |  | NATURAL GAS |  | 1000 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | ONE PRODUCER ON THE SYSTEM WAS NOTIFIED | [6 empty] | NO |  |  |  |  | NO | [9 empty] | OFFSHORE | [28 empty] | 150 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EUGENE ISLAND | 188 | PLATFORM | INTERSTATE | OFFSHORE PLATFORM, INCLUDING PLATFORM-MOUNTED EQUIPMENT AND PIPING | PIPE | PIPE BODY | 12 |  | 0.375 | 52000 | API | OTHER | UNKNOWN | UNKNOWN | OTHER | UNKNOWN | [27 empty] | 1968 | 1968 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 312 |  | NO | NO | NO |  | 0 | 0 | 10000 | 11934.109332779 | 40000 | 24660.1941747573 | 90000 | 107406.983995011 | 40000 | 47736.4373311162 | 0 | 0 |  |  | 180000 | 102259.33826136 | 191737.724833664 | [8 empty] | 900 |  | 1300 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS EVENT WAS NOT RELATED TO ANY CONTROLLER ASSISTED OPERATIONS. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  |  | YES | [7 empty] | YES |  |  |  | NO | [11 empty] | YES | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | LOUIS SALINAS | COMPLIANCE ENGINEER | louis_salinas@transcanada.com | 832-320-5305 | 832-320-6305 |  |  |  | LOUIS SALINAS |  | 832-320-5305 | No Email Address | AFTER EXAMINING A PIPE CLAMP, OPERATIONS PERSONNEL OBSERVED A SMALL AMOUNT OF CONDENSATE ESCAPING FROM A SECTION OF 12-INCH PIPE THAT CONTAINED SOME EXTERNAL CORROSION. THE PIPELINE IS A RECYCLE LINE USED IN OPERATIONS TO ASSIST WITH THE TRANSFER OF GAS BETWEEN SEVERAL LINES ON THE PLATFORM. THE PIPELINE WAS SUBSEQUENTLY ISOLATED AND BLOWN DOWN. A SEGMENT OF PIPE WAS REPLACED ON OCTOBER 16, 2010 TO COMPLETE THE REPAIR PROCESS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100085 | 15259 | 2010-11-03 12:49 | SUPPLEMENTAL FINAL | 32513 | AMEREN ILLINOIS COMPANY | 2125 EAST STATE ROUTE 104 | PAWNEE | IL | 62558 | 2010-10-02 14:59 | 2010 |  |  | 39.5606 | -90.6526 | 955867 | 2010-10-02 16:58 |  | NATURAL GAS |  | 48299 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-10-03 06:00 | 2010-10-03 11:20 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 2 | 2010-10-02 14:59 | 2010-10-02 15:38 | ONSHORE | IL | 62352 | MILTON | PIKE |  |  | MILTON TO MACOMB | 6 MC 22210-1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 24 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 |  | 0.188 | 35000 | GRADE B | LONGITUDINAL ERW - LOW FREQUENCY |  | REPUBLIC STEEL | COAL TAR | [28 empty] | 1966 | 1966 | CARBON STEEL |  | MECHANICAL PUNCTURE | 5 | 4 | [7 empty] | CLASS 1 LOCATION | NO |  | 131 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 317293 | 195612.674757282 | 6431 | 7674.82571191021 | 19294 | 23025.6705466639 | 0 | 0 |  |  | 343018 | 216892.879942742 | 226313.171015856 | [8 empty] | 385 |  | 400 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 3000 | NO |  | YES | [5 empty] | YES |  |  | YES |  |  |  | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT CAUSE - 3RD PARTY DAMAGE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | TRENCHER | DRAINAGE | NO |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | YES | 4 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | JEROME S THEMIG | MANAGER GAS COMPLIANCE | jthemig@ameren.com | 217 625 6804 |  |  |  |  | JEROME S THEMIG | MANAGER GAS COMPLIANCE | 217 625 6804 | jthemig@ameren.com | ON SATURDAY, OCTOBER 2ND, 2010, AMEREN ILLINOIS RECEIVED A CALL AT 14:59 FROM AN EMERGENCY RESPONDER SAYING THERE WAS A TRANSMISSION LINE HIT NEAR MILTON, ILLINOIS. AT 15:02 DISPATCH CONTACTED A QUALIFIED EMPLOYEE WHO ARRIVED ON THE SCENE AT 15:38. GAS SUPERVISION ARRIVED ON THE SCENE AT 16:15 TO ASSESS THE DAMAGE AND IDENTIFY APPROPRIATE METHODS TO CONTROL THE RELEASE OF GAS. THE METHOD SELECTED TO CONTROL THE RELEASE OF GAS WAS TO UTILIZE A DOWNSTREAM VALVE AND A STOPPER FITTING TO MINIMIZE CUSTOMER IMPACT. ADDITIONAL EQUIPMENT AND QUALIFIED EMPLOYEES WERE DISPATCHED TO THE SCENE TO INSTALL THE EIGHT INCH FITTING AND STOPPER. AT APPROXIMATELY 6:00 A.M. ON SUNDAY, OCTOBER 3, 2010, THE STOPPER WAS INSTALLED AND THE DOWNSTREAM VALVE CLOSED AT THE MILTON STATION TO ISOLATE A 3,000' SECTION OF MAIN. REPAIRS WERE STARTED SHORTLY AFTER 6:00 ONCE THE TRANSMISSION PIPELINE WAS BLOWN DOWN AND IT WAS SAFE TO APPROACH THE HIT LOCATION. REPAIRS TO THE TRANSMISSION PIPELINE WERE COMPLETED AT 10:30 AND THE STOPPER REMOVED AT APPROXIMATELY 11:00. THE APPARENT CAUSE OF THE INCIDENT WAS FAILURE OF THE EXCAVATOR TO CONTACT THE ONE-CALL-SYSTEM FOR A LOCATE REQUEST. THE EXCAVATOR WAS AWARE OF THE ILLINOIS DAMAGE PREVENTION LAWS AND THE REQUIREMENT TO CALL IN A LOCATE REQUEST PRIOR TO EXCAVATING. PIPELINE MARKERS WERE VISIBLE AT BOTH ENDS OF THE FIELD AND A CALL TO 811 WOULD HAVE REDUCED THE RISK OF THIS TRANSMISSION PIPELINE DAMAGE. ESTIMATE VOLUME AND COST OF GAS RELEASED UNINTENTIONALLY UPDATED IN SUPPLEMENTAL REPORT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100086 | 16359 | 2010-11-09 08:02 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION LP (SPECTRA ENERGY CORP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2010-10-12 09:30 | 2010 |  |  | 36.8305 | -85.6678 | 956712 | 2010-10-12 10:30 |  | NATURAL GAS |  | 1836 | 30040 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-10-12 10:46 | 2010-10-15 13:35 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-10-12 09:30 | 2010-10-12 09:30 | ONSHORE | KY | 42167 | TOMPKINSVILLE | MONROE | MILEPOST | 351.75 | TOMPKINSVILLE COMPRESSOR STATION |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 1 |  | 0.179 | 35000 | API 5L | SEAMLESS |  | WHEATLIT | PAINT | [28 empty] | 1954 | 1954 | CARBON STEEL |  | OTHER | [8 empty] | VEHICLE STRUCK PIPELINE CAUSING LEAK | CLASS 1 LOCATION | NO |  | 29 |  | NO | NO | NO |  | 0 | 0 | 120160 | 143400.257742673 | 7344 | 4527.61165048544 | 3500 | 4176.93826647267 | 0 | 0 | 0 | 0 |  |  | 131004 | 72435.8076455049 | 152104.807659631 | [8 empty] | 806 |  | 1000 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PERSONNEL AT THE FIELD SITE WERE RESPONSIBLE FOR THE EVENT AND REPORTED ITS OCCURRENCE. | [12 empty] | NO |  |  | YES | 1 | 0 | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OPERATOR'S CONTRACTOR | [260 empty] | DWAYNE TESCHENDORF | PRINCIPAL ENGINEER | deteschendorf@spectraenergy.com | 713-627-5573 | 713-386-4468 |  |  |  | RICK KIVELA | DIRECTOR OF OPERATIONAL COMPLIANCE | 713-627-6388 | rwkivela@spectraenergy.com | A CONTRACTOR EMPLOYEE DROVE A COMPANY VEHICLE INTO 1-INCH DIAMETER ESD PIPING WHICH SUBSEQUENTLY LEAKED NATURAL GAS FROM THE DAMAGE. THE COMPANY HAD TO BLOW DOWN 19 MILES OF 30-INCH DIAMETER PIPE TO STOP THE LEAK AND COMPLETE THE PIPE REPLACEMENT.
2021-02-26 10:37 | YES | YES | GT (Gas Transmission) | 20100087 | 15904 | 2010-11-09 10:01 | SUPPLEMENTAL | 32113 | CROSSTEX NORTH TEXAS PIPELINE, L.P. | 1722 ROUTH ST, SUITE 1300 | DALLAS | TX | 75201 | 2010-05-25 10:45 | 2010 |  |  | 33.2739 | -95.415 | 951587 | 2010-05-25 15:20 |  | NATURAL GAS |  | 1 |  |  | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 |  | NO | COMPRESSOR UNIT #4 WAS SHUT IN | [6 empty] | YES |  |  |  |  | NO | [6 empty] | 0 | 2010-05-25 10:45 | 2010-05-25 10:45 | ONSHORE | TX | 75415 | BEN FRANKLIN | DELTA |  |  | COOPER COMPRESSOR | UNIT #4 | NO | OPERATOR-CONTROLLED PROPERTY | TRANSITION AREA | OTHER | 1" NIPPLE ON FUEL LINE |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | 1" NIPPLE ON FUEL LINE | 2007 |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 595 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 2386.82186655581 | 5418 | 6465.90043649969 | 0 | 0 |  |  | 7418 | 4063.6331324049 | 8852.7223030555 | [8 empty] | 1000 |  | 1290 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CROSSTEX EMPLOYEES ON SITE | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | 1" NIPPLE ON FUEL LINE TO UNIT #4 CRACKED | YES | [177 empty] | WILLIAM L. WORLEY | DOT COMPLIANCE MANAGER | bill.worley@crosstexenergy.com | 2149539500 | 2149539501 |  |  |  | WILLIAM L. WORLEY | DOT COMPLIANCE MANAGER | 2149539500 | bill.worley@crosstexenergy.com
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20100088 | 15114 | 2010-11-11 10:24 | ORIGINAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 4720 PIEDMONT ROW DR. | CHARLOTTE | NC | 28210 | 2010-10-16 22:45 | 2010 |  |  | 36.2298 | -75.8833 | 957194 | 2010-10-17 02:48 |  | NATURAL GAS |  | 1082 | 174 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-10-17 02:30 | 2010-10-17 11:33 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 60 | 2010-10-16 22:45 | 2010-10-17 | ONSHORE | NC | 27965 | POPLAR BRANCH | CURRITUCK | MILEPOST | MLV 17 | E1 | MLV 17 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | INSULATING GASKET & FLANGE | 2005 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | INSULATING GASKET | OTHER | [8 empty] | ARCING FROM FALLEN POWER LINE | CLASS 3 LOCATION | NO |  | 145 |  | NO | NO | NO |  | 0 | 0 | 816 | 973.82332155477 | 5046 | 3110.88349514563 | 52726 | 62923.7848680108 | 1978 | 2360.5668260237 | 0 | 0 |  |  | 60566 | 33639.4448502925 | 69369.0585107349 | [8 empty] | 125 |  | 1000 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 84480 | YES | [7 empty] | YES |  | YES | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE NATURE OF THE INCIDENT - CAUSED BY OUTSIDE FORCES | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | [103 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [261 empty] | FARRIS BERRY | MANAGER - OPERATIONS PERFORMANCE | farris.berry@piedmontng.com | 704-731-4618 | 704-731-4098 |  |  |  | PINKNEY BYNUM | DIRECTOR - OPERATIONS COMPLIANCE AND PERFORMANCE | 704-731-4399 | pinkney.bynum@piedmontng.com | PIEDMONT NATURAL GAS (PNG) WAS NOTIFIED OF THE INCIDENT AT 11:20 P.M. ON SATURDAY, OCTOBER 16. THE PNG FIRST RESPONDER ARRIVED AT APPROXIMATELY 12:00 A.M. ON SUNDAY, OCTOBER 17, AND FOUND THE ABOVE GROUND MAIN LINE VALVE ASSEMBLY ON FIRE. PNG ISOLATED THE LEAK BY CLOSING MAIN LINE VALVES #16 AND #18 AT APPROXIMATELY 2:30 A.M. THE ISOLATED SECTION WAS PURGED AT 3:45 A.M. TO EXTINGUISH THE FIRE. PNG BELIEVES THE FIRE WAS CAUSED BY A FALLEN ELECTRICAL LINE SEVERAL MILES AWAY WHERE THE HIGH VOLTAGE TO GROUND CAUSED A SHORT AT THE INSULATING GASKETS LOCATED AT THE MAIN LINE VALVE ASSEMBLY, CAUSING THE FIRE. A NEW GASKET WAS INSTALLED ON THE ASSEMBLY AND PRESSURE (60 PSIG) WAS PLACED BACK ONTO THE PIPELINE AT APPROXIMATELY 10:30 A.M. THE PIPELINE IS OPERATED AT LOW PRESSURE IN ORDER TO MAINTAIN ODORANT FLOW. PNG LOST A TOTAL OF 45 CUSTOMERS WHEN ISOLATING THE MAIN LINE VALVE. ALL RE-LIGHTS WERE COMPLETED ON OCTOBER 18. PNG IS REPLACING THE ENTIRE MAINLINE VALVE FACILITY.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20100089 | 15115 | 2010-11-12 10:50 | ORIGINAL FINAL | 21349 | VIRGINIA NATURAL GAS | 544 S. INDEPENDSNCE BLVD | VIRGINIA BEACH | VA | 23452 | 2010-10-12 16:00 | 2010 |  |  | 37.6415 | -77.4204 | 956859 | 2010-10-13 12:45 |  | NATURAL GAS |  | 100 | 6923 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-10-13 12:00 | 2010-10-13 23:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-10-12 16:00 | 2010-10-12 16:30 | ONSHORE | VA | 23116-2014 | MECHANICSVILLE |  | MILEPOST | MLV-180 | VNG JOINT-USE PIPELINE | RICHMOND TAP VALVE | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | DRAIN LINES | [38 empty] | 1992 |  | CARBON STEEL |  | LEAK |  |  | OTHER | VEHICLE DAMAGE - THREADED CONN | [5 empty] | CLASS 3 LOCATION | YES | METHOD1 | 586 |  | NO | NO | NO |  | 0 | 0 | 25650 | 30610.9904385783 | 370 | 228.106796116505 | 50700 | 60505.9343171898 | 2300 | 2744.84514653918 | 0 | 0 |  |  | 79020 | 43321.5177731184 | 94089.8766984237 | [8 empty] | 950 |  | 1250 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | REMOTELY CONTROLLED | 41206 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE BUSH HOG DAMAGE TO THE PIPELINE CAUSED A FUZZ LEAK AT THE THREADED CONNECTION, WHICH CANNOT BE DETECTED BY THE SCADA SYSTEM. THEREFORE, GAS CONTROL WAS NOT INVOLVED IN THE INCIDENT DETECTION. HOWEVER, GAS CONTROL DID PROVIDE SUPPORT IN THE REPAIR EFFORT, BY MANAGING AND REDUCING THE PIPELINE PRESSURE, AND ISOLATING THE DAMAGED SECTION OF PIPELINE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OPERATOR'S CONTRACTOR | [260 empty] | BILL ROBINSON | STAFF ENGINEER REGULATORY COMPLIANCE | brobinso@aglresources.com | 757-616-7530 | 757-616-7517 |  |  |  | ROBERT S. DUVALL | VICE PRESIDENT AND GENERAL MANAGER VIRGINIA OPS | 757-616-7503 | rduvall@aglresources.com | A VIRGINIA NATURAL GAS (VNG) MOWING CONTRACTOR DAMAGED AN ABOVE GROUND 1/2" BLEED VALVE WITH HIS BUSH HOG EQUIPMENT WHILE MOWING THE VNG TRANSMISSION RIGHT-OF-WAY (ROW). THE 1/2" BLEED VALVE EXTENDED FROM AN UNDERGROUND 8" TAP VALVE, AND THE BUSH HOG BENT THE 1/2" PIPE AND CAUSED A FUZZ LEAK AT THE VALVE THREADED CONNECTION AT THE TOP OF THE PIPE. AT THE TIME OF THE DAMAGE, IT WAS UNCLEAR IF THE TAP VALVE HAD BEEN DAMAGED UNDERGROUND; THEREFORE, THE PIPELINE HAD TO BE COMPLETELY BLOWN-DOWN TO EXCAVATE SAFELY AROUND THE TAP VALVE. APPROXIMATELY 7-MILES OF 24" TRANSMISSION PIPELINE WAS BLOWN-DOWN FOR THIS REPAIR OPERATION. THE TAP VALVE WAS EXCAVATED AND FOUND TO BE UNDAMAGED BY THE VEHICLE IMPACT. THE 1/2" PIPE AND BLEED VALVE WERE REPLACED, AND THE PIPELINE WAS BROUGHT BACK INTO SERVICE. THE COMPANY'S ABOVE GROUND APPURTENANCES WERE PROTECTED ON TWO SIDES BY AN "L" SHAPED PROTECTIVE BARRIER THAT WAS LOCATED BETWEEN THE VALVE AND THE NEARBY ROADWAYS (APPROXIMATELY 75' FROM CHAMBERLAYNE ROAD AND 40' FROM RICHFOOD ROAD). IT IS ALSO NOTED THAT VIRGINIA DEPARTMENT OF TRANSPORTATION (VDOT) APPROVED GUARDRAILS EXIST ALONG THE ADJACENT ROADWAYS TO KEEP CARS FROM ACCIDENTLY ENTERING THE ROW NEAR THE VALVE SITE. THE BUSH HOG HIT THE PIPE FROM THE OPEN-END OF THE "L" SHAPED PROTECTIVE STRUCTURE. THIS ABOVE GROUND EQUIPMENT HAS BEEN IN PLACE SINCE 1992, AND HAS NEVER HAD AN ISSUE WITH VEHICLE PROTECTION OR ROW MOWING. THE MOWING CONTRACTOR IS REQUIRED TO USE A HAND-HELD WEED EATER WHEN WORKING IN CLOSE PROXIMITY TO ANY ABOVE GROUND EQUIPMENT ON THE VNG ROW. VIRGINIA NATURAL GAS WILL INSTALL ADDITIONAL PROTECTIVE BARRIERS AROUND THIS VALVE SITE TO ELIMINATE ANY FUTURE ACCIDENTAL DAMAGE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100090 | 16118 | 2010-11-12 14:03 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2010-10-14 15:15 | 2010 |  |  | 30.982 | -89.2197 | 957012 | 2010-10-14 16:47 |  | NATURAL GAS |  | 24320 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-10-14 18:15 | 2010-10-15 11:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 7 | 2010-10-14 15:15 | 2010-10-14 16:55 | ONSHORE | MS | 39425 | BROOKLIN | FORREST | MILEPOST | 23.89 | BAXTERVILLE 20" | INDEX 311 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 20 |  | 0.25 | 46000 | API-5L | LONGITUDINAL ERW - LOW FREQUENCY |  | YOUNGSTOWN | COAL TAR | [28 empty] | 1949 | 1949 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 120 | 20 |  | CLASS 1 LOCATION | NO |  | 323 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 95071 | 58611.7330097087 | 79929 | 95388.1424859697 | 5000 | 5967.05466638952 | 0 | 0 |  |  | 180000 | 107290.154919383 | 159966.930162068 | [8 empty] | 546 |  | 550 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 16918 | NO |  | YES | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PIPELINE WAS OPERATING AT 546 POUNDS, WHICH WAS IN THE NORMAL OPERATING RANGE. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) |  | YES | [13 empty] | YES | POOR ERW WELD BOND LINE STRENGTH, INCLUDING THE PRESENCE OF ELONGATED INCLUSIONS | [13 empty] | YES | POOR ERW WELD BOND LINE STRENGTH, INCLUDING THE PRESENCE OF ELONGATED INCLUSIONS AND OTHER IMPERFECTIONS IN THE SEAM. | [55 empty] | YES | YES | YES |  | YES | YES |  |  | 2011 | [11 empty] | 2011 | [19 empty] | 2011 | [9 empty] | 2011 | [13 empty] | YES | 2011 | 717 | NO | [13 empty] | NO | [63 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 2706886357 |  |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 2706886361 | jeff.mcmaine@bwpmlp.com | GULF SOUTH WAS NOTIFIED OF A POSSIBLE RUPTURE ON A PIPELINE LOCATED IN FORREST COUNTY, MS. GULF SOUTH EMPLOYEES INVESTIGATED AND DETERMINED THAT THE INDEX 311 BAXTERVILLE 20" HAD FAILED AND WAS BLOWING GAS TO ATMOSPHERE. COMPANY EMPLOYEES CLOSED BLOCK VALVES ON EACH SIDE OF THE INCIDENT LOCATION AND THE PIPELINE BLEW DOWN TO ZERO. COMPANY EMPLOYEES REMOVED THE FAILED PIPE AND SENT IT TO BE TESTED TO DETERMINE THE CAUSE OF THE FAILURE. THE PIPELINE WAS REPAIRED BY INSTALLING NEW PIPE, PURGED, AND RETURNED TO SERVCE. THE PIPELINE IS PRESENTLY BEING OPERATED AT LESS THAN 80% OF THE PRESSURE AT THE TIME OF THE INCIDENT. STRESS ENGINEERING EXAMINED THE FAILED PIPE AND DETERMINED THE INCIDENT WAS DUE TO A LONGITUDINAL SEAM FAILURE. UPDATE: BAXTERVILLE 20",INDEX 311 FROM MP 0 TO MP 25 HAS BEEN HYDROSTATICALLY TESTED SUCCESSFULLY TO AT LEAST 1.25 TIMES OF MAOP. THE PIPELINE FROM MP 0 TO MP 25 WAS RETURNED TO NORMAL SERVICE ON APRIL 23, 2012 WITH AN MAOP OF 550 PSIG. 9-16-13 CHANGED SEAM TYPE AT THE REQUEST OF BLAINE KEENER, PHMSA NATIONAL FIELD COORDINATOR
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100091 | 15874 | 2010-11-15 12:24 | SUPPLEMENTAL FINAL | 32414 | MARKWEST OKLAHOMA GAS COMPANY, LLC | 1515 ARAPAHOE ST TOWER 1, SUITE 1600 | DENVER | CO | 80202 | 2010-10-14 10:05 | 2010 |  |  | 34.2602 | -96.1778 | 957072 | 2010-10-15 11:00 |  | NATURAL GAS |  | 5812 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-10-14 10:05 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-10-14 10:05 | 2010-10-14 10:05 | ONSHORE | OK | 74525 |  | ATOKA | MILEPOST | MAIN LINE 5 | ARKOMA 2 COMPRESSOR STATION | ARKOMA 2 COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | FILTER/STRAINER/SEPARATOR | [38 empty] | 2009 |  | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | SEPERATOR (42" X 10') |  |  |  | CLASS 1 LOCATION | NO |  | 268 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 19790 | 12200.6310679612 | 120000 | 143209.311993349 | 0 | 0 | 0 | 0 |  |  | 139790 | 78385.8012651697 | 155409.94306131 | [8 empty] | 1400 |  | 1480 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT APPEARS THAT THE DISCHARGE HEADER RELIEF VALVE LIKELY FAILED IN THE OPEN POSITION SEEMLY DUE TO A FAILURE OF THE TUBING OF THE PILOT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [14 empty] | YES | [176 empty] | BRUCE L. GILLICK | DIRECTOR OF ENVIRONMENTAL HEALTH AND SAFETY | bgillick@markwest.com | 303-925-9228 | 303-825-0920 |  |  |  | JOHN MOLLENKOPF | CHIEF OPERATIONS OFFICER SVP | 303-925-9246 | jmollenkopf@markwest.com | SEE ATTACHMENT BELOW FOR NARRATIVE
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20100092 | 17075 | 2010-11-15 16:12 | SUPPLEMENTAL FINAL | 10035 | POSTROCK KPC PIPELINE, LLC | 210 PARK AVE, SUITE 2750 | OKLAHOMA CITY | OK | 73102 | 2010-11-10 10:15 | 2010 |  |  | 38.5054 | -95.4032 | 959522 | 2010-11-10 12:08 |  | NATURAL GAS |  | 2770 | 744.61 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-11-10 10:30 | 2010-12-09 16:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 2 | 2010-11-10 11:15 | 2010-11-10 13:30 | ONSHORE | KS | 66095 | WILLIAMSBURG | FRANKLIN | MILEPOST | MP 257 19+46 | P-50 | MASTERGAS TO OTTAWA | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 12 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 |  | 0.188 | 42000 | API 5LX | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | REPUBLIC | COAL TAR | [28 empty] | 1949 | 1949 | CARBON STEEL |  | MECHANICAL PUNCTURE | 2 | 3 | [7 empty] | CLASS 1 LOCATION | NO |  | 157 |  | NO | NO | NO |  | 0 | 0 | 2978 | 3553.9777593016 | 11080 | 6830.87378640777 | 2638 | 3148.21804198711 | 6000 | 7160.46559966743 | 0 | 0 |  |  | 22696 | 13445.2043974199 | 20693.5351873639 | [8 empty] | 498 |  | 695 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | MANUAL | 688512 | NO |  |  |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY NOTIFIED OPERATOR OF DAMAGE TO PIPELINE. CONTROL ROOM VERIFIED DAMAGE TO PIPELINE WITH PRESSURE MONITORING. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  | YES | PRIVATE LANDOWNER | [7 empty] | FARMER | FARM EQUIPMENT | AGRICULTURE | NO |  |  | UNKNOWN/OTHER | NO | NO | YES | 696 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER |  |  | THERE WAS NO NOTIFICATION MADE TO THE ONE CALL CENTER. | [262 empty] | ADAM COWART | CORPORATE COMPLIANCE MANAGER | acowart@mvpipelines.com | 620-886-0082 | 913-764-6021 |  |  |  | ADAM COWART | CORPORATE COMPLIANCE MANAGER | 620-886-0082 | acowart@mvpipelines.com | THIRD PARTY DAMAGE FROM FARMER CONDUCTING DEEP TILL ACTIVITIES IN FARM FIELD. PIPELINE BECAME SHALLOW DUE TO ERROSION ON FARM FIELD. PREVIOUS DEPTH OF COVER WAS 24". THE AMOUNT OF EROSION THAT OCCURRED AT THE POINT OF DAMAGE WAS 12".
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100093 | 16156 | 2010-11-17 11:05 | SUPPLEMENTAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2010-10-28 17:56 | 2010 |  |  | 32.4258 | -88.0403 | 958368 | 2010-10-28 19:37 |  | NATURAL GAS |  | 1380 | 3 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-10-28 18:52 | 2010-10-29 23:40 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2010-10-28 18:22 | 2010-10-28 18:22 | ONSHORE | AL | 35470 | LIVINGSTON | SUMTER | MILEPOST | 118.9 | OFF OF SOUTH MAIN PIPELINE | LIVINGSTON REGULATOR STATION | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1951 |  | CARBON STEEL |  | OTHER | [8 empty] | IGNITION OCCURRED INSIDE REGULATOR BUILDING WITH GAS IGNITING FROM AN INDETERMINATE SOURCE. | CLASS 1 LOCATION | NO |  | 42 |  | NO | NO | NO |  | 0 | 0 | 12 | 14.3209311993349 | 5175 | 3190.41262135922 | 200000 | 238682.186655581 | 30000 | 35802.3279983371 | 0 | 0 |  |  | 235187 | 129309.85431949 | 277689.248206477 | [8 empty] | 400 |  | 400 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS CONTROL HAD NO REMOTE MONITORING CAPABILITIES FOR THE REGULATOR STATION. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | THE LIVINGSTON REGULATOR STATION BUILDING WAS NOT DESIGNED WITH ANY TYPE OF VENTILATION SUCH AS A TURBINE VENT OR A RIDGE VENT. MONTHS PRIOR TO THE INCIDENT, BROKEN WINDOWS IN THE BUILDING WERE REPLACED, RESULTING IN A GREATER LACK OF VENTILATION DUE TO THE SUBSTANTIAL SEAL PRODUCED BY THE NEW WINDOWS. THE BUILDING CONTAINED CONTROL EQUIPMENT DESIGNED TO VENT GAS AS A PART OF NORMAL OPERATION. IT IS BELIEVED THAT THE VENTED GAS BUILT UP INSIDE THE BUILDING AND IGNITED FROM AN UNPROVEN SOURCE. | [147 empty] | MARTIN MULLER | COMPLIANCE ENGINEER | martin_muller@kindermorgan.com | 205-325-3863 | 205-325-3508 |  |  |  | REJI GEORGE | DIRECTOR COMPLIANCE - CODES AND STANDARDS | 713-420-5433 | reji_george@kindermorgan.com | A MEMBER OF THE GENERAL PUBLIC NOTIFIED SOUTHERN NATURAL GAS (SNG) COMPANY'S GAS CONTROL OF A LOUD BLOWING SOUND IN THE VICINITY OF SNG'S LIVINSTON (AL) REGULATOR STATION. UPON ARRIVAL AT THE SCENE, SNG OPERATIONS PERSONNEL FOUND THE REGULATOR STATION BUILDING AND PIPING ENGULFED IN FLAMES. SURROUNDING GRASS WAS ALSO BURNING. PERSONNEL CLOSED THE STATION'S TAP VALVES TO STOP FUEL FLOW TO THE FIRE. LOCAL VOLUNTEER FIREMEN ASSISTED THE COMPANY PERSONNEL IN EXTINGUISHING THE FIRE. TEMPORARY SERVICE WAS RESTORED TO THE TOWN OF LIVINGSTON. POST INCIDENT INVESTIGATION REVEALED THE MOST LIKELY CAUSE TO BE A CONCENTRATION OF NATURAL GAS, VENTED FROM CONTROL EQUIPMENT DESIGNED TO DO SO, INSIDE THE REGULATOR BUILDING DUE TO LACK OF VENTILATION. THE GAS IGNITED FROM AN UNKNOWN SOURCE ALTHOUGH POSSIBLE SOURCES COULD HAVE BEEN AN ELECTRICAL SHORT OR LIGHTNING.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100095 | 16950 | 2010-11-29 16:16 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2010-10-29 13:09 | 2010 |  |  | 28.8622 | -98.0819 | 958442 | 2010-10-29 14:20 |  | NATURAL GAS |  | 9736 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-10-29 13:50 | 2010-11-01 10:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-10-29 13:20 | 2010-10-29 13:40 | ONSHORE | TX | 78118 | KARNES CITY | KARNES | MILEPOST | 11.9 | FALL CITY TO FASHING | 9158 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 43 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.28 | 52000 | API5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1958 | 1958 | CARBON STEEL |  | MECHANICAL PUNCTURE | 3 | 3 | [7 empty] | CLASS 1 LOCATION | NO |  | 422 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 43812 | 27010.3106796117 | 100540 | 119985.535231761 | 0 | 0 | 0 | 0 |  |  | 144352 | 83079.3422436044 | 146995.845911372 | [8 empty] | 850 |  | 935 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 63360 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A THIRD PARTY LINE STRIKE THAT WAS IMEDIATELY BLOCKED IN AND HAD NO FIRE OR INJURY ASSOCIATED WITH THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [7 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 103004554 | TEXAS EXCAVATION SAFETY SYSTEMS, INC. | UTILITY OWNER | YES | NO | YES | 69 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | EXCAVATION PRACTICES NOT SUFFICIENT (OTHER) | [263 empty] | NEAL BURRELL | SR. PIPELINE COMPLIANCE SPECIALIST | wnburrell@eprod.com | 713-381-3536 |  |  |  |  | NEAL BURRELL | SR. PIPELINE COMPLIANCE SPECIALIST | 713-381-3536 | wnburrell@eprod.com | THIS WAS A THIRD PARTY LINE STRIKE. THE THIRD PARTY CONTRACTOR DID NOT ALLOW SUFFICIENT TIME (48 HOURS) REQUIRED BY THE STATE OF TEXAS FOR ENTERPRISE PRODUCTS TO MARK THE PIPELINE. PART D 7D, 7E, 7F, NAD 7G COST TOTALS ASSOCIATED WITH THESE SECTIONS HAVE NOT BEEN FULLY DETERMINED. THIS SECTION WILL HAVE TO BE UPDATED WHEN MORE INFORMATION IS GATHERED. PART G 3 15 LINE WAS PROPERLY MARKED ON INITIAL ONE CALL ON OCTOBER 12, 2010 (TICKET 1028529458). SECOND ONE CALL, THE CONTRACTOR HIT THE LINE BEFORE THE 48 HOURS EXPIRED AND DID NOT CONTACT ENTERPRISE PRODUCTS FOR CLEARANCE BEFORE PROCEEDING TO DIG. THE TECHNICIAN WAS NOT ON SITE WHEN THE LINE WAS HIT ON THE SECOND ONE CALL. SUPPLEMENTAL COMMENT: THE RAILROAD COMMISSION OF TEXAS CONDUCTED AN INVESTIGATION INTO THE 3RD PARTY LINE STIKE. THE RESULTS OF THE INVESTIGATION CONCLUDED THAT ENTERPRISE PRODUCT WAS NOT AT FAULT FOR THE LINE STRIKE. FINAL REPORT: COSTS HAVE BEEN UPDATED TO REFLECT TOTAL REPAIR COSTS. 12/14/2015 - UPDATED INCIDENT REPORT PER PHSMA REQUEST - COMPLETED PART C - ITEM 4 - ENTERED THE YEAR PIPE WAS INSTALLED. NB
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100096 | 15128 | 2010-12-02 14:49 | ORIGINAL | 31604 | EQT MIDSTREAM | 625 LIBERTY AVENUE, SUITE 1700 | PITTSBURGH | PA | 15222 | 2010-11-04 10:15 | 2010 |  |  | 40.2793 | -79.9169 | 958936 | 2010-11-04 11:17 |  | NATURAL GAS |  | 7885 | 47 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-11-04 10:30 | 2010-11-04 18:41 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-11-04 10:15 | 2010-11-04 10:15 | ONSHORE | PA | 15025 | JEFFERSON HILLS | ALLEGHENY | SURVEY STATION NO. | 31200 | H-129 |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | MECHANICAL COUPLING | 1966 |  | CARBON STEEL |  | OTHER | [8 empty] | PIPELINE DISENGAGED FROM MECHANICAL COUPLING | CLASS 3 LOCATION | NO |  | 163 |  | NO | NO | NO |  | 1000 | 1193.41093327791 | 180 | 214.813967990023 | 30350 | 18710.9223300971 | 90000 | 107406.983995011 | 0 | 0 | 0 | 0 |  |  | 121530 | 69347.5149552771 | 127526.131226376 | [8 empty] | 119 |  | 216 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL |  | 8250 | NO | [5 empty] | YES | LINE DOES NOT CONTAIN LAUNCHER/RECEIVER | YES |  | YES |  |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EQT MIDSTREAM OPERATIONS AND CONTRACTOR PERSONNEL WERE ON SITE TO COMPLETE A TIE IN. GAS CONTROL PERSONNEL WERE NOT ADJUSTING PRESSURES OR MAKING OPERATIONAL ADJUSTMENTS ON THE H-129 LINE AT THE TIME OF THE INCIDENT | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | MECHANICAL COUPLING | [6 empty] | YES | [175 empty] | JOE LOMBARDO | MANAGER COMPLIANCE | jlombardo@eqt.com | 412-395-3135 | 412-395-2128 |  |  |  | JOE LOMBARDO | MANAGER COMPLIANCE | 412-395-3135 | jlombardo@eqt.com
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20100097 | 15450 | 2010-12-06 16:55 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | TX | 77002 | 2010-11-11 09:30 | 2010 |  |  | 29.8631 | -93.0691 | 959610 | 2010-11-11 11:00 |  | NATURAL GAS |  | 1000 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | [7 empty] | NO |  |  |  |  | NO | [9 empty] | ONSHORE | LA | 70743 | GRAND CHENIER | CAMERON |  |  |  |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8.625 |  | 0.25 | 35000 | API | OTHER | UNKNOWN | REPUBLIC STEEL | COAL TAR | [28 empty] | 1956 | 1956 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 191 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 10000 | 6165.04854368932 | 55000 | 65637.6013302848 | 5000 | 5967.05466638952 | 0 | 0 |  |  | 70000 | 39260.0122830703 | 77769.7045403636 | [8 empty] | 775 |  | 1090 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 14000 | NO | [5 empty] | YES | PIPELINE WAS NOT DESIGNED TO BE PIGGABLE (PRE-1970). | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  | YES |  |  |  |  | YES |  |  |  | YES |  | YES |  |  |  | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | LOUIS SALINAS | COMPLIANCE ENGINEER | louis_salinas@transcanada.com | 832-320-5305 | 832-320-6305 |  |  |  | LOUIS SALINAS |  | 832-392-5209 | No Email Address | A SUSPECTED LEAK ON TRANSCANADA'S 8-IN LINE 708, CAMERON PARISH, LOUISIANA WAS REPORTED TO THE COMPANY BY SOME FISHERMEN ON NOVEMBER 11, 2010. THE LEAK WAS LOCATED IN THE MARSH AND WAS VERIFIED BY COMPANY PERSONNEL. THE LINE WAS ISOLATED AND BLOWN DOWN SLOWLY. A SUBSEQUENT INVESTIGATION REVEALED THAT INTERNAL CORROSION WAS THE MOST LIKELY CAUSE OF THE LEAK. AT THIS TIME, IT IS NOT ANTIDIPATED THAT THE LINE WILL BE NEEDED FOR SERVICE AND THEREFORE A REPAIR PLAN IS NOT IMMINENT. THEREFORE, A PLAN TO ABANDON THE LINE WILL BE DEVELOPED.
2021-02-26 10:37 | YES | YES | GT (Gas Transmission) | 20100098 | 15334 | 2010-12-07 19:30 | SUPPLEMENTAL FINAL | 22655 | WILLISTON BASIN INTERSTATE PIPELINE CO | 1250 WEST CENTURY AVENUE | BISMARCK | ND | 58503 | 2010-11-08 12:57 | 2010 |  |  | 48.5238 | -102.8768 | 959291 | 2010-11-08 14:24 |  | NATURAL GAS |  | 5230 | 0 | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | NO | [5 empty] | 0 |  | YES |  | 2010-11-08 14:05 | 2010-11-10 19:46 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-11-08 13:40 | 2010-11-08 14:10 | ONSHORE | ND | 58852 | TIOGA | MOUNTRAIL | SURVEY STATION NO. | 244+01 | WILLISTON TIOGA MINOT SYSTEM | TIOGA TO MCGREGOR SEGMENT | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 40 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8.625 |  | 0.188 | 42000 | API 5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | STUPP CORPORATION | COAL TAR | [28 empty] | 1961 | 1961 | CARBON STEEL |  | MECHANICAL PUNCTURE | 24 | 27.1 | [7 empty] | CLASS 1 LOCATION | NO |  | 164 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 19497 | 12019.9951456311 | 22099 | 26373.1882145084 | 1000 | 1193.41093327791 | 0 | 0 | THE $1,000 IS ESTIMATED TO INCLUDE EMPLOYEES WHO RESPONDED AT OFFICE ALSO. |  | 42596 | 25115.4711613555 | 39586.5942934174 | [8 empty] | 650 |  | 700 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 70190 | NO |  | YES | [5 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  | YES | CONTROL ROOM RESPONDED PROPERLY AND FATIGUE WAS NOT DETERMINED TO BE A CONCERN. | YES | YES | [7 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  | YES | PRIVATE LANDOWNER | [7 empty] | CONTRACTOR | TRENCHER | ELECTRIC | NO |  |  | UNKNOWN/OTHER | NO | NO | YES | 54 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | CRAIG WAGNER | PIPELINE INTEGRITY AND COMPLIANCE MANAGER | craig.wagner@wbip.com | 406-359-7216 | 406-359-7225 |  |  |  | CRAIG WAGNER | PIPELINE INTEGRITY AND COMPLIANCE MANAGER | 406-359-7216 | craig.wagner@wbip.com | AEVENIA ENERGY AND ELECTRICAL CONSTRUCTION WAS CONTRACTED BY MONTRAIL WILLIAMS ELECTRIC COOPERATIVE TO PLOW PRIMARY ELECTRICAL CABLES UNDERGROUND FROM AN OIL WELL LOCATION OWNED BY AMERADA HESS CORPORATION ACROSS A WHEAT FIELD TO A POWER POLE. NONE OF THE PARTIES HAD MADE A ONE-CALL NOTIFICATION PRIOR TO THE START OF THE PROJECT. WILLISTON BASIN THEREFORE HAD NOT HAD THE CHANCE TO LOCATE IT'S PIPELINE PRIOR TO THE START OF THIS EXCAVATION. MONTRAIL WILLIAMS HAD STAKED THE PROPOSED ROUTE WITH WHITE "MONTRAIL WILLIAMS ELECTRIC PROPOSED EXCAVATION" FLAGS FOR THE CONTRACTOR. THE CREW CONSISTED OF TWO DOZER OPERATORS AND ONE EMPLOYEE WHO WAS WALKING NEAR THE PLOW. THE PLOWING OPERATION STARTED AT THE OIL WELL LOCATION AND PROCEEDED WEST APPROXIMATELY 260 FEET WHEN IT STRUCK A WILLISTON BASIN INTERSTATE PIPELINE NATURAL GAS TRANSMISSION LINE. THE 8 INCH LINE WAS OPERATING AT APPROXIMATELY 650 PSIG AT THE TIME. THE LINE FAILED AFTER BEING STRUCK BY THE PLOW KILLING THE PERSON WHO WAS ON THE GROUND STANDING NEAR TO THE FAILURE POINT. THE TWO OPERATORS OF THE DOZERS JUMPED OFF OF THEIR EQUIPMENT AND RAN A DISTANCE FROM THE ESCAPING GAS. THE FORCE OF THE ESCAPING GAS BLEW THE PERSON ON THE GROUND A DISTANCE OF APPROXIMATELY 80 FEET KILLING HIM. THE GAS DID NOT IGNITE. WILLISTON BASIN WAS ABLE TO ISOLATE THE FAILED PIPELINE SECTION IN APPROXIMATELY 1 HOUR AND 8 MINUTES. THE REMAINING GAS IN THE ISOLATED SECTION SELF EVACUATED THROUGH THE FAILURE POINT. THE LOCATION WAS BLOWN DOWN AND CLEARED FOR GAS 35 MINUTES AFTER ISOLATION. TWO PIPELINE MARKER POSTS WERE CLEARLY VISIBLE FROM THE ACCESS ROAD INTO THE SITE. THE CLOSEST MARKER POST TO THE POINT OF FAILURE (MP 4.72) WAS WITHIN SIGHT AND WAS LOCATED APPROXIMATELY 517 FEET SOUTH OF THE POINT OF FAILURE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20100101 | 16106 | 2010-12-09 11:34 | SUPPLEMENTAL | 20044 | PRAXAIR, INC | 10 RIVERVIEW DR. | DANBURY | CT | 06810 | 2010-11-15 15:07 | 2010 |  |  | 29.5721 | -94.9418 | 959914 | 2010-11-15 16:30 |  | OTHER GAS | UNKNOWN | 1 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | [9 empty] | NO |  |  |  |  | NO | [9 empty] | OFFSHORE | [28 empty] | 7 | IN STATE WATERS | TX | GALVESTON BAY |  | HARRIS |  |  |  | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTRASTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | OTHER | [37 empty] | UNKNOWN |  |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | UNKNOWN | OTHER | [8 empty] | LEAK IS NOT IN A PRAXAIR PIPELINE, SO PRAXAIR DID NOT INVESTIGATE THE LEAK TO THE EXTENT NECESSARY TO ANSWER PART C QUESTIONS | CLASS 1 LOCATION | NO |  | 10 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20000 | 23868.2186655581 | 0 | 0 |  |  | 20000 | 10956.1421741842 | 23868.2186655581 | [8 empty] | 10 |  | 10 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 10 | NO | [5 empty] | YES | UNKNOWN - THIS IS NOT A PRAXAIR PIPELINE | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | AIR PATROL |  | CONTRACTOR WORKING FOR THE OPERATOR | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) | [11 empty] | YES | UNKNOWN - THIS IS NOT A PRAXAIR PIPELINE | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [146 empty] | JOHN MAITINO | PIPELINE REGULATORY COMPLIANCE MANAGER | john_maitino@praxair.com | 281-478-1944 | 281-478-1937 |  |  |  | JOHN MAITINO | PIPELINE REGULATORY COMPLIANCE MANAGER | 281-478-1944 | john_maitino@praxair.com | 11/15/2010 DURING A ROUTINE AERIAL SURVEY OF PRAXAIR'S PIPELINE IN THE GALVESTON BAY, THE SURVEY PILOT OBSERVED VIOLENT BUBBLING NEAR THE PIPELINE. HE RECORDED A GPS READING AND REPORTED IT TO PRAXAIR PERSONNEL. PRAXAIR PERSONNEL FILED AN INCIDENT REPORT WITH THE NRC. PRAXAIR'S CONTROL ROOM WAS NOTIFIED. THEY REPORTED NO EVIDENCE OF A LEAK FROM THEIR OPERATING INFORMATION. PRAXAIR PLOTTED THE GPS LOCATIONS OF THE APPARENT LEAK AND OF PRAXAIR'S ONLY PIPELINE IN THE VICINITY IN BOTH GOOGLE EARTH AND IN PRAXAIR'S GIS. BOTH PLOTS SHOWED THE LEAK TO BE ABOUT 1600 FEET FROM PRAXAIR'S PIPELINE. PRAXAIR PERSONNEL CONTACTED THE COAST GUARD AT ABOUT 16:00, THEN OTHER PIPELINE OPERATORS THEY WERE AWARE OF, INCLUDING DAVIS PETROLEUM (FRANCIS LEBEAUX), AND KINDER MORGAN. 11/16/2010 PRAXAIR PERSONNEL REPORTED THE LEAK TO FLORIDA GAS, WHO SAID THEY NO LONGER OPERATED ANY PIPELINES IN THE AREA, AND SUGGESTED CALLING ENERGY TRANSFER, WHO ALSO SAID THEY HAD NO PIPELINES IN THE AREA. DAVIS PETROLEUM REPORTED THAT THEIR PLATFORMS WERE BLOCKED IN AND PRESSURE WAS HOLDING. THEY ALSO REPORTED THAT THEIR GIS SHOWS AN ABANDONED GAS WELL NEAR THE GPS COORDINATES OF THE LEAK. PRAXAIR ALSO FILED A REPORT WITH THE TEXAS RAILROAD COMMISSION. THE COAST GUARD REPORTED THAT THERE WAS NO OIL SHEEN IN THE VICINITY AND THAT THEY HAD NO FURTHER PLANS TO OBSERVE THE SITE. PRAXAIR PERSONNEL TOOK A BOAT OUT TO THE LOCATION OF THE LEAK, BUT WERE UNABLE TO LOCATE IT DUE TO ROUGH WATER CONDITIONS. IN THE AFTERNOON, PRAXAIR PERSONNEL MADE ANOTHER FLIGHT OVER THE LEAK AREA WITH THE AERIAL SURVEYOR. THE LEAK WAS EASY TO FIND AND STILL PRESENT. 11/17/2010 PRAXAIR MADE A SECOND TRIP TO THE LEAK SITE WITH A LARGER BOAT, BUT COULD NOT LOCATE THE LEAK. AN AIRCRAFT WAS DISPATCHED TO GUIDE THE BOAT TO THE LEAK AREA. ON ARRIVAL, THE LEAK AND PRAXAIR'S PIPELINE WERE PRECISELY MARKED WITH BUOYS. THE DISTANCE BETWEEN THE BUOYS WAS MEASURED AT 1600 FEET. PRAXAIR'S PIPELINE IS UNDER THREE FEET OF COVER, AND THE WATER DEPTH IS ABOUT 7 - 8 FEET AT ITS CLOSEST POINT TO THE LEAK LOCATION. PRAXAIR'S CONTROL ROOM STAFF CONTINUE TO REPORT NO OPERATIONAL OBSERVATIONS THAT WOULD INDICATE A LEAK ON ITS PIPELINE NEAR THE LEAK. PRAXAIR PERSONNEL DO NOT BELIEVE THAT THE LEAK IS FROM THE PRAXAIR PIPELINE, AND CONSIDER THE MATTER CLOSED.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20100102 | 15898 | 2010-12-09 17:26 | SUPPLEMENTAL FINAL | 22175 | TARGA MIDSTREAM SERVICES, L.P. | 310 LOWRY HWY | LAKE ARTHUR | LA | 70549 | 2010-11-10 10:30 | 2010 |  |  | 29.1483 | -93.2904 | 959377 | 2010-11-10 11:22 |  | NATURAL GAS |  | 640 | 3667 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-11-10 14:30 | 2010-11-13 20:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-11-10 10:30 | 2010-11-11 12:00 | OFFSHORE | [28 empty] | 50 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST CAMERON | 118 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTRASTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12 |  | 0.312 | 52000 | API 5LX | SEAMLESS |  | UNKNOWN | EPOXY | [28 empty] | 1968 | 1968 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 298 |  | NO | NO | NO |  | 0 | 0 | 14668 | 17504.9515693203 | 2560 | 1578.25242718447 | 153515 | 183206.479422158 | 4622 | 5515.94533361048 | 0 | 0 |  |  | 175365 | 96300.0533751872 | 207805.628752273 | [8 empty] | 920 |  | 1300 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | MANUAL | 355597 | NO | YES |  |  | YES |  |  |  | NO | [6 empty] | OFFSHORE GATHERING | NO |  |  |  |  | OTHER | BOEMRE AGENT |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | NO | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | TIM HUFFER | MANAGER REGULATORY COMPLIANCE | thuffer@targaresources.com | 337-583-4642 | 337-583-4630 |  |  |  | TIM HUFFER | MANAGER REGULATORY COMPLIANCE | 337-583-4642 | thuffer@targaresources.com | ON 11/10/2010 AT 10:30 AM COMPANY RECIEVED NOTIFICATION OF GAS LEAK THAT COULD BE COMING FROM COMPANY PIPELINE IN WC188. INVESTIGATION DETERMINED LEAK FROM TARGA PIPELINE. PRODUCERS WERE NOTIFIED TO SHUT DOWN PRODUCTION AND DE-PRESSURING OF THE PIPELINE COMMENCED. CLAMP USED TO REPAIR PIPELINE, AND REPAIRS COMPLETED ON 11/12/2010.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100103 | 16030 | 2010-12-10 13:43 | SUPPLEMENTAL FINAL | 19730 | TRUNKLINE GAS CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2010-11-12 11:21 | 2010 |  |  | 32.3538 | -91.8379 | 959689 | 2010-11-12 12:56 |  | NATURAL GAS |  | 71664 | 556 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-11-12 11:21 | 2010-11-21 11:50 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-11-12 11:21 | 2010-11-12 11:21 | ONSHORE | LA | 71269 | ALTO | RICHLAND | SURVEY STATION NO. | 172+85 | 100-2; VS 63 | POLLOCK 100-2 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | HOT TAP EQUIPMENT | [38 empty] | 2010 |  | CARBON STEEL |  | OTHER | [8 empty] | FAILURE OF THE TAPPING MACHINE | CLASS 1 LOCATION | NO |  | 621 |  | NO | NO | NO |  | 0 | 0 | 2038 | 2432.17148202037 | 262666 | 161934.86407767 | 0 | 0 | 20208 | 24116.4481396799 | 0 | 0 |  |  | 284912 | 180071.743477562 | 188483.48369937 | [8 empty] | 700 |  | 900 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 54136 | NO |  | YES | [5 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT OCCURED DURING A HOT TAPPING OPERATION & A PERSON AT THE SITE MADE THE NOTIFICATION | [12 empty] | YES | 1 | 0 | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | FAILURE OF THE TAPPING MACHINE DURING THE TAPPING OPERATION | [15 empty] | YES | PART FAILED | [161 empty] | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | DURING THE SETTING OF THE PIG BAR ASSEMBLY FOR THE TAP, THE TAPPING MACHINE EXPERIENCED A FAILURE RESULTING IN A RELEASE OF NATURAL GAS. BECAUSE OF THE VOLUME OF GAS BEING RELEASED, IT WAS DECIDED THAT NO ATTEMPT TO CLOSE THE TAP VALVE SHOULD BE MADE. GATE VALVE 63 AND GATE VALVE 64 WERE CLOSED ISOLATING THE SEGMENT AND THE SEGMENT WAS BLOWN DOWN. **THIS REPORT IS BEING SUBMITTED IN RESPONSE TO PHMSA'S REQUEST, (DOCKET ID PHMSA-2013-0028), FOR SUPPLEMENTAL REPORTS FROM OPERATORS WHO SUBMITTED REPORTS FOR INCIDENTS OCCURRING AFTER JANUARY 1, 2010, WITH ANY OF THE FOLLOWING: (1) ``PIPE GIRTH WELD'' WAS SELECTED AS THE ``ITEM INVOLVED IN INCIDENT'' IN PART C3 OF THE REPORT. THE REVISED REPORT COLLECTS DATA ABOUT THE PIPE ADJACENT TO THE GIRTH WELD. (2) ``FUNCTION OF PIPELINE SYSTEM'' IS NULL IN PART E5F OF THE REPORT. THE REVISED REPORT COLLECTS THE FUNCTION OF THE PIPELINE SYSTEM FOR ALL INCIDENTS.** THIS SUPPLEMENTAL REPORT IS TO ACKNOWLEDGE THAT THE TWO RELEVANT SECTIONS IN PHMSA'S REQUEST HAVE BEEN REVIEWED AND NO FURTHER ACTIONS WERE NEEDED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20100104 | 15205 | 2010-12-16 14:43 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | TX | 77002 | 2010-12-03 05:30 | 2010 |  |  | 28.7833 | -91.7167 | 961308 | 2010-12-03 10:25 |  | NATURAL GAS |  | 10 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE PIPELINE WAS ALREADY SHUT-IN DUE TO OTHER REPAIRS. | [6 empty] | NO |  |  |  |  | NO | [9 empty] | OFFSHORE | [28 empty] | 125 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EUGENE ISLAND | 175 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 10.75 |  | 0.344 | 46000 | API | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | AMERICAN STEEL | OTHER | UNKNOWN | [27 empty] | 1967 | 1967 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 217 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 5000 | 3082.52427184466 | 50000 | 59670.5466638952 | 20000 | 23868.2186655581 | 0 | 0 |  |  | 75000 | 41542.2904899035 | 86621.289601298 | [8 empty] | 100 |  | 1300 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 22000 | NO |  | YES |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  | YES |  |  |  |  | YES |  |  |  | YES |  | YES |  |  |  | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | LOUIS SALINAS |  | louis_salinas@transcanada.com | 832-320-5305 | 832-320-6305 |  |  |  | LOUIS SALINAS |  | 832-320-5305 | No Email Address | A LEAK WAS DISCOVERED ON THE ANR 10-IN LINE 736, IN EUGENE ISLAND BLK. 175, WHILE THE LINE WAS BEING INSPECTED FOR OTHER REPAIRS. A VERY SMALL AMOUNT OF GAS WAS RELEASED. THE PIPELINE WAS REPAIRED ON DECEMBER 5, 2010 AT THE POINT OF THE LEAK, USING A REPAIR CLAMP.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100105 | 16115 | 2010-12-20 10:26 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2010-11-23 09:13 | 2010 |  |  | 29.2244 | -90.3872 | 960582 | 2010-11-23 10:15 |  | NATURAL GAS |  | 1 | 17403 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-11-23 16:30 | 2010-12-03 17:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-11-23 09:13 | 2010-11-23 09:13 | OFFSHORE | [28 empty] | 7 | IN STATE WATERS | LA |  |  | LAFOURCHE |  |  |  | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE SEAM | 36 |  | 0.5 | 60000 | API 5L OR EQUIVALENT | DSAW |  | US STEEL | OTHER | CONCRETE | [27 empty] | 1974 | 1974 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 861 |  | NO | NO | NO |  | 0 | 0 | 65000 | 77571.7106630638 | 0 | 0 | 535513 | 639087.069112451 | 0 | 0 | 0 | 0 |  |  | 600513 | 328965.290272293 | 716658.779775515 | [8 empty] | 810 |  | 1200 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 145823 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS FIRST SIGHTED BY ON SITE PERSONNEL AND SCADA INFORMATION REGARDING MAOP WAS NOT A FACTOR. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | YES | [14 empty] | YES | SEPARATION OF PIPE SEAM WELD MATERIAL PERPENDICULAR TO LONG SEAM. | [6 empty] | YES | [63 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | YES |  |  | 2010 | [6 empty] | YES | [53 empty] | KENNETH C. PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | ken_peters@kindermorgan.com | 2053257554 | 2053253729 |  |  |  | REJI GEORGE | DIRECTOR COMPLIANCE - CODES AND STANDARDS | 713-420-5433 | reji_george@kindermorgan.com | A CONTRACTOR WAS INVOLVED IN PERFORMING A SHALLOW WATER PIPE COVER INSPECTION FOR TENNESSEE GAS PIPELINE (TGP) IN STATE WATERS OFF THE COAST OF LOUSIANA WHEN BUBBLES WERE DETECTED IN THE VICINITY OF A TGP PIPELINE. USING DIVERS, A 1/16" CRACK WAS FOUND IN THE PIPE SEAM OF TGP'S 500-2 PIPELINE, VALVE SECTION 523-2. THE CRACK WAS PERPENDICULAR TO THE LONG SEAM. ULTRASOUND INSPECTION SHOWED NO EVIDENCE OF INTERNAL OR EXTERNAL CORROSION. THE PIPELINE WAS REPAIRED BY CLAMP INSTALLATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100106 | 15588 | 2010-12-21 10:16 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2010-11-30 14:50 | 2010 |  |  | 31.7869 | -93.1256 | 961059 | 2010-11-30 16:10 |  | NATURAL GAS |  | 14980 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-11-30 16:00 | 2012-05-11 14:20 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-11-30 14:50 | 2010-11-30 16:00 | ONSHORE | LA | 71457 | NATCHITOCHES | NATCHITOCHES | MILEPOST | 40-2D + 1.39 | LINE 100-2 | 40-2D | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 56 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 |  | 0.312 | 52000 | API 5L OR EQUIVALENT | DSAW |  | CONSOLIDATED | COAL TAR | [28 empty] | 1948 | 1948 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 567 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 54000 | 33291.2621359223 | 52000 | 62057.3685304511 | 10000 | 11934.109332779 | 0 | 0 |  |  | 116000 | 68478.603846767 | 107282.739999152 | [8 empty] | 671 |  | 750 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 29257 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO OVERPRESSURE CONDITION WAS PRESENT. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES | [6 empty] | YES | [12 empty] | YES |  | YES |  |  |  | YES | [59 empty] | YES | YES |  |  | YES |  |  |  | 2010 | [31 empty] | 2010 | [23 empty] | YES | 1985 | 1024 | NO | [13 empty] | NO | [63 empty] | KENNETH C. PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | ken.peters@elpaso.com | 2053257554 | 2053253729 |  |  |  | KENNETH C. PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | 2053257554 | ken.peters@elpaso.com | A LOUD NOISE WAS REPORTED TO TENNESSEE GAS PIPELINE (TGP) BY A MEMBER OF THE GENERAL PUBLIC IN THE VICINITY OF TGP PIPELINE FACILITIES IN NATCHITOCHES, LOUISIANA. UPON INITIAL INVESTIGATION, TGP OPERATIONS PERSONNEL FOUND A NATURAL GAS LEAK IN THE 100-2 PIPELINE. VISUAL EXAMINATION REVEALED THAT THE LEAK WAS COMING FROM A CRACK IN A WRINKLE BEND. THE CRACK WAS 1/2" WIDE AND PROPAGATED FOR A LENGTH OF 50.5" AROUND THE CIRCUMFERENCE OF THE PIPELINE. METALLUGICAL ANALYSIS REVEALED THAT THE CRACK IN THE WRINKLE BEND WAS LIKELY DUE TO CONCENTRATED MECHANICAL STRESSES COMING FROM EXTERNAL STRESSES FROM PROBABLE SHIFTING OF THE SURROUNDING SOIL, TRIAXIAL STATE OF STRESSES INHERENT TO IN-SERVICE WRINKLE BENDS (GEOMETRIC), AND INTERNAL LINE PRESSURE FROM NORMAL PIPELINE OPERATIONS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100107 | 15221 | 2010-12-21 21:09 | SUPPLEMENTAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2010-11-22 03:59 | 2010 |  |  | 40.86 | -88.5419 | 960465 | 2010-11-22 06:11 |  | NATURAL GAS |  | 10201 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-11-22 04:49 | 2011-03-21 08:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2010-11-22 03:59 | 2010-11-22 04:14 | ONSHORE | IL | 61764 | PONTIAC | LIVINGSTON | SURVEY STATION NO. | STATION 80 | PONTIAC STATION 80 | NORTH LEG OF MT. SIMON STRUCTURE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 41 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 |  | 0.375 | 52000 | API 5LX | SEAMLESS |  |  | COAL TAR | [28 empty] | 1969 | 1969 | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | DIAGNAL | 324 | 12 |  | CLASS 1 LOCATION | NO |  | 358 |  | NO | NO | NO |  | 200000 | 238682.186655581 | 0 | 0 | 44215 | 27258.7621359223 | 1800000 | 2148139.67990023 | 2152 | 2568.22032841405 | 41000 | 48929.8482643941 | METALURGICAL AND ENVIRONMENTAL ANALYSIS |  | 2087367 | 1147513.58621357 | 2465578.69728454 | [8 empty] | 1429 |  | 1654 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 11200 | NO |  |  |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  | YES |  |  |  |  | YES |  |  |  | YES | [5 empty] | NO | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | LETICIA QUEZADA | MANAGER REGULATORY COMPLIANCE | lquezad@nicor.com | 630-388-2316 |  |  |  |  | LETICIA QUEZADA | MANAGER REGULATORY COMPLIANCE | 630-388-2316 | lquezad@nicor.com | 12-INCH PIPELINE CONNECTING GAS STORAGE INJECTION/WITHDRAWL WELLS (AQUIFER-TYPE STORAGE RESERVOIR) TO A CENTRAL STORAGE STATION RUPTURED WITH WITH SUBSEQUENT IGNITION.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20100108 | 16367 | 2010-12-27 15:40 | SUPPLEMENTAL | 18646 | ENBRIDGE OFFSHORE (GAS TRANSMISSION) LLC | 1100 LOUISIANA ST. SUITE 3300 | HOUSTON | TX | 77002 | 2010-11-28 14:14 | 2010 |  |  | 28.3242 | -93.4567 | 960887 | 2010-11-28 15:57 |  | NATURAL GAS |  | 1 | 2151 | 0.16 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-11-28 15:57 | 2010-12-03 16:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-11-28 14:14 | 2010-12-01 20:40 | OFFSHORE | [28 empty] | 195 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST CAMERON | 543 | BELOW WATER, PIPE ON OR ABOVE SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 |  | 0.438 | 46000 | API 5L-X-46 | SEAMLESS |  | ? | OTHER | 1 13/64 CONCRETE AND 9/16 ASPHALT | [27 empty] | 1976 | 1976 | CARBON STEEL |  | LEAK | [9 empty] | CLASS 1 LOCATION | NO |  | 1 |  | NO | NO | NO |  | 0 | 0 | 8600 | 10263.33402619 | 100 | 61.6504854368932 | 300000 | 358023.279983372 | 100 | 119.341093327791 | 0 | 0 |  |  | 308800 | 169171.970316138 | 368467.605588326 | [8 empty] | 775 |  | 1200 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | OFFSHORE GATHERING | YES | YES | YES | NO | NO | AIR PATROL |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS A PIN HOLE LEAK OFFSHORE | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING | [5 empty] | YES | BEING INVESTIGATED AT THIS TIME | YES |  |  |  | YES | [5 empty] | YES | [316 empty] | LESLIE STEVENS | COMPLIANCE COORDINATOR |  | 832-214-1649 | 985-851-4126 |  |  |  | LESLIE STEVENS | COMPLIANCE COORDINATOR | 832-214-1649 | leslie.stevens@enbridge.com | A SHEEN WAS SPOTTED ON THE WATER WITH AN OCCASIONAL BUBBLE 10 TO 12 FEET IN DIAMETER ON NOVEMBER 28TH AT 14:14 HOURS SE OF WC 544 PLATFORM. THE RESPOONSE TEAM WAS MOBILIZED AND THE NRC WAS NOTIFIED AT 15:57 . A DIVE BOAT WAS MOBILIZED (JOANNE MORRISON) AND ARRIVED ON LOCATION DECEMBER 1ST AT APPROXIMATELY 20:40 HOURS. THE DIVERS CONFIRMED THE LEAK ON THE PIPE AT 6 O'CLOCK POSITION DECEMBER 2ND AT APPOXIMATELY 7:00 HOURS. A 16" PLIDCO CLAMP WAS INSTALLED AND THE LINE RETURNED TO SERVICE AT 16:15 HOURS ON DECEMBER 3RD.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20100109 | 16247 | 2010-12-29 19:53 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2010-11-29 14:40 | 2010 |  |  | 37.0046 | -120.4833 | 960985 | 2010-11-29 18:58 |  | NATURAL GAS |  | 8500 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | [7 empty] | NO |  |  |  |  | NO | [7 empty] | 2010-11-29 15:00 | 2010-11-29 16:00 | ONSHORE | CA | 93610 | 20 MILES EAST OF LOS BANOS & FIVE MILES SOUTH OF HIGHWAY 152 | MADERA |  |  |  |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 |  | 0.156 | 42000 | GRADE B | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | ASPHALT | [28 empty] | 1985 | 1985 | CARBON STEEL |  | MECHANICAL PUNCTURE | [9 empty] | CLASS 1 LOCATION | NO |  | 150 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 82000 | 97859.6965287882 | 0 | 0 | 0 | 0 |  |  | 82000 | 44920.1829141551 | 97859.6965287882 | [8 empty] | 250 |  | 650 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | [16 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [7 empty] | CONTRACTOR | FARM EQUIPMENT | AGRICULTURE | YES | 336506 | UNDERGROUND SERVICE ALERT--NORTHERN CALIFORNIA | UTILITY OWNER | YES | YES |  |  | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO MAINTAIN CLEARANCE | [263 empty] | CHERYL DIZON | GAS COMPLIANCE ENGINEER | c1dz@pge.com | 925-979-8205 | 925-328-5733 |  |  |  | FRANCES YEE | REGULATORY COMPLIANCE MANAGER | 925-974-4120 | fsc2@pge.com | ON MONDAY, NOVEMBER 29, 2010 AT APPROXIMATELY 1440 HOURS, A CONTRACTOR RIPPING AN AGRICULTURAL FIELD, STRUCK L-186 RELEASING GAS INTO THE ATMOSPHERE AT MP 21, APPROXIMATELY 20 MILES EAST OF LOS BANOS, AND APPROXIMATELY FIVE MILES SOUTH OF HIGHWAY 152. THE FARMER NOTIFIED PG&E OF THE GAS INCIDENT AT APPROXIMATELY 1500 HOURS AND PG&E PERSONNEL WERE ON SITE AT APPROXIMATELY 1600 HOURS. IT WAS DECIDED TO ALLOW GAS TO CONTINUE ESCAPING AND CONTINUE SERVICE TO FOUR DOWNSTREAM CUSTOMERS UNTIL COMPRESSED NATURAL GAS (CNG) WAS BROUGHT IN AND CONNECTED TO THE PIPELINE. A PRESSURE CONTROL FITTING WAS INSTALLED DOWNSTREAM OF THE LOCATION AND VALVE 19.17 WAS CLOSED TO ISOLATE THE SEGMENT. ONCE THE TAP FOR THE CNG WAS IN PLACE, PG&E STOPPED THE FLOW OF GAS ON THE TRANSMISSION LINE AT APPROXIMATELY 0605 HOURS ON NOVEMBER 30, AND COMPLETED REPAIRS OF THE TRANSMISSION PIPELINE BY REPLACING A 3-FOOT SECTION. PG&E COMPLETED REPAIRS AND PLACED THE TRANSMISSION PIPELINE BACK INTO OPERATION AT APPROXIMATELY 1230 HOURS ON NOVEMBER 30. THERE WERE NO FATALITIES OR INJURIES AS A RESULT OF THIS INCIDENT AND NO SERVICE INTERRUPTION. THERE WERE NO PUBLIC SAFETY OFFICIALS OR MEDIA ON-SITE. THE INCIDENT IS REPORTABLE TO THE CPUC AND DOT DUE TO PROPERTY DAMAGES, INCLUDING THE LOSS OF GAS, THAT EXCEED $82,000. A USA TICKET WAS IN EFFECT (# S 0343708 AND 0343731) FOR THE TRIANGLE T RANCH WHERE THE INCIDENT OCCURRED AND PG&E HAD WORKED WITH THE LANDOWNER TO DELINEATE, POTHOLE AND PROVIDE A BOUNDARY OF RIPPING OPERATIONS OVER THE PAST COUPLE WEEKS. THE CONTRACTOR PERFORMING THE RIPPING (DAVID PRICE) DID NOT OBTAIN HIS OWN USA TICKET. THE PIPELINE HAD BEEN MARKED BY PG&E AND A BOUNDARY TWENTY FEET ON EITHER SIDE OF THE PIPE HAD BEEN ESTABLISHED BY THE LANDOWNER. THE CAUSE OF THIS INCIDENT WAS THE FAILURE OF THE EXCAVATOR TO PROPERLY EXPOSE AND PROTECT PG&E FACILITIES. THE EXCAVATOR KNEW THE LINE LOCATION BUT THOUGHT HE WAS CLEAR WHEN HE LOWERED HIS RIPPER AND STRUCK THE LINE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100110 | 15356 | 2010-12-30 12:18 | SUPPLEMENTAL FINAL | 2564 | COLORADO INTERSTATE GAS CO | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2010-12-02 07:58 | 2010 |  |  | 38.7255 | -102.9304 | 961208 | 2010-12-02 09:35 |  | NATURAL GAS |  | 313870 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-12-02 08:40 | 2011-05-17 01:20 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-12-02 07:58 | 2010-12-02 08:24 | ONSHORE | CO | 80825 | KIT CARSON | CHEYENNE | MILEPOST | 104 + 1763.8 | LINE 2A |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.312 | 41000 | API 5L OR EQUIVALENT | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | YOUNGSTOWN SHEET & TUBE | COAL TAR | [28 empty] | 1947 | 1947 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 223.8 | 25.2 |  | CLASS 1 LOCATION | NO |  | 419 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 131825 | 81270.7524271845 | 44200 | 52748.7632508834 | 0 | 0 | 0 | 0 |  |  | 176025 | 108470.153492973 | 134019.515678068 | [8 empty] | 808 |  | 920 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 73920 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURES IN EXCESS OF MAOP WERE NOT PRESENT PRIOR TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) |  | YES | [13 empty] | YES | ENVIRONMENTALLY ASSISTED HYDROGEN STRESS CRACKING MECHANISM | [6 empty] | YES | [6 empty] | YES | HARDENED MICROSTRUCTURE IN THE HEAT AFFECTED ZONE AND IMPERFECTIONS IN THE FORM OF SURFACE LAPS AND PRE-EXISTING CRACKS. | [55 empty] | YES | YES |  |  | YES |  |  |  | 2006 |  | HARD SPOTS | [29 empty] | 2003 | [23 empty] | YES | 2011 | 1387 | NO | [13 empty] | NO | [63 empty] | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | ken.peters@elpaso.com | 2053257554 | 2053253729 |  |  |  | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | 2053257554 | ken.peters@elpaso.com | ON DECEMBER 2, 2010, COLORADO INTERSTATE GAS (CIG) LOCAL OPERATING PERSONNEL NOTICED A PRESSURE DROP ON CIG'S 20-INCH LINE 2A AT THE COMPANY'S KIT CARSON COMPRESSOR STATION AT APPROXIMATELY 7:58 AM MST. FIELD INVESTIGATION REVEALED THAT A RUPTURE HAD OCCURRED APPROXIMATELY 9 MILES WEST OF THE COMPRESSOR STATION NEAR CHEYENNE COUNTY ROAD J. THE PIPELINE WAS ISOLATED. THERE WAS NO FIRE AND THERE WERE NO INJURIES NOR FATALITIES. POST INCIDENT INVESTIGATION REVEALED THAT THE RUPTURE ORIGINATED FROM AN AXIAL CRACK LOCATED IN THE HEAT AFFECTED ZONE (HAZ) OF THE ERW LONGITUDINAL SEAM WELD AT THE 6 O'CLOCK POSITION OF THE PIPELINE. THE CRACK GROWTH WAS DUE TO AN ENVIRONMENTALLY ASSISTED HYDROGEN STRESS CRACKING MECHANISM. THE ORIGINAL MANUFACTURING PROCESS CREATED A HARDENED MICROSTRUCTURE IN THE HAZ OF THE LONGITUDINAL SEAM WELD RENDERING IT SUSCEPTIBLE TO THIS CONDITION. MANUFACTURING IMPERFECTIONS, IN THE FORM OF SURFACE LAPS AND PREEXISTING CRACKS, ADJACENT TO THE LONGITUDINAL SEAM WELD SERVED AS STRESS CONCENTRATORS AND SITES FOR CRACK INITIATION DURING SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20100111 | 15148 | 2010-12-30 16:50 | ORIGINAL FINAL | 12576 | CENTERPOINT ENERGY - MISSISSIPPI RIVER GAS TRANSMISSION CORP | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2010-11-30 06:20 | 2010 |  |  | 38.6748 | -90.1571 | 961004 | 2010-11-30 09:36 |  | NATURAL GAS |  | 1897 | 250 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-11-30 08:00 | 2010-12-05 13:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-11-30 06:20 | 2010-11-30 06:50 | ONSHORE | IL | 62060 | MADISON | MADISON | SURVEY STATION NO. | 109+45 | MRT - LINE A-122 | MRT - LINE A-122 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 70 |  | YES |  |  |  |  | YES | UNCASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.5 | 65000 | API-5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | STUPP CORPORATION | EPOXY | [28 empty] | 2010 | 2009 | CARBON STEEL |  | LEAK |  |  | OTHER | EROSION CAUSED HOLE | [5 empty] | CLASS 3 LOCATION | YES | METHOD2 | 195 |  | NO | NO | NO |  | 0 | 0 | 1100 | 1312.7520266057 | 8345 | 5144.73300970874 | 145955 | 174184.292766577 | 4425 | 5280.84337975473 | 0 | 0 |  |  | 159825 | 88315.5991444229 | 185922.621182646 | [8 empty] | 182 |  | 200 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 17592 | NO |  |  | YES |  |  |  |  | YES |  |  |  |  | YES | SEE 5.D | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS CAUSED BY A RUPTURED WATER LINE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [103 empty] | OTHER OUTSIDE FORCE DAMAGE | [9 empty] | WATER LINE RUPTURED AND ALONG WITH SANDY SOIL ERODED A HOLE IN THE TRANSMISSION PIPELINE. | [251 empty] | JOHNNY L. CAVITT | DOT COMPLIANCE MANAGER | johnny.cavitt@centerpointenergy.com | 318-429-3606 | 318-429-3927 |  |  |  | JOHNNY L. CAVITT | DOT COMPLIANCE MANAGER | 318-429-3606 | johnny.cavitt@centerpointenergy.com | ON THE MORNING OF NOVEMBER 30, 2010 AT 0620 THE FIRE CHIEF FROM THE CITY OF MADISON CALLED MISSISSIPPI RIVER TRANSMISSION (MRT) SYSTEM CONTROL TO REPORT A GAS LEAK AT THE INTERSECTION OF WASHINGTON AVE. AND RACE ST. MRT'S SYSTEM CONTROLLER NOTIFIED FIELD PERSONNEL AND OUR FIRST RESPONDERS ARRIVED ON THE SCENE AT 0650. THERE WAS A WATER LEAK AT THIS SITE ALSO AND WE COULD NOT IMMEDIATELY CONFIRM THAT IT WAS A GAS LEAK. WE CLOSED THE INLET BLOCK VALVE (BV42311 AT STATION 00+01) AT 0725 ON LINE A-122. THE DOWNSTREAM BLOCK VALVE (BV42312 AT STATION 175+92) WAS CLOSED AT 0755 ON LINE A-122. WE MONITORED THE LINE PRESSURE AND CONFIRMED THAT WE WERE LEAKING GAS AT 0837 ON OUR PIPELINE. MRT'S CONTRACTOR BROUGHT IN A 6" WATER PUMP TO REMOVE THE WATER AT 0930 SO WE COULD EXCAVATE THE AREA OF THE LEAK. THE WATER COMPANY WAS CALLED TO THE SCENE AND THEY DENIED THAT THEY HAD A LEAK. THERE WAS ALSO A LIFT STATION DRAINAGE LINE IN THIS AREA. IT WAS SHUT OFF. AT 1630 AFTER NOT MAKING MUCH PROGRESS IN THE WATER REMOVAL, THE WATER COMPANY WAS CALLED AGAIN. THEY ARRIVED AT 1745 AND CONFIRMED THAT THEY DID HAVE A LEAK. THE WATER LINE WAS SHUTOFF AND EXCAVATION WAS STARTED ONCE THE WATER WAS REMOVED. AT 2130 A 4 BOLT LEAK CLAMP WAS INSTALLED ON THE GAS LINE TO SEAL OFF THE LEAK CAUSED BY EROSION FROM THE WATER AND SANDY SOIL. POSITIVE PRESSURE WAS MAINTAINED ON THE PIPELINE TO PREVENT WATER FROM ENTERING THE PIPE. THE LINE WAS BLOWN DOWN TO PREPARE FOR REPAIRS AT A LATER DATE. THE WATER COMPANY FINISHED THEIR LEAK REPAIRS AT 0230 ON DECEMBER 1ST. WATER WAS CONTINUOUSLY PUMP FROM THE AREA UNTIL DECEMBER 3RD. MRT'S CONTRACT WELDERS STARTED FABRICATING THE REPLACEMENT PIPE AND FITTINGS AT THE COLUMBIA MEASURING STATION ON DECEMBER 1ST. ON DECEMBER 2ND, THE PIPE AND FITTINGS WERE TRANSPORTED TO THE CONTRACTORS WELDING SHOP TO FINISH THE FABRICATION AND X-RAY. AT THE LEAK SITE THERE WAS MORE EXCAVATION DONE AND A 20 FT. SECTION OF PIPE WAS REMOVED. FOREMAN PLUGS WERE INSTALLED IN THE ENDS OF THE PIPE TO PREVENT ANYTHING FROM ENTERING THE PIPELINE. AN 8 HOUR HYDROTEST WAS PERFORMED ON THE NEW PIPE AND FITTING ON DECEMBER 3RD. DECEMBER 4TH THE CONTRACTOR DUG OUT MORE DITCH AND STARTED TO MAKE THE WELDS ON THE REPLACEMENT PIPE AND FITTINGS. BOTH OF THE WELDS WERE X-RAYED AND PASSED THE X-RAY. ON DECEMBER 5TH, FINISHED DIGGING OUT THE DOWNSTREAM END OF THE LINE IN ORDER TO FINISH THE TIE-INS. THE WELDS FROM THE PREVIOUS DAY WERE BLASTED AND RECOATED. LINE WAS TIED-IN AT 1100. AFTER PASSING THE X-RAY, THE LAST WELD WAS BLASTED AND RECOATED. THE LINE WAS PURGED, LOADED, AND PLACED BACK IN SERVICE AT 1330 ON DECEMBER 5TH.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110002 | 15289 | 2011-01-06 11:17 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2010-12-08 16:25 | 2010 |  |  | 29.5314 | -96.1425 | 961743 | 2010-12-08 17:38 |  | NATURAL GAS |  | 69908 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-12-08 16:25 | 2011-01-27 15:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 2 | 2010-12-08 16:25 | 2010-12-08 16:25 | ONSHORE | TX | 77435-9487 | EAST BERNARD | WHARTON | MILEPOST | 0 | EAST BERNARD STATION 17 | HIGH PRESSURE GAS GATHERING HEADER | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 39 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 |  | 0.5 | 40000 | API 5L OR EQUIVALENT | OTHER | UNKNOWN. | A.O. SMITH | COAL TAR | [28 empty] | 1947 | 1947 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 141 | 24 |  | CLASS 1 LOCATION | NO |  | 454 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 600000 | 369902.912621359 | 110000 | 131275.20266057 | 5000 | 5967.05466638952 | 0 | 0 |  |  | 715000 | 446492.963132627 | 507145.169948318 | [8 empty] | 717 |  | 750 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 46780 | NO | [5 empty] | YES | SEGMENT CONTAINING FAILURE IS A CAPPED "STUB" OF PIPE THUS RENDERING A CONFIGURATION THAT DOES NOT ACCOMMODATE AN INTERNAL INSPECTION TOOL. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATING PRESSURES WERE IN NORMAL RANGE. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | MIC DETERIORATING THE INSIDE WALL OF THE PIPE. |  |  | YES |  |  |  |  | YES | [6 empty] | YES | DEAD END (WELD CAP). | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | ken.peters@elpaso.com | 2053257554 | 2053253729 |  |  |  | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | 2053257554 | ken.peters@elpaso.com | ON DECEMBER 8, 2010, TENNESSEE GAS PIPELINE (TGP) OPERATIONS PERSONNEL AT THE COMPANY'S EAST BERNARD COMPRESSOR STATION (STATION 17) HEARD A LOUD NOISE APPROXIMATELY 1,100 FEET SOUTH OF THEIR LOCATION. TGP GAS CONTROL OBSERVED A CORRESPONDING PRESSURE DROP IN THE PIPELINE NEAR THE STATION. A 24-INCH PIPE HAD RUPTURED WITHOUT GAS IGNITION. THE CAUSE HAS BEEN DETERMINED TO BE INTERNAL CORROSION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110003 | 16155 | 2011-01-07 16:13 | SUPPLEMENTAL FINAL | 2564 | COLORADO INTERSTATE GAS CO | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2010-12-12 02:30 | 2010 |  |  | 39.6034 | -104.1575 | 962042 | 2010-12-12 05:01 |  | NATURAL GAS |  | 74480 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-12-15 14:00 | 2011-08-02 02:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2010-12-12 02:45 | 2010-12-12 02:45 | ONSHORE | CO | 80103 | BYERS | ARAPAHOE | MILEPOST | 0 + 01.5 | LATIGO STORAGE | LINE NO. 103F37 | NO | OPERATOR-CONTROLLED PROPERTY | BELOWGROUND STORAGE OR ABOVEGROUND STORAGE VESSEL, INCLUDING ATTACHED APPURTENANCE |  |  |  |  | NO | [22 empty] | INTERSTATE | ABOVEGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | FILTER/STRAINER/SEPARATOR | [38 empty] | 1979 |  | CARBON STEEL |  | LEAK |  |  | OTHER | HOLE IN DUMP VALVE BODY | [5 empty] | CLASS 1 LOCATION | NO |  | 211 |  | NO | NO | NO |  | 100000 | 119341.09332779 | 0 | 0 | 279321 | 172202.752427184 | 1667682 | 1990229.93203076 | 620000 | 739914.778632301 | 0 | 0 |  |  | 2667003 | 1486519.58555838 | 3021688.55641804 | [8 empty] | 926 |  | 2130 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLERS WERE NOT INVOLVED AND OPERATION WAS WELL BELOW MAOP. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | FAILURE OF EQUIPMENT BODY (EXCEPT COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL | MATERIAL/WELD/EQUIP FAILURE | FAILURE OF EQUIPMENT BODY | [166 empty] | FAILURE OF EQUIPMENT BODY (EXCEPT COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL | [35 empty] | YES | HOLE IN DUMP VALVE BODY CAUSED BY CORROSIVE EFFECT OF RESERVOIR SANDS | [161 empty] | MARTIN MULLER | COMPLIANCE ENGINEER | martin_muller@kindermorgan.com | 205-325-3863 | 205-325-3508 |  |  |  | REJI GEORGE | DIRECTOR COMPLIANCE - CODES AND STANDARDS | 713-420-5433 | reji_george@kindermorgan.com | A LAND OWNER CONTACTED COLORADO INTERSTATE GAS COMPANY'S GAS CONTROL TO REPORT A FIRE IN THE VICINITY OF THE LATIGO STORAGE FACILITIES IN THE EARLY MORNING HOURS OF DECEMBER 12, 2010. RESPONDING CIG OPERATIONS PERSONNEL FOUND A FIRE AT WELL #31. THIS FIRE WAS CAUSED WHEN GAS ESCAPING FROM A HOLE IN THE BODY OF A SEPARATOR DUMP VALVE IGNITED. THE SEPARATOR WAS PART OF THE SURFACE EQUIPMENT ASSOCIATED WITH AN UNDERGROUND GAS STORAGE INJECTION/WITHDRAWAL WELL. THE HOLE WAS CAUSED BY THE CORROSIVE EFFECTS OF RESERVOIR SAND AND PRODUCED FLUIDS FLOWING UNDER PRESSURE THROUGH THE SEPARATOR VALVE ON THEIR WAY FROM THE SEPARATOR TO THE STORAGE FIELD'S DRAIN SYSTEM.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110004 | 15152 | 2011-01-07 17:01 | ORIGINAL FINAL | 22655 | WILLISTON BASIN INTERSTATE PIPELINE CO | 1250 WEST CENTURY AVENUE | BISMARCK | ND | 58503 | 2010-12-10 09:58 | 2010 |  |  | 47.0341 | -103.0939 | 961911 | 2010-12-10 11:40 |  | NATURAL GAS |  | 3910 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-12-10 10:59 | 2010-12-13 17:03 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 0 | 2010-12-10 10:55 | 2010-12-10 11:00 | ONSHORE | ND | 58622 | BELFIELD | BILLINGS | SURVEY STATION NO. | 327+28 | LITTLE KNIFE FIELD LINE | LITTLE KNIFE FIELD LOOP LINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8.625 |  | 0.188 | 42000 | API 5 L | LONGITUDINAL ERW - HIGH FREQUENCY |  | MULTIPLE, UNKNOWN EXACTLY WHICH ONE | COLD APPLIED TAPE | [28 empty] | 1980 | 1980 | CARBON STEEL |  | MECHANICAL PUNCTURE | 2 | 8 | [7 empty] | CLASS 1 LOCATION | NO |  | 188 |  | NO | NO | NO |  | 450000 | 537034.919975057 | 0 | 0 | 18819 | 11602.0048543689 | 5112 | 6100.71669091665 | 308 | 367.570567449595 | 0 | 0 | NON-OPERATOR COSTS OBTAINED FROM CONTRACTOR WILL NOT BE PAID/REIMBURSED BY WBI |  | 474239 | 261510.638691066 | 555105.212087792 | [8 empty] | 626 |  | 918 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 42292 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS CONTROLLER TOOK IMMEDIATE ACTION AND FOLLOW-UP UPON NOTIFICATION CONSISTENT WITH EMERGENCY RESPONSE PROCEDURES. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | YES |  |  | YES | PRIVATE LANDOWNER | [7 empty] | CONTRACTOR | TRENCHER | LIQUID PIPELINE | YES | 10131463 | ONLY ONE CENTER, NORTH DAKOTA ONE CALL | UTILITY OWNER | YES | YES | YES | 77 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO MAINTAIN THE MARKS | [263 empty] | CRAIG WAGNER | PIPELINE INTEGRITY AND COMPLIANCE MANAGER | craig.wagner@wbip.com | 406-359-7216 | 406-359-7225 |  |  |  | CRAIG WAGNER | PIPELINE INTEGRITY AND COMPLIANCE MANAGER | 406-359-7216 | craig.wagner@wbip.com | ON 12/10/2010 A CONTRACTOR WAS INSTALLING A NEW 12 INCH PIPELINE FOR A LIQUIDS PIPELINE COMPANY WHEN THE CONTRACTOR'S TRENCHER STRUCK WILLISTON BASIN'S EIGHT INCH NATURAL GAS TRANSMISSION LINE. THE NEW PIPELINE RUNS PARALLEL TO AN EXISTING LIQUIDS PIPELINE AND CROSSES WILLISTON BASIN'S PIPELINE ON PRIVATE LAND AT AN APPROXIMATELY RIGHT ANGLE. THE TRENCHER STRIKE RESULTED IN TWO HOLES ON THE SIDE OF THE EIGHT INCH WBI PIPELINE RELEASING GAS THAT WAS OPERATING AT APPROXIMATELY 626 PSIG. THE GAS IGNITED AND BURNED THE TRENCHER AND TWO PICKUPS PARKED NEARBY. NO MAJOR INJURIES OR DEATHS OCCURRED. THE CONTRACTOR IMMEDIATELY CALLED WBI'S CONTACT PERSON, QUAIN KUDRNA, AND INFORMED HIM OF THE SITUATION. QUAIN IMMEDIATELY RESPONDED AND NOTIFIED WBI'S GAS CONTROL. WBI WAS ABLE TO ISOLATE THE SECTION OF PIPELINE WITHIN ONE HOUR. THE CONTRACTOR INITIATED A ONE-CALL ON FRIDAY, 11/26/2010. ON MONDAY, 11/29/2010, QUAIN TRAVELED TO THE PROPOSED SITE AND LOCATED WBI'S PIPELINE AT THE LOCATION WHERE THE EXISTING LIQUIDS LINE CROSSED AND NEW PIPELINE WAS PLANNED TO CROSS. QUAIN CALLED THE CONTRACTOR CONTACT AT THAT TIME AND INFORMED HIM OF THE CROSSING AND THAT WBI WILL NEED TO BE AT THE LOCATION PRIOR TO CROSSING TO EXPOSE WBI'S PIPELINE. THE CONTRACTOR INFORMED QUAIN THAT THEY WOULD BE AT THE LOCATION AT THE END OF THAT WEEK AND HE WOULD CALL QUAIN BACK WHEN THEY WERE THERE. THE CONTRACTOR DID NOT CALL QUAIN BACK THAT WEEK AND THE END OF THE FOLLOWING WEEK IS WHEN THE CONTRACTOR HIT WBI'S LINE. THE CONTRACTOR ADMITTED THAT HE FORGOT TO CALL BACK. THE CONTRACTOR ALSO STATED THAT HE DID NOT REMEMBER SEEING THE WBI FLAGS AT THE SITE. AFTER THE GAS WAS BLOWN DOWN AND SITE WAS DETERMINED TO BE SAFE, WBI PERSONNEL INVESTIGATED THE LOCATION. IT WAS NOTED THAT THE CONTRACTOR HAD BLADED THE ROW PRIOR TO EXCAVATING TO REMOVE SNOW WHICH WOULD LIKELY DESTROY THE MARKER FLAGS ON THE ROW. ONE CHARRED MARKER FLAG STILL REMAINED ON THE BLADED ROW BUT WAS FLAT ON THE GROUND. TWO MARKER FLAGS WERE FOUND INTACT ADJACENT TO THE BLADED ROW. ESTIMATES OF DAMAGE TO CONTRACTOR EQUIPMENT WERE OBTAINED FROM CONTRACTOR CONTACT SCOTT LAWSON. THE LOCATE TICKET WITH QUAIN'S NOTES FROM THE DAY HE MARKED AND CALLED ARE ATTACHED IN ADDITION TO SOME PICTURES.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110005 | 15153 | 2011-01-13 17:17 | ORIGINAL | 18532 | TEXAS GAS SERVICE COMPANY | 1301 S MOPAC EXPY, SUITE 400 | AUSTIN | TX | 78746-6918 | 2010-12-14 10:42 | 2010 |  |  | 26.1707 | -97.7138 | 962347 | 2010-12-15 17:30 |  | NATURAL GAS |  | 10 | 13 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | [7 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-12-14 10:42 | 2010-12-14 10:42 | ONSHORE | TX | 78550-3534 | HARLINGEN | CAMERON |  |  | LINE 198 | SAN SALVADOR TO SAN BENITO 10" | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 180 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10.75 |  | 0.25 | 52000 | API5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | CONSOLIDATED PIPE AND SUPPLY | EPOXY | [28 empty] | 2010 | 2010 | CARBON STEEL |  | OTHER | [8 empty] | 2ND PARTY DAMAGE. FACILITIES DAMAGED DURING BORING OPERATION. (DID NOT UNCOVER FACILITIES.) | CLASS 3 LOCATION | YES | METHOD1 | 189 |  | NO | NO | NO |  | 0 | 0 | 65 | 77.5717106630638 | 50 | 30.8252427184466 | 203000 | 242262.419455415 | 2000 | 2386.82186655581 | 0 | 0 | NONE |  | 205115 | 112368.022676256 | 244757.638275352 | [8 empty] | 320 |  | 650 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 43666 | NO |  |  |  | YES |  |  |  | YES | YES | [5 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | 2ND PARTY |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE DAMAGE RESULTS IN A VERY SMALL LOSS OF GAS, LESS THAN 10 MCF. SCADA EQUIPMENT WOULD NOT HAVE PICKED UP THIS SMALL AMOUNT OF GAS LOSS. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [10 empty] | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | BORING | NATURAL GAS | NO | 103360291 | TEXAS EXCAVATION SAFETY SYSTEM *GLITCH IN YOUR SYSTEM. YES, ONE CALL CENTER WAS NOTIFIED. | CONTRACT LOCATOR | UNKNOWN/OTHER | UNKNOWN/OTHER |  |  | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO MAINTAIN CLEARANCE | [263 empty] | DEAN LAFLAMME | MANAGER REGIONAL ENGINEERING | dlaflamme@txgas.com | (512) 370-8318 | (512) 370-8400 |  |  |  | DEAN LAFLAMME | MANAGER REGIONAL ENGINEERING | (512) 370-8318 | dlaflamme@txgas.com | A CONTRACTOR WORKING FOR TEXAS GAS SERVICE (STRIKE CONSTRUCTION ' 2ND PARTY CONTRACTOR) WAS INSTALLING A 12' COATED LINE. DURING THE BORING OPERATION WHILE INSTALLING THIS 12' LINE THEY DAMAGED TEXAS GAS SERVICE'S 10' TRANSMISSION COATED STEEL LINE ON 12/14/10. IN LIEU OF REPAIRING THE DAMAGED SECTION (WHICH WAS 15' DEEP) IT WAS DETERMINED (ON 12/15/2010) TO REPLACE THE ENTIRE LINE SEGMENT WHICH WAS IN QUESTION. THE NEW INSTALLATION OF THE DAMAGED FACILITIES WERE OVER THE $50,000 MAKING THIS A REPORTABLE INCIDENT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110006 | 15155 | 2011-01-17 17:29 | ORIGINAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION LP (SPECTRA ENERGY CORP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2010-12-19 09:15 | 2010 |  |  | 28.4419 | -93.195 | 962663 | 2010-12-19 11:15 |  | NATURAL GAS |  | 424 | 22615 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-12-22 22:20 | 2010-12-23 04:25 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-12-19 09:15 | 2010-12-19 09:15 | OFFSHORE | [28 empty] | 165 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST CAMERON | 513 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 20 |  | 0.406 | 52000 | API-5L X-52 | SEAMLESS |  | U.S. STEEL | OTHER | CONCRETE COATED | [27 empty] | 1975 | 1975 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 524 |  | NO | NO | NO |  | 0 | 0 | 158300 | 188916.950737892 | 2968 | 1829.78640776699 | 500000 | 596705.466638952 | 0 | 0 | 0 | 0 |  |  | 661268 | 362518.442316993 | 787452.203784612 | [8 empty] | 762 |  | 1440 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 81629 | NO |  |  |  | YES |  | YES | NO PLATFORMS FROM WHICH TO LAUNCH AND RECEIVE TOOLS | YES |  |  | YES |  | YES | NO PLATFORM FROM WHICH TO LAUNCH TOOLS | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | NOTIFICATION FROM PLATFORM OPERATOR |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE GAS LOSS WAS SO INSIGNIFICANT THAT SCADA WOULD NOT BE ABLE TO DETECT IT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DWAYNE TESCHENDORF | PRINCIPAL ENGINEER | deteschendorf@spectraenergy.com | 713-627-5573 | 713-386-4468 |  |  |  | RICK KIVELA | DIRECTOR OF OPERATIONAL COMPLIANCE | 713-627-6388 | rwkivela@spectraenergy.com | INDICATIONS OF BUBBLES ON THE SURFACE OF THE WATER IN WEST CAMERON BLOCK 513 WERE REPORTED BY A NEARBY PLATFORM OPERATOR AT 9:15 AM ON DECEMBER 19, 2010. UPON INVESTIGATION, IT WAS DETERMINED THE LEAK WAS CAUSED BY A PINHOLE RESULTING FROM INTERNAL CORROSION. A LEAK CLAMP WAS INSTALLED AS A PERMANENT REPAIR AT A COST OF $500,000.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110007 | 15835 | 2011-01-21 10:31 | SUPPLEMENTAL FINAL | 19270 | TEXAS GAS TRANSMISSION LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2010-12-24 00:47 | 2010 |  |  | 30.05 | -92.05 | 963040 | 2010-12-24 02:15 |  | NATURAL GAS |  | 654 | 157 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-12-24 00:47 | 2011-11-28 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 0 | 2010-12-24 00:50 | 2010-12-24 01:20 | ONSHORE | LA | 70592 | YOUNGSVILLE | LAFAYETTE | MILEPOST | 40.1899 | YOUNGSVILLE COMPRESSOR STATION |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 1965 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 700 |  | YES | NO | NO |  | 2000 | 2386.82186655581 | 600 | 716.046559966743 | 2000 | 1233.00970873786 | 300000 | 358023.279983372 | 1500 | 1790.11639991686 | 0 | 0 |  |  | 306100 | 167866.458910574 | 364149.274518549 | [8 empty] | 1000 |  | 1052 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS DUE TO COMPRESSOR COMPONENT MALFUNCTION | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | OTHER | ENGINE BOLTS THAT SECURED THE UNLOADER TO THE COMPRESSOR. | [20 empty] | YES | HIGH CYCLE FATIGUE. | [161 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 270-688-6357 | 270-688-5871 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 270-688-6361 | jeff.mcmaine@bwpmlp.com | ON DECEMBER 24TH, 2010 AT 12:50 AM THE TEXAS GAS, GAS CONTROL CENTER, RECEIVED VARIOUS ALARMS INDICATING FIRE, VIBRATION, AND EMERGENCY SHUTDOWN (ESD) ALARMS WERE ACTIVATED. THE GAS CONTROLLER CONTACTED THE LOCAL OPERATOR ON DUTY AND HE WAS DISPATCHED TO THE SITE. TEXAS GAS' FIRST RESPONDER ARRIVED ON LOCATION AT APPROXIMATELY 1:20 AM. UPON ARRIVING, THE FIRE DEPARTMENT AND STATE POLICE WERE ON SITE AND THE LOCATION WAS SECURE. ONCE CLEARED BY THE FIRE CHIEF ON SITE, TEXAS GAS PERSONNEL ENTERED THE SITE TO ASSESS THE DAMAGE. A GAS UNLOADER ON ENGINE #1 HAD SEPARATED FROM THE COMPRESSOR WHICH RESULTED IN A GAS RELEASE AND ULTIMATE IGNITION. THE EIGHT ENGINE BOLTS THAT SECURED THE UNLOADER WERE GATHERED AND SENT TO A METALLURGIST TO BE ANALYZED. THE METALLURGICAL REPORT DETERMINED THAT SIX OF THE EIGHT BOLTS FAILED DUE TO HIGH CYCLE FATIGUE. THE REPAIRED UNLOADER WAS TESTED BY DRESSER-RAND. THE UNLOADER WAS INSTALLED ON ENGINE #1 ON 11-21-2011. THE UNIT WAS RETURNED TO SERVICE ON 11-28-2011. ADDED DATA TO PART E5.F AS REQUESTED BY PHMSA.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110008 | 15170 | 2011-01-21 10:57 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2010-12-22 13:42 | 2010 |  |  | 27.8446 | -97.5246 | 962960 | 2010-12-22 20:30 |  | NATURAL GAS |  | 333 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-12-22 20:30 | 2010-12-27 22:05 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-12-22 13:42 | 2010-12-22 14:15 | ONSHORE | TX | 78401 | CORPUS CHRISTI | NUECES | MILEPOST |  | SOUTHERN COAST TO REYNOLDS | 201 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [8 empty] | CARBON STEEL |  | OTHER | [8 empty] | A PIECE OF CONCRETE ROLL DURING THE DEMOLITION OF A BUILDING AND HIT THE ABOVE GROUND RISER CAUSING IT TO CRACK | CLASS 1 LOCATION | NO |  |  |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 1332 | 821.184466019417 | 24812 | 29610.9120764914 | 7365 | 8789.47152359177 | 0 | 0 |  |  | 33509 | 18478.1485602372 | 39221.5680661026 | [8 empty] | 453 |  | 868 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 21120 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) | [5 empty] | YES | [7 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [103 empty] | OTHER OUTSIDE FORCE DAMAGE | [9 empty] | DURING A DEMOLITION PROJECT ON BUILDING A PIECE OF THE CONCRETE SLAB HIT A 1" ABOVE GROUND VALVE AND RISER ON THAT RAN 11 FEET OFF THE MAINLINE. | [251 empty] | MATTHEW STRATMANN | PIPELINE COMPLIANCE SPECIALIST | mstratmann@eprod.com | 713-381-8209 |  |  |  |  | MATTHEW STRATMANN | PIPELINE COMPLIANCE SPECIALIST | 713-381-8209 | mstratmann@eprod.com | THE CONTROL CENTER FOR ENTERPRISE PRODUCTS OPERATING LLC (ENTERPRISE) WAS NOTIFIED BY A THIRD PARTY CONTRACTOR THAT THEY HAD HIT AN ABOVE GROUND RISER ON AN ENTERPRISE PIPELINE WITH A PIECE OF CONCRETE. ENTERPRISE RESPONDED TO THE INCIDENT AND INITIALLY DETEMINED THAT THE LINE LEAKING DID NOT BELONG TO ENTERPRISE. AFTER FUTHER INVESTIGATION IT WAS DETERMINED THAT THE LEAK WAS ON AN ENTERPRISE PIPELINE. THE TAP AND ABOVE GROUND RISER WAS 11 FEET LONG. ENTERPRISE ACQUIRED THIS PIPELINE IN 2005. NONE OF THE INFORMATION ACQUIRED DURING THE ACQUISION INDICATED THAT THIS TAP EXISTED. THE IS LINE WAS BUILT IN 1967 AND PREVIOUS OPERATORS DID NOT DOCUMEMENT THE PRESENCE OF THE TAP. AS PART OF THE REPAIR ACTIVITY ASSOCIATED WITH THIS INCIDENT, ENTERPRISE REMOVED THE TAP FROM THE PIPELINE.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20110009 | 15166 | 2011-01-25 14:35 | ORIGINAL FINAL | 19570 | WILLIAMS GAS PIPELINE - TRANSCO | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2010-12-30 10:45 | 2010 |  |  | 29.1111 | -94.4042 | 963399 | 2010-12-30 15:45 |  | NATURAL GAS |  | 500 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | UNNECESSARY DUE TO MINIMAL LEAKAGE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-12-30 10:50 | 2010-12-31 23:20 | OFFSHORE | [28 empty] | 60 | IN STATE WATERS | TX | HIGH ISLAND | 206 | GALVESTON |  |  |  | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | FLANGE ASSEMBLY | [38 empty] | 1977 |  | CARBON STEEL |  | LEAK |  |  | OTHER | LEAK THRU THREAD | [5 empty] | CLASS 1 LOCATION | NO |  | 314 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 2139 | 1318.70388349515 | 0 | 0 | 154000 | 183785.283724797 | 0 | 0 |  |  | 156139 | 85729.4549353928 | 185103.987608293 | [8 empty] | 940 |  | 1440 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 3 | NO | [5 empty] | YES | 1" BLEEDER VALVE | YES |  |  |  |  | YES | SUBSEA TIE IN ASSEMBLY NOT PIGGABLE | TYPE B GATHERING | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK RATE BETWEEN THE THE THREADS OF 1" PLEECO BLEEDER VALVE FITTING AND THE FLANGE THREADS WAS SO SMALL THAT IT WAS NOT DETECTABLE BY CONTROL ROOM MONITORING EQUIPMENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | THREADED FITTING | [19 empty] | YES | GRADUAL THREAD WEAR OVER TIME CAUSED BY INCREASED GAS LEAKEAGE. | [161 empty] | EDGAR RODRIGUEZ | PIPELINE SAFETY SPECIALIST II | edgar.x.rodriguez@williams.com | 713-215-2846 | 713-215-2222 |  |  |  | MARIE SOTAK | PIPELINE SAFETY MANAGER | 713-215-2111 | marie.sotak@williams.com | ON 12/30/2010 AT 10:45, GAS CONTROL WAS NOTIFIED BY USCG THAT BUBBLES WERE REPORTED NEAR A WILLIAMS PIPELINE IN BLOCK HI206. A DIVE BOAT WAS MOBILIZED TO INVESTIGATE BUBBLES. DIVERS FOUND A 1" PLEECO BLEEDER VALVE LEAKING GAS FROM VALVE LW856 BLIND FLANGE. SUB-SEA ASSEMBLY VALVE LW855 & LW856 WERE CLOSED AND PIPING BLED DOWN. THREADS WERE DAMAGED/CUT BY GAS LEAK THAT INCREASED IN SEVERITY OVER TIME. 1" PLEECO BLEEDER VALVE WAS REPLACED. SUB-SEA ASSEMBLY WAS REPRESSURED, VERIFIED NO LEAKS AND JOB WAS COMPLETED. THIS IS A RARE OCURRENCE AND IF FUTURE SIMILAR FAILURES OCCUR THE ASSESSMENT OF COMPREHENSIVE CORRECTIVE ACTION WILL BE REVISITED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110010 | 15214 | 2011-01-27 20:35 | SUPPLEMENTAL FINAL | 602 | CENTERPOINT ENERGY GAS TRANSMISSION | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2010-12-28 18:00 | 2010 |  |  | 35.246 | -92.8122 | 963249 | 2010-12-28 19:27 |  | NATURAL GAS |  | 31653 | 48 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2010-12-28 18:40 | 2011-01-07 16:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-12-28 18:00 | 2010-12-28 18:00 | ONSHORE | AR | 72823 | BLACKWELL | CONWAY | SURVEY STATION NO. | 140+86 | CEGT LINE BT-3 | SG 6160 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | IN OR SPANNING AN OPEN DITCH |  |  |  | YES | [6 empty] | YES | UNCASED | UNNAMED SLOUGH | 3 | BELOW WATER, PIPE ON OR ABOVE BOTTOM | [11 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 |  | 0.156 | 35000 | GRADE B | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | ASPHALT | [28 empty] | 1959 |  | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | EXTERNAL CORROSION | 17 | 6 |  | CLASS 1 LOCATION | NO |  | 117 |  | NO | NO | NO |  | 0 | 0 | 191 | 227.94148825608 | 125978 | 77666.0485436893 | 85000 | 101439.929328622 | 2500 | 2983.52733319476 | 28000 | 33415.5061317813 | $16,000 RELIGHT COST, $12,000 FOR KIEFNER AND ASSOCIATES ANALYSIS |  | 241669 | 143896.271307528 | 215732.952825543 | [8 empty] | 632 |  | 800 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | CHECK VALVE | 47520 | NO | [5 empty] | YES | GAS DELIVERED IN MID SECTION OF PIPELINE CAUSING FLOW DIRECTION ISSUES. | YES |  |  | YES |  | YES | GAS DELIVERED IN MID SECTION OF PIPELINE | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLERS DO NOT HAVE CONTROL OF THE LINE, THEY ONLY MONITOR IT FOR PRESSURE AND FLOW DATA. | [12 empty] | YES | 2 | 0 | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | YES | [7 empty] | YES | YES |  |  | NO | [11 empty] | YES | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | JIMMY CROSS | DOT WAIVER SPECIALIST | jimmy.cross@centerpointenergy.com | 318 429-3664 | 318 429-3927 |  |  |  | JOHNNY CAVITT | DOT COMPLIANCE MANAGER | 318 429-3660 | johnny.cavitt@centerpointenergy.com | ON 12/28/10 AT APPROXIMATELY 13:30 HRS. CEGT FIELD PERSONNEL WERE RAISING THE PRESSURE ON LINE BT-3 PER A REQUEST FROM SYSTEM CONTROL FROM 585 PSIG TO 685 PSIG. AT 17:00 HRS. 685 PSIG WAS OBTAINED. WHILE LETTING THE PRESSURE SETTLE OUT FROM LINE J TO LINE BT-3, SYSTEM CONTROL CALLED THE FIELD PERSONNEL AND ADVISED THAT PRESSURE WAS DROPPING FROM LINE BT-3 TO LINE B. THE FIELD PERSONNEL WENT TO CHECK THE BT-3 TO B DELIVERY JUNCTION AND DISCOVERED NO GAS AT THE JUNCTION. A LOCAL GAME AND FISH COMMISSION OFFICER CALLED AND REPORTED A BLOWOUT IN A CREEK BED IN ED GORDON WILDLIFE REFUGE ABOUT 1/2 MILE NORTH OF I-40 AT THE BLACKWELL EXIT AND GUIDED CEGT'S PERSONNEL TO THE LEAK LOCATION. AT 18:34 HRS. PIPELINE FIELD PERSONNEL ISOLATED LINE BT-3 BOTH UP AND DOWNSTREAM FROM THE RUPTURE SITE. THE RUPTURE SITE WAS MONITORED THROUGH THE NIGHT. ON THE MORNING OF 12/28/2011 CREWS ARRIVED ON SITE, WELDED CAPS ON EACH END OF THE RUPTURED PIPE AND RESTORED SERVICE ON THE PIPELINE AT A PRESSURE OF 200 PSIG. ON THURSDAY, 1/6/11 THE REPAIR CREW REPLACED 60 FEET OR PRE-TESTED PIPE AND THE TIE-INS WERE COMPLETED. THE PIPELINE WAS PRESSURED TO 548 PSIG, 80 % OF THE PREVIOUS OPERATING PRESSURE, UNTIL AN INVESTIGATION IS COMPLETED. THE PIPELINE WAS PUT BACK INTO SERVICE AT 16:00 HRS ON 01/07/2011. KIEFNER & ASSOCIATES, INC. REPORT CONCLUSION: THE FAILURE WAS CAUSED BY EXTERNAL CORROSION. THE EXTERNAL CORROSION HAD REDUCED THE PIPE WALL THICKNESS TO 0.010 INCH. THE REMAINING WALL THICKNESS FAILED BY DUCTILE TENSILE OVERLOAD RESULTING IN A RUPTURE MEASURING APPROXIMATELY 17 INCHES LONG. THE CAUSE OF THE EXTERNAL CORROSION COULD NOT BE CONCLUSIVELY IDENTIFIED, BUT IT DID NOT APPEAR TO HAVE BEEN CAUSED BY MICROBIOLOGICALLY INFLUENCED CORROSION. THE MECHANICAL PROPERTIES AND CHEMICAL COMPOSITION OF THE FAILED PIPE SPECIMEN MET THE REQUIREMENTS OF API 5L FOR THE PIPE GRADE AND VINTAGE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110011 | 15836 | 2011-02-01 09:24 | SUPPLEMENTAL FINAL | 19270 | TEXAS GAS TRANSMISSION LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2011-01-09 18:05 | 2011 |  |  | 32.6767 | -92.02 | 964142 | 2011-01-09 19:30 |  | NATURAL GAS |  | 0 | 6696 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | STATION WAS ALREADY IN BY-PASS MODE. NO HORSEPOWER WAS ON-LINE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-01-09 18:05 | 2011-01-09 18:25 | ONSHORE | LA | 71280 | STERLINGTON | OUCHITA | MILEPOST | 0 | GUTHRIE COMPRESSOR STATION | EIS-1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [8 empty] | CARBON STEEL |  | OTHER | [8 empty] | FALSE SIGNAL SENT TO ESD DEVICE DUE TO ICING. | CLASS 1 LOCATION | NO |  | 30 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 29529 | 19983.2131438721 | 0 | 0 | 542 | 634.174240880375 | 0 | 0 |  |  | 30071 | 21008.607150911 | 20617.3873847525 | [8 empty] | 760 |  | 810 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LOCAL WEATHER CONDITIONS WAS CAUSE OF THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | YES |  |  |  | YES | WINTER STORM - ICING | [301 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 270-688-6357 | 270-688-5871 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 270-688-6361 | jeff.mcmaine@bwpmlp.com | ON 01-09-2011 AT APPROXIMATELY 6:05 PM, AN ESD BLOWDOWN VALVE OPENED UNINTENTIONALLY DUE TO ICING OF THE CONTROL PILOT AND VALVE. THE VALVE VENTED FOR APPROXIMATELY 40 MINUTES AT 760 PSIG RESULTING IN AN ESTIMATED GAS LOSS OF 6,696 MCF. THE ON-DUTY EMPLOYEE MANULLY CLOSED THE VALVE. THE REPAIR WAS MADE BY DE-ICING THE VALVE AND INSTALLING A NEW PILOT CONTROL. THE PIPELINE SYSTEM WAS RETURNED TO NORMAL OPERATIONS. ADDED DATA TO PART E5.F AS REQUESTED BY PHMSA.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110012 | 16129 | 2011-02-02 11:01 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2011-01-04 07:50 | 2011 |  |  | 29.1709 | -90.7219 | 963666 | 2011-01-04 10:00 |  | NATURAL GAS |  | 1 | 966 | 4 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-01-13 15:00 | 2011-01-24 11:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-01-04 07:50 | 2011-01-04 11:00 | ONSHORE | LA | 70344 | CHAUVIN | TERREBONNE | SURVEY STATION NO. | 29597 | 523M-100 | 523M-101A | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 120 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 26 |  | 0.417 | 52000 | API 5L | DSAW |  | US STEEL | COAL TAR | [9 empty] | PIPE GIRTH WELD | [18 empty] | 1968 | 1968 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 621 |  | NO | NO | NO |  | 0 | 0 | 3864 | 4521.12410841655 | 4 | 2.70692717584369 | 709000 | 829574.791114734 | 50000 | 58503.1587528021 | 0 | 0 |  |  | 762868 | 409729.33421172 | 892601.780903128 | [8 empty] | 777 |  | 1200 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 95040 | NO |  |  |  | YES |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | BOEMRE |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO BREACH OF OPERATING PARAMETERS INCLUDING NO EXCEEDANCE OF MAOP. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | PINHOLE IN GIRTH WELD. |  |  |  |  | YES | NOT DETERMINED. | YES | [7 empty] | YES | GIRTH WELD AT 6 O'CLOCK POSITION. | YES | NO | NO | NO | [168 empty] | NO | [63 empty] | YES | 1968 | 1669 | NO | [13 empty] | NO | [63 empty] | ZACHARY RAGAIN | ENGINEER - PIPELINE | zachary_ragain@kindermorgan.com | 7134206633 |  |  |  |  | ZACHARY RAGAIN | ENGINEER - PIPELINE | 7134206633 | zachary_ragain@kindermorgan.com | FEDERAL AGENCY BOEMRE WAS FLYING PERSONNEL INTO SHORE FROM THE OCS AND NOTICED BUBBLES WITH ACCOMPANYING SHEEN IN THE VICINITY OF TENNESSEE GAS PIPELINE'S (TGP) 26" 523M-100 PIPELINE. BOEMRE CONTACTED THE NRC DUE TO THE SHEEN AND RECEIVED REPORT NUMBER 963608. UPON RECEIVING THE NRC REPORT, THE US COAST GUARD NOTIFIED TGP WHO INITIATED MEASURES TO CONTAIN THE SHEEN AND A SITE INVESTIGATION WITH DIVERS SINCE THE PIPE WAS UNDER 3 FEET OF WATER. VISUAL EXAMINATION REVEALED A PINHOLE LEAK IN A GIRTH WELD THAT WAS REPAIRED BY INSTALLING A CLAMP.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110015 | 16727 | 2011-02-08 16:43 | SUPPLEMENTAL FINAL | 602 | CENTERPOINT ENERGY GAS TRANSMISSION | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2011-01-11 17:30 | 2011 |  |  | 32.1445 | -94.1141 | 964351 | 2011-01-12 10:15 |  | NATURAL GAS |  | 52874 | 391 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-01-12 16:00 | 2011-01-12 22:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-01-12 13:25 | 2011-01-12 13:25 | ONSHORE | TX | 75639 | DEBERRY | PANOLA | SURVEY STATION NO. | 422+58 | CEGT LINE NT-1 | SG12902 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12.75 |  | 0.25 | 24000 | UNKNOWN | LAP WELDED |  | UNKNOWN | NONE | [28 empty] | 1944 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 185 |  | NO | NO | NO |  | 0 | 0 | 1818 | 2127.17485225188 | 245864 | 166383.985790409 | 40000 | 46802.5270022417 | 10000 | 11700.6317505604 | 12000 | 14040.7581006725 | PIPE LAB ANALYSIS |  | 309682 | 206773.834463834 | 241055.077496135 | [8 empty] | 295 |  | 500 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 21648 | NO | [5 empty] | YES | NO PIG TRAPS | YES |  | YES | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  | YES | THIS LEAK DID NOT OCCUR DUE TO CONTROLLER'S ACTIONS. | YES | YES | [7 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | THERMAL STRESS |  | YES |  |  |  | YES | EXTREME COLD - AXIAL STRESSES DUE TO TEMPERATURE CHANGES | [301 empty] | JIMMY CROSS | DOT WAIVER SPECIALIST | jimmy.cross@centerpointenergy.com | 318 429-3664 | 318 429-3927 |  |  |  | JOHNNY CAVITT | DOT COMPLIANCE MANAGER | 318 429-3660 | johnny.cavitt@centerpointenergy.com | ON 01/11/11 AT 17:30 A THIRD PARTY CALLED CEGT SYSTEM CONTROL AND REPORTED A PIPELINE BLOWOUT OFF OF FM-31 TRAVELING SOUTH ON FM-31 FROM DEBERRY, TX ON LEFT SIDE OF ROAD ABOUT 1 MILE NORTH OF FM-123. AT 17:35 CEGT SYSTEM CONTROL DISPATCHED A CEGT FIELD TECHNICIAN TO INVESTIGATE AND VERIFY THE LEAK. AT 20:05 CEGT TECHNICIANS REPORTED TO SYSTEM CONTROL THAT THE LEAK IS JUST OFF A DIRT ROAD WITH TWO ENTRANCES. THE LEAK IS IN THE WOODS WITH NO STRUCTURES IN THE AREA OR, BUT GAS WAS BLOWING ACROSS THE ROAD. IT WAS STILL NOT DETERMINED IF THE LEAK BELONG TO CEGT AND SINCE IT WAS DARK IT WAS DECIDED TO MONITOR THE LOCATION OVER NIGHT. AT 20:50 CEGT TECHNICIANS REPORTED TO SYSTEM CONTROL THAT BOTH ENTRANCES TO THE DIRT ROAD LEADING INTO THE LEAK ARE BLOCKED OFF AND WILL BE MANNED OVER NIGHT. ON 01/12/2011AT 07:53 SYSTEM CONTROL AND OPERATIONS HELD A CALL TO PLAN THE STEPS NEEDED TO DETERMINE IF THE LEAK WAS ON A CEGT PIPELINE. AT 10:15 SYSTEM CONTROL NOTIFIED NRC OF THE LEAK AND INDICATED CEGT WAS IN THE PROCESS OF DETERMINING IF THE LEAK WAS ON CEGT'S PIPELINE. AT 10:45 VALVES WERE SHUT ISOLATING THE PIPELINE SEGMENT WITH THE POSSIBLE LEAK AND IT WAS DETERMINED THAT THE LEAK WAS ON CEGT'S SYSTEM. VALVES WERE OPENED BACK UP, BUT THE PRESSURE WAS REDUCED FROM 300 LB. TO 250 LB. DUE TO A SIGNIFICANT LOAD IN SHREVEPORT AND THE SURROUNDING AREA, LOWERING THE PRESSURE WAS THE CHOSEN COURSE OF ACTION UNTIL NOTIFYING CUSTOMERS OF THE NEED TO REDUCE THEIR TAKES. CEGT CONTACTED THE LARGE INDUSTRIAL CUSTOMERS IN THE AREA TO REQUEST THEY REDUCE THEIR TAKES AND TO NOTIFY THEM THAT THEY MAY SEE LOWER PRESSURES BEGINNING AT 13:00. AT 16:00 THE LINE WAS BLOWN DOWN FROM 250# TO ZERO. A 26 FOOT SECTION OF THE PIPELINE WAS REMOVED AND REPLACED WITH TESTED EMERGENCY PIPE. AT 21:00 X-RAYS WERE COMPLETE THE LINE WAS PURGED AND PACKED. CONTROL OF THE PIPELINE WAS GIVEN BACK TO SYSTEM CONTROL AT 22:15. THE SECTION OF PIPE REMOVED THAT WAS REMOVED AND SENT TO KIEFNER & ASSOCIATES FOR METALLURGICAL ANALYSIS. THE CONCLUSION IS AS FOLLOWS: THE FAILURE WAS CAUSED BY A BUCKLE THAT FORMED IN THE PIPE WALL FROM COMPRESSIVE AXIAL OR BENDING STRESS ON THE PIPELINE. IT IS NOT KNOWN WHEN OR HOW THE BUCKLE WAS FORMED. THE FAILURE WAS CAUSED BY AXIAL TENSILE STRESS ACTING ON THE BUCKLED PIPE WHICH RESULTED IN A CIRCUMFERENTIALLY ORIENTED FRACTURE IN THE BOTTOM QUADRANT OF THE PIPE THAT EXTENDED FROM THE 3 TO 9 OCLOCK PIPE POSITIONS. BECAUSE THE FRACTURE PROPAGATED AFTER PENETRATING THE PIPE WALL, IT IS CLASSIFIED AS A RUPTURE RATHER THAN A LEAK, EVEN THOUGH THE PIPELINE WAS NOT COMPLETELY SEPARATED. THE BUCKLE WAS POSITIONED IN AN AREA OF REDUCED WALL THICKNESS NEAR THE END OF A JOINT OF PIPE A FEW INCHES AWAY FROM A GIRTH WELD. THE GIRTH WELD ITSELF WAS NOT INVOLVED IN THE FAILURE. THE CURVATURE STRAIN WITH THE BUCKLES PROFILE WAS DETERMINED TO BE 9 PERCENT USING THE TEMPLATE OVERLAY METHOD , WHICH EXCEEDS THE 6 PERCENT STRAIN SAFE LIMIT. THE PIPE JOINT WHICH CONTAINED THE FAILURE MET THE REQUIREMENTS OF THE APPROPRIATE EDITION OF API 5L. NO OTHER DEFECTS WERE PRESENT NEAR THE FAILURE ORIGIN. LAB ANALYSIS CONCLUDE THAT THE PIPE JOINT SPECIMEN CONTAINING THE FAILURE MET THE REQUIREMENTS OF THE APPROPRIATE EDITION OF API 5L. TENSILE TEST RESULTS SHOWED A YIELD STRENGTH OF 41.800 PSI/API 5L REQUIREMENTS OF 30,0000 MINIMUM. API STD 5L, TENTH EDITION, AUGUST 1944 FOR LAP-WELDED, BESSEMER LINE PIPE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110016 | 16830 | 2011-02-09 11:11 | SUPPLEMENTAL FINAL | 32249 | BLUEWATER GAS STORAGE, LLC | 231 W. MICHIGAN ST | MILWAUKEE | WI | 53203 | 2011-01-12 09:00 | 2011 |  |  | 42.8925 | -82.6681 | 964333 | 2011-01-12 09:30 |  | NATURAL GAS |  | 635 | 635 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-01-12 09:00 |  | YES |  |  |  | YES |  |  |  |  | YES | [6 empty] | 0 | 2011-01-12 09:00 | 2011-01-12 09:15 | ONSHORE | MI | 48063 | COLUMBUS | ST. CLAIR COUNTY | MILEPOST | COLUMBUS III | BLUEWATER GAS STORAGE | COLUMBUS III COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | OTHER | GAS PROCESSING EQUIPMENT |  |  | NO | [22 empty] | INTERSTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | OTHER | [37 empty] | DEHYDRATION UNIT HEAT EXCHANGER | 2005 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | ALUMINUM | RUPTURE |  |  |  |  | OTHER | RUPTURE IN THE HOT PASS OF THE WEST GAS/GAS EXCHANGER | 42 | 34 |  | CLASS 2 LOCATION | NO |  | 478 |  | NO | NO | NO |  | 5000 | 5850.31587528021 | 3500 | 4095.22111269615 | 0 | 0 | 3000000 | 3510189.52516813 | 5000 | 5850.31587528021 | 0 | 0 |  |  | 3013500 | 1618520.32810271 | 3525985.37803138 | [8 empty] | 1120 |  | 1200 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | OTHER | RELEASE RESULTING IN EXPLOSION/FIRE |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | [8 empty] | YES | 1 | 0 | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | GENERAL CORROSION | [5 empty] | YES | AQUEOUS CHLORIDES |  | YES | [6 empty] | YES | ALUMINUM PLATE FIN HEAT EXCHANGER | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [313 empty] | SHERYL NGUYEN | EHS COMPLIANCE SPECIALIST | snguyen@paalp.com | 713.993.5673 | 713.646.4310 |  |  |  | JORDAN R JANAK | DIRECTOR ENVIRONMENTAL REGULATOR COMPLIANCE | 713.993.5162 | jrjanak@paalp.com | THE BLUEWATER GAS STORAGE FACILITY IS A GAS STORAGE FACILITY IN A DEPLETED RESERVOIR. GAS IS INJECTED INTO THE STORAGE FIELD DURING THE SUMMER MONTHS AND TYPICALLY WITHDRAWN DURING THE WINTER MONTHS. DURING WITHDRAWAL, THE GAS HAS TO RUN THROUGH A JOULE-THOMSON (JT) PLANT IN ORDER TO LOWER THE BTU CONTENT OF THE GAS, BUT ALSO TO RECOVER NATURAL GAS LIQUIDS (NGL) FROM THE GAS STREAM. THE JT UNIT WAS THE LOCATION OF THE INCIDENT ON 1/12/11. AT APPROXIMATELY 9:00 AM ON 1/12/11, THERE WAS A RELEASE OF GAS, AN EXPLOSION AND A FIRE IN THE JT PLANT. WHILE THE EXACT CAUSE IS NOT YET KNOWN, IT APPEARS THAT THE GAS RELEASE OCCURRED FROM A RUPTURE IN THE HOT PASS OF THE WEST GAS/GAS EXCHANGER (CALLED THE JT TOWER AT THE FACILITY). THE RESULT OF THE GAS RELEASE WAS A LARGE EXPLOSION AND FIRE. THE FIRE CONSUMED THE GAS FROM THE RELEASE (ESTIMATED TIME WAS SEVERAL MINUTES), AND THEN SOME FLAMMABLE MATERIAL (PRIMARILY INSULATION) CONTINUED TO BURN FOR SOME TIME. THERE WAS CONSIDERABLE DAMAGE TO THE JT FACILITY (BOTH TRAINS), AND THE ENTIRE STORAGE FACILITY CEASED OPERATION. SUPPLEMENTAL NARRATIVE: AFTER A THOROUGH INVESTIGATION, IT HAS BEEN DETERMINED THAT THE CAUSE OF THIS RELEASE WAS CORROSION OF THE ALUMINUM FINS OR PLATES OF THE GAS/GAS EXCHANGER DUE TO AQUEOUS CHLORIDES OR ACIDIC COMPOUNDS IN THE GLYCOL STREAM, RESULTING IN THE FAILURE OF THE EXCHANGER. THE CORRECTIVE ACTIONS TAKEN TO ENSURE SAFE OPERATION OF THE JT PLANT IN THE FUTURE ARE: - THE ALUMINUM PLATE FIN WILL BE REPLACED WITH A CARBON STEEL SHELL AND TUBE EXCHANGER AS THE GAS/GAS EXCHANGER. THE SHELL AND TUBE EXCHANGERS ARE MUCH LESS PRONE TO CATASTROPHIC CORROSION ISSUES DUE TO THE METALLURGY AND PHYSICAL DESIGN OF THE SHELL AND TUBE. THE SHELL AND TUBE EXCHANGER HAS A HEAD THAT CAN BE EASILY REMOVED FOR INSPECTION OR CLEANING. - A NEW INLET FILTER COALESCER WILL BE USED TO REMOVE MORE OF THE PARTICULATE MATTER AND CHLORIDES IN THE INLET GAS. THE FILTER IS A FULL-FLOW FILTER, HANDLING THE ENTIRE STREAM UPSTREAM OF THE GAS/GAS EXCHANGER. - THE GLYCOL WILL ALSO BE TESTED ON A MORE FREQUENT BASIS THAN PREVIOUSLY. THE ANALYSIS WILL CHECK FOR CHLORIDE CONCENTRATION, IRON, SULFUR, CALCIUM, PH, GLYCOL STRENGTH AND OTHER CONTAMINANTS IN GLYCOL. IN ADDITION, THE ENTIRE JT PLANT OPERATION HAS BEEN MOVED TO A SAFER LOCATION AND ALL EXISTING EQUIPMENT WAS VISUALLY INSPECTED INTERNALLY AND EXTERNALLY AND WAS DEEMED SAFE TO PUT BACK INTO OPERATION. THE ENTIRE GLYCOL REGENERATION SYSTEM WAS ALSO INSPECTED AND CLEANED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110017 | 15287 | 2011-02-10 11:24 | SUPPLEMENTAL FINAL | 12576 | CENTERPOINT ENERGY - MISSISSIPPI RIVER GAS TRANSMISSION CORP | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2011-01-26 12:30 | 2011 |  |  | 32.5323 | -91.5766 | 965761 | 2011-01-26 15:10 |  | NATURAL GAS |  | 841 | 6056 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-01-26 17:38 | 2011-01-27 08:19 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-01-26 12:30 | 2011-01-26 13:24 | ONSHORE | LA | 71220 | BASTROP | MOREHOUSE | SURVEY STATION NO. | 705+69 | MRT LINE M/L-2 | SG12176 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 22 |  | 0.25 | 45000 | X-45 | FLASH WELDED |  | AO SMITH | OTHER | MASTIC | [27 empty] | 1947 | 1947 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 407 |  | NO | NO | NO |  | 0 | 0 | 27252 | 31886.5616466273 | 3785 | 2561.4298401421 | 85000 | 99455.3698797636 | 0 | 0 | 12000 | 14040.7581006725 | LAB ANALYSIS |  | 128037 | 69390.0413492017 | 147944.119467205 | [8 empty] | 679 |  | 720 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 52800 | YES | [7 empty] | YES |  | YES | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [64 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | [10 empty] | YES |  |  |  |  | YES | [6 empty] | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO |  | PREVIOUS DAMAGE | [121 empty] | YES | YES |  |  | YES |  |  |  | 2005 | [31 empty] | 2005 | [22 empty] | NO | YES | 1989 | 933 | NO | [13 empty] | NO | [63 empty] | JIMMY CROSS | DOT WAIVER SPECIALIST | jimmy.cross@centerpointenergy.com | 318 429-3664 | 318 429-3927 |  |  |  | JOHNNY CAVITT | DOT COMPLIANCE MANAGER | 318 429-3660 | johnny.cavitt@centerpointenergy.com | ON 01/26/2011 AT 12:30 A THIRD PARTY WORKING NEAR MRT LINE ML-2 CALLED CEGT SYSTEM CONTROL AND REPORTED A LEAK NEAR MILE POST 13. SYSTEM CONTROL NOTIFIED AN AREA PIPELINE TECHNICIAN. AT 12:39 THE TECHNICIAN CONTACTED THE THIRD PARTY THAT REPORTED THE LEAK TO GET FURTHER DETAILS. AT 12:45 HE THEN CONTACTED TWO ADDITIONAL TECHNICIANS TO ASSIST IN INVESTIGATING THE LEAK. THEY ARRIVED AT THE LEAK SITE AT 13:24 AND MADE THE DETERMINATION THAT THERE WAS A LEAK ON ML-2. A TECHNICIAN AT THE SCENE CALLED SYSTEM CONTROL TO CONFIRM THE LEAK AT 13:38. AT 13:40 TECHNICIANS ON LOCATION CONTACTED TECHNICIANS NEAR MILE POST 23 AND HAD THEM GO TO THE VALVE TO AWAIT NOTIFICATION FROM SYSTEM CONTROL TO ISOLATE THE LEAK. TECHNICIANS AT THE SITE OF THE LEAK SECURED THE AREA AND STOOD BY AWAITING INSTRUCTIONS FROM SYSTEM CONTROL. AT 15:45 TECHNICIANS WERE INSTRUCTED TO SETUP VALVES TO CROSS OVER GAS FROM ML-2 TO ML-3 AND THEN CLOSE THE VALVE AT MILE POST 23. AT 15:46 THE TECHNICIANS AT MILE POST 13 WAS INSTRUCTED TO PUT VALVES IN SEQUENCE TO CROSS OVER GAS FROM ML-2 TO ML-3 TO ISOLATE THE LEAK. AT 16:15 THE TECHNICIANS REDUCED THE FLOW ON ML-3 TO PULL DOWN ML-2 PRESSURE AND THEN CLOSED THE VALVE AT MILE POST 13. TECHNICIANS THEN BEGAN BLOWING DOWN ML-2 AT 17:24 PM. AT 17:38 ALL VALVES WERE LOCKED AND TAGGED. AT 18:25 THEY HAD THE PRESSURE DOWN AND REPAIR CONTRACTORS MADE THE CUT AND SPOOLED IN A JOINT OF PIPE. ON JANUARY 27TH AT 2:40 WELD X-RAYS BEGAN. THE X-RAYS RESULTS WERE GOOD AND SYSTEM CONTROL WAS NOTIFIED THAT THE REPAIR CREW WAS READY TO PURGE AND PACK. SYSTEM CONTROL HAD ARRANGED FOR ALTERNATIVE GAS SUPPLIES AND ADVISED THE REPAIR CREW TO HOLD OFF ON THE PURGE UNTIL 6:30. THE CREW RETURNED TO THE REPAIR SITE AT 6:15 AND AT 6:34 BEGAN THE PURGE. THE PURGE WAS COMPLETED AT 7:04 AND THE PACK BEGAN AT 7:05. THE PIPELINE EQUALIZED AT 8:19 AT 600#. ALL VALVES WERE PUT BACK IN THE NORMAL OPERATING POSITIONS AND CONTROL OF THE PIPELINE WAS TURNED OVER TO SYSTEM CONTROL AT 8:40. THE SECTION OF PIPE REMOVED WAS SENT TO KIEFNER & ASSOCIATES FOR METALLURGICAL ANALYSIS. THE CONCLUSION IS AS FOLLOWS: THE LEAK WAS ATTRIBUTABLE TO PREVIOUS MECHANICAL DAMAGE. THE LEAK ORIGINATED AT A CRACK MEASURING APPROXIMATELY 5 1/2 INCHES LONG LOCATED WITHIN A 9-INCH LONG GOUGE. THE GOUGE WAS ORIENTED AT APPROXIMATELY 45 DEGREES TO THE AXIS OF THE PIPE. THE DENT OR DEFORMATION ASSOCIATED WITH THE GOUGE WAS MINOR, MEASURING LESS THAN 1% OF THE PIPE OD. THE CRACK LIKELY GREW THROUGH THE PIPE WALL THICKNESS BY FATIGUE IN RESPONSE TO PRESSURE-CYCLE INDUCED FATIGUE. THE MECHANICAL PROPERTIES AND CHEMICAL COMPOSITION OF THE PIPE SPECIMEN MET THE REQUIREMENTS OF API SPECIFICATION 5LX APPROPRIATE TO THE PIPE VINTAGE AND GRADE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110018 | 16138 | 2011-02-17 10:58 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2011-01-25 13:20 | 2011 |  |  | 29.1422 | -90.7307 | 965658 | 2011-01-25 13:50 |  | NATURAL GAS |  | 1 | 17281 | 20 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-01-25 16:30 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-01-25 13:20 | 2011-01-25 18:00 | ONSHORE | LA | 70344 | CHAUVIN | TERREBONNE | SURVEY STATION NO. | 40383 | 523M-100 | 523M-101A | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 96 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 26 |  | 0.417 | 52000 | API 5L | DSAW |  | US STEEL | COAL TAR | [9 empty] | PIPE GIRTH WELD | [18 empty] | 1968 | 1968 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 621 |  | NO | NO | NO |  | 0 | 0 | 77804 | 91035.5952720603 | 4 | 2.70692717584369 | 616933 | 721850.584776849 | 500000 | 585031.587528021 | 0 | 0 | NONE |  | 1194741 | 641683.948334402 | 1397920.47450411 | [8 empty] | 833 |  | 1200 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 163680 | NO |  |  |  | YES |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | AIR PATROL |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO BREACH OF OPERATING PARAMETERS INCLUDING NO EXCEEDANCE OF MAOP. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN | [5 empty] | YES | NOT DETERMINED. PIPELINE IS SCHEDULED FOR ABANDONMENT AND WILL NOT BE PLACED BACK INTO SERVICE. HENCE, THE PIPE WAS NOT CUT OPEN TO ALLOW ANALYSIS. | YES |  | YES | PIPELINE IS SCHEDULED FOR ABANDONMENT AND WILL NOT BE PLACED BACK INTO SERVICE. HENCE, THE PIPE WAS NOT CUT OPEN TO ALLOW ANALYSIS. SUSPICION OF INTERNAL CORROSION IS BASED ON THE PIPE'S HISTORY. |  |  |  |  | YES | GIRTH WELD (PINHOLE). | YES | YES | NO | NO | [168 empty] | NO | [63 empty] | YES | 1968 | 1669 | NO | [13 empty] | NO | [63 empty] | ZACHARY RAGAIN | ENGINEER - PIPELINE | zachary_ragain@kindermorgan.com | 7134206633 | 7134206633 |  |  |  | ZACHARY RAGAIN | ENGINEER - PIPELINE | 7134206633 | zachary_ragain@kindermorgan.com | COMPANY PERSONNEL FLYING ROUTINE AERIAL PATROL NOTICED BUBBLES WITH AN ACCOMPANYING SHEEN IN THE VICINITY OF TENNESSEE GAS PIPELINE'S (TGP) 26" 523M-100 PIPELINE. THE PATROLLING EMPLOYEE CONTACTED LOCAL GROUND OPERATING PERSONNEL WHO MOBILIZED TO CLOSE VALVES AND INVESTIGATE THE REPORT. A PINHOLE LEAK WAS FOUND IN A GIRTH WELD WHICH WAS REPAIRED BY INSTALLING A CLAMP. THIS PIPELINE IS SCHEDULED FOR ABANDONMENT AND WILL NOT BE PLACED BACK INTO SERVICE. YEAR OF PIPE MANUFACTURE IS ASSUMED TO BE COMMENSURATE WITH YEAR OF INSTALLATION
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110019 | 15931 | 2011-02-17 11:28 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | TX | 77002 | 2011-01-30 08:09 | 2011 |  |  | 40.6091 | -93.5537 | 966102 | 2011-01-30 18:09 |  | NATURAL GAS |  | 32600 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-01-30 08:09 | 2011-01-30 11:39 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-01-30 08:09 | 2011-01-30 08:55 | ONSHORE | IA | 50147 | LINEVILLE | WAYNE | MILEPOST | 35 | LINEVILLE COMPRESSOR STATION | LINE 100 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | FIRE DETECTION UNIT, SUCTION VALVE, DISC | 1949 |  | CARBON STEEL |  | OTHER | [8 empty] | A MINOR FIRE CAUSED A STATION EMERGENCY SHUTDOWN. A STATION DISCHARGE BLOCK VALVE AND A SUCTION BLOCK VALVE FAILED TO CLOSE COMPLETELY CAUSING AN EXCESSIVE AMOUNT OF GAS TO BE VENTED. STATION BYPASS VALVE FAILED TO OPEN AUTOMATICALLY. BLOWDOWN VALVES WERE CLOSED MANUALLY TO STOP THE GAS FROM VENTING. | CLASS 1 LOCATION | NO |  | 506 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 195600 | 132368.738898757 | 5000 | 5850.31587528021 | 10000 | 11700.6317505604 | 0 | 0 |  |  | 210600 | 145289.030134571 | 149919.686524597 | [8 empty] | 925 |  | 975 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | INCORRECT OPERATION AS EQUIPMENT FAILURE OCCURRED AS A RESULT OF FAILURE TO MAINTAIN THE VALVES. |  |  | YES |  |  | NORMAL OPERATING CONDITIONS | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | LOUIS SALINAS | COMPLIANCE ENGINEER | louis_salinas@transcanada.com | 832-320-5305 | 832-320-6305 |  |  |  | LOUIS SALINAS | COMPLIANCE ENGINEER | 832-320-5305 | louis_salinas@transcanda.com | STATION ESD, CAUSED BY FIRE DETECTION ON UNIT 705. REASON FOR FIRE WAS FOUND TO BE A 3/8" OIL LINE BROKEN ON # 11 POWER CYLINDER SPRAYING OIL ON EXHAUST HEADER. STATION DISCHARGE VALVE 34-48 DID NOT FULLY CLOSE. ALSO, STATION SUCTION VALVE 34-25 DID NOT FULLY CLOSE. THIS CAUSED GAS TO VENT OUT OF BLOWDOWN AND ESTIMATED 32.6 MMCF WAS RELEASED. EVENT SET OFF THE UV DETECTORS CAUSED BY FLASH FIRE. STATION DISCHARGE VALVE DID NOT CLOSE COMPLETELY AND INDICATORS MAY NOT BE ACCURATE FOR THIS VALVE POSITIONING IN THE OPEN POSITION. STEPS TAKEN TO RETURN TO NORMAL OPERATION: VERIFIED WHAT UNIT CAUSED THE ESD. BLOWDOWN VALVE F WAS CLOSED. THIS STOPPED THE VENTING OF THE GAS. BY-PASS 10 AND 20 WERE OPENED MANUALLY TO BYPASS THE STATION. YARD VALVES REPOSITIONED TO NORMAL IN THE STATION YARD. UNITS WERE VERIFIED FOR START SEQUENCE. UNIT 705 THAT CAUSED THE ESD, WAS REPAIRED AND STARTED AS WELL. THERE ARE TWO MAIN LINES COMING INTO THE STATION (24" 100 AND 24 "1-100) AND THREE MAIN LINES LEAVING THE STATION (24" 100, 24" 1-100, AND 30" 2-100). VALVE 100-34-10, STATION BY-PASS VALVE (MAIN LINE VALVE) ON 100 LINE WILL OPEN WITH SIGNAL FROM STATION PROCESSOR BASED PRESSURE DIFFERENTIAL ACROSS VALVE VALVE 100-34-20, STATION BY-PASS VALVE (MAIN LINE VALVE) ON 1-100 LINE WILL OPEN WITH SIGNAL FROM STATION PROCESSOR BASED PRESSURE DIFFERENTIAL ACROSS VALVE VALVE 100-34-E, SUCTION VENT VALVE WILL OPEN ON LOSS OF PILOT PRESSURE VALVE 100-34-F, SUCTION VENT VALVE WILL OPEN ON LOSS OF PILOT PRESSURE VALVE 100-34-15, SUCTION BLOCK VALVE OFF OF 100 LINE WILL CLOSE ON LOSS OF PILOT PRESSURE VALVE 100-34-25, SUCTION BLOCK VALVE OFF OF 1-100 LINE WILL CLOSE ON LOSS OF PILOT PRESSURE VALVE 100-34-16, DISCHARGE BLOCK VALVE OFF OF 100 LINE WILL CLOSE ON LOSS OF PILOT PRESSURE VALVE 100-34-26, DISCHARGE BLOCK VALVE OFF OF 1-100 LINE WILL CLOSE ON LOSS OF PILOT PRESSURE VALVE 100-34-48, DISCHARGE BLOCK VALVE OFF OF 2-100 LINE WILL CLOSE ON LOSS OF PILOT PRESSURE
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110020 | 15837 | 2011-02-22 16:26 | SUPPLEMENTAL FINAL | 19270 | TEXAS GAS TRANSMISSION LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2011-02-04 05:30 | 2011 |  |  | 32.96 | -92.52 | 966539 | 2011-02-04 07:45 |  | NATURAL GAS |  | 13110 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE FACILITIES PERFORMED AS DESIGNED. NO SHUTDOWN WAS NECESSARY. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-02-04 05:30 | 2011-02-04 06:01 | ONSHORE | LA | 71418 | COLUMBIA | CALDWELL PARISH | MILEPOST | 59.4155 | COLUMBIA COMPRESSOR STATION | BASTROP-EUNICE SYSTEM | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1956 |  | CARBON STEEL |  | OTHER | [8 empty] | THE PILOT CONTROL FROZE AND ACTIVATED THE BLOWDOWN VALVE. | CLASS 1 LOCATION | NO |  | 511 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 29414 | 19905.3889875666 | 415 | 485.576217648257 | 320 | 374.420216017933 | 0 | 0 |  |  | 30149 | 21031.5816595424 | 20765.3854212328 | [8 empty] | 725 |  | 810 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LOCAL WEATHER CONDITIONS WERE THE CAUSE OF THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | YES |  |  |  | YES | WINTER STORM - ICING | [301 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 270-688-6357 | 270-688-5871 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 270-688-6361 | jeff.mcmaine@bwpmlp.com | ON 02-04-2011, AT APPROXIMATELY 5:30 AM, AN ESD BLOW DOWN VALVE OPENED UNINTENTIONALLY DUE TO ICING OF THE PILOT CONTROL AND VALVE. THE VALVE VENTED FOR APPROXIMATLEY 31 MINUTES. AN INSPECTION OF THE VALVE WAS IMMEDIATLY DONE AND IT WAS DETERMINED THE PILOT HAD FROZEN. WE WERE EXPERIENCING AN ICE STORM WHEN THIS OCCURRED. THE PRESSURE ON THE DISCHARGE HEADER WAS 725 PSIG. THE MAOP IS 810 PSIG AT THIS LOCATION. THE PILOT WAS REPLACED AND THE PIPELINE SYSTEM WAS RETURNED TO NORMAL OPERATIONS. ADDED DATA TO PART E5.F AS REQUESTED BY PHMSA.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110021 | 16020 | 2011-02-23 14:23 | SUPPLEMENTAL FINAL | 5304 | FLORIDA GAS TRANSMISSION CO | 5444 WESTHEIMER ROAD | HOUSTON | TX | 77056 | 2011-01-24 22:30 | 2011 |  |  | 30.8518 | -89.689 | 965754 | 2011-01-26 02:23 |  | NATURAL GAS |  | 53 | 11966 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-01-25 02:05 | 2011-02-22 11:49 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-01-24 22:30 | 2011-01-24 22:30 | ONSHORE | MS | 39470-6006 | POPLARVILLE | PEARL RIVER | MILEPOST | MILEPOST 88.6 | 100 LINE | LAMEA-9 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 |  | 0.375 | 52000 | API 5LX 52 | LONGITUDINAL ERW - LOW FREQUENCY |  | REPUBLIC | FIELD APPLIED EPOXY | [28 empty] | 1959 | 1957 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 517 |  | NO | NO | NO |  | 0 | 0 | 51569 | 60338.987874465 | 228 | 154.294849023091 | 441616 | 516718.619115549 | 0 | 0 | 0 | 0 |  |  | 493413 | 265044.632806977 | 577211.901839037 | [8 empty] | 717 |  | 975 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | MANUAL | 62445 | NO |  | YES | [5 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS DISCOVERED BY EMPLOYEE IN THE FIELD (BUBBLES IN A POOL OF WATER). VOLUME LOSS WAS SO SMALL AS TO NOT BE DETECTABLE BY SCADA. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [8 empty] | YES | UNKNOWN UNTIL LABORATORY ANALYSIS IS COMEPLETE | [12 empty] | YES | [63 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | OPERATOR EMPLOYEES WERE CONDUCTING WORK IN THE AREA OF THE LEAK. EMPLOYEES WERE AROUND THIS LOCATION AT 6:00 PM THAT DAY AND DID NOT NOTICE ANY ISSUES. WHEN THEY RETURNED AT 10:30 PM THEY FOUND BUBBLES IN STANDING WATER OVER THE LINE IN THE VICINITY OF A CROSSOVER VALVE. EXCAVATION AND EXAMINATION REVEALED THAT GAS WAS ESCAPING BETWEEN THE PIPE AND THE REINFORCING SLEEVE FOR THE CROSSOVER TAP AT ABOUT THE 2 O'CLOCK POSITION. WHEN THE SECTION WAS REMOVED A CRACK WAS FOUND IN THE MAINLINE PIPE IN THE VICINITY OF THE TAP FILET WELD. LABORATORY FINDINGS ' THE FAILURE INITIATED AT AN IMPERFECTION AT THE TOE OF THE FILLET WELD THAT CONNECTED THE BRANCH TO THE PIPELINE ' UNDERCUT AND OTHER IMPERFECTIONS WERE OBSERVED AT THE TOE OF THE WELD REMOTE FROM THE FAILURE ' THE FRACTURE INITIATED AT A TOE CRACK AND FAILED AS A RESULT OF AN OVERLOAD DUE TO OUTSIDE FORCES ' HARDNESS WAS LOW **THIS REPORT IS BEING SUBMITTED IN RESPONSE TO PHMSA'S REQUEST, (DOCKET ID PHMSA-2013-0028), FOR SUPPLEMENTAL REPORTS FROM OPERATORS WHO SUBMITTED REPORTS FOR INCIDENTS OCCURRING AFTER JANUARY 1, 2010, WITH ANY OF THE FOLLOWING: (1) ``PIPE GIRTH WELD'' WAS SELECTED AS THE ``ITEM INVOLVED IN INCIDENT'' IN PART C3 OF THE REPORT. THE REVISED REPORT COLLECTS DATA ABOUT THE PIPE ADJACENT TO THE GIRTH WELD. (2) ``FUNCTION OF PIPELINE SYSTEM'' IS NULL IN PART E5F OF THE REPORT. THE REVISED REPORT COLLECTS THE FUNCTION OF THE PIPELINE SYSTEM FOR ALL INCIDENTS.** THIS SUPPLEMENTAL REPORT IS TO ACKNOWLEDGE THAT THE TWO RELEVANT SECTIONS IN PHMSA'S REQUEST HAVE BEEN REVIEWED AND NO FURTHER ACTIONS WERE NEEDED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110022 | 16142 | 2011-02-24 14:44 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2011-01-28 08:20 | 2011 |  |  | 28.2844 | -91.4275 | 965922 | 2011-01-28 09:04 |  | NATURAL GAS |  | 1 | 33707 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-01-28 16:00 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-01-28 08:20 | 2011-01-28 14:00 | OFFSHORE | [28 empty] | 244 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EUGENE ISLAND | 321 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | WELD/FUSION |  | 30 |  | 0.526 | 60000 | API 5LX | DSAW |  | BETHLEHEM | COAL TAR | [9 empty] | PIPE GIRTH WELD | [18 empty] | 1975 | 1974 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 732 |  | NO | NO | NO |  | 0 | 0 | 134828 | 157757.277766456 | 4 | 2.70692717584369 | 647500 | 757615.905848787 | 50000 | 58503.1587528021 | 0 | 0 |  |  | 832332 | 447037.745053375 | 973879.049295221 | [8 empty] | 900 |  | 1250 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 168960 | NO | [5 empty] | YES | ALL FACILITIES SUBSEA; NO ABOVE SURFACE LAUNCHERS AND RECEIVERS. | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | ANOTHER OPERATOR DISCOVERED BUBBLES WHILE IN ROUTE TO LAND AND PHONED NRC |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WERE NO ABNORMAL PRESSURE CONCERNS. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN | [5 empty] | YES | NOT DETERMINED BUT INTERNAL CORROSION IS SUSPECTED. DIVER OBSERVATION ONLY. WILL NOT BE DETERMINED AS PIPELINE REMAINS OUT OF SERVICE AND WILL BE ABANDONED | YES | [7 empty] | YES | GIRTH WELD IN VICINITY OF 4 O'CLOCK POSITION ON PIPE. | YES | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | ZACHARY RAGAIN | ENGINEER - PIPELINE | zachary_ragain@kindermorgan.com | 7134206633 |  |  |  |  | ZACHARY RAGAIN | ENGINEER - PIPELINE | 7134206633 | zachay_ragain@kindermorgan.com | TENNESSEE GAS PIPELINE (TGP) WAS NOTIFIED BY THE PHMSA SOUTHWEST REGION OF A 15' DIAMETER RING OF BUBBLES IN THE VICINITY OF ITS 30 INCH 523M-2300 PIPELINE ON THE OCS IN EUGENE ISLAND BLOCK 321. WHEN THE WEATHER ALLOWED FOR A HELICOPTER FLIGHT OFFSHORE TO INVESTIGATE, IT WAS DETERMINED THAT THIS WAS TGP'S PIPELINE WHEREUPON TGP REPORTED TO THE NRC. A REPAIR CLAMP HAS BEEN INSTALLED BUT THE LINE WILL NOT BE PLACED BACK INTO SERVICE, BEING SLATED FOR ABANDONMENT. THE CAUSE OF THE LEAK IS SUSPECTED TO BE INTERNAL CORROSION BASED ON THE LINE'S HISTORY AND THE ORIENTATION OF THE LEAK.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110023 | 30233 | 2011-01-06 10:09 | SUPPLEMENTAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2010-12-10 15:55 | 2010 |  |  | 29.3117 | -88.8302 | 961947 | 2010-12-10 16:26 |  | NATURAL GAS |  | 20 | 244 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | PRESSURE WAS LOWERED SUFFICIENTLY TO ALLOW FOR REPAIR. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2010-12-10 15:55 | 2010-12-10 15:55 | OFFSHORE | [28 empty] | 100 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | MAIN PASS | 140 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | VALVE | [31 empty] | MAINLINE | BALL |  | CAMERON |  |  |  | 1972 | 1972 | CARBON STEEL |  | LEAK |  |  | OTHER | BODY BLEED | [5 empty] | CLASS 1 LOCATION | NO |  | 335 |  | NO | NO | NO |  | 0 | 0 | 976 | 1164.76907087924 | 80 | 49.3203883495146 | 200000 | 238682.186655581 | 0 | 0 | 0 | 0 |  |  | 201056 | 110147.214166026 | 239896.27611481 | [8 empty] | 808 |  | 1200 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 89854 | NO | YES |  |  |  |  | YES | SUBSEA TIE-IN ASSEMBLIES | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | MINOR LEAK AND OPERATING PRESSURES WERE NOT A FACTOR. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | VALVE BODY BLEED LEAKED. | [15 empty] | YES | BODY BLEED SHOULD HAVE BEEN REPLACED WITH A PLUG AT INSTALLATION. | [161 empty] | KENNETH C PETERS | SENIOR ENGINEER - CODES STANDARDS | ken_peters@kindermorgan.com | 2053257554 | 2053253729 |  |  |  | JAIME HERNANDEZ | DIRECTOR - CODES STANDARDS | 7134209443 | jaime_hernandez@kindermorgan.com | A LEAK WAS IDENTIFIED ON SOUTHERN NATURAL GAS (SNG) COMPANY'S 14" MAIN PASS 107 PIPELINE IN THE GULF OF MEXICO, OUTER CONTINENTAL SHELF. THE LEAK WAS DETERMINED TO BE FROM A BODY BLEED, WHICH SHOULD HAVE BEEN REPLACED WITH A PLUG AT INSTALLATION, ON A 14" CAMERON BALL VALVE. THE BODY BLEED WAS REPLACED WITH A THREADED PLUG AND THE PIPELINE RESUMED NORMAL SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110024 | 15189 | 2011-03-02 09:27 | SUPPLEMENTAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 STATE ROUTE 56; BOX 20010 | OWENSBORO | KY | 42301 | 2011-02-10 23:40 | 2011 |  |  | 38.1724 | -95.2995 | 967148 | 2011-02-11 01:31 |  | NATURAL GAS |  | 36873 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | [7 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-02-10 23:40 | 2011-02-11 00:10 | ONSHORE | KS | 66091-3133 | WELDA | ANDERSON | MILEPOST | STATION #5411 | SOUTHERN STAR CENTRAL GAS PIPELINE | WELDA STATION YARD | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | REGULATOR/CONTROL VALVE | [38 empty] | 1946 |  | CARBON STEEL |  | OTHER | [8 empty] | EQUIPMENT MALFUNCTION | CLASS 1 LOCATION | NO |  | 363 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 146202 | 98939.541740675 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 146202 | 102575.115452931 | 98939.541740675 | [8 empty] | 630 |  | 690 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL |  | 3 | NO | [5 empty] | YES | STATION YARD PIPING AND VALVES | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | EXTREME COLD TEMPERATURES WITH A MIXTURRE OF MOISTURE, OIL AND DIRT IN THE PILOT | [161 empty] | MITCH JACKSON | PIPELINE SAFETY SPECIALIST | mitch.jackson@sscgp.com | 270-852-4437 | 270-852-5016 |  |  |  | DAVID SINCLAIR | PIPELINE COMPLIANCE MANAGER | 270-852-4424 | david.l.sinclair@sscgp.com | AT 22:40 ON 2/10/2011 GAS CONTROL SAW PRESSURE DROPPING ON THE OTTAWA 20" (LINE DS) AND THE GRABHAM-WELDA 30" (LINE D). LINE PRESSURE BEFORE THE LOSS WAS 632 PSIG, WITH AN MAOP OF 690 PSIG. GAS CONTROL CONTACTED DISTRICT PERSONNEL AT 22:50 TO GO TO WELDA STATION TO INVESTIGATE. DISTRICT OPERATORS CALLED GAS CONTROL AT 00:10 ON 02/11/2011 AND ASKED THAT THEY SHUT GATE #7. IMMEDIATELY THE GRABHAM-WELDA 30" STARTED GAINING PRESSURE SO THEY KNEW THE PROBLEM WAS ON THE OTTAWA 20". UPON ARRIVAL AT WELDA STATION DISTRICT OPERATORS HEARD THE R.V. BLOWING. KNOWING THE PRESSURE WAS BELOW MAOP THEY SHUT THE VALVE BELOW THE R.V. WHICH SHUT OFF THE BLOWING GAS AT APPROXIMATELY 01:25 ON 02/11/2011. THE R.V. WAS THAWED OUT WHICH ALLOWED IT TO RESEAL AND THEN THE VALVE WAS OPENED PUTTING THE R.V. BACK INTO SERVICE. THE SET POINT FOR THE R.V. WAS TESTED AND THE R.V. HAD ALL MOISTURE AND OIL BLOWN OUT FROM THE VENT ON THE PILOT. THE PILOT WAS REMOVED AND TAKEN TO THE SHOP TO CLEAN. THE PILOT WAS TAKEN APART AND FOUND MOISTURE, OIL AND DIRT INSIDE THE PILOT. THE PILOT WAS CLEANED AND PUT BACK INTO SERVICE AND THE SET POINT WAS AGAIN CHECKED AND ADJUSTED TO 690 PSIG.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110025 | 15851 | 2011-03-04 09:48 | SUPPLEMENTAL FINAL | 30769 | MISSOURI GAS ENERGY | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2011-02-02 13:52 | 2011 |  |  | 38.9306 | -94.508 | 966410 | 2011-02-02 17:55 |  | NATURAL GAS |  | 3913 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | PRESSURE WAS REDUCED, LEAK WAS MADE SAFE AND REPAIRS WERE MADE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 10 | 2011-02-02 13:52 | 2011-02-02 14:25 | ONSHORE | MO | 64134 | KANSAS CITY | JACKSON | SURVEY STATION NO. | 4+92 | MAYFAIR 16" EAST | 107TH & BLUE RIDGE BLVD. | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 108 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.25 | 35000 | API 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1948 | 1948 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 41 | 0.5 |  | CLASS 3 LOCATION | YES | METHOD1 | 175 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 31042 | 21007.108348135 | 0 | 0 | 40360 | 47223.7497452619 | 0 | 0 |  |  | 71402 | 43455.9703088458 | 68230.8580933969 | [8 empty] | 222 |  | 250 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 9280 | NO | YES |  | YES | YES |  |  |  | YES |  | YES | YES |  |  |  | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SYSTEM PRESSURES WERE OPERATING BELOW SYSTEM MAOP. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [52 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | SUBSIDENCE |  |  |  |  | NO | [306 empty] | RAYMOND D. WILSON | GENERAL MANAGER ENGINEERING | ray.wilson@sug.com | 816-360-5893 | 816-360-5569 |  |  |  | STEVE HOLCOMB | VICE PRESIDENT FIELD OPERATIONS | 816-360-5605 | steve.holcomb@sug.com | THE 16" STEEL GAS MAIN INCURRED A PARTIAL CIRCUMFERENTIAL BREAK. PRESSURE & MEASUREMENT DEPARTMENT CLOSED ISOLATION VALVES, LOWERED PRESSURES ON THE SYSTEM FROM 222 PSIG TO 35 PSIG. CONSTRUCTION CREWS INSTALLED A 16" FULL CIRCLE BAND CLAMP TO STOP THE BLOWING GAS. THEY THEN INSTALLED A REPAIR WELD SLEEVE AS A PERMANENT REPAIR. VALVES WERE THEN OPENED AND PRESSURE RESTORED TO NOT EXCEED 177 PSIG UNTIL FURTHER INVESTIGATION IS COMPLETE. THIS PIPE HAS BEEN CATHODICALLY PROTECTED BY RECTIFIER SINCE 1964. CAUSE OF THE DAMAGE IS UNKNOWN AND STILL UNDER INVESTIGATION. SUPPLEMENTAL REPORT DATA (4/13/12): MISSOURI PUBLIC SERVICE COMMISSION FILED A REPORT DEC. 9, 2011 (CASE NO. GS-2011-0248), BASED ON THEIR SAFETY STAFF'S RECOMMENDATIONS. MGE AND MPSC SAFETY STAFF AGREED THAT MGE WILL REPLACE THE ENTIRE LENGTH OF THE MAYFAIR 16 INCH PIPELINE IN TWO PHASES. PHASE 1 WILL REPLACE THE SECTION WHERE THE INCIDENT OCCURRED AND WILL BE COMPLETED BETWEEN JUNE 1, 2012 AND OCTOBER 1, 2012. ONCE THE PIPELINE IS REMOVED FROM SERVICE, MGE WILL REMOVE THE REPAIRED SECTION OF PIPE THAT CAUSED THE ORIGINAL INCIDENT AND PERFORM AN INVESTIGATION OF THE FRACTURE TO DETERMINE THE CAUSE. NO OTHER DATA HAS BEEN DISCOVERED, TO DATE, TO DETERMIN THE CAUSE OF THE FRACTURE. FINAL REPORT DATA (3/28/2013): MGE COMPLETED REPLACEMENT OF THIS SECTION OF 16 INCH STEEL MAIN ON 11/06/2012. THE SECTION OF PIPE THAT CAUSED THE ORIGINAL INCIDENT WAS CUT OUT AND REMOVED FROM THE GROUND AND SENT FOR METALLURGICAL ANALYSIS. THE CONCLUSION FROM THE DATA COLLECTED FROM THE SCANNING ELECTRON MICROSCOPE (SEM) AND METALLOGRAPHIC WORK IS THAT THE FAILURE MECHANISM IS STRESS CORROSION CRACKING (SCC) WHICH RESULTED FROM SETTLEMENT OF THE SOIL UNDER THE 16 INCH STEEL GAS MAIN THAT WAS INSTALLED IN 1997, RESULTING IN A SIGNIFICANT TORSIONAL LOAD ON THE PIPE APPROXIMATELY 13 FEET TO THE WEST (POINT OF BREAK).
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110026 | 16820 | 2011-03-04 12:35 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2011-02-10 22:30 | 2011 |  |  | 40.7341 | -80.8925 | 967142 | 2011-02-11 00:17 |  | NATURAL GAS |  | 62374 | 89152 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-02-10 22:55 | 2011-09-23 15:05 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 1 | 2011-02-10 22:30 | 2011-02-10 23:15 | ONSHORE | OH | 44423 | HANOVERTON | COLUMBIANA | MILEPOST | 214-4 + 60677 | LINE 200-4 | VALVE SECTION 214-4 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | YES |  |  |  |  | YES | CASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 36 |  | 0.344 | 60000 | API 5L OR EQUIVALENT | DSAW |  | NATIONAL TUBE | COAL TAR | [28 empty] | 1963 | 1963 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 113 | 12 |  | CLASS 1 LOCATION | NO |  | 698 |  | NO | NO | NO |  | 0 | 0 | 251367 | 294115.270124312 | 79705 | 53938.9076376554 | 2500000 | 2925157.9376401 | 50000 | 58503.1587528021 | 0 | 0 |  |  | 2881072 | 1560506.7571105 | 3331715.27415487 | [8 empty] | 733 |  | 790 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | AUTOMATIC | 60784 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WERE NO ABNORMAL PRESSURE EXCURSIONS. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | YES | [6 empty] | YES | YES | HYDROGEN ASSISTED CRACK IN GIRTH WELD | [12 empty] | YES | [6 empty] | YES | TENSILE OVERLOAD | [55 empty] | YES | YES | [6 empty] | 2005 | [55 empty] | NO |  |  | Yes, but the point of the Accident was not identified as a dig site |  | 2010 | [11 empty] | NO | [63 empty] | MERLIN MOSEMAN | CODES AND STANDARDS ENGINEER | merlin_moseman@kindermorgan.com | 7134204614 | 7134207464 |  |  |  | MERLIN MOSEMAN | CODES AND STANDARDS ENGINEER | 7134204614 | merlin_moseman@kindermorgan.com | GAS CONTROL PERSONNEL FOR TENNESSEE GAS PIPELINE (TGP) NOTICED PRESSURE DROPS RELATIVE TO ITS PIPELINE IN VALVE SECTION 214 DOWNSTREAM OF CARROLLTON COMPRESSOR STATION AND NEAR THE TOWN OF HANOVERTON, OH AROUND 10:30 PM EST ON FEBRUARY 10, 2011. SHORTLY THEREAFTER, TGP RECEIVED A REPORT FROM A LOCAL LANDOWNER OF A FIRE SOME 11,000 FEET NORTH OF VALVE 214 IN LINE 4. UPON RESPONDING, FIELD PERSONNEL VERIFIED THAT A RUPTURE HAD OCCURRED IN LINE 4 WHERE IT CROSSES MCKAIG ROAD IN COLUMBIANA COUNTY, OH. THERE WAS NO FORMAL EVACUATION OF LOCAL RESIDENTS ALTHOUGH EMERGENCY REPONDERS DID ADVISE SOME TO LEAVE THEIR HOMES AS A PRECAUTIONARY MEASURE (TGP WAS NOT INVOLVED IN ANY EVACUATION). POST-INCIDENT ROOT CAUSE ANALYSIS REVEALED THE FAILURE OCCURRED AS A RESULT OF TENSILE OVERLOAD ON A PRE-EXISTING HYDROGEN ASSISTED CRACK IN THE UNDERBEAD OF THE GIRTH WELD. THE CRACK ORIGINATED DURING THE WELDING PROCESS AT THE TIME OF ORIGINAL CONSTRUCTION. THE TENSILE OVERLOAD WAS THE RESULT OF A NUMBER OF INTERACTING STRESSORS INCLUDING BUT NOT LIMITED TO THERMAL CONTRACTION STRESSES. THE PIPELINE HAS BEEN REPAIRED, PURGED, AND LOADED WITH NATURAL GAS TO A PRESSURE OF 491 PSIG.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110027 | 15323 | 2011-03-04 16:42 | SUPPLEMENTAL FINAL | 602 | CENTERPOINT ENERGY GAS TRANSMISSION | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2011-02-18 20:48 | 2011 |  |  | 34.5436 | -92.954 | 967943 | 2011-02-18 23:06 |  | NATURAL GAS |  | 770 | 5256 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-02-22 11:00 | 2011-02-25 19:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-02-18 20:48 | 2011-02-18 20:48 | ONSHORE | AR | 71901 | HOT SPRINGS | GARLAND | SURVEY STATION NO. | 878+53 | CEGT LINE BT-1AS | SG17539 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 49 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.25 | 46000 | X-46 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | FIELD APPLIED EPOXY | [28 empty] | 1963 | 1959 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 349 |  | NO | NO | NO |  | 0 | 0 | 18664 | 21838.059099246 | 2957 | 2001.09591474245 | 113789 | 133140.318626452 | 6525 | 7634.66221724067 | 10000 | 11700.6317505604 | LAB ANALYSIS |  | 151935 | 82089.2018912338 | 176314.767608241 | [8 empty] | 864 |  | 1000 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 34848 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | MULTIPLE FACTORS ARE BELIEVED TO HAVE CONTRIBUTED TO THE CAUSE OF THE CIRCUMFERENTIAL CRACK. EXTERNAL CORROSION REDUCED THE WALL THICKNESS BY APPROXIMATELY 50% AT THE POINT OF FAILURE, THE PIPE MAY NOT HAVE BEEN PROPERLY SUPPORTED PRIOR TO RESTORING FILL AND THE PIPE WAS SUBJECTED TO RELATIVELY HIGH AXIAL LOADS. | [147 empty] | JIMMY CROSS | DOT WAIVER SPECIALIST | jimmy.cross@centerpointenergy.com | 318 429-3664 | 318 429-3927 |  |  |  | JOHNNY CAVITT | DOT COMPLIANCE MANAGER | 318 429-3660 | johnny.cavitt@centerpointenergy.com | CEGT LINE BT-1-AS LEAK 02/18/2011 ON 2/18/2011 AT 20:00 THE PUBLIC REPORTED A POSSIBLE LEAK TO SOUTHERN GAS OPERATIONS (SGO). SGO DISPATCHED AN EMPLOYEE TO INVESTIGATE AND AT 20:15 REPORTED THEY HAD FOUND A LEAK ON CEGT'S ROW FOR THE BT-1 SYSTEM. AT 20:17 SGO CONTACTED THE CEGT PIPELINE TEAM TO ADVISE THEM OF THE LEAK. A TEAM MEMBER WAS SENT TO THE LEAK LOCATION TO VERIFY THE LEAK. AT 20:48 THE LEAK WAS CONFIRMED TO BE ON CEGT'S LINE BT-1-AS AND REPORTED TO SYSTEM CONTROL. IT WAS DETERMINED TO BE A MINOR LEAK. CEGT BEGAN WORKING WITH SGO TO UNDERSTAND THE CUSTOMER LOAD. EMPLOYEES WERE STATIONED AT THE LEAK TO MAN IT UNTIL THE LEAK WAS STOPPED. AT 21:15 CEGT AREA MANAGEMENT NOTIFIED SYSTEM CONTROL THAT THEY HAD GENERATED A PLAN TO LOWER THE PRESSURE ON A 16 MILE SECTION OF BT1-AS FROM 870# TO 400#. AT 22:00 PERSONNEL WERE DISPATCHED TO BEGIN MOVING ALL CUSTOMERS POSSIBLE TO AN ALTERNATIVE CEGT PIPELINE. ON 2/19/2011 AT 01:30 CREWS BEGAN BLOWING DOWN AND THE PRESSURE WAS LOWERED TO 400# BY 03:30. PERSONNEL STAYED AT EACH MLV LOCATION MONITORING PRESSURES (12 HOUR ROTATION FOR DURATION OF INCIDENT). ON 2/21/2011 AT 11:00 EXCAVATION BEGAN TO INSTALL A STOPPLE FITTING 3.5 MILES NORTH OF THE LEAK. ON 2/22/2011 AT 11:00 THE STOPPALL WAS COMPLETED AND CEGT TEAM PERSONNEL BLEW DOWN A 6.6 MILE PIPELINE SECTION CONTAINING THE LEAK. AT 15:00 THE LEAK WAS EXPOSED ENOUGH TO DETERMINE A CAUSE, APPROXIMATELY A 4" CRACK IN THE PIPE. ON 2/23/2011 AT 16:30 PIPE WAS DELIVERED AND WELD CAPS WERE INSTALLED. AT 19:00 A 4 HOUR HYDRO TEST BEGAN, IT ENDED NEAR 24:00. ON 2/24/2011 AT 07:00 CONTRACTORS BEGAN TO REMOVE THE PIPE TO BE REPLACED. AT 10:00 THE CREW BEGAN INSTALLING THE NEW SECTION OF PIPE. ON 2/25/2011 CREWS COMPLETED THE REPLACEMENT AND AT 17:00 BEGAN PURGING. THE PURGE WAS COMPLETED AT 19:30. ON 2/26/2011 AT 07:30 THE CREW BEGAN BACKFILLING AT LEAK EXCAVATION, RECOATING AT STOPPLE FITTING LOCATION AND THEN RELOADED THE LINE. AT 16:00 THE SYSTEM WAS RETURNED TO NORMAL OPERATIONS. THE SECTION OF PIPE REMOVED WAS SENT TO KIEFNER & ASSOCIATES FOR METALLURGICAL ANALYSIS. IT WAS DETERMINED THAT THE FINAL FAILURE MODE WAS DUCTILE OVERLOAD OF THE REMAINING LIGAMENT BENEATH THE SCC. THE REMAINING LIGAMENT WAS OBSERVED TO BE APPROXIMATELY 50% OF THE PIPE WALL THICKNESS MINIMUM. THE FACT THAT THESE CRACKS WERE CRITICAL AT THIS SIZE INDICATES THE PRESENCE OF A RELATIVELY HIGH AXIAL LOAD. THE FINDINGS ARE AS FOLLOWS:
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110028 | 15791 | 2011-03-10 10:20 | SUPPLEMENTAL | 26330 | ENOGEX LLC | 515 CENTRAL PARK DR., STE. 110 | OKLAHOMA CITY | OK | 73105 | 2011-02-10 06:29 | 2011 |  |  | 35.3092 | -99.3017 | 967098 | 2011-02-10 13:50 |  | NATURAL GAS |  | 9909 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | FACILITY NON-OPERATIONAL DUE TO WEATHER RELATED POWER OUTAGE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-02-10 06:29 | 2011-02-10 07:35 | ONSHORE | OK | 73626 | CANUTE | WASHITA |  |  | CANUTE COMPRESSOR STATION | CANUTE COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | INSTRUMENTATION | [38 empty] | 2010 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | ALUMINUM HOUSING AND O-RING | OTHER | [8 empty] | INCORRECT OPERATION OF ESD VALVE | CLASS 1 LOCATION | NO |  | 305 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 43056 | 29137.3641207815 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 43056 | 30208.028419183 | 29137.3641207815 | [8 empty] | 835 |  | 1200 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A STATION ESD IS NOT MONITORED BY CONTROL ROOM PERSONNEL. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [13 empty] | YES | [173 empty] | JIM ROSS | DOT COMPLIANCE COORDINATOR | rossji@oge.com | (405) 557-5206 | (405) 815-6308 |  |  |  | PAUL M BREWER | VP OPERATIONS | (405) 525-7788 | brewerpm@oge.com | AT 06:00 ON 2/10/11 PURCHASED POWER WAS LOST AT THE ENOGEX CANUTE COMPRESSOR STATION, DUE TO THE POWER COMPANY'S TRANSFORMER FAILURE. BATTERY BACKUP TOOK OVER AND LASTED FOR APROXIMATELY 30 MINUTES. AT 06:29 AFTER THE BATTERY BACK UP RAN DOWN THE COMPRESSOR UNITS SHUT DOWN AND THE STATION ESD SYSTEM WAS AUTOMATICALLY ACTIVATED. AT THIS TIME GAS CONTROL RECEIVED AN ALARM THAT THE UNITS SHUT DOWN. GAS CONTROL NOTIFIED THE COMPRESSOR FOREMAN AND HE CONTACTED A COMPRESSOR TECH TO RESPOND TO THE ALARM. THE COMPRESSOR TECH ARRIVED ON LOCATION AT APPROXIMATELY 07:35. THE COMPRESSOR TECH FOUND ALL COMPRESSOR UNITS SHUT DOWN AND THE ESD SYSTEM HAD ACTIVATED. THE COMPRESSOR TECH CONFIRMED NATURAL GAS WAS VENTING TO ATMOSPHERE THROUGH A 2 INCH ESD VENT VALVE FOR UNIT 413 AND THAT THE SUCTION ESD VALVE FOR THE UNIT WAS NOT FULLY CLOSED. AFTER FURTHER INSPECTION IT WAS DISCOVERED THAT THE SOLENOID VALVE CONNECTED TO THE ESD VALVE ACTUATOR HAD AN INTERNAL ICE BLOCKAGE THAT PREVENTED PROPER OPERATION OF THE ACTUATED VALVE. THIS RESULTED IN A RELEASE OF NATURAL GAS THROUGH THE 2 INCH VENT VALVE AT A PRESSURE OF 835 PSIG FOR APPROXIMATELY 2.5 HOURS. PERSONNEL REMOVED THE ACTUATOR ON THE VENT VALVE AND MANUALLY CLOSED THE VALVE TO STOP THE GAS RELEASE. IN ADDITION, THE SOLENOID VALVE WAS THAWED TO CLOSE THE SUCTION ESD VALVE. IN ORDER TO PREVENT RECURRENCE, NEW BATTERIES WERE INSTALLED FOR THE BACK UP SYSTEM. IN ADDITION, THE INSTRUMENT GAS SUPPLY TO THE ESD SYSTEM WILL BE CONVERTED OVER TO A DRIER INSTRUMENT AIR SYSTEM. UPDATE MARCH 5, 2013: COMPLETED SECTION E.5.F.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110029 | 15838 | 2011-03-14 15:27 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2011-02-14 21:40 | 2011 |  |  | 32.8616 | -94.1599 | 967474 | 2011-02-14 22:19 |  | NATURAL GAS |  | 14400 | 600 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-02-14 21:40 | 2011-07-16 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2011-02-14 22:14 | 2011-02-14 22:15 | ONSHORE | TX | 75633 | CARTHAGE | PANOLA | MILEPOST | 0 | CARTHAGE JUNCTION COPRESSOR STATION | INDEX 816 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2007 |  | CARBON STEEL |  | OTHER | [8 empty] | CHECK VAVLE FAILED ALLOWING GAS TO FLOW IN THE REVERSE DIRECTION DAMAGING TURBINE COMPRESSOR AND SUBSEQUENT ELBOW RUPTURE | CLASS 1 LOCATION | NO |  | 1058 |  | NO | NO | NO |  | 0 | 0 | 2592 | 3032.80374974526 | 62208 | 42098.1314387211 | 30000000 | 35101895.2516813 | 1000 | 1170.06317505604 | 0 | 0 |  |  | 30065800 | 16158270.4195833 | 35148196.2500448 | [8 empty] | 1137 |  | 1333 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INVESTIGATION DETERMINED CAUSE WAS A COMPONENT FAILURE. NO ACTION OF GAS CONTROIL COULD LEAD TO CAUSE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [5 empty] | YES | [29 empty] | YES | OVERTORDQUING OF CENTER BOLT BY MANUFACTURER DURING ASSEMBLE OF CHECK VALVE | [161 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 270-688-6357 | 270-688-5871 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 270-688-6361 | jeff.mcmaine@bwpmlp.com | SUMMARY OF OPERATIONS JUST PRIOR TO INCIDENT ON 02-14-2011. A) THREE TURBINES WERE RUNNING WITH A SUCTION PRESSURE OF 688 PSI AND A DISCHARGE PRESSURE OF 1137 PSI. B) AT 09:11:24 PM, GAS CONTROL PUT A STOP IN T7. C) AT 09:25:03 PM, ESD WAS ACTIVATED BY FIRE DETECTORS. THE INITIAL FIRE WAS A LUBE OIL FIRE. SUBSEQUENTLY AFTER AN ELBOW RUPTURED THE RELEASED GAS IGNITED AND BURNED UNTIL GAS FLOW WAS STOPPED. THE ROOT CAUSE OF THE INCIDENT WAS DETERMENED TO BE THE FAILURE OF A CHECK VALVE IN THE TURBINE UNIT DISCHARGE LINE. 1) CHECK VAVLE ON TURBINE UNIT T7 DISCHARGE LINE WAS DAMAGED. CHECK VALVE INTERNALS SEPERATED WHEN CENTER BOLT FAILED. FAILURE CAUSE WAS DETERMINED TO BE OVERTORQUING OF CENTER BOLT BY MANUFUCTURE DURING VALVE ASSEMBLY. 2) DICCHARGE VALVE ON UNIT T7 DID NOT FULLY CLOSE DURING THE UNIT SHUT DOWN BECAUSE PARTS OF THE CHECK VALVE INTERNALS WAS STUCK IN THE VAVLE. 3) 24" ELBOW LOCATED IN THE BASEMENT ON THE SUCTION LINE OF UNIT T7 COMPRESSOR, RUPTURED FROM A MANUFACTURING DEFECT WHICH WAS WEAKENED BY THE HEAT FROM THE LUBE OIL FIRE ALOWING GAS TO BE RELEASED INTO THE COMPRESSOR BUILDING AND IGNITE. THE DAMAGED FACILITIES HAVE BEEN REPAIRED AND RETURNED TO SERVICE ON 07-16-2011. UPDATED PART E.5F AS REQUESTED BY PHMSA.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110030 | 15282 | 2011-03-15 16:02 | SUPPLEMENTAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2011-02-18 13:30 | 2011 |  |  | 33.6298 | -85.5117 | 967893 | 2011-02-18 14:40 |  | NATURAL GAS |  | 2100 | 741 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | VALVE SEGMENT WAS ISOLATED PRIOR TO INCIDENT BUT CONTAINED PRESSURE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-02-18 13:30 | 2011-02-18 13:30 | ONSHORE | AL | 36264 | HEFLIN | CLEBURNE | MILEPOST | 396.6 | NORTH MAIN LOOP | 24" | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 84 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 |  | 0.25 | 52000 | API 5L OR EQUIVALENT | DSAW |  | REPUBLIC | COAL TAR | [28 empty] | 1948 | 1948 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 370 |  | NO | NO | NO |  | 1000 | 1170.06317505604 | 2964 | 3468.06725086611 | 8400 | 5684.54706927176 | 126000 | 147427.960057061 | 5000 | 5850.31587528021 | 30000 | 35101.8952516813 | METALLURGICAL LAB & GEOLOGISTS. |  | 173364 | 94493.9216445423 | 198702.848679217 | [8 empty] | 290 |  | 500 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | YES | NO | PHMSA |  |  | MANUAL | MANUAL | 43623 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE DID NOT EXCEED ESTABLISHED OPERATING LIMITS. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES | YES | GEOTECHNICAL AND HYDRO-GEOLOGICAL |  |  |  |  | YES | [14 empty] | YES |  |  |  | YES | [59 empty] | YES | YES |  |  | YES |  |  |  | 2007 | [31 empty] | 2007 | [23 empty] | YES | 1998 | 823 | NO | [13 empty] | NO | [63 empty] | KENNETH C. PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | ken.peters@elpaso.com | 2053257554 | 2053253729 |  |  |  | KENNETH C. PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | 2053257554 | ken.peters@elpaso.com | SOUTHERN NATURAL GAS (SNG) COMPANY'S GAS CONTROL NOTICED A PRESSURE DROP IN ITS SCADA SYSTEM ON FEBRUARY 18, 2011 THAT INDICATED A POSSIBLE PIPELINE LEAK. FIELD PERSONNEL WERE DISPATCHED TO INVESTIGATE THE 24" NORTH MAIN LOOP PIPELINE. A CRACK IN A WRINKLE BEND WAS FOUND AT MILEPOST 396.6 RELEASING NATURAL GAS. THE PIPELINE WAS ALREADY ISOLATED DUE TO CAO CPF 2-2010-1001H, CONTAINING GAS BETWEEN THE CLOSED VALVES AT A PRESSURE OF 290 PSIG. THE LINE WAS BLOWN DOWN WITH A 135 FEET SECTION CUT OUT, WELD CAPS BEING INSTALLED ON EITHER SIDE OF THE CUT. THE LINE SEGMENT IS OUT OF SERVICE AND WILL REMAIN SO UNTIL 2012 WHEN IT IS PLANNED FOR ABANDONMENT. THE POST-INCIDENT INVESTIGATION AND EVALUATIONS REVEALED FAILURE LIKELY TO HAVE BEEN CAUSED BY COMBINED MECHANICAL STRESSES IN A WRINKLE BEND, WITH SUCH STRESSES COMING FROM NORMAL PIPELINE OPERATIONS, HYDROGEOLOGICAL INFLUENCE IN THE SOIL, AND THE NATURE OF WRINKLE BEND CONFIGURATION.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110031 | 15773 | 2011-03-22 16:08 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION CORP | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2011-02-22 00:55 | 2011 |  |  | 38.5642 | -78.6229 | 968331 | 2011-02-22 12:40 |  | NATURAL GAS |  | 3890 | 72 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-02-22 01:35 | [5 empty] | NO |  |  |  |  | NO | [9 empty] | ONSHORE | VA | 22657 | STRASBURG | SHENANDOAH COUNTY |  |  | STRASBURG COMPRESSOR STATION |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [8 empty] | CARBON STEEL |  | LEAK |  |  | OTHER | ESD TRIGGER AIR SUPPLY PIPPING | [5 empty] | CLASS 1 LOCATION | NO |  | 78 |  | NO | YES | NO |  | 0 | 0 | 285 | 333.468004890972 | 1517 | 1026.60213143872 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1802 | 1217.39565781439 | 1360.07013632969 | [8 empty] | 660 |  | 800 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | HARDWARE FAILURE DUE TO LOSS OF AIR PRESSURE TO MOVE ACTUATOR | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | DICOVERY OF WATER IN THE ESD TRIGGER AIR SUPPLY PIPING. | [161 empty] | GEORGE HAMATY | ENGINEER | ghamaty@nisource.com | 3043573728 | 3043573804 |  |  |  | GEORGE HAMATY | ENGINEER | 3043573728 | ghamaty@nisource.com | ON FEBRUARY 22, 2011 @ 00:50, THE 4-INCH ESD VENT VALVE ON THE STATION DISCHARGE LINE INADVERTENTLY OPENED. AT THIS TIME THE STATION FIRE VALVES WERE OPEN BUT NEITHER COMPRESSOR UNIT WAS RUNNING. AIR TEMPERATURE WAS ABOUT 25&#9675;F. THIS VALVE REMAINED OPEN FOR SEVERAL MINUTES AND CONTINUALLY VENTED GAS AS THE DISCHARGE PRESSURE AT THE STATION DROPPED. A COMPANY EMPLOYEE WHO LIVES NEAR THE STATION HEARD THE GAS BLOWING AND WENT TO FACILITY TO CHECK ON IT. UPON ARRIVAL HE FOUND THE OPEN VALVE AND ACTIVATED THE ESD SYSTEM TO ISOLATE THE STATION FROM THE PIPELINE AND TO ALLOW THE STATION PIPING TO COMPLETELY BLOWDOWN. THE EVIDENCE OF WATER AND OTHER SOLID MATERIAL IN THE ESD TRIGGER AIR SUPPLY PIPING HAD INITIATED (AS A RECOMMENDATION) A CREATION OF A WORK MANAGEMENT PREVENTIVE MAINTENANCE WORK ORDER, TO BLOW ANY DEBRIS FROM THE ESD TRIGGER AIR LINES TO ALL OF THE FIRE VALVES AND VENT VALVES WHEN THE ESD SYSTEM IS LOADED AT THE BEGINNING OF EACH OPERATING SEASON.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110032 | 15782 | 2011-03-23 13:59 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION CORP | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2011-02-27 12:22 | 2011 |  |  | 37.6547 | -82.036 | 968668 | 2011-02-27 14:08 |  | NATURAL GAS |  | 8526 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-02-27 12:22 | 2011-02-27 13:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-02-27 12:22 | 2011-02-27 12:22 | ONSHORE | WV | 25670 | DELBARTON | MINGO | MILEPOST | COMPRESSOR | GRANT COMPRESSOR STATION | C90-29 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [8 empty] | CARBON STEEL |  | OTHER | [8 empty] | MECHANICAL FAILURE ON A RELIEF VALVE WHERE DEBRIS BLOCKED THE VALVE. | CLASS 2 LOCATION | NO |  | 99 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 38113 | 25792.2788632327 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 38113 | 26740.026642984 | 25792.2788632327 | [8 empty] | 1003 |  | 1030 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE MECHANICAL FAILURE OF THE RELIEF VALVE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | DEBRIS IN THE VALVE | [161 empty] | JAY FRAME | ENGINEER | jgframe@nisource.com | 3043572188 | 3043573804 |  |  |  | JAY FRAME | ENGINEER | 3043572188 | jgframe@nisource.com | ON FEBRUARY 27TH, 2011 AT APPROXIMATELY 10:30, GAS CONTROL NOTICED A LOSS IN PRESSURE AT GRANT COMPRESSOR STATION. COMPANY PERSONNEL WERE NOTIFIED AND REPORTED ON SITE AT 11:00 AM. A BLOW DOWN VALVE WAS FOUND OPEN AND VENTING GAS TO ATMOSPHERE. THE VALVE WAS MANUALLY SHUT. THE SITE WAS SECURED AT 11:30 . AN INVESTIGATION INTO THE CAUSE OF THE FAILURE WAS INITIATED AND THE RELIEF VALVE ON THE SCHAFER OPERATING SYSTEM WAS FOUND TO BE LEAKING AND BLOCKED WITH DEBRIS. THE PLUGGED/MALFUNCTIONING RELIEF VALVE WAS REPLACED WITH A NEW ONE. SYSTEM WAS PLACED BACK IN SERVICE AND ALL NEEDED HORSEPOWER WAS PUT BACK ON LINE AT 13:15. A ROOT CAUSE ANALYSIS REPORT WAS INITIATED AND THE FOLLOWING RECOMMENDATIONS WERE REPORTED. MODIFY MAINTENANCE PLAN TO INCLUDE THOSE RELIEF VALVES. CURRENT RECOMMENDATION IS TO REPLACE THESE VALVES ONCE A YEAR DURING THE ANNUAL ESD TEST. THIS RECOMMENDATION NEEDS TO BE SHARED WITH ALL STATIONS IN NGT&S THAT MAY HAVE SIMILAR SCHAFER OPERATOR CONFIGURATIONS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110033 | 15254 | 2011-03-25 14:56 | SUPPLEMENTAL FINAL | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | ONE ENERGY PLAZA | DETROIT | MI | 48226 | 2011-02-23 11:12 | 2011 |  |  | 42.787 | -82.5286 | 968441 | 2011-02-24 14:10 |  | NATURAL GAS |  | 6013 | 5049 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-02-25 12:00 | 2011-02-26 23:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-02-24 12:57 | 2011-02-24 12:57 | ONSHORE | MI | 48054 | CHINA | ST. CLAIR | MILEPOST | 59 | BELLE RIVER MILLS COMPRESSOR STATION | 36" MILFORD-BELLE RIVER LOOP | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 105 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION | [19 empty] | FILLET WELD | [18 empty] | 2007 |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 2 LOCATION | NO |  | 52 |  | NO | NO | NO |  | 0 | 0 | 32300 | 37793.0405543102 | 38500 | 26054.1740674956 | 79507 | 93028.2128591807 | 0 | 0 | 0 | 0 |  |  | 150307 | 87061.9525683938 | 156875.427480986 | [8 empty] | 775 |  | 1000 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | AUTOMATIC | 87968 | NO |  |  |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO UNUSUAL OR ABNORMAL OPERATING CONDITIONS CONTRIBUTED TO THE INCIDENT | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES |  |  |  |  | YES | MECHANICAL VIBRATION | [16 empty] | YES | YES | [62 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | MICHAEL R. LASKOWSKI |  |  | 313-389-7762 |  |  |  |  | ROBERT H. FRECKELTON |  | 313-389-7755 |  | LEAK DISCOVERED DURING ROUTINE FACILITY CHECKS BY EMPLOYEES OF OPERATOR AND EMPLOYEES OF ANOTHER OPERATOR WITH FACILITIES AT SAME LOCATION. POTENTIAL LIKELY CAUSATIONS (INCLUDING FAILURES IN VALVE BODY BLEED OR GREASE/SEALANT LINE EXTENSION PIPING) INVESTIGATED, BUT COULD NOT BE CONFIRMED. DECISION MADE TO ISOLATE AND REDUCE PRESSURE IN PIPELINE SEGMENT TO ALLOW FURTHER INVESTIGATION. AFTER ISOLATING 2 ADJACENT VALVE SECTIONS AND REDUCING PRESSURE THOUGH FLOW TO LOWER PRESSURE SYSTEM, IMPACTED SEGMENT FURTHER ISOLATED AND REMAINING GAS VENTED TO ATMOSPHERE. IMPACTED SEGMENT WAS PURGED (GAS TO AIR) USING AIR MOVERS IN ANTICIPATION OF NECESSITY TO PERFORM WELDING OPERATIONS TO COMPLETE REPAIRS. INVESTIGATION THROUGH EXCAVATION REVEALED CRACK IN 2 INCH FILLET WELD AT SOCKET WELDED CONNECTION INSTALLED IN 2007 AS FACILITY MODIFICATION TO ALLOW LIQUID REMOVAL FROM LOW POINT IN A NON-PIGGABLE SECTION OF STATION PIPING. ICE FROM FREEZING OF GROUND WATER IN VICINITY OF LEAK (DUE TO COOLING OF GAS AS A RESULT OF PRESSURE REDUCTION) IMPACTED ADJACENT 2 INCH PIPING (NOT RELATED TO SIPHON), PROMPTING REPAIRS TO ADJACENT (NONLEAKING) 2 INCH PIPING IN ADDITION TO PIPING AT LOCATION OF LEAK. AFTER REPAIRS WERE COMPLETED AND NONDESTRUCTIVE INSPECTIONS COMPLETED, LINE SEGMENT WAS PURGED (AIR TO GAS), PRESSURIZED AND RETURNED TO NORMAL OPERATION.
2021-02-26 10:37 | NO | NO | GG (Gas Gathering) | 20110034 | 15842 | 2011-03-25 22:26 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2011-02-24 16:45 | 2011 |  |  | 28.2722 | -98.2875 | 968473 | 2011-02-24 17:30 |  | NATURAL GAS |  | 20 | 0 | 0.12 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE LEAK WAS ON 1/2 INCH SUPPLY TUBING ON THE PLATFORM | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-02-24 16:45 | 2011-02-24 17:30 | OFFSHORE | [28 empty] | 50 | IN STATE WATERS | TX | MATAGORDA BAY | MATAGORDA 558 BLOCK | MATAGORDA |  |  |  | PLATFORM | INTERSTATE | OFFSHORE PLATFORM, INCLUDING PLATFORM-MOUNTED EQUIPMENT AND PIPING | TUBING | [38 empty] | 1988 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 1 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 80 | 54.1385435168739 | 0 | 0 | 2000 | 2340.12635011208 | 0 | 0 |  |  | 2080 | 1130.30762954723 | 2394.26489362896 | [8 empty] | 100 |  | 1000 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | OFFSHORE GATHERING | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS CAUSED BY A 1/2 INCH TUBING FAILURE. THE ONLY REASON THE INCIDENT IS REPORTABLE IS BECAUSE APPROXIMATELY 5 GALLONS OF TRAPPED CONDENSATE CAUSED A SHEEN ON THE WATER | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | DEFECTIVE OR LOOSE TUBING OR FITTING | MATERIAL/WELD/EQUIP FAILURE | DEFECTIVE OR LOOSE TUBING/FITTING | [166 empty] | DEFECTIVE OR LOOSE TUBING OR FITTING | [35 empty] | YES | CAUSE IS UNKNOWN AT THIS TIME | [161 empty] | MATTHEW STRATMANN | PIPELINE COMPLIANCE SPECIALIST | mstratmann@eprod.com | 713-381-8209 |  |  |  |  | MATTHEW STRATMANN | PIPELINE COMPLIANCE SPECIALIST | 713-381-8209 | mstratmann@eprod.com | THIS INCIDENT HAPPENED ON PLATFORM 558 IN MATAGORDA BAY. IT WAS REPORTED TO ENTERPRISE BY THE GENERAL LAND OFFICE. UPON NOTIFICATION AN ENTERPRISE TECHICIAN FLEW TO THE PLATFORM AND FOUND A SECTION OF 1/2 INCH SUPPLY GAS TUBING CRACKED AND LEAKING. THE TECHNICIAN PROMPTLY BLOCKED AND THE TUBING. THE TECHNICIAN ALSO NOTICED A SLIGHT SHEEN ON THE WATER. THIS HAS BEEN CALCULATED TO BE APPROXIMATELY 5 GALLONS OF CONDENSATE THAT WAS RELEASE FROM THE TUBING. THE TUBING HAS ALREADY BEEN REPAIRED. ENTERPRISE'S ANSWER TO PART D NUMBER 1 WAS 1. THERE IS NO PIR FOR THIS SYSTEM. THIS IS AN OFFSHORE GATHERING SYSTEM. THE SYSTEM WILL NOT ACCEPT 0.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110035 | 15841 | 2011-03-26 22:33 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2011-02-24 13:00 | 2011 |  |  | 30.3403 | -101.5165 | 968462 | 2011-02-24 15:30 |  | NATURAL GAS |  | 3120 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-02-24 13:56 | 2011-02-27 08:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-02-24 13:00 | 2011-02-24 13:56 | ONSHORE | TX | 76943 | OZONA | CROCKETT | MILEPOST | 9 | SONORA WEST LOOP LATERAL | 146-114 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8.625 |  | 0.188 | 42000 | API5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | EPOXY | [28 empty] | 1981 | 1981 | CARBON STEEL |  | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 1 LOCATION | NO |  | 216 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 12100 | 8188.45470692718 | 10000 | 11700.6317505604 | 0 | 0 | 0 | 0 |  |  | 22100 | 13860.2415225141 | 19889.0864574876 | [8 empty] | 1100 |  | 1318 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 105600 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER RECOGNIZED THE INCIDENT IMMEDIATELY AND THE SCADA SYSTEM IDENTIFIED THE INCIDENT | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 110456923 | DIG_TESS | UNKNOWN/OTHER | NO | YES | YES | 60 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | EXCAVATION PRACTICES NOT SUFFICIENT (OTHER) | [263 empty] | MATTHEW STRATMANN | PIPELINE COMPLIANCE SPECIALIST | mstratmann@eprod.com | 713-381-8209 |  |  |  |  | MATTHEW STRATMANN | PIPELINE COMPLIANCE SPECIALIST | 713-381-8209 | mstratmann@eprod.com | THERE ARE THREE ONE-CALL TICKETS THAT ARE INVOLVED WITH THIS INCIDENT; ONE FROM MEADOR CONSTRUCTION (TICKET 110246447 ON 24JAN2011) AND TWO FROM CUSTOM TRENCH (TICKET 110271657 ON 27JAN2011, AND TICKET 110446923 14JAN2011). EACH TICKET HAS THE SAME SCOPE OF WORK AND START & END GPS COORDINATES. IN RESPONSE TO THESE ONE-CALL TICKETS, THE ENTERPRISE PIPELINE WAS NOT MARKED BECAUSE THE ENTERPRISE LINE LOCATOR WAS INFORMED BY EXCAVATOR EMPLOYEES THAT THE PLANNED EXCAVATION WOULD REMAIN ON THE ADJACENT ROW, AND WOULD NOT ENCROACH UPON THE ENTERPRISE ROW. THE ROUTE FOR A NEW APPROXIMATELY 6 MILE DCP PIPELINE HAD BEEN SURVEYED AND STAKED IN ROW THAT IS IMMEDIATELY ADJACENT TO THE ENTERPRISE PRODUCTS ROW. WHEN THE FIRST ONE-CALL WAS MADE (TICKET 110246447), THE ENTERPRISE LINE LOCATOR MET WITH MEADOR CONSTRUCTION REPRESENTATIVE MATTHEW LLOYD AND DCP CONSTRUCTION REP MIGUEL FLYNN ON 26JAN2011 TO DISCUSS THE PLANNED EXCAVATION AND WAS INFORMED THE EXCAVATION WOULD PARALLEL THE EXISTING ENTERPRISE PIPELINE, BUT REMAIN 40 FEET AWAY FROM THE ENTERPRISE PIPELINE AND ON THE ADJACENT ROW AND WOULD FOLLOW THE STAKED SURVEY ROUTE. THE ENTERPRISE LOCATOR VERIFIED THE STAKED ROUTE WAS 40' FROM THE EXISTING ENTERPRISE PIPELINE FOR THE ENTIRE 6 MILE LENGTH OF THE NEW SURVEY ROUTE. WHEN THE SECOND ONE-CALL WAS MADE (TICKET 110271657), THE ENTERPRISE LINE LOCATOR CALLED CUSTOM TRENCH EMPLOYEE STEVEN MORRIS ON 27JAN2011 TO DISCUSS THE PLANNED EXCAVATION. ON 14FEB2011 THE THIRD ONE-CALL (TICKET 110446923) WAS MADE BY CUSTOM TRENCH TO REFRESH THE SECOND ONE-CALL FOR THIS PROJECT, AT WHICH TIME THE ENTERPRISE LINE LOCATOR RETURNED TO THE EXCAVATION SITE AND VERIFIED CUSTOM TRENCH WAS STILL ON THE ADJACENT ROW AND NOT ON THE ENTERPRISE ROW. CUSTOM TRENCH CONTINUED TO FOLLOW THE SURVEYED ROUTE WITH THEIR EXCAVATION UNTIL THEY DECIDED TO RELOCATE TO THE EAST END OF THE WORK AREA TO BEGIN ANOTHER EXCAVATION. AT THE EAST END LOCATION THE EXCAVATOR DEVIATED FROM THE WORK PLAN WITHOUT NOTIFYING ENTERPRISE AND BEGAN EXCAVATING OUTSIDE OF THE SURVEYED AND STAKED ROUTE, AND ONTO THE ENTERPRISE ROW. ON 24FEB2011 THE EXCAVATOR STRUCK THE ENTERPRISE PIPELINE WITH A TRENCHING MACHINE. ENTERPRISE WAS NOT NOTIFIED OF THE CHANGE IN PLANS, NOR DID THE ACTIVE ONE-CALL TICKET INDICATE A CHANGE IN CUSTOM TRENCH'S SCOPE OF WORK.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110036 | 16819 | 2011-03-28 15:34 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2011-03-01 07:15 | 2011 |  |  | 39.9452 | -81.6804 | 968824 | 2011-03-01 10:12 |  | NATURAL GAS |  | 29745 | 13338 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-03-01 08:20 | 2011-03-22 16:09 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-03-01 07:15 | 2011-03-01 08:00 | ONSHORE | OH | 43732 | CUMBERLAND | GUERNSEY | MILEPOST | 209-1@2258 | LINE 200-1 | VALVE SECTION 209-1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 33 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 26 |  | 0.281 | 52000 | EXCEEDS API 5L | FLASH WELDED |  | A.O. SMITH | COAL TAR | [9 empty] | PIPE GIRTH WELD | [18 empty] | 1950 | 1950 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 31.2 | 0.4 |  | CLASS 1 LOCATION | NO |  | 504 |  | NO | NO | NO |  | 10000 | 11700.6317505604 | 53344 | 62415.8500101895 | 118980 | 80517.5488454707 | 200825 | 234977.93713063 | 6800 | 7956.42959038109 | 0 | 0 |  |  | 389949 | 229010.904355108 | 397568.397327231 | [8 empty] | 709 |  | 790 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 63307 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURES WERE NEVER ABNORMAL OR IN EXCESS OF MAOP. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | YES | [6 empty] | YES | [12 empty] | YES |  | YES | [63 empty] | YES | YES |  |  | YES |  |  |  | 2004 | [31 empty] | 2004 | [23 empty] | YES | 1969 | 1054 | NO | [13 empty] | NO | [63 empty] | MERLIN MOSEMAN | ENGINEER - PIPELINE | merlin_moseman@kindermorgan.com | 7134204614 |  |  |  |  | MERLIN MOSEMAN | ENGINEER - PIPELINE | 7134204614 | merlin_moseman@kindermorgan.com | ON MARCH 1, 2011, TENNESSEE GAS PIPELINE (TGP) COMPANY PERSONNEL ARRIVED TO BEGIN THEIR WORK DAY AT COMPRESSOR STATION 209 NEAR CUMBERLAND, OHIO, AND NOTICED AN AUDIBLE SOUND LIKE RELEASING GAS JUST NORTHEAST OF THE STATION YARD. UPON INVESTIGATION, THE POINT OF THE RELEASE WAS FOUND IN TGP'S 26" 200-1 PIPELINE. ISOLATION VALVES WERE CLOSED AND THE SECTION OF PIPE WAS DEPRESSURIZED. THERE WAS NO ASSOCIATED FIRE OR EXPLOSION. A ROOT CAUSE ANALYSIS HAS DETERMINED THE CAUSE TO BE THE FAILURE OF A GIRTH WELD IN THE FORM OF A CRACK THAT ORIGINATED AT INTERNAL UNDERCUTTING AT THE TOE OF THE GIRTH WELD ROOT PASS AND EXTENDING THROUGH THE WELD METAL OF THE WELD, ALSO ASSISTED BY TENSILE AXIAL STRESSES DUE TO THERMAL STRESS AT THE LOW AMBIENT TEMPERATURE WITH NO GAS FLOW AND BENDING STRESS AT THE SAG BEND.. THE CRACK WAS LIKELY PRODUCED DURING THE INITIAL WELDING PROCESS AND RAN FROM THE 9 O'CLOCK POSITION TO THE 3 O'CLOCK POSITION AROUND THE PIPE. THE DEFICIENT WELD WAS REMOVED, NEW PIPE INSTALLED, AND THE SECTION HAS BEEN PLACED BACK INTO SERVICE. YEAR OF PIPE MANUFACTURE IS ASSUMED TO BE COMMENSURATE WITH YEAR OF INSTALLATION 2/10/2015 - PART C - TYPE OF INCIDENT CHANGED FROM "LEAK" TO "RUPTURE". 3/27/2015 - PART E - UPDATED MAOP DETERMINATION METHOD TO 192.619(A)(3). 7/20/2015 - PART A - LOCAL TIME OF INCIDENT REVISED FROM TIME OF DETERMINATION AT 8:00 TO TIME THAT TGP PERSONNEL HEARD HISSING AT 7:15 AM. TIME OF TELEPHONIC REPORT TO THE NRC REVISED FROM 9:15 TO 10:12. BOTH REVISIONS BASED UPON INPUT FROM PHMSA.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110037 | 15406 | 2011-03-29 10:08 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2011-03-01 10:20 | 2011 |  |  | 28.3167 | -91.4111 | 968846 | 2011-03-01 11:55 |  | NATURAL GAS |  | 1.9 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | PIPELINE WAS ALREADY SHUT IN DUE TO ANOTHER LEAK ON JANUARY 28, 2011. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-03-01 10:20 | 2011-03-02 02:00 | OFFSHORE | [28 empty] | 244 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EUGENE ISLAND | 302 | BELOW WATER, PIPE ON OR ABOVE SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | REPAIR SLEEVE OR CLAMP | [38 empty] | 2010 |  | CARBON STEEL |  | LEAK |  |  | OTHER | 2" VALVE BROKE OFF IN THREADS | [5 empty] | CLASS 1 LOCATION | NO |  | 732 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 7 | 4.73712255772647 | 58000 | 67863.6641532504 | 1000 | 1170.06317505604 | 70000 | 81904.4222539229 | SANDBAGS |  | 129007 | 69289.5046279991 | 150942.886704787 | [8 empty] | 247 |  | 1250 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 168960 | NO | [5 empty] | YES | ALL FACILITIES SUBSEA, NO ABOVE SURFACE LAUNCHERS & RECEIVERS. | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | AIR PATROL |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO ABNORMAL PRESSURE CONCERNS. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ROUTINE OR NORMAL FISHING OR OTHER MARITIME ACTIVITY NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | FISHING OR MARITIME ACTIVITY | [103 empty] | ROUTINE OR NORMAL FISHING OR OTHER MARITIME ACTIVITY NOT ENGAGED IN EXCAVATION | [261 empty] | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | ken.peters@elpaso.com | 2043257554 | 2053253729 |  |  |  | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | 2053257554 | ken.peters@elpaso.com | TENNESSEE GAS PIPELINE (TGP) COMPANY'S AERIAL PATROL OF ITS OPERATIONS IN THE GULF OF MEXICO DISCOVERED A 10' DIAMETER RING OF BUBBLES IN THE VICINITY OF ITS 30 INCH 523M-2300 PIPELINE. INVESTIGATION REVEALED THAT A SHRIMPER'S NET HAD CAUGHT ON AND BROKEN OFF A 2" VALVE IN A REPAIR CLAMP PREVIOUSLY INSTALLED ON THE PIPE. DIVERS REPAIRED THE LEAK BY INSTALLING A NEW 2" VALVE. THIS PIPELINE WAS ALREADY VALVED OFF AND INACTIVE FROM AN EARLIER LEAK THAT OCCURRED JANUARY 28, 2011. THE PIPELINE IS BEING CONSIDERED FOR ABANDONMENT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110038 | 15471 | 2011-04-03 22:32 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2011-03-02 20:40 | 2011 |  |  | 28.4486 | -97.5235 | 969023 | 2011-03-02 22:10 |  | NATURAL GAS |  | 1000 | 3000 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-03-02 20:40 | 2011-05-17 12:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-03-02 20:40 | 2011-03-02 20:40 | ONSHORE | TX | 78119 | KENNEDY | KARNES |  |  | SADF EAST MAINLINE | 22 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.281 | 52000 | API5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | EPOXY | [28 empty] | 1962 | 1962 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 20 | 20 |  | CLASS 1 LOCATION | NO |  | 446 |  | NO | NO | NO |  | 0 | 0 | 12000 | 14040.7581006725 | 4000 | 2706.92717584369 | 200000 | 234012.635011208 | 0 | 0 | 2356471 | 2757219.94018749 | THE PIPELINE WAS HYDROTESTED AND AND ILI WAS RAN |  | 2572471 | 1382306.15394527 | 3007980.26047521 | [8 empty] | 145 |  | 1045 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 52800 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT HAPPENED DURING A MAINTENANCE ACTIVITY WITH THE LINE OUT OF SERVICE | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | METALLUGY ANALYSIS WAS INCONCLUSIVE SO CAUSE WAS UNKNOWN. AS A RESULT THE PIPELINE WAS HYDROTESTED AND AN ILI WAS RAN. | [147 empty] | MATTHEW STRATMANN | PIPELINE COMPLIANCE SPECIALIST | mstratmann@eprod.com | 713-381-8209 |  |  |  |  | MATTHEW STRATMANN | PIPELINE COMPLIANCE SPECIALIST | 713-381-8209 | mstratmann@eprod.com | ON WEDNESDAY MARCH 2, 2011 ENTERPRISE PRODUCTS CONTROL CENTER WAS NOTIFIED OF A SMALL LEAK ON LINE 22 SADF EAST MAINLINE, SOUTH OF KENNEDY, TX. OPERATION RESPONDED ISOLATED THE LINE AND STARTED REPAIR ACTIVITIES. ON THE NIGHT MARCH 4, 2011 OPERATIONS STARTED TO PURGING ACTIVITY TO PREPARE THE LINE FOR RESTART. ON MARCH 5, 2011 IT IT WAS DISCOVERED THAT THE LINE HAD RUPTURED IN SEVERAL SPOTS NEAR THE BURNELL COMPRESSOR STATION. IT WAS NOTED THAT THE LINE NEVER REACHED MORE THAT 145PSIG DURING PURGE ACTIVITIES. THE RUPTURED PIPE WAS SENT OUT FOR METALLURGY TESTING AND ANALYSIS AT STORK METALLURGY AND TESTING IN HOUSTON, TX. THE RESULTS OF THE ANALYSIS WERE INCONCLUSIVE. BECAUSE OF THE RUPTURES ON THE PIPELINE, IT WAS DECIDED TO CONDUCT AN DEFORMATION AND MFL INTERNAL INSPECTION ON THE PIPELINE. AFTER THE INSPECTIONS THE PIPELINE WAS HYDOTESTED TO INSURE THAT IT IS MECHANICALLY SOUND. REPAIR COSTS HAVE BEEN UPDATED TO REFLECT THE COST OF THE HYDROTEST AND ILI. THE LINE WAS RESTARTED ON MAY 17, 2011.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110039 | 15389 | 2011-04-12 15:58 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2011-03-14 10:45 | 2011 |  |  | 31.9919 | -88.9315 | 970025 | 2011-03-14 12:30 |  | NATURAL GAS |  | 1577 | 37000 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-03-14 20:00 | 2011-03-19 09:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 35 | 2011-03-14 10:45 | 2011-03-14 10:45 | ONSHORE | MS | 39347 | PACHUTA | JASPER | MILEPOST | 538+11.82 | LINE 500-2 BARNETT DRIP | 538-2 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 80 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PULSATION BOTTLE OR DRIP/DRIP COLLECTION DEVICE | [38 empty] | 1976 |  | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 2 LOCATION | NO |  | 1101 |  | NO | NO | NO |  | 25000 | 29251.579376401 | 167856 | 196402.124312207 | 7144 | 4834.57193605684 | 100000 | 117006.317505604 | 17000 | 19891.0739759527 | 50000 | 58503.1587528021 | LAB COSTS |  | 367000 | 198287.23308747 | 425888.825859024 | [8 empty] | 887 |  | 936 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 81840 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO EXCURSION BEYOND OPERATIN LIMITS. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING | [5 empty] | YES | ELECTROCHEMICAL CORROSION AS A RESULT OF POOR INTERNAL COATING APPLICATION, INADEQUATE COATING ADHESION, AND INTERNAL CONDITIONS CONDUCIVE TO ELECTROCHEMICAL CORROSION. SALT AND WATER WERE FOUND IN THE SLUDGE COLLECTED FROM THE DRIP. |  | YES | [6 empty] | YES | 4 O'CLOCK POSITION IN PIPE COMPRISING DRIP ASSEMBLY | NO | YES | NOT APPLICABLE - NOT MAINLINE PIPE | YES | [313 empty] | KENNETH C. PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | ken.peters@elpaso.com | 2053257554 | 2053253729 |  |  |  | KENNETH C. PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | 2053257554 | ken.peters@elpaso.com | A LOCAL LANDOWNER NOTIFIED TENNESSEE GAS PIPELINE (TGP) COMPANY GAS CONTROL PERSONNEL OF A SUSPECTED LEAK THAT TURNED OUT TO BE AT THE DRIP ASSEMBLY OFF OF TGP'S 500-2 PIPELINE IN THE BARNETT COMMUNITY NEAR PACHUTA, MISSISSIPPI. TGP FIELD PERSONNEL RESPONDED TO ISOLATE AND BLOW DOWN THE VALVE SECTION AS LOCAL RESIDENTS WERE EVACUATED AS A PRECAUTION BY LOCAL EMERGENCY RESPONDERS. THE LEAKING DRIP ASSEMBLY HAS SINCE BEEN REMOVED AND REPLACED WITH STRAIGHT LINE PIPE (36" OD) AND THE SEGMENT WAS RETURNED TO SERVICE. INVESTIGATION AND METALLURGICAL ANALYSIS CONCLUDED THAT THE CAUSE WAS ELECTROCHEMICAL CORROSION AS A RESULT OF POOR INTERNAL COATING APPLICATION, INADEQUATE COATING ADHESION, AND INTERNAL CONDITIONS CONDUCIVE TO ELECTROCHEMICAL CORROSION. SALT AND WATER WERE ALSO FOUND IN THE SLUDGE COLLECTED FROM THE DRIP.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110040 | 15822 | 2011-04-14 17:21 | SUPPLEMENTAL FINAL | 22655 | WILLISTON BASIN INTERSTATE PIPELINE CO | 1250 WEST CENTURY AVENUE | BISMARCK | ND | 58503 | 2011-03-16 20:15 | 2011 |  |  | 46.5944 | -104.405 | 970704 | 2011-03-21 12:30 |  | NATURAL GAS |  | 3700 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-03-17 09:15 | 2011-04-13 10:17 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-03-16 20:15 | 2011-03-16 20:36 | ONSHORE | MT | 59313 | BAKER | FALLON | SURVEY STATION NO. | 6+00 | STORAGE LINE | #7 WELL LINE | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | IN OR SPANNING AN OPEN DITCH |  |  |  | YES | YES | UNCASED | [20 empty] | INTERSTATE | ABOVEGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | PIPE | PIPE BODY | 3.5 |  | 0.216 | 24000 | UNKNOWN | SEAMLESS |  | UNKNOWN | NONE | [28 empty] | 1926 | 1926 | CARBON STEEL |  | RUPTURE | [6 empty] | 11 |  |  | CLASS 1 LOCATION | NO |  | 50 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 14292 | 9671.85079928952 | 2740 | 3205.97309965356 | 540 | 631.834114530263 | 0 | 0 | THIS WAS A THREE INCH LINE WHICH WAS INEXPENSIVE TO FIX. |  | 17572 | 11788.9016705392 | 13509.6580134733 | [8 empty] | 156 |  | 400 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION IN STORAGE FIELD | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [52 empty] | HEAVY RAINS/FLOODS |  | OTHER |  |  | THIS SPAN WAS FLOODED COMPLETELY. THERE WAS ICE AND DEBRI THAT WAS FLOATING DOWN THE CREEK THAT WAS HITTING AND/OR SNAGGING THE THREE INCH LINE WHICH CAUSED IT TO FAIL. | YES |  |  |  | YES | WE HAD AN EXTREME AMOUNT OF SNOWPACK IN THIS AREA. THE WEATHER TURNED WARM AND MELTING OCCURRED QUITE FAST WHICH RESULTED IN LOCAL FLOODING OF THIS AREA (SOUTH FORK OF CABIN CREEK). | [301 empty] | KENT KAHL | DOT COMPLIANCE SUPERVISOR | kent.kahl@wbienergy.com | 406-359-7222 | 406-359-7225 |  |  |  | KENT KAHL | DOT COMPLIANCE SUPERVISOR | 406-359-7222 | kent.kahl@wbienergy.com | THIS INCIDENT OCCURRED AT A THREE INCH STORAGE WELL LINE SPAN OVER THE SOUTH FORK OF CABIN CREEK ON THE EVENING OF MARCH 16TH. THE THREE INCH LINE FAILED DUE TO EXTERNAL FORCES FROM WATER, ICE AND DEBRIS FROM A LOCALIZED SPRING THAW/FLOOD EVENT. THIS AREA IS REMOTE WITH ONE RESIDENCE (FORMER COMPANY FIELDMAN HOUSE) LOCATED APPROXMIATELY 1,600 FEET FROM THE SPAN. AT THE TIME OF FAILURE THE RESIDENT (RETIRED EMPLOYEE) HEARD THE ESCAPING GAS AND CALLED OUR CABIN CREEK STATION WHO CALLED GAS CONTROL. PERSONNEL WERE DISPATCHED TO INVESTIGATE HOWEVER THEY COULD NOT ACCESS THE IMMEDIATE AREA OF THE LINE BREAK DUE TO FLOODING. THE PIPELINE FEEDING THE BREAK FROM THE MAINLINE WAS SHUT IN THAT EVENING. DUE TO THE HAZARDOUS CONDITIONS ASSOCIATED WITH FLOODING AND THE REMOTE LOCATION (NO AFFECTED PUBLIC), COMPANY PERSONNEL CHOSE TO WAIT UNTIL THE NEXT MORNING TO ATTEMPT TO GET TO THE WELL. THE NEXT MORNING WATER HAD RECEDED TO THE POINT WHERE THEY COULD CLEAR ICE FROM AN ACCESS BRIDGE WITH A BACKHOE, ACCESS THE WELL AND SHUT IT IN ON MARCH 17TH. THIS LINE IS NOT METERED SO IT WAS DIFFICULT TO DETERMINE GAS LOSS. IT WAS FINALLY DETERMINED THROUGH MODELING THAT THE GAS LOSS DID EXCEED 3 MMCF AND IS REPORTED IN THIS INCIDENT REPORT AS 3.6 MMCF. THE WELL LINE WAS SHUT OFF UNTIL THE AREA DRIED OUT AND THE LINE WAS REPAIRED. THIS WAS COMPLETED ON APRIL 13TH. PIPE GRADE IS LISTED AS 24K (UNKNOWN GRADE). THE WELL WAS COMPLETED IN 1926 SO USED 1926 FOR PIPE MANUFACTURE AND INSTALLATION DATE. A PICTURE OF THE SPAN TAKEN ON THE MORNING OF MARCH 17TH IS ATTACHED. APPENDED PART E5F TO STORAGE GATHERING PER DOT EMAIL REQUEST FROM BLAINE KEENER ON 3/4/13.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110041 | 15330 | 2011-04-20 11:32 | SUPPLEMENTAL FINAL | 6660 | GREAT LAKES GAS TRANSMISSION CO | 700 LOUISIANA STREET | HOUSTON | TX | 77002 | 2011-04-06 09:00 | 2011 |  |  | 42.7881 | -82.4778 | 972153 | 2011-04-06 11:39 |  | NATURAL GAS |  | 1 | 8600 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-04-06 09:00 | 2011-04-19 17:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-04-06 09:00 | 2011-04-06 09:00 | ONSHORE | MI | 48054 | ST. CLAIR | ST. CLAIR | MILEPOST | MP 972.92 | 100 LINE |  | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | FLANGE ASSEMBLY | [38 empty] | 1967 |  | CARBON STEEL |  | LEAK |  |  | OTHER | GASKET | [5 empty] | CLASS 3 LOCATION | YES | METHOD2 | 516 |  | NO | NO | NO |  | 0 | 0 | 35610 | 41665.9496637457 | 5 | 3.38365896980462 | 325000 | 380270.531893214 | 0 | 0 | 0 | 0 |  |  | 360615 | 193683.486594892 | 421939.865215929 | [8 empty] | 800 |  | 974 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | AUTOMATIC | 735 | NO | [5 empty] | YES | YARD PIPING | YES |  |  |  |  | YES | YARD PIPING | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS EXTREMELY SMALL FROM A FLANGE WHICH WOULD NOT AFFECT FLOW DATA AND, THUS, WOULD NOT BE NORMALLY DETECTED THROUGH SCADA BY A GAS CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [52 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | OTHER |  |  |  | POSSIBLE SOIL SETTLEMENT RESULTING IN DOWNWARD SETTLING OF 24"PIPE THAT RESULTED IN FLANGE COCKING SLIGHTLY THUS CAUSING A SMALL LEAK PAST GASKET AT APPROXIMATE 12 O'CLOCK POSITION. | NO | [306 empty] | ROBERT J. CADORIN | SENIOR REGULATORY COMPLIANCE SPECIALIST | robert_cadorin@transcanada.com | 248-205-7669 |  |  |  |  | ROBERT J. CADORIN | SENIOR REGULATORY COMPLIANCE SPECIALIST | 248-205-7669 | robert_cadorin@transcanada.com | INVESTIGATION OF SLIGHT BUBBLING EMANATING FROM THE GROUND DURING THE ANNUAL CP SURVEY AT THE MLV/LAUNCHER SITE REVEALED THAT NATURAL GAS WAS LEAKING FROM A FLANGE LOCATED UNDERGROUND. POSSIBLE SOIL SETTLEMENT MOST LIKELY RESULTED IN A DOWNWARD SETTLING OF THE 24" PIPE ON THE DOWNSTREAM SIDE OFF THE FLANGE. THIS IN TURN THAT CAUSED THE FLANGE TO COCK SLIGHTLY, THUS CAUSING A SMALL LEAK PAST THE GASKET AT THE APPROXIMATE 12 O'CLOCK POSITION. BECAUSE THE FLANGE COULD NOT BE SEPARATED, IT WAS CUT OUT ALONG WITH A VALVE A FEW FEET UPSTREAM OF THE FLANGE, AS WELL AS SOME DOWNSTREAM PIPING AND A SMALLER CROSSOVER VALVE TO RELIEVE THE SOIL STRESSES ON THE PIPING. NEW PIPE WAS INSTALLED WITHOUT REPLACING THE FLANGE OR VALVES.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110042 | 16037 | 2011-04-22 12:50 | SUPPLEMENTAL FINAL | 5304 | FLORIDA GAS TRANSMISSION CO | 42 LONGWATER DRIVE PO BOX 9149 | NORWELL | MA | 02061 | 2011-03-24 15:00 | 2011 |  |  | 30.1435 | -83.3336 | 971066 | 2011-03-24 17:10 |  | NATURAL GAS |  | 3524 | 182 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-03-24 21:10 | 2011-03-26 15:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-03-24 15:00 | 2011-03-24 15:15 | ONSHORE | FL | 32066 | BUCKVILLE | LAFAYETTE | MILEPOST | 0 | MADISON LATERAL CROSSOVER | FLBJM | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 44 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 2 |  | 0.154 | 24000 | UNKNOWN | LONGITUDINAL ERW - LOW FREQUENCY |  | UNKNOWN | FIELD APPLIED EPOXY | [28 empty] | 1966 | 1965 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 51 |  | NO | NO | NO |  | 0 | 0 | 728 | 851.805991440799 | 14095 | 9538.53463587922 | 754 | 882.227633992256 | 17210 | 20136.7872427145 | 41529 | 48591.5535969024 | COST TO PROVIDE ALTERNATE GAS SERVICE TO THE TOWN OF MADISON DURING THE OUTAGE. |  | 74316 | 42233.121129926 | 80000.9091009291 | [8 empty] | 960 |  | 975 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 61766 | NO | [5 empty] | YES | ILI TOOLS ARE NOT AVAILAVLE FOR THIS SMALL DIAMETER | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER WAS NOT INVOLVED IN THE DETECTION OR RESPONSE TO THE INCIDENT | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | [10 empty] | YES |  |  | YES | PRIVATE LANDOWNER | [7 empty] | UTILITY | BACKHOE/TRACKHOE | NATURAL GAS | YES | 8110825 | SUNSHINE STATE ONE-CALL | UTILITY OWNER | YES | NO | NO |  | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO MAINTAIN CLEARANCE | [263 empty] | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | EMPLOYEE WAS EXCAVATING TO INSTALL AN ISOLATION CAP FOR HYDROSTATIC TESTING. FAILURE WAS A 4 INCH LONG BY 1/8 INCH WIDE CRACK. PIPE VINTAGE OF 1965 BASED UPON PIPE OTHER PIPE PURCHASED FOR THE PROJECT. **THIS REPORT IS BEING SUBMITTED IN RESPONSE TO PHMSA'S REQUEST, (DOCKET ID PHMSA-2013-0028), FOR SUPPLEMENTAL REPORTS FROM OPERATORS WHO SUBMITTED REPORTS FOR INCIDENTS OCCURRING AFTER JANUARY 1, 2010, WITH ANY OF THE FOLLOWING: (1) ``PIPE GIRTH WELD'' WAS SELECTED AS THE ``ITEM INVOLVED IN INCIDENT'' IN PART C3 OF THE REPORT. THE REVISED REPORT COLLECTS DATA ABOUT THE PIPE ADJACENT TO THE GIRTH WELD. (2) ``FUNCTION OF PIPELINE SYSTEM'' IS NULL IN PART E5F OF THE REPORT. THE REVISED REPORT COLLECTS THE FUNCTION OF THE PIPELINE SYSTEM FOR ALL INCIDENTS.** PART E5F OF THIS REPORT HAS BEEN COMPLETED.
2021-02-26 10:37 | NO | NO | GG (Gas Gathering) | 20110043 | 16117 | 2011-04-25 19:32 | SUPPLEMENTAL | 31130 | DCP MIDSTREAM | 370 17TH STREET SUITE 2500 | DENVER | CO | 80202 | 2011-03-25 11:18 | 2011 |  |  | 29.8222 | -94.3444 | 97115 | 2011-03-25 13:59 |  | NATURAL GAS |  | 9000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE RELEIF DEVICE RELIEVED GAS TO PROTECT THE MAOP | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-03-25 11:18 | 2011-03-25 12:00 | ONSHORE | TX | 77665 | WINNIE | JEFFERSON | MILEPOST | WINNIE,TX | WINNIE COMPRESSOR STATION | WINNIE COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | RELIEF VALVE |  |  | CARBON STEEL |  | OTHER | [8 empty] | OVER PRESSURE PROTECTION RELIEF DEVICE RELEASED NATURAL GAS TO THE ATMOSPHERE FROM A GAS GATHERING PIPELINE SYSTEM. | CLASS 2 LOCATION | NO |  | 2640 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 40500 | 27407.6376554174 | 0 | 0 | 1000 | 1170.06317505604 | 0 | 0 | GAS LOST AND FIELD TECH PAY |  | 41500 | 28951.8323227665 | 28577.7008304734 | [8 empty] | 720 |  | 720 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TYPE A GATHERING | NO |  |  |  |  | OTHER | AUDIBLE |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CAUSE FOR THE RELEASE WAS TO DO A MOTOR VEHICLE STRUCK A POWER LINE POLE INTERRUPTING THE POWER SUPPLY TO THE PLANT RESULTING IN THE OVER PRESSURE PROTECT VALVE TO FAIL SAFE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [103 empty] | OTHER OUTSIDE FORCE DAMAGE | [9 empty] | THE CAUSE FOR THE RELEASE WAS TO DO A MOTOR VEHICLE STRUCK A POWER LINE POLE INTERRUPTING THE POWER SUPPLY TO THE PLANT RESULTING IN THE OVER PRESSURE PROTECT VALVE TO FAIL SAFE. | [251 empty] | ROBERT J HURT | PIPELINE COMPLIANCE SPECIALIST | rjhurt@dcpmidstream.com | 713-248-7362 | 713-735-3141 |  |  |  | ROBERT J HURT | PIPELINE COMPLIANCE SPECIALIST | 713-248-7362 | rjhurt@dcpmidstream.com | ON MARCH 25, 2011 AN OVER PRESSURE PROTECTION RELIEF DEVICE RELEASED NATURAL GAS TO THE ATMOSPHERE FROM A GAS GATHERING PIPELINE SYSTEM. A POWER OUTAGE OCCURRED IN THE AREA OF THE DCP MIDSTREAM PLANT IN PORT AUTHOR, TEXAS. AN EMERGENCY VALVE WAS CLOSED SHUT, PROTECTING THE PLANTS PIPING RESULTING IN THE PACKING OF THE PIPELINE. THE PIPELINE SYSTEM WHICH TRANSPORTS GAS FROM MULTIPLE PRODUCERS AND A COMPRESSOR STATION LOCATED IN WINNIE, TEXAS WHERE THE OVER PRESSURE PROTECTION DEVICE IS LOCATED. THE RELIEF DEVICE RELIEVED GAS FOR APPROXIMATELY 1 HOUR BEFORE THE BLOCK VALVE LOCATED AT THE PORT ARTHUR PLANT WAS OPENED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110044 | 15924 | 2011-04-26 13:53 | SUPPLEMENTAL FINAL | 13769 | NORTHERN BORDER PIPELINE COMPANY | 717 TEXAS AVENUE | HOUSTON | TX | 77002 | 2011-03-28 15:16 | 2011 |  |  | 48.25 | -105.3211 | 971446 | 2011-03-29 14:28 |  | NATURAL GAS |  | 46280 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-03-28 15:16 | 2011-03-28 18:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 |  |  | ONSHORE | MT | 59201 | WOLF POINT | ROOSEVELT | MILEPOST | MT 106.70 | WOLF POINT COMPRESSOR STATION | 6006000 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | MAINLINE | BALL |  | CAMERON |  |  |  | 1982 | 1982 | CARBON STEEL |  | OTHER | [8 empty] | COMPRESSOR STATION EMERGENCY SHUTDOWN (ESD), THE STATION DISCHARGE VALVE FAILED TO CLOSE | CLASS 1 LOCATION | NO |  | 1098 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 138840 | 93957.4422735346 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 138840 | 97409.946714032 | 93957.4422735346 | [8 empty] | 1200 |  | 1440 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PANEL LOCKUP THAT RESULTED IN THE STATION ESD WAS THE RESULT OF AN ELECTRONIC ISSUE WITH THE PANEL. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [30 empty] | YES | VALVE FAILED TO CLOSE DURING ESD | [161 empty] | DANIEL CERKONEY | COMPLIANCE ENGINEER | dan_cerkoney@transcanada.com | 701-483-1434 | 701-483-1431 |  |  |  | DANIEL CERKONEY | COMPLIANCE ENGINEER | 701-483-1434 | dan_cerkoney@transcanada.com | THE COMPRESSOR STATION EMERGENCY SHUTDOWN (ESD) WAS CAUSED BY A CONTROL PANEL LOCK UP. WHEN THE STATION ESD OCCURRED, THE STATION DISCHARGE VALVE FAILED TO CLOSE. THE INACTIVATION OF THE VALVE RESULTED IN NATURAL GAS TO VENT FROM THE PIPELINE UNTIL TECHNICIANS RESPONDED AND MANUALLY CLOSED THE STATION BLOWDOWN VALVE TO STOP THE RELEASE OF GAS. THE VALVE WAS CLOSED APPROXIMATELY 40 MINUTES AFTER THE ESD. TROUBLESHOOT COMPONENTS ON VALVE OPERATOR. OPERATION WAS TESTED NUMEROUS TIMES AND FUNCTIONED AS DESIGNED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110045 | 15555 | 2011-04-28 16:56 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2011-03-31 11:15 | 2011 |  |  | 38.5763 | -82.9396 | 971625 | 2011-03-31 13:07 |  | NATURAL GAS |  | 1000 | 5200 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES | [7 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-03-31 11:15 | 2011-03-31 11:15 | ONSHORE | KY | 41144 | GREENUP | GREENUP | SURVEY STATION NO. | 6866 | LINE 200-1 | 200-1D | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 26 |  | 0.281 | 52000 | API 5L OR EQUIVALENT | FLASH WELDED |  | A.O. SMITH | COAL TAR | [28 empty] | 1950 | 1950 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 2 LOCATION | NO |  | 504 |  | NO | NO | NO |  | 1000 | 1170.06317505604 | 20800 | 24337.3140411657 | 4000 | 2706.92717584369 | 168930 | 197658.772162217 | 600 | 702.037905033625 | 0 | 0 |  |  | 195330 | 105567.799451684 | 226575.114459316 | [8 empty] | 678 |  | 790 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 44020 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | AIR PATROL |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE WAS WITHIN OPERATING LIMITS AND BELOW MAOP. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED |  | YES | [15 empty] | STRESS CORROSION CRACKING | [5 empty] | YES | [63 empty] | YES | YES |  |  | YES |  |  |  | 1991 | [31 empty] | 1991 | [23 empty] | YES | 1969 | 1051 | NO | [13 empty] | NO | [63 empty] | KENNETH C. PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | ken.peters@elpaso.com | 2053257554 | 2053253729 |  |  |  | KENNETH C. PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | 2053257554 | ken.peters@elpaso.com | A POTENTIAL LEAK WAS FOUND ON TENNESSEE GAS PIPELINE (TGP) COMPANY'S 26" 200-1D PIPELINE NEAR GREENUP, KENTUCKY, BY AN AERIAL INSTRUMENTED LEAK SURVEY. EXCAVATION AND INVESTIGATION OF THE LEAK REVEALED A SMALL CRACK ON THE TOP OF THE PIPE BODY. THE PIPE WAS REPAIRED BY INSTALLING A NEW SEGMENT WITH THE DEFECTIVE SECTION BEING REMOVED AND SENT TO THE COMPANY'S LABORATORY FOR METALLURGICAL ANALYSIS. THE METALLURGICAL ANALYSIS HAS BEEN COMPLETED AND EXTERNAL STRESS CORROSION CRACKING WAS DETERMINED TO BE THE CAUSE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110046 | 15367 | 2011-05-05 13:11 | SUPPLEMENTAL FINAL | 6640 | GRAYVILLE GAS DEPT, CITY OF | 122 S COURT ST | GRAYVILLE | IL | 62844 | 2011-05-04 22:30 | 2011 |  |  | 38.1833 | -87.9805 | 974929 | 2011-05-05 10:05 |  | NATURAL GAS |  | 5500 | 100 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-05-05 08:30 | 2011-09-29 14:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-05-04 23:00 | 2011-05-04 23:15 | ONSHORE | IL | 62844 | GRAYVILLE | WHITE | MILEPOST | 4.3 MILES SSE | CITY OF GRAYVILLE TRANSMISSION MAIN | 6" | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6.625 |  | 0.188 | 42000 | API 5L GRADE B | SEAMLESS |  | UNKNOWN | EPOXY | [28 empty] | 1964 | 1963 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 6 | 6 |  | CLASS 1 LOCATION | NO |  | 100 |  | NO | NO | NO |  | 1000 | 1170.06317505604 | 500 | 585.031587528021 | 27500 | 18610.1243339254 | 150000 | 175509.476258406 | 5000 | 5850.31587528021 | 0 | 0 |  |  | 184000 | 103348.525830899 | 201725.011230196 | [8 empty] | 400 |  | 480 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 15840 | NO |  | YES | YES | YES |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | NO |  |  |  |  | OTHER | DISTRIBUTION COMPANY OTHER THAN OPERATOR SERVED BY SAME LINE, PRESSURE ALARM |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [52 empty] | HEAVY RAINS/FLOODS |  | WASHOUTS/SCOURING |  |  |  | YES |  |  |  | YES | EXTREME HIGH WATER/FLOODING | [301 empty] | C. LINDSAY ENLOE | GAS ENGINEER | lindsay@usdi.us | 6182771520 | 6182771586 |  |  |  | ANDY BROCK | GAS COMMISIONER | 6183753671 | grayville@frontier.com | AT APPROXIMATELY 10:30 PM LOCAL TIME ON 5/4/2011 THE 6 INCH MAIN OWNED AND OPERATED BY THE CITY OF GRAYVILLE, ILLINOIS THAT SERVES GRAYVILLE, IL , CONSUMERS GAS COMPANY'S NORTH SYSTEM, AND MT. CARMEL PUBLIC UTILITY COMPANY RUPTURED IN A FLOOD PLAIN OF THE WABASH RIVER. THE PRESSURE MONITOR ON THE MT. CARMEL UTILITY SYSTEM INDICATED LOW PRESSURE AT APPROXIMATELY 11:00 PM. THE CITY OF GRAYVILLE WAS NOTIFIED AND THE INVESTIGATION REVEALED THAT THE PRESSURE AT THE GRAYVILLE STATION, WHICH NORMALLY OPERATES AT 400 PSIG, WAS IN THE NEIGHBORHOOD OF 100 PSIG. FURTHER INVESTIGATION REVEALED THAT THE 6 INCH TRANSMISSION MAIN HAD FAILED IN THE FLOOD PLAIN. THE 6 INCH MAIN WAS SHUT OFF AT THE GRAYVILLE STATION AT APPROXIMATELY 12:00 AM. THE SYSTEMS WERE KEPT IN OPERATION THROUGH THE 4 INCH TRANSMISSION MAIN THAT PARALLELS THE 6 INCH TRANSMISSION MAIN. THE 6 INCH VALVE AT THE TEXAS EASTERN DELIVERY POINT WAS STILL OPEN AND IT WAS DECIDED TO LEAVE THE VALVE OPEN UNTIL DAYLIGHT DUE TO THE DANGER OF TRAVERSING THE FLOOD PLAIN IN THE DARK. AT DAYLIGHT TWO BOATS WERE TAKEN TO THE DELIVERY POINT WHERE THE 6 INCH VALVE IS LOCATED. THE 6 INCH VALVE WAS CLOSED AT APPROXIMATELY 8:30 AM. THE 6 INCH MAIN IS UNDER SEVERAL FEET OF WATER AND THE DECISION ON REPAIRS WILL BE MADE WHEN THE WATER RECEDES AND THE SITE CAN BE ACCESSED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110047 | 15725 | 2011-05-06 18:03 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | TX | 77002 | 2011-04-13 15:30 | 2011 |  |  | 28.9767 | -91.9057 | 972875 | 2011-04-13 16:30 |  | NATURAL GAS |  | 2000 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | LINE WAS IN THE PROCESS OF BEING PRESSURED UP TO PLACE INTO SERVICE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 |  |  | OFFSHORE | [28 empty] | 100 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SOUTH MARSH ISLAND | 9 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12.75 |  | 0.375 | 46000 | API | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | AMERICAN STEEL | COAL TAR | [28 empty] | 1968 | 1968 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 323 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 5000 | 3383.65896980462 | 450000 | 526528.428775219 | 10000 | 11700.6317505604 | 0 | 0 |  |  | 465000 | 250569.333836716 | 541612.719495584 | [8 empty] | 250 |  | 1300 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 93000 | NO |  | YES |  | YES |  |  |  | YES |  | YES | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  | YES |  |  |  |  | YES | [5 empty] | YES |  |  |  | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | LOUIS SALINAS | COMPLIANCE ENGINEER | louis_salinas@transcanada.com | 832-320-5305 | 832-320-6305 |  |  |  | LOUIS SALINAS |  | 832-320-5305 | No Email Address | WHILE PERFORMING THE CLAMP INSTALLATION AND PRESSURE TEST ON THE 747 OFFSHORE PIPELINE, AN ADDITIONAL LEAK APPEARED IN THE EARLY STAGES OF THE PRESSURE TEST. THE PRESSURE TEST WAS IMMEDIATELY STOPPED WITH INTERNAL AND EXTERNAL NOTIFICATIONS BEING MADE. REVISED REPAIR OPTIONS AND METHODS WERE EVALUATED. A REPAIR CLAMP WAS INSTALLED IN SEPTEMBER 2012.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110049 | 15402 | 2011-05-12 17:40 | SUPPLEMENTAL FINAL | 6660 | GREAT LAKES GAS TRANSMISSION CO | 700 LOUISIANA STREET | HOUSTON | TX | 77002 | 2011-04-13 13:45 | 2011 |  |  | 45.2611 | -84.7687 | 972854 | 2011-04-13 15:03 |  | NATURAL GAS |  | 3000 | 25500 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-04-13 13:45 | 2011-04-29 17:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-04-13 13:45 | 2011-04-13 13:45 | ONSHORE | MI | 49713 | BOYNE FALLS | CHARLEVOIX | MILEPOST | 722.81 | BOYNE FALLS COMPRESSOR STATION (CS 11) | 100 LINE | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 72 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1973 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 775 |  | NO | NO | NO |  | 0 | 0 | 115000 | 134557.265131445 | 12420 | 8405.00888099467 | 114000 | 133387.201956389 | 0 | 0 | 0 | 0 |  |  | 241420 | 131707.434950831 | 276349.475968828 | [8 empty] | 800 |  | 974 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | AUTOMATIC | 91290 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS MINOR IN NATURE, EMANATING FROM UNION CONNECTION ON A BELOW GROUND VALVE BODY BLEED FITTING. THIS WOULD NOT AFFECT GAS FLOW SUFFICIENTLY TO BE DETECTED VIA SCADA. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | THREADED FITTING | [16 empty] | YES | [165 empty] | ROBERT CADORIN | REGULATORY COMPLIANCE SPECIALIST | robert_cadorin@transcanada.com | 248-205-7669 |  |  |  |  | ROBERT CADORIN | REGULATORY COMPLIANCE SPECIALIST | 248-205-7669 | robert_cadorin@transcanada.com | LEAK WAS DETECTED AS BUBBLES ARISING ADJACENT TO THE 100 LINE PIG LAUNCHER VALVE 100-0-L. THE LAUNCHER AND VALVE ARE LOCATED WITHIN THE FENCED, COMPRESSOR STATION YARD. FOLLOWING A 20% PRESSURE REDUCTION AND EXCAVATION OF THE VALVE, IT WAS DETERMINED THAT THE BODY BLEED FITTING ON THE BOTTOM OF THE VALVE WAS LEAKING AT THE THREADED CONNECTION. THE PIPELINE VALVE SECTION WAS THEN BLOWN DOWN TO SAFELY MAKE REPAIRS. THE BODY BLEED FITTING AND ASSOCIATED PIPING WERE REMOVED AND REPLACED. FIELD EXAMINATION OF THE REMOVED PIPING AND FITTING DETERMINED THE CAUSE OF THE LEAK TO BE A POSSIBLE MISALIGNMENT OF THE PIPE UNION ON THE UNDERGROUND PORTION OF THE VALVE'S BODY BLEED PIPING. NO LEAKAGE WAS OBSERVED AT THE PIPE THREADS OF THIS FITTING DURING THE EXAMINATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110050 | 15354 | 2011-05-12 17:40 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2011-04-29 14:16 | 2011 |  |  | 44.2502 | -94.9546 | 974422 | 2011-04-29 15:42 |  | NATURAL GAS |  | 4114 | 73 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | UTILIZED STOPPLES TO MAINTAIN CUSTOMER SERVICE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-04-29 14:19 | 2011-04-29 15:30 | ONSHORE | MN | 56087 | SPRINGFIELD | BROWN | MILEPOST | 0.2 | 6-INCH TRACY, MINNESOTA BRANCH LINE | MNB65201 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 38 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 |  | 0.156 | 42000 | 5LX | LONGITUDINAL ERW - LOW FREQUENCY |  | REYNOLDS | EXTRUDED POLYEHYLENE | [28 empty] | 1967 |  | CARBON STEEL |  | MECHANICAL PUNCTURE | 0.5 | 1.5 | [7 empty] | CLASS 1 LOCATION | NO |  | 117 |  | NO | NO | NO |  | 0 | 0 | 335 | 391.971163643774 | 18485 | 12509.3872113677 | 28820 | 33721.2207051151 | 38704 | 45286.125127369 | 147546 | 172638.141226819 | CONTRACTOR COSTS. |  | 233890 | 128660.893528149 | 264546.845434314 | [8 empty] | 700 |  | 796 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 400 | NO | [5 empty] | YES | THIS LINE DOES NOT HAVE ANY HCA'S SO IT HAS NOT BEEN ASSESSED FOR PIGGABLE CAPABILITIES. | YES |  |  |  |  | YES | NOT ASSESSED FOR PIGGING CAPABILITIES | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LINE WAS HIT BY CONTRACT TILER WHICH CONTROLLERS HAD NO CAPABILITY OR CONTROL TO MONITOR. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | TRENCHER | DRAINAGE | YES | 111110360 | GOPHER STATE ONE CALL | UNKNOWN/OTHER | NO | NO |  |  | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NOTIFICATION TO ONE-CALL CENTER MADE, BUT NOT SUFFICIENT | [265 empty] | BYRON WOOD | SR. PIPELINE SAFETY SPECIALIST | byron.wood@nngco.com | 402-398-7396 | 402-398-7606 |  |  |  | THOMAS CORELL | DIRECTOR OF PIPELINE SAFETY AND INTEGRITY | 402-398-7715 | thomas.correll@nngco.com | ON APRIL 29, 2011, AT APPROXIMATELY 14:16, LARRY POTTER AT 38364 200TH ST., SPRINGFIELD, MN 56087, CONTACTED NORTHERN NATURAL GAS COMPANY'S (NORTHERN) OPERATIONS COMMUNICATION CENTER (OCC) TO REPORT THAT A PIPELINE LOCATED ON HIS PROPERTY HAD BEEN HIT BY A CONTRACTOR HE HAD HIRED TO INSTALL DRAINAGE TILE ON HIS PROPERTY. MR. POTTER INDICATED THAT THERE WAS DAMAGE TO THE PIPELINE AND THAT GAS WAS VENTING TO ATMOSPHERE. THE LOCATION OF THE DAMAGED PIPELINE IS THE TRACY BRANCH LINE AT APPROXIMATE MILEPOST 0.20. THE LEGAL DESCRIPTION IS SECTION NW1/2 17, TOWNSHIP 109N, RANGE 34W ALL IN BROWN COUNTY, MINNESOTA APPROXIMATELY 1/2 MILE NORTH OF U.S. HIGHWAY 14 AND 1/8 MILE EAST OF COUNTY ROAD 5. NORTHERN IMMEDIATELY DISPATCHED EMPLOYEES TO THE SITE AND UPON ARRIVAL THEY CONFIRMED THAT IT WAS NORTHERN'S TRACY, MN (MNB65201) 6-INCH BRANCH LINE THAT HAD BEEN HIT. THERE WAS NO FIRE, NO EXPLOSION, NO INJURIES AND NO EVACUATIONS. A GAS DETECTOR WAS UTILIZED TO CHECK THE AREA AND A 20% LEL READING WAS INDICATED APPROXIMATELY 50 YARDS DOWNWIND. A PIR OF 109 FEET WAS ESTABLISH AS A SAFE ZONE RADIUS AROUND THE INCIDENT SITE. THE TRACY BRANCH LINE PROVIDES GAS SERVICE TO THE TOWNS OF SANBORN, WALNUT GROVE, REVERE AND TRACY, MINNESOTA AND THE HIGHWATER ETHANOL PLANT. BOTTLE TRUCKS WERE BROUGHT IN FROM WATERLOO, IA, FARMINGTON, MN, SOUTH SIOUX CITY, IA, OGDEN, IA AND NORTH BRANCH, MN AS BACKUPS TO SUPPLY GAS TO THE TOWNS DURING THE REPAIR PROCESS. A STOPPLE BYPASS HAD TO BE INSTALLED TO MAINTAIN SERVICE TO THE HIGHWATER ETHANOL PLANT DURING THE PIPELINE REPAIRS. APPROXIMATELY 31 FEET OF 6-INCH NOMINAL DIAMETER PIPE WAS REPLACED WITH NEW 6-INCH, 0.280 WALL THICKNESS, ERW, GRADE X42 TESTED PIPE WITH FBE COATING. ROOT CAUSE OF THIS EVENT: THE LANDOWNER HAD MADE A ONE CALL, HOWEVER IT APPEARS THAT THE DESCRIPTION OF THE WORK AREA DID NOT COVER THE AREA OF HIS PROPERTY THAT THE PIPELINE CROSSED, THEREFORE NORTHERN DID NOT RECEIVE NOTIFICATION OF A ONE CALL REQUEST TO LOCATE AND MARK THE PIPELINE ON THE PROPERTY. THERE WAS REQUIRED PERMANENT LINE MARKERS IN THE FENCE LINES INDICATING THE PRESENCE OF A PIPELINE ON THE PROPERTY. THIS IS BEING INVESTIGATED FURTHER BY NORTHERN WITH THE LANDOWNER/CONTRACTOR AND THE ONE CALL CENTER. FILING OF AN INCIDENT REPORT WAS REQUIRED AS THE COST TO COMPLETE REPAIRS EXCEEDED THE $50,000.00 REPORTING THRESHOLD. A SUPPLEMENTAL REPORT WILL BE FILED WHEN ALL FINAL COST OF REPAIRS IS CALCULATED. SUPPLEMENTAL/FINAL REPORT: REVISED COST INCURRED IN PART D, SECTION 7 AS A FINAL ESTIMATED OF ALL COST HAVE BEEN CALCULATED BY NORTHERN. NO FURTHER ACTIONS ARE REQUIRED OR PLANNED OTHER THAN FOLLOW UP BY NORTHERN'S LEGAL DEPARTMENT. THIS FINAL REPORT IS SUBMITTED TO CLOSE OUT THE ORIGINAL REPORT NO. 20110050 -15237 DATED 05/12/2011. SUPPLEMENTAL/FINAL REPORT FILED ON ORIGINAL REPORT # 20110050-15237 DTD 05/12/2011 AND PREVIOUS SUPPLEMENTAL/FINAL REPORT #20110050-15284 TO UPDATE AREAS FROM DISCUSSION WITH MNOPS REPRESENTATIVES REVIEW I.E., UPDATED A7, FILLED IN 19A AND 19B THAT DID NOT CARRY OVER FROM ORIGINAL REPORT, ATTEMPTED TO PUT UNKNOW IN YEAR OF MANUFACTURE BUT FORM WOULD NOT ALLOW, REVISED PIR TO 117 FEET BASED ON 796 MAOP, LENGTH OF 400 FEET OF PIPE ISOLATED WAS DISTANCE BETWEEN STOPPLE VALVES (FORM WOULD NOT ALLOW ADDITIONAL DESCRIPTION). ATTEMPTED TO RESPOND TO G3, LINE 16 REGARDING DID THE DAMAGE CAUSE AN INTERRUPTION IN SERVICE WITH NO, HOWEVER THE FORM SHOWED NUMBERS 15 AND 17 BUT DID NOT LIST ITEM 16. THE EVENT IS CONSIDERED COMPLETE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110051 | 15392 | 2011-05-19 10:11 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2011-04-20 15:00 | 2011 |  |  | 29.0472 | -90.2293 | 973590 | 2011-04-20 16:20 |  | NATURAL GAS |  | 1 | 3615 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-04-21 15:00 | 2011-06-06 16:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-04-20 15:30 | 2011-04-21 02:00 | OFFSHORE | [28 empty] | 20 | IN STATE WATERS | LA | BAY MARCHAND | 5 | LAFOURCHE |  |  |  | BELOW WATER, PIPE ON OR ABOVE SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | OTHER | [37 empty] | 2" JUMPER BY-PASS LINE AROUND VALVE | 2003 |  | CARBON STEEL |  | OTHER | [8 empty] | 2" JUMPER BY-PASS LINE WAS SEVERED BY SHRIMPING NETS | CLASS 1 LOCATION | NO |  | 45 |  | NO | NO | NO |  | 0 | 0 | 14460 | 16919.1135113104 | 4 | 2.70692717584369 | 502000 | 587371.713878133 | 1000 | 1170.06317505604 | 0 | 0 |  |  | 517464 | 277925.331358653 | 605463.597491675 | [8 empty] | 674 |  | 1069 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 47520 | NO | [5 empty] | YES | LEAK WAS IN A 2" BY-PASS AROUND A VALVE WHICH DOES NOT LEND ITSELF TO PIGGING. | YES |  |  |  |  | YES | SEE 5D ABOVE. | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | PRODUCER PERSONNEL SAW BUBBLES FROM PLATFORM. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURES WERE WITHIN NORMAL OPERATING LIMITS. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ROUTINE OR NORMAL FISHING OR OTHER MARITIME ACTIVITY NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | FISHING OR MARITIME ACTIVITY | [103 empty] | ROUTINE OR NORMAL FISHING OR OTHER MARITIME ACTIVITY NOT ENGAGED IN EXCAVATION | [261 empty] | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | ken.peters@elpaso.com | 2053257554 | 2053253729 |  |  |  | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | 2053257554 | ken.peters@elpaso.com | PRODUCER PERSONNEL SAW BUBBLES FROM HIS PLATFORM IN THE VICINITY OF TENNESSEE GAS PIPELINE (TGP) COMPANY'S 524C-400 PIPELINE. HE REPORTED THIS TO TGP. UPON NOTIFICATION, TGP MOBILIZED TO ISOLATE THE LEAK AND SEND DIVERS DOWN TO INVESTIGATE IN LOUISIANA STATE WATERS, BAY MARCHAND BLOCK 5. DIVERS FOUND A BREAK IN THE 2" BY-PASS LINE AROUND A 6" TAP VALVE WHERE A LATERAL LINE BRANCHES OFF OF THE 16" 524C-400 LINE. THE PRESENCE OF SHRIMP NET PIECES INDICATED THAT A SHRIMPER CAUGHT A NET ON THE LINE WHICH SEVERED THE 2" PIPE. THE SUBSEA ASSEMBLY WAS REBUILT AND THE LINE WAS PLACED BACK INTO SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110052 | 15973 | 2011-05-20 09:58 | SUPPLEMENTAL FINAL | 31712 | GUARDIAN PIPELINE, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103-4298 | 2011-05-02 09:35 | 2011 |  |  | 43.8249 | -88.3188 | 974609 | 2011-05-02 11:40 |  | NATURAL GAS |  | 63.5 | 27115 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-05-02 10:50 | 2011-05-04 11:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-05-02 09:35 | 2011-05-02 09:35 | ONSHORE | WI | 53049 | ST. PETER | FOND DU LAC | MILEPOST | 51.27 | GUARDIAN PIPELINE | GUARDIAN II - MLV 513 TO MLV 514 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 78 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 30 |  | 0.298 | 70000 | API-5L PSL-2 | SPIRAL WELDED |  | CORINTH PIPE WORKS | EPOXY | [9 empty] | PIPE GIRTH WELD | [18 empty] | 2008 | 2007 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 654 |  | NO | NO | NO |  | 0 | 0 | 124729 | 145940.809761565 | 292 | 197.60568383659 | 100000 | 117006.317505604 | 20000 | 23401.2635011208 | 17645 | 20645.7647238639 | PURGE GAS |  | 262666 | 141123.284759402 | 307191.761175991 | [8 empty] | 803 |  | 999 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 98991 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS LEAK WAS REPORTED BY LANDOWNER AND CONFIRMED BY GUARDIAN EMPLOYEES. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | YES | [7 empty] | YES | [13 empty] | YES | YES |  |  |  | YES | [58 empty] | YES |  |  |  | YES | [35 empty] | 2008 | [23 empty] | NO |  |  | Yes, and an investigative dig was cunducted at the point of the Accident | 2008 | [12 empty] | YES | 2008 | [6 empty] | YES | [55 empty] | MARK A. MICKELBERG | SR GAS ENGINEER | mark.mickelberg@oneok.com | 1-651-994-0332 | 1-651-994-4553 |  |  |  | CRAIG A. FORSANDER | VICE PRESIDENT - NATURAL GAS PIPELINES | 1-918-588-7414 | craig.forsander@oneok.com | ON MAY 2, 2011 AT APPROXIMATELY 08:25 AM A LANDOWNER CALLED THE GUARDIAN RIGHT-OF WAY AGENT TO REPORT A POSSIBLE GAS LEAK. THE RIGHT-OF WAY AGENT NOTIFIED OPERATIONS WHICH INVESTIGATED THE LEAK SITE. THE INVESTIGATION REVEALED BUBBLES IN STANDING WATER, IN A CULTIVATED FIELD. GUARDIAN OPERATIONS PERSONNEL CONFIRMED THAT IT WAS A GAS LEAK AND PROCEEDED TO ISOLATED THE PIPELINE AND REDUCED THE PRESSURE FROM 803 PSIG DOWN TO 185 PSIG. THE LINE WAS EXPOSED AND A WELD DEFECT WAS SUSPECTED IN A 30" GIRTH WELD WHICH WAS ON A 8 FOOT LONG JOINT OF PIPE USED FOR REPAIR OF A DENT FOUND DURING THE CALIPER PIG RUN DURING THE ORIGINAL CONSTRUCTION. THE PIPELINE WAS BLOWN DOWN AND A 40 FOOT PIECE OF 30" .375" WALL GRADE X70 PRETESTED PIPE WAS INSTALL AT THE LEAK LOCATION. THE PIPELINE WAS RETURNED TO SERVICE ON MAY 5, 2011. A FAILURE ANALYSIS AND METALURGICAL STUDY WAS COMPLETED ON THE FAILED GIRTH WELD. THE REPORT INDICATES THE LEAKAGE WAS DUE TO LACK OF FUSION IN THE WELD AT THE 6 O'CLOCK POSITION ON THE GIRTH WELD AND WIDE WELD GAP DUE TO MISALIGNMENT. IN ADDITION TO THE WIDE ROOT GAP, THE USE OF ONLY TWO FILL PASSES IN THE AREA OF THE LEAKAGE ALSO CONTRIBUTED TO THE LACK OF FUSION AND RESULTING LEAK.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110053 | 15873 | 2011-05-20 10:56 | SUPPLEMENTAL FINAL | 19270 | TEXAS GAS TRANSMISSION LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2011-04-24 09:05 | 2011 |  |  | 37.5915 | -87.197 | 973865 | 2011-04-24 10:30 |  | NATURAL GAS |  | 23767 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | A RELIEF VALVE VENTED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-04-24 09:05 | 2011-04-24 09:42 | ONSHORE | KY | 42327 | GLENVILLE | MCLEAN | MILEPOST | 488.605 | MAINLINE SYSTEM |  | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1982 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE VENTED AT 820 PSIG SET POINT. | CLASS 1 LOCATION | NO |  | 157 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 95000 | 64289.5204262877 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 95000 | 66651.865008881 | 64289.5204262877 | [8 empty] | 820 |  | 810 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE EXCEEDED MAOP, BUT DID NOT EXCEED THE APPLICABLE ALLOWANCE IN 192.201 | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) | [6 empty] | YES | [6 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | PIPELINE OR EQUIPMENT OVERPRESSURED | INCORRECT OPERATION | PIPELINE/EQUIPMENT OVERPRESSURED | [204 empty] | PIPELINE OR EQUIPMENT OVERPRESSURED | [6 empty] | YES | PLEASE SEE SECTION H. | NORMAL OPERATING CONDITIONS | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 270-688-6357 | 270-688-5871 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 270-688-6361 | jeff.mcmaine@bwpmlp.com | ON 04-24-2011, AT APPROXIMATELY 7:35 AM, GAS CONTROL NOTED THE PIPELINE PRESSURE WAS INCREASING IN THE NORTHERN PART OF THE MAINLINE SYSTEM NEAR JEFFERSONTOWN STATION. AT THE TIME, THE DISCHARGE PRESSURE AT THE SLAUGHTERS STATION WAS 784 PSIG AND THE STATION TURBINE WAS RUNNING IN A SLOWED BACK POSITION. IN ORDER TO INCREASE THE INJECTIONS INTO OUR HANSON STORAGE FIELD, THE GAS CONTROLLER INCREASED THE TURBINE SPEED TO INCREASE PRESSURES ON THE DISCHARGE OF SLAUGHTERS TOWARD THE HANSON STORAGE FIELD. (THE HANSON FIELD IS 8 MILES FROM THE STATION ON THE STORAGE LATERAL LINE.) THE GAS CONTROLLER WAS WATCHING THE DISCHARGE PRESSURE INCREASE AT SLAUGHTERS STATION, BUT NOT THE RELIEF VALVE AT GLENVILLE, KY WHICH IS LOCATED 18 MILES DOWNSTREAM OF THE SLAUGHTERS STATION ON THE MAINLINE SYSTEM. AT ABOUT 8:45 AM, THE GAS CONTROLLER RECEIVED A HIGH ALARM AT THE GLENVILLE RELIEF VALVE. AT THAT TIME, HE SENT A REMOTE CHANGE TO REDUCE THE SPEED ON THE TURBINE AT SLAUGHTERS STATION. AT 9:15 AM HE RECEIVED A PHONE CALL FROM A PROPERTY OWNER ABOUT THE GLENVILLE RELIEF VALVE BLOWING. AT 9:40 AM, THE GAS CONTROLLER INITIATED AN ENGINE SHUTDOWN AT SLAUGHTERS STATION TO REDUCE THE PRESSURE TOWARD THE GLENVILLE RELIEF VALVE ON THE MAINLINE SYSTEM. AT 9:42 AM, FIELD PERSONNEL SHUT OFF THE RELIEF VALVE. ADDED DATA TO PART E5.F AS REQUESTED BY PHMSA.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110151 | 16025 | 2011-05-24 09:12 | SUPPLEMENTAL FINAL | 15105 | PANHANDLE EASTERN PIPELINE CO | 5051 WESTHEIMER ROAD | HOUSTON | TX | 770565306 | 2011-04-25 02:07 | 2011 |  |  | 39.5736 | -90.3549 | 973910 | 2011-04-25 04:45 |  | NATURAL GAS |  | 58700 | 5155 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-04-25 03:20 | 2011-05-05 08:10 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 30 | 2011-04-25 02:20 | 2011-04-25 03:26 | ONSHORE | IL | 62633 | MANCHESTER | SCOTT | SURVEY STATION NO. | 1666+17 | PLEASANT HILL 200 | 41-05-002-2000 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 10 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | COUPLING | 1940 |  | CARBON STEEL |  | OTHER | [8 empty] | PIPE PULLED OUT OF THE COUPLING | CLASS 1 LOCATION | NO |  | 429 |  | NO | NO | NO |  | 2000 | 2340.12635011208 | 21865 | 25583.4313226004 | 232728 | 157494.436944938 | 286759 | 335526.146015896 | 3000 | 3510.18952516813 | 20000 | 23401.2635011208 | OTHER COST IS FAILURE ANALYSIS ESTIMATE |  | 566352 | 342467.705429696 | 547855.593659835 | [8 empty] | 749 |  | 800 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 73898 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  |  | YES | [5 empty] | YES | LESSONS LEARNED REGARDING STAFFING, ALARM MANAGEMENT AND LABELING. | YES | 1 | 0 | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [52 empty] | HEAVY RAINS/FLOODS |  | FLOTATION |  |  |  | NO | [306 empty] | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | THE PLEASANT HILL 200 LINE IS 22-IN. OD X 0.281-IN. WT, API 5L GRADE X42, SEAMLESS PIPELINE. THE CAUSE OF THE COUPLING SEPARATION AT MP 31.5 WAS THE COMBINED EFFECT OF LOCAL LOSS OF SOIL COVER IN CONJUNCTION WITH RECENT HIGH RAINFALL. THE MONTH PRECEDING THE INCIDENT EXPERIENCED HISTORICALLY HIGH QUANTITIES OF RAINFALL. THE RESULTING WATER TABLE WAS HIGH ENOUGH TO PRODUCE UPWARD BUOYANT FORCES ON THE PIPE, WHILE THE PROBABLE SATURATION OF THE SOIL COVER REDUCED ITS BREAKOUT RESISTANCE. THE COMBINATION OF BUOYANT FORCES AND UPWARD THRUST FORCES PRODUCED BY AN APPARENT SMALL ANGULAR MISALIGNMENT AT THE SEPARATED COUPLING EXCEEDED THE UPTHRUST RESISTANCE OF THE SOIL. **THIS REPORT IS BEING SUBMITTED IN RESPONSE TO PHMSA'S REQUEST, (DOCKET ID PHMSA-2013-0028), FOR SUPPLEMENTAL REPORTS FROM OPERATORS WHO SUBMITTED REPORTS FOR INCIDENTS OCCURRING AFTER JANUARY 1, 2010, WITH ANY OF THE FOLLOWING: (1) ``PIPE GIRTH WELD'' WAS SELECTED AS THE ``ITEM INVOLVED IN INCIDENT'' IN PART C3 OF THE REPORT. THE REVISED REPORT COLLECTS DATA ABOUT THE PIPE ADJACENT TO THE GIRTH WELD. (2) ``FUNCTION OF PIPELINE SYSTEM'' IS NULL IN PART E5F OF THE REPORT. THE REVISED REPORT COLLECTS THE FUNCTION OF THE PIPELINE SYSTEM FOR ALL INCIDENTS.** THIS SUPPLEMENTAL REPORT IS TO ACKNOWLEDGE THAT THE TWO RELEVANT SECTIONS IN PHMSA'S REQUEST HAVE BEEN REVIEWED AND NO FURTHER ACTIONS WERE NEEDED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110158 | 16185 | 2011-05-26 17:03 | SUPPLEMENTAL FINAL | 31531 | ONEOK WESTEX TRANSMISSION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2011-04-26 08:15 | 2011 |  |  | 31.7794 | -102.2411 | 974050 | 2011-04-26 10:43 |  | NATURAL GAS |  | 74 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-04-26 08:15 | 2011-05-06 13:00 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 35 | 2011-04-26 08:15 | 2011-04-26 08:15 | ONSHORE | TX | 79766 | ODESSA | ECTOR |  |  | DORA ROBERTS COMPRESSOR STATION | UNIT 6051 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 1983 |  | CARBON STEEL |  | OTHER | [8 empty] | SEE PART H NARRATIVE DESCRIPTION | CLASS 1 LOCATION | NO |  | 527 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 333 | 225.351687388988 | 96092 | 112433.710617485 | 500 | 585.031587528021 | 0 | 0 |  |  | 96925 | 52112.2172055653 | 113244.093892402 | [8 empty] | 854 |  | 960 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ONSITE PERSONNEL PRESENT AT TIME OF INCIDENT, CONTROL ROOM PERSONNEL WERE NOT INVOLVED | [12 empty] | YES | 1 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | SEE PART H NARRATIVE DESCRIPTION |  |  | YES |  |  | ROUTINE MAINTENANCE | NO | [150 empty] | PATTI FORD | SENIOR PIPELINE SAFETY ENGINEER | patti.ford@oneok.com | 918 588 7131 | 918 732 1311 |  |  |  | WESLEY R. DUNBAR | VICE PRESIDENT | 918 588 7424 | wes.dunbar@oneok.com | THE INCIDENT OCCURRED ON 26 APRIL 2011 AT APPROXIMATELY 0815 HOURS WHEN GAS RELEASED THROUGH AN OPEN FLANGE WAS INTRODUCED INTO THE COMPRESSOR AIR INTAKE AND SUBSEQUENTLY IGNITED INSIDE THE TURBOCHARGER, WHICH THEN FAILED AND CAUGHT FIRE. THE INVESTIGATION TO DATE INDICATES THAT ALL PROCESSES WERE NOT ADEQUATELY FOLLOWED BY THE PIPELINE OPERATOR. PURSUANT TO DOT REGULATIONS, THE PIPELINE OPERATOR WAS DISQUALIFIED IMMEDIATELY AFTER THE INCIDENT. THE INVESTIGATION TO DATE INDICATES THAT A COMPRESSOR FAILURE DID NOT CAUSE THE INCIDENT. SUPPLEMENTAL: UPDATED NUMBER EVACUATED, EQUIPMENT INSTALLATION YEAR, INCIDENT COSTS, AND PRESSURE AT TIME OF INCIDENT. INTERNAL INVESTIGATION CONFIRMED THE INCIDENT WAS CAUSED BY FAILURE TO FOLLOW APPROPRIATE OPERATING PROCEDURES AND WAS NOT ANY EQUIPMENT FAILURE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110162 | 15925 | 2011-06-01 07:51 | SUPPLEMENTAL FINAL | 13769 | NORTHERN BORDER PIPELINE COMPANY | 13710 FNB PARKWAY | OMAHA | NE | 68154 | 2011-05-01 13:05 | 2011 |  |  | 45.255 | -102.717 | 974540 | 2011-05-01 15:25 |  | NATURAL GAS |  | 34000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-05-01 14:05 | 2011-05-01 16:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-05-01 13:05 | 2011-05-01 14:05 | ONSHORE | ND | 58642 | MANNING | DUNN | MILEPOST | MP16.80 | MANNING COMPRESSOR STATION | 6020000 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1982 |  | CARBON STEEL |  | OTHER | [8 empty] | UNIT VENT VALVE OPENED AFTER EMERGENCY GENERATOR FAILURE. BECAUSE THE EMERGENCY GENERATOR FAILED THE ELECTRIC OPERATED UNIT VALVES WERE NOT ABLE TO CLOSE. | CLASS 1 LOCATION | NO |  | 1098 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 102000 | 69026.6429840142 | 0 | 0 | 1000 | 1170.06317505604 | 0 | 0 |  |  | 103000 | 72100.144933779 | 70196.7061590702 | [8 empty] | 1100 |  | 1435 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | BECAUSE THE EMERGENCY GENERATOR FAILED THE ELECTRIC OPERATED UNIT VALVES WERE NOT ABLE TO CLOSE. THIS EVENT WAS NOTED BY THE CONTROLLER AND OPERATIONS PERSONNEL WAS DISPATCHED TO THE LOCATION. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | UNIT VENT VALVE OPENED AFTER EMERGENCY GENERATOR FAILURE. BECAUSE THE EMERGENCY GENERATOR FAILED THE ELECTRIC OPERATED UNIT VALVES WERE NOT ABLE TO CLOSE. | [15 empty] | YES | WEATHER RELATED FAILURE OF THE EMERGENCY GENERATOR | [161 empty] | DANIEL CERKONEY | COMPLIANCE ENGINEER | dan_cerkoney@transcanada.com | 701-483-1434 | 701-483-1431 |  |  |  | DANIEL CERKONEY | COMPLIANCE ENGINEER | 701-290-1176 | dan_cerkoney@transcanada.com | THE COMPRESSOR UNIT VENT VALVE OPENED AFTER EMERGENCY GENERATOR FAILURE DURING A SNOW STORM WHICH RESULTED IN GAS BLOWING FROM THE VENT FOR 60 MINUTES. BECAUSE THE EMERGENCY GENERATOR FAILED THE ELECTRIC OPERATED UNIT VALVES WERE NOT ABLE TO CLOSE. THIS ALLOWED GAS TO VENT THROUGH THE UNIT VENT VALVES FOR 60 MINUTES. PERSONNEL WERE DISPATCHED TO THE LOCATION TO CORRECT THE RELEASE OF GAS. DUE TO THE DRIVING CONDITIONS, RESPONSE TIME WAS HINDERED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110164 | 15250 | 2011-06-02 13:52 | ORIGINAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION LP (SPECTRA ENERGY CORP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2011-05-04 12:30 | 2011 |  |  | 29.2879 | -96.7439 | 974867 | 2011-05-04 15:30 |  | NATURAL GAS |  | 5 | 8693 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-05-05 12:00 | 2011-05-06 11:50 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-05-04 12:30 | 2011-05-04 12:30 | ONSHORE | TX | 77650 | HALLETTSVILLE (15 MILES SOUTHEAST OF) | LAVACA | MILEPOST | MP 4.78 | LINE 21 |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION | [19 empty] | FILLET WELD | [18 empty] | 1953 |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 388 |  | NO | NO | NO |  | 0 | 0 | 43465 | 50856.7959038109 | 25 | 16.9182948490231 | 176439 | 206444.776543713 | 0 | 0 | 0 | 0 |  |  | 219929 | 118125.751091438 | 257318.490742373 | [8 empty] | 1000 |  | 1236 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 86064 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS SO SMALL THAT CONTROLLERS WOULD NOT HAVE BEEN ABLE TO DETECT IT WITH SCADA. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | YES | [14 empty] | YES | OUTSIDE FORCE | [6 empty] | YES | [63 empty] | YES | YES |  |  | YES |  |  |  | 2009 | [31 empty] | 2009 | [23 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | deteschendorf@spectraenergy.com | 713-627-5573 | 713-386-4468 |  |  |  | RICK KIVELA | DIRECTOR OF OPERATIONAL COMPLIANCE | 713-627-6388 | rwkivela@spectraenergy.com | WHILE DISCONNECTING AN ABANDONED METER STATION FROM TEXAS EASTERN TRANSMISSION 16-INCH LINE 21 A LEAKING CRACK IN THE WELD AT A THREAD-O-LET WAS DISCOVERED. THE 16-INCH LINE WAS ISOLATED, BLOWN DOWN AND REPAIRED BY REPLACING A SEGMENT OF PIPE. REPAIR TO THE 16-INCH LINE EXCEEDED $50,000 RESULTING IN A DOT REPORTABLE INCIDENT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110166 | 16242 | 2011-06-03 12:33 | SUPPLEMENTAL FINAL | 13845 | NORTHWEST PIPELINE CORP (WGP) | 295 CHIPETA WAY | SALT LAKE CITY | UT | 84108 | 2011-04-27 13:20 | 2011 |  |  | 42.6276 | -111.8379 | 974628 | 2011-05-02 12:55 |  | NATURAL GAS |  | 29 | 12913 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | NOT IMMEDIATELY, SMALL FARM TAP LEAK. THREADED FITTING LEAKED. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-04-27 13:20 | 2011-04-27 13:20 | ONSHORE | ID | 83241 |  | CARIBOU | MILEPOST | 553.48 | 1400 LINE | 1400 LINE | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | IN UNDERGROUND ENCLOSED SPACE (E.G. VAULT) |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | THREADED 2" PIPE, PART OF THE FARM TAP. | 1961 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 40 |  | NO | NO | NO |  | 0 | 0 | 52964 | 61971.2260036682 | 117 | 79.1776198934281 | 81000 | 94775.1171795394 | 0 | 0 | 0 | 0 |  |  | 134081 | 72032.7945943755 | 156825.520803101 | [8 empty] | 708 |  | 850 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 87869 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | DISCOVERED DURING SCHEDULED MAINTENANCE AT SITE BY OPERATOR. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | FARM TAP THAT WAS NOT MONITORED IN SCADA | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | THREADED FITTING | [9 empty] | YES | [172 empty] | BOYD SCHOW | SR. TECH. SPEC. | boyd.schow@williams.com | 801-584-6741 |  |  |  |  | JARED ELLSWORTH | MANAGER PIPELINE SAFETY | 801-584-6539 | jared.ellsworth@williams.com | WILLIAMS (NORTHWEST PIPELINE) IDENTIFIED A 2" THREADED TAP VALVE THAT WAS NOT SEALING PROPERLY DURING REGULAR MAINTENANCE. THE 2" PIPELINE COMES OFF OF THE 22" MAINLINE IN IDAHO STATE AND FEEDS A SINGLE HOME. AFTER ANALYZING THE SITUATION, WILLIAMS FEELS THAT THE BEST APPROACH IS TO REMOVE THE 2" TAP VALVE. TO ACCOMPLISH THIS TASK, WILLIAMS ISOLATE THE SEGMENT OF 22" MAINLINE PIPE, BLEW DOWN THE MAINLINE, ISOLATE THE 2" PIPELINE AND CUT OUT THE SECTION OF MAINLINE THAT CONTAINS THE 2" TAP. INSTEAD OF A SMALL PUP TO ACCOMODATE THE CUT OUT, A FULL JOINT OF NEW 22" PIPE WAS INSTALLED IN THE MAINLINE TO ELIMINATE THREE COMPOSITE SLEEVES FOUND DURING THE EXCAVATION OF THE PIPE WHILE THE PIPE WAS OUT OF SERVICE. THE CUSTOMER WAS TRANSFERED ONTO ANOTHER AVAILABLE SERVICE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110168 | 16067 | 2011-06-06 09:29 | SUPPLEMENTAL FINAL | 12874 | QUESTAR PIPELINE COMPANY | 333 SOUTH STATE STREET P.O. BOX 45360 | SALT LAKE CITY | UT | 84145-0360 | 2011-05-11 01:18 | 2011 |  |  | 40.0389 | -109.4535 | 975910 | 2011-05-11 03:45 |  | NATURAL GAS |  | 16400 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE RELEASE WAS THROUGH TWO 2 INCH VENT VALVES THAT FAILED OPEN. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-05-11 01:18 | 2011-05-11 02:05 | ONSHORE | UT | 84078 | VERNAL | UINTAH |  |  | FIDLAR COMPRESSOR STATION | SUCTION AND DISCHARGE HEADER VENT VALVES | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1996 |  | CARBON STEEL |  | OTHER | [8 empty] | DUE TO AN ELECTRICAL FUSE FAILING, TWO 2" VENT VALVES WERE OPENED AND VENTED TO ATMOSPHERE | CLASS 1 LOCATION | NO |  | 59 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 68100 | 46085.4351687389 | 200 | 234.012635011208 | 300 | 351.018952516813 | 0 | 0 |  |  | 68600 | 48047.4081684881 | 46670.4667562669 | [8 empty] | 777 |  | 1290 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLERS DID NOT HAVE ENOUGH INFORMATION TO MAKE A DETERMINATION THAT THERE WAS A PROBLEM AT THE STATION. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [7 empty] | YES | [16 empty] | YES | [173 empty] | CHAD WILDING | SUPERVISOR OF PIPELINE COMPLIANCE | chad.wilding@questar.com | 801-324-3814 |  |  |  |  | LAWRENCE A. CONTI | VICE PRESIDENT OPERATIONS AND GAS CONTROL | 801-324-5061 | larry.conti@questar.com | A FUSE FAILED THAT CAUSED TWO 2" VENT VALVES TO OPEN AND VENT GAS TO THE ATMOSPHERE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110170 | 15932 | 2011-06-08 10:42 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | TX | 77002 | 2011-05-11 16:15 | 2011 |  |  | 42.6671 | -85.9564 | 975983 | 2011-05-11 17:55 |  | NATURAL GAS |  | 4500 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | FOLLOWING THE INVESTIGATION OF THE GAS RELEASE, THE STATION WAS RETURNED TO SERV | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 |  |  | ONSHORE | MI | 49419 | HAMILTON | ALLEGAN |  |  | HAMILTON COMPRESSOR STATION |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | OTHER | COMPRESSOR STATION |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | STATION BLOCK GATE (BYPASS VALVE) |  |  | CARBON STEEL |  | OTHER | [8 empty] | WHEN THE STATION PRESSURE EQUALIZED, THE STATION BLOCK GATE (BYPASS VALVE) OPENED WHICH ALLOWED GAS TO FLOW THROUGH THE OPEN VENTS ON THE 30 INCH PIG LAUNCHER. THE PIG LAUNCHER HAD BEEN LEFT IN AN ABNORMAL LINE-UP, WITH THE ILI PIG IN THE DEPRESSURIZED TRAP, FOR AN EARLY MORNING LAUNCH. | CLASS 1 LOCATION | NO |  | 369 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 20250 | 13703.8188277087 | 0 | 0 | 40000 | 46802.5270022417 | 0 | 0 | 0 |  | 60250 | 35690.9660900566 | 60506.3458299504 | [8 empty] | 876 |  | 850 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE EXCEEDED MAOP, BUT DID NOT EXCEED THE APPLICABLE ALLOWANCE IN 192.201 | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LOCAL OPERATIONS PERSONNEL HAD BEEN PERFORMING MAINTENANCE WORK AND THEREFORE WERE RESPONSIBLE FOR OPERATING THE EQUIPMENT THAT MAY NOT HAVE BEEN UTILIZED PROPERLY. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | PIPELINE OR EQUIPMENT OVERPRESSURED | INCORRECT OPERATION | PIPELINE/EQUIPMENT OVERPRESSURED | [204 empty] | PIPELINE OR EQUIPMENT OVERPRESSURED |  |  |  | YES |  | YES |  |  | NON-ROUTINE OPERATING CONDITIONS (ABNORMAL OPERATIONS OR EMERGENCIES) | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | LOUIS SALINAS | COMPLIANCE ENGINEER | louis_salinas@transcanada.com | 832-320-5305 | 832-320-6305 |  |  |  | LOUIS SALINAS |  | 832-320-5305 | No Email Address | THE HAMILTON STATION, OPERATING AT 809 PSI, TRIPPED ON MAIN LINE OVER PRESSURE DUE TO A HIGH PRESSURE CONDITION IN THE TRIP CIRCUITRY PIPING. IT IS BELIEVED THAT HIGH TEMPERATURES IN THE BUILDING CAUSED THE PRESSURE TO INCREASE ABOVE THE 876 PSI SET POINT. WHEN THE STATION PRESSURE EQUALIZED, THE STATION BLOCK GATE (BYPASS VALVE) OPENED WHICH ALLOWED GAS TO FLOW THROUGH THE OPEN VENTS ON THE 30 INCH PIG LAUNCHER. THE PIG LAUNCHER HAD BEEN LEFT IN AN ABNORMAL LINE-UP, WITH THE ILI PIG IN THE DEPRESSURIZED TRAP, FOR AN EARLY MORNING LAUNCH.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110175 | 16349 | 2011-06-09 16:50 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION CORP | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2011-05-13 19:02 | 2011 |  |  | 37.6046 | -83.9246 | 976244 | 2011-05-13 19:44 |  | NATURAL GAS |  | 53 | 2 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-05-13 19:02 | 2011-05-27 14:24 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2011-05-13 19:02 | 2011-05-13 19:02 | ONSHORE | KY | 40336 | 8 MILES SSE OF IRVINE, KY | ESTILL |  |  | STATION CAMP C/S |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1984 |  | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 26 |  | NO | NO | NO |  | 0 | 0 | 9 | 10.5305685755044 | 239 | 161.738898756661 | 120000 | 140407.581006725 | 1000 | 1170.06317505604 | 0 | 0 |  |  | 121248 | 65160.3903342852 | 141749.913649113 | [8 empty] | 230 |  | 1000 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | UNEXPECTED FACILITY FAILURE TRIGGERED THE EVENT. THERE WAS NO CONTROLLER INVOLVEMENT AT THE TIME OF THE FAILURE, AND THE FACILITY HAD BEEN OPERATING WELL WITHIN NORMAL OPERATIONAL PARAMETERS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | SEAL FAILURE | [21 empty] | YES | CROSSHEAD SLIDE FAILURE AND SEIZURE | [161 empty] | DAVID ADLER | SYSTEM INTEGRITY ENGINEER | dadler@nisource.com | 304-357-2378 | 304-357-3804 |  |  |  | P. MICHAEL HOFFMAN | MANAGER SYSTEM INTEGRITY | 304-357-2548 | mikehoffman@nisource.com | AT 16:04 ON FRIDAY, MAY 13, 2011, A POSSIBLE FIRE WAS REPORTED BY COLUMBIA'S MONITORING CENTER. THE EVENT WAS AT THE COMPANY'S STATION CAMP COMPRESSOR STATION, A SMALL UNMANNED STATION IN RURAL CENTRAL KENTUCKY. THE STATION CONSISTS OF FOUR AJAX 230 HORSEPOWER UNITS. THE LOCAL FIRE DEPARTMENT WAS ON SITE AND HAD CLOSED A ROAD ADJACENT TO THE STATION. COMPANY EMPLOYEES HAD ARRIVED AT THE SITE AT APPROXIMATELY 16:00 AND CONFIRMED THAT UNIT #3 WAS ON FIRE. BY 16:35 THE STATION WAS SHUT IN AND THE FIRE WAS EXTINGUISHED. AFTER A THOROUGH EXAMINATION, IT WAS DETERMINED THAT ONLY UNIT #3 HAD BEEN DAMAGED. IT WAS DECLARED TO BE UNAVAILABLE FOR SERVICE, PENDING FURTHER ASSESSMENT AND REPAIR. THE OTHER UNITS WERE LATER RETURNED TO SERVICE WITHOUT INCIDENT. THE UNITS AT THIS STATION ARE OWNED BY EXTERRAN AND LEASED TO COLUMBIA. A REPRESENTATIVE OF EXTERRAN ARRIVED AT THE SITE AT APPROXIMATELY 18:45 AND PROVIDED AN INITIAL DAMAGE ESTIMATE OF $125,000 TO $250,000. THIS ESTIMATE WAS RECEIVED AT APPROXIMATELY 19:02. UPON RECEIPT OF THIS ESTIMATE, IT WAS DETERMINED THAT AN INCIDENT HAD OCCURRED. THE NRC AND PHMSA SOUTHERN REGION OFFICES WERE NOTIFIED AT 19:44 AND 20:08 RESPECTIVELY. OVER THE COURSE OF THE NEXT THREE DAYS THE CIRCUMSTANCES OF THE EVENT WERE ESTABLISHED. IT WAS DECIDED THAT THE COMPRESSOR CROSSHEAD SLIDE HAD FAILED AND SIEZED ON UNIT #3. THE RESULTANT HEAT AND DAMAGE IGNITED CRANKCASE OIL VAPORS (VIA THE OIL BREATHER) AND A NEARBY LUBE OIL DAY STORAGE TANK. THE HEAT FROM THE OIL FIRE HAD, IN TURN, DAMAGED A VALVE IN THE STARTING GAS SYSTEM, CAUSING GAS LEAKAGE AND A SUBSEQUENT SMALL SECONDARY FIRE. THIS SECONDARY FIRE CAUSED NO APPARENT ADDITIONAL DAMAGE. REPAIRS WERE MADE TO THE UNIT AND IT WAS RETURNED TO SERVICE ON MAY 27. FINAL REPAIR COSTS TOTALLED APPROXIMATELY $120,000.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110177 | 15516 | 2011-06-09 17:04 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION CORP | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2011-05-12 09:15 | 2011 |  |  | 38.0371 | -82.5992 | 976050 | 2011-05-12 11:11 |  | NATURAL GAS |  | 2128 | 300 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-05-12 09:45 | 2011-05-21 00:05 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-05-12 09:15 | 2011-05-12 09:15 | ONSHORE | KY | 41230 | 5.3 MILES SOUTH OF LOUISA, KY | LAWRENCE COUNTY, KY | SURVEY STATION NO. | 213575 | LINE P | STATION SERIES 085 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 120 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | COUPLING | 1929 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 234 |  | NO | NO | NO |  | 0 | 0 | 1350 | 1579.58528632566 | 9576 | 6480.3836589698 | 0 | 0 | 550 | 643.534746280823 | 160000 | 187210.108008967 | INCREMENTAL COST: UNTIMELY REPLACEMENT OF PIPE ALREADY SCHEDULED FOR REPLACEMENT |  | 171476 | 93673.3582068753 | 195913.611700543 | [8 empty] | 187 |  | 288 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 43317 | NO | YES | YES | YES | YES |  |  |  | YES |  | YES |  |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT ATTRIBUTED TO UNEXPECTED OUTSIDE FORCE. PIPELINE WAS OPERATING WELL WITHIN NORMAL OPERATIONAL PARAMETERS AT THE TIME OF INCIDENT. APPROPRIATE RESPONSE MADE BY CONTROL ROOM. | [12 empty] | YES | 1 | 0 | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [52 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | LANDSLIDE |  |  |  |  | NO | [306 empty] | DAVID ADLER | SYSTEM INTEGRITY ENGINEER | dadler@nisource.com | 304-357-2378 | 304-357-3804 |  |  |  | P. MICHAEL HOFMAN | MANAGER SYSTEM INTEGRITY | 304-357-2548 | mikehoffman@nisource.com | AT ABOUT 3:00 A.M. ON THE MORNING OF MAY 12, A SLOW PRESSURE DROP WAS NOTED ON LINE B NEAR COLUMBIA GAS TRANSMISSION'S WALBRIDGE COMPRESSOR STATION. THE CONTROLLER ON DUTY CONTACTED THE LOCAL TEAM LEADER, WHO THOUGHT THAT ONE OR MORE PRODUCERS IN THE AREA UPSTREAM OF THE PRESSURE DEVICE MIGHT BE MAKING AN OPERATIONAL CHANGE. A DECISION WAS MADE TO MONITOR THE PRESSURE FOR A SHORT WHILE. THE PRESSURE CONTINUED TO SLOWLY DROP. IT WAS DECIDED TO HAVE FIELD OPERATIONS START CHECKING THE LINE. BY SHORTLY AFTER 3:30 A.M., LOCAL FIELD EMPLOYEES WERE BEING CONTACTED. THEY BEGAN CHECKING LINE B AND OTHER UPSTREAM LINES THAT FEED INTO LINE B BETWEEN 4:30 AND 5:00 A.M. THE AREA TRAVERSED BY LINE B AND ITS UPSTREAM FEEDER LINES IS REMOTE AND RUGGED, OFTEN WITH MILES BETWEEN ROAD ACCESS POINTS. CHECKING THE SYSTEM WAS DIFFICULT AND SLOW. AT A FEW MINUTES AFTER 9:00, A CREW CHECKING UPSTREAM FEEDER LINE P CAME UPON A LANDSLIDE AREA. IT WAS DETERMINED THAT GAS WAS ESCAPING FROM THE COUPLED LINE IN THIS AREA. IT SHOULD BE NOTED THAT THIS PART OF EASTERN KENTUCKY HAD EXPERIENCED AN UNUSUALLY WET SPRING. THIS IS THOUGHT TO HAVE CONTRIBUTED TO THE LANDSLIDE. THE SITUATION WAS CALLED IN TO THE CONTROL ROOM. QUESTIONS WERE ASKED, INVESTIGATED, AND ANSWERED TO OBTAIN ACCURATE INFORMATION. AS SOON AS SUFFICIENT INFORMATION WAS OBTAINED TO DETERMINE THAT AN INCIDENT HAD OCCURED, A CALL WAS MADE TO THE NRC AND PHMSA'S SOUTHERN REGION OFFICE. MATERIALS AND EQUIPMENT WERE ASSEMBLED OVER THE NEXT DAY, AND RESTORATION WORK WAS BEGUN ON MAY 14. THE LINE WAS READIED FOR PLACEMENT IN SERVICE BY 9:00 MAY 20, AND WAS FULLY RESTORED TO SERVICE BY 12:05 A.M. ON MAY 21. NOTE THAT THE GAS LOSS CALCULATIONS REFLECT OUR BEST RECONSTRUCTION OF THE EVENTS AFTER DISCOVERY OF THE CONDITION. HOWEVER, IT IS POSSIBLE THAT GAS LOSS VOLUME MAY HAVE EXCEEDED 3,000 MCF THROUGH THE DURATION OF THE INCIDENT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110184 | 15275 | 2011-06-15 17:46 | SUPPLEMENTAL FINAL | 13845 | NORTHWEST PIPELINE CORP (WGP) | 2800 POST OAK BLVD | HOUSTON | TX | 77056 | 2011-05-24 12:30 | 2011 |  |  | 42.6206 | -111.8576 | 977297 | 2011-05-24 17:47 |  | NATURAL GAS |  | 1920 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-05-24 18:48 | 2011-06-21 14:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-05-24 12:30 | 2011-05-24 12:30 | ONSHORE | ID | 83246 | LAVA | CARIBOU | MILEPOST | M.P. 554.6 | IGNACIO TO SUMAS 1401 LOOP LINE | 1401 LN MLV 8L1 TO 8L2 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 96 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 |  | 0.25 | 60000 | API 5L GRADE X60 | LONGITUDINAL ERW - HIGH FREQUENCY |  | AMERICAN PIPE | EPOXY | [28 empty] | 1992 | 1992 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 445 |  | NO | NO | NO |  | 0 | 0 | 62180 | 72754.5282249847 | 7680 | 5197.30017761989 | 68500 | 80149.3274913389 | 0 | 0 | 0 | 0 |  |  | 138360 | 75575.1815092877 | 158101.155893943 | [8 empty] | 713 |  | 850 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 87869 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | AIR PATROL |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PIPE WAS SITTING ON A ROCK THAT DENTED THE PIPE CREATING A CRACK IN THE PIPE CAUSING A SLOW LEAK. THE GAS RELEASE WAS SO MINUTE, IT WAS NOT DETECTABLE WITH THE SCADA MONITORED SYSTEM. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [7 empty] | YES | [10 empty] | YES |  |  |  | YES | [63 empty] | YES | YES |  |  | YES |  |  |  | 2010 | [31 empty] | 2010 | [23 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | BOYD SCHOW | SENIOR TECHNICAL SPECIALIST | boyd.schow@williams.com | 801-584-6741 |  |  |  |  | BOYD SCHOW | SENIOR TECHNICAL SPECIALIST | 801-584-6741 | boyd.schow@williams.com | DURING THE ANNUAL POCATELLO AIR PATROL OF THE PIPELINE, A LOCATION WITH DEAD VEGETATION WAS IDENTIFIED AT MILE POST 554.6. A GROUND PATROL WAS SENT TO INVESTIGATE AND FOUND THE DEAD VEGETATION AND USED A FLAME PACK TO IDENTIFY LEAKING GAS. BY PROBING AND SNIFFING, IT WAS DETERMINED THAT THE LEAK WAS ON THE 24" 1401 LOOP LINE. THE PIPELINE WAS IMMEDIATELY BLOWN DOWN TO 43 PSIG FROM MLV 8L-2. EXCAVATION MACHINERY WAS BROUGHT ON SITE AND BEGAN EXCAVATION. THE PIPE WAS FOUND SITTING ON A ROCK AND GAS WAS ESCAPING FROM THAT LOCATION. THE BLOW DOWN CONTINUED TO A SLIGHT POSITIVE PRESSURE. A TEMPORY PATCH WAS PUT OVER THE HOLE FOR THE NIGHT. THE FOLLOWING MORNING THE PIPE WAS CUT AND A 7.81 FT PUP WAS INSTALLED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110186 | 15990 | 2011-06-20 13:58 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2011-05-25 17:45 | 2011 |  |  | 37.4254 | -122.0933 | 977449 | 2011-05-25 22:30 |  | NATURAL GAS |  | 0 | 3000 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-05-25 19:50 | 2011-05-27 17:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-05-25 17:45 | 2011-05-25 17:45 | ONSHORE | CA | 94035 | MOUNTAIN VIEW | SANTA CLARA | MILEPOST | FIRE VALVE | L-132A | CHARLESTON & GARCIA REG STATION VALVE #49-C3D | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [22 empty] | INTRASTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1980 |  | CARBON STEEL |  | OTHER | [8 empty] | VALVE STEM BROKE DURING OPERATION OF VALVE. | CLASS 3 LOCATION | YES | METHOD2 | 62 |  | NO | NO | NO |  | 0 | 0 | 10000 | 11700.6317505604 | 0 | 0 | 30000 | 35101.8952516813 | 0 | 0 | 0 | 0 |  |  | 40000 | 21483.5948644793 | 46802.5270022417 | [8 empty] | 285 |  | 400 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | YES | NO | STATE | [20 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | OTHER | OPERATOR WAS ON SCENE AT TIME OF INCIDENT |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | A PORTION OF THE RUBBER GASKET SURROUNDING THE VALVE GATE HAD BECOME DISLODGED W | [161 empty] | LAURENCE DENISTON | INTERIM MANAGER | lcd1@pge.com | 9259744313 |  |  |  |  | FRANCES YEE | ACTING DIRECTOR | 9259744316 | fsc2@pge.com | DURING A SCHEDULED HYDROTEST JOB, THE VALVE STEM ON AN INLET FIRE VALVE TO A REGULATOR STATION AT 2445 GARCIA AVENUE IN MOUNTAIN VIEW BROKE AT 1745 HOURS. THE VALVE WAS BEING OPERATED TO RELEASE WATER FROM THE LINE. THE VALVE WAS BROKEN IN THE PARTIALLY OPEN POSITION CAUSING GAS TO ESCAPE. IN ORDER TO ISOLATE THE BROKEN VALVE TO MAKE REPAIRS, APPROXIMATELY 7000 FEET OF LINE 132A (RENGSTORFF STATION [MOUNTAIN VIEW GOLF COURSE] TO THE SIERRA VISTA REGULATOR STATION [AT ROCK AND SIERRA VISTA AVENUE]) WAS BLOWN DOWN STARTING AT 1950 HOURS. GAS FLOW STOPPED AT APPROXIMATELY 2020 HOURS. THE DELAY BETWEEN THE BREAKING OF THE VALVE STEM AND THE START OF THE BLOW DOWN WAS THE TIME REQUIRED TO DEVELOP THE PLAN FOR THE SITUATION AND TO OBTAIN THE REQUIRED CLEARANCES. THE ESTIMATED VOLUME OF THE GAS RELEASED TO ATMOSPHERE WAS 3,000 MCF WHICH CAUSED THE NEED TO REPORT THIS INCIDENT. NO SERVICE HAS BEEN LOST.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110193 | 15263 | 2011-06-23 11:35 | ORIGINAL FINAL | 26330 | ENOGEX LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2011-05-24 15:45 | 2011 |  |  | 36.6385 | -97.816 |  |  |  | NATURAL GAS |  | 361.93 | 2404.93 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-05-24 16:15 | 2011-05-24 17:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-05-24 15:45 | 2011-05-24 16:15 | ONSHORE | OK | 73078 | PIEDMONT | CANADIAN | MILEPOST | NONE | WIEDEMANN JUNCTION | NONE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | 1 INCH PIPE NIPPLE |  |  | CARBON STEEL |  | OTHER | [8 empty] | UTILITY POLE FELL ON TOP OF ABOVE GROUND PIPING AND BROKE 1 INCH PIPE NIPPLE AT THREADED CONENCTION TO PIPELINE. | CLASS 1 LOCATION | NO |  | 293 |  | NO | NO | NO |  | 0 | 0 | 8437 | 9871.82300794783 | 1494 | 1011.03730017762 | 100 | 117.006317505604 | 600 | 702.037905033625 | 0 | 0 |  |  | 10631 | 5955.57843400572 | 11701.9045306647 | [8 empty] | 381 |  | 720 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | REMOTELY CONTROLLED | 68640 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS CAUSED BY AN ACT OF GOD, I.E. TORNADO. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | [52 empty] | HIGH WINDS | [5 empty] | YES |  |  | YES | [303 empty] | MIKE REED | MANAGER EHS ASSESSMENT AND COMPLIANCE | reedmd@oge.com | 405 558-4685 | 405 557-8618 |  |  |  | PAUL M BREWER | VP OPERATIONS | 405 525-7788 | brewerpm@oge.com | A TORNADO STRUCK THE L-102 WIEDEMANN JUNCTION. A UTILITY POLE LOCATED OUTSIDE THE JUNCTION FELL ACROSS THE ABOVE GROUND PORTION OF OUR SIXTEEN INCH PIPELINE AND BROKE A 1 INCH PIPE NIPPLE AT THE THREADED CONNECTION TO THE PIPELINE. GAS CONTROL REMOTELY CLOSED THE NEAREST AUTOMATED UPSTREAM VALVE AT OUR 12-12 JUCTION AND THE NEAREST DOWNSTREAM VALVE AT OUR EDMOND JUNCTION. ON-CALL PERSONNEL ARRIVED ONSITE TO DISCOVER NATURAL GAS VENTING THROUGH THE BROKEN NIPPLE. PERSONNEL ISOLATED A 16 INCH MANUAL VALVE INSIDE THE JUNCTION AND VENTED A 10 MILES SEGMENT OF PIPELINE PRIOR TO REPLACING THE BROKEN NIPPLE AND 1 INCH VENT VALVE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110194 | 16024 | 2011-06-23 11:46 | SUPPLEMENTAL FINAL | 15105 | PANHANDLE EASTERN PIPELINE CO | 5051 WESTHEIMER ROAD | HOUSTON | TX | 77056 | 2011-05-29 08:07 | 2011 |  |  | 37.2126 | -100.3558 | 977716 | 2011-05-29 13:06 |  | NATURAL GAS |  | 45000 | 1750 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-05-29 08:30 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-05-29 08:07 | 2011-05-29 08:07 | ONSHORE | KS | 67864 | MEADE | MEADE |  |  | BORCHERS STORAGE FIELD | LOWEN 1-10/35-03-034-08 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 72 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6.625 |  | 0.219 | 46000 | 5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | TEX-TUBE | FIELD APPLIED EPOXY | [28 empty] | 1981 | 1981 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 90 | 14 |  | CLASS 1 LOCATION | NO |  | 198 |  | NO | NO | NO |  | 0 | 0 | 7000 | 8190.44222539229 | 180000 | 121811.722912966 | 20000 | 23401.2635011208 | 1000 | 1170.06317505604 | 0 | 0 |  |  | 208000 | 141326.260632489 | 154573.491814535 | [8 empty] | 1639 |  | 1875 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 3039 | NO | YES | [6 empty] | NO | [6 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 2 | 0 | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | GENERAL CORROSION |  |  | YES |  |  |  |  | YES | YES |  |  | YES | [5 empty] | YES | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | AT 8:07 AM ON MAY 29, 2011, PANHANDLE EASTERN PIPE LINE COMPANY RECEIVED A CALL FROM A RETIRED EMPLOYEE REPORTING BLOWING GAS AT THE BORCHERS STORAGE FIELD. A PEPL EMPLOYEE WAS AT THE FIELD AND ISOLATED THE AFFECTED LINE SEGMENT WITHIN 23 MINUTES. VISUAL OBSERVATION OF THE FAILED PIPE SEGMENT INDICATES INTERNAL WALL LOSS DUE TO CORROSION FOR 5 FEET IN THE VICINITY OF THE FRACTURE IMMEDIATELY DOWNSTREAM OF A 4" TO 6" REDUCER, IN A LOW POINT OF THE PIPE. LABORATORY ANALYSIS OF THE FAILED PIPE SEGMENT CONCLUDED THAT THE INTERNAL CORROSION WAS LIKELY THE RESULT OF AQUEOUS CORROSION CAUSED BY WATER AND OTHER CONTAMINANTS IN THE PRODUCT STREAM. IT IS ALSO LIKELY THAT UNDER DEPOSIT CORROSION CREATED THE LOCAL ENVIRONMENT THAT RESULTED IN THE CORROSION OBSERVED. THE CORROSION DEPOSITS WERE NOT CONSISTENT WITH MICROBIOLOGICAL-ASSISTED CORROSION, AND THE CORROSION WAS NOT ASSOCIATED WITH THE ERW SEAM. **THIS REPORT IS BEING SUBMITTED IN RESPONSE TO PHMSA'S REQUEST FOR SUPPLEMENTAL REPORTS FROM OPERATORS WHO SUBMITTED REPORTS FOR INCIDENTS OCCURRING AFTER JANUARY 1, 2010, WITH ANY OF THE FOLLOWING: (1) ``PIPE GIRTH WELD'' WAS SELECTED AS THE ``ITEM INVOLVED IN INCIDENT'' IN PART C3 OF THE REPORT. THE REVISED REPORT COLLECTS DATA ABOUT THE PIPE ADJACENT TO THE GIRTH WELD. (2) ``FUNCTION OF PIPELINE SYSTEM'' IS NULL IN PART E5F OF THE REPORT. THE REVISED REPORT COLLECTS THE FUNCTION OF THE PIPELINE SYSTEM FOR ALL INCIDENTS. THIS REPORT HAS NO FURTHER UPDATES AND IS BEING SUBMITTED AS A FINAL.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110195 | 15788 | 2011-06-23 12:44 | SUPPLEMENTAL FINAL | 26330 | ENOGEX LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2011-05-24 16:00 | 2011 |  |  | 35.5366 | -98.1038 | 977425 | 2011-05-25 17:13 |  | NATURAL GAS |  | 1773 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-05-24 16:30 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-05-24 16:00 | 2011-05-24 16:15 | ONSHORE | OK | 73014 | CALUMET | CANADIAN | MILEPOST |  | DEVON CANNA PLANT | L-300 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | ALL PIPING IN METER YARD | 2010 |  | CARBON STEEL |  | OTHER | [8 empty] | FLYING DEBRIS CAUSED BY TORNADO DESTROYED INSTRUMENTATION, DAMAGED ABOVE GROUND PIPING, AND BROKE THREE 1 INCH PIPE NIPPLES. | CLASS 1 LOCATION | NO |  | 398 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 7322 | 4955.03019538188 | 1200000 | 1404075.81006725 | 400 | 468.025270022417 | 0 | 0 |  |  | 1207722 | 649859.786678761 | 1409498.86553265 | [8 empty] | 700 |  | 1300 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | OTHER | NOTIFICATION FROM DEVON PLANT EMPLOYEES |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS CAUSED BY AN ACT OF GOD, I.E. TORNADO. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | [52 empty] | HIGH WINDS | [5 empty] | YES |  |  | YES | [303 empty] | MIKE REED | MANAGER EHS ASSESSMENT AND COMPLIANCE | reedmd@oge.com | 405 558-4685 | 405 557-8618 |  |  |  | PAUL M BREWER | VP OPERATIONS | 405 525-7788 | brewerpm@oge.com | A COMPREHENSIVE INSPECTION WAS PERFORMED TO DETERMINE THE FULL EXTENT OF THE DAMAGE FOLLOWING A TORNADO STRUCK THE ENOGEX METERING AND PIPELINE FACILITY ADJACENT TO THE DEVON CANNA PLANT. EXTENSIVE DAMAGE TO A ULTRASONIC METER, CONTROL VALVE, PRESSURE MONITOR VALVE, ISOLATION VALVE, EFM, SCADA EQUIPMENT, GAS QUALITY MONITORING EQUIPMENT INCLUDING A GAS CHROMATOGRAPH AS WELL AS ABOVE GROUND PIPING PREVENTS THE REPAIR OF THIS FACILITY. ALL METERING EQUIPMENT AND PIPING THAT CONNECTS THE DEVON PLANT OUTLET TO OUR L-300 WAS REMOVED AND THE ENTIRE FACILITY WAS REDESIGNED AND CONSTRUCTED. UPDATE MARCH 5, 2013: COMPLETED SECTION E.5.F.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110198 | 15982 | 2011-06-23 16:37 | SUPPLEMENTAL | 31304 | DEVON GAS SERVICES, LP | 333 W SHERIDAN AVE | OKLAHOMA CITY | OK | 73102 | 2011-05-24 16:25 | 2011 |  |  | 35.5357 | -98.1023 | 979962 | 2011-06-17 13:04 |  | NATURAL GAS |  | 345 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | PRESSURE SOURCE (UPSTREAM PROCESS. PLANT) WAS SHUTDOWN IN ANTICIPATION OF STORM | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-05-24 16:35 | 2011-05-24 16:35 | ONSHORE | OK | 73014 | CALUMET | CANADIAN | SURVEY STATION NO. | 34+21.5 | CANA PLANT RESIDUE 20" PIPELINE / SALES HEADER | 909006 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | MULTIPLE COMPONENTS | 2010 |  | CARBON STEEL |  | LEAK |  |  | OTHER | IMPACT FROM AIRBORN DEBRIS | [5 empty] | CLASS 1 LOCATION | NO |  | 498 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 121577 | 142252.770633788 | 0 | 0 | 0 | 0 |  |  | 121577 | 65297.7753209701 | 142252.770633788 | [8 empty] | 850 |  | 1300 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | TORNADO | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | [52 empty] | HIGH WINDS | [5 empty] | YES |  |  | YES | [303 empty] | DARIN BANTHER | EHS PROFESSIONAL | darin.banther@dvn.com | 4055227962 | 4052342731 |  |  |  | DARIN BANTHER | EHS PROFESSIONAL | 4055227962 | darin.banther@dvn.com | AS A RESULT OF A TORNADO WARNING AND A CLEAR OBSERVATION THAT EMERGENCY PREPARATIONS WERE NECESSARY, DEVON'S CANA PLANT EMERGENCY SHUT DOWN (ESD) SYSTEM WAS ACTIVATED BY CANA PLANT OPERATIONS PERSONNEL AT APPROXIMATELY 4:00P.M. CST, AT WHICH TIME THE EMPLOYEES SOUGHT SHELTER IN THE ON-SITE STORM SHELTER. AT APPROXIMATELY 4:25P.M. CST, THE TORNADO HAD PASSED. AFTER EMERGING FROM THE TORNADO SHELTER, PLANT PERSONNEL BEGAN TO MAKE INITIAL OBSERVATION REPORTS FROM A SAFE DISTANCE TO DEVON'S GAS CONTROL CENTER AS WELL AS DEVON MANAGEMENT. IT WAS EVIDENT FROM OBSERVATION THAT DAMAGE WAS INCURRED AT THE RESIDUE SALES HEADER (THE DOWNSTREAM PORTION OF DEVON'S ~3420FT REGULATED RESIDUE TRANSMISSION PIPELINE THAT DELIVERS RESIDUE GAS FROM THE CANA PLANT TO THIRD PARTY PIPELINES--CURRENTLY ONEOK AND ENOGEX). IMMEDIATE ACTIONS WERE AIMED AT PROTECTING LIFE FIRST AND PROPERTY SECOND, AND INCLUDED SECURING THE SITE PERIMETER FROM ANY UNAUTHORIZED ACTIVITY. DEVON STOOD UP A LOCAL INCIDENT COMMAND SYSTEM (ICS) STRUCTURE AND MOBILIZED A TEAM COMPRISED OF OPERATIONS AND ENVIRONMENTAL, HEALTH & SAFETY (EHS) REPRESENTATIVES TO CONDUCT INITIAL INSPECTIONS AND SAFETY ASSESSMENTS PRIOR TO PERMITTING ACTIVITY WITHIN THE PLANT. ICS WAS LATER STOOD DOWN AND A PROJECT TEAM WAS ESTABLISHED TO CONDUCT MORE DETAILED ASSESSMENTS. REPAIRS TO THE RESIDUE SALES HEADER WERE MADE IN ACCORDANCE WITH 49 CFR PART 192 AND THE HEADER IS PLANNED TO BE RETURNED TO SERVICE WEDNESDAY JULY 20, 2011.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110199 | 16175 | 2011-06-24 11:30 | SUPPLEMENTAL FINAL | 31532 | ONEOK GAS STORAGE, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2011-05-24 16:55 | 2011 |  |  | 35.7492 | -97.6675 | 978829 | 2011-06-06 15:45 |  | NATURAL GAS |  | 42887.4 | 31.5 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-05-24 19:05 | 2011-05-25 20:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-05-24 18:30 | 2011-05-24 18:45 | ONSHORE | OK | 73025 | EDMOND | LOGAN |  |  | EDMOND STORAGE | F-352 AND 4 WELLS | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | SCRAPER/PIG TRAP | [38 empty] | 1992 |  | CARBON STEEL |  | OTHER | [8 empty] | TORNADO DAMAGE | CLASS 1 LOCATION | NO |  | 385 |  | NO | NO | NO |  | 0 | 0 | 132 | 154.448339107398 | 179533 | 121495.689165187 | 126321 | 147803.550336254 | 1025 | 1199.31475443244 | 0 | 0 |  |  | 307011 | 194427.240344294 | 270653.002594981 | [8 empty] | 1470 |  | 2160 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 7920 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ONEOK EMPLOYEE WHO LIVES NEARBY NOTIFIED EDMOND STORAGE MANAGMENT | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [52 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | POTENTIAL DEBRIS STRIKE DURING EF-5 (PER NATIONAL WEATHER SERVICE) TORNADO | YES |  |  | YES | [303 empty] | PATTI FORD | SENIOR PIPELINE SAFETY ENGINEER | patti.ford@oneok.com | 918 588 7131 | 918 732 1311 |  |  |  | WESLEY R. DUNBAR | VICE PRESIDENT | 918 588 7424 | wes.dunbar@oneok.com | AN EF-5 TORNADO CAME THROUGH THE ONEOK GAS STORAGE'S EDMOND STORAGE FACILITY LOCATED NORTH OF EDMOND, OKLAHOMA, AT APPROXIMATELY 1655 HOURS ON 24MAY2011. A ONEOK EMPLOYEE WHO LIVED NEAR THE INCIDENT SITE NOTIFIED THE EDMOND STORAGE SUPERVISOR AFTER THE TORNADO STRUCK THAT THERE WAS LEAKING GAS. ONEOK PERSONNEL WERE DISPATCHED AND VERIFIED A LEAK CAUSED BY A MISSING VENT STACK ON THE F-352 PIG LAUNCHER LOCATED APPROXIMATELY 1.5 MILES WEST OF THE EDMOND STORAGE COMPRESSOR STATION (DAMAGE INCLUDED MISSING VENT STACK AND FENCING). FURTHER FIELD INVESTIGATION REVEALED OTHER DAMAGE (MEASUREMENT, CATHODIC PROTECTION, FENCING, PIPE GUARDS, CORROSION COUPON HOLDERS, ELECTRIC SERVICE) AT FOUR STORAGE WELLS (BRIDAL H-1, BRIDAL H-2, MESSENBAUGH S-1, MESSENBAUGH S-2). THE LINES TO THE LAUNCHER AND ALL FOUR WELLS WERE SHUT IN AND BLOWN DOWN BY 1905 HOURS. THE OKLAHOMA CORPORATION COMMISSION WAS NOTIFIED OF THE DAMAGE AT 2130 HOURS ON MAY 24, 2011. REPAIRS HAVE BEEN COMPLETED ON THE LAUNCHER AND THE PIPELINE HAS BEEN RESTORED TO SERVICE. ALL WELLS ARE BACK IN SERVICE BUT FACILITY REPAIRS ARE ONGOING. PHMSA WAS NOTIFIED AT 1545 HOURS ON JUNE 6, 2011 AFTER THE VOLUME OF UNINTENTIONAL GAS LOST WAS DETERMINED TO BE GREATER THAN 3 MCF. UPDATE: ALL FACILITY REPAIRS ARE COMPLETED AND ALL INCIDENT GAS VOLUMES AND COSTS UPDATED APPROPRIATELY. FINAL UPDATE: ONLY CHANGE WAS TO MAKE THIS THE FINAL INCIDENT REPORT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110200 | 15857 | 2011-06-24 13:15 | SUPPLEMENTAL FINAL | 31286 | ONEOK GAS TRANSPORTATION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2011-05-24 16:00 | 2011 |  |  | 35.5364 | -98.1025 | 977301 | 2011-05-24 19:14 |  | NATURAL GAS |  | 41240 | 5304 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-05-24 16:00 | 2011-10-19 07:26 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-05-24 16:15 | 2011-05-24 16:15 | ONSHORE | OK | 73014 | CALUMET | CANADIAN |  |  | DEVON CANA |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | PIPE, VALVES, METERING, REGULATION, ETC | 2010 |  | CARBON STEEL |  | OTHER | [8 empty] | TORNADO DAMAGE | CLASS 1 LOCATION | NO |  | 580 |  | NO | NO | NO |  | 0 | 0 | 18148 | 21234.306500917 | 168258 | 113865.538188277 | 1572052 | 1839400.1544732 | 20311 | 23765.1531485633 | 0 | 0 |  |  | 1778769 | 983038.719931942 | 1998265.15231096 | [8 empty] | 680 |  | 843 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ONSITE OPERATOR EMPLOYEE WAS ONSITE JUST AFTER TORNADO STRUCK | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [52 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | DAMAGE CAUSED BY EF-5 (PER NATIONAL WEATHER SERVICE) TORNADO | YES |  |  | YES | [303 empty] | PATTI FORD | SENIOR PIPELINE SAFETY ENGINEER | patti.ford@oneok.com | 918 588 7131 | 918 732 1311 |  |  |  | MICHEL E. NELSON | SENIOR VICE PRESIDENT | 918 588 7944 | michel.nelson@oneok.com | AN EF-5 TORNADO CAME THROUGH THE ONEOK GAS TRANSPORTATION'S DEVON CANA MEASUREMENT FACILITY LOCATED SOUTH OF CALUMET OKLAHOMA AT APPROXIMATELY 1600 HOURS ON 24MAY2011. A ONEOK EMPLOYEE DISCOVERED LEAKING GAS AND DAMAGE AT THE DEVON CANA MEASUREMENT FACILITY JUST AFTER THE TORNADO STRUCK. FURTHER VISUAL FIELD INVESTIGATION REVEALED SUBSTANTIAL DAMAGE TO THE ENTIRE FACILITY. THE OKLAHOMA CORPORATION COMMISSION AND PHMSA WERE NOTIFED OF THE INCIDENT ON 24MAY2011. APPROXIMATELY 14 MILES OF THE A-1129 24INCH MAINLINE WAS ISOLATED AND BLOWN DOWN ALONG WITH THE DEVON CANA MEASUREMENT FACITLITES BY 2046 HOURS ON 24MAY2011. INITIAL EMERGENCY REPAIRS ISOLATED THE DEVON CANA MEASURMENT FACILITIES FROM THE A-1129 MAINLINE WHICH ALLOWED THE MAINLINE TO BE PLACED BACK IN SERVICE ON 26MAY2011. FITNESS FOR SERVICE ASSESSMENTS OF THE DEVON CANA FACILITY EQUIPMENT AND PIPING ARE CONTINUING. THE DEVON CANA MEASUREMENT FACILITIES WERE REBUILT ENTIRELY. THE FACILITY WAS READY FOR SERVICE ON 19OCT2011.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110202 | 16148 | 2011-06-24 17:30 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2011-05-26 12:54 | 2011 |  |  | 29.222 | -98.097 | 977497 | 2011-05-26 14:00 |  | NATURAL GAS |  | 14395 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-05-26 13:30 | 2011-05-28 13:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-05-26 12:54 | 2011-05-26 13:30 | ONSHORE | TX | 78114 | FLORESVILLE | WILSON |  |  | HWY 887 TO ADKINS | 9122 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 20 |  | 0.25 | 46000 | API5L | LONGITUDINAL ERW - LOW FREQUENCY |  | YOUNGSTOWN STEEL | COAL TAR | [28 empty] | 1950 | 1949 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 480 | 10 |  | CLASS 1 LOCATION | NO |  | 398 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 57580 | 38966.21669627 | 58000 | 67863.6641532504 | 0 | 0 | 0 | 0 |  |  | 115580 | 71549.2587346673 | 106829.88084952 | [8 empty] | 538 |  | 575 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 38016 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS NOTICED IMMEDIATELY AND THE CONTOL CENTER SENT FIELD PERSONNEL TO MAKE APPROPRIATE ISOLATIONS. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) |  |  | YES | METALLURGICAL ANALYSIS WAS INCONCLUSIVE. | [11 empty] | YES | METALLURGICAL ANALYSIS WAS INCONCLUSIVE. | [6 empty] | YES | [63 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | MICHAEL D. SMITH | PIPELINE COMPLIANCE SPECILIEST | mdsmith@eprod.com | 505-908-7241 |  |  |  |  | MICHAEL D. SMITH | PIPELINE COMPLIANCE SPECILIEST | 505-908-7241 | mdsmith@eprod.com | LINE 9122 HWY 887 TO ADKINS RUPTURED AT APPROXIMATELY 12:54PM ON MAY 26, 2011. THE CONTROL CENTER WAS NOTIFIED BY A RANCHER THAT WAS IN THE VICINITY OF THE PIPELINE WHEN THE RUPTURE OCCURRED. FIELD OPERATIONS WAS IMMEDIATELY DISPATCHED TO THE INCIDENT. AT 13:30 FIELD OPERATIONS STARTED MAKING VALVE ISOLATIONS. COUNTY EMERGENCY RESPONSE PERSONNEL WERE ALREADY AT THE INCIDENT WHEN ENTERPRISE FIELD OPERATIONS ARRIVED. THE AREA WAS IMMEDIATELY SECURED. AFTER SECURING THE AREA, ENTERPRISE PRODUCTS STARTED AN INCIDENT INVESTIGATION AND THE PIPE ASSOCIATED WITH THE INCIDENT WAS SENT TO A METALLURGY LAB FOR ANALYSIS. SUPPLEMENTAL COMMENTS: METALLURGY TESTING AND ANALYSIS WAS CONDUCTED BY STORK METALLURGY AND TESTING IN HOUSTON, TX. THE RESULTS WERE INCONCLUSIVE. SUPPLEMENTAL COMMENTS 1-30-12 ENTERPRISE PRODUCTS HAS COMPLETED AN INLINE INSPECTION (MFL) ON THE NORTH SECTION OF LINE 9122, FROM HWY 887 TO THE END OF THE PIPELINE. THE NORTH SECTION WAS ALSO HYDROTESTED TO 1.5 TIMES MAOP. THE SOUTH SECTION OF THE PIPELINE WAS HYDROTESTED IN 2006 AS A PART OF THE INTEGRITY MANAGEMENT PROGRAM. MFL AND HYDROTEST DATA HAVE BEEN REVIEWED BY THE RAILROAD COMMISSION OF TEXAS AS A PART OF THEIR INVESTIGATION. ON COMPLETION OF THE HYDROTEST THE PIPELINE WAS RETURNED TO SERVICE AT IT'S ORIGINAL MAOP OF 612 PSIG. SUPPLEMENTAL FINAL 7-11-13 CORRECTED THE SMYS OF THE PIPELINE TO BE X46 IN PART C. SUPPLEMENT FINAL 9-24-13 CORRECTED THE APPARANT CAUSE IN PART G TO "MATERIAL FAILURE OF PIPE OR WELD" PER FURTHER DISCUSSION WITH PHMSA. SINCE THE TIME OF THE INCIDENT, BOTH AN ILI TOOL RUN AND HYDROTEST (PRESSURE TEST) HAVE BEEN CONDUCTED ON LINE 9122. THERE WAS ONE FAILURE DURING THE PRESSURE TEST AND THE METALLURGICAL ANALYSIS INDICATED THAT THE HYDROTEST FAILURE WAS CAUSED BY A "HOOK CRACK IN THE SEAM".
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110203 | 16975 | 2011-06-24 18:55 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2011-05-25 12:42 | 2011 |  |  | 34.7146 | -114.4933 | 977515 | 2011-05-26 14:10 |  | NATURAL GAS |  | 0 | 465 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-05-25 14:00 | 2011-05-31 22:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-05-25 12:42 | 2011-05-25 12:42 | ONSHORE | CA | 92363 | NEEDLES | SAN BERNARDINO | MILEPOST | L-300B | TOPOCK COMPRESSOR STATION | ODORIZER | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | ODORIZER | 1957 |  | CARBON STEEL |  | OTHER | [8 empty] | OVER-ODORIZED GAS | CLASS 1 LOCATION | YES | METHOD2 | 603 |  | NO | NO | NO |  | 0 | 0 | 2000000 | 2340126.35011208 | 0 | 0 | 0 | 0 | 1400000 | 1638088.44507846 | 0 | 0 |  |  | 3400000 | 1826105.56348074 | 3978214.79519054 | [8 empty] | 493 |  | 660 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | YES | NO | STATE |  |  | MANUAL | MANUAL | 506880 | NO |  | YES |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS INCIDENT WAS NOT PRESSURE RELATED, IT WAS AN OVER-ODORIZATION INCIDENT. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | PERSONNEL MONITORING THE ODORIZER WERE NOT INFORMED OF THE SHUT DOWN OF A LINE; THUS THEY DID NOT SHUT OFF THE ODORIZER RESULTING IN ORDORANT POOLING IN A PIPE WITH NO FLOW. | YES |  |  |  |  | NORMAL OPERATING CONDITIONS | NO | [150 empty] | STEPHEN RAMOS | COMPLIANCE ENGINEER | s3rc@pge.com | 9253286107 |  |  |  |  | LAURENCE DENISTON | MANAGER REGULATORY COMPLIANCE | 9253285756 | lcd1@pge.com | ON MAY 25, 2011 AT 1242 HOURS, PG&E DETERMINED THAT THE ODORANT LEVEL IN TRANSMISSION LINE 300B EXCEEDED LIMITS AT TOPOCK COMPRESSOR STATION. BECAUSE OF CONCERN OF ODOR COMPLAINTS FROM CUSTOMERS SMELLING THE ODORANT AT APPLIANCES THROUGHOUT THE SOUTHERN PG&E TERRITORY, THE DECISION WAS MADE TO VENT >3 MMCF OF GAS TO ATMOSPHERE AT SEVERAL LOCATIONS ON LINE 300B AND SOUTH OF RIDGECREST ON LINE 311. VENTING OCCURRED ON TWO OCCASIONS: 1) AT 1840 HOURS ON 5/26/11 AND COMPLETED AT 0545 HOURS ON 5/27/11 AND 2) AT 1453 HOURS ON TUESDAY MAY 31 AND WAS COMPLETED LATER THE SAME DAY AT APPROXIMATELY 2200 HOURS. GAS SERVICE REPRESENTATIVES WERE STANDING BY DURING THE VENTING, PURGING AND RE-PRESSURIZATION ACTIVITIES; HOWEVER NO CUSTOMER CALLS WHERE RECEIVED. THE ESTIMATED AMOUNT OF GAS VENTED IS 465 MMCF. THERE WERE NO INJURIES OR FATALITIES. THERE WERE NO MAJOR MEDIA OR PUBLIC AGENCIES PRESENT. THIS INCIDENT IS REPORTABLE DUE TO DAMAGES EXCEEDING $50,000. ON SEPTEMBER 11, 2014, PG&E DETERMINED THAT THE VOLUME OF GAS INTENTIONALLY RELEASE SHOULD BE CORRECTED TO 465 MMCF AND THE COST OF GAS INTENTIONALLY RELEASED SHOULD BE CORRECTED TO $2,000,000. PLEASE NOTE THAT PART A, QUESTION 11, "ESTIMATED VOLUME OF INTENTIONAL AND CONTROLLED RELEASE/BLOWDOWN" SHOULD BE 465,000 MCF.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110211 | 15280 | 2011-06-29 15:50 | ORIGINAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2011-06-01 15:05 | 2011 |  |  | 32.384 | -90.1419 | 978146 | 2011-06-01 15:35 |  | NATURAL GAS |  | 227 | 143 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-06-01 15:15 | 2011-06-07 21:25 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-06-01 15:05 | 2011-06-01 15:15 | ONSHORE | MS | 39211 | JACKSON | HINDS | MILEPOST | 070+60 | CANTON 6" | INDEX 301-18 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 240 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | UNDETERMINED | 1973 |  | CARBON STEEL |  | OTHER | [8 empty] | UNABLE TO DETERMINE LEAK SIZE AND TYPE DUE TO LEAK LOCATION IN DITCH EMBANKMENT. A NEW CROSSING WAS INSTALLED. PIPE SECTION WITH LEAK WAS ABANDONED IN PLACE. | CLASS 3 LOCATION | NO |  | 98 |  | NO | NO | NO |  | 0 | 0 | 628 | 734.799673935194 | 996 | 674.02486678508 | 80000 | 93605.0540044834 | 200 | 234.012635011208 | 0 | 0 |  |  | 81824 | 44110.692327378 | 95247.8911802148 | [8 empty] | 298 |  | 405 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 7587 | NO |  |  | YES | YES |  | YES | LOW OPERATING PRESSURES. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INVESTIGATION LEADS TO A DETERMINATION THE PIPELINE WAS OPERATING AT 298 PSIG, WHICH IS IN THE NORMAL OPERATING RANGE. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [146 empty] | GLENN FLOYD | TECHNICAL SPECIALIST | glenn.floyd@bwpmlp.com | 662-781-1710 | 662-781-1712 |  |  |  | JACK L. ADAMS | DIRECTOR OF DOT COMPLIANCE AND SECURITY | 713-479-8099 | jack.adams@bwpmlp.com | GULF SOUTH WAS IN THE PROCESS OF PERFORMING A PIGGING PROJECT ON THE INDEX 301-18 CANTON 6" IN HINDS COUNTY, MISSISSIPPI, WHEN NOTIFICED OF A POSSIBLE LEAK ON THE PIPELINE SYSTEM AT WHITE OAK CREEK CROSSING. GULF SOUTH EMPLOYEES INVESTIGATED AND DETERMINED THAT THERE WAS A LEAK ON THE SYSTEM AND ISOLATED THE PIPELINE SEGMENT BY CLOSING BLOCK VALVES ON EACH SIDE OF THE INCIDENT LOCATION AND BLEW THE PIPELINE DOWN TO ZERO. A DETERMINATION WAS MADE TO INSTALL A NEW CROSSING DUE TO THE LEAK LOCATION WITHIN A DITCH EMBANKMENT. THE PIPELINE SECTION WITH THE LEAK WAS ABANDONED IN PLACE. THE NEW SECTION IS OPERATING NORMALLY.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110226 | 15290 | 2011-07-05 16:34 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2011-06-07 14:42 | 2011 |  |  | 29.0971 | -92.35 | 978958 | 2011-06-07 17:53 |  | NATURAL GAS |  | 27947 | 87646 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-06-08 16:00 | 2011-06-14 13:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-06-07 16:15 | 2011-06-09 17:50 | OFFSHORE | [28 empty] | 60 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | VERMILLION | 116 | BELOW WATER, PIPE ON OR ABOVE SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | VALVE | [31 empty] | MAINLINE | BALL |  | GROVE |  |  |  | 1972 | 1971 | CARBON STEEL |  | LEAK |  |  | OTHER | BROKEN 1" NIPPLE | [5 empty] | CLASS 1 LOCATION | NO |  | 293 |  | NO | NO | NO |  | 0 | 0 | 370741 | 433790.391583452 | 118217 | 80001.2024866785 | 261000 | 305386.488689627 | 4000 | 4680.25270022417 | 0 | 0 |  |  | 753958 | 424390.931286946 | 823858.335459982 | [8 empty] | 806 |  | 1253 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 384384 | NO |  |  | YES | YES |  | YES | PLATFORM RESTRICTIONS AND NO LAUNCHERS OR RECEIVERS EXIST TO ACCOMMODATE AN ILI. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | PRODUCER BLACK ELK ENERGY NOTIFIED BOEMRE WHO NOTIFIED TGP. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATING PRESSURE LIMITS WERE NOT EXCEEDED. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ROUTINE OR NORMAL FISHING OR OTHER MARITIME ACTIVITY NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | FISHING OR MARITIME ACTIVITY | [103 empty] | ROUTINE OR NORMAL FISHING OR OTHER MARITIME ACTIVITY NOT ENGAGED IN EXCAVATION | [261 empty] | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | ken.peters@elpaso.com | 2053257554 | 2053253729 |  |  |  | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | 2053257554 | ken.peters@elpaso.com | BOEMRE (FORMERLY MMS), CONTACTED BY BLACK ELK ENERGY, NOTIFIED TGP OF A LEAK OFFSHORE IN VERMILLION BLOCK 116 THAT APPEARED TO BE IN THE VICINITY OF TGP FACILITIES. TGP MOBILIZED PERSONNEL AND BEGAN TO ISOLATE FACILITIES AROUND THE LEAK LOCATION. TGP'S 509A-1500 LINE WAS FOUND TO BE THE SOURCE OF THE LEAK. DIVERS DISCOVERED THAT A 1" BODY BLEED VALVE AND NIPPLE WAS BROKEN IN THE NIPPLE THREADS, POSSIBLY CAUSED BY OUTSIDE FORCE IMPACT SUCH AS A SHRIMP NET. IT SHOULD BE NOTED THAT BLACK ELK ENERGY CALLED THE NRC ABOUT THE LEAK AND WAS ASSIGNED NO. 978918, WHICH TGP CLAIMED UPON CONTACTING THE NRC. TGP WAS ASSIGNED A NEW NRC NUMBER OF 978958. THE LEAK WAS REPAIRED BY DRILLING OUT THE DAMAGED NIPPLE AND REPLACING WITH A 1-1/4" NIPPLED AND VALVE. THE REPAIRED FACILITY WAS PLACED BACK INTO SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110227 | 16047 | 2011-07-06 16:18 | SUPPLEMENTAL FINAL | 19730 | TRUNKLINE GAS CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2011-06-10 13:37 | 2011 |  |  | 29.5359 | -92.3308 | 979305 | 2011-06-10 15:38 |  | NATURAL GAS |  | 5000 | 7152 | 120 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-06-10 17:01 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-06-10 15:06 | 2011-06-10 16:25 | ONSHORE | LA | 70548 | FRESHWATER CITY | VERMILION | SURVEY STATION NO. | 20+29 | 210A-2400 | ROW NO. 3628 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 216 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.375 | 52000 | API 5LX | DSAW |  | KAISER | COAL TAR | [28 empty] | 1978 | 1977 | CARBON STEEL |  | LEAK |  |  | OTHER | UNKNOWN | [5 empty] | CLASS 1 LOCATION | NO |  | 419 |  | NO | NO | NO |  | 10000 | 11700.6317505604 | 30000 | 35101.8952516813 | 20973 | 14193.0959147425 | 1452000 | 1698931.73018137 | 358000 | 418882.616670063 | 0 | 0 |  |  | 1870973 | 1008330.88948039 | 2178809.96976842 | [8 empty] | 840 |  | 1440 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 121018 | NO |  |  | YES |  |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS SMALL ENOUGH TO NOT IDETIFIABLE BY THE CONTROLLER FROM THE DATA PROVIDED BY SCADA | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | PINHOLE LEAK AT 6 O'CLOCK POSITION |  |  |  |  | YES | LOW FLOW ON A DEAD-END LATERAL |  |  | YES | HISTORICAL DATA |  |  |  |  | YES | DEAD-END LEG OF SUB-SEA LATERAL | YES | NO | NO | NO | [168 empty] | NO | [63 empty] | YES | 2009 | 1941 | NO | [13 empty] | NO | [63 empty] | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | THIS PIPELINE LEAK WAS REPORTED TO TGC GAS CONTROL CENTER AT 1506 HRS. BY A LOCAL OILFIELD OPERATOR WORKING FOR AN UNIDENTIFIED PRODUCER IN THE AREA. THIS OPERATOR WAS WORKING FROM A FLOAT PLANE AND FLEW OVER THE LEAK LOCATION. GAS CONTROL CONTACTED THE LOCAL OPERATIONS PERSONNEL WHO DISPATCHED A HELICOPTER TO THE LOCATION TO VERIFY THE REPORT. UPON ARRIVAL THE LOCAL PERSONNEL CONFIRMED THE LEAK AND WAS ABLE TO LAND NEAR THE DOWNSTREAM VALVE SETTING AND CLOSE THE ISOLATION VALVE. ONCE ADDITIONAL PERSONNEL ARRIVED ON LOCATION THE HELICOPTER WAS DISPATCHED OFFSHORE TO VR 26B AND THE UPSTREAM ISOLATION VALVE CLOSED AND THE PIPELINE WAS SHUT IN AT 1701 HRS. AND PRESSURIZATION PROCESS COMMENCED. DURING THE DEPRESSURIZATION PROCESS THE PIPELINE BEGAN TO LEAK CONDENSATE. TGC PERSONNEL IMMEDIATELY DISPATCHED AN LOCAL OSRO TO THE LOCATION TO ISOLATE THE RELEASE AND BEGIN CLEAN-UP OPERATIONS. ONCE THE RELEASE WAS CONTAINED PIPELINE REPAIR RESOURCES WERE MOBILIZED AND AN ATTEMPT WAS MADE TO EXCAVATE THE PIPELINE. BECAUSE OF THE DEPTH OF THE PIPE AND THE UNSTABLE SOIL CONDITIONS THE DECISION WAS MADE TO BRING IN A GEOTECHNICAL ENGINEERING CONTRACTOR TO PERFORM SOIL ANALYSIS AND PROVIDE AN EXCAVATION SHORING SYSTEM TO MEET OSHA REGULATIONS. THE INVESTIGATION AND REPAIR OPERATION ARE ON HOLD UNTIL THE SHORING SYSTEM IS AVAILABLE AND CAN BE INSTALLED TO ALLOW SAFE ENTRANCE INTO THE EXCAVATION. THIS LINE WAS ABANDONED FOLLOWING THE INVESTIGATION INTO REPAIRING THE PIPELINE. THE COST AND DIFFICULTY OF REPAIR WERE THE ATTRIBUTING FACTORS FOR THE DECISION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110228 | 16139 | 2011-07-06 16:26 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2011-06-14 08:45 | 2011 |  |  | 29.0472 | -90.2293 | 979623 | 2011-06-14 11:15 |  | NATURAL GAS |  | 675 | 1970 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-06-14 14:20 | 2011-06-28 19:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-06-14 10:10 | 2011-06-15 18:30 | OFFSHORE | [28 empty] | 40 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | BAY MAR | 5 | BELOW WATER, PIPE ON OR ABOVE SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | WELD/FUSION |  | 16 |  | 0.406 | 42000 | API 5LX | SEAMLESS |  | NATIONAL TUBE | COAL TAR | [9 empty] | PIPE GIRTH WELD | [18 empty] | 1961 | 1961 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 361 |  | NO | NO | NO |  | 0 | 0 | 7884 | 9224.77807214183 | 2700 | 1827.17584369449 | 306000 | 358039.331567149 | 4000 | 4680.25270022417 | 0 | 0 |  |  | 320584 | 172626.592910914 | 373771.538183209 | [8 empty] | 700 |  | 1069 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 81840 | NO | YES |  | YES |  |  | YES | AT SUBSEA TIE-IN WHERE A DIFFERENT DIAMETER LINE INTERSECTS AT 90 DEGREES. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | TGP WAS NOTIFIED BY BOTH BOEMRE AND BY STONE ENERGY, A PRODUCER. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURES WERE NOT OUTSIDE NORMAL OPERATING LIMITS. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED | YES | YES | [15 empty] | OTHER | OVERLOAD FRACTURE INDUCED BY EXTERNAL BENDING AND/OR TENSILE FORCES. |  |  |  |  | YES | [63 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | ZACHARY RAGAIN | ENGINEER - PIPLINE | zachary_ragain@kindermorgan.com | 7134206633 |  |  |  |  | ZACHARY RAGAIN | ENGINEER - PIPLINE | 7134206633 | zachary_ragain@kindermorgan.com | TENNESSEE GAS PIPELINE (TGP) WAS NOTIFIED ON JUNE 14, 2011, BY BOEMRE AND BY A PRODUCER, STONE ENERGY, OF BUBBLES ON THE OCS IN BAY MAR BLOCK 5, THE COORDINATES OF WHICH INDICATED THEY WERE COMING FROM TGP'S PIPELINE FACILITY. UPON INVESTIGATION, DIVERS REMOVED PROTECTIVE MATS FROM A SUBSEA TIE-IN ASSEMBLY ON TGP'S 524C-400 PIPELINE AND FOUND A CRACK IN THE NECK OF A 2" FLANGE THAT WAS PART OF THE TIE-IN OF AN INTERSECTING PIPELINE. REPAIRS WERE MADE AND THE PIPELINE FACILITY WAS PLACED BACK INTO SERVICE. METALLURGICAL ANALYSIS CONCLUDED THAT THE CRACK IN THE WELD OF THE 2" FLANGE WAS LIKELY DUE TO OVERLOAD FRACTURE DUE TO EXTERNAL BENDING AND/OR TENSILE FORCES. SUCH FORCES WERE POSSIBLY CAUSED BY INSTABILITY OF THE SUBSEA FLOOR AND CONCRETE MATS PLACED OVER ASSEMBLY AT TIME OF CONSTRUCTION. YEAR OF PIPE MANUFACTURE IS ASSUMED TO BE COMMENSURATE WITH YEAR OF INSTALLATION.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110231 | 15362 | 2011-07-07 14:44 | SUPPLEMENTAL FINAL | 31978 | ATMOS PIPELINE - TEXAS | 5420 LBJ FREEWAY, SUITE 1800 | DALLAS | TX | 75240 | 2011-06-10 10:28 | 2011 |  |  | 31.5484 | -97.0841 | 979271 | 2011-06-10 13:18 |  | NATURAL GAS |  | 1059 | 1074 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-06-10 10:48 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-06-10 10:28 | 2011-06-10 10:28 | ONSHORE | TX | 76705 | WACO | MCLENNAN | SURVEY STATION NO. | 7+59 | ATMOS PIPELINE - TEXAS | L8 (3RD) | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12.75 |  | 0.25 | 35000 | B35 | LAP WELDED |  | UNKNOWN | COAL TAR | [28 empty] | 1952 | 1952 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 19 | 46.5 |  | CLASS 2 LOCATION | NO |  | 197 |  | NO | NO | NO |  | 0 | 0 | 5351 | 6261.00804972488 | 5073 | 3433.06039076377 | 24383 | 28529.6503973915 | 2016 | 2358.84736091298 | 50000 | 58503.1587528021 | DAMAGED MFL TOOL |  | 86823 | 47466.3065957539 | 99085.7249515952 | [8 empty] | 348 |  | 500 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 53377 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATIONS PERSONNEL HAD PIPELINE CONFIGURED FOR PERFORMING PIGGING OPERATIONS AT TIME OF INCIDENT AND WERE ON SITE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [64 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | [10 empty] | YES |  |  |  |  | YES | [6 empty] | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO |  | DATA NOT COLLECTED | [121 empty] | YES | YES |  |  | YES |  |  | YES | 2011 | [31 empty] | 2011 | [17 empty] | GAUGE PLATE PIG | 2011 |  |  |  | NO | NO |  |  | NO | [13 empty] | NO | [63 empty] | TOMMY A. CLARK | OPERATIONS SUPERVISOR | tommy.clark@atmosenergy.com | 254-662-7434 | 254-662-7400 |  |  |  | PATTI RICHARDS | VICE PRESIDENT - TECHNICAL SERVICES | 214-206-2807 | patti.richards@atmosenergy.com | COMPANY AND CONTRACT PERSONNEL ON SITE PERFORMING ILI PIGGING OPERATIONS. DURING PIGGING OPERATIONS, PIPELINE FAILURE OCCURRED 759 FEET FROM STATION (RIVER JUNCTION) AND END OF PIPELINE L8(3RD) (STATION 0+00). PIPELINE WAS PLACED OUT OF SERVICE FOR INVESTIGATION, AND THE DAMAGED PIPE SENT TO STORK LABS IN HOUSTON, TEXAS TO BE ANALYZED. RESULTS OF THE EXAMINATION INDICATED THAT THE PIPE HAD BEEN LONGITUDINALLY GOUGED BY OUTSIDE FORCES CONSISTENT WITH A BACKHOE OR SIMILAR EQUIPMENT. THERE ARE NO RECORDS OF THE PIPE BEING DAMAGED IN THE AREA. PIPELINE REMAINS OUT OF SERVICE WHILE ONGOING REMEDIATION ACTIVITIES ARE BEING PERFORMED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110239 | 15428 | 2011-07-11 17:34 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2011-06-13 13:15 | 2011 |  |  | 38.0904 | -121.7507 | 979566 | 2011-06-13 18:00 |  | NATURAL GAS |  | 2000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-06-13 16:00 | 2011-06-15 12:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-06-13 13:22 | 2011-06-13 14:00 | ONSHORE | CA | 94571 | RIO VISTA | SOLANO | MILEPOST | 3.9 | LINE 114 |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 39 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.4 | 29 | GRB | SEAMLESS |  |  | ASPHALT | [28 empty] | 1942 | 1942 | CARBON STEEL |  | MECHANICAL PUNCTURE | 6 | 6 | [7 empty] | CLASS 1 LOCATION | NO |  | 250 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 10000 | 6767.31793960924 | 60000 | 70203.7905033625 | 0 | 0 | 0 | 0 | NONE |  | 70000 | 39241.3780871275 | 76971.1084429718 | [8 empty] | 360 |  | 510 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | REMOTELY CONTROLLED | 2012 | NO |  |  | YES | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS INCIDENT WAS A THIRD PARTY DIG-IN; THERE WERE NO CONTROLLER OR CONTROL ROOM ISSUES ASSOCIATED WITH THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  | YES | PRIVATE BUSINESS | [7 empty] | CONTRACTOR | BACKHOE/TRACKHOE | GRADING | NO |  |  | DATA NOT COLLECTED | YES | NO | NO |  | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | LAURENCE DENISTON | SR. PROGRAM MANAGER | lcd1@pge.com | 925 974 4313 |  |  |  |  | BILL GIBSON | DIRECTOR REGULATORY COMPLIANCE | 9259744210 | No Email Address | ON JUNE 13, 2011 AT 1315 HOURS A THIRD PARTY SUBCONTRACTOR, KNIFE RIVER CONSTRUCTION, STRUCK AND PUNCTURED GAS TRANSMISSION LINE 114 WHILE GRADING INTO A SLOPE ADJACENT TO TOLAND LANE. THE WORK BEING PERFORMED WAS PART OF A LARGER PROJECT TO CUT A DRAINAGE DITCH IN CONJUCTION WITH THE DEVELOPMENT OF A WIND FARM. THE SUBCONTRACTOR DID NOT NOTIFY USA OR PG&E OF THE WORK BEING PERFORMED. THE SUB-CONTRACTOR DID NOT HAVE A VALID USA TICKET AND, AS SUCH, THE AREA WAS NOT PROPERLY DELINEATED OR MARKED AND LOCATED. THE CONTRACTOR CALLED 911 AND PG&E TO REPORT THE INCIDENT. THE FIRE DEPARTMENT WAS ON SCENE. IT IS ESTIMATED THAT 1.5 TO 2 MMCF OF GAS WAS RELEASED TO ATMOSPHERE AT MP 3.9 ON LINE 114. THERE WERE NO INJURIES OR FATALITIES AS A RESULT OF THIS INCIDENT. NO MAJOR MEDIA WAS PRESENT. THIS INCIDENT IS REPORTABLE DUE TO ESTIMATED DAMAGES EXCEEDING $50,000.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110254 | 15302 | 2011-07-22 10:21 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2011-06-26 14:40 | 2011 |  |  | 29.2683 | -92.3569 | 980838 | 2011-06-26 16:10 |  | NATURAL GAS |  | 11500 | 85750 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-06-27 09:00 | 2011-06-30 17:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-06-26 15:50 | 2011-06-28 15:45 | OFFSHORE | [28 empty] | 27 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | VERMILLION | 76 | BELOW WATER, PIPE ON OR ABOVE SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | DRAIN LINES | [40 empty] | CARBON STEEL |  | LEAK |  |  | OTHER | 1/2" PIPE BROKEN BY SHRIMP NET | [5 empty] | CLASS 1 LOCATION | NO |  | 37 |  | NO | NO | NO |  | 0 | 0 | 343000 | 401331.669044222 | 46000 | 31129.6625222025 | 250000 | 292515.79376401 | 4000 | 4680.25270022417 | 0 | 0 | NONE |  | 643000 | 352916.187988233 | 729657.378030659 | [8 empty] | 800 |  | 1253 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 384384 | NO | [5 empty] | YES | PIPE THAT BROKE WAS AUXILIARY DRAIN PIPE, ONLY 1/2 INCH IN DIAMETER. | YES |  |  |  |  | YES | 1/2 INCH AUXILIARY DRAIN PIPING. | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | IT WAS OBSERVED AND CALLED IN BY AN OFFSHORE PRODUCER IN THE AREA. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURES WERE WITHIN NORMAL OPERATING RANGE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ROUTINE OR NORMAL FISHING OR OTHER MARITIME ACTIVITY NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | FISHING OR MARITIME ACTIVITY | [103 empty] | ROUTINE OR NORMAL FISHING OR OTHER MARITIME ACTIVITY NOT ENGAGED IN EXCAVATION | [261 empty] | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | ken.peters@elpaso.com | 2053257554 | 2053253729 |  |  |  | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | 2053257554 | ken.peters@elpaso.com | A GULF OF MEXICO OFFSHORE PRODUCER OBSERVED BUBBLES IN VERMILLION AREA BLOCK 76 AND CALLED IT IN TO TGP GAS CONTROL. THE FIELD PERSONNEL RESPONSIBLE FOR THIS AREA OF THE PIPELINE OPERATIONS RESPONDED AND DETERMINED THAT THE LEAK WAS ON TGP'S 509A-1601 PIPELINE, A LATERAL TIED INTO TGP'S BLUEWATER WEST LEG. ISOLATION VALVES WERE CLOSED IN ORDER TO INVESTIGATE. DIVERS DETERMINED THE SOURCE OF THE LEAK WAS A BROKEN 1/2-INCH DRAIN LINE ON THE SIDE OF A 6-INCH TIE-IN VLAVE. PHYSICAL EVIDENCE INDICATED THAT THE LINE WAS BROKEN BY A HUNG SHRIMP NET. REPAIRS WERE MADE AND THE FACILITY WAS PLACED BACK INTO SERVICE.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20110256 | 15897 | 2011-07-22 14:35 | SUPPLEMENTAL FINAL | 22175 | TARGA MIDSTREAM SERVICES, L.P. | 810 LOWRY HWY | LAKE ARTHUR | LA | 70549 | 2011-07-02 12:00 | 2011 |  |  | 29.3194 | -93.4964 | 981764 | 2011-07-05 16:30 |  | NATURAL GAS |  | 1320 | 55 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-07-05 16:10 | 2011-07-07 17:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-07-05 15:45 | 2011-07-06 20:00 | OFFSHORE | [28 empty] | 50 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST CAMERON | 118 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12 |  | 0.312 | 52000 | API 5LX | SEAMLESS |  | UNKNOWN | EPOXY | [28 empty] | 1968 | 1968 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 298 |  | NO | NO | NO |  | 0 | 0 | 300 | 351.018952516813 | 7000 | 4737.12255772646 | 163000 | 190720.297534135 | 5500 | 6435.34746280823 | 0 | 0 |  |  | 175800 | 95571.9603813887 | 202243.786507186 | [8 empty] | 920 |  | 1300 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | MANUAL | 355597 | NO | YES |  |  | YES |  |  |  | NO | [6 empty] | OFFSHORE GATHERING | NO |  |  |  |  | OTHER | BOEMRE AGENT |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | TIM HUFFER | MANAGER REGULATORY COMPLIANCE | thuffer@targaresources.com | 337-583-4642 | 337-583-4630 |  |  |  | TIM HUFFER | MANAGER REGULATORY COMPLIANCE | 337-583-4642 | thuffer@targaresources.com | ON JULYE 5, 2011 TARGA RECEIVED NOTIFICATION FROM ALEX ALVARADO WITH BOEMRE OF A GAS LEAK IN WEST CAMERON 188 OFFSHORE GULF OF MEXICO. THIS REPORT WAS BASED ON A JULY 2, 2011 NRC REPORT. THE NRC NUMBER OF THE JULY 2ND REPORT IS UNKNOWN. TARGA INVESIGATED THE LEAK ON JULY 5TH AND DETERMINED THE LEAK ORIGINATED FROM A COMPANY OPERATED PIPELINE. REPAIR TO THE PIPELINE WAS COMPLETED BY INSTALLATION OF A CLAMP. TARGA'S REPORT TO THE NRC IS NUMBER 981764.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110261 | 16143 | 2011-07-29 09:34 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2011-07-08 11:42 | 2011 |  |  | 28.2807 | -91.4298 | 982085 | 2011-07-08 15:05 |  | NATURAL GAS |  | 1000 | 27544 | 0.5 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | PIPELINE WAS SHUT IN DUE TO PLANNED ABANDONMENT. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-07-08 14:45 | 2011-07-11 17:45 | OFFSHORE | [28 empty] | 244 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EUGENE ISLAND | 320 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | WELD/FUSION |  | 30 |  | 0.562 | 60000 | API 5LX | DSAW |  | BETHLEHEM | COAL TAR | [9 empty] | PIPE GIRTH WELD | [18 empty] | 1975 | 1974 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 757 |  | NO | NO | NO |  | 0 | 0 | 110178 | 128915.220501325 | 4000 | 2706.92717584369 | 673214 | 787702.910332178 | 3850 | 4504.74322396576 | 0 | 0 | NONE. |  | 791242 | 425626.099023724 | 923829.801233312 | [8 empty] | 247 |  | 1250 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 168590 | NO | [5 empty] | YES | NO PLATFORM CONNECTED, NO LAUNCHERS/RECEIVERS, AND PIPE IS TO BE ABANDONED DUE TO HURRICANE IKE. | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | BOEMRE PATROL OBSERVED AND CONTACTED COAST GUARD WHO CONTACTED TGP GAS CONTROL. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE WAS NOT FLOWING AND PRESSURE WAS WELL BELOW MAOP. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN | [5 empty] | YES | NOT DETERMINED DUE TO IMMINENT ABANDONMENT OF PIPELINE, BUT SUSPICION IS MICROBIOLOGICAL. |  |  | YES | NOT DETERMINED DUE TO IMMINENT ABANDONMENT OF PIPELINE, BUT SUSPICION IS MICROBIOLOGICAL. |  |  |  |  | YES | IN HEAT AFFECTED ZONE OF GIRTH WELD. | YES | YES | NO | NO | [168 empty] | NO | [63 empty] | YES | 1975 | 1937 | NO | [13 empty] | NO | [63 empty] | ZACHARY RAGAIN | ENGINEER - PIPELINE | zachary_ragain@kindermogan.com | 7134206633 | 7134206633 |  |  |  | ZACHARY RAGAIN | ENGINEER - PIPELINE | 7134206633 | zachary_ragain@kindermorgan.com | BOEMRE OBSERVED BUBBLES AND A LIGHT SHEEN IN THE VICINITY OF TENNESEE GAS PIPELINE'S (TGP) FACILITIES ON THE OCS IN EUGENE ISLAND BLOCK 320. BOEMRE CONTACTED THE COAST GUARD WHO CONTACTED TGP GAS CONTROL. THE LEAK WAS DETERMINED TO BE COMING FROM TGP'S 30" 523M-2300 PIPELINE WHICH WAS ISOLATED DUE TO PENDING ABANDONMENT AND UNDER ONLY 247 PSIG OF GAS PRESSURE. DIVERS DETERMINED A PIN HOLE LEAK TO BE THE CAUSE AND REPAIRED WITH A CLAMP. ABANDONMENT OF THE LINE WILL PROCEED. SUBSEQUENT TO THE ABOVE JULY 8, 2011 OCCURRENCE, THERE WAS A LEAK FROM THIS TGP 523M-2300 PIPELINE THAT INVOLVED ONLY LIQUIDS AND RESULTED IN A SMALL SHEEN ON FEBRUARY 3, 2012. THERE WAS NO GAS RELEASED. CONSEQUENTLY, PURSUANT TO APPROVAL TO DO SO FROM MR. GENE ROBERSON, PHMSA SW REGION, THIS IS BEING NOTED HERE AND IT WAS ASSIGNED NRC NO. 1002085.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110264 | 15933 | 2011-08-02 16:07 | SUPPLEMENTAL FINAL | 13769 | NORTHERN BORDER PIPELINE COMPANY | 13710 FNB PARKWAY | OMAHA | NE | 68154 | 2011-07-05 23:00 | 2011 |  |  | 48.5959 | -107.3238 | 981794 | 2011-07-06 00:45 |  | NATURAL GAS |  | 27090 | 27090 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-07-06 00:10 | 2011-07-06 08:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-07-05 23:00 | 2011-07-06 12:10 | ONSHORE | MT | 59261 | SACO | PHILLIPS | MILEPOST | 0 | MONCHY | NORTHERN BORDER MAINLINE VAVLE 1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1982 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL | OTHER | [8 empty] | 1/4'' PILOT VALVE SUPPLY STAINLESS STEEL TUBING | CLASS 1 LOCATION | NO |  | 1098 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 831600 | 562770.159857904 | 75000 | 87754.7381292031 | 5000 | 5850.31587528021 | 0 | 0 |  |  | 911600 | 626416.568059332 | 656375.213862387 | [8 empty] | 1400 |  | 1435 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NORTHERN BORDER GAS CONTROL IDENTIFIED THE SIGNIFICANT LOSS IN PRESSURE FROM 1400 PSI DOWN TO 1175 PSI AT THE MONCHY FACILITY LOCATED AT THE US/CANADIAN BORDER. GAS CONTROL DISPATCHED PERSONNEL TO THE SITE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [13 empty] | YES | [177 empty] | DANIEL C CERKONEY | COMPLIANCE ENGINEER | dan_cerkoney@transcanada.com | 701-483-1314 | 701-483-1431 |  |  |  | DANIEL C CERKONEY | COMPLIANCE ENGINEER | 701-290-1176 | dan_cerkoney@transcanada.com | THE 1/4" PILOT VALVE SUPPLY PRESSURE TUBING FAILED, RESULTING IN THE ACTIVATION OF THE MAIN LINE RELIEF VALVE (PSV-5014) AT THE MONCHY FACILITY. TECHNICIAN DISASSEMBLED PILOT VALVE TO INVESTIGATE FOR DAMAGE AND FOUND O-RING FROM THE NOZZLE & SEAT OF PILOT RELIEF VALVE HAD DEGRADATED TO THE POINT OF ALLOWING GAS FLOW IN THE PILOT RELIEF VALVE. THIS RESULTED IN THE PILOT RELIEF VENT LINE TO VENT AT LINE PRESSURE. THE VENTING CAUSED THE VIBRATION ON THE SUPPLY TUBING WHICH IN TURN RUPTURED FROM THIS EXTREME VIBRATION. WHEN THE SUPPLY TUBING FAILED THE 8" RELIEF BECAME UNSEATED AND CAME FULLY OPEN. THIS PILOT RELIEF VALVE IS CALIBRATED & TESTED ANNUALLY AND IS RE-KITTED WITH A PILOT SOFT GOODS KIT ANNUALLY.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110265 | 15935 | 2011-08-03 10:34 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | TX | 77002 | 2011-07-09 06:46 | 2011 |  |  | 41.6203 | -88.5835 | 982145 | 2011-07-09 09:14 |  | NATURAL GAS |  | 13000 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | FACILITY SHUT DOWN CAUSED THE INCIDENT. | [6 empty] | NO |  |  |  |  | NO | [7 empty] | 2011-07-09 06:46 | 2011-07-09 06:46 | ONSHORE | IL | 60541 | SANDWICH | KENDALL | MILEPOST | VS 52 | SANDWICH COMPRESSOR STATION |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [8 empty] | CARBON STEEL |  | OTHER | [8 empty] | MAINLINE RELIEF VALVE OPENED AND DISCHARGED TWICE (ABOUT 40 MINUTES AND ABOUT 15 MINUTES) WHEN ENGINES SHUT DOWN AND BYPASS VALVES OPENED. TURNS OUT RELIEF SET POINT WAS ABOUT 30 PSI TOO LOW AND THE STATION DISCHARGE PRESSURE WAS ABOVE THIS LOW SET POINT. ENGINES WENT DOWN BECAUSE OF AN INCORRECT (ALSO LOW) MAXIMUM DISCHARGE VALUE IN THE NEW STATION CONTROL LOGIC. | CLASS 1 LOCATION | NO |  | 153 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 52000 | 35190.053285968 | 0 | 0 | 500 | 585.031587528021 | 0 | 0 |  |  | 52500 | 36751.6710459303 | 35775.0848734961 | [8 empty] | 811 |  | 975 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [5 empty] | YES | POST INCIDENT TESTING AND A REVIEW OF SCADA TREND DATA REVEALED THAT THIS WAS A SOFTWARE AND CONTROLS SET POINT ISSUE. THE ESD SET POINT WAS SET TOO LOW. THERE WAS AN INCORRECT ADJUSTMENT IN DEC. 2010. ALSO, THE VALVE SET POINT COULD HAVE MIGRATED. ONE POSSIBLE SOLUTION IS TO VERFY SET POINTS MORE FREQUENTLY. | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | JOB - TOOLS AND EQUIPMENT - INADEQUATE MAINTENANCE |  |  |  | YES | RELIEF SET POINT WAS INCORRECT. ALSO THERE WAS AN INCORRECT MAXIMUM DISCHARGE VALUE IN THE STATION CONTROL LOGIC. | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | LOUIS SALINAS | COMPLIANCE ENGINEER | louis_salinas@transcanada.com | 832-320-5305 | 832-320-6305 |  |  |  | LOUIS SALINAS |  | 832-320-5305 | No Email Address | MAINLINE RELIEF VALVE OPENED AND DISCHARGED TWICE (ABOUT 40 MINUTES AND ABOUT 15 MINUTES) WHEN ENGINES SHUT DOWN AND BYPASS VALVES OPENED. TURNS OUT RELIEF SET POINT WAS ABOUT 30 PSI TOO LOW AND THE STATION DISCHARGE PRESSURE WAS ABOVE THIS LOW SET POINT. ENGINES WENT DOWN BECAUSE OF AN INCORRECT (ALSO LOW) MAXIMUM DISCHARGE VALUE IN THE NEW STATION CONTROL LOGIC.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110267 | 15780 | 2011-08-04 07:23 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION CORP | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2011-07-12 07:58 | 2011 |  |  | 40.1671 | -81.6131 | 982426 | 2011-07-12 10:04 |  | NATURAL GAS |  | 55629 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-07-12 08:20 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-07-12 07:58 | 2011-07-12 08:15 | ONSHORE | OH | 43749 |  | GUERNSEY | SURVEY STATION NO. | 282+84 | SO-1451 | VS-3056 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 44 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8.625 |  | 0.277 | 35000 | UNKNOWN | SEAMLESS |  | UNKNOWN | COAL TAR | [28 empty] | 1954 | 1954 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 8.6 | 12 |  | CLASS 1 LOCATION | NO |  | 207 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 261679 | 177086.499111901 | 17500 | 20476.1055634807 | 1500 | 1755.09476258406 | 12500 | 14625.7896882005 | METALLURGICAL ANALYSIS |  | 293179 | 200511.945520609 | 213943.489126166 | [8 empty] | 966 |  | 1215 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 9560 | NO | YES | YES | [5 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | REVIEW OF CIRCUMSTANCES INDICATED NO FURTHER INVESTIGATION WAS NECESSARY. PIPELINE WAS OPERATING BELOW ITS MAOP. SCADA ALERTED CONTROLLER TO A PRESSURE DROP. CONTROLLER RECOGNIZED PRESSURE DROP AS ABNORMAL AND ACTIONS WERE TAKEN IN ACCORDANCE WITH PROCEDURES. INCIDENT WAS CAUSED BY FACTORS NOT RELATED TO THE OPERATION OF THE PIPELINE. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | GREGORY LAGO | ENGINEER | glago@nisource.com | (304) 357-2465 | (304) 357-3804 |  |  |  | MIKE HOFFMAN | MANAGER-SYSTEM INTEGRITY | (304) 357-2548 | mikehoffman@nisource.com | INCIDENT OCCURRED ON LINE SO-1451, A NATURAL GAS STORAGE FIELD MAINLINE. A METALLURGICAL ANALYSIS PERFORMED BY AN OUTSIDE CONSULTANT DETERMINED THAT THE CAUSE OF THE INCIDENT WAS INTERNAL CORROSION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110273 | 16823 | 2011-08-05 14:08 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2011-07-10 10:31 | 2011 |  |  | 34.2373 | -118.9028 | 982246 | 2011-07-10 16:30 |  | NATURAL GAS |  | 3270 | 1920 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-07-10 12:20 | 2011-07-19 14:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-07-10 10:31 | 2011-07-10 11:00 | ONSHORE | CA | 93012 | CAMARILLO | VENTURA | SURVEY STATION NO. | 138969.6 | LINE 404 | 3949 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 18 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 18 |  | 0.25 | 50000 | X-50 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | A O SMITH COMPANY | COAL TAR | [28 empty] | 1944 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 61 | 18 | [7 empty] | CLASS 1 LOCATION | NO |  | 278 |  | NO | NO | NO |  | 0 | 0 | 7500 | 8775.47381292031 | 13000 | 8797.51332149201 | 200000 | 234012.635011208 | 1000 | 1170.06317505604 | 0 | 0 |  |  | 221500 | 121104.01975863 | 252755.685320677 | [8 empty] | 590 |  | 650 | OTHER | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | AUTOMATIC | 51057 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE WAS ALREADY DAMAGED ONCE THE CALL WAS MADE TO THE CONTROLLER. AUTOMATED LINE BREAK CONTROLS ACTUATED TO SHUT IN THE PIPELINE WITHIN MINUTES OF THE DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  | YES | PRIVATE EASEMENT | [7 empty] | FARMER | FARM EQUIPMENT | AGRICULTURE | NO |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER |  | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | TROY BAUER | PIPELINE SAFETY AND COMPLIANCE ADVISOR | tbauer@semprautilities.com | 909-376-2708 |  |  |  |  | TROY BAUER | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 909-376-2708 | tbauer@semprautilities.com | FARMER STRUCK LINE WHILE WORKING FIELD WITH A TRACTOR. NO REQUEST TO ONE CALL CENTER. UTILITY WAS NOT AWARE THAT WORK WAS IN PROGRESS. NO IGNITION OR INJURIES. TWO CUSTOMERS TEMPORARILY IMPACTED BY SHUTDOWN. LINE PUT BACK INTO SERVICE JULY 19 AFTER PIPE WRAP CLEANUP WAS COMPLETED. INCIDENT BECAME REPORTABLE WHEN POTENTIAL OF DAMAGE EXCEEDING $50,000 AND/OR ESCAPING EXCEEDING 3 MILLION CUBIC FEET WAS DETERMINED. ALL REPAIRS COMPLETE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110294 | 15608 | 2011-08-16 21:01 | SUPPLEMENTAL FINAL | 32487 | TRANSCANADA NORTHERN BORDER INC | 700 LOUISIANA ST | HOUSTON | TX | 77002 | 2011-07-20 19:30 | 2011 |  |  | 44.3933 | -105.8387 | 983351 | 2011-07-21 00:13 |  | NATURAL GAS |  | 50555 | 41938 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-07-20 19:40 | 2011-08-05 19:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-07-20 20:15 | 2011-07-20 20:15 | ONSHORE | WY | 82716 | GILLETTE | CAMPBELL | MILEPOST | 16.2 | BISON PIPELINE | MLV 0 - MLV 17 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 |  | 0.438 | 70000 | API 5L | SINGLE SAW |  | WELSPUN | EPOXY | [28 empty] | 2010 | 2007 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  |  |  |  | CLASS 1 LOCATION | NO |  | 846 |  | NO | NO | NO |  | 0 | 0 | 184765 | 216186.72253923 | 234550 | 158727.442273535 | 4280685 | 5008671.88251477 | 10000 | 11700.6317505604 | 1990000 | 2328425.71836152 | TESTING AND CONTINGENCIES |  | 6700000 | 3637087.65712773 | 7723712.39743962 | [8 empty] | 1340 |  | 1440 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | AUTOMATIC | 96626 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER SAW SCADA INFORMATION SHOWING UNEXPECTED PRESSURE DROP ON BISON PIPELINE AND CONTACTED UPSTREAM SUPPLIER. AFTER CONTACTING FIELD OPERATIONS, CONTROLLER RECONTACTED UPSTREAM SUPPLIER OF CONTINUED PRESSURE LOSS , WHO SHUT IN THEIR COMPRESSION, DROPPING FLOW INTO BISON PIPELINE TO ZERO. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | YES | [7 empty] | YES | INSTALLATION-RELATED DAMAGE SUSPECTED DURING BACKFILL | [8 empty] | YES | YES |  |  | YES | [63 empty] | YES | [6 empty] | YES | [50 empty] | COMBINATION TOOL | 2011 |  |  |  |  | NO |  |  | NO | [13 empty] | NO | [63 empty] | LOUIS SALINAS | REGULATORY COMPLIANCE ENGINEER-SPECIALIST | louis_salinas@transcanada.com | 832-320-5305 |  |  |  |  | LOUIS SALINAS | REGULATORY COMPLIANCE ENGINEER-SPECIALIST | 832-320-5305 | louis_salinas@transcanada.com | THE BISON PIPELINE EXPERIENCED A RUPTURE FAILURE AT APPROXIMATE MILEPOST 16.2 IN CAMPBELL COUNTY, WYOMING, AT ABOUT 1930 HOURS ON JULY 20, 2011. THERE AREA OF THE FAILURE WAS REMOTE FROM ROADS OR STRUCTURES RESULTING IN DAMAGE RESTRICTED TO THE PIPELINE RIGHT-OF-WAY. THERE WERE NO INJURIES OR FATALITIES. PRELIMINARY EXAMINATION OF THE PIPE IN THE FIELD AND LABORATORY HAS INDICATED THAT THE FAILURE MAY HAVE BEEN THE RESULT OF MECHANICAL DAMAGE INCURRED DURING PIPELINE INSTALLATION. THE RESULTS OF THE STUDIES HAVE BEEN FINALIZED AND HAVE BEEN SUBMITTED UNDER SEPARATE COVER, AS PART OF THE CORRECTIVE ACTION ORDER.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110297 | 16071 | 2011-08-19 14:03 | SUPPLEMENTAL FINAL | 12874 | QUESTAR PIPELINE COMPANY | 333 SOUTH STATE STREET P.O. BOX 45360 | SALT LAKE CITY | UT | 84145-0360 | 2011-07-21 02:45 | 2011 |  |  | 41.5241 | -109.3196 | 983448 | 2011-07-21 17:25 |  | NATURAL GAS |  | 22000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | [7 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-07-21 02:45 | 2011-07-21 03:15 | ONSHORE | WY | 82901 | ROCK SPRINGS | SWEETWATER |  |  | KANDA COMPRESSOR STATION | UNIT 4 DISCHARGE PIPING | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1981 |  | CARBON STEEL |  | OTHER | [8 empty] | THERE WAS AN OBSTRUCTION IN THE 3/8" TUBE SENSING LINE OF THE RELIEF VALVE, CAUSING THE RELIEF VALVE TO OPEN. | CLASS 1 LOCATION | NO |  | 146 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 91350 | 61819.4493783304 | 0 | 0 | 100 | 117.006317505604 | 0 | 0 |  |  | 91450 | 64144.7391825431 | 61936.455695836 | [8 empty] | 930 |  | 1025 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER'S ACTIONS DID NOT CONTRIBUTE BUT RATHER ASSISTED IN DETERMINING THE CAUSE OF THE INCIDENT. THE INCIDENT WAS CAUSED BY AN OBSTRUCTION IN THE 3/8" TUBE SENSING LINE OF THE RELIEF VALVE, CAUSING THE RELIEF VALVE TO OPEN. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | OBSTRUCTION IN THE 3/8" TUBE SENSING LINE OF THE RELIEF VALVE | [161 empty] | CHAD WILDING | SUPERVISOR OF PIPELINE COMPLIANCE | chad.wilding@questar.com | 801-324-3814 |  |  |  |  | LARRY CONTI | VICE PRESIDENT - ENGINEERING AND OPERATIONS | 801-324-5061 | larry.conti@questar.com | USING SCADA INFORMATION, CONTROL ROOM PERSONNEL FOUND A DROP IN PRESSURE. THEY DISPATCHED OPERATIONAL PERSONNEL TO INVESTIGATE THE ISSUE. THE OPERATIONAL PERSONNEL FOUND A RELIEF VALVE RELEASING GAS EVEN THOUGH THE PRESSURE WAS BELOW THE RELIEF SET POINT. OPERATIONAL PERSONNEL FOUND AN OBSTRUCTION IN THE RELIEF VALVE 3/8" TUBE SENSING LINE CAUSING THE RELIEF VALVE TO OPEN PREMATURELY. OPERATIONAL PERSONNEL REPAIRED THE ISSUE AND RETURNED THE RELIEF VALVE TO PROPER OPERATIONS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110301 | 15322 | 2011-08-22 16:28 | ORIGINAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2011-08-16 14:58 | 2011 |  |  | 35.6159 | -108.7833 | 986200 | 2011-08-16 17:10 |  | NATURAL GAS |  | 18341 | 6436 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-08-16 15:55 | 2011-08-16 21:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-08-16 15:06 | 2011-08-16 15:12 | ONSHORE | NM | 87375 | YA TA HEY | MCKINLEY | MILEPOST | 4+1290.18 | LINE 2207 | SAN JUAN TO GALLUP | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | GRAVEL ROAD | 6 |  | YES |  |  |  |  | YES | UNCASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 4.5 |  | 0.188 | 42000 | API 5L OR EQUIVALENT | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1952 |  | CARBON STEEL |  | MECHANICAL PUNCTURE | 7.8 | 3 | [7 empty] | CLASS 2 LOCATION | NO |  | 90 |  | NO | NO | NO |  | 0 | 0 | 28962 | 33887.3696759731 | 82535 | 55854.0586145648 | 102500 | 119931.475443244 | 0 | 0 | 0 | 0 |  |  | 213997 | 128513.347422991 | 209672.903733782 | [8 empty] | 650 |  | 845 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 39600 | NO | [5 empty] | YES | NO LAUNCHERS OR RECEIVERS PRESENT. | YES |  |  |  |  | YES | SINGLE SOURCE OF SUPPLY TO HOMES | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | OTHER | NOTIFICATION BY NEW MEXICO STATE POLICE |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY DAMAGE CAUSED RELEASE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES | YES | COUNTY ROAD | [9 empty] | COUNTY | GRADER/SCRAPER | GRADING | NO |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO |  | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | ken.peters@elpaso.com | 2053257554 | 2053253729 |  |  |  | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | 2053257554 | ken.peters@elpaso.com | EL PASO NATURAL GAS (EPNG) COMPANY WAS NOTIFIED ON AUGUST 16, 2011, BY THE NEW MEXICO STATE POLICE OF A NATURAL GAS RELEASE AT MCKINLEY COUNTY ROAD 57. EPNG GAS CONTROL CONFIRMED A RAPID PRESSURE DROP IN THE EPNG 4" 2207 LINE AND DISPATCHED FIELD PERSONNEL TO THE SCENE. A MCKINLEY COUNTY ROAD GRADER HAD PUNCTURED THE PIPELINE BUT THERE WAS NO FIRE OR EXPLOSION AND NO INJURIES NOR FATALITIES. EPNG PERSONNEL ISOLATED THE PIPELINE AND REPAIRED IT BY CUTTING IN A NEW CYLINDER OF PIPE. THE PIPELINE WAS SUCCESSFULLY PLACED BACK INTO SERVICE ON THE EVENING OF THE 16TH.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110308 | 16140 | 2011-08-24 16:07 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2011-07-27 04:20 | 2011 |  |  | 35.6168 | -109.4696 | 984020 | 2011-07-27 09:05 |  | NATURAL GAS |  | 81475 | 18378 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-07-27 07:34 | 2011-07-29 04:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-07-27 04:20 | 2011-07-27 07:05 | ONSHORE | AZ | 86505 | GANADO | APACHE | MILEPOST | 119+1752 | LINE 1201 | SAN JUAN TO FRANCONIA JUNCTION | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 35 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 30 |  | 0.339 | 52000 | API 5LX | DSAW |  | KAISER | FIELD APPLIED EPOXY | [9 empty] | PIPE GIRTH WELD | [18 empty] | 1953 | 1953 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 46 | 1.5 |  | CLASS 1 LOCATION | NO |  | 602 |  | NO | NO | NO |  | 0 | 0 | 75350 | 88164.2602404728 | 334000 | 226028.419182948 | 159800 | 186976.095373955 | 0 | 0 | 0 | 0 |  |  | 569150 | 360630.608709203 | 501168.774797377 | [8 empty] | 740 |  | 845 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 98715 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLERS RECEIVED PROPER ALARMS AND NOTIFIED FIELD PERSONNEL OF PRESSURE DROP. FURTHERMORE, MAOP WAS NOT EXCEEDED. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | YES | [7 empty] | YES | EXTERNAL STRESSES INDUCED BY DUCTILE OVERLOAD | [13 empty] | YES |  |  |  | YES | [58 empty] | YES | YES |  |  | YES |  |  | YES | 2003 | [31 empty] | 2003 | [17 empty] | COMBINATION TOOL | 2010 |  |  |  |  | NO |  |  | NO | [13 empty] | NO | [63 empty] | ZACHARY RAGAIN | ENGINEER - PIPELINE | zachary_ragain@kindermorgan.com | 7134206633 |  |  |  |  | ZACHARY RAGAIN | ENGINEER -PIPELINE | 7134206633 | zachary_ragain@kindermorgan.com | A SECURITY GUARD CONTACTED EL PASO NATURAL GAS (EPNG) IN THE PRE-DAWN HOURS OF JULY 27, 2011, TO REPORT WHAT SOUNDED LIKE A RELEASE OF NATURAL GAS. EPNG PERSONNEL CONFIRMED A PRESSURE DROP IN ITS 30" 1201 PIPELINE AND FIELD TECHNICIANS RESPONDED TO THE SCENE. THERE WAS NO FIRE OR EXPLOSION, ONLY A RELEASE OF NATURAL GAS FROM A CIRCUMFERENTIAL CRACK IN A GIRTH WELD. VISUAL EXAMINATION AND METALLURGICAL ANALYSIS REVEALED THAT THE FAILURE WAS DUE TO DUCTILE OVERLOAD POSSIBLY RESULTING FROM EXTERNAL STRESSES. THE PIPELINE HAS BEEN REPAIRED AND PLACED BACK INTO SERVICE.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20110311 | 15434 | 2011-08-25 15:42 | SUPPLEMENTAL FINAL | 32296 | TARGA RESOURCES OPERATING LP | 811 LOUISIANA ST SUITE 2100 | HOUSTON | TX | 77002 | 2011-07-29 12:15 | 2011 |  |  | 29.1464 | -89.4834 | 984257 | 2011-07-29 13:40 |  | NATURAL GAS |  | 2000 | 4000 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-07-29 17:30 | 2011-07-31 18:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-07-29 17:30 | 2011-07-31 14:30 | OFFSHORE | [28 empty] | 25 | IN STATE WATERS | LA | WEST DELTA | 26 | PLAQUEMINE |  |  |  | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 22 |  | 0.5 | 52000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1969 | 1969 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 464 |  | NO | NO | NO |  | 0 | 0 | 18000 | 21061.1371510088 | 9000 | 6090.58614564831 | 225000 | 263264.214387609 | 1000 | 1170.06317505604 | 0 | 0 |  |  | 253000 | 137364.315884692 | 291586.000859323 | [8 empty] | 920 |  | 1182 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 107749 | YES | [7 empty] | NO | [6 empty] | TYPE A GATHERING | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NO | NO | [168 empty] | YES | YES | [6 empty] | 1995 | [55 empty] | YES | 1969 | 2128 | NO | [13 empty] | NO | [63 empty] | TIM HUFFER | MANAGER REGULATORY COMPLIANCE | thuffer@targaresources.com | 337-583-4642 | 337-583-4630 |  |  |  | TIM HUFFER | MANAGER REGULATORY COMPLIANCE | 337-583-4642 | thuffer@targaresources.com | ON JULY 29TH, 2011, TARGA RESOURCES RECEIVED NOTICE OF GAS LEAK OFFSHORE VENICE, LOUISIANA NEAR THE AREA OF TARGA'S OFFSHORE PIPELINE. HELICOPTER FLY-OVER BY TARGA PERSONNEL THAT DAY CONFIRMED LEAKING PIPELINE WAS A TARGA OPERATED PIPELINE. NO-SHEEN FOUND ON THE WATER COMING FROM THE LEAK. STEPS WERE INTITIATED TO REDUCE PRESSURE IN THE PIPELINE FOR REPAIR PROCESS AND TO SOURCE EQUIPMENT AND PERSONNEL TO COMPLETE REPAIR PROCEDURE. REPAIRS WERE COMPLETED ON7/31/2011 BY INSTALLATION OF REPAIR CLAMP. CAUSE OF LEAK WAS A PIN-HOLE DUE TO INTERNAL CORROSION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110313 | 15326 | 2011-08-26 10:02 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2011-08-04 11:00 | 2011 |  |  | 28.8115 | -92.1433 | 984924 | 2011-08-04 13:40 |  | NATURAL GAS |  | 45 | 900 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-08-04 14:00 | 2011-08-09 07:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-08-04 12:30 | 2011-08-06 17:00 | OFFSHORE | [28 empty] | 110 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SOUTH MARSH ISLAND | 29 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12.75 |  | 0.375 | 42000 | API 5L OR EQUIVALENT | OTHER | UNKNOWN | U.S. STEEL | COAL TAR | [28 empty] | 1974 | 1974 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 311 |  | NO | NO | NO |  | 0 | 0 | 3600 | 4212.22743020175 | 180 | 121.811722912966 | 266775 | 312143.603525576 | 2500 | 2925.1579376401 | 0 | 0 |  |  | 273055 | 146684.686460347 | 319402.80061633 | [8 empty] | 868 |  | 1250 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 125928 | NO |  |  |  | YES |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | OPERATOR NOTIFIED BY BOEMRE WHO WAS NOTIFIED BY USCG PATROL OF BUBBLES IN WATER |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE WAS NOT ABOVE NORMAL OPERATING LIMITS. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN | [5 empty] | YES | VISUALLY INSPECTED BY DIVERS AND ASSUMED TO BE INTERNAL CORROSION. | YES |  |  |  | YES | [5 empty] | YES | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | ken.peters@elpaso.com | 2053257554 | 2053253729 |  |  |  | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | 2053257554 | ken.peters@elpaso.com | A US COAST GUARD PATROL OBSERVED A FIVE FEET DIAMETER RING OF BUBBLES IN THE WATER IN THE SOUTH MARSH ISLAND (SMI) AREA BLOCK 29 ON THE OCS. THE USCG CONTACED BOEMRE WHO IN TURN NOTIFIED TENNESSEE GAS PIPELINE (TGP). TGP DISPATCHED COMPANY PERSONNEL AND DIVERS WHO IDENTIFIED A PINHOLE LEAK IN TGP'S 12" 523M-1300 PIPELINE. A CLAMP WAS INSTALLED AND THE PIPELINE WAS PLACED BACK INTO SERVICE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110316 | 15880 | 2011-08-30 13:10 | SUPPLEMENTAL | 31159 | KANSAS GAS SERVICE | 7421 W 129TH | OVERLAND PARK | KS | 66213 | 2011-08-03 06:55 | 2011 |  |  | 37.6317 | -98.2427 | 984756 | 2011-08-03 08:43 |  | NATURAL GAS |  | 10000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | AUTOMATED VALVE WAS INADVERTENTLY FAILED OPEN | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-08-03 06:55 | 2011-08-03 06:55 | ONSHORE | KS | 67068 | KINGMAN | KINGMAN | MILEPOST | 1604-34 | CALISTA COMPRESSOR STATION | VENT VALVE G1-025 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1987 |  | CARBON STEEL |  | OTHER | [8 empty] | FAILURE OF VALVE ACTUATOR | CLASS 3 LOCATION | NO |  | 38 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 57100 | 38641.3854351687 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 57100 | 40061.2788632327 | 38641.3854351687 | [8 empty] | 426 |  | 740 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  |  |  | YES | [6 empty] | YES | 1 | 0 | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | AN ACTUATED VALVE FUNCTIONING AS A VENT VALVE FAILED | [22 empty] | YES | AN ACTUATED VALVE FUNCTIONING AS A VENT VALVE FAILED | [161 empty] | ROBERT HUBBELL | MANAGER MEASUREMENT AND CONTROLS | robert.hubbell@oneok.com | 620-728-4309 | 620-728-4397 |  |  |  | LYNN CROUSE | DIRECTOR TRANSMISSION OPERATIONS | 620-728-4302 | lcrouse@kgas.com | ON 8/2/11, THE VENT VALVE ON THE CALISTA COMPRESSOR STATION UNIT NUMBER 2 INADVERTENTLY OPENED WHEN THE UNIT WAS SHUT DOWN BY GAS CONTROL AT 22:10 HOURS. THE VENT VALVE (DESIGNATED G1-025) IS A 2-INCH ANSI 300 PLUG VALVE WITH A SHAFER AIR-OVER-HYDRAULICS ACTUATOR. THE VALVE IS USED TO BLOW DOWN COMPRESSOR UNIT PIPING FOR MAINTENANCE PURPOSES. THE GAS CONTROL ROOM RECEIVED ALARMS AFTER SHUTDOWN FROM THEIR SUPERVISORY CONTROL AND DATA ACQUISITION (SCADA) SYSTEM ABOUT THE OPEN VENT VALVE BUT THE GAS CONTROLLER DID NOT MAKE ANY NOTIFICATION TO FIELD PERSONNEL OR MANAGEMENT. GAS VENTED THROUGH THE VENT VALVE AT APPROXIMATELY 420 PSIG LINE PRESSURE UNTIL COMPANY CREWS ARRIVED AT THE STATION THE NEXT MORNING AND HEARD THE GAS VENTING AND CLOSED THE VENT VALVE. TECHNICIANS UNSUCCESSFULLY TRIED TO REPLICATE THE VALVE FAILURE BY STARTING AND STOPPING THE COMPRESSOR UNIT NUMBER 2, BUT THE VALVE NEVER OPENED. THE EXACT CAUSE OF THE EQUIPMENT FAILURE IS UNKNOWN. ALL VALVES UTILIZING THE AIR-OVER-HYDRAULIC ACTUATORS WERE REMOVED TO PREVENT REOCCURRENCE OF THIS SITUATION. ALTHOUGH EQUIPMENT FAILURE WAS DETERMINED TO BE THE ROOT CAUSE OF THE INCIDENT, IF THE GAS CONTROLLER HAD NOTIFIED FIELD PERSONNEL IN A TIMELY MANNER, THE AMOUNT OF GAS RELEASED WOULD HAVE BEEN LESS THAN THE 3,000 MCF REPORTING THRESHOLD.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110336 | 17166 | 2011-09-12 16:35 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2011-08-15 15:19 | 2011 |  |  | 37.7616 | -95.2093 | 986049 | 2011-08-15 16:15 |  | NATURAL GAS |  | 17700 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-08-15 17:00 | 2011-08-15 20:10 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-08-15 15:19 | 2011-08-15 16:08 | ONSHORE | KS | 66772 | SAVONBURG | ALLEN | SURVEY STATION NO. | 105 / 75711.3 | FT. SCOTT 12" | YJ | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 50 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 |  | 0.203 | 42000 | API 5LX | LONGITUDINAL ERW - HIGH FREQUENCY |  | LTV - REPUBLIC | COLD APPLIED TAPE | [28 empty] | 1987 | 1985 | CARBON STEEL |  | MECHANICAL PUNCTURE | 2 | 8 | [7 empty] | CLASS 1 LOCATION | NO |  | 187 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 61643 | 41715.7779751332 | 116300 | 136078.347259018 | 7875 | 9214.24750356633 | 2517 | 2945.04901161606 | SUPPLEMENTAL MAILING FOR STAKEHOLDERS IN ALLEN COUNTY. |  | 188335 | 111293.631222081 | 189953.421749333 | [8 empty] | 371 |  | 450 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 62500 | NO | YES | YES | YES | YES | YES |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [7 empty] | FARMER | GRADER/SCRAPER | UNKNOWN/OTHER | NO |  |  | UNKNOWN/OTHER | NO | NO | NO |  | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | DAVID COOMES | PIPELINE COMPLIANCE ENGINEER | david.coomes@sscgp.com | 270-852-4391 |  |  |  |  | DAVID SINCLAIR | MANAGER PIPELINE COMPLIANCE | 270-852-4424 | david.l.sinclair@sscgp.com | ON AUGUST 15, 2011 A CALL WAS PLACED BY DOZER OPERATOR, RON HALLACY WITH BEACHNER CONSTRUCTION, TO OUR EMERGENCY NUMBER AT 15:19. THE CALL WAS ANSWERED BY SOUTHERN STAR GAS CONTROL CENTER. THE CONTROL ROOM OPERATOR THAT ANSWERED THE PHONE IMMEDIATELY CONTACTED THE PERSON ON CALL IN THE WELDA WORK LOCATION TO RESPOND TO THE INCIDENT. THE ON CALL PERSON IN THE WELDA WORK LOCATION CONTACTED THE REGION MANAGER FOR THE AREA AND THE REGION MANAGER RESPONDED AS WELL. THE ON CALL OPERATOR IN THE WELDA WORK LOCATION ARRIVED ON SITE AT 16:08 AND FOUND A DOZER HAD STRUCK SSCGP FT. SCOTT 12" LINE AND GAS WAS BLOWING. LOCAL LAW ENFOREMNET WAS CONTACTED BY THE SSCGP ON CALL AT 16:10 TO CLOSE THE SEGEMNT OF CALIFORNIA ROAD NEAREST THE INCIDENT SITE. THE SEGMNET WAS ISOLATED AND CUSTOMERS WERE INFORMED OF POSSIBLE INTERRUPTION. THE REGION MANAGER ARRIVED ON SITE AT 19:00. AT 19:38 THE CREW FROM SSCGP STARETD TO EXPOSE PIPE AND INSTALL EMERGENCY SLEEVE. BY 20:00 THE EMERGENCY SLEEVE WAS INSTALLED. GAS CONTROL WAS CONTACTED TO LET THEM KNOW THAT NORMAL PRESSURE COULD BE RESTORED ON THE FT. SCOTT LINE. AT 20:50 THE LINE PACK HAD STARTED. THE SSCGP CUSTOMERS WERE NOTIFIED THAT THE SEGMENT HAD BEEN TEMPORARILY REPAIRED AND THAT THE SEGEMENT HAD BEEN RESTORED BUT WOULD BE OPERATING AT A REDUCED PRESSURE.
2021-02-26 10:37 | YES | YES | GT (Gas Transmission) | 20110343 | 16089 | 2011-09-15 11:43 | SUPPLEMENTAL FINAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2011-08-16 09:53 | 2011 |  |  | 41.0342 | -88.0884 | 986120 | 2011-08-16 11:10 |  | NATURAL GAS |  | 0.01 |  | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 |  | YES |  | 2011-08-16 09:54 | 2011-08-20 08:23 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 0 | 2011-08-16 09:53 | 2011-08-16 09:53 | ONSHORE | IL | 60941 | HERSCHER | KANKAKEE |  |  | HERSCHER STORAGE FACILITY STATION 201 | HERSCHER STORAGE FACILITY | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 1952 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | COMPRESSOR ENGINE CRANKCASE | OTHER | [8 empty] | CRANKCASE EXPLOSION | CLASS 1 LOCATION | NO |  | 606 |  | NO | NO | NO |  | 0 | 0 | 250 | 292.51579376401 | 1 | 0.676731793960924 | 1318206 | 1542384.29773792 | 2612 | 3056.20501324638 | 92910 | 108710.569594457 | INCIDENT INVESTIGATION COSTS |  | 1413979 | 759433.964080748 | 1654444.26487119 | [8 empty] | 0 |  | 858 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | UNIT 5 WAS OFFLINE AT THE TIME OF THE INCIDENT AND THEREFORE WAS NOT MONITORED BY THE CONTOLLER | [12 empty] | YES | 3 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | THE CREW DID NOT IDENTIFY WHETHER THERE MAY HAVE BEEN A COMBUSTIBLE MIXTURE INSIDE THE CRANKCASE, WHICH WAS A POTENTIAL HAZARD. THE CREW ALSO DID NOT USE THE PORTABLE GAS DETECTOR INSIDE THE CRANKCASE AND DID NOT COVER AND/OR ADEQUATELY COVER THE OPENING TO THE CRANKCASE. |  |  |  | YES | SEE THE INVESTIGATION REPORT SUBMITTED TO PHMSA AND DATED JUNE 18, 2012 | OTHER MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | MARTIN MULLER | COMPLIANCE ENGINEER | martin_muller@kindermorgan.com | 2053253863 | 2053253508 |  |  |  | REJI GEORGE | DIRECTOR COMPLIANCE CODES AND STANDARDS | 7134205433 | reji_george@kindermorgan.com | A CREW PERFORMED MAINTENANCE ON COMPRESSOR UNIT #5 TO REPAIR AN OIL LEAK BELOW THE TURBOCHARGER. TO REPAIR THE LEAK, THE CREW INTENDED TO SUPPORT THE TURBOCHARGER STAND WITH A HYDRAULIC JACK, CUT THE TWO LEGS OFF WITH A PORTABLE GRINDER, INSTALL A GASKET UNDER EACH LEG, AND THEN REPLACE EACH LEG TO ITS ORIGINAL POSITION BY WELDING AT THE LOCATION OF THE CUT. THE CREW COMPLETED ALL OF THESE TASKS UP TO THE POINT OF WELDING THE SECOND LEG. THE INCIDENT OCCURRED WHEN THE CREW WAS WELDING THE SECOND LEG. IN ORDER TO HAVE SUFFICIENT ROOM TO PERFORM WORK ON THE SECOND LEG, THE CREW HAD REMOVED THE CRANKCASE BREATHER. THE CREW HAD USED PORTABLE GAS DETECTORS IN AND AROUND THE WORK AREA, BUT THEY FAILED TO POSITION THE PORTABLE GAS DETECTORS INSIDE THE CRANKCASE, SO THE CREW WAS NOT AWARE THAT THERE WAS COMBUSTIBLE GAS IN THE CRANKCASE. AFTER PERFORMING A POST-INCIDENT INVESTIGATION, IT IS BELIEVED THAT THERE WAS EXCESSIVE LEAKAGE OF THE PACKING GLAND SEALS, WHICH RESULTED IN THE GAS MIGRATING TO THE CRANKCASE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110345 | 15947 | 2011-09-14 | SUPPLEMENTAL FINAL | 602 | CENTERPOINT ENERGY GAS TRANSMISSION | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2011-08-16 21:19 | 2011 |  |  | 35.0931 | -97.5521 | 986213 | 2011-08-16 22:19 |  | NATURAL GAS |  | 47000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-08-16 21:19 | 2011-08-17 01:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-08-16 21:19 | 2011-08-16 21:19 | ONSHORE | OK | 73004 | AMBER | GRADY | MILEPOST | VALVE STATION | AMBER COMPRESSOR STATION | SG20225 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1995 |  | CARBON STEEL |  | OTHER | [8 empty] | LIGHTENING CAUSED THE STATION TO GO INTO ESD. POWER GAS VALVE FAILED AND THE STATION DID NOT ESD CORRECTLY. | CLASS 1 LOCATION | NO |  | 1000 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 188000 | 127225.577264654 | 0 | 0 | 8200 | 9594.51803545955 | 0 | 0 |  |  | 196200 | 136304.669806899 | 136820.095300113 | [8 empty] | 715 |  | 1000 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | YES | [6 empty] | YES |  |  | YES | [24 empty] | YES | THERE WERE NO ADDITIONAL FACTORS THAT CONTRIBUTED TO THE EQUIPMENT FAILURE. | [161 empty] | JIMMY CROSS | DOT WAIVER SPECIALIST | jimmy.cross@centerpointenergy.com | 318 429-3664 | 318 429-3997 |  |  |  | JOHNNY CAVITT | MANAGER OF DOT COMPLIANCE | 318 429-3606 | johnny.cavitt@centerpointenergy.com | ON AUGUST 16, 2011 AT 20:45 A CEGT WESTERN REGION EMPLOYEE REPORTED TO CEGT SYSTEM CONTROL THAT A THIRD PARTY CONTACTED HIM ABOUT BLOWING GAS AT AMBER STATION. CEGT SYSTEM CONTROL CONTACTED AMBER FIELD PERSONNEL TO GO TO THE AMBER STATION AND CHECK OUT THE REPORT. AT 21:19 AN AMBER TEAM EMPLOYEE ADVISED CEGT SYSTEM CONTROL THAT THEY DO HAVE GAS BLOWING AT AMBER STATION AND THAT HE IS CURRENTLY UNSURE WHAT THE CAUSE IS. AMBER EMPLOYEES ADVISED THAT EMERGENCY PERSONNEL (FIRE AND POLICE) ARE ON SCENE. AT 21:30 AMBER EMPLOYEES CONTACTED THE CEGT SYSTEM CONTROL MANAGER AND INFORMED HIM OF THE SITUATION AT AMBER AND REQUESTED ASSISTANCE ON REPORTING THE INCIDENT. AT 21:40 AN AMBER EMPLOYEE CONTACTED SYSTEM CONTROL AND ADVISED THAT WHEN HE ARRIVED AT 21:15 GAS WAS STILL BLOWING. HE INFORMED SYSTEM CONTROL THAT HE MANIPULATED VALVES TO STOP THE RELEASE AT 21:29. HE ADVISED FIRE AND POLICE HAVE CLOSED THE ROAD OUTSIDE OF THE STATION. AT 22:41 CEGT SYSTEM CONTROL MANAGER CONTACTED PERSONNEL ON LOCATION AND CONFIRMED THAT THE ROAD CLOSURE WAS COUNTY ROAD 1280. THE ROAD WAS REOPENED WHEN THE STATION WAS SECURED AND FIRE AND POLICE WERE RELEASED. AMBER EMPLOYEES, ON THE SCENE, REPORTED THAT THE STATION ESD'ED AND WAS BLOWING GAS FROM THE SUCTION AND DISCHARGE LINES. EMPLOYEES OPERATED THE MAINLINE VALVE TO GET THE STATION BACK UNDER CONTROL. EMPLOYEES BEGAN GOING THROUGH THE YARD CHECKING THE SYSTEMS. THEY REPORTED THAT POWER AND COMMUNICATIONS WILL BE RESTORED WHEN THE STATION IS TAKEN OUT OF ESD MODE. A LIGHTENING STORM CAUSED AN ELECTRICAL SUPPLY PROBLEM THAT IN TURN CAUSED THE STATION TO ESD. THE STATION BACKUP GENERATOR DID NOT START. A POWER GAS VALVE FAILED AND DID NOT ISOLATE THE SUCTION AND DISCHARGE LINES, RESULTING IN GAS CONTINUING TO BLOW FROM THE MAINLINE TO THE STATION BLOW DOWN. ON AUGUST 17, 2011 AT 01:45 AMBER TEAM EMPLOYEES HAD THE REPAIRS MADE, RESUMED NORMAL OPERATIONS AT THE STATION AND LEFT THE LOCATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110350 | 15586 | 2011-09-19 15:57 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2011-08-22 09:25 | 2011 |  |  | 29.1714 | -90.7217 | 986765 | 2011-08-22 11:53 |  | NATURAL GAS |  | 4 | 4500 | 0.5 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | WAS PREVIOUSLY SHUT IN FOR PLANNED ABANDONMENT. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-08-22 11:15 | 2011-08-22 15:30 | OFFSHORE | [28 empty] | 4 | IN STATE WATERS | LA | OAK BAYOU |  | TERREBONNE |  |  |  | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 26 |  | 0.417 | 52000 | API 5L OR EQUIVALENT | DSAW |  | US STEEL | OTHER | COAL TAR WITH CONCRETE COATING | [27 empty] | 1968 | 1968 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 621 |  | NO | NO | NO |  | 0 | 0 | 18000 | 21061.1371510088 | 16 | 10.8277087033748 | 759503 | 888666.491644589 | 350000 | 409522.111269615 | 0 | 0 |  |  | 1127519 | 605581.66708939 | 1319260.56777392 | [8 empty] | 100 |  | 1200 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 163680 | NO | [5 empty] | YES | HURRICANE KATRINA DESTROYED PLATFORM LAUNCHER. PIPELINE IS PLANNED FOR ABANDONMENT ANYWAY. | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE WAS ISOLATED DUE TO PLANNED ABANDONMENT AND PRESSURE WAS ONLY AT 100 PSIG, FAR BELOW MAOP. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN | [5 empty] | YES | NOT EVALUATED DUE TO PLANNED ABANDONMENT. |  |  | YES | THIS LINE HAD A HISTORY OF INTERNAL CORROSION BUT THIS PARTICULAR ANOMALY WAS NOT EVALUTATED DUE TO THE PLANNED ABANDONMENT OF THE LINE. | YES | [5 empty] | NO | YES | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | ken.peters@elpaso.com | 2053257554 | 2053253729 |  |  |  | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | 2053257554 | ken.peters@elpaso.com | A LOCAL LANDOWNER IN THE LOUISIANA COASTAL MARSH AREA REPORTED SEEING A SMALL SHEEN OF LIQUID IN THE VICINITY OF TENNESEE GAS PIPELINE'S (TGP) 26" 523M-100 LINE. TGP PERSONNEL INVESTIGATED AND DISPATCHED DIVERS WHO CONFIRMED A PINHOLE LEAK IN THE BODY OF THE PIPE. TGP ALSO MOBILIZED A LIQUID CLEAN-UP CONTRACTOR TO ADDRESS THE SMALL LIQUID ACCUMULATION. A CLAMP WAS INSTALLED OVER THE PINHOLE IN THE PIPE AND THE LINE WILL REMAIN SHUT IN FOR ABANDONMENT. SUBSEQUENT TO THIS AUGUST 22, 2011 REPORT, SEVERAL OTHER LEAKS OCCURRED THAT ONLY INVOLVED SMALL SHEENS AND DID NOT INVOLVE ANY ASSOCIATED GAS RELEASE. THE PIPELINE HAD BEEN TAKEN OUT OF SERVICE AND WAS AWAITING ABANDONMENT. THESE ARE NOTED HERE PURSUANT TO APPROVAL TO DO SO FROM MR. GENE ROBERSON, PHMSA SW REGION: 11/7/2011 NRC NO. 994780; 12/6/2011 NRC NO. 997331; 3/23/2012 NRC NO. 1006704.
2021-02-26 10:37 | NO | NO | GG (Gas Gathering) | 20110360 | 15344 | 2011-09-23 16:55 | SUPPLEMENTAL FINAL | 9011 | J - W GATHERING CO | 15505 WRIGHT BROTHERS DRIVE | ADDISON | TX | 75001 | 2011-08-31 15:35 | 2011 |  |  | 32.3489 | -93.6785 |  |  |  | NATURAL GAS |  | 5311 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-08-31 15:45 | 2011-09-13 14:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 4 | 2011-08-31 15:40 | 2011-08-31 15:45 | ONSHORE | LA | 71115 | SHREVEPORT | CADDO | SURVEY STATION NO. | ELLERBE ROAD | ELLERBE ROAD | ELLERBE ROAD | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6.625 |  | 0.156 | 42000 | X42 | SEAMLESS |  | UNKNOWN | PAINT | [28 empty] | 1975 | 1975 | CARBON STEEL |  | OTHER | [8 empty] | MOTOR VEHICLE COLLIDED WITH ABOVE GROUND PIPE. | CLASS 2 LOCATION | NO |  | 157 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 22000 | 14888.0994671403 | 25500 | 29836.6109639291 | 5500 | 6435.34746280823 | 0 | 0 |  |  | 53000 | 32084.9547588702 | 51160.0578938776 | [8 empty] | 760 |  | 1186 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 26000 | NO |  |  |  | YES |  |  |  | NO | [6 empty] | TYPE A GATHERING | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS CAUSED ENTIRELY BY A THIRD PARTY VEHICLE CRASH INTO THE ABOVE GROUND PIPE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [260 empty] | JIM RUMSEY | REGULATORY AFFAIRS | jrumsey@jwenergy.com | 9032912811 | 8668403098 |  |  |  | JIM RUMSEY | REGULATORY AFFAIRS | 9032912811 | jrumsey@jwenergy.com | A MOTOR VEHICLE OPERATED BY A THIRD PARTY WAS TRAVELING SOUTH WITHIN THE 11000 BLOCK OF ELLERBE ROAD IN SHREVEPORT, LA, WHEN THE OPERTOR SWERVED TO AVOID A COLLISION WITH A DOG THAT WAS IN THE ROADWAY. THE OPERATOR OF THE VEHICLE LOST CONTROL OF THE VEHICLE AND VEERED OFF OF THE ROADWAY AND COLLIDED WITH AN ABOVE GROUND VALVE RISER OWNED AND OPERATED BY J-W GATHERING COMPANY. THE COLLISION COMPRIMISED THE AVOBE GROUND PIPING AND RESULTED IN A RELEASE OF NATURAL GAS. NOTIFICATIONS WERE PROMPTLY MADE TO THE LOUISIANA DEPARTMENT OF NATURAL RESOURCES, LOUISIANA STATE POLICE EMERGENCY SERVICES, AND LOUISIANA DEPARTMENT OF ENVIRONMENTAL QUALITY. THE PIPELINE WAS BLOCKED IN BY USE OF MANUAL BLOCK VALVES AND DEPRESSURIZED. THE DAMAGE THAT RESULTED FROM THE COLLISION WAS SUBSEQUENTLY REPAIRED AND THE PIPELINE PLACED BACK INTO SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110370 | 16168 | 2011-09-30 13:26 | SUPPLEMENTAL | 2196 | CENTRAL HUDSON GAS & ELECTRIC CORP | 284 SOUTH AVENUE | POUGHKEEPSIE | NY | 12601 | 2011-08-29 03:56 | 2011 |  |  | 41.4541 | -74.0416 | 987621 | 2011-08-29 11:20 |  | NATURAL GAS |  | 11666 | 35 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-08-29 10:30 | 2011-12-19 17:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 85 | 2011-08-29 04:30 | 2011-08-29 04:30 | ONSHORE | NY | 12520 | CORNWALL | ORANGE | SURVEY STATION NO. | 116 + 61 | TP-C |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 6 |  | 0.219 | 35000 | API 5L GRADE B | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | REPUBLIC | OTHER | BARRETT MILLWRAP ENAMEL SPEC . B-2GF | [8 empty] | PIPE GIRTH WELD | [18 empty] | 1961 | 1954 | CARBON STEEL |  | LEAK |  |  | OTHER | BREAK AT WELD-MUDSLIDE | [5 empty] | CLASS 3 LOCATION | NO |  | 99 |  | NO | NO | NO |  | 0 | 0 | 153 | 179.019665783574 | 51020 | 34526.8561278863 | 440000 | 514827.797024658 | 50000 | 58503.1587528021 | 0 | 0 |  |  | 541173 | 299051.771342893 | 608036.83157113 | [8 empty] | 450 |  | 565 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 5800 | NO |  |  | YES |  |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [52 empty] | HEAVY RAINS/FLOODS |  | MUDSLIDE |  |  |  | YES |  | YES | [304 empty] | LENORE J. CLARKE | SECTION LEADER-GAS SYSTEM SAFETY AND COMPLIANCE | lclarke@cenhud.com | 8454865521 | 8454865697 |  |  |  | PAUL E. HAERING | VICE PRESIDENT- ENGINEERING- OPERATIONS SERVICES | 8454865351 | phaering@cenhud.com | DURING TROPICAL STORM IRENE, SEVERAL HUNDRED FEET OF THE MOODNA CREEK BANK LOCATED IN THE TOWN OF CORNWALL, NEW YORK, COLLAPSED DUE TO BANK EROSION CAUSED BY EXCESSIVE HURRICANE RAIN WATER AND UNDERMINED THIS 6" CARBON STEEL (0.219" WALL THICKNESS) 1961 VINTAGE PIPELINE OPERATING AT 450 PSIG AT THE TIME OF THE FAILURE WITH AN MAOP OF 565 PSIG. THE PIPELINE FAILED AT A WELD ADJACENT TO A 90 DEGREE BEND ON AN OLD RAILROAD BED AT THE TOP OF THE RIVER BANK. APPROXIMATELY 1370 FEET OF THIS 6" PIPELINE WAS RE-ROUTED AND INSTALLED ON A NEW RIGHT OF WAY AWAY FROM THE ERODED MOODNA CREEK BANK. THE NEW PIPELINE SECTION WAS CONSTRUCTED WITH 0.280" WALL THICKNESS X42/X52 STEEL AND A 6" ABOVE GRADE VALVE AND PLACED IN SERVICE ON 12/19/2011. ORIGINAL SUBMITTAL ESTIMATE OF REPAIR COSTS WAS UPDATED TO INCLUDE ADDITIONAL COSTS DUE TO CONSTRUCTION OF ABOVE GRADE VALVE, EASEMENT CONSIDERATIONS DUE TO A NEW NEGOTIATED RIGHT OF WAY WITH THE ADJACENT PROPERTY OWNER, AND CONSTRUCTION EASEMENT CONSIDERATIONS WITH THE NEW RIGHT OF WAY.
2021-02-26 10:37 | NO | NO | GG (Gas Gathering) | 20110371 | 15747 | 2011-09-30 13:58 | SUPPLEMENTAL FINAL | 19570 | WILLIAMS GAS PIPELINE - TRANSCO | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2011-09-08 18:34 | 2011 |  |  | 28.1002 | -91.8014 | 988916 | 2011-09-08 12:22 |  | NATURAL GAS |  | 50 | 7052 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-09-13 14:30 | 2011-09-14 16:05 |  |  |  |  | NO |  |  |  |  | NO | [7 empty] | 2011-09-13 | 2011-09-14 11:15 | OFFSHORE | [28 empty] | 73 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EUGENE ISLAND | 135 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | FLANGE ASSEMBLY | [38 empty] | 1986 |  | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 209 |  | NO | NO | NO |  | 0 | 0 | 28612 | 33477.8475647035 | 202 | 136.699822380107 | 59100 | 69150.7336458121 | 0 | 0 | 0 | 0 | MATERIAL $500, LABOR $3600, TRANSPORTATION $5000, DIVE VESSEL $50,000 |  | 87914 | 47250.9497317965 | 102765.281032896 | [8 empty] | 700 |  | 1404 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 144249 | NO |  |  |  | YES |  |  |  | NO | [6 empty] | TYPE A GATHERING | YES | YES | YES | NO | NO | OTHER | COAST GUARD CONTACTED REPORTED LEAK TO NRC AND WGP-TRANSCO'S GAS CONTROL |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS DETERMINED TO BE CAUSED BY A MECHANICAL COMPONET DURING THE INITIAL INVESTIGATION. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | OTHER | 1" PLEECO BLEEDER PORT PLUG WAS NOT SEALING PROPERLY ALLOWING GAS TO SEEP OUT OF PIPELINE. THE COMPONENT WAS REPLACED AND THE LEAK WAS ELIMINATED. | [18 empty] | YES | WEAR ON 1" PLEECO BLEEDER PORT PLUG OVER TIME WAS CAUSE OF LEAK. | [161 empty] | JOHNNY LOPEZ | PIPELINE SAFETY SPECIALIST | johnny.lopez@williams.com | 7132152995 | 7132152222 |  |  |  | MARIE SOTAK | MANAGER PIPELINE SAFETY | 7132152111 | marie.sotak@williams.com | INVESTIGATION OF A LEAK CONFIRMATION ON A 16" OFFSHORE GATHERING PIPELINE OWNED BY TRANSCO, WAS DETERMINED TO BE A 1" PLEECO BLEEDER PORT PLUG. ATTEMPTS TO STOP THE LEAK BY TIGHTENING THE PLUG DID NOT WORK. THE PLUG WAS REMOVED AND REPLACED WITH A1" STAINLESS STEEL BALL VALVE AND PLUG. THE LINE WAS PRESSUREIZED, CHECKED FOR LEAKS. THE LINE WAS PUT BACK INTO SERVICE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110372 | 15774 | 2011-10-02 17:24 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION CORP | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2011-09-04 06:00 | 2011 |  |  | 40.8194 | -82.4219 | 988385 | 2011-09-04 08:40 |  | NATURAL GAS |  | 9303 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-09-04 07:45 | 2011-10-19 08:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-09-04 07:45 | 2011-09-04 07:45 | ONSHORE | OH | 44903 | MANSFIELD | RICHLAND | MILEPOST | PAVONIA | PAVONIA COMPRESSOR STATION | PAVONIA STORAGE FIELD | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [8 empty] | CARBON STEEL |  | LEAK |  |  | OTHER | MECHANICAL FAILURE | [5 empty] | CLASS 1 LOCATION | NO |  | 115 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 34421 | 23293.785079929 | 642 | 751.180558385979 | 0 | 0 | 0 | 0 | COST OF GAS LOST AMOUNT OF 9,303 MCF, $642 WAS THE COST OF THE NEW RV. |  | 35063 | 24494.5363867401 | 24044.9656383149 | [8 empty] | 1039 |  | 1210 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | OTHER | INTEGRATION DEPARTMENT |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS A MECHANICAL FAILURE OF THE RELIEF VALVE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | 4-IN RELIEF VALVE RELIEVED THE FLOW INTO ATMOSPHERE BEFORE SET POINT WAS REACHED | [161 empty] | GEORGE HAMATY | ENGINEER | ghamaty@nisource.com | 3045538306 | 3043573804 |  |  |  | MICHAEL HOFFMAN | MANAGER | 3043572548 | mikehoffman@nisource.com | A 4-IN RELIEF VALVE (RV) HAD FAILED WHERE IT RELIEVED NATURAL GAS INTO ATMOSPHERE BEFORE REACHING ITS SET POINT AT PAVONIA COMPRESSOR STATION, OH. TOTAL AMOUNT OF NATURAL GAS RELEASED INTO ATMOSPHERE WAS CALCULATED TO BE 9,303 MCF. A QUALITY INVESTIGATION CONSULTANT CONDUCTED A FULL ANALYSIS TO THE FAILED RV AND PROVIDED A ROOT CAUSE ANALYSIS DETAILING THE FOLLOWING: A DESTRUCTIVE/NON-DESTRUCTIVE TEST WAS PERFORMED TO THE REMOVED SOFT GOODS FROM THE FAILED RV AT A CERTIFIED RUBBER LABORATORY FACILITY WHERE IT WAS CONFIRMED THAT THE USED SOFT GOODS WERE PER THE MANUFACTURER'S RECOMMENDED MATERIAL LIST. A NEWLY PUBLISHED MAINTENANCE MANUAL OF THE FAILED RV PROVIDED ONLINE BY THE MANUFACTURER INDICATED THAT THE PRESSURE RATINGS FOR THE INSTALLED PILOT VALVE WERE REDUCED TO A LOWER LEVEL FOR ALL DIAPHRAGM-TYPE INSTALLATIONS. ALL HIGHER PRESSURE VALUES ABOVE THE ASSIGNED THRESHOLD MUST GO TO A PISTON-TYPE PILOT INSTALLATION. THIS INFORMATION THAT WAS RELEVANT TO THE PILOT VALVE WAS NOT PROVIDED TO THE MAINTENANCE FACILITY HENCE IT WAS NOT IMPLEMENTED ONTO THE FAILED RV. AN IN-HOUSE MEMORANDUM WAS ISSUED TO SEARCH FOR ALL SIMILAR INSTALLATIONS TO THE FAILED RV. A SIMILAR INSTALLATION WAS IDENTIFIED AT THE SAME FACILITY AND WAS REMOVED. A DIFFERENT TYPE OF RVS WAS INSTALLED AND NEW CAPACITY CALCULATIONS AND VERIFICATIONS WERE COMPLETED AND THE FACILITY WAS RETURNED BACK TO SERVICE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110374 | 15349 | 2011-10-07 20:30 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2011-09-09 11:19 | 2011 |  |  | 36.7351 | -121.6123 | 989053 | 2011-09-09 13:20 |  | NATURAL GAS |  | 1500 | 1500 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-09-09 13:55 | 2011-09-10 03:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-09-09 11:25 | 2011-09-09 11:56 | ONSHORE | CA | 93901 | SALINAS | MONTEREY | MILEPOST | 19.15 | LINE 103 |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 20 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 |  | 0.25 | 33000 |  | SINGLE SAW |  |  | ASPHALT | [28 empty] | 1930 | 1930 | CARBON STEEL |  | MECHANICAL PUNCTURE | 1 | 2 | [7 empty] | CLASS 1 LOCATION | NO |  | 155 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 55000 | 64353.4746280823 | 5000 | 5850.31587528021 | 0 | 0 |  |  | 60000 | 32225.392296719 | 70203.7905033625 | [8 empty] | 323 |  | 350 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 1850 | NO |  | YES |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS CAUSED BY A DIG-IN; THERE WERE NO ISSUES WITH THE CONTROL ROOM ACTIONS. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  | YES | PRIVATE BUSINESS | [7 empty] | FARMER | FARM EQUIPMENT | AGRICULTURE | NO |  |  | DATA NOT COLLECTED | YES | YES | YES | 24 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | LAURENCE DENISTON | SR. PROGRAM MANAGER | lcd1@pge.com | 925 974 4313 |  |  |  |  | JOE PENNINGTON | PRINCIPAL PORTFOLIO MANAGER | 925 974 4257 | No Email Address | ON SEPTEMBER 9, 2011 AT APPROXIMATELY 1119 HOURS A FARMER, MKM FARMS, RIPPING AN AGRICULTURE FIELD STRUCK LINE 103, A 12-INCH STEEL TRANSMISSION PIPELINE, AT MILE POINT 19.15 RESULTING IN A RELEASE OF GAS. PG&E WAS NOTIFIED AT 11:25, AND WAS ON SCENE AT 1156 HOURS. PG&E CLOSED MAINLINE VALVES AT 13:55 AND THE ISOLATED PIPELINE SECTION WAS DEPRESSURIZED AT 1633 HOURS. SERVICE WAS INTERRUPTED TO 39 CUSTOMERS AS A RESULT OF THIS DIG-IN. REPAIRS WERE COMPLETED AT 0300 HOURS ON 9/10/11 AND FINAL SERVICE RESTORATION WAS COMPLETED AT 1330 HOURS ON SEPTEMBER 10, 2011. THE FARMER DID NOT CALL USA BUT WAS AWARE OF THE LOCATION OF THE PIPELINE. PIPELINE MARKERS WERE VISIBLE AT THE SITE OF THE DIG-IN, AND THE FARMER HAD MADE A LINE IN THE FIELD FROM PIPELINE MARKER TO MARKER PRIOR TO THE START OF RIPPING THE FIELD. THERE WAS NO IGNITION, INJURIES OR FATALITIES AS A RESULT OF THIS INCIDENT. DAMAGES EXCEED $50,000 MAKING THIS INCIDENT REPORTABLE TO THE CPUC AND DOT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110375 | 15350 | 2011-10-12 11:11 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2011-09-19 07:00 | 2011 |  |  | 29.0971 | -93.35 | 990059 | 2011-09-19 08:30 |  | NATURAL GAS |  | 0.25 | 5 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-09-20 07:00 | 2011-09-23 10:50 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-09-19 07:00 | 2011-09-19 07:00 | OFFSHORE | [28 empty] | 70 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | VERMILLION | 116 | BELOW WATER, PIPE ON OR ABOVE SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1972 |  | CARBON STEEL |  | LEAK |  |  | OTHER | THREADS OF FITTING ON VLV BODY | [5 empty] | CLASS 1 LOCATION | NO |  | 318 |  | NO | NO | NO |  | 0 | 0 | 20 | 23.4012635011208 | 1 | 0.676731793960924 | 122500 | 143332.738944365 | 3000 | 3510.18952516813 | 0 | 0 |  |  | 125521 | 67416.2222833151 | 146867.006464828 | [8 empty] | 830 |  | 1253 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 40 | NO | [5 empty] | YES | SUBSEA HEADER ASSEMBLY | YES |  |  |  |  | YES | SUBSEA HEADER ASSEMBLY | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE WAS WITHIN OPERATING LIMITS AND LEAK WAS VERY SMALL IN 70 FEET OF WATER. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | PIPE NIPPLE | [9 empty] | YES | [172 empty] | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | ken.peters@elpaso.com | 2053257554 | 2053253729 |  |  |  | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | 2053257554 | ken.peters@elpaso.com | WHILE ABANDONING ITS 509A-2900 OFFSHORE PIPELINE, TENNESSEE GAS PIPELINE (TGP) COMPANY'S CONTRACTED DIVERS WERE UNCOVERING A MATTED ("BURIED" WITH SANDBAGS) VALVE ASSEMBLY TO CLOSE A SIDE VALVE AND DISCOVERED A MINOR LEAK COMING FROM THE THREADS ON A 1-INCH NIPPLE AT THE BODY OF A DIFFERENT SIDE VALVE IN THE UNDERWATER ASSEMBLY. THIS FABRICATED ASSEMBLY WAS ABOUT 40 FEET IN LENGTH AND COULD BE ISOLATED SUCH THAT GAS LOSS WAS VERY MINIMAL. REPAIRS WERE MADE BY REPLACING THE COMPONENT WITH A NEW 1-INCH NIPPLE AND VALVE (INTENDED FOR BODY BLEED).
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110376 | 15351 | 2011-10-12 16:50 | ORIGINAL FINAL | 602 | CENTERPOINT ENERGY GAS TRANSMISSION | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2011-09-24 00:30 | 2011 |  |  | 34.8573 | -92.3218 | 990655 | 2011-09-24 02:40 |  | NATURAL GAS |  | 5831 | 233.2 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-09-24 06:30 | 2011-09-24 13:55 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-09-24 01:45 | 2011-09-24 01:45 | ONSHORE | AR | 72118 | NORTH LITTLE ROCK | PULASKI | MILEPOST | 274+50 | CEGT LINE B | SG29069 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | 2" BLOW DOWN | 1950 |  | CARBON STEEL |  | OTHER |  |  |  | BROKE AT WELD, VEHICLE STRIKE |  |  |  |  | VEHICLE STRUCK 2" ABOVE GROUND BLOW DOWN RISER, BROKE AT 2" WELD FOR RISER CONNECTED TO 10" PIPELINE | CLASS 1 LOCATION | NO |  | 154 |  | NO | NO | NO |  | 0 | 0 | 835 | 977.002751171795 | 20875 | 14126.7761989343 | 17583 | 20573.2208070104 | 500 | 585.031587528021 | 6500 | 7605.41063786427 | FENCE AND GATE REPAIR/REPLACEMNT |  | 46293 | 28297.6206941112 | 43867.4419825088 | [8 empty] | 427 |  | 500 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 17049 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CAUSED BY THIRD PARTY VEHICLE STRIKING ABOVE GROUND FACILTIES | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [260 empty] | JIMMY CROSS | DOT WAIVER SPECIALIST | jimmy.cross@centerpointenergy.com | 318 429-3664 | 318 429-3997 |  |  |  | JOHNNY CAVITT | MANAGER OF DOT COMPLIANCE | 318 429-3606 | johnny.cavitt@centerpointenergy.com | ON SEPTEMBER 24, 2011 AT 00:30 CEGT SYSTEM CONTROL RECEIVED A PHONE CALL FROM A THIRD PARTY RESIDENCE AT 5319 JOSLIN STREET, NORTH LITTLE ROCK, ARKANSAS OF LOUD NOISE, POSSIBLE GAS BLOWING IN WOODS NEAR HIS HOME. AT 00:31CEGT SYSTEM CONTROL NOTIFIED A CEGT WEST POINT TEAM MEMBER AND GAVE HIM THE CALLERS REPORT INFORMATION. AT 00:45 SYSTEM CONTROL NOTIFIED SOUTHERN GAS OPERATIONS (SGO - DISTRIBUTION) REGARDING THE REPORTED INFORMATION OF A POSSIBLE LEAK. AT 00:55 A CEGT CARLISLE TEAM MEMBER NOTIFIED CEGT SYSTEM CONTROL THAT HE AND A SGO TECHNICIAN WERE IN ROUTE TO THE LOCATION. AT 01:45 CEGT AND SGO PERSONNEL NOTIFIED SYSTEM CONTROL THAT THE LEAK IS ON CEGT'S LINE B AND THAT IT APPEARS THAT SOMEONE HIT A 2 INCH ABOVE GROUND LINE AND THAT GAS IS STILL BLOWING. NORTH LITTLE ROCK POLICE WERE CHASING A STOLEN VEHICLE AT HIGH SPEEDS. THE VEHICLE RAN THROUGH CEGT'S FACILITY GATE AND EXITED THE OTHER END OF FENCED IN YARD. THE CHASE ENDED ON CEGT'S LINE B ROW UPSTREAM FROM THE LINE B DELIVERY TO NORTH LITTLE ROCK FACILITY AND YARD. ONCE THE PERPETRATORS WERE APPREHENDED, THE NLR POLICE DEPARTMENT CALLED IN 3 WRECKERS TO PICKUP STOLEN VEHICLE AND 2 SEVERELY DAMAGED POLICE CARS. ONE OF THE WRECKERS GOT TANGLED IN THE DOWN FENCING AND RAN OVER OUR 2 INCH BLOW DOWN AND BROKE IT OFF AT THE TOP OF LINE B. AT 02:36 CEGT SYSTEM CONTROL WAS NOTIFIED BY THE CARLISLE TEAM THAT THE VALVES WERE CLOSED TO ISOLATE THE AFFECTED SECTION ON LINE B IN PREPARATION TO START REPAIRS. AT 02:40 CEGT SYSTEM CONTROL NOTIFIED NRC (INCIDENT #990655) OF THE ABOVE INCIDENT. AT 06:30 TECHNICIANS REPORTED TO SYSTEM CONTROL THAT THE PRESSURE IS AT ZERO, THE SEGMENT IS ISOLATED. REPAIRS ARE IN PROGRESS. AT 14:30 TECHNICIANS REPORTED TO SYSTEM CONTROL THAT THAT EVERYTHING IS BACK TO NORMAL OPERATION AND SGO HAS BEEN NOTIFIED. AT 19:30 SGO REPORTS TO SYSTEM CONTROL THAT THE LAST AFFECTED DOMESTIC CUSTOMER IS NOW BACK IN SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110377 | 15404 | 2011-10-13 12:16 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2011-09-21 00:09 | 2011 |  |  | 37.8988 | -84.0659 | 990301 | 2011-09-21 02:52 |  | NATURAL GAS |  | 50000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-09-21 01:15 | [5 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-09-21 00:09 | 2011-09-21 00:30 | ONSHORE | KY | 40391 | WINCHESTER | CLARK | MILEPOST | 3.7 | 100-2 | 105-2 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | YES | [6 empty] | YES | UNCASED | HOWARD CREEK | 1 | BELOW WATER, PIPE BURIED BELOW BOTTOM (NOT IN BORED/DRILLED CROSSING) | [11 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 26 |  | 0.281 | 52000 | API 5L OR EQUIVALENT | FLASH WELDED |  | A.O. SMITH | COAL TAR | [28 empty] | 1948 | 1948 | CARBON STEEL |  | OTHER | [8 empty] | FAILURE OF PIPE AT MECHANICAL GOUGES | CLASS 1 LOCATION | NO |  | 491 |  | NO | NO | NO |  | 1000 | 1170.06317505604 | 0 | 0 | 195500 | 132301.065719361 | 600 | 702.037905033625 | 1000 | 1170.06317505604 | 0 | 0 |  |  | 198100 | 138558.955868678 | 135343.229974506 | [8 empty] | 708 |  | 750 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 43824 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE WAS WITHIN NORMAL OPERATING LIMITS. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [64 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | [10 empty] | NO |  |  | YES | PRIVATE LANDOWNER | YES | [6 empty] | UNKNOWN/OTHER | BACKHOE/TRACKHOE | UNKNOWN/OTHER | NO |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | NO | NO |  | PREVIOUS DAMAGE | [121 empty] | YES | YES |  |  | YES |  |  | YES | 2006 | [31 empty] | 2006 | [17 empty] | CLEANING | 2006 |  |  |  | YES | YES | 1973 | 1049 | NO | [13 empty] | NO | [63 empty] | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | ken.peters@elpaso.com | 2053257554 | 2053253729 |  |  |  | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | 2053257554 | ken.peters@elpaso.com | TENNESSEE GAS PIPELINE (TGP) COMPANY'S GAS CONTROL BEGAN RECEIVING PHONE CALLS FROM LAND OWNERS ABOUT A PIPELINE RUPTURE IN THE COMMUNITY OF TRAPP NEAR CLAY CITY, KY, SHORTLY AFTER MIDNIGHT ON SEPTEMBER 21, 2011. RESPONDING TGP PERSONNEL DISCOVERED THAT A FAILURE HAD OCCURRED IN THE HOWARD CREEK CROSSING ON LINE 100-2 AT 105-2+3.70. POST INCIDENT INVESTIGATION REVEALED THAT EXCAVATION EQUIPMENT HAD BEEN USED A FEW DAYS PRIOR TO THE INCIDENT AT THE CREEK CROSSING. MARKS ON THE PIPE INDICATED STRIKES BY THE EXCAVATION EQUIPMENT, LEAVING GOUGES ON THE PIPE'S SURFACE. METALLURGICAL ANALYSIS CONFIRMED THE INITIAL FIELD CONCLUSION THAT THE FAILURE RESULTED FROM MECHANICAL DAMAGE TO THE PIPE. THE FAILED PIPELINE HAS NOT BEEN REPAIRED. SINCE IT IS NOT NEEDED FOR MAINTAINING SERVICE UNDER CURRENT LOAD DEMANDS, REPAIR IS DELAYED UNTIL OPPORTUNITY FOR FAVORABLE WEATHER.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110378 | 16301 | 2011-10-19 16:37 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2011-09-19 18:45 | 2011 |  |  | 38.1179 | -122.5671 | 990236 | 2011-09-20 11:44 |  | NATURAL GAS |  | 11 | 193 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE LEAKING PIPE WAS CAPPED, BUT A FEED SETUP FOR CUSTOMER SUPPORT | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-09-19 18:45 | 2011-09-19 18:45 | ONSHORE | CA | 94945 | NOVATO | MARIN | MILEPOST | 10.38 | L-21G | 123.5 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 240 |  | YES |  |  |  |  | YES | CASED | [16 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.281 | 42000 | X42 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | ASPHALT | [28 empty] | 1961 | 1961 | CARBON STEEL |  | LEAK |  |  | OTHER | UNKNOWN AT THIS TIME | [5 empty] | CLASS 3 LOCATION | YES | METHOD2 | 289 |  | NO | NO | NO |  | 0 | 0 | 5000 | 5850.31587528021 | 0 | 0 | 1740000 | 2035909.92459751 | 0 | 0 | 254000 | 297196.046464235 | $254,000 WAS SPENT ON THE INVESTIGATION |  | 1999000 | 1073642.65335235 | 2338956.28693703 | [8 empty] | 341 |  | 450 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 21120 | NO |  | YES | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WERE NO OPERATIONAL ISSUES ASSOCIATED WITH THIS INCIDENT - THE INCIDENT IS A RELATIVELY SMALL LEAK ON THE LINE IDENTIFIED BY A MARK AND LOCATE EMPLOYEE. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES | YES |  |  | YES | YES | 1972 | YES | YES | YES | YES |  |  | 2014 | 2010 |  |  | YES | [190 empty] | NO | [63 empty] | YES | 1972 | 1060 | Yes, and an investigative dig was cunducted at the point of the Accident | 2011 | [12 empty] | NO | [63 empty] | SONAL PATNI | SR. COMPLIANCE ENGINEER | s1pw@pge.com | 925 3285778 |  |  |  |  | LAURENCE DENISTON | INTERIM MANAGER | 925 328 5756 | lcd1@pge.com | ON THE MORNING OF SEPTEMBER, 19, 2011, PG&E PERSONNEL DISCOVERED GAS READINGS AT THE CASING VENTS FOR A 20-INCH CASING SURROUNDING 16-INCH STEEL GAS TRANSMISSION LINE L-21G UNDER REDWOOD BOULEVARD, SOUTH OF ATHERTON AVENUE IN NOVATO. PG&E CREWS EXCAVATED THE PIPE AND CASING ON BOTH SIDES OF THE ROADWAY IN AN ATTEMPT TO IDENTIFY THE LOCATION OF THE LEAK. UNFORTUNATELY, THE SOURCE OF THE LEAK WAS NOT AT EITHER SIDE OF THE ROADWAY, BUT APPEARS TO BE LOCATED SOMEWHERE UNDER THE ROADWAY. DUE TO THE LOCATION OF THE LEAK IT IS NOT FEASIBLE TO ATTEMPT TO REPAIR THE LEAK. A NEW PIPE WILL BE INSTALLED UNDER THE ROADWAY TO REPLACE THE LEAKING PIPE. MOBILIZATION TO START CONSTRUCTION IS SCHEDULED TO BEGIN OCTOBER 19 OR 20, 2011. PLANS ARE ALSO BEING DEVELOPED FOR THE REMOVAL OF THE OLD PIPE TO FACILITATE THE ROOT CAUSE ANALYSIS OF THE LEAK. PG&E WILL PROVIDE THE RESULTS OF THE ROOT CAUSE ANALYSIS TO THE CPUC UPON COMPLETION OF THE ANALYSIS. THERE WERE NO INJURIES OR FATALITIES AS A RESULT OF THIS INCIDENT. DAMAGES ARE EXPECTED TO EXCEED $50,000 FOLLOWING FURTHER EVALUATION ON SEPTEMBER 20, 2011 AFTERWHICH THE DOT WAS NOTIFIED. THIS INCIDENT INITIALLY BECAME REPORTABLE WHEN SAN FRANCISCO MAJOR MEDIA TV CHANNEL 5 WAS OBSERVED ON SCENE AT 1845 HOURS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110379 | 15775 | 2011-10-26 12:31 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION CORP | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2011-09-28 07:00 | 2011 |  |  | 42.1898 | -76.9805 | 991048 | 2011-09-28 09:48 |  | NATURAL GAS |  | 22119.6 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE COMPRESSOR STATION WAS OUT-OF-SERVICE AND IN BY-PASS MODE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-09-28 07:27 | 2011-09-28 07:27 | ONSHORE | NY | 14830 | CORNING |  |  |  | CORNING COMPRESSOR STATION | SOLENOID VALVE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [8 empty] | CARBON STEEL |  | OTHER | [8 empty] | SOLENOID VALVE FAILURE | CLASS 1 LOCATION | NO |  | 42 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 86266 | 58378.944937833 | 450 | 526.528428775219 | 0 | 0 | 0 | 0 | NONE |  | 86716 | 60765.7934617636 | 58905.4733666083 | [8 empty] | 915 |  | 938 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | YES | NO | PHMSA | [20 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | STATION WAS OUT-OF-SERVICE AT THE TIME THE INCIDENT TOOK PLACE. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | A SOLENOID VALVE NEXT TO THE HEATER DID NOT OPERATE TO SHUT THE VALVE. THE GAS WAS SHUT AFTER THE OPERATOR MANUALLY TRIPPED THE SOLENOID VALVE. | [147 empty] | GEORGE HAMATY | ENGINEER | ghamaty@nisource.com | (304) 357-3728 | (304) 357-3804 |  |  |  | PERRY MICHAEL HOFFMAN | MANAGER | (304) 357-2548 | mikehoffman@nisource.com | ON SEPTEMBER 28, 2011, THE COMPRESSOR STATION ENGINEER DISCOVERED THAT THE 2-INCH VENT PIPE WAS BLOWING NATURAL GAS WHEN HE ARRIVED AT THE SITE. HE MANUALLY TRIPPED THE SOLENOID VALVE TO SHUT-OFF THE GAS FLOWING THROUGH THE VENT PIPE. THE COMPRESSOR STATION WAS IN BY-PASS MODE AND NOT OPERATING. INVESTIGATION OF THE EVENT RESULTED IN THE IDENTIFICATION OF A 'CAUSAL FACTORS' . THE ELECTRONIC ESD SYSTEM AT CORNING CS WAS UNNECESSARILY ACTIVATED. THE FUEL GAS ESD BLOCK VALVE DID NOT CLOSE AS DESIGNED . SINCE THE FUEL GAS BLOCK VALVE FAILED TO CLOSE, GAS FROM THE PIPELINE WAS VENTED FOR AN EXTENDED DURATION OF TIME. IN LIEU OF THIS INCIDENT AND ITS INVESTIGATION, SEVERAL CORRECTIVE ACTIONS WERE IMPLEMENTED AND EXECUTED AS FOLLOWS: 1. THE ETHERNET CONNECTION BETWEEN THE REMOTE I/O PANELS AND THE GUARDLOGIC PLC SHOULD BE ELIMINATED, OR A REDUNDANT ETHERNET COMMUNICATION BETWEEN THE REMOTE I/O PANELS AND THE GUARDLOGIC PLC SHOULD BE INSTALLED. HARD-WIRING THESE DEVICES MAY PROVIDE THE HIGHEST RELIABILITY. 2. INSTALL POINT-OF-USE FILTRATION ON ALL THE ESD OPERATOR CONTROLS THAT EMPLOY VERSA VALVES. IN ADDITION, IMPLEMENT THE MANUFACTURER'S RECOMMENDATION TO AVOID THE USE OF TEFLON-TAPE ON CONTROL TUBING FOR VERSA VALVES. THE SMALL DIAMETER OF THE INTERNALLY DRILLED PASSAGES OF THESE VALVES IS PRONE TO BLOCKAGE BY DIRT AND DEBRIS. 3. INSPECT THE CORNING CS VERSA VALVES AND OTHER SIMILAR SHUTTLE VALVES FOR CONTAMINATION BY DIRT AND DEBRIS.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110380 | 16070 | 2011-10-27 15:13 | SUPPLEMENTAL FINAL | 12874 | QUESTAR PIPELINE COMPANY | 333 SOUTH STATE STREET P.O. BOX 45360 | SALT LAKE CITY | UT | 84145-0360 | 2011-09-28 09:50 | 2011 |  |  | 39.8193 | -111.4646 | 991083 | 2011-09-28 13:26 |  | NATURAL GAS |  | 2280 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELIEF VALVE LINE WAS ISOLATED AND THE VALVE WAS RESEATED MANUALLY. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-09-28 09:50 | 2011-09-28 09:50 | ONSHORE | UT | 84269 | INDIANOLA | UTAH |  |  | THISTLE CREEK COMPRESSOR STATION | DISCHARGE GAS COOLER THERMAL RELIEF | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2005 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE RELIEVED NEAR SET-POINT, BUT DID NOT RE-SEAT AFTER THE PRESSURE DROPPED | CLASS 1 LOCATION | NO |  | 20 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 8600 | 5819.89342806394 | 0 | 0 | 300 | 351.018952516813 | 0 | 0 |  |  | 8900 | 6194.87474123493 | 6170.91238058076 | [8 empty] | 1330 |  | 1436 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY BECAUSE THE PIPING SEGMENT WAS BEING OPERATED BELOW MAOP AND THE RELIEF VALVE IS NOT REMOTELY CONTROLLED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | RELIEF VALVE OPENED AND VENTED GAS, BUT DID NOT RESEAT ITSELF. | [161 empty] | CHAD WILDING | SUPERVISOR OF PIPELINE COMPLIANCE | chad.wilding@questar.com | 801-324-3814 |  |  |  |  | LARRY CONTI | VICE PRESIDENT OF ENGINEERING AND OPERATIONS | 801-324-5061 | larry.conti@questar.com | SUPPLEMENTAL BEING FILED TO CLARIFY THE CAUSE OF THE INCIDENT. DISCHARGE PRESSURES FROM THISTLE CREEK COMPRESSOR STATION WERE OPERATING NEAR THE PRE-SET RELIEF POINT OF THE THERMAL RELIEF VALVE OFF THE DISCHARGE GAS COOLERS. THE RELIEF VALVE BEGAN TO RELIEVE. THE SITUATION WAS IDENTIFIED BY AN OPERATING EMPLOYEE THE NEXT MORNING. THE RELIEF VALVE WAS ISOLATED, MANUALLY RESEATED, AND TESTED TO BE WITHIN 5% OF ITS INTENDED SET-POINT. IT WAS RESET A LITTLE HIGHER, WITHIN DOT LIMITS, AND OPERATING PRESSURES HAVE NOT BEEN NEAR THE SETPOINT SINCE THE INCIDENT OCCURED. INITIALLY, THE ESTIMATED GAS RELEASE WAS 3.79 MMSCF, BUT UPON FINALIZING THE VENTED GAS CALCULATION, IT WAS DETERMINED THAT THE TOTAL VOLUME OF RELEASED GAS WAS 2.28 MMSCF. QUESTAR PIPELINE COMPANY IS FILING THIS REPORT TO FOLLOW-UP WITH THE REPORT MADE TO THE NRC, THOUGH THE FINAL VENTED GAS VOLUME WAS DETERMINED TO BE BELOW THE REPORTING THRESHOLD FOR UNINTENTIONAL RELEASES.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110382 | 15445 | 2011-11-02 12:18 | SUPPLEMENTAL FINAL | 31286 | ONEOK GAS TRANSPORTATION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2011-10-03 09:10 | 2011 |  |  | 35.053 | -98.4446 | 991505 | 2011-10-03 12:21 |  | NATURAL GAS |  | 4106 | 7 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-10-03 10:37 | 2011-10-04 03:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-10-03 09:32 | 2011-10-03 10:35 | ONSHORE | OK | 73062 | MOUNTAIN VIEW | KIOWA |  |  | FM-196 |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 4 |  | 0.141 | 25000 | A-25 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1974 |  | CARBON STEEL |  | MECHANICAL PUNCTURE | 48 | 4 | [7 empty] | CLASS 1 LOCATION | NO |  | 136 |  | NO | NO | NO |  | 0 | 0 | 27 | 31.5917057265131 | 16424 | 11114.6429840142 | 63482 | 74277.9504789077 | 1500 | 1755.09476258406 | 0 | 0 |  |  | 81433 | 46438.7305257904 | 87179.2799312324 | [8 empty] | 160 |  | 180 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 2590 | NO | YES |  |  |  |  | YES | SMALL DIAMETER PIPE | YES |  | YES | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT CAUSED BY THIRD PARTY DAMAGE | [12 empty] | YES | 1 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | TRENCHER | TELECOMMUNICATIONS | YES | 11092909470685 | OKLAHOMA ONE-CALL SYSTEM, INC. | UTILITY OWNER | YES | NO | YES | 17 | LOCATING PRACTICES NOT SUFFICIENT |  | FACILITY MARKING OR LOCATION NOT SUFFICIENT | [264 empty] | PATTI FORD | SENIOR PIPELINE SAFETY ENGINEER | patti.ford@oneok.com | 918 588 7131 | 918 732 1311 |  |  |  | MICHEL E. NELSON | SENIOR VICE PRESIDENT | 918 588 7944 | michel.nelson@oneok.com | ONEOK GAS TRANSPORTATION PIPELINE FM-196 WAS STRUCK BY A THIRD PARTY CONTRACTOR AT APPROXIMATELY 0910 HOURS ON OCTOBER 3, 2011. THE THIRD PARTY CONTRACTOR PLOWING IN TELEPHONE LINES CONTACTED A ONEOK PIPELINE OPERATOR AFTER THEY STRUCK THE PIPELINE. THE PIPELINE HAD AN APPROXIMATELY 48 INCH BY 4 INCH GASH WHICH ALLOWED GAS TO ESCAPE THE PIPELINE CAUSING THE TOWN OF MOUNTAIN VIEW, OK TO LOSE NATURAL GAS SERVICE. OKLAHOMA NATURAL GAS WAS CONTACTED AND THEY RESPONDED APPROPRIATELY TO THE TOWN OUTAGE. THE OKLAHOMA CORPORATION COMMISSION WAS NOTIFIED OF THIS INCIDENT AT 1005 HOURS. PHMSA WAS NOTIFIED VIA THE NATIONAL RESPONSE CENTER AT 1221 HOURS. THE NRC NUMBER IS 991505. THE PIPELINE WAS REPAIRED VIA PIPE REPLACEMENT AND SERVICE WAS RESTORED AT 0345 HOURS ON OCTOBER 4, 2011.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110383 | 15824 | 2011-11-02 13:38 | SUPPLEMENTAL FINAL | 22655 | WILLISTON BASIN INTERSTATE PIPELINE CO | 1250 WEST CENTURY AVENUE | BISMARCK | ND | 58503 | 2011-10-06 00:46 | 2011 |  |  | 44.9919 | -108.8671 | 991743 | 2011-10-06 06:03 |  | NATURAL GAS |  | 3800 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE RELEASE POINT WAS ISOLATED AND SHUT IN. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-10-06 00:46 | 2011-10-06 01:34 | ONSHORE | WY | 82435-1164 | POWELL | PARK | SURVEY STATION NO. | 0+00 | ELK BASIN COMPRESSOR STATION | ELK BASIN COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1981 |  | CARBON STEEL |  | OTHER | [8 empty] | A RELIEF VALVE OPENED AS DESIGNED. AFTER THE RELIEF VALVE OPENED, A 1/4" NIPPLE SUPPLYING PILOT GAS TO THE RELIEF VALVE FAILED WHICH PREVENTED THE RELIEF VALVE FROM RESEATING. | CLASS 1 LOCATION | NO |  | 56 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 13448 | 9100.6891651865 | 2 | 2.34012635011208 | 81 | 94.7751171795394 | 0 | 0 |  |  | 13531 | 9479.67615028518 | 9197.80440871615 | [8 empty] | 719 |  | 720 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | RELIEF VALVE FAILED TO RESEAT/CLOSE AFTER PRESSURE WAS RELIEVED. | [161 empty] | KENT KAHL | ENGINEER | kent.kahl@wbienergy.com | 406-359-7222 | 406-359-7244 |  |  |  | KENT KAHL | DOT COMPLIANCE SUPERVISOR | 406-359-7222 | kent.kahl@wbienergy.com | A DOWNSTREAM STATION REGULATOR #6 (R6) WENT CLOSED DUE TO THE WARM NIGHT TEMPERATURES WHICH REQUIRED A MINIMAL AMOUNT OF GAS TO HOLD THE BILLINGS LINE. THE UPSTREAM REGULATOR #5 (R5)WAS LEAKING ENOUGH GAS TO CREATE AN EXCESS PRESSURE BUILD UP ON THE "SHUT-IN" DRY BED DEHY INLET PIPING. RELIEF VALVE #12 (RV12) OPENED AS DESIGNED AT A SCADA REPORTED PRESSURE OF 719 PSIG TO PROTECT THE MAOP (720 PSIG) OF THE DRY BED DEHY PIPING. AFTER THE RELIEF VALVE OPENED RELEASING GAS, A 1/4 INCH PIPE NIPPLE BROKE OFF ON THE RELIEF VALVE PIPING SUPPLYING PILOT GAS TO THE RELIEF VALVE. THE PIPE NIPPLE THAT FAILED SUPPLIED PILOT GAS TO THE RELIEF VALVE WHICH RESULTED IN LOST PILOT PRESSURE AND PREVENTED THE RELIEF VALVE FROM RESEATING. ONCE THE OPERATOR REACHED THE STATION, THE DEHY PRESSURE WAS VERIFIED AND THE VALVE SUPPLYING GAS TO THE RELIEF VALVE AND PILOT VALVE WAS CLOSED. THE DEHY WAS THEN SHUT IN. ACCORDING TO SCADA TRENDING, GAS VENTED FOR 1 HR AND 15 MINUTES. THE ESTIMATED VOLUME RELEASED WAS CALCULATED TO BE APPROXIMATELY 3,800 MCF WHICH EXCEEDS THE REPORTABLE INCIDENT THRESHOLD OF 3,000 MCF. THE OVERPRESSURE CONDITION RESULTED FROM A LEAKING REGULATOR, NOT BY ACTIONS OF THE GAS CONTROLLER OR STATION PERSONNEL. GAS CONTROL DOES NOT HAVE SUPERVISORY CONTROL OF ANY STATION REGULATORS AND THE STATION WAS UNATTENDED AT THE TIME OF THE INCIDENT. THE PIR CALCULATED IN THIS REPORT WAS BASED ON A 3" BLOW DOWN STACK AND 720 PSIG MAOP. APPENDED PART E5F TO TRANSMISSION SYSTEM PER DOT EMAIL REQUEST FROM BLAINE KEENER ON 3/4/13.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110384 | 15945 | 2011-11-11 15:18 | SUPPLEMENTAL FINAL | 602 | CENTERPOINT ENERGY GAS TRANSMISSION | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2011-10-23 03:14 | 2011 |  |  | 34.3195 | -93.5032 | 993339 | 2011-10-23 04:13 |  | NATURAL GAS |  | 2712 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-10-23 04:01 | 2011-10-23 04:01 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 10 | 2011-10-23 03:14 | 2011-10-23 03:14 | ONSHORE | AR | 71943 | GLENWOOD | PIKE | MILEPOST | GLENWOOD TBS | GLENWOOD TOWN BORDER STATION | MS350705 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1992 |  | CARBON STEEL |  | OTHER | [8 empty] | LIGHTENING STRIKE CAUSING FIRE. | CLASS 2 LOCATION | NO |  | 916 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 8841 | 5982.98579040853 | 172676 | 202041.828815977 | 2400 | 2808.1516201345 | 0 | 0 | N/A |  | 183917 | 100234.37939964 | 210832.96622652 | [8 empty] | 155 |  | 500 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | OTHER | DISTRIBUTION PERSONNEL |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [52 empty] | LIGHTNING |  |  | DIRECT HIT |  |  | YES |  |  |  | YES | SEVERE THUNDERSTORM | [301 empty] | JIMMY CROSS | DOT WAIVER SPECIALIST | jimmy.cross@centerpointenergy.com | 318 429-3664 | 318 429-3997 |  |  |  | JOHNNY CAVITT | MANAGER OF DOT COMPLIANCE | 318 429-3606 | johnny.cavitt@centerpointenergy.com | ON 10/23/2011 AT 01:26 CEGT SYSTEM CONTROL RECEIVED CALL FROM A DISTRIBUTION FIELD TECHNICIAN REPORTING THAT THE GLENWOOD TOWN BORDER STATION WAS ON FIRE. SYSTEM CONTROL NOTIFIED CEGT FIELD TECHNICIANS AT 01:36 AND 01:42. THEY WERE DISPATCHED TO THE LOCATION TO INVESTIGATE THE REPORTED FIRE. AT 03:14 FIELD PERSONNEL REPORTED TO SYSTEM CONTROL THAT THEY WERE ON SCENE AND THEY CONFIRMED THAT THE TOWN BORDER STATION IS ON FIRE. THEY REPORTED THAT THE RELIEF VALVE IS BLOWING, BUT NOT ON FIRE. FIELD PERSONNEL ARE WORKING ON A PLAN TO GET THE GAS SHUT OFF TO TOWN BORDER. AT 03:58 VALVES ARE SHUT OFF AND THE FIRE WAS OUT AT 4:01. THE SITUATION WAS UNDER CONTROL AND SECURED. AT 04:01 THE FACILITY WAS SHUT DOWN, BUT THE GAS SUPPLY TO CUSTOMERS WAS MAINTAINED FROM AN ALTERNATE SOURCE. NO CUSTOMERS LOST SERVICE DUE TO THE INCIDENT. FIVE HOMES (10 PEOPLE) WERE TEMPORARILY EVACUATED DURING THE INCIDENT BY THE FIRE DEPARTMENT. THE FIRE DEPARTMENT ALLOWED EVACUEES TO RETURN AS SOON AS THE FIRE WAS OUT AND ALL WERE BACK IN THEIR HOMES THE FOLLOWING MORNING. ON 11/10/2011 A TEMPORARY REGULATOR STATION WAS INSTALLED WHILE A REPLACEMENT STATION IS BEING CONSTRUCTED. ALTHOUGH THE FACILITY WAS REROUTED AND FED BY ALTERNATE SOURCES, THE CHANGE TO COLDER WEATHER BROUGHT ON THE NEED TO INSTALL THE TEMPORARY REGULATOR STATION WHILE CONSTRUCTING THE REPLACEMENT REGULATOR STATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110385 | 16036 | 2011-11-14 16:18 | SUPPLEMENTAL FINAL | 5304 | FLORIDA GAS TRANSMISSION CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2011-10-20 17:20 | 2011 |  |  | 27.9073 | -81.8584 | 993196 | 2011-10-20 19:55 |  | NATURAL GAS |  | 41 | 0 | 6 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | [7 empty] | NO |  |  |  |  | NO | [6 empty] | 9 | 2011-10-20 17:20 | 2011-10-20 17:20 | ONSHORE | FL | 33830 | BARTOW | POLK | MILEPOST | 00+48 | BARTOW MEASURING STATION | 99276 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1963 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE VENTING | CLASS 2 LOCATION | NO |  | 65 |  | NO | NO | NO |  | 242246 | 283443.123904626 | 0 | 0 | 145 | 98.1261101243339 | 0 | 0 | 4680 | 5475.89565926228 | 0 | 0 |  |  | 247071 | 132723.185431621 | 289017.145674013 | [8 empty] | 200 |  | 200 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CLEANING OPERATION WAS BEING CONDUCTED BY FIELD OPERATIONS PERSONNEL | [12 empty] | YES | 3 | 0 | YES | 3 | 0 | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [204 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | [6 empty] | YES | UNABLE TO CONFIRM LOCATION OF TRACKING PIG IN TIME TO SHUT IN INLET VALVE TO METER STATION | OTHER MAINTENANCE | NO | [150 empty] | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | IN PREPARATION OF A MAINTENANCE PROJECT TO CLEAN A SEGMENT OF THE 12' SARASOTA LATERAL, DIESEL FUEL WAS INTRODUCED INTO THE PIPELINE AT THE LAUNCHER SITE TO SERVE AS A CARRIER TO PICK UP ANY SOLIDS IN THE LINE. THE CUSTOMERS TAP LOCATED APPROXIMATELY 20 MI DOWNSTREAM OF THE LAUNCHER SITE WAS OPENED SERVING THE CUSTOMERS LOAD. THE PROJECT PLAN CALLED FOR CLOSING THE CUSTOMERS TAP VALVE BEFORE THE COLUMN OF DIESEL REACHED THE TAP THEN REOPENING THE TAP VALVE ONCE THE PIG PUSHING THE DIESEL COLUMN PAST THE CUSTOMERS TAP. ARRANGEMENTS HAD BEEN MADE TO SUPPLY THE CUSTOMERS LOAD WITH AN ALTERNATE DELIVERY (GULFSTREAM) AS A BACK UP TO FGT SO AS NOT TO IMPACT THE CUSTOMERS LOAD REQUIREMENTS DURING THE PROJECT. THE PIG WAS EQUIPPED WITH A TRANSMITTER AND TRACKED ALONG THE PIPELINE VIA ELECTRONIC TRACKING EQUIPMENT AND GEO PHONES. PERSONNEL TRACKING THE PIG WERE UNABLE TO DETECT THE PIG WHEN IT REACHED A POINT THAT WAS ESTABLISHED FOR COMMUNICATING TO PERSONNEL AT CUSTOMERS TAP VALVE TO CLOSE THE VALVE AND A PORTION OF THE DIESEL IN THE GAS STREAM ENTERED THE METER AND REGULATOR STATION THAT CAUSED THE RELIEF VALVE TO BRIEFLY ACTIVATE, VENTING DIESEL ENTRAINED GAS THROUGH THE RELIEF VALVE. THE DIESEL MIST CARRIED SOME DISTANCE AWAY AND EVENTUALLY SETTLED ON SEVERAL NEARBY PROPERTIES AND VEHICLES RESULTING IN A CLEANUP REQUIREMENT. **THIS REPORT IS BEING SUBMITTED IN RESPONSE TO PHMSA'S REQUEST, (DOCKET ID PHMSA-2013-0028), FOR SUPPLEMENTAL REPORTS FROM OPERATORS WHO SUBMITTED REPORTS FOR INCIDENTS OCCURRING AFTER JANUARY 1, 2010, WITH ANY OF THE FOLLOWING: (1) ``PIPE GIRTH WELD'' WAS SELECTED AS THE ``ITEM INVOLVED IN INCIDENT'' IN PART C3 OF THE REPORT. THE REVISED REPORT COLLECTS DATA ABOUT THE PIPE ADJACENT TO THE GIRTH WELD. (2) ``FUNCTION OF PIPELINE SYSTEM'' IS NULL IN PART E5F OF THE REPORT. THE REVISED REPORT COLLECTS THE FUNCTION OF THE PIPELINE SYSTEM FOR ALL INCIDENTS.** PART E5F OF THIS REPORT HAS BEEN COMPLETED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110386 | 16059 | 2011-11-18 11:24 | SUPPLEMENTAL FINAL | 19570 | WILLIAMS GAS PIPELINE - TRANSCO | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2011-10-30 18:55 | 2011 |  |  | 29.1451 | -90.8995 | 994031 | 2011-10-30 19:00 |  | NATURAL GAS |  | 225 | 17087 | 29.5 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-10-31 08:45 | 2011-11-08 12:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-10-31 08:00 | 2011-10-31 08:00 | ONSHORE | LA | 70353 | DULAC | TERREBONNE | MILEPOST | 31.644 | SELA-D | 22-7060 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | MARSH | 60 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 26 |  | 0.434 | 52000 | API 5L | SEAMLESS |  | REPUBLIC STEEL | OTHER | CONCRETE OVER SOMASTIC COATING | [8 empty] | PIPE GIRTH WELD | [18 empty] | 1968 | 1967 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 634 |  | NO | NO | NO |  | 20000 | 23401.2635011208 | 57300 | 67044.6199307112 | 7000 | 4737.12255772646 | 650000 | 760541.063786427 | 30000 | 35101.8952516813 | 0 | 0 |  |  | 764300 | 411649.349825041 | 890825.965027667 | [8 empty] | 805 |  | 1250 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | MANUAL | 91661 | NO |  |  |  | YES |  | YES | PIG TRAPS NOT DESIGNED FOR A PIG TOOL. | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PINHOLE LEAK NOT LARGE ENOUGH TO HAVE AN INDICATION OF PRESSURE DROP OR CHANGE IN CONDITIONS. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  | YES | [5 empty] | YES | [7 empty] | YES | GIRTH WELD 6 O'CLOCK POSITION. | YES | YES | YES | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | EDGAR RODRIGUEZ | PIPELINE SAFETY SPECIALIST | edgar.x.rodriguez@williams.com | 713-215-2846 | 713-215-2222 |  |  |  | MARIE SOTAK | MANAGER PIPELINE SAFETY | 713-215-2111 | marie.sotak@williams.com | ON THE EVENING OF OCTOBER 30TH, WILLIAMS RECEIVED A CALL FROM THE USCG STATING THAT THERE WERE BUBBLES SEEN COMING FROM COORDINATES 90 53.92N ' 29 08.750W. THE TRANSCO DISTRICT MANAGER DETERMINED THAT IT WAS SAFER TO WAIT UNTIL MORNING BEFORE SENDING A CREW OFFSHORE. AT THE TIME OF THE LEAK, TRANSCO COULD NOT VERIFY WHETHER IT WAS THEIR LINE LEAKING OR NOT. WHEN CREWS ARRIVED AT THE LEAK SITE, A DETERMINATION WAS MADE THAT IT WAS IN FACT TRANSCO'S PIPELINE. THE VALVES WERE CLOSED, THE LINE WAS BLOWN DOWN, AND A CLAMP WAS INSTALLED. THE LEAK WAS DETERMINED TO BE A PINHOLE LEAK AT THE 6 O'CLOCK POSITION ON THE GIRTH WELD. THE PIPELINE WAS RESTORED TO SERVICE ON NOVEMBER 8, 2011.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110387 | 15382 | 2011-10-03 | ORIGINAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2011-09-23 13:50 | 2011 |  |  | 45.6115 | -95.7836 | 990624 | 2011-09-23 15:48 |  | NATURAL GAS |  | 1700 | 40 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-09-23 15:00 | 2011-09-24 12:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-09-23 13:56 | 2011-09-23 15:55 | ONSHORE | MN | 56323 | CYRUS | STEVENS | MILEPOST | M.P. 37.03 | MORRIS BRANCH LINE | 6-INCH MNB 65101 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6.625 |  | 0.156 | 42000 | 5LX | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | REPUBLIC | EXTRUDED POLYEHYLENE | [28 empty] | 1967 |  | CARBON STEEL |  | MECHANICAL PUNCTURE | 15 | 6 | [7 empty] | CLASS 1 LOCATION | NO |  | 129 |  | NO | NO | NO |  | 0 | 0 | 150 | 175.509476258406 | 6392 | 4325.66962699822 | 10172 | 11901.8826166701 | 14371 | 16814.9778887304 | 48650 | 56923.5734664764 | COST OF LOCAL DISTRIBUTIONS LABOR FOR RE-LIGHTING OF CUSTOMERS |  | 79735 | 43876.4005708668 | 90141.6130751335 | [8 empty] | 528 |  | 975 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 152856 | NO | [5 empty] | YES | PIPELINE DOES NOT CONTAIN HCA'S THEREFORE HAS NOT YET BEEN ASSESSED FOR COMPATABILITY OF IN-LINE INSPECTION. | YES |  |  |  |  | YES | PIPELINE DOES NOT CONTAIN HCA'S THEREFOR | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE WAS STRUCK BY OUTSIDE 3RD PARTY CONTRACTOR, WHICH CONTROL ROOM PERSONNEL DID NOT HAVE ANY KNOWLEDGE OF OR CONTROL OVER. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | TRENCHER | DRAINAGE | NO |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | YES | 20 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | BYRON WOOD | SR. PIPELINE SAFETY SPECIALIST | byron.wood@nngco.com | 402-398-7396 | 402-398-7606 |  |  |  | THOMAS CORRELL | DIRECTOR OF PIPELINE SAFETY AND INTEGRITY | 402-398-7715 | thomas.correll@nngcom.com | ON SEPTEMBER 23, 2011, AT APPROXIMATELY 1:50 P.M., MECHANIZED FARM TILING EQUIPMENT, OWNED AND OPERATED BY LEROY EDLUND, STRUCK THE MORRIS, MINNESOTA SIX-INCH DIAMETER BRANCH LINE (MNB65101) NEAR MILEPOST 37.03 LOCATED IN THE NORTHWEST 1/4 OF THE NORTHEAST 1/4 OF SECTION 26, T125N, R41W IN STEVENS COUNTY, MINNESOTA. LEROY EDLUND OWNS THE TILING OPERATION AND OPERATES IT UNDER THE NAME LEROY EDLUND CONSTRUCTION. EDLUND WAS INSTALLING FARM DRAINAGE TILE UTILIZING A FARM TILING IMPLEMENT ATTACHED TO A 9380 CASE IH TRACTOR. THE BLADE PLOWED A DEPTH OF APPROXIMATELY THREE FEET DEEP. EDLUND WAS ASSISTED BY DAN THOMPSON, WHO WAS OPERATING A FARM TRACTOR STRINGING TILE IN FRONT OF THE 9380 CASE IH TRACTOR OPERATED BY EDLUND. THE PIPELINE PRESSURE AT THE TIME OF THE INCIDENT WAS 528 PSIG. THE FARM TILING IMPLEMENT STRUCK AND SEVERED THE PIPELINE AT A DEPTH OF THREE-FEET. THE ESCAPING GAS DID NOT IGNITE. EDLUND AND THOMPSON VACATED THE EQUIPMENT AND RAN OUT OF THE FIELD. EDLUND CONTRACTED NORTHERN'S OPERATION COMMUNICATION CENTER (OCC) AT 1:56 P.M. INDICATING THAT HE HAD STRUCK A PIPELINE WHILE WORKING IN THE FARM FIELD. THE MORRIS BRANCH LINE CONSISTS OF 42.23 MILES OF PIPELINE CONSISTING OF 16.45 MILES OF EIGHT-INCH X 0.188 WALL THICKNESS PIPE AND 25.78 MILES OF SIX-INCH X 0.156 WALL THICKNESS PIPE. THE PIPE THAT WAS HIT WAS SIX-INCH X 0.156 WALL THICKNESS, GRADE X-42. THE PIPE WAS COATED WITH X-TRUCOAT COATING. THE PIPELINE WAS INSTALLED IN 1967 AND HAS AN MAOP OF 975 PSIG. THERE WAS A LOSS OF SERVICE TO THE THREE COMMUNITIES OF MORRIS, BENSON AND HANCOCK, MINNESOTA. RESIDENTS AND BUSINESSES IN THESE COMMUNITIES WERE TEMPORARILY OUT OF NATURAL GAS SERVICE FROM APPROXIMATELY 3:30 P.M. ON SEPTEMBER 23, 2011, TO APPROXIMATELY 12:00 P.M. ON SEPTEMBER 24, 2011. CENTER POINT ENERGY, THE LOCAL DISTRIBUTION COMPANY, UTILIZED THEIR ODORIZED NATURAL GAS TRUCK AT THE HOSPITAL IN MORRIS, MINNESOTA TO MAINTAIN SERVICE TO THEIR SANITIZING SYSTEM. CENTER POINT ENERGY HAD TO RE-LIGHT APPROXIMATELY 3,600 CUSTOMERS THAT LOST GAS SERVICE TO THE INCIDENT. REPAIRS WERE MADE BY REPLACING THE DAMAGE PIPE WITH 13-FEET AND SIX-INCHES OF SIX-INCH DIAMETER, 0.280-INCH WALL THICKNESS, X-42 PIPE COATED PIPE. THE JOINT OF PIPE WAS BACK BEVELED TO 0.219-INCH FOR TRANSITION. MIDWEST X-RAY CHECK THE PIPE FOR UT AND MAG PARTICLE FOR CRACKING AND IT CHECKED OUT OK WITH A WALL THICKNESS OF 0.155 TO 0.156 RECORDED ON THE PIPE. THE PIPE WELDS WERE X-RAY INSPECTED AND THE PIPE WAS BACKFILLED WITH SOIL PRIOR TO COMMENCING PURGING AND RE-PRESSURIZATION FOR RETURNING TO SERVICE. THERE WERE NO INJURIES, NO EXPLOSION, NO FIRE AND NO EVACUATION OF PERSONNEL. WHEN ASKED ABOUT WHETHER HE HAD MADE A ONE-CALL PRIOR TO EXCAVATION, MR. EDLUND ACKNOWLEDGED THAT HE HAD NOT MADE A ONE-CALL AND ADMITTED THAT HE KNEW A ONE-CALL WAS REQUIRED PRIOR TO INITIATING EXCAVATION ACTIVITIES. THE SECTION OF DAMAGED PIPE IS BEING EXAMINED BY AN OUTSIDE SERVICES METALLURGICAL COMPANY. FILING OF AN INCIDENT REPORT WAS REQUIRED AS IT IS EXPECTED THAT THE TOTAL COST OF THE INCIDENT WILL EXCEED THE $50,000 REPORTING THRESHOLD. IN ADDITION, THE LOSS OF SERVICE TO COMMUNITIES IS CONSIDERED AS A SIGNIFICANT EVENT BY NORTHERN. A SUPPLEMENTAL REPORT WILL BE FILED WHEN ALL FINAL COST OF REPAIRS AND THE METALLURGICAL REPORT FINDINGS ARE AVAILABLE. SUPPLEMENT/FINAL REPORT - TOTAL COST OF REPAIRS HAS BEEN UPDATED TO THE FINAL CALCULATED COSTS
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110388 | 15792 | 2011-12-01 16:11 | SUPPLEMENTAL FINAL | 26330 | ENOGEX LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2011-11-04 11:55 | 2011 |  |  | 34.7953 | -97.7997 | 994587 | 2011-11-04 15:25 |  | NATURAL GAS |  | 7464 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | FACILITY WAS NOT OPERATING AT TIME OF INCIDENT. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-11-04 11:55 | 2011-11-04 13:30 | ONSHORE | OK | 73082 | RUSH SPRINGS | GRADY | MILEPOST |  | COMANCHE TIE COMPRESSOR STATION |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | COMPRESSOR UNIT SUCTION BYPASS VALVE |  |  | CARBON STEEL |  | OTHER | [8 empty] | LOAD VALVE INADVERTENTLY LEFT OPEN FOLLOWING UNIT STARTUP. | CLASS 1 LOCATION | NO |  | 57 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 26806 | 18140.4724689165 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 26806 | 18807.0515097691 | 18140.4724689165 | [8 empty] | 687 |  | 1200 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | SCADA BASED EVENT NOTIFIED CONTROLLER OF STATION ESD. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA BASED EVENT NOTIFIED CONTROLLER OF STATION ESD AND CONTROLLER RESPONDED CORRECTLY. CONTROLLER HAD NO WAY OF KNOWING THAT COMPRESSOR TECHNICIAN LEFT COMPRESSOR UNIT BYPASS VALVE OPEN AND THAT GAS WAS ESCAPING FROM THE ESD VENT VALVE. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | COMPRESSOR TECHNICIAN LEFT COMPRESSOR UNIT LOAD VALVE OPEN FOLLOWING ROUTINE STARTUP OF UNIT. | YES |  |  |  |  | NORMAL OPERATING CONDITIONS | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | MIKE REED | MANAGER EHS ASSESSMENT AND COMPLIANCE | reedmd@oge.com | 405 558-4685 | 405 557-8618 |  |  |  | PAUL M BREWER | VP OPERATIONS | 405 525-7788 | brewerpm@oge.com | ON NOVEMBER 4, 2011 AT 11:55 AM THE COMANCHE TIE COMPRESSOR STATION WAS AUTOMATICALLY SHUTDOWN PER A ESD. THE ESD SYSTEM AUTOMATICALLY BLOCKED IN THE STATION AND VENTED ALL GAS TO A SAFE LOCATION; HOWEVER, A 2 INCH BYPASS VALVE AROUND THE COMPRESSOR SUCTION VALVE WAS INADVERTENTLY LEFT OPEN FOLLOWING ROUTINE STARTUP BY A COMPRESSOR TECHNICIAN. THIS ALLOWED GAS TO FLOW AROUND THE CLOSED SUCTION AND ESCAPE TO ATMOSPHERE THROUGH THE ESD VENT VALVE UNTIL ENOGEX PERSONNEL RESPONDING TO THE STATION DOWN ALARM BY GAS CONTROL IDENTIFIED THE SOURCE OF GAS AND PROPERLY ISOLATED. UPDATE MARCH 5, 2013: COMPLETED SECTION E.5.F.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110389 | 16877 | 2011-12-02 15:00 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION CORP | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2011-11-03 00:45 | 2011 |  |  | 39.7257 | -78.4217 | 994393 | 2011-11-03 02:45 |  | NATURAL GAS |  | 15000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-11-03 05:00 | 2012-01-01 08:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2011-11-03 00:45 | 2011-11-03 00:45 | ONSHORE | PA | 17211 | ARTEMAS | BEDFORD | SURVEY STATION NO. | C58 | ARTEMAS COMPRESSOR STATION | C-58 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 2 |  | 0.218 | 35000 | API 5L | SEAMLESS |  | UNKNOWN | NONE | [28 empty] | 2003 | 1999 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 4 | 2 |  | CLASS 1 LOCATION | NO |  | 75 |  | YES | NO | NO |  | 5000 | 5850.31587528021 | 0 | 0 | 53400 | 36137.4777975133 | 23300000 | 27262471.9788058 | 1000 | 1170.06317505604 | 0 | 0 |  |  | 23359400 | 12554881.9119097 | 27305629.8356536 | [8 empty] | 1942 |  | 2400 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE UNINTENDED GAS RELEASE APPEARS TO HAVE INITIATED AT THE TWO INCH LIQUID DUMP PIPING AT THE BOTTOM OF THE SUMP TANK BELOW THE FILTER SEPARATOR. THIS AREA WAS NOT EQUIPPED WITH AN RTU, SO IT COULD NOT BE SEEN BY THE CONTROLLER. | [12 empty] | YES | 1 | 0 | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | GENERAL CORROSION | [5 empty] | YES | THE METALLURGICAL ANALYSIS COIULD NOT DETERMINE THE EXACT CORROSION MECHANISM AT THE 2-INCH PIPE. |  | YES |  |  | YES | [5 empty] | YES | NO | YES | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | GEORGE HAMATY | ENGINEER | ghamaty@cpg.com | (304) 357-3728 |  |  |  |  | PERRY MICHAEL HOFFMAN | MANAGER SYSTEM INTEGRITY | (304) 357-2548 | mikehoffman@cpg.com | AT APPROXIMATELY 12:30 AM ON THURSDAY, NOVEMBER 3, 2011, A NEIGHBOR OF THE ARTEMAS COMPRESSOR STATION CALLED THE LOCAL COLUMBIA GAS TRANSMISSION MAINTENANCE MECHANIC TO REPORT AN INCIDENT AND FIRE AT THE STATION. THAT EMPLOYEE CONTACTED A SECOND COMPANY EMPLOYEE FOR ASSISTANCE AT THE STATION. THE NGT&S MONITORING CENTER WAS ALSO CONTACTED TO INFORM THEM OF THE POSSIBLE INCIDENT. UPON CONFIRMING THE FIRE AND INITIATING AN ESD OF THE STATION, THE AREA WAS SECURED. COMPANY PERSONNEL WORKED WITH THE LOCAL FIRE DEPARTMENT TO ENSURE THE SAFETY OF THE PUBLIC AND THE AREA. IT WAS FOUND THAT THE DUMP VALVE FOR THE ARTEMAS B FIELD SLUG CATCHER HAD FAILED IN THE OPEN POSITION. UPON CLOSING THIS VALVE, THE FIRE WAS FULLY EXTINGUISHED. THE RESULTS OF THE ANALYSIS BY A THIRD PARTY EXPERT IN METALLURGY AND FAILURE ANALYSIS INDICATED THAT THE RUPTURE WAS LIKELY DUE TO WATER FREEZING IN THE DRAIN LINE. THE FROZEN LIQUID CAUSED THE PIPING TO EXPAND, PRODUCING DUCTILE TEARING AT INTERNAL CORROSION FEATURES. THE RESULTANT FLAW SIZE WAS CRITICAL FOR THE MATERIAL PROPERTIES, DIMENSIONS, AND OPERATING PRESSURE OF THE PIPING. FREEZING OCCURRED SOMETIME PRIOR TO THE FAILURE. THE PRESENCE OF THE INTERNAL CORROSION WAS A CONTRIBUTING FACTOR TO THE FAILURE. THE COMPANY HAS DEVELOPED AN INTEGRITY PLAN COVERING PRESSURIZED LIQUID/DUMP PIPING FROM VESSELS AT ITS ACTIVE COMPRESSOR STATIONS. THE PLAN SUMMARIZES IMMEDIATE INITIAL STEPS AS WELL AS LONG TERM STEPS THAT WILL BE TAKEN TO ADDRESS DUMP/DRAIN VALVE PIPING COMPANY-WIDE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110390 | 16529 | 2011-12-07 11:40 | SUPPLEMENTAL | 2364 | DUKE ENERGY OHIO | 139 EAST FOURTH STREET PO BOX 960 - ROOM 460-ANNEX | CINCINNATI | OH | 45202 | 2011-11-11 08:48 | 2011 |  |  | 39.1204 | -84.4514 | 995229 | 2011-11-11 10:13 |  | NATURAL GAS |  | 11917 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-11-11 12:01 | 2011-11-11 19:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 1 | 2011-11-11 08:48 | 2011-11-11 08:48 | ONSHORE | OH | 45226 | 2817 RIVERSIDE DR., CINCINNATI (EAST END) | HAMILTON | SURVEY STATION NO. | 274+18 | LINE "D" | 3000 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 48 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.25 | 35000 | ASTM A-139 | SPIRAL WELDED |  | ARMCO | COAL TAR | [28 empty] | 1948 | 1948 | CARBON STEEL |  | MECHANICAL PUNCTURE | 5 | 6.5 | [7 empty] | CLASS 3 LOCATION | YES | METHOD2 | 196 |  | NO | YES | NO |  | 10000 | 11700.6317505604 | 0 | 0 | 62304 | 42163.0976909414 | 24341 | 28480.5077440391 | 0 | 0 | 0 | 0 |  |  | 96645 | 62156.6011495884 | 82344.2371855409 | [8 empty] | 191 |  | 200 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 9470 | NO |  | YES |  |  |  | YES | PHYSICAL COMPONENTS NOT AVAILABLE FOR PIG LAUNCHING OR RECEIVING | YES |  |  |  |  | YES | LOSS OF CUSTOMERS AND SEE "5D OTHER" | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS INCIDENT WAS CAUSED BY AN EXCAVATOR HITTING AN EXISTING PIPELINE ON COMPANY PROPERTY - GAS CONTROL ROOM OPERATORS WERE ON DUTY IN THE GAS CONTROL ROOM AND MONITORED THE ENTIRE INCIDENT WHEN IT OCCURED AND WERE IN CONSTANT CONTACT WITH ON-SITE FIELD SUPERVISORS AND CREWS - CONTROL ROOM OPERATORS FOLLOWED APPROPRIATE PROCEDURES AND SAFETY MEASURES - MONITORED GAS FLOW AND TOOK NECESSARY ACTION TO ENSURE GAS LOAD AND FLOW WAS SUFFICIENT TO MEET CUSTOMER NEEDS | [12 empty] | YES | 1 | 0 | YES | 2 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [10 empty] | YES |  |  |  |  | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 112502625 | OHIO UTILITY PROTECTION SERVICE (OUPS) | CONTRACT LOCATOR | YES | YES | YES | 9 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO MAINTAIN CLEARANCE | [263 empty] | JAMES T CALLAHAN | LEAD REGULATORY COMPLIANCE SPECIALIST - GAS OPS | jim.callahan@duke-energy.com | 513-287-2824 | 513-651-5229 |  |  |  | JAMES E MEHRING | VP GAS OPERATIONS | 513-287-2535 | jim.mehring@duke-energy.com | ON FRIDAY, NOVEMBER 11, 2011 AT 8:48 A.M. A CONTRACTOR WORKING AT OUR GAS PLANT, HIT TRANSMISSION LINE "D" WITH A 5' BUCKET FROM A BACKHOE. THE LINE WAS LOCATED PROPERLY. THERE WERE NO INJURIES. WE WERE ABLE TO ISOLATE THE DAMAGE BY SHUTTING DOWN TWO VALVES. WE REPLACED A SIX FOOT SECTION OF THE 20" STEEL COATED MAIN WITH PRETESTED PIPE. THREE SERVICES WERE TURNED OFF UNTIL REPAIRS COULD BE MADE. GAS WAS RESTORED AT 8:00 P.M.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110391 | 16028 | 2011-12-08 20:21 | SUPPLEMENTAL FINAL | 19610 | TRANSWESTERN PIPELINE COMPANY LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2011-11-10 15:43 | 2011 |  |  | 35.2802 | -112.7376 | 995198 | 2011-11-10 16:56 |  | NATURAL GAS |  | 1 | 80700 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-11-10 16:32 | 2011-11-12 18:23 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-11-10 15:43 | 2011-11-10 15:43 | ONSHORE | AZ | 86337 | SELIGMAN | YAVAPAI | MILEPOST | MP 52.31 | TW 30 INCH MAINLINE BETWEEN STATION 1 AND STATION2 | AZMM121 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 40 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 |  | 0.375 | 60000 | API 5LX | DSAW |  | KAISER STEEL | COAL TAR | [28 empty] | 1960 | 1959 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 657 |  | NO | NO | NO |  | 0 | 0 | 305046 | 356923.091298145 | 1 | 0.676731793960924 | 15800 | 18486.9981658855 | 150 | 175.509476258406 | 0 | 0 |  |  | 320997 | 172404.402026539 | 375586.275672083 | [8 empty] | 636 |  | 1008 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 85302 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A PINHOLE LEAK WAS DISCOVERED DURING EXCAVATION TO REPAIR AN ANAMOLY. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1960 | YES | YES | YES |  |  |  | 2011 |  |  |  | YES | [190 empty] | YES | YES |  |  | YES |  |  |  | 2011 | [31 empty] | 2011 | [23 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | ON NOVEMBER 10, 2011 VERIFICATION DIGS WERE CONDUCTED ON TRANSWESTERN'S (LINE NUMBER AZMM121) 30' PIPELINE AS A RESULT OF AN ILI RUN THAT WAS PERFORMED MAY 12, 2011. THE PIPELINE PRESSURE WAS LOWERED TO 80% OF THE OPERATING PRESSURE PER TRANSWESTERN'S SOP I.11 AND A 40' JOINT OF PIPE WAS EXPOSED IN THE LOCATION SHOWN ON THE ILI DIG SHEET. THE COATING WAS REMOVED FROM THE PIPE AND CORROSION WAS FOUND IN THE LOCATION AS IDENTIFIED ON THE ILI REPORT. THE SURFACE OF THE PIPE WAS SANDBLASTED TO REMOVE THE REMAINING COATING AND THE CORROSION TECHNICIAN BEGAN INSPECTING THE CORRODED AREA TO VERIFY THE ACCURACY OF THE ILI REPORT. THE DEEPEST PIT FOUND IN AN AREA OF GENERAL CORROSION (7.6' LONG X 10.5' WIDE) MEASURED 48% DEEP WITH A LENGTH AND WIDTH OF 0.625'. AFTER ALL THE CORROSION MEASUREMENTS WERE COMPLETED WET MAGNETIC PARTICLE INSPECTION WAS CONDUCTED TO LOOK FOR ANY SIGNS OF SCC CRACKS, THERE WERE NO VISIBLE SIGNS OF SCC. ONCE THE WET MAGNETIC PARTICLE TESTING WAS COMPLETED THE PIPE SURFACE WAS RE-BLASTED TO REMOVE THE WET MAGNETIC PARTICLE MEDIUM AND WHITE CONTRAST PAINT OFF THE PIPE. ONCE THE SANDBLASTING WAS COMPLETED THE CORROSION TECHNICIAN WENT BACK DOWN INTO THE DITCH TO INSPECT THE SURFACE OF THE PIPE FOR COATING REPAIR. WHILE IN THE DITCH THE TECHNICIAN HEARD A LEAK AND IMMEDIATELY NOTIFIED GAS CONTROL AND OPERATIONS MANAGEMENT OF A LEAK (15.43). THE PIPELINE WAS IMMEDIATELY ISOLATED (APPROXIMATELY 16.2 MILES OF PIPELINE) FROM MAINLINE VALVES 2010 AND 2011. AT 16.32 OPERATIONS BEGAN BLOWING DOWN THE PIPELINE. BLOW DOWN WAS COMPLETED AT 21.07 WITH LESS THAN 5PSI LINE PRESSURE IN THE PIPELINE. THE BELL HOLE WAS CHECKED FOR GAS WITH A GAS DETECTOR AND NO GAS WAS DETECTED IN THE DITCH. A FULL ENCIRCLEMENT PRESSURE CONTAINING SLEEVE WAS INSTALLED OVER THE PINHOLE LEAK AND THE PIPELINE WAS RETURNED TO SERVICE ON NOVEMBER 12 AT 18.23 GE PII (MANUFACTURE AND OPERATOR OF THE ILI TOOL) DID A DETAILED ANALYSIS OF THE REPORTED 48% WALL LOSS PIT THAT LEAKED AND CONCLUDED THAT THE DIMENSIONS OF THE PIT WERE BEYOND THE CAPABILITIES OF THE MAGNETIC TOOL TO PROPERLY SIZE THE PINHOLE LEAK. **THIS REPORT IS BEING SUBMITTED IN RESPONSE TO PHMSA'S REQUEST, (DOCKET ID PHMSA-2013-0028), FOR SUPPLEMENTAL REPORTS FROM OPERATORS WHO SUBMITTED REPORTS FOR INCIDENTS OCCURRING AFTER JANUARY 1, 2010, WITH ANY OF THE FOLLOWING: (1) ``PIPE GIRTH WELD'' WAS SELECTED AS THE ``ITEM INVOLVED IN INCIDENT'' IN PART C3 OF THE REPORT. THE REVISED REPORT COLLECTS DATA ABOUT THE PIPE ADJACENT TO THE GIRTH WELD. (2) ``FUNCTION OF PIPELINE SYSTEM'' IS NULL IN PART E5F OF THE REPORT. THE REVISED REPORT COLLECTS THE FUNCTION OF THE PIPELINE SYSTEM FOR ALL INCIDENTS.** THIS SUPPLEMENTAL REPORT IS TO ACKNOWLEDGE THAT THE TWO RELEVANT SECTIONS IN PHMSA'S REQUEST HAVE BEEN REVIEWED AND NO FURTHER ACTIONS WERE NEEDED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110392 | 15574 | 2011-12-12 16:21 | SUPPLEMENTAL FINAL | 19570 | WILLIAMS GAS PIPELINE - TRANSCO | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2011-12-03 15:07 | 2011 |  |  | 32.2578 | -87.8536 | 997113 |  |  | NATURAL GAS |  | 61700 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-12-03 15:45 |  | YES |  |  |  | YES |  |  |  |  | YES | [6 empty] | 0 | 2011-12-03 15:08 | 2011-12-03 15:25 | ONSHORE | AL | 36782 | SWEETWATER | MARENGO | MILEPOST | 817.77 |  |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 36 |  | 0.344 | 60000 | API 5L | DSAW |  | NATIONAL TUBE | ASPHALT | [28 empty] | 1964 | 1964 | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | 47 FT 3 IN LONG SECTION OF PIPELINE BLOWN OUT |  |  |  | CLASS 1 LOCATION | NO |  | 703 |  | NO | NO | NO |  | 200000 | 234012.635011208 | 0 | 0 | 82770 | 56013.0905861457 | 6961000 | 8144809.76156511 | 10000 | 11700.6317505604 | 405000 | 473875.585897697 | WGP COSTS INCLUDING EMERGENCY RESPONSE, REMEDIAL ACTIONS, ETC. |  | 7658770 | 4127064.18171959 | 8920411.70481072 | [8 empty] | 783 |  | 800 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 801150 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  | YES | FATIGUE WAS NOT A FACTOR AS ALARMS WERE RESPONDED TO IMMEDIATELY BY CONTROLLERS. | YES | YES | [7 empty] | YES | 3 | 0 | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [8 empty] | YES |  | YES | METALLURGICAL ANALYSIS | YES | YES | 1964 | NO | YES |  | YES |  |  |  | 2004 |  |  | YES | [190 empty] | YES | YES |  |  | YES |  |  |  | 2011 | [31 empty] | 2011 | [23 empty] | YES | 1980 | 1070 | NO | [13 empty] | NO | [63 empty] | MARIE G. SOTAK | MANAGER PIPELINE SAFETY - EAST | marie.sotak@williams.com | 713-215-2111 | 713-215-2222 |  |  |  | JOSIAH R. NEAVE | DIRECTOR PIPELINE INEGRITY- SAFETY -GIS | 713-215-4811 | joe.r.neave@williams.com | ON SATURDAY, DECEMBER 3, 2011, TRANSCO EXPERIENCED A RUPTURE ON ITS 36 INCH MAINLINE C APPROXIMATELY 7 MILES DOWNSTREAM OF STATION 90 NEAR LINDEN, AL. THE RUPTURE DID IGNITE, HOWEVER THERE WERE NO INJURIES. THERE WAS APPROXIMATELY 8 ACRES OF FORESTED AREA BURNED. OPERATIONS PERSONNEL RESPONDED AND HAD THE SEGMENT ISOLATED WITHIN 45 MINUTES OF THE RUPTURE. MAINLINE B WAS PARTIALLY EXPOSED BY THE RUPTURE AND WAS TAKEN OUT OF SERVICE AND PHMSA ORDERED THAT THE ADJACENT MAINLINES (MAINLINES A, D, AND E) BE OPERATED WITH A 20% REDUCTION IN PRESSURE. A SUBSEQUENT CONFERENCE CALL WITH PHMSA ON MONDAY, DECEMBER 5TH, 2011, RESULTED IN PHMSA ALLOWING WGP TO OPERATE MAINLINES 30 INCH A, 36 INCH D, AND 42 INCH E WITHOUT ANY PRESSURE LIMITATIONS. A ROOT CAUSE ANALYSIS WAS COMPLETED AND APPROVED BY PHMSA. THE CAUSE OF THE ACCIDENT WAS DUE TO EXTERNAL CORROSION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110393 | 17180 | 2011-12-12 16:36 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2011-11-16 08:41 | 2011 |  |  | 39.4661 | -82.0235 | 995666 | 2011-11-16 10:19 |  | NATURAL GAS |  | 79000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-11-16 09:55 | 2014-06-06 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 6 | 2011-11-16 08:48 | 2011-11-16 09:50 | ONSHORE | OH | 45732 | Not Within a Municipality | MORGAN (HOMER TOWNSHIP) | MILEPOST | 205-4 + 11.28 | 200-4 LINE | 205-4 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 36 |  | 0.344 | 60000 | API 5L OR EQUIVALENT | DSAW |  | NATIONAL TUBE | COAL TAR | [28 empty] | 1963 | 1963 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 113 | 120 |  | CLASS 1 LOCATION | NO |  | 698 |  | NO | YES | NO |  | 1200000 | 1404075.81006725 | 0 | 0 | 255170 | 172681.651865009 | 400000 | 468025.270022417 | 28600 | 33463.8068066028 | 0 | 0 |  |  | 1883770 | 1053731.47432113 | 2078246.53876128 | [8 empty] | 761 |  | 790 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | AUTOMATIC | 82261 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURES DID NOT EXCEED NORMAL OPERATING LIMITS AND BASED ON INVESTIGATION TO DATE, THERE IS NO REASON TO BELIEVE THE ACTIONS FO THE CONTROLLERS PLAYED ANY ROLE IN THE FAILURE. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [52 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | LANDSLIDE |  |  |  |  | NO | [306 empty] | MERLIN MOSEMAN | ENGINEER - PIPELINE | merlin_moseman@kindermorgan.com | 7134204614 | 7134207464 |  |  |  | MERLIN MOSEMAN | ENGINEER - PIPELINE | 7134204614 | merlin_moseman@kindermorgan.com | TENNESSEE GAS PIPELINE (TGP) WAS NOTIFIED BY A LOCAL RESIDENT OF A RUPTURE AND A FIRE ON ITS 200-4 PIPELINE IN MORGAN COUNTY, OHIO, NOVEMBER 16, 2011. TGP PERSONNEL RESPONDED AND ISOLATED THE VALVE SECTION. THERE WERE NO FATALITIES NOR INJURIES REQUIRING HOSPITALIZATION. INVESTIGATION INTO THE CAUSE OF THE RUPTURE RESULTED IN THE CONCLUSION THAT THE FAILURE WAS DUE TO EXCESSIVE STRAIN FROM THE ONGOING PROGRESSION OF AN EARTH LANDSLIDE ON ONE OF THE PIPELINE'S GIRTH WELDS AND SUBSEQUENT FAILURE OF THE WELD. A CRACK IN THE GIRTH WELD ACTED AS A STRESS CONCENTRATOR AND THE DISPLACEMENT (STRAIN) OF THE PIPELINE OCCURRED THROUGH THE LANDSLIDE. EVEN IN THE ABSENCE OF A CRACK IN THE GIRTH WELD, THE LANDSLIDE LIKELY COULD HAVE RESULTED IN A PIPELINE FAILURE AT A LATER TIME IF THE LANDSLIDE REMAINED UNDETECTED AND UNMITIGATED. PART A - PIPELINE RESTART DATE ADDED. PART C - THERE WAS COMPLETE SEPARATION OF THE PIPELINE. PART B - REVISED PIPELINE STATIONING FOR INCIDENT LOCATION (MHM). PART B - RE-ENTERED ENTIRE PART B INFORMATION DELETED BY PHMSA (MHM)
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110394 | 16069 | 2011-12-13 11:35 | SUPPLEMENTAL FINAL | 12874 | QUESTAR PIPELINE COMPANY | 333 SOUTH STATE STREET P.O. BOX 45360 | SALT LAKE CITY | UT | 84145-0360 | 2011-11-13 17:00 | 2011 |  |  | 39.8193 | -111.4646 | 995469 | 2011-11-14 11:54 |  | NATURAL GAS |  | 0 | 2690 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELIEF VALVE LINE WAS ISOLATED AND THE VALVE WAS RESEATED MANUALLY. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-11-14 10:00 | 2011-11-14 10:00 | ONSHORE | UT | 84269 | INDIANOLA | UTAH |  |  | THISTLE CREEK COMPRESSOR STATION | DISCHARGE GAS COOLER THERMAL RELIEF | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2005 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE RELIEVED NEAR SET-POINT, BUT DID NOT RESEAT ITSELF. | CLASS 1 LOCATION | NO |  | 20 |  | NO | NO | NO |  | 0 | 0 | 9700 | 11349.6127980436 | 0 | 0 | 0 | 0 | 300 | 351.018952516813 | 0 | 0 |  |  | 10000 | 5370.89871611983 | 11700.6317505604 | [8 empty] | 1312 |  | 1436 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | BECAUSE THE PIPING SEGMENT WAS BEING OPERATED BELOW MAOP AND THE RELIEF VALVE IS NOT REMOTELY CONTROLLED | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | RELIEF VALVE OPENED AND VENTED GAS, BUT DID NOT RESEAT ITSELF. | [161 empty] | CHAD WILDING | SUPERVISOR OF PIPELINE COMPLIANCE | chad.wilding@questar.com | 801-324-3814 |  |  |  |  | LARRY CONTI | VICE PRESIDENT OF ENGINEERING AND OPERATIONS | 801-324-5061 | larry.conti@questar.com | SUPPLEMENTAL BEING FILED TO CORRECT THE CAUSE OF THE INCIDENT. DISCHARGE PRESSURES FROM THISTLE CREEK COMPRESSOR STATION WERE OPERATING NEAR THE RELIEF POINT OF THE THERMAL RELIEF VALVE FROM THE DISCHARGE GAS COOLERS. THE RELIEF VALVE OPENED AND BEGAN TO RELIEVE, BUT DID NOT RESEAT. THE SITUATION WAS IDENTIFIED BY AN OPERATING EMPLOYEE NEXT MORNING. THE RELIEF VALVE WAS ISOLATED, MANUALLY RESEATED, AND TESTED TO BE WITHIN 5% OF ITS SETPOINT. INITIALLY, A REPORT WAS MADE TO THE NRC BECAUSE IT WAS THOUGHT THAT THIS EVENT WAS AN UNINTENTIONAL RELEASE OF GAS NEAR THE 3 MMSCF REPORTING THRESHOLD. THE ACTUAL VENTED GAS WAS APPROXIMATELY 2.69 MMSCF, WHICH IS BELOW THE REPORTING THRESHOLD; HOWEVER, QUESTAR PIPELINE COMPANY IS FILING THIS REPORT TO FOLLOW-UP WITH THE REPORT MADE TO THE NRC. QUESTAR PIPELINE ENGINEERING SERVICES COMPLETED AN ANALYSIS OF THE THERMAL RELIEF LINE AND CONCLUDED THAT IT IS NOT NEEDED, BECAUSE THE DISCHARGE GAS COOLER WILL NOT BE BLOCKED FROM THE MAIN STATION DISCHARGE RELIEF VALVE DURING AND ESD OR UNIT ISOLOATION. CONSEQUENTLY, THE ISOLATION VALVE TO THE THERMAL RELIEF VALVE OF THE GAS COOLER HAS BEEN LOCKED CLOSED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110395 | 16072 | 2011-12-13 11:36 | SUPPLEMENTAL FINAL | 12874 | QUESTAR PIPELINE COMPANY | 333 SOUTH STATE STREET P.O. BOX 45360 | SALT LAKE CITY | UT | 84145-0360 | 2011-11-18 17:00 | 2011 |  |  | 41.5349 | -109.719 | 996000 | 2011-11-19 11:20 |  | NATURAL GAS |  | 0 | 6800 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELIEF VALVE VENTED TO SAFE LOCATION, ISOLATED LINE AND REPAIRED REGULATOR | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-11-19 08:00 | 2011-11-19 08:00 | ONSHORE | WY | 82935 | NEAR GREEN RIVER | SWEETWATER | MILEPOST | MP 95.97 | DISTRICT REGULATING STATION #SC0019 TAP | MAINLINES 1 & 13 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1983 |  | CARBON STEEL |  | OTHER | [8 empty] | REGULATOR FROZE-OFF AND CAUSED THE STATION PRESSURE TO RISE TO THE RELIEF VALVE SET-POINT, THUS ACTIVATING THE RELIEF VALVE AS INTENDED. THE RELIEF VALVE OPERATED AS DESIGNED AND RELIEVED TO PREVENT OVER-PRESSURIZATION ON THE DOWNSTREAM PIPING. | CLASS 1 LOCATION | NO |  | 40 |  | NO | NO | NO |  | 0 | 0 | 25000 | 29251.579376401 | 0 | 0 | 0 | 0 | 300 | 351.018952516813 | 0 | 0 |  |  | 25300 | 13588.3737517832 | 29602.5983289179 | [8 empty] | 220 |  | 860 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [25 empty] | YES | REGULATOR FROZE AND ALLOWED PRESSURE TO RISE UNTIL RELIEF VALVE ACTIVATED. | [161 empty] | CHAD WILDING | SUPERVISOR OF PIPELINE COMPLIANCE | chad.wilding@questar.com | 801-324-3814 |  |  |  |  | LARRY CONTI | VICE PRESIDENT OF ENGINEERING AND OPERATIONS | 801-324-5061 | larry.conti@questar.com | SUPPLEMENTAL BEING FILED TO CLARIFY THE INCIDENT CAUSE. REGULATOR FROZE-OFF AND CAUSED THE STATION PRESSURE TO RISE TO THE RELIEF VALVE SET-POINT, THUS ACTIVATING THE RELIEF VALVE AS INTENDED. THE RELIEF VALVE OPERATED AS DESIGNED AND RELIEVED TO PREVENT OVER-PRESSURIZATION ON THE DOWNSTREAM PIPING.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20110396 | 15546 | 2011-12-15 15:03 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2011-11-21 20:14 | 2011 |  |  | 34.3178 | -90.0488 | 996191 | 2011-11-21 22:00 |  | NATURAL GAS |  | 83487 |  | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-11-21 21:30 | 2012-04-20 18:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 71 | 2011-11-21 20:30 | 2011-11-21 20:45 | ONSHORE | MS | 38606 | BATESVILLE | PANOLA | MILEPOST | 2.391 | 100-1 | 63-1D | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 120 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | REPAIR SLEEVE OR CLAMP | [38 empty] | 1944 |  | CARBON STEEL |  | LEAK |  |  | OTHER | FROM UNDER A WELD SLEEVE. | [5 empty] | CLASS 1 LOCATION | NO |  | 454 |  | NO | NO | NO |  | 1000 | 1170.06317505604 | 0 | 0 | 273698 | 185220.138543517 | 450000 | 526528.428775219 | 10000 | 11700.6317505604 | 0 | 0 |  |  | 734698 | 439624.558699447 | 724619.262244352 | [8 empty] | 748 |  | 750 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | MANUAL | 48365 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE AT THE TIME OF THE INCIDENT NOR PRIOR TO THE INCIDENT WAS NOT BEYOND NORMAL OPERATING LIMITS. | [12 empty] | YES | 4 | 0 | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [103 empty] | OTHER OUTSIDE FORCE DAMAGE | [9 empty] | AN EXISTING SAG CONDITION IN THE PIPELINE UNDER AN UNUSUALLY LARGE DEPTH OF SOIL THAT IMPOSED A HIGH LOAD STRESS ON THE SAG CONDITION, THE PIPELINE BEING UNABLE TO WITHSTAND SAID LOAD. | [251 empty] | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | ken.peters@elpaso.com | 2053257554 | 2053253729 |  |  |  | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | 2053257554 | ken.peters@elpaso.com | TENNESSEE GAS PIPELINE (TGP) OPERATIONS AND GAS CONTROL PERSONNEL NOTICED A PRESSURE DROP NEAR BATESVILLE COMPRESSOR STATION (STATION 63) NEAR BATESVILLE, MS, ON NOVEMBER 21, 2011. SHORTLY THEREAFTER, TGP WAS NOTIFIED BY A MEMBER OF THE GENERAL PUBLIC ABOUT A LEAK JUST DOWNSTREAM OF THE COMPRESSOR STATION. THE GAS IGNITED AND ALTHOUGH SEVERAL HOMES WERE EVACUATED, NO DAMAGE WAS INCURRED BY THE STRUCTURES. THE LEAK WAS ISOLATED, THE FIRE EXTINGUISHED, WITH NO INJURIES OR FATALITIES. A ROOT CAUSE ANALYSIS WAS PERFORMED WITH THE RESULTS NOW ADDED TO THIS REPORT IN PART G.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110397 | 15789 | 2011-12-19 11:10 | SUPPLEMENTAL FINAL | 26330 | ENOGEX LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2011-11-19 01:40 | 2011 |  |  | 36.4292 | -95.701 | 995985 | 2011-11-19 10:13 |  | NATURAL GAS |  | 12690 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | GAS DELIVERY TO POWER PLANT WAS NOT INTERRUPTED. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-11-19 01:45 | 2011-11-19 03:00 | ONSHORE | OK | 74053 | OOLAHGA | ROGERS | MILEPOST |  | NEPS GAS YARD |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ABOVEGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | OTHER | [37 empty] | GAS RELEASE THROUGH PSV |  |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENDED GAS RELEASE | CLASS 1 LOCATION | NO |  | 408 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 44399 | 30046.214920071 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 44399 | 31150.2753108348 | 30046.214920071 | [8 empty] | 605 |  | 605 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | NOTIFICATION FROM NEPS CONTROL ROOM OPERATOR |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | WHILE THE FACILITY IS MONITORED BY A CONTROLLER, THE ACTIVATION AND SUBSEQUENT RELESE OF GAS THROUGH A PSV IS NOT DETECTABLE BY THE SCADA SYSTEM; THEREFORE, THE CONTROLLER HAD NO WAY OF KNOWING GAS WAS BEING RELEASED THROUGH THE PSV. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | PV-6, A RECYCLE VALVE INSIDE THE CLAREMORE COMPRESSOR STATION, WAS PROGRAMMED TO OPEN WHEN 750 PSIG IS DETECTED ON L-4B AND ROUTE GAS FROM THE DISCHARGE TO SUCTION SIDE OF THE CLAREMORE COMPRESSOR STATION. | [147 empty] | MIKE REED | MANAGER EHS ASSESSMENT AND COMPLIANCE | reedmd@oge.com | 405 558-4685 | 405 557-8618 |  |  |  | PAUL M BREWER | VP OPERATIONS | 405 525-7788 | brewerpm@oge.com | PRIOR TO THE INCIDENT ON 11/19/2011 A SEGMENT OF L-4 BETWEEN N/E/ TAP AND KEETONVILLE YARD HAD BEEN REMOVED FROM SERVICE FOR ILI REMEDIATION AND REPAIRS. THIS OUTAGE REQUIRED GAS TO BE RE-ROUTED FROM NEPS AT OOLAHGA, OK DOWN L-4 TO THE L-4 TO L-4A JUNCTION AT KEETONVILLE, OK TO CONTINUE THE SUPPLY OF GAS THROUGH L-4A & L-4B TO CUSTOMERS CONNECTED TO L-4C INSIDE THE PRYOR INDUSTRIAL PARK. ON 11/18/2011, THE CLAREMORE COMPRESSOR STATION WAS REMOVED FROM SERVICE FOR MAINTENANCE OF MEASUREMENT EQUIPMENT. THIS OUTAGE ELIMINATED THE USE OF L-4A AND L-4B TO SUPPLY GAS TO L-4C; THEREBY REQUIRING THE USE OF AN ALTERNATE VALVE INSIDE THE AECI GAS YARD AT CHOTEAU, OK TO ROUTE GAS FROM L-281 INTO L-4E TO SUPPLY GAS TO CUSTOMERS CONNECTED TO L-4C INSIDE THE PRYOR INDUSTRIAL PARK. THE FLOW OF GAS FROM L-281 INTO L-4E TO SUPPLY GAS TO L-4C HAD NOT BEEN ATTEMPTED PRIOR TO THIS DATE. DUE TO THE GAS LOAD AT THE TWO POWER PLANTS AT AECI AND THE DEMAND REQUIRED BY CUSTOMERS IN THE PRYOR INDUSTRIAL PARK, IT WAS DETERMINED THAT PCV-281 IN THE AECI GAS YARD COULD NOT SUPPLY THE AMOUNT OF GAS NECESSARY. XV-102, A 16' VALVE WAS OPENED BY GAS CONTROL TO BYPASS GAS FLOW AROUND PCV-281 AND SUPPLEMENT THE FLOW THROUGH PCV-281. AT AN UNKNOWN TIME ON THE EVENING OF 11/18/2011, THE AECI POWER PLANT REDUCED THE DEMAND LOAD INTO THE POWER PLANTS. GAS FLOW THEN TOOK THE PATH OF LEAST RESISTANCE, WHICH WAS INTO L-4E AND L-4C. GAS FLOW CONTINUED TO FLOW BACKWARD INTO L-4B TOWARD THE CLAREMORE COMPRESSOR STATION. PC-6, A RECYCLE/SURGE CONTROL VALVE INSIDE THE CLAREMORE STATION, DETECTED THE INCREASING PRESSURE IN L-4B AND OPENED AT A SETPOINT OF 750 PSIG, THEREBY ROUTING GAS AROUND THE CLAREMORE STATION INTO L-4A. THE COMPRESSOR STATION WAS NOT NEEDED AND THEREFORE NOT OPERATING AT THIS TIME. THIS GAS FLOW CONTINUED TO FLOW INTO L-4, THUS STEADILY INCREASING THE PRESSURE IN L-4 UNTIL THE SETPOINT ON AVAILABLE OVERPRESSURE WAS SATISFIED AND THE PSV AT THE NEPS GAS YARD ACTIVATED. THE NEPS CONTROL ROOM OPERATOR INITIALLY NOTIFIED AN ONG REPRESENTATIVE TO RESPOND TO GAS VENTING IN THE GAS YARD. UPON ARRIVAL, THE ONG INDICATED TO THE NEPS CONTROL ROOM THAT THE GAS RELEASE WAS FROM A ENOGEX PSV. THE NEPS CONTROL ROOM OPERATOR THEN IMMEDIATELY NOTIFIED ENOGEX GAS CONTROL AT 1:40 AM. THE ENOGEX ON-CALL PERSONNEL ARRIVED AT NEPS AT 3:00 AM AND IMMEDIATELY CONFIRMED WITH GAS CONTROL THAT THE L-4 OPERATING PRESSURE WAS 369 PSIG OR 236 PSIG BELOW THE MAOP OF 605. THE PSV WAS THEN ISOLATED TO END THE RELEASE OF GAS AND GAS CONTROL WAS INSTRUCTED TO CLOSE XV-102 IN THE AECI GAS YARD AT CHOTEAU. THE ENOGEX ON-CALL PERSONNEL THEN DROVE TO THE CLAREMORE COMPRESSOR STATION TO ISOLATE PV-6 TO STOP THE FLOW OF GAS INTO L-4A. THE ENOGEX ON-CALL PERSONNEL THEN RETURNED TO NEPS TO PLACE THE PSV BACK INTO SERVICE. AN INSPECTION OF THE PSV AT NEPS GAS YARD REVEALED MINOR SCARRING OF THE SEAT MATERIAL THAT PREVENTED THE PSV FROM AUTOMATICALLY RESEATING ONCE THE L-4 PRESSURE FELL BELOW THE PSV SETPOINT OF 605. AN INVESTIGATION OF THIS INCIDENT REVEALED THAT PV-6 LOCATED IN THE CLAREMORE COMPRESSOR STATION WAS PROGRAMMED TO OPEN WHEN THE COMPRESSOR DISCHARGE PRESSURE IS EQUAL TO OR GREATER THAN 750 PSIG. IT WAS ALSO DETERMINED THAT THE PV-6 SURGE VALVE IS NOT NEEDED WHEN THE COMPRESSORS ARE NOT RUNNING. A CHANGE IN THE CONTROL LOGIC PROGRAM AT THE CLAREMORE COMPRESSOR STATION IS SCHEDULED FOR DECEMBER 22, 2011 TO INTERLOCK THE OPERATION OF PV-6 WHEN THE COMPRESSORS ARE NOT RUNNING OR DURING AN ESD CONDITION. THIS WILL PREVENT PV-6 FROM ROUTING GAS FROM L-4B INTO L-4A AND INTO L-4. UPDATE MARCH 5, 2013: COMPLETED SECTION E.5.F.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110398 | 16073 | 2011-12-26 15:43 | SUPPLEMENTAL FINAL | 12874 | QUESTAR PIPELINE COMPANY | 333 SOUTH STATE STREET P.O. BOX 45360 | SALT LAKE CITY | UT | 84145-0360 | 2011-11-27 13:10 | 2011 |  |  | 41.4917 | -110.2754 | 996959 | 2011-12-01 16:54 |  | NATURAL GAS |  | 5400 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | SENSING LINE TUBING WAS ISOLATED AND REPAIRED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-11-30 16:10 | 2011-11-30 16:10 | ONSHORE | WY | 82937 | NEAR LYMAN | UINTA | MILEPOST | MP 3.9 | TL90 INTERCONNECT WITH ML116 | OVERTHRUST | YES | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | TUBING | [38 empty] | 2002 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL TUBING | OTHER | [8 empty] | TUBING BROKE OFF FROM NEEDLE VALVE ON A SENSING LINE FOR A PRESSURE TRANSDUCER | CLASS 1 LOCATION | NO |  | 7 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 19500 | 13196.269982238 | 500 | 585.031587528021 | 300 | 351.018952516813 | 0 | 0 |  |  | 20300 | 14110.8441885862 | 14132.3205222828 | [8 empty] | 945 |  | 1305 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EVENT WAS NOT SIGNIFICANT ENOUGH TO CAUSE AN ALARM | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | SENSING LINE TUBING BROKE DOWNSTREAM OF ITS CONNECTING NEEDLE VALVE. THE CAUSE OF THE BREAK WAS DUE TO PROLONGED VIBRATION FROM NORMAL OPERATION AND THE TUBING BEING INADEQUATELY SECURED OR SUPPORTED TO THE LARGER. PIPING. | [5 empty] | YES | [172 empty] | CHAD WILDING | SUPERVISOR OF PIPELINE COMPLIANCE | chad.wilding@questar.com | 801-324-3814 |  |  |  |  | LARRY CONTI | VICE PRESIDENT OF ENGINEERING AND OPERATIONS | 801-324-5061 | larry.conti@questar.com | SUPPLEMENTAL BEING FILED TO CLARIFY THE CAUSE OF THE INCIDENT. TUBING FOR A SENSING LINE TO A PRESSURE TRANSDUCER WAS INADEQUATELY SECURED DURING INITIAL INSTALLATION AND BROKE FREE FROM ITS CONNECTION POINT BECAUSE OF PROLONGED VIBRATION FROM NORMAL OPERATION. LOCAL OPERATOR RESPONDED AND ISOLATED THE SENSING LINE VALVES. THE OPERATOR REPAIRED THE TUBING AND REPORTED THE EVENT TO QUESTAR PIPELINE COMPANY'S GAS CONTROL. AFTER GAS LOSS CALCULATIONS WERE MADE IT WAS DETERMINED THAT THIS EVENT MET THE CRITERIA OF AN UNINTENTIONAL RELEASE OF GAS IN EXCESS OF 3 MMSCF AND THE EVENT WAS REPORTED TO THE NRC.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20110399 | 15422 | 2011-12-28 05:21 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2011-12-14 09:02 | 2011 |  |  | 40.8438 | -73.8669 | 998195 | 2011-12-15 11:34 |  | NATURAL GAS |  | 364 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-12-15 11:07 | 2011-12-17 01:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-12-14 09:02 | 2011-12-14 09:17 | ONSHORE | NY | 10462-3520 | NEW YORK | BRONX |  |  |  |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 68 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | COMPRESSION COUPLING | 1948 |  | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 4 LOCATION | YES | METHOD1 | 259 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 1095 | 741.021314387211 | 33369 | 39043.8380884451 | 5749 | 6726.69319339719 | 1200 | 1404.07581006725 | MATERIALS |  | 41413 | 22422.6398877017 | 47915.6284062967 | [8 empty] | 221 |  | 245 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | REMOTELY CONTROLLED |  | NO | [5 empty] | YES | DRIP POTS | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS DETECTED BY COMPANY EMPLOYEE ON LOCATION. NO CONTROL ROOM FUNCTION IS RELATED TO LEAK DETECTION AS IT APPLIES TO THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | MECHANICAL COUPLING | [19 empty] | YES | COMPRESSION COUPLING LEAK | [161 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPT. MANAGER--GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | dadariov@coned.com | ON DECEMBER 14, 2011 A CON EDISON PUBLIC IMPROVEMENT INSPECTION SUPERVISOR ON LOCATION FOR AN UNRELATED SEWER PROJECT WAS APPROACHED BY A CUSTOMER FROM 1710 VICTOR ST., BRONX, N.Y. REPORTING A GAS ODOR OUTSIDE. THE GAS EMERGENCY RESPONSE CENTER (GERC) WAS CONTACTED AND GAS DISTRIBUTION SERVICES (GDS) WAS DISPATCHED. UPON INVESTIGATING, GDS REPORTED A 20% GAS-IN-AIR READING 32' WEST OF THE BUILDING ALONG THE CURBLINE AND 60% GAS-IN-AIR READING IN A STREET PATCH IN CLOSE PROXIMITY. THE LEAK WAS CLASSIFIED A TYPE 1 DUE TO A 24" 1948 245 PSI TRANSMISSION MAIN ON THE STREET APPROXIMATELY 2' AWAY FROM A 6" LOW PRESSURE CAST IRON DISTRIBUTION MAIN. GAS CONSTRUCTION RESPONDED AND PERFORMED AN INVESTIGATION. AT 18:48 HRS., CONSTRUCTION SUPERVISION REPORTED TO THE GERC A PROBABLE TRANSMISSION MAIN LEAK WAS SUSPECTED OVER A 24" COUPLING WITH A 57% READING OVER SAME. AN OPERATIONAL PLAN WAS INITIATED AND ALL OPERATING AREAS, TRANSMISSION ENGINEERING, PRESSURE CONTROL, GAS CONTROL, LEAK SURVEY, GERC AND SENIOR MANAGEMENT PARTICIPATED. A PLAN TO ISOLATE THE SECTION OF TRANSMISSION AND REDUCE PRESSURE TO APPROXIMATELY 60 PSI WAS IDENTIFIED AND ONCE REDUCED, EXCAVATION OVER THE SUSPECTED LEAKING COUPLING WOULD BEGIN. CONSTRUCTION, GDS AND PRESSURE CONTROL CREWS PROCEEDED WITH THE TRANSMISSION MAIN ISOLATION AND PRESSURE REDUCTION. OPERATIONS CONTINUED AROUND-THE-CLOCK UNTIL THE 24" TRANSMISSION MAIN WAS EXPOSED AND A VISIBLE LEAK ON A 24" COUPLING WAS DETECTED. A WELDED REPAIR SLEEVE WAS INSTALLED TO SECURE THE LEAK. A SECOND WELDED REPAIR SLEEVE WAS INSTALLED ON THE COUPLING NORTH OF THE LEAK AS A PRECAUTION. ALL WELDS WERE X-RAYED AND APPROVED. ON SATURDAY DECEMBER 17, 2011 AT 01:30 HRS. PRESSURE RESTORATION BEGAN AND AT 05:00 HRS. NORMAL SYSTEM CONDITIONS RESUMED. THERE WERE NO EVACUATIONS OR INJURIES. THE NYS PSC, US DOT AND NYC DEP WERE NOTIFIED. THIS WAS A SERIOUS LEVEL INCIDENT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120002 | 15886 | 2012-01-03 10:05 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2011-12-07 09:26 | 2011 |  |  | 38.3884 | -96.2077 | 997467 | 2011-12-07 17:25 |  | NATURAL GAS |  | 1340 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | SETTING WAS HAND REGULATED WHILE REPAIRS WERE MADE TO THE REGULATOR AND RV . | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 25 | 2011-12-07 09:34 | 2011-12-07 09:47 | ONSHORE | KS | 66801 | EMPORIA | LYONS | SURVEY STATION NO. | 140/46278.7 | EMPORIA TOWN BORDER | Q-024 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1987 |  | CARBON STEEL |  | OTHER | [8 empty] | A MALFUNCTION OF THE REGULATION WHICH CASUSED THE PRESSURE OF THE PIPELINE TO RISE ABOVE THE MAXIMUM ALLOWABLE OPERATING PRESSURE. | CLASS 1 LOCATION | NO |  | 180 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 4806 | 3252.3730017762 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 4806 | 3371.88277087034 | 3252.3730017762 | [8 empty] | 420 |  | 300 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS CONTROL ONLY MONITORED PRESSURE AND FLOW AT THAT POINT AND DID NOT HAVE CONTROL CAPABILITIES. THE ALARM WAS ACTED UPON IN A TIMELY MANNER WITH FIELD PERSONNEL BEING IMMEDIATELY NOTIFIED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES |  |  | YES | [25 empty] | YES | LIQUIDS IN GAS STREAM | [161 empty] | DAVID COOMES | COMPLIANCE ANALYST | david.coomes@sscgp.com | 12708524391 |  |  |  |  | DAVID SINCLAIR | MGR. PIPELINE COMPLIANCE | 270-852-4424 | david.l.sinclair@sscgp.com | AT 09:26 AM THE GAS CONTROL ROOM RECEIVED A HIHI ALARM. A GAS CONTROLLER NOTIFIED A SOUTHERN STAR MEASUREMENT TECHNICIAN TO INVESTIGATE THE ISSUE AT 09:34 AM. AT 09:37 THE TECHNICIAN WAS CALLED AGAIN TO BE TOLD THAT THE EMERGENCY RESPONDERS WERE ON SITE AND RELIEF VALVE WAS BLOWING ON THE REGULATOR SETTING. SOUTHERN STAR'S TECHNICIAN TOOK 10 MINUTES TO ARRIVE AT THE SITE AND THE REGULATOR WAS SHUT IN WITHIN 30 MINUTES OF THE NOTIFICATION OF AN ISSUE. DURING THIS INCIDENT THE EMPORIA FIRE AND POLICE DEPARTMENT ALONG WITH THE SHERIFF'S DEPARTMENT HAD THE SOUTH PRAIRE ROAD BLOCKED FROM SOUTH AVENUE AND HAD EVACUATED APPROXIMATELY 25 RESIDENTS FROM THE AREA. THE INCIDENT WAS A RESULT OF THE REGULATOR NOT HOLDING AND THE RELIEF VALVE NOT FUNCTIONING AS DESIGNED. THE HIGH PRESSURE CAUSED THE RELIEF VALVE TO BLOW GAS FOR APPROXIMATELY 25 MINUTES. THE REGULATORS AND RELIEF VALVES WERE REBUILT AND FOUND TO CONTAIN OIL WHICH CAME FROM THE LINE. THE DOWNSTREAM LINES WERE WALKED WITH INSTRUMENTATION TO VERIFY THE LINES CONTAINED THE OVERPRESSURIZATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120003 | 16068 | 2012-01-03 16:32 | SUPPLEMENTAL FINAL | 12874 | QUESTAR PIPELINE COMPANY | 333 SOUTH STATE STREET P.O. BOX 45360 | SALT LAKE CITY | UT | 84145-0360 | 2011-12-04 08:40 | 2011 |  |  | 41.3283 | -110.6137 | 997138 | 2011-12-04 10:00 |  | NATURAL GAS |  | 2000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-12-04 09:10 | 2012-05-31 08:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2011-12-04 08:40 | 2011-12-04 09:10 | ONSHORE | WY | 82930 | NEAR EVANSTON, WY | UINTA |  |  | LEROY STORAGE FIELD | LEROY STORAGE WELL NO. 11 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | DEHYDRATOR/DRIER/TREATER/SCRUBBER | [38 empty] | 2010 |  | CARBON STEEL |  | OTHER | [8 empty] | TUBING TO A GLYCOL PUMP BROKE AT THREADED CONNECTION TO THE PUMP. AS A RESULT, GLYCOL AND NATURAL GAS LEAKED FROM THE TUBING AND IGNITED. | CLASS 1 LOCATION | NO |  | 8 |  | YES | NO | NO |  | 0 | 0 | 0 | 0 | 6240 | 4222.80639431616 | 134000 | 156788.46545751 | 2000 | 2340.12635011208 | 0 | 0 |  |  | 142240 | 77422.1976724446 | 163351.398201938 | [8 empty] | 1485 |  | 1800 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO ALARM EXISTED TO PROVIDE INDICATION TO THE CONTROLLER THAT A TUBING BREAK HAD OCCURRED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | 1/4" TUBING LINE BROKE AT GLYCOL PUMP RELEASING GLYCOL AND NATURAL GAS IN A DEHYDRATOR BUILDING AND A FIRE RESULTED. | [15 empty] | YES | 1/4" TUBING LINE BROKE | [161 empty] | CHAD WILDING | SUPERVISOR OF PIPELINE COMPLIANCE | chad.wilding@questar.com | 801-324-3814 |  |  |  |  | LARRY CONTI | VICE PRESIDENT OF ENGINEERING AND OPERATIONS | 801-324-5061 | larry.conti@questar.com | THIS SUPPLEMENTAL REPORT IS BEING FILED TO DOCUMENT THE OPERATOR'S ESTIMATED COST OF PROPERTY LOSS AND REPAIR AND TO SUBMIT THE FINAL VERSION OF THIS REPORT AND COMPLETE PART E5F. THE LEROY STORAGE FIELD WAS ON STAND-BY FOR WITHDRAWAL. SEVERAL DEHY UNITS, INCLUDING THE UNIT ON WELL 11 WERE IDLING. THE WELL WAS OPEN, THE GLYCOL REBOILER WAS OPERATING AT 375 DEGREES, AND ONE OF THE TWO GLYCOL PUMPS WAS CIRCULATING GLYCOL THROUGH THE UNIT. STORAGE FIELD OPERATING PRESSURE WAS 1485 PSIG. SOMETIME PRIOR TO THE FIRE, A 1/4 INCH DIAMETER TUBING LINE ON THE BOTTOM OF A GLYCOL PUMP BROKE RELEASING A GLYCOL AND GAS MIXTURE INSIDE THE DEHY UNIT BUILDING. AT SOME POINT, THE GLYCOL AND GAS WERE IGNITED AND THE RESULTING FIRE DAMAGED THE DEHY UNIT. THE UINTA COUNTY (WYOMING) FIRE DEPARTMENT MONITORED THE FIRE, QUESTAR PIPELINE COMPANY OPERATING PERSONNEL ARRIVED ON SCENE AT 09:10 AM. AT 09:30 AM THE FIRE DEPARTMENT PERSONNEL ASSISTED COMPANY OPERATORS IN CLOSING THE WELLHEAD WING VALVE, MASTER VALVE, AND TWO VALVES NEAR THE DEHY, THE INJECTION BLOCK VALVE AND WITHDRAWAL BLOCK VALVE. THE VALVE ON THE PLANT END OF THE LEROY #11 STORAGE LATERAL WAS ALREADY CLOSED (NO VOLUME SET POINT). CLOSING THESE VALVES ISOLATED PRESSURE IN THE DEHY UNIT AND PRODUCTION LINE. THE BROKEN TUBING LINE INSIDE THE DEHY UNIT CONTINUED TO VENT GAS, AND THE FIRE CONTINUED TO BURN. A 1/2 INCH VENT VALVE ON THE PRODUCTION LINE, NEAR THE WELLHEAD ESD VALVE WAS USED TO VENT PRESSURE TO ATMOSPHERE, AND HELP LOWER THE PRESSURE ON THE DEHY PIPING. THE CONTROL VALVE ON THE WELL #11 LATERAL AT THE LEROY PLANT WAS LOCKED OUT AND TAGGED OUT, AND THE LATERAL WAS DEPRESSURED TO 140 PSIG USING A BLOWDOWN VENT IN THE PLANT. AT APPROXIMATELY 10:00 AM, AS THE PRESSURE ON THE ISOLATED DEHY UNIT NEARED ZERO, THE FIRE SUBSIDED AND THE FIRE DEPARTMENT SPRAYED WATER AND FOAM ON AND IN THE DEHY UNIT, TO EXTINGUISH THE FIRE AND COOL THE PIPING AND VESSELS. THE VALVES WERE CONFIRMED CLOSED, THE UNIT TOTALLY DEPRESSURED AND MOSTLY COOLED, THE FIRE DEPARTMENT DEMOBILIZED AT 11:15 AM. THE DEHY FACILITY WAS REPAIRED AND PLACED INTO SERVICE ON MAY 31, 2012.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120004 | 17622 | 2012-01-07 19:47 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION CORP | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2011-12-08 04:45 | 2011 |  |  | 38.8777 | -81.6909 | 997496 | 2011-12-08 08:35 |  | NATURAL GAS |  | 16424 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RIPLEY COMPRESSOR STATION WAS SHUT DOWN | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-12-08 04:54 | 2011-12-08 05:37 | ONSHORE | WV | 25271 | RIPLEY | JACKSON | MILEPOST | COMPRESSOR ST | RIPLEY COMPRESSOR STATION | RIPLEY | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | MECHANICAL FAILURE | CLASS 1 LOCATION | NO |  | 227 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 56006 | 37901.0408525755 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 56006 | 39293.730017762 | 37901.0408525755 | [8 empty] | 732 |  | 1700 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | OTHER | COINCIDING REPORTING BY BOTH GAS CONTROLLER AND 911 DISPATCHER |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ALL SYSTEMS IN THE CONTROL ROOM WERE FUNCTIONING NORMALLY. ALARM WAS SET OFF; ACTION WAS TAKEN BY THE CONTROLLER AS PER TRAINING. MONITORING CENTER WAS NOTIFIED AND A CONFIRMATION WAS GIVEN TO THE MONITORING CENTER (AT THE SAME TIME) BY THE JACKSON COUNTY 911 DISPATCHER ABOUT THE INCIDENT CONFIRMING THE CONTROLLER'S IDENTIFICATION TO THIS PRESSURE DROP. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | ESD PILOT AIR POPPET VALVE, WHICH TRIGGERS THE ESD BLOWDOWN VALVE (8"), SOMETIMES REFERRED TO A "SHUTTLE VALVE" FAILED AFTER IT WAS STUCK IN THE OPEN POSITION. | [22 empty] | YES | PROBABLE MOISTURENESS IN SHUTTLE VALVE | [161 empty] | CHRIS LEGG | REGIONAL REGULATORY COMPLIANCE SPECIALIST | chris_legg@transcanada.com | 304-722-8530 |  |  |  |  | HOWARD LEE ROMACK | MANAGER US REGULATORY COMPLIANCE | 832-320-5315 | lee_romack@transcanada.com | A SHUTTLE VALVE HAD FAILED CAUSING AN UNINTENDED RELEASE OF NATURAL GAS TO VENT INTO ATMOSPHERE VIA AN 8-IN BLOW-OUT PIPE. THE COMPRESSOR STATION WAS SHUT DOWN TO STOP THE FLOW OF NATURAL GAS INTO ATMOSPHERE AND TO SECURE THE SITE FOR FURTHER INVESTIGATIONS. AN INVESTIGATIVE TEAM WAS LAUNCHED TO LOOK INTO THE PROBABLE CAUSE OF THIS INCIDENT. THE MANUFACTURER IS ASSISTING THE COMPANY ENGINEERING TEAM IN LOOKING INTO THE ROOT CAUSE OF THIS SHUTTLE VALVE FAILURE. ADDITIONAL INFORMATION WILL BE SUBMITTED IN THE FINAL INCIDENT REPORT. SUPPLEMENT/FINAL REPORT (SUBMITTED ON 02/28/2018 BY CHRIS LEGG) AN ONSITE INVESTIGATION WAS CONDUCTED ON 12/08/2011 FOLLOWING THE INCIDENT. THE ESD PILOT AIR POPPET VALVE, WHICH TRIGGERS THE ESD BLOWDOWN VALVE (8"), SOMETIMES REFERRED TO A "SHUTTLE VALVE", FAILED AFTER IT WAS STUCK IN THE OPEN POSITION. ED CLARKSON, WV PSC WAS ON-SITE DURING THE INVESTIGATION. DURING THE INVESTIGATION, SEVERAL SMALL LEAKS WERE LOCATED AROUND TUBING FITTINGS IN THE PILOT AIRLINE. POSSIBLE THAT PILOT LINE VENTED BETWEEN A FREEZE POINT AND THE TUBING LEAKS, WHICH THEN ALLOWED THE ACTUATOR TO GO OPEN. THE PILOT AIRLINE WAS DISASSEMBLED, BUT NO OBVIOUS SIGNS OF A FREEZE OR OTHER BLOCKAGE WAS SEEN. THE OTHER POSSIBILITY WAS THAT LIQUIDS IN THE POWER GAS FROZE INSIDE THE POPPET VALVE ASSEMBLY AND FORCED THE POPPET VALVE OPEN, WHICH THEN CAUSED THE ACTUATOR TO GO OPEN. AS A RESPONSE TO THE FAILURE, THE ESD PILOT AIR POPPET VALVE ON THE ACTUATOR WAS REBUILT AND FURTHER INSPECTED ON 12/13/2011 (MAXIMO WORK ORDER#: B2568587). AS A PREVENTATIVE MEASURE, ALL OF THE OTHER ESD PILOT AIR POPPET VALVES AT THE STATION WERE ALSO LATER REBUILD.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120005 | 15651 | 2012-01-09 10:50 | SUPPLEMENTAL FINAL | 2564 | COLORADO INTERSTATE GAS CO | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2011-12-10 18:40 | 2011 |  |  | 41.468 | -111.4928 | 997776 | 2011-12-10 20:38 |  | NATURAL GAS |  | 1000 | 181 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-12-10 20:00 | 2011-12-17 01:03 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2011-12-10 18:40 | 2011-12-10 18:40 | ONSHORE | UT | 84319 | NEAREST TOWN IS HYRUM | CACHE | MILEPOST | 73 + 1205 | RUBY PIPELINE300-A | VALVE 6 | YES | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | 1-INCH POWER GAS LINE | 2011 |  | CARBON STEEL |  | OTHER | [8 empty] | 1-INCH POWER GAS PIPE BROKE AT A FITTING | CLASS 1 LOCATION | NO |  | 1100 |  | NO | NO | NO |  | 0 | 0 | 603150 | 705723.604035052 | 3350 | 2267.05150976909 | 1622000 | 1897842.4699409 | 50000 | 58503.1587528021 | 0 | 0 |  |  | 2278500 | 1224310.37663779 | 2664336.28423852 | [8 empty] | 1178 |  | 1440 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | REMOTELY CONTROLLED | 37 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURES AND OPERATING PARAMETERS WERE NORMAL. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [52 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | SUBSIDENCE |  |  |  |  | NO | [306 empty] | KENNETH C PETERS | ENGINEER - PIPELINE EP | ken_peters@kindermorgan.com | 2053257554 | 2053253729 |  |  |  | KENNETH C PETERS | ENGINEER - PIPELINE EP | 2053257554 | ken_peters@kindermorgan.com | COLORADO INTERSTATE GAS (CIG) COMPANY GAS CONTROL EMPLOYEES NOTICED A PRESSURE DIFFERENTIAL ON THE 42" RUBY PIPELINE DURING THE EARLY EVENING OF DECEMBER 10, 2011. FIELD OPERATIONS EMPLOYEES WERE DISPATCHED TO MLV 6 AND FOUND A FIRE IN PROGRESS AT THE VALVE SITE. THE AFFECTED SEGMENT WAS ISOLATED AND BLOWN DOWN IN ORDER TO EXTINGUISH THE FIRE. THE ENSUING INVESTIGATION DETERMINED THAT THE LIKELY CAUSE OF THE INCIDENT WAS EARTH SETTLEMENT STRESSING A 1-INCH POWER GAS LINE WHICH BROKE, RELEASED GAS, AND IGNITED. THE SOURCE OF THE IGNITION IS BELIEVED TO BE THE ONSITE THERMOELECTRIC GENERATOR (TEG). PREVAILING WIND IS BELIEVED TO HAVE CARRIED THE RELEASED GAS TOWARD THE TEG, WHERE IT IGNITED, WITH SECONDARY FIRES SPREADING TO OTHER EQUIPMENT AT THE SITE. THE PIPELINE HAS BEEN REPAIRED AND PLACED BACK INTO SERVICE. PLEASE NOTE THAT FORM WOULD NOT ACCEPT THE DIGITS REQUIRED FOR THE ACTUAL VOLUME OF GAS IN PART A, QUESTION 11. THE ACTUAL VOLUME IS 181,055 MCF OR 181.055 MMCF.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120006 | 15833 | 2012-01-10 14:13 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2011-12-11 20:55 | 2011 |  |  | 29.0289 | -97.9559 | 997847 | 2011-12-11 23:40 |  | NATURAL GAS |  | 21566 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-12-11 22:15 | 2011-12-31 17:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-12-11 20:55 | 2011-12-11 22:15 | ONSHORE | TX | 78113 | FALLS CITY | KARNES |  |  | BURNELL TO FALLS CITY | 9122 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.25 | 46000 | API-5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | YOUNGSTOWN STEEL | COAL TAR | [28 empty] | 1962 | 1962 | CARBON STEEL |  | RUPTURE | [6 empty] | 10 | 2 |  | CLASS 1 LOCATION | NO |  | 341 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 86264 | 58377.5914742451 | 120000 | 140407.581006725 | 0 | 0 | 15000 | 17550.9476258406 | COST OF AERIAL PATROL LEAK SURVEYS |  | 221264 | 133029.832489998 | 216336.120106811 | [8 empty] | 847 |  | 612 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 | YES | YES | NOT MANDATED |  |  | MANUAL | MANUAL | 42240 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES | [9 empty] | YES | THE INVESTIGATION INDICATED THAT ALARMS NOT IN PLACE TO HELP IDENTIFY THE CONDITION. | YES | 1 | 0 | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [11 empty] | YES | [9 empty] | YES | [166 empty] | MATTHEW STRATMANN | PIPELINE COMPLIANCE SPECIALIST | mstratmann@eprod.com | 713-381-8209 |  |  |  |  | MATTHEW STRATMANN | PIPELINE COMPLIANCE SPECIALIST | 713-381-8209 | mstratmann@eprod.com | ON DECEMBER 11, 2011 AN ENTERPRISE PRODUCTS PIPELINE, BURNELL TO ADKINS LINE 9122, OVERPRESSURED AND HAD A FAILURE. THE OVERPRESSURIZATION WAS CAUSED TO BOTH MONITOR AND REGULATOR STATION VALVES FAILING TO FUCTION PROPERLY AT THE SAME TIME. THE PIPELINES ESTABLISHED MAOP IS 612 PSIG. DUE TO THE FAILURE OF THE PIPELINE REGULATORS THE PIPELINE WAS PRESSURED UP TO 847PSIG BEFORE FAILING. ONE CITY, PANNA MARIA, TX, LOST GAS SUPPLY FOR APPROXIMATELY 2 DAYS. THE TOTAL NUMBER OF RESIDENTS WITHOUT GAS DURING THIS TIME PERIOD WAS ABOUT TEN HOUSEHOLDS. THE PIPELINE WAS OUT OF SERVICE FOR TWENTY DAYS. IT WAS STARTED BACK UP ON DECEMBER 31, 2011. SUPPLEMENTAL/FINAL REPORT 8-7-12 THE FAILURE INVESTIGATION IDENTIFIED DEBRIS LODGED IN THE PRESSURE SENSING TUBES ON BOTH REGULATORS. THE INVESTIGATION ALL INDICATED THAT THERE WAS NOT A HIGH PRESSURE ALARM IN PLACE TO NOTIFY OF THE INCREASE IN PRESSURE. TO ADDRESS THESE ITEMS, REDUNDANT PRESSURE SENSING CONTROLS WERE INSTALLED AT THIS SITE AND A HIGH PRESSURE ALARM WAS ADDED TO THE CONTROL LOGIC.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120007 | 16822 | 2012-01-12 13:43 | SUPPLEMENTAL FINAL | 31371 | BUCKEYE DEVELOPMENT & LOGISTICS, LLC | ONE GREENWAY PLAZA SUITE 600 | HOUSTON | TX | 77046 | 2011-12-13 20:00 | 2011 |  |  | 29.4 | -95.15 | 998059 | 2011-12-14 08:27 |  | NATURAL GAS |  | 2.85 | 1139 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-12-14 01:00 | 2011-12-20 10:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-12-13 20:00 | 2011-12-13 21:00 | ONSHORE | TX | 77017 | HOUSTON | HARRIS | SURVEY STATION NO. | 7571 | WEBSTER NATURAL GAS | R7756 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  |  |  | YES |  |  |  |  | YES | CASED | [16 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10 |  | 0.279 | 42000 | X-42 | SEAMLESS |  | REPUBLIC LINE PIPE | COAL TAR | [28 empty] | 1957 | 1971 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | YES | METHOD2 | 218 |  | NO | NO | NO |  | 0 | 0 | 4600 | 5382.29060525779 | 12 | 8.12078152753108 | 120000 | 140407.581006725 | 20000 | 23401.2635011208 | 0 | 0 |  |  | 144612 | 77671.6146180412 | 169199.255894631 | [8 empty] | 533 |  | 860 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | REMOTELY CONTROLLED | 33289 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE RELEASE WAS CAUSED BY CORROSION, NOT PIPELINE OPERATIONS. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1957 | YES | YES | YES |  |  |  | 2011 |  |  |  | YES | [190 empty] | NO | [63 empty] | YES | 2007 | 1363 | NO | [13 empty] | NO | [63 empty] | MARK COPELAND | COMPLIANCE SPECIALIST | mcopeland@buckeye.com | 936-336-5773 | 936-336-5773 |  |  |  | CLAUDIA PANKOWSKI | DIRECTOR OF REGULATORY COMPLIANCE | 610-904-4113 | cpankowski@buckeye.com | AT 8:00 PM ON DECEMBER 13, 2011,CENTER POINT ENERGY CALLED THE CONTROL CENTER NOTIFYING THEM OF A GAS ODOR AT HWY 3 AND BROOKGLEN DRIVE IN HOUSTON, TX.THE CONTROL CENTER CALLED THE OPERATIONS ON CALL PERSON TO RESPOND. LOCAL OPERATIONS PERSONNEL DISCOVERED AN LEL AROUND A 10 FOOT AREA OF THE INTERSECTION OF HIGHWAY 3 AND BROOKGLEN DRIVE. EMERGENCY RESPONSE PROCEDURES WERE INITIATED AND AT THE REQUEST OF THE TPC PLANT, A CONTROLLED SHUTDOWN WAS COORDINATED WHICH ALLOWED THEM TO GET ANOTHER SUPPLIER ONLINE BEFORE THE PIPELINE WAS SHUT DOWN AND ISOLATED. A PORTABLE FLARE WAS BROUGHT OUT TO FLARE DOWN THE PIPELINE. THE PIPELINE WAS PURGED AND INERTED WITH NITROGEN BY APPROXIMATELY 10:00 PM ON DECEMBER 14, 2011. EXCAVATION OF THE RELEASE SITE WAS STARTED ON DECEMBER 15, 2011 AND THE DAMAGED SECTION OF PIPE WAS IDENTIFIED IN THE AFTERNOON LOCATED APPROXIMATELY 20 FEET INSIDE THE CASING UNDER BROOKGLEN DRIVE. IT WAS DECIDED TO REPAIR THE PIPELINE BY EXCAVATING BOTH ENDS OF THE CASING AND REPLACING THE ENTIRE PIPE SECTION INSIDE IT. THE INSTALLATION OF THE CERTIFIED REPLACEMENT PIPE WAS COMPLETED ON DECEMBER 18, 2011 AND THE PIPELINE WAS RETURNED TO SERVICE ON DECEMBER 20, 2011. NO FURTHER REMEDIATION OR REPAIRS ARE NECESSARY. ANALYSIS OF THE DAMAGED AREA OF THE PIPE DETERMINED THE CAUSE TO BE EXTERNAL CORROSION DUE TO BEING SHORTED TO THE CASING. DURING EXCAVATION IT WAS DISCOVERED THAT THE VENT PIPE WAS DETACHED FROM THE CASING RESULTING IN A BAD CP READING. NEW CASING VENTS WERE INSTALLED ON BOTH SIDES OF THE CASING. SUPPLEMENTAL REPORT FILED TO CORRECT PART C, QUESTION 1. APRIL 17, 2015 UPDATE INCLUDED PIPE MANUFACTURER.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120008 | 15421 | 2012-01-13 10:39 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2011-12-22 09:15 | 2011 |  |  | 28.9368 | -90.3533 | 998785 | 2011-12-22 09:45 |  | NATURAL GAS |  | 1 | 17247 | 1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-12-22 15:00 | 2012-01-01 13:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-12-22 09:15 | 2011-12-28 17:30 | OFFSHORE | [28 empty] | 60 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SOUTH TIMBALIER | 37 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 20 |  | 0.406 | 60000 | API 5L OR EQUIVALENT | DSAW |  | KAISER | OTHER | FUSION BOND EPOXY WITH CONCRETE | [27 empty] | 1977 | 1977 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 511 |  | NO | NO | NO |  | 0 | 0 | 51741 | 60540.2387405747 | 3 | 2.03019538188277 | 307366 | 359637.637864275 | 15000 | 17550.9476258406 | 0 | 0 |  |  | 374110 | 200931.185394881 | 437730.854426073 | [8 empty] | 771 |  | 1373 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 53011 | NO | [5 empty] | YES | PIG BARRELLS NOT DESIGNED TO ACCOMMODATE THE LENGTH OF AN ILI TOOL. | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | PRODUCTION OPERATOR OBSERVED FROM ITS AIR TRANSPORT AND FROM ITS PLATFORM. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATING PRESSURES WERE NORMAL AND LEAK WAS VERY SMALL IN TERMS OF CAUSING PRESSURE DROP. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN | [5 empty] | YES | MICROBIOLOGICAL BASED ON PIPELINE'S HISTORY BUT THIS CANNOT BE CONFIRMED SINCE PIPE WAS NOT CUT OPEN. | YES |  | YES | MICROBIOLOGICAL BASED ON PIPELINE'S HISTORY BUT THIS CANNOT BE CONFIRMED SINCE PIPE WAS NOT CUT OPEN. FIELD EXAMINATION WAS EXTERNAL BY DIVERS. | YES | [5 empty] | YES | YES | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | ken.peters@elpaso.com | 2053257554 | 2053253729 |  |  |  | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | 2053257554 | ken.peters@elpaso.com | PRODUCTION OPERATOR PERSONNEL REPORTED BUBBLES AND A LIGHT SHEEN IN THE VICINITY OF TENNESSEE GAS PIPELINE (TGP) COMPANY'S PIPELINE ON THE OCS IN THE SOUTH TIMABALIER AREA, BLOCK 37. TGP DISPATCHED DIVERS WHO FOUND A PINHOLE LEAK AT THE 6 O'CLOCK POSITION ON ITS 20" 524J-100 PIPELINE. INTERNAL CORROSION IS SUSPECTED AS THE CAUSE. THE LEAK WAS REPAIRED BY INSTALLATION OF A CLAMP AND THE PIPELINE WAS PLACED BACK INTO SERVICE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120009 | 16711 | 2012-01-14 16:39 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION CORP | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2011-12-15 12:59 | 2011 |  |  | 39.4751 | -79.051 | 998230 | 2011-12-15 14:52 |  | NATURAL GAS |  | 15581 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | PIPELINE WAS RETURNED BACK INTO SERVICE AFTER NECESSARY REPAIRS WERE PERFORMED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 30 | 2011-12-15 13:00 | 2011-12-15 13:40 | ONSHORE | WV | 26726 | MINERAL | MINERAL | MILEPOST | 8012-010 | LINE 8012 | TRANSMISSION | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 30 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 |  | 0.322 | 24000 | UNKNOWN | OTHER | UNKNOWN | UNKNOWN | COAL TAR | [28 empty] | 1965 | 1965 | CARBON STEEL |  | OTHER | [8 empty] | COAL MINE BACKHOE OPERATOR HAD PULLED THE COUPLED LINE PIPE FROM THE GROUND (30-IN DEPTH OF COVER). | CLASS 1 LOCATION | NO |  | 64 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 53131 | 35955.4369449378 | 5200 | 6084.32851029142 | 0 | 0 | 0 | 0 |  |  | 58331 | 40069.5014354018 | 42039.7654552293 | [8 empty] | 130 |  | 135 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL |  | NO | YES |  |  |  |  | YES | IN ADDTITION TO VARIABLE DIAMATERS, IT IS A COUPLED PIPE. | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | OTHER | A LOCAL DISTRIBUTION COMPANY NOTIFIED THE COMPANY'S MONITORING CENTER. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT THAT WAS INITIATED BY BY A THIRD PARTY (MECAHNICAL DAMAGE), HAD NO INVOLVEMENT WITH THE CONTROL ROOM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [64 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | [10 empty] | NO |  |  |  |  | YES | [6 empty] | UNKNOWN/OTHER | BACKHOE/TRACKHOE | LANDSCAPING | NO |  |  | UNKNOWN/OTHER | YES | YES |  |  | OTHER |  |  |  | BACKHOE OPERATOR FAILED TO SUBMIT A ONE CALL TICKET BEFORE HE STARTED OPERATING THE HEAVY EQUIPMENT. | [117 empty] | NO | [62 empty] | NO | NO |  |  | NO | [13 empty] | NO | [63 empty] | GEORGE HAMATY | ENGINEER | ghamaty@nisource.com | 3043573728 | 3043573804 |  |  |  | PERRY MICHAEL HOFFMAN | MANAGER | 3043572548 | mikeoffman@nisource.com | A LOCAL DISTRIBUTION COMPANY PERSONNEL NOTIFIED COLUMBIA GAS TRANSMISSION (COLUMBIA) MONITORING CENTER REGARDING A POTENTIAL RELEASE OF NATURAL GAS DUE TO A DAMAGE BY A THIRD PARTY HEAVY MACHINERY. COLUMBIA PERSONNEL WERE DISPATCHED TO INVESTIGATE AND SECURE THE LOCATION IF CONFIRMED TO BE A COLUMBIA OWNED PIPELINE. THE AREA WAS SECURED, THEREAFTER; NECESSARY EMERGENCY REPAIR PIPE WAS INSTALLED WHERE COORDINATED EFFORTS WERE MADE BETWEEN THE COLUMBIA PERSONNEL AND THE DISTRIBUTION COMPANIES (BETWEEN THE STATES OF MARYLAND AND WEST VIRGINIA) ENSURED THAT ALL LOST CUSTOMERS WERE RELIT AFTER NECESSARY REPAIRS WERE PERFORMED TO RESTORE THE SERVICE BACK TO CUSTOMERS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120010 | 15762 | 2012-01-20 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2011-12-23 08:58 | 2011 |  |  | 39.5497 | -97.2537 | 998872 | 2011-12-23 12:37 |  |  |  | 0 | 3000 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-12-23 08:58 | [5 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-12-23 08:58 | 2011-12-23 09:10 | ONSHORE | KS | 66973-0160 | CLIFTON | CLAY | SURVEY STATION NO. |  | CLIFTON COMPRESSOR STATION | COMPRESSOR UNIT 31 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | DRAIN LINES | [38 empty] | 1970 |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 44 |  | NO | NO | NO |  | 0 | 0 | 18000 | 21061.1371510088 | 0 | 0 | 245000 | 286665.47788873 | 0 | 0 | 0 | 0 |  |  | 263000 | 141254.636233952 | 307726.615039739 | [8 empty] | 900 |  | 1000 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | PIPE NIPPLE | [16 empty] | YES | [165 empty] | BYRON H. WOOD | SR PIPELINE SAFETY SPECIALIST - PIPELINE SAFETY | byron.wood@nngco.com | 402-398-7396 |  |  |  |  | THOMAS G. CORRELL | SR DIRECTOR PIPELINE PIPELINE SAFETY AND RISK | 402-398-7715 | thomas.correll@nngco.com | ON DECEMBER 23, 2011, AT 8:58 A.M., THE CLIFTON COMPRESSOR STATION EXPERIENCED AN UNPLANNED EMERGENCY SHUTDOWN DUE TO A SEAL OIL FIRE IN COMPRESSOR BUILDING 5. THE SEAL OIL FIRE OCCURRED ON UNIT 31, A G.E. FRAME III 9100-HORSEPOWER TURBINE COMPRESSOR, BETWEEN THE UNIT POWER TURBINE AND THE COMPRESSOR. THE FIRE AND GAS DETECTION SYSTEM DETECTED THE SEAL OIL FIRE IMMEDIATELY AND ACTIVATED THE STATION EMERGENCY SHUTDOWN SYSTEM, WHICH FUNCTIONED AS DESIGNED AND SAFELY SHUT DOWN THE UNIT AND THE STATION. ALL EMERGENCY VALVES TRAVELED TO THE CORRECT POSITION FOLLOWING ACTIVATION. THE ELECTRICAL POWER TO UNIT 31 WAS MANUALLY ISOLATED AND LOCKED OUT BY OPERATIONS PERSONNEL, AS IT IS NOT TRIPPED BY THE EMERGENCY SHUTDOWN SYSTEM. THIS IS BY DESIGN TO AVOID CATASTROPHIC DAMAGE TO THE TURBINES, DUE TO LACK OF LUBE OIL DURING POST-TRIP SPIN DOWN. AFTER ENSURING CONDITIONS WERE SAFE, CLIFTON VOLUNTEER FIRE DEPARTMENT PERSONNEL ENTERED THE BUILDING AND EXTINGUISHED THE RESIDUAL BURNING SEAL OIL. UNIT 31 WAS ON-LINE DECEMBER 23, 2011, WHEN THE FITTING FAILURE OCCURRED. ON DECEMBER 22, 2011, AT 3:45 P.M., OPERATIONS PERSONNEL PERFORMED A DAILY WALK THROUGH WHILE THE UNIT WAS DOWN AND NO ABNORMAL CONDITIONS WERE IDENTIFIED. THE UNIT WAS STARTED REMOTELY BY GAS CONTROL AT 3 A.M. DECEMBER 23, 2011, AND NO WALK THROUGH WAS CONDUCTED BEFORE THE 8:58 A.M. SHUTDOWN. THE FITTING THAT FAILED IS BELIEVED TO BE PART OF THE ORIGINAL 1970 INSTALLATION. THE CAUSE OF THE FIRE WAS DUE TO A FAILURE IN THE THREADED 1-INCH-DIAMETER END OF A 2- TO 1-INCH-DIAMETER SWEDGE FITTING, THAT THREADED INTO THE BOTTOM OF THE SEAL OIL PRESSURE REGULATOR. THE FITTING FAILURE ALLOWED HIGH PRESSURE COMPRESSOR SEAL OIL TO SPRAY ONTO THE BACK OF THE TURBINE EXHAUST AND IGNITE. SUPPLEMENTAL/FINAL REPORT TO ORGINAL REPORT NO. 20120010 - 15427, REPORT DATE 01/20/2012 - A METALLURICAL ANALYSIS OF THE FAILURE OF THE THREADED FITTING BY AN OUTSIDE METALLURICAL LABORATORY INDICATES THAT THE ROOT CAUSE WAS FROM THE FITTING BEING IN STRESS BINDING POSITION AND METAL FATIGUE OF THE THREADS. THIS EVENT IS CONSIDERED COMPLETE WITH NO FUTHER ACTIONS PENDING OR PLANNED. SUPPLEMENTAL/FINAL: UPDATED REPORT 20120010 DATED 1/20/2012 PER PHMSA REQUEST BY INDICATING IN PART E5F TRANSMISSION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120011 | 15883 | 2012-01-27 13:38 | SUPPLEMENTAL FINAL | 2620 | COLUMBIA GULF TRANSMISSION CO | 700 LOUISIANA ST. SUITE 700 | HOUSTON | TX | 77002 | 2012-01-02 19:50 | 2012 |  |  | 37.7927 | -84.0298 | 999450 | 2012-01-02 21:15 |  |  |  | 206923 | 14202 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-01-02 21:15 |  | YES |  |  |  | YES |  |  |  |  | YES | [6 empty] | 30 |  |  | ONSHORE | KY | 40336 | IRVINE | ESTILL | MILEPOST | 68.3 | LINE 200 | BETWEEN VS 212-2 AND 213 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 38 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 |  | 0.323 | 65000 | API 5L | DSAW |  | US STEEL | COAL TAR | [28 empty] | 1965 | 1965 | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER |  |  |  |  | CLASS 1 LOCATION | NO |  | 657 |  | YES | YES | NO |  | 100000 | 114830 | 43742 | 50228.9386 | 637323 | 513361.655391121 | 902000 | 1035766.6 | 0 | 0 | 5000 | 5741.5 | MISC. |  | 1688065 | 1086071.44646638 | 1719928.69399112 | [8 empty] | 909 |  | 1008 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 46464 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CAUSE OF THE FAILURE WAS NOT RELATED TO THE CONTROL ROOM OR THE CONTROLLERS SINCE THE SYSTEM WAS OPERATING NORMALLY AND BELOW ITS MAOP AT THE TIME OF THE INCIDENT. | [12 empty] | YES | 3 | 0 | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [52 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | SUBSIDENCE |  |  |  |  | NO | [306 empty] | GEORGE HAMATY | ENGINEER | ghamaty@nisource.com | 3043573728 | 3043573804 |  |  |  | PERRY MICHAEL HOFFMAN | MANAGER | 3043572548 | mikeoffman@nisource.com | BASED ON THE SITE EVALUATION INFORMATION, AERIAL PHOTOGRAPHY, THE ABNORMALLY HIGH RAINFALL AMOUNTS PRIOR TO THE INCIDENT, THE APPEARANCE OF THE FAILED SECTIONS AND THE PRELIMINARY REPORT PROVIDED BY THE THIRD PARTY METALLURGIST, THE MOSTLY LIKELY PRIMARY CAUSE OF THE FAILURE WAS PIPE FAILURE DUE TO LAND MOVEMENT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120012 | 15811 | 2012-02-02 12:38 | SUPPLEMENTAL | 2714 | DOMINION TRANSMISSION, INC | 925 WHITE OAKS BOULEVARD | BRIDGEPORT | WV | 26330 | 2012-01-06 09:30 | 2012 |  |  | 41.0597 | -78.7288 | 999735 | 2012-01-06 11:13 |  | NATURAL GAS |  | 1 | 19110 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-01-06 14:50 | 2012-01-09 17:09 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-01-06 09:30 | 2012-01-06 09:30 | ONSHORE | PA | 15848 | LUTHERSBURG | CLEARFIELD | MILEPOST | LUTHER GATE | LN-50 | LN-50 LUTHER GATE | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 65 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | WELDOLET | 1969 |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | YES | METHOD2 | 655 |  | NO | NO | NO |  | 0 | 0 | 66298 | 76129.9934 | 3 | 2.41649048625793 | 55000 | 63156.5 | 0 | 0 | 0 | 0 |  |  | 121301 | 63938.6810854123 | 139288.909890486 | [8 empty] | 890 |  | 1000 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 53224 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | MINOR LEAK WOULD NOT HAVE BEEN DETECTED BY SCADA | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | CRACK DISCOVERED IN WELDOLET ON SIDE CONNECTION TO LN50. SMALL LEAK RESULTED, HOWEVER GAS LOSS INCURRED DURING BLOWDOWN TRIGGERED INCIDENT REPORTING REQUIREMENT. | [147 empty] | SHAWN MILLER | COMPLIANCE ENGINEER | shawn.a.miller@dom.com | 3046273404 | 3046273360 |  |  |  | JAMES SHAFER | MANAGER PIPELINE INTEGRITY | 3046273430 | james.m.shafer@dom.com | EMPLOYEE WAS READING CORROSION TEST STATION AT LN 50 GATE SITE 107 ( LUTHERSBURG GATES) -EMPLOYEE REMOVED A TS CAP NEAR GATE#107-J AND NOTICED GAS ESCAPING OUT OF THE TS PIPE. EMPLOYEE IMMEDIATELY REPORTED THE LEAK TO SUPERVISORY PERSONNEL. INVESTIGATION FOUND THAT GAS APPEARED TO BE COMING FROM THE 107-J GATE. THIS IS A 6' TEMPORARY FEED FROM LUTHER STATION TO LN-50. IT WAS ALSO DETERMINED THAT THE GAS WAS MIGRATING UNDERGROUND AND WE WERE PICKING UP READINGS BY THE PARKING LOT AND CLOSE TO THE GARAGE/WAREHOUSE BUILDING. NOTIFIED GAS CONTROL OF THE FINDINGS AND BEGAN ARRANGEMENTS TO ISOLATE THE SEGMENT OF LN 50 FROM LUTHERSBURG GATE# 107 TO BIG RUN GATE # 90. THE PRESSURE ON LN 50 WAS 890# AND WAS BLOWN TO ATMOSPHERE. AFTER EXCAVATING THE VALVE, IT WAS FOUND THAT THE LEAK WAS AT THE 6' WOL ON LN 50. LUTHERSBURG TRANSMISSION WITH THE ASSISTANCE OF LUTHERSBURG G&P EMPLOYEES REPLACED THE SECTION OF 30" PIPE. THE PIPE WAS REPLACED WITH A STRAIGHT PIECE OF PIPE AND THE 'J' VALVE WAS REMOVED. THE 6' WAS CUT & CAPPED. THE LINE WAS PUT BACK IN SERVICE AND TURNED OVER TO GAS CONTROL AT 5:09 PM, MONDAY THE 9TH.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120013 | 15492 | 2012-02-03 15:16 | SUPPLEMENTAL | 11032 | LACLEDE GAS CO | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2012-01-05 14:10 | 2012 |  |  | 38.5852 | -90.6425 | 999686 | 2012-01-05 15:46 |  | NATURAL GAS |  | 16 | 94 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-01-06 22:30 | 2012-01-12 01:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-01-05 14:10 | 2012-01-05 14:10 | ONSHORE | MO | 63025 | WILDWOOD | ST. LOUIS | MILEPOST | MARKER POSTS | 16" WASHINGTON ELLISVILLE LINE | S-15 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 156 |  | YES |  |  |  |  | YES | BORED/DRILLED | [16 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.25 | 52000 | API 5LX52 | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | EPOXY | [28 empty] | 1992 | 1991 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | NO |  | 191 |  | NO | NO | NO |  | 0 | 0 | 1028 | 1180.4524 | 165 | 132.906976744186 | 235530 | 270459.099 | 0 | 0 | 0 | 0 |  |  | 236723 | 124827.512497674 | 271772.458376744 | [8 empty] | 180 |  | 300 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 5100 | NO | [5 empty] | YES | NO ACCOMODATIONS FOR LAUNCHERS AND RECEIVERS | YES |  | YES |  |  | YES | POTENTIAL FOR SIGNIFICANT OUTAGES | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SYSTEM OPERATING PRESSURE WAS WITHIN NORMAL RANGE | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  |  | YES | [7 empty] | YES |  |  |  | YES | YES | 1991 | YES | YES | YES | YES | YES |  | 2011 | 1991 | 2012 |  | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | MARK D. LAUBER | SUPERINTENDENT MAINTENANCE ENGINEERING | mlauber@lacledegas.com | 314-658-5413 | 314-535-5075 |  |  |  | CRAIG R. HOEFERLIN | ASSISTANT VP ENGINEERING AND FIELD SERVICES | 314-658-5410 | choeferlin@lacledegas.com | FIELD INSTALLED SHRINK SLEEVE WAS DAMAGED AND DISBONDED DURING INSTALLATION WHEN THE PIPE WAS PULLED THROUGH THE BORE HOLE EXPOSING THE EXTERIOR OF THE STEEL PIPE TO THE EFFECTS OF "TENTING" AND ATMOSPHERIC CORROSION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120014 | 15705 | 2012-02-09 17:05 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | TX | 77002 | 2012-01-11 12:50 | 2012 |  |  | 41.9206 | -86.5055 | 1000140 | 2012-01-11 13:02 |  | NATURAL GAS |  | 800 | 500 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-01-11 15:00 | 2012-01-23 12:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 |  |  | ONSHORE | MI | 49106 | BARODA | BERRIEN | MILEPOST | MP 918 | ANR LINE 100 |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 22 |  | 0.25 | 52000 | API 5LX | FLASH WELDED |  | A O SMITH | COAL TAR | [28 empty] | 1949 | 1949 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 2 LOCATION | NO |  | 442 |  | NO | NO | NO |  | 0 | 0 | 3000 | 3444.9 | 5000 | 4027.48414376321 | 350000 | 401905 | 10000 | 11483 | 0 | 0 |  |  | 368000 | 195512.775687104 | 420860.384143763 | [8 empty] | 784 |  | 850 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 79200 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | RIGHT-OF WAY CLEARING CREW |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A MATERIALS OR EQUIPMENT-RELATED INCIDENT. CONTROLLER ACTIONS DID NOT CONTRIBUTE TO THE CAUSE. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES | [7 empty] | YES | UNREPAIRED BURN-THROUGH OF A WELD. | [19 empty] | YES | POOR WELDING PRACTICE AND INSPECTION. | [55 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | LOUIS SALINAS | COMPLIANCE ENGINEER | louis_salinas@transcanada.com | 832-320-5305 | 832-320-6305 |  |  |  | LOUIS SALINAS |  | 832-320-5305 | No Email Address | BRUSHING CREW NOTICED BUBBLES IN WATER IN AN AREA OVER THE PIPELINE AND NOTIFIED STATION PERSONNEL. UPON FURTHER INVESTIGATION, IT WAS DETERMINED THAT GAS LEAK WAS FROM COMPANY PIPELINE. LEAK DETECTION EQUIPMENT WAS USED. SUBSEQUENTLY, A METALLURGICAL STUDY FOUND THAT THE CAUSE WAS DETERMINED TO BE AN UNREPAIRED BURN-THROUGH OF A WELD.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120015 | 17562 | 2012-02-14 12:59 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION CORP | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2012-01-21 08:18 | 2012 |  |  | 39.7655 | -80.6442 | 1000917 | 2012-01-21 12:31 |  | NATURAL GAS |  | 3176 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE VALVE WAS SET IN BY-PASS MODE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-01-21 08:18 | 2012-01-21 08:23 | ONSHORE | WV | 26033 | CAMERON | MARSHALL | MILEPOST | C88-108 | ADALINE COMPRESSOR STATION | VALVE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1953 |  | CARBON STEEL |  | OTHER | [8 empty] | VALVE ACTUATOR, PNEUMATIC WAS MOMENTARILY STUCK IN THE OPEN POSITION REACHING A REPORTABLE LEVEL OF UNINTENDED AMOUNT NATURAL GAS THAT WAS RELEASED INTO ATMOSPHERE. | CLASS 1 LOCATION | NO |  | 121 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 9877 | 7955.89217758985 | 0 | 0 | 0 | 0 | 0 | 0 | NO DAMAGE. |  | 9877 | 8248.23467230444 | 7955.89217758985 | [8 empty] | 465 |  | 860 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO APPARENT OR PROBABLE CAUSE IS AVAILABLE THAT LED TO THE FAILURE OF THIS VALVE. AWAITING THE ROOT CAUSE ANALYSIS REPORT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | APPURTENANCE FAILURE | [16 empty] | YES | [167 empty] | GEORGE HAMATY | ENGINEER | george_hamaty@transcanada.com | (304) 553-8306 |  |  |  |  | LEE ROMACK | MANAGER USRC | (832) 584-3178 | lee_romack@transcanada.com | AFTER AN INVESTIGAITON WAS COMPLETED INTO THIS REPORTABLE ICNIDENT, A CAUSAL FACTOR WAS IDENTIFED TO BE THE ROOT CAUSE BEHIND THIS REPORTABEL INCIDENT. THIS CAUSAL FACTOR WAS THE COMPRESSED AIR USED IN THE PILOT AIR SYSTEM THAT IS PART OF THE COMPRESSOR SATTION ESD SYSTEM. THE DEW POINT OF THE CONTROL AIR WAS ABOVE THE AMBIENT TEMPERATURE AT THE TIME OF THE INCIDENT DUE TO EQUIPMENT FAILURE DURING THE FALL OF 2011. INDICATIONS TO THE PRESENCE OF MOISTURE WAS FOUND IN THE BULK AIR STORAGE TANKS WHICH SUPPLY AIR TO ALL THE CONTROL SYSTEMS AT THE STATION. IN LIEU OF THIS FINDING, A NUMBER OF RECOMMENDATIONS WERE ISSUED AND IMPLEMENTED ACCORDINGLY. THE RECOMMENDATIONS WERE: (I) INSTALL NEW COMPRESSED AIR DRYING SYSTEM INCLUDING A NEW AFTERCOOLER, AIR DRYER AND WATER TRAPS. (INSTALLED AND FULLY FUNCTIONAL AS OF NOVEMBER 2, 2012.) (II) INSTALL FILTER/DRYER ON PILOT AIR SUPPLY SYSTEM. (INSTALLED AND WAS IN OPERATION AS OF JANUARY 31, 2013.) (III) ELIMINATE EXISTING MOISTURE IN THE ESD PILOT AIR SYSTEM. ACCUMULATED MOISTURE WAS REMOVED INTO OUTSIDE STORAGE TANKS. SMALL ESD STORAGE TANK CHECKED, NO WATER FOUND. PILOT AIR LINES TO BE PURGED WHEN NEW AIR SYSTEM IS INSTALLED. (COMPLETED ON DECEMBER 3, 2012.) (IV) TRAIN ADALINE COMPRESSOR STATION OPERATIONS PERSONNEL REGARDING THE IMPORTANCE OF THE AIR DRYING EQUIPMENT AND THE DOWNSTREAM SYSTEMS. (COMPLETED ON JANUARY 31, 2013.)
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120016 | 15537 | 2012-02-20 11:22 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2012-01-23 13:10 | 2012 |  |  | 40.8681 | -73.865 | 1001660 | 2012-01-30 10:10 |  | NATURAL GAS |  | 134 | 1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-01-30 09:48 | 2012-02-03 13:37 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-01-23 13:10 | 2012-01-23 13:10 | ONSHORE | NY | 10467-8304 | NEW YORK | BRONX |  |  | 24" BRONX |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 45 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PULSATION BOTTLE OR DRIP/DRIP COLLECTION DEVICE | [38 empty] | 1948 |  | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 4 LOCATION | YES | METHOD1 | 259 |  | NO | NO | NO |  | 0 | 0 | 5 | 5.7415 | 402 | 323.809725158562 | 129400 | 148590.02 | 42300 | 48573.09 | 218000 | 250329.4 | MATERIALS AND CONTRACTOR SUPPORT |  | 390107 | 205749.213745243 | 447822.061225159 | [8 empty] | 168 |  | 245 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 2273 | NO |  |  | YES |  |  | YES | DRIP POTS | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO ABNORMAL OPERATING CONDITIONS PRESENT | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | MECHANICAL COUPLING | [19 empty] | YES | COMPRESSION COUPLING LEAK AT SEAL | [161 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-579-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPARTMENT MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-579-2350 | dadariov@coned.com | ON JANUARY 23, 2012 BRONX GAS OPERATIONS-CAPITAL CONSTRUCTION REPORTED TO THE GAS EMERGENCY RESPONSE CENTER (GERC) A SUSPECTED, UNCONFIRMED TRANSMISSION MAIN LEAK ON THE 24" MAIN NEAR TRANSMISSION DRIP #24020 AT HOLLAND AVE. AND ARNOW AVE. AS PART OF AN ONGOING INVESTIGATION OF A LEAK ORIGINALLY SUSPECTED TO BE ON A 6"LOW PRESSURE CAST IRON MAIN IN THE VICINITY OF THE DRIP. DURING CONTINGENCY PREPARATION, A SECOND SUSPECTED, UNCONFIRMED LEAK WAS IDENTIFIED AT 24" DRIP 24021 AT ADEE AVE. AND WALLACE AVE. AN OPERATIONAL PLAN WAS DEVELOPED INVOLVING THE INSTALLATION OF A 24" CONTROL FITTING NORTH OF THE SUSPECTED LEAK AT DRIP 24021 AND THE USE OF AN EXISTING STRADDLE CONNECTION AT REGULATOR STATION GR-126 IN CONJUNCTION WITH V-6405 TO THE SOUTH IN ORDER TO MAINTAIN SUPPLY TO REGULATOR STATIONS GR-126, GR-110 AND GR-192. A WELDED 24" CONTROL FITTING WAS INSTALLED AND WITH V-6405 CLOSED, THE AFFECTED SECTION OF MAIN WAS ISOLATED ON 1-30-12 AT 09:48 HRS, AND THE MAIN WAS REDUCED TO LOW PRESSURE. A NEW 24" WELDED TRANSMISSION VALVE (#57434) WAS INSTALLED AND CLOSED, AND THE STOPPER WAS REMOVED RETURNING THE MAIN TO TRANSMISSION PRESSURE UP TO THE NEWLY INSTALLED CLOSED VALVE. DRIPS 24021 AND 24020 WERE EXCAVATED, CUT OUT AND REPLACED WITH NEW 24" MAIN. A COUPLING APPROXIMATELY 50' NORTH OF DRIP 24020 WAS EXPOSED AND A WELDED REPAIR SLEEVE INSTALLED AS A PREVENTIVE MEASURE. LEAK SURVEY PERFORMED A SURVEILLANCE OF THE AFFECTED SECTION PRIOR TO RETURNING THE MAIN TO TRANSMISSION PRESSURE AND NO LEAKS WERE FOUND. THE MAIN WAS RETURNED TO NORMAL OPERATING PRESSURE ON FEBRUARY 3, 2012 AT 13:37 HRS. THERE WERE NO INJURIES OR EVACUATIONS. THE US DOT, NYS PSC AND NYC DEP WERE NOTIFIED. THIS WAS A SERIOUS LEVEL INCIDENT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120017 | 15645 | 2012-02-20 15:43 | SUPPLEMENTAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2012-01-23 13:40 | 2012 |  |  | 29.1427 | -89.6106 | 1001064 | 2012-01-23 14:00 |  | NATURAL GAS |  | 1 | 124 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-01-23 14:30 | 2012-03-05 17:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-01-23 13:40 | 2012-01-23 13:40 | OFFSHORE | [28 empty] | 60 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST DELTA | 29 | SPLASH ZONE OF RISER | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12.75 |  | 0.375 | 42000 | API 5L OR EQUIVALENT | SEAMLESS |  | NATIONAL TUBE | OTHER | SPLASHTRON RUBBER | [27 empty] | 1958 | 1958 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 292 |  | NO | NO | NO |  | 0 | 0 | 372 | 427.1676 | 3 | 2.41649048625793 | 330000 | 378939 | 4000 | 4593.2 | 0 | 0 |  |  | 334375 | 176249.986485412 | 383961.784090486 | [8 empty] | 770 |  | 1100 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 72832 | NO | [5 empty] | YES | LAUNCHERS AND RECEIVERS ARE NOT LONG ENOUGH FOR AN ILI TOOL. | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | LOCAL PLATFORM OPERATIONS PERSONNEL |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURES WERE WITHIN NORMAL OPERATING RANGE AT ALL TIMES. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  |  | YES | [7 empty] | YES |  |  |  | NO | [11 empty] | YES | NO | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KENNETH C PETERS | COMPLIANCE ENGINEER | ken.peters@elpaso.com | 2053257554 | 2053253729 |  |  |  | KENNETH C PETERS | COMPLIANCE ENGINEER | 2053257554 | ken.peters@elpaso.com | LOCAL PRODUCTION PLATFORM OPERATIONS PERSONNEL NOTIFIED SOUTHERN NATURAL GAS (SNG) COMPANY OF A POSSIBLE LEAK ON ITS 12" RISER PIPE ON THE EPL WEST DELTA BLOCK 29 PLATFORM. THE REPORT DESCRIBED THE RELEASE AS A MINOR SPRAY AT OR NEAR THE WATER LEVEL. UPON INVESTIGATION, SNG PERSONNEL DETERMINED THAT THIS WAS A RELEASE OF NATURAL GAS CAUSED BY EXTERNAL CORROSION. THE PIPELINE WAS REPAIRED BY INSTALLATION OF NEW PIPE. THE PIPELINE WAS RETURNED TO SERVICE MARCH 5, 2012.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120018 | 15453 | 2012-02-24 10:27 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2012-02-01 13:38 | 2012 |  |  | 28.936 | -90.3527 | 1001902 | 2012-02-01 14:10 |  | NATURAL GAS |  | 935 | 8853 | 1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-02-01 15:05 | 2012-02-06 23:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-02-01 13:38 | 2012-02-03 12:30 | OFFSHORE | [28 empty] | 60 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SOUTH TIMBALIER | 37 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 20 |  | 0.406 | 60000 | API 5L OR EQUIVALENT | DSAW |  | KAISER | OTHER | FUSION BOND EPOXY WITH CONCRETE | [27 empty] | 1977 | 1977 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 511 |  | NO | NO | NO |  | 0 | 0 | 26559 | 30497.6997 | 2805 | 2259.41860465116 | 250898 | 288106.1734 | 7000 | 8038.1 | 0 | 0 |  |  | 287262 | 152279.726560465 | 328901.391704651 | [8 empty] | 704 |  | 1373 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 174398 | NO | [5 empty] | YES | PIG BARRELS NOT LONG ENOUGH FOR AN II TOOL. | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | LOCAL PRODUCTION PLATFORM PERSONNEL NOTIFIED GAS CONTROL. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATING PRESSURES WERE WITHIN NORMAL RANGE. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN | [5 empty] | YES | SUSPECTED MICROBIOLOGICAL, BASED ON PIPE'S HISTORY, BUT SINCE PIPE IS OFFSHORE, IT WAS NOT CUT OPEN TO ALLOW A DEFINITIVE CONCLUSION. | YES |  | YES | PIPELINE HISTORY. | YES | [5 empty] | YES | YES | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | ken.peters@elpaso.com | 2053257554 | 2053253729 |  |  |  | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | 2053257554 | ken.peters@elpaso.com | OFFSHORE LOUISIANA PRODUCTION PLATFORM PERSONNEL SAW BUBBLES IN THE VICINITY OF TENNESSEE GAS PIPELINE'S (TGP) 524J-100 PIPELINE IN SOUTH TIMBALIER BLOCK 37. TGP GAS CONTROL WAS NOTIFIED AND CONSEQUENTLY ADVISED TGP FIELD PERSONNEL WHO DISPATCHED DIVERS TO INVESTIGATE. DIVERS FOUND A PINHOLE LEAK ON THE PIPELINE IN THE 6 O'CLOCK POSITION, THOUGHT TO HAVE BEEN CAUSED BY INTERNAL CORROSION. THE PIPELINE WAS REPAIRED BY CLAMP INSTALLATION AND PLACED BACK INTO SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120019 | 15988 | 2012-02-24 12:50 | SUPPLEMENTAL FINAL | 21349 | VIRGINIA NATURAL GAS | 544 S. INDEPENDSNCE BLVD | VIRGINIA BEACH | VA | 23452-1104 | 2012-01-18 10:00 | 2012 |  |  | 38.0689 | -77.52 | 1001222 | 2012-01-25 11:25 |  | NATURAL GAS |  | 1 | 1750 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-01-24 09:40 | 2012-01-25 13:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-01-18 10:00 | 2012-01-18 10:00 | ONSHORE | VA | 23116-2014 | MECHANICSVILLE | HANOVER COUNTY | MILEPOST | M&R-143 | VNG JOINT-USE PIPELINE | LADYSMITH M&R | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | 24 INCH WELD-END INSULATOR | 2000 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | EPOXY INSULATOR MATERIAL | LEAK |  |  | CRACK | [6 empty] | CLASS 2 LOCATION | NO |  | 626 |  | NO | NO | NO |  | 0 | 0 | 7800 | 8956.74 | 0 | 0 | 0 | 0 | 6890 | 7911.787 | 84718 | 97281.6794 | CONTRACTOR LABOR AND MATERIAL COST (MATERIALS, EXCAVATION, WELDING, TESTING) |  | 99408 | 52397.9568 | 114150.2064 | [8 empty] | 900 |  | 1250 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | REMOTELY CONTROLLED | 10600 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK FOUND ON THE PIPELINE WAS VERY SMALL AND COULD NOT BE DETECTED BY THE SCADA SYSTEM. THEREFORE, GAS CONTROL WAS NOT INVOLVED IN THE ACTUAL INCIDENT. HOWEVER, GAS CONTROL DID PROVIDE SUPPORT IN THE REPAIR EFFORT, BY MANAGING THE PIPELINE PRESSURE, AND ISOLATING THE DAMAGED SECTION OF PIPE. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [52 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | EARTHQUAKE |  |  |  |  | NO | [306 empty] | BILL ROBINSON | MANAGER DISTRIBUTION QUALITY ASSURANCE PROGRAM | brobinso@aglresources.com | 757-616-7530 | 757-616-7517 |  |  |  | ROBERT S DUVALL | VICE PRESIDENT AND GENERAL MANAGER OF VA OPERATION | 757-616-7503 | rduvall@aglresources.com | VIRGINIA NATURAL GAS EMPLOYEES SMELLED GAS WHILE PERFORMING ROUTINE MAINTENANCE AT THE LADYSMITH M&R STATION (M&R-143) ON 01/18/12. ALL ABOVE GROUND PIPING AND EQUIPMENT WAS IMMEDIATELY INVESTIGATED AT THE SITE AND NO LEAKS WERE FOUND. VNG CALLED IN A MISS UTILITY LOCATE TICKET TO EXCAVATE IN THE AREA TO SEARCH FOR THE POTENTIAL LEAK. THE TICKET WAS CLEARED AND EXCAVATION BEGAN ON 01/23/12. A SMALL LEAK WAS FOUND AT THE 24 INCH WELD-END INSULATOR THAT WAS NEAR THE LADYSMITH M&R STATION. VNG NOTIFIED THE VIRGINIA STATE CORPORATION COMMISSION OF THE FOUND LEAK AND BEGAN STAGING EQUIPMENT, MATERIAL AND LABOR TO MAKE THE REPAIR. THE AFFECTED SECTION OF PIPELINE WAS ISOLATED BY CLOSING MLV-140 AND MLV-145, AND THE 2-MILE SECTION OF 24 INCH PIPELINE WAS PURGED OF GAS. AFTER THE SECTION OF PIPELINE WAS FREE OF GAS, THE FAILED INSULATOR WAS REMOVED AND A LENGTH OF PRE-TESTED PIPE WAS INSTALLED. THE PIPELINE WAS RE-ACTIVATED ON 01/25/12. IT IS NOTED THAT THE WEATHER WAS MILD AND DOWNSTREAM CUSTOMERS HAD ALTERNATE SOURCES OF FUEL TO OPERATE AND/OR DID NOT NEED TO OPERATE. THE FAILED 24 INCH WELD-END INSULATOR WAS SHIPPED TO AN INDEPENDENT, THIRD-PARTY LABORATORY FOR FURTHER INVESTIGATION. THE INDEPENDENT LABORATORY CONCLUDED THAT THE INSULATOR SUFFERED EITHER A SINGLE, SEVERE BENDING MOMENT OR SEVERAL, SUCCESSIVE, LESS CATASTROPHIC BENDING MOMENTS THAT CAUSED THE INTERIOR AND EXTERIOR EPOXY TO CRACK AND OPEN A PATH AT THE CENTER GASKET FOR MATERIAL TO ESCAPE. THE ONLY KNOWN PHYSICAL OR ENVIRONMENTAL FACTOR THAT COULD HAVE CONTRIBUTED TO THE FAILURE OF THE FITTING IS THE EARTHQUAKE THAT OCCURRED IN VIRGINIA ON AUGUST 23, 2011.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120020 | 15593 | 2012-02-24 12:55 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2012-02-08 15:17 | 2012 |  |  | 29.9378 | -90.3537 | 1002508 | 2012-02-08 16:30 |  | NATURAL GAS |  | 368 | 11374 | 1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-02-08 17:35 | [5 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-02-08 15:17 | 2012-02-15 08:35 | OFFSHORE | [28 empty] | 60 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SOUTH TIMBALIER | 37 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 20 |  | 0.406 | 60000 | API 5L OR EQUIVALENT | DSAW |  | KAISER | OTHER | FUSION BOND EPOXY WITH CONCRETE. | [27 empty] | 1977 | 1977 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 511 |  | NO | NO | NO |  | 0 | 0 | 34122 | 39182.2926 | 1104 | 889.268498942918 | 256104 | 294084.2232 | 7000 | 8038.1 | 0 | 0 |  |  | 298330 | 157589.769631712 | 342193.884298943 | [8 empty] | 741 |  | 1373 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 174398 | NO | [5 empty] | YES | PIG BARRELS ARE NOT LONG ENOUGH TO ACCOMMODATE II TOOLS. | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | LOCAL PRODUCTION PLATFORM PERSONNEL SENT A TEXT MESSAGE TO A TGP TECHNICIAN. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE REMAINED WELL WITHIN NORMAL OPERATING RANGE. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN | [5 empty] | YES | MICROBIOLOGICAL BUT BASED ON HISTORY OF PIPE; NOT FIELD OR LABORATORY CONFIRMED. | YES |  | YES | BASED ON HISTORY OF PIPE. | YES | [5 empty] | YES | YES | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | ken.peters@elpaso.com | 2053257554 | 2053253729 |  |  |  | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | 2053257554 | ken.peters@elpaso.com | LOCAL PRODUCTION PLATFORM PERSONNEL OBSERVED BUBBLES IN THE VICINITY OF TENNESSEE GAS PIPELINE'S (TGP'S) 524J-100 PIPELINE AND SENT A TEXT MESSAGE TO A TGP TECHNICIAN. THIS TECHNICIAN REPORTED TO HIS MANAGER AND A TGP HELICOPTER WAS DISPATCHED TO CONFIRM THE BUBBLES AND THE PIPELINE COORDINATES. TGP COMMISSIONED A DIVER TO THE SITE WHO CONFIRMED A PINHOLE LEAK AND INSTALLED A CLAMP. THE PIPELINE REMAINS OUT OF SERVICE PENDING TGP'S OPERATIONAL DECISION TO RE-ROUTE GAS FLOW AND ABANDON THIS PIPELINE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120021 | 15936 | 2012-02-24 15:51 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | TX | 77002 | 2012-01-30 09:00 | 2012 |  |  | 40.629 | -93.5415 | 1001679 | 2012-01-30 10:53 |  | NATURAL GAS |  | 17020 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-01-30 09:00 | 2012-01-30 17:00 |  |  |  |  | NO |  |  |  |  | NO | [9 empty] | ONSHORE | IA | 50147 | LINEVILLE | WAYNE | MILEPOST | 35 | LINEVILLE COMPRESSOR STATION | LINE 100 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1949 |  | CARBON STEEL |  | OTHER | [8 empty] | THE INITIAL CAUSE OF THE ESD WAS A FAILED COPPER OIL LINE THAT CAUSED A FIRE. THE FIRE DETECTION RESULTED IN THE ESD OF THE COMPRESSOR STATION. DURING THE STATION ISOLATION AND BLOW-DOWN IT WAS DISCOVERED THAT ONE OF THE STATION ISOLATION VALVES WAS NOT IN THE PROPER OPERATING POSITION RESULTING A REPORTABLE GAS RELEASE. | CLASS 1 LOCATION | NO |  | 506 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 100000 | 80549.6828752643 | 5000 | 5741.5 | 10000 | 11483 | 0 | 0 |  |  | 115000 | 91416.0137420719 | 97774.1828752643 | [8 empty] | 900 |  | 975 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | THE OPERATOR EMPLOYEE DID NOT CONFIRM THAT THE ISOLATION VALVE WAS LEFT IN THE PROPER OPERATING POSITION. |  |  | YES |  |  | NON-ROUTINE OPERATING CONDITIONS (ABNORMAL OPERATIONS OR EMERGENCIES) | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | LOUIS SALINAS | COMPLIANCE ENGINEER | louis_salinas@transcanada.com | 832-320-5305 | 832-320-6305 |  |  |  | LOUIS SALINAS |  | 832-320-5305 | No Email Address | ANR'S LINEVILLE COMPRESSOR STATION EXPERIENCED AN ESD EVENT AT APPROXIMATELY 6:30 AM ON JANUARY 30TH 2012. THE INITIAL CAUSE OF THE ESD WAS A FAILED COPPER OIL LINE THAT CAUSED A FIRE. THE FIRE DETECTION RESULTED IN THE ESD OF THE COMPRESSOR STATION. DURING THE STATION ISOLATION AND BLOW-DOWN IT WAS DISCOVERED THAT ONE OF THE STATION ISOLATION VALVES WAS NOT IN THE PROPER OPERATING POSITION, RESULTING A REPORTABLE GAS RELEASE. THE VENTING OF GAS WAS STOPPED BY FIELD PERSONAL AT APPROXIMATELY 7:00 AM.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120022 | 15937 | 2012-02-24 16:58 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | TX | 77002 | 2012-02-08 09:00 | 2012 |  |  | 28.5267 | -91.6476 | 1002473 | 2012-02-08 11:00 |  | NATURAL GAS |  | 1000 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE LEAK WAS A SMALL NON-HAZARDOUS PIN-HOLE LEAK, ABOVE WATER ON THE PLATFORM P. | [6 empty] | NO |  |  |  |  | NO | [9 empty] | OFFSHORE | [28 empty] | 125 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EUGENE ISLAND | 250 | PLATFORM | INTERSTATE | OFFSHORE PLATFORM, INCLUDING PLATFORM-MOUNTED EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1970 |  | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 110 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 4000 | 3221.98731501057 | 80000 | 91864 | 5000 | 5741.5 | 0 | 0 |  |  | 89000 | 48143.8805496829 | 100827.487315011 | [8 empty] | 800 |  | 1250 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | PLATFORM OPERATOR EL PASO NOTIFIED OUR PERSONNEL OF THE POSSIBLE LEAK ON PIPING. |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  |  | YES | [7 empty] | YES |  |  |  | NO | [11 empty] | YES | NO | [335 empty] | LOUIS SALINAS |  |  | 832-320-5305 | 832-320-6305 |  |  |  | LOUIS SALINAS |  | 832-320-5305 |  | PLATFORM OWNER AT EUGENE ISLAND 250 CALLED TO INFORM US THAT WE HAD A BONNET LEAKING ON A CHECK VALVE ON THE VENT SYSTEM. WHEN PIPELINE TECHS ARRIVED ON THE PLATFORM TO INVESTIGATE, THEY FOUND IT WASN'T ON THE BONNET OF THE CHECK VALVE. THERE IS A LOW PRESSURE LEAK ON A 4" VENT PIPE JUST BEFORE IT CONNECTS TO THE PRODUCERS VENT SYSTEM. IT IS AN ATMOSPHERIC CORROSION LEAK WHERE THE PIPE IS SITTING ON AN ANGLE IRON BRACE. THE VENT SYSTEM IS OPEN TO ATMOSPHERE BUT THERE IS ENOUGH LEAKING GAS IN THE SYSTEM TO DETECT THE LEAK. SUBSEQUENTLY, THE LEAK WAS REPAIRED BY REMOVING THE LINE, IN NOVEMBER, 2012.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120023 | 16154 | 2012-02-27 15:24 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2012-02-01 07:46 | 2012 |  |  | 42.7541 | -74.4018 | 1001854 | 2012-02-01 09:36 |  | NATURAL GAS |  | 492 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-02-01 07:46 | 2012-02-06 11:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-02-01 07:46 | 2012-02-01 07:46 | ONSHORE | NY | 12031-0110 | CARLISLE | SCHOHARIE | MILEPOST | 249 | COMPRESSOR STATION 249 | 249 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | OTHER | COMPRESSOR ENGINE WITHIN A BUILDING |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 1964 |  | CARBON STEEL |  | LEAK |  |  | OTHER | COMPRESSOR COMPONENT FAILURE | [5 empty] | CLASS 1 LOCATION | NO |  | 571 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 1300 | 1047.14587737844 | 103000 | 118274.9 | 0 | 0 | 0 | 0 |  |  | 104300 | 55376.9236786469 | 119322.045877378 | [8 empty] | 724 |  | 760 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURES REMAINED WITHIN NORMAL OPERATING RANGE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | OTHER | COMPRESSOR ROD FRACTURE AT THE THREADED CONNECTION TO THE CROSSHEAD. | [8 empty] | YES |  | YES | [9 empty] | YES | FAILURE DUE TO HIGH CYCLE LOW NOMINAL STRESS AXIAL FATIGUE. | [161 empty] | MARTIN MULLER | COMPLIANCE ENGINEER | martin_muller@kindermorgan.com | 205-325-3863 | 205-325-3508 |  |  |  | REJI GEORGE | DIRECTOR COMPLIANCE - CODES AND STANDARD | 713-420-5433 | reji_george@kindermorgan.com | NATURAL GAS WAS RELEASED AT TENNESSEE GAS PIPELINE (TGP) COMPANY'S COMPRESSOR STATION 249 FROM UNIT 1A WHEN A COMPRESSOR ROD FAILED IN ITS THREADS. THE STATION'S ESD SYSTEM ACTIVATED AND EVACUATED THE STATION OF NATURAL GAS. THE UNIT HAS BEEN REPAIRED AND IS BACK IN SERVICE. A ROOT CAUSE ANALYSIS DETERMINED THAT THE FAILURE WAS LIKELY DUE TO A COMBINATION OF FACTORS, INCLUDING HIGH CYCLE LOW NOMINAL STRESS AXIAL FATIGUE, INSUFFICIENT TIGHTENING DURING THE LATEST MAINTENANCE ACTIVITY, AND THE PRESENCE OF LOWER STRENGTH MATERIAL NOT MEETING THE CHEMISTRY AND MECHANICAL PROPERTY REQUIREMENTS OF THE SPECIFICATION FOR NEW REPLACEMENT COMPRESSOR RODS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120024 | 15938 | 2012-03-01 15:55 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | TX | 77002 | 2012-02-06 15:00 | 2012 |  |  | 28.7047 | -91.7643 | 1002288 | 2012-02-06 16:30 |  | NATURAL GAS |  | 1000 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | [9 empty] | NO |  |  |  |  | NO | [9 empty] | OFFSHORE | [28 empty] | 108 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EUGENE ISLAND | 199 | PLATFORM | INTERSTATE | OFFSHORE PLATFORM, INCLUDING PLATFORM-MOUNTED EQUIPMENT AND PIPING | PIPE | PIPE BODY | 8.625 |  | 0.25 | 42000 | API | DSAW |  | LTV | OTHER | UNKNOWN | [28 empty] | 1986 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 211 |  | NO | NO | NO |  | 0 | 0 | 20000 | 22966 | 0 | 0 | 140000 | 160762 | 10000 | 11483 | 0 | 0 |  |  | 170000 | 89607 | 195211 | [8 empty] | 875 |  | 1050 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  | YES |  |  |  |  | YES | [5 empty] | YES |  |  |  | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | LOUIS SALINAS |  |  | 832-320-5305 | 832-320-6305 |  |  |  | LOUIS SALINAS |  | 832-320-5305 | louis_salinas@transcanada.com | AT EI 199 A ATMOSPHERIC BOLT ON CLAMP INSTALLED IN OCTOBER 2003 HAS DEVELOPED A LEAK AT THE SEAM EDGE OF THE CLAMP. THE CLAMP IS INSTALLED ON AN 8" DEAD LEG SECTION OF PIPE. TO ISOLATE THE CLAMPED SECTION OF PIPE THE ENTIRE 737 20" PIPELINE WILL HAVE TO BE ISOLATED AND BLOWDOWN. A REPAIR PROCEDURE WAS DEVELOPED. IN JULY 2012, A SECTION OF THE LINE WAS REMOVED, AND THE REMAINING PIPE SEGEMENT WAS BLINDED OFF. THE PROJECT IS COMPLETE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120025 | 15693 | 2012-03-02 17:09 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | TX | 77002 | 2012-02-07 14:45 | 2012 |  |  | 41.5662 | -85.1674 | 1002399 | 2012-02-07 16:16 |  | NATURAL GAS |  | 500 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-02-07 15:00 | 2012-03-09 12:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 2 | 2012-02-07 14:45 | 2012-02-07 15:00 | ONSHORE | IN | 46761 | LAGRANGE | STEUBEN | MILEPOST | 44.9 | ANR 504 TIE-LINE |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 22 |  | 0.281 | 52000 | API | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COLD APPLIED TAPE | [28 empty] | 1956 | 1956 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 469 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 5000 | 4027.48414376321 | 753000 | 864669.9 | 5000 | 5741.5 | 0 | 0 |  |  | 763000 | 403717.275687104 | 874438.884143763 | [8 empty] | 834 |  | 858 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 79000 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A SMALL LEAK DUE TO AN UNDETERMINED CAUSE. NO CONTROL ROOM ISSUES HAVE BEEN IDENTIFIED AS CONTRIBUTING TO THE EVENT. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) |  | YES | [12 empty] | YES | YES | EXTERNAL BENDING FORCES TO DUE CONTINUED WET/DRY AREAS. | [7 empty] | YES | [62 empty] | YES | YES |  |  | YES |  |  |  | 2006 | [31 empty] | 2006 | [23 empty] | YES | 1975 | 1380 | NO | [13 empty] | YES |  | 2012 |  |  | 2012 |  |  |  | YES |  |  | YES | [51 empty] | LOUIS SALINAS |  |  | 832-320-5305 | 832-320-6305 |  |  |  | LOUIS SALINAS |  | 832-320-5305 | louis_salinas@transcanada.com | ON CALL TCPL EMPLOYEE RECEIVED A CALL FROM GAS CONTROL ADVISING A LANDOWNER HAD CALLED IN REPORTING A BUBBLING NOISE IN THE AREA OF THE PIPELINE. TCPL EMPLOYEES INVESTIGATED AND FOUND A SLOW BUBBLE FORMATION EVERY 3 TO 4 SECONDS WAS OBSERVED CLOSE PROXIMITY TO THE 22 INCH 504 TIELINE LOCATED IN THE LAGRANGE SECTION NEAR ORLAND, INDIANA, EAST OF STATE ROUTE 327 NEAR MILEPOST 45. COMPANY INVESTIGATED FURTHER AND USED INSTRUMENTS TO DETECT A GAS LEAK. FOLLOWING ISOLATION OF THE SEGMENT, THE AREA WAS EXCAVATED AND THE PIPE SEGMENT CONTAINING THE LEAK WAS REMOVED FROM THE PIPELINE. SUBSEQUENTLY, THE COMPANY'S PIPE INTEGRITY GROUP HAS EXAMINED THE FAILED SEGMENT OF PIPE THROUGH METALLURGICAL ANALYSIS AND DISCOVERED THAT THE FAILURE WAS DUE TO A LACK OF FUSION IN THE LONGITUDINAL WELD.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120026 | 15885 | 2012-03-05 14:26 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2012-02-08 05:05 | 2012 |  |  | 40.2186 | -102.6862 | 1002451 | 2012-02-08 09:23 |  | NATURAL GAS |  | 5360 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | REGULATOR RUN ISOLATED AND SHUT IN WHILE REPAIRS WERE MADE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-02-08 07:52 | 2012-02-08 07:52 | ONSHORE | CO | 80759 |  | YUMA | SURVEY STATION NO. | 150/223331 | LINE W/YUMA STATION | YUMA STATION FUEL RUN | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1980 |  | CARBON STEEL |  | OTHER | [8 empty] | THE REGULATOR WAS UNABLE TO HOLD PRESSURE BECAUSE THE PILOT HEATER FAILURE. | CLASS 1 LOCATION | NO |  | 51 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 13453 | 10836.3488372093 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 13453 | 11234.5348837209 | 10836.3488372093 | [8 empty] | 430 |  | 720 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [25 empty] | YES | FAILURE OF PILOT HEATER ON THE REGULATOR CAUSED THE RELEASE OF GAS. | [161 empty] | DAVID COOMES | PIPELINE COMPLIANCE ANALYST | david.coomes@sscgp.com | 270.852.4391 |  |  |  |  | DAVID SINCLAIR | MANAGER OF PIPELINE COMPLIANCE | 270.852.4424 | david.sinclair@sscgp.com | GAS CONTROLLER RECEIVED A CALL FROM THE YUMA STATION OPERATOR AT APPROXIMATELY 0752 CST ON 08 FEB 2012 IN REGARDS TO A RELIEF VALVE BLOWING. THE RELIEF VALVE IS LOCATED DOWNSTREAM OF THE HIGH PRESSURE FUEL GAS REGULATOR 013153R AND UPSTREAM OF THE LOW PRESSURE FUEL GAS REGULATOR 013152R. THE STATION OPERATOR HAD NO INDICATION OF WHEN THE RELIEVE VALVE ACTIVATED. BASED ON THE YUMA MAINLINE PRESSURE PROFILE ON SCADA, INDICATIONS WERE THERE THAT SHOWS THAT THE RELIEF VALVE PROBABLY WAS ACTIVATED APPROXIMATELY AT 0505 ON 08 FEB 2012 AND WAS SHUT-IN AT APPROXIMATELY 0812. AT 0820 CST THE OPERATOR CALLED GAS CONTROL TO INFORM THEM IT THE R.V. HAD GONE OFF DUE TO A FREEZE IN THE REGULATOR RUN. NO ALARMS WERE INDICATED AT YUMA STATION OF ANY POTENTIAL MALFUNCTION. A CALL WAS PLACED TO THE NATIONAL RESPONSE CENTER AT 0923 CST ON 08 FEB 2012. THE NRC CREATED TICKET 1002451 IN RESPONSE TO THIS REPORTING. YUMA STATION HAS A HEAT EXCHANGER THAT WARMS THE GAS BEFORE IT ENTERS THE FUEL RUN. THERE IS ALSO A PILOT HEATER FOR THE REGULATOR INSTALLED. DUE TO THE FACT THAT YUMA STATION WAS OFF LINE THE HEAT FROM BOTH THE HEAT EXCHANGER AND THE PILOT HEATER WERE ONLY WARMING STAGNANT GAS. THE AMBIENT TEMPERATURE AT YUMA AT THE TIME OF THIS INCIDENT WAS APPROXIMATELY 0 DEGREES F. THIS ALLOWED THE MOISTURE INSIDE THE PILOT FOR REGULATOR 13153R TO FEEZE CAUSING THE REGULATOR TO FAIL WHICH ACTIVATED THE R.V.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120027 | 15939 | 2012-03-09 11:15 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | TX | 77002 | 2012-02-12 16:15 | 2012 |  |  | 40.629 | -93.5415 | 1002811 | 2012-02-12 19:00 |  | NATURAL GAS |  | 21000 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-02-12 17:36 | 2012-02-12 19:00 |  |  |  |  | NO |  |  |  |  | NO | [9 empty] | ONSHORE | IA | 50147 | LINEVILLE | WAYNE | MILEPOST | 35 | LINEVILLE COMPRESSOR STATION | LINE 100 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1949 |  | CARBON STEEL |  | OTHER | [8 empty] | STATION ISOLATION VALVE DID NOT FUNCTION PROPERLY. | CLASS 1 LOCATION | NO |  | 506 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 120000 | 96659.6194503171 | 20000 | 22966 | 10000 | 11483 | 0 | 0 |  |  | 150000 | 116024.416490486 | 131108.619450317 | [8 empty] | 875 |  | 975 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | INCORRECT OPERATION AS THE VALVE ACTUATOR WAS NOT MOUNTED ON THE VALVE IN THE CORRECT POSITION AND THAT CAUSED THE VALVE TO MALFUNCTION |  |  | YES |  |  | NORMAL OPERATING CONDITIONS | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | LOUIS SALINAS |  |  | 832-320-5305 | 832-320-6305 |  |  |  | LOUIS SALINAS |  | 832-320-5305 |  | ANR SOUTHWEST LINEVILLE IA COMPRESSOR STATION EXPERIENCED AN ESD EVENT AT 16:42 CST ON FEBRUARY 12. 2012. THE INITIAL CAUSE OF THE ESD IS BELIEVED TO BE A FAILED COPPER TUBING OIL LINE, UNIT 705 THAT CAUSED A FLASH FIRE. THE FIRE DETECTION RESULTED IN THE ESD OF THE COMPRESSOR STATION. DURING THE ISOLATION AND BLOW-DOWN IT WAS DISCOVERED THAT ONE OF THE STATION ISOLATION VALVES DID NOT TRAVEL TO ITS DESIRED ISOLATION POSITION RESULTING IN A REPORTABLE GAS RELEASE. ALSO, IT WAS DISCOVERED THAT THE VALVE ACTUATOR WAS NOT MOUNTED ON THE VALVE IN THE CORRECT POSITION AND THAT CAUSED THE VALVE TO MALFUNCTION. THE VENTING OF GAS WAS STOPPED BY FIELD PERSONNEL AT APPROXIMATELY 17:36. INITIAL CALCULATIONS ESTIMATE APPROXIMATELY 21 MILLION CUBIC FEET OF GAS LOSS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120028 | 16022 | 2012-03-13 08:16 | SUPPLEMENTAL FINAL | 5304 | FLORIDA GAS TRANSMISSION CO | 5051 WESTHEIMER ROAD | HOUSTON | TX | 77056 | 2012-02-13 02:26 | 2012 |  |  | 30.6405 | -91.0162 | 1002823 | 2012-02-13 05:15 |  | NATURAL GAS |  | 2250 | 1290 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-02-13 02:35 | 2012-03-08 19:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-02-13 02:30 | 2012-02-13 03:20 | ONSHORE | LA | 70770 | PRIDE | EAST BATON ROUGE | SURVEY STATION NO. | 319+21 | LAMEB-8 | 8-0 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 54 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 |  | 0.344 | 60000 | API 5LX | DSAW |  | KAISER | OTHER | BUCOTE - BUTADIENE STYRENE COATING SYSTEM | [27 empty] | 1966 | 1965 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 528 | 60 |  | CLASS 1 LOCATION | NO |  | 647 |  | NO | NO | NO |  | 3000 | 3444.9 | 3225 | 3703.2675 | 5625 | 4530.91966173362 | 10000 | 11483 | 450000 | 516735 | 0 | 0 |  |  | 471850 | 250444.607647992 | 539897.087161734 | [8 empty] | 965 |  | 976 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | AUTOMATIC | 72494 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  | YES | THE PROMPT ACTION BY THE CONTROLLERS INDICATED THAT FATIGUE WAS NOT AN ISSUE. | YES | YES | [7 empty] | YES | 3 | 0 | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES | YES |  |  | YES | YES | 1966 | YES | YES | YES | YES |  |  | 2011 | 2003 |  |  | YES | [190 empty] | YES | YES |  |  | YES |  |  |  | 2005 | [31 empty] | 2005 | [23 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | ON 2/13/2012 AT 2:30 A.M. FGT GAS CONTROL CONTACTED THE ZACHARY STATION ON-CALL EMPLOYEE THAT ONE OF THE STATION'S COMPRESSOR ENGINES WENT OFFLINE. WHILE GAS CONTROL WAS STILL CONVERSING WITH THE ON-CALL EMPLOYEE, 2 MORE COMPRESSORS WENT OFFLINE AND A PRESSURE DROP WAS NOTED. ONE OF THE FGT STATION EMPLOYEES THAT LIVES IN THE VICINITY NOTIFIED GAS CONTROL AT 2:33 A.M. THAT HE HEARD A LOUD NOISE IN THE GENERAL AREA OF THE PIPELINE AND THAT HE WAS RESPONDING. INTERNAL COMPANY NOTIFICATIONS WERE MADE AND RESPONSE WAS INITIATED. THE ZACHARY STATION OPERATIONS MANAGER CONFIRMED THE LINE RUPTURE UPON ARRIVING AT THE PEAIRS ROAD LOCATION. THE PRIDE VOLUNTEER FIRE DEPARTMENT, EAST BATON ROUGE FIRE DEPARTMENT, EAST BATON ROUGE SHERRIFF'S DEPARTMENT AND THE LOUISIANA STATE POLICE WERE ALREADY ONSITE WHEN THE FGT OPERATIONS MANAGER ARRIVED. SHORTLY AFTER ARRIVAL VERBAL AGENCY NOTIFICATIONS WERE MADE TO LSP/LDEQ SPOC HOTLINE. SUBSEQUENT DISCUSSIONS WITH SERGEANT WILLIAM HUNTER OF THE LOUISIANA STATE POLICE ON 2/14/2012, REVEALED THAT NO MANDATORY EVACUATIONS OR OFFICIAL ROAD CLOSURES HAD BEEN INITIATED. DUE TO THE RUPTURE, THE LINE PRESSURE DROP INITIATED THE CLOSURE OF AUTOMATIC VALVE MLV8-1A. THE VALVE CLOSURE STOPPED THE HIGH-PRESSURE GAS LOSS. HOWEVER, BEFORE INITIATION OF REPAIRS ADDITIONAL MEASURES WERE EMPLOYED TO INSURE 0% GAS AT THE LOCATION. PHMSA REQUESTED THAT FGT ADD THE YEAR OF THE LAST TEST POINT SURVEY TO THIS REPORT, ALTHOUGH THE NEAREST TEST POINT WAS NOT CLOSE TO THE POINT OF THE INCIDENT. ALSO ADDED THAT A METALURGICAL REPORT CONFIRMED EXTERNAL CORROSION. **THIS REPORT IS BEING SUBMITTED IN RESPONSE TO PHMSA'S REQUEST FOR SUPPLEMENTAL REPORTS FROM OPERATORS WHO SUBMITTED REPORTS FOR INCIDENTS OCCURRING AFTER JANUARY 1, 2010, WITH ANY OF THE FOLLOWING: (1) ``PIPE GIRTH WELD'' WAS SELECTED AS THE ``ITEM INVOLVED IN INCIDENT'' IN PART C3 OF THE REPORT. THE REVISED REPORT COLLECTS DATA ABOUT THE PIPE ADJACENT TO THE GIRTH WELD. (2) ``FUNCTION OF PIPELINE SYSTEM'' IS NULL IN PART E5F OF THE REPORT. THE REVISED REPORT COLLECTS THE FUNCTION OF THE PIPELINE SYSTEM FOR ALL INCIDENTS. THIS REPORT HAS NO FURTHER UPDATES AND IS BEING SUBMITTED AS A FINAL.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120029 | 16041 | 2012-03-14 16:01 | SUPPLEMENTAL FINAL | 19730 | TRUNKLINE GAS CO | 5051 WESTHEIMER ROAD | HOUSTON | TX | 770565306 | 2012-03-06 07:45 | 2012 |  |  | 29.6954 | -91.3564 | 1004924 | 2012-03-06 10:22 |  | NATURAL GAS |  | 900 | 0 | 0.01 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-03-06 07:45 | 2012-03-06 09:25 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-03-06 07:45 | 2012-03-06 07:45 | ONSHORE | LA | 70392 | PATTERSON | ST. MARY | MILEPOST | VALVE STATION | PATTERSON COMPRESSOR STATION | PATTERSON STA. #314 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | INSTRUMENTATION | [38 empty] | 1978 |  | CARBON STEEL |  | OTHER | [8 empty] | THE PATTERSON COMPRESSOR STATION EXPERIENCED AN EMERGENCY SHUT DOWN (ESD). DURING THE ESD, A SMALL AMOUNT OF TURBINE OIL WAS RELEASED TO THE ATMOSPHERE. THE TURBINE OIL SETTLED ON PRIVATE PROPERTY TO THE NORTH WEST OF THE PATTERSON COMPRESSOR STATION. SOME OF THIS TURBINE OIL SETTLED ON US HIGHWAY 90 AND IMPACTED SEVERAL VEHICLES THAT WERE ON THE HIGHWAY. SEVERAL HOMES NORTH OF US HIGHWAY 90 WERE ALSO IMPACTED BY THE TURBINE OIL. | CLASS 1 LOCATION | NO |  | 717 |  | NO | YES | NO |  | 0 | 0 | 0 | 0 | 1989 | 1602.13319238901 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1989 | 1661.00422832981 | 1602.13319238901 | [8 empty] | 1050 |  | 1200 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT HAPPENED WHILE FIELD PERSONNEL WERE CONDUCTING AN OPERATIONAL TASK AT THE LOCATION. CONTROLLERS WERE NOT INVOLVED. | [12 empty] | YES | 11 | 0 | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | IN PREPARATION FOR A NATURAL GAS PIPELINE PIG RUN, A STATION TURBINE WAS BROUGHT ONLINE TO ACCOMMODATE FLOW AND PRESSURE NEEDS ASSOCIATED WITH THE PIGGING OPERATION. UPON BRINGING THE TURBINE ONLINE, HIGHER PRESSURE WAS SENSED ON ONE SIDE OF THE STATION QUICK VENT STAND. THE PRESSURE WAS SENSED RAPIDLY AND COULD NOT EQUALIZE BEFORE AN AUTOMATED ESD OCCURRED. THE ESD SYSTEM IS DESIGNED TO ACTIVATE UPON SENSING SUCH A PRESSURE DIFFERENTIAL, THEREFORE THE ESD SYSTEM FUNCTIONED AS DESIGNED. | [147 empty] | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | AT THE TIME OF THE ESD, NATURAL GAS VENTED, AND TURBINE OIL ACCUMULATED IN THE PIPING DISCHARGED INTO THE AIR. BECAUSE AUTOMATED ESD RELEASES RESULT IN THE RAPID RELEASE OF PRESSURIZED NATURAL GAS, THE TURBINE OIL BECAME ATOMIZED AND TRAVELED OFFSITE SETTLING TO THE NORTH AND WEST OF THE FACILITY ALONG US HIGHWAY 90 AND LA HIGHWAY 182. DURING THE MIGRATION OFFSITE, THE TURBINE OIL IMPACTED VEHICLES TRAVELING ON US HIGHWAY 90 RESULTING IN VEHICLES PULLING OFF OF THE HIGHWAY ONTO THE HIGHWAY SHOULDER. AS A RESULT, ONE COLLISION OCCURRED. THE ST. MARY PARISH SHERRIFF?S DEPARTMENT AND THE LSP WERE PRESENT ON SCENE SHORTLY AFTER. TGC?S SPILL RESPONSE CONTRACTOR WAS CONTACTED AT APPROXIMATELY 8:53 A.M. ON 3/6/12 FOR INCIDENT IMPACT ASSESSMENT AND RESPONSE ASSISTANCE. SUBSEQUENT TO THE INCIDENT, TWO PRIVATE CITIZENS NOTIFIED TGC THEY SOUGHT MEDICAL ATTENTION AT NEARBY HOSPITALS. THEY WERE RELEASED SHORTLY AFTER TREATMENT. INCIDENT DID NOT MEET THE TYPICAL CRITERIA FOR REPORTING. REPORTING WAS INITIATED, SINCE TGC CONSIDERED THIS A "SIGNIFICANT EVENT". **THIS REPORT IS BEING SUBMITTED IN RESPONSE TO PHMSA'S REQUEST, (DOCKET ID PHMSA-2013-0028), FOR SUPPLEMENTAL REPORTS FROM OPERATORS WHO SUBMITTED REPORTS FOR INCIDENTS OCCURRING AFTER JANUARY 1, 2010, WITH ANY OF THE FOLLOWING: (1) ``PIPE GIRTH WELD'' WAS SELECTED AS THE ``ITEM INVOLVED IN INCIDENT'' IN PART C3 OF THE REPORT. THE REVISED REPORT COLLECTS DATA ABOUT THE PIPE ADJACENT TO THE GIRTH WELD. (2) ``FUNCTION OF PIPELINE SYSTEM'' IS NULL IN PART E5F OF THE REPORT. THE REVISED REPORT COLLECTS THE FUNCTION OF THE PIPELINE SYSTEM FOR ALL INCIDENTS.** PART E5F OF THIS REPORT HAS BEEN COMPLETED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120031 | 15778 | 2012-03-23 15:28 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION CORP | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2012-02-29 08:10 | 2012 |  |  | 41.1688 | -83.0289 | 1004355 | 2012-02-29 13:38 |  |  |  | 4782.5 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-02-29 10:15 | 2012-03-01 10:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 4 |  |  | ONSHORE | OH | 44867 | REPUBLIC | SENECA | MILEPOST | VS-1512 | LINE D-100 |  | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | VENT PIPE |  |  | CARBON STEEL |  | OTHER | [8 empty] | AN ASPHALT TRUCK ROLLED OVER AND CAUGHT FIRE DAMAGING THE ABOVEGROUND VENT PIPE, RISERS THAT ARE OWNED AND OPERATED BY TWO OTHER OPERATORS. ASPHALT WAS LEAKING ONTO THE ROAD AND CAUGHT FIRE. THIS HAD EXTENDED THE LENGTH OF TIME FOR THE FIRE TO START TO FLAME OUT. | CLASS 1 LOCATION | NO |  | 307 |  | YES | NO | NO |  | 0 | 0 | 0 | 0 | 12721 | 10246.7251585624 | 4551 | 5225.9133 | 0 | 0 | 0 | 0 |  |  | 17272 | 13022.077343129 | 15472.6384585624 | [8 empty] | 390 |  | 495 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [260 empty] | GEORGE HAMATY | ENGINEER | ghamaty@nisource.com | 3043573728 | 3043573804 |  |  |  | PERRY MICHAEL HOFFMAN | MANAGER | 3043572548 | mikehoffman@nisource.com | AN ASPHALT TRUCK TRAVELING ON CR-38 IN SENECA COUNTY, NEAR THE TOWN OF REPUBLIC, OH. THE TRUCK WAS CARRYING ASPHALT AND UPON ROLLING OVER IT CAUGHT FIRE. IT HAPPENED THAT THIS VEHICLE ROLL-OVER TOOK PLACE NEAR A GAS BEARING FACILITY WHERE IT DAMAGED A RISER AND ANOTHER VENT PIPE. THE FACILITY WAS ISOLATED AND SECURED FOR PUBLIC SAFETY. THE FIRST RESPONDERS CONTACTED THE EMERGENCY OFFICIALS WHO SECURED THE COUNTY ROAD AND HELPED THE NEIGHBORING RESIDENCE TO EVACUATE UNTIL THE FLAME DID SUBSIDE AND TO SECURE THE AREA. REPAIRS WERE MADE TO THE FACILITY AND THE SYSTEM PRESSURE WAS RESTORED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120032 | 15763 | 2012-03-29 08:31 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2012-03-10 12:40 | 2012 |  |  | 42.393 | -92.327 | 1005340 | 2012-03-10 16:38 |  | NATURAL GAS |  | 3607 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | ONLY THE UNIT WITH THE RELIEF VALVE BLOWING WAS SHUT DOWN | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-03-10 12:40 | 2012-03-10 13:40 | ONSHORE | IA | 50701 | WATERLOO | BLACKHAWK | SURVEY STATION NO. |  | WATERLOO, IOWA COMPRESSOR STATION IA-067 | COMPRESSOR UNIT # 2 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1975 |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENTIONAL RELEASE OF NATURAL GAS WAS FROM UNIT # 2 RELIEF VALVE WHICH HAD OPENED. | CLASS 1 LOCATION | NO |  | 86 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 10279 | 8279.70190274841 | 0 | 0 | 200 | 229.66 | 0 | 0 |  |  | 10479 | 8689.36291754757 | 8509.36190274841 | [8 empty] | 946 |  | 960 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SYSTEM AND EQUIPMENT WERE ALL OPERATING NORMAL AND BELOW MAOP WHEN RELIEF VALVE OPENED, WHICH CONTROLLERS DO NOT HAVE DIRECT OPERATIONAL CONTROL OVER. SET POINTS ARE SET BY FIELD OPERATIONS PERSONNEL. THERE WERE NO SPECIFIC PRESSURE/FLOW ANOMALIES IDENTIFED PRIOR TO THE EVENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | PULSATION IN DISCHARGE PIPING CAUSED ACTIVATION OF RELIEF VALVE | [161 empty] | BYRON H WOOD | SR. PIPELINE SAFETY SPECIALIST - PIPELINE SAFETY | byron.wood@nngco.com | 402-398-7396 |  |  |  |  | THOMAS CORRELL | SR. DIRECTOR PIPELINE SAFETY AND RISK | 402-398-7715 | thomas.correll@nngco.com | ON MARCH 10, 2012, NORTHERN'S OPERATIONS COMMUNICATION CENTER & GAS CONTROL RECEIVED A CALL FROM A NEIGHBOR NEAR THE WATERLOO, IOWA COMPRESSOR STATION STATING THAT HE THOUGHT HE COULD HEAR GAS BLOWING AT THE COMPRESSOR STATION. GAS CONTROL IMMEDIATELY CONTACTED THE WATERLOO, IOWA COMPRESSOR PLANT TEAM ON-CALL PERSON. THE ON-CALL PERSON WAS AWARE THAT ON THURSDAY, MARCH 8, 2012, THE TEAM PERSONNEL HAD INSPECTED AND TESTED COMPRESSOR UNIT # 2'S DISCHARGE RELIEF VALVE AND HAD RESET IT FROM A PRESSURE OF 1,030 PSIG TO A SET POINT PRESSURE OF 999 PSIG. DUE TO CONCERNS THAT UNIT DISCHARGE PRESSURE PULSATIONS COULD IMPACT THE RELIEF VALVE AND CAUSE IT TO BLOW PREMATURELY, THE TEAM ALSO HAD TESTED THE PULSATION IMPACT ON THE RELIEF ON MARCH 8, 2012, BY PUTTING UNIT 2 ON-LINE AND RUNNING THE DISCHARGE PRESSURE TO 958 PSIG, WHICH IS 2 PSIG BELOW THE 960 PSIG MAOP, AND THEY DID NOT HAVE ANY PROBLEMS WITH THE RELIEF VALVE BEING ACTIVATED. AS THE ON-CALL PERSON WAS AWARE OF THE PREVIOUS WORK AND CHANGES TO THE RELIEF VALVE HE WAS FAIRLY CERTAIN THAT THIS COULD BE THE CAUSE OF THE BLOWING GAS SO HE REQUESTED THAT GAS CONTROL REMOTELY SHUTDOWN UNIT # 2. UPON ARRIVAL AT THE PLANT THERE WAS NO GAS BLOWING. A REVIEW OF THE HISTORICAL PRESSURE TRENDS ON THE LOCATION HMI INDICATED THAT THE RELIEF VALVE STARTED TO VENT AT APRPOXIAMTELY 946 PSIG, WHICH IS WELL BELOW THE 999 PSIG SET POINT, AND ALSO WELL BELOW THE MAOP OF 960 PSIG. WHEN INSPECTING AND CHANGING THE SET POINT LOCATION PERSONNEL WERE AWARE THAT THE RELIEF VALVE WAS EQUIPPED WITH AN ANDERSON GREENWOOD AGCO PRESSURE SPIKE SNUBBER.IT WAS BELIEVED THAT THIS WOULD PREVENT PREMATURE ACTIVATION OF THE RELIEF VALVE. ADDITIONAL REVIEW INDICATED THAT THE UNITS WERE BEING OPERATED AT A REDUCED RATE OF SPEED AND LOAD AND THIS UNDOUBTEDLY CONTRIBUTED TO DISCHARGE PRESSURE PULSATIONS, SURGES AND SPIKES THAT WERE OUTSIDE OF THE OPERATIONAL CAPABILITY OF THE AGCO PRESSURE SNUBBER TO DAMPEN. ON MONDAY, MARCH 12, 2012 THE TEAM INSPECTED, RESET AND TESTED THE RELIEF VALVE AT A SET POINT OF 1,030 PSIG AND THE UNIT WAS PUT BACK INTO OPERATIONAL SERVICE. THE LOCATION IS DISCUSSING WITH THE EQUIPMENT VENDOR WHETHER THERE IS OPTIONS ON OTHER DEVICES THAT THEY MAY HAVE FOR INSTALLATION ON THE RELIEF VALVE THAT WOULD ALLOW FOR OPERATION AS AT A PRESSURE SET POINT OF 999 PSIG. THIS REPORT IS BEING FILED AS IT WAS DETERMINED THAT THE TOTAL GAS RELEASED BY THE RELIEF VALVE OPENING EXCEEDED THE THREE MILLION CUBIC FEET REPORTING THRESHOLD. NO FURTHER ACTIONS AS PENDING OR ARE REQUIRED AT THIS TIME SO THIS REPORT IS BEING CONSIDERED AS THE ORIGINAL/FINAL REPORT FOR THIS EVENT. 10/09/2012 A SUPPLEMENTAL/FINAL REPORT WAS FILED ON REPORT # 20120032-15474 DATED 03/29/2012 AS A FOLLOW UP TO RECOMMENDATIONS FROM A PHMSA REVIEW. ITEMS 6, 19A, PART C ITEM 3 AND 4 WERE REVISED. SUPPLEMENTAL/FINAL: UPDATE REPORT PER PHMSA REQUEST PART E5F BY INDICATING TRANSMISSION ON REPORT 20120032 DATED 3/29/2012.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120035 | 15819 | 2012-04-05 16:49 | SUPPLEMENTAL FINAL | 18608 | STANDARD PACIFIC GAS LINE INC | PG&E GAS OPS COMPLIANCE 6111 BOLLINGER CANYON RD | SAN RAMON | CA | 94583 | 2012-03-08 11:45 | 2012 |  |  | 38.0042 | -122.0884 | 1005245 | 2012-03-08 11:00 |  | NATURAL GAS |  | 5 | 395 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-03-09 00:30 | 2012-03-09 14:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-03-08 11:45 | 2012-03-08 11:45 | ONSHORE | CA | 94553 | MARTINEZ | CONTRA COSTA COUNTY | MILEPOST | 181.42 | SP3 |  | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 72 |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | DRAIN LINES | [40 empty] | CARBON STEEL |  | MECHANICAL PUNCTURE | 0.5 | [8 empty] | CLASS 3 LOCATION | YES | METHOD2 | 359 |  | NO | NO | NO |  | 0 | 0 | 3200 | 3674.56 | 0 | 0 | 60000 | 68898 | 0 | 0 | 0 | 0 |  |  | 63200 | 33312.72 | 72572.56 | [8 empty] | 400 |  | 468 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS CAUSED BY AN AT-FAULT DIG-IN; CONTROLLS AND CONTROL ROOM ISSUES DID NOT PLAY A PART. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | [10 empty] | NO |  |  |  |  | YES | [6 empty] | UTILITY | BACKHOE/TRACKHOE | NATURAL GAS | YES | 56229 | USA NORTH | UTILITY OWNER | YES | YES | YES | 14 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO USE HAND TOOLS WHERE REQUIRED | [263 empty] | LAURENCE DENISTON | SR. PROGRAM MANAGER | lcd1@pge.com | 925 974 4313 |  |  |  |  | BILL GIBSON | DIRECTOR REGULATORY COMPLIANCE AND SUPPORT | 925 974 4210 | wlg3@pge.com | AT APPROXIMATELY 1145 HOURS ON MARCH 8, 2012, A GENERAL CONSTRUCTION (GC) GAS CREW, STRUCK A 3/4-INCH STEEL GAUGE LINE ON SP3 AT MP 181.42 WHILE EXCAVATING TO EXPOSE AND REPAIR A VALVE RESULTING IN A RELEASE OF GAS. THE EXCAVATION WAS INSIDE A STATION. THE FLOW OF GAS WAS STOPPED AT 0030 HOURS ON 3/9/12. THE 24-INCH MAIN WAS MARKED AND LOCATED (USA # 056229) BEFORE CONSTRUCTION STARTED THE JOB. THERE WERE NO INJURIES, FATALITIES, NO IGNITION AND NO MEDIA PRESENT. THIS BECAME REPORTABLE AT APPROXIMATELY 0930 HOURS ON MARCH 9, 2012 WHEN IT WAS DETERMINED THAT THE COST OF THE REPAIRS WILL BE IN EXCESS OF $50K. ONE CUSTOMER LOST SERVICE AS A RESULT OF THIS INCIDENT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120037 | 16137 | 2012-04-12 15:54 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2012-03-23 15:45 | 2012 |  |  | 28.5383 | -91.665 | 1006716 | 2012-03-23 16:45 |  | NATURAL GAS |  | 413 | 4980 | 50 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-03-23 17:18 | 2012-04-07 16:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-03-23 15:45 | 2012-03-24 11:24 | OFFSHORE | [28 empty] | 150 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EUGENE ISLAND | 241 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | WELD/FUSION |  | 24 |  | 0.438 | 60000 | API 5LX | DSAW |  | US STEEL | COAL TAR | [9 empty] | PIPE GIRTH WELD | [18 empty] | 1975 | 1975 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 585 |  | NO | NO | NO |  | 0 | 0 | 9960 | 11437.068 | 826 | 665.340380549683 | 1114825 | 1280153.5475 | 50000 | 57415 | 0 | 0 |  |  | 1175611 | 619918.96208351 | 1349670.95588055 | [8 empty] | 914 |  | 1250 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 25872 | NO | YES | [6 empty] | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | ANOTHER PIPELINE OPERATOR'S LOCAL PERSONNEL |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURES WERE WITHIN NORMAL OPERATING RANGES; NO ABNORMAL EXCURSIONS. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [8 empty] | YES | WELD DEFECT DURING ORIGINAL CONSTRUCTION. | [13 empty] | YES | [62 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | ZACHARY RAGAIN | ENGINEER - PIPELINE | zachary_ragain@kindermorgan.com | 7134206633 | 7134206633 |  |  |  | ZACHARY RAGAIN | ENGINEER - PIPELINE | 7134206633 | zachary_ragain@kindermorgan.com | ANR PIPELINE COMPANY PERSONNEL NOTIFIED TENNESSEE GAS PIPELINE (TGP) PERSONNEL OF A SHEEN MEASURING 3 MILES LONG AND 1/4 MILE WIDE IN THE VICINITY OF TGP'S 24" 523M-3700 PIPELINE ON THE OCS IN EUGENE ISLAND BLOCK 241. TGP INVESTIGATED AND OBSERVED THE SHEEN WITH BUBBLES. DISPATCHED DIVERS DETERMINED THAT TGP'S LINE WAS LEAKING THROUGH A PINHOLE IN A GIRTH WELD. THE LEAK WAS REPAIRED BY INSTALLING A CLAMP AND THE PIPELINE WAS PLACED BACK INTO SERVICE. YEAR OF PIPE MANUFACTURE IS ASSUMED TO BE COMMENSURATE WITH YEAR OF INSTALLATION
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120038 | 16963 | 2012-04-13 15:40 | SUPPLEMENTAL FINAL | 15329 | PEOPLES GAS LIGHT & COKE CO | 200 E RANDOLPH STREET | CHICAGO | IL | 60601 | 2011-12-01 14:30 | 2011 |  |  | 41.6681 | -87.5586 | 996953 | 2011-12-01 17:15 |  | NATURAL GAS |  | 1750 | 16.89 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-12-01 20:45 | 2011-12-07 22:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-12-01 14:30 | 2011-12-01 14:45 | ONSHORE | IL | 60633 | CHICAGO | COOK | SURVEY STATION NO. | 90+70.2 | CAL #3 | SEGMENT #9 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 60 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 2 |  | 0.218 | 35000 | UNKNOWN | SEAMLESS |  | UNKNOWN | COLD APPLIED TAPE | [28 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 2 | 2 |  | CLASS 3 LOCATION | YES | METHOD1 | 28 |  | NO | NO | NO |  | 0 | 0 | 79 | 92.4349908294273 | 8200 | 5549.20071047957 | 65000 | 76054.1063786427 | 38000 | 44462.4006521296 | 0 | 0 |  |  | 111279 | 61115.7952240266 | 126158.142732081 | [8 empty] | 270 |  | 287 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 200 | NO | [5 empty] | YES | DOES NOT APPLY. RELEASE FROM A 2" DIAMETER SERVICE STUB OFF THE TRANSMISSION LINE. | YES |  |  |  |  | YES | DOES NOT APPLY. 2" DIAMETER SERVICE STUB | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EXCAVATION DAMAGE WAS THE CAUSE OF THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [10 empty] | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 181429599 | DIGGER CHICAGO UTILITY NETWORK | UTILITY OWNER | YES | NO | NO |  | LOCATING PRACTICES NOT SUFFICIENT |  | INCORRECT FACILITY RECORDS/MAPS | [264 empty] | SHAWN BARTELS | COMPLIANCE SPECIALIST | srbartels@peoplesgasdelivery.com | (312)240-5421 |  |  |  |  | TOM WEBB | COMPLIANCE MANAGER | (312)240-4650 | tjwebb@peoplesgasdelivery.com | WHILE PERFORMING INTEGRITY MANAGEMENT ASSESSMENT WORK ON A 36" DIAMETER TRANSMISSION LINE, AN UNMARKED AND UNMAPPED 2" DIAMETER SERVICE LINE STUB WAS DAMAGED BY EXCAVATION EQUIPMENT RESULTING IN RELEASE OF GAS ON THE 2" STUB. THE INCIDENT IMPACTED MORE THAN THE 2" SERVICE LINE. THE 2" TAP ON THE 36" TRANSMISSION LINE WAS IMPACTED, AND THE OPERATING PRESSURE OF THE TRANSMISSION LINE HAD TO BE REDUCED, AND A PORTION TAKEN OUT OF SERVICE TO REPLACE A SECTION OF THE 36" TRANSMISSION LINE. THIS INCIDENT REPORT WAS ORIGINALLY FILED AS A DISTRIBUTION INCIDENT UNDER REPORT # 20110400-15372 FILED ON 12/22/2011. DETREMINATION WAS MADE TO REFILE THIS INCIDENT AS A TRANSMISSION LINE INCIDENT REPORT FOR THE RECORD. A REQUEST FOR RETRACTION OF THE DISTRIBUTION INCIDENT REPORT WILL BE SENT TO PHMSA. DECEMBER 16, 2015 UPDATE: AT THE REQUEST OF PHMSA, PGL HAS AGAIN LOOKED INTO IDENTIFYING THE YEAR THAT THE ITEM INVOLVED IN THE INCIDENT WAS INSTALLED. THE EXACT YEAR THAT THE 2" DIAMETER SERVICE LINE WAS INSTALLED COULD NOT BE DETERMINED SO IS HAS BEEN MARKED AS "UNKNOWN" IN THE FORM.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120039 | 15694 | 2012-04-17 17:21 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | TX | 77002 | 2012-03-21 06:15 | 2012 |  |  | 28.5306 | -90.98 | 1006394 | 2012-03-21 07:59 |  | NATURAL GAS |  | 5000 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-03-21 08:00 | 2012-07-06 12:00 |  |  |  |  | NO |  |  |  |  | NO | [7 empty] | 2012-03-21 06:15 |  | OFFSHORE | [28 empty] | 108 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SHIP SHOAL | 204 | SPLASH ZONE OF RISER | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12.75 |  | 0.375 | 46000 | API | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | AMERICAN STEEL | OTHER | UNKNOWN | [27 empty] | 1970 | 1970 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 312 |  | NO | NO | NO |  | 0 | 0 | 20000 | 22966 | 20000 | 16109.9365750529 | 202000 | 231956.6 | 5000 | 5741.5 | 0 | 0 |  |  | 247000 | 136353.602748414 | 276774.036575053 | [8 empty] | 762 |  | 1300 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 8659 | NO |  |  |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | THE PRODUCER AT THE PLATFORM CALLED OUR FIELD OFFICE TO NOTIFY US OF THE LEAK. |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  |  | YES | [7 empty] | YES |  |  |  | NO | [11 empty] | YES | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | LOUIS SALINAS |  | louis_salinas@transcanada.com | 832-320-5305 | 832-320-6305 |  |  |  | LOUIS SALINAS |  | 832-320-5305 | louis_salinas@transcanada.com | THE PRODUCER OPERATOR AT SHIP SHOAL 204 CALLED IN TO REPORT A LEAK ON THE INCOMING ANR RISER. AFTER REPEATED CALLS BACK TO THE PRODUCER AND GETTING A PHOTOGRAPH FROM THE LOCATION, IT WAS ESTABLISHED THAT THE LEAK WAS ON THE INCOMING 12" 763 LATERAL. THE ATMOSPHERIC LEAK IS 9 FEET ABOVE THE WATERLINE UNDER A PIPE SUPPORT CLAMP WELDED TO THE LEG OF THE PLATFORM. THE ACCOUNT FROM THE PRODUCERS STATES THERE ARE NO ENVIRONMENTAL OR SAFETY ISSUES AT THIS TIME. THE PIPELINE WAS IMMEDIATELY ISOLATED WITH NOTIFICATIONS TO GAS CONTROL AND COMPLIANCE. REPAIR PLAN: ANR PIPELINE HAS SHUT IN ITS 12-IN. PIPELINE AND ALL PRODUCTION SOURCES UPSTREAM OF SS 204 BECAUSE OF A LEAK IN THE LINE. THE LEAK, ASSUMED TO BE THE RESULT OF CORROSION, IS ON THE 12-IN. RISER UNDER A RISER CLAMP AT THE +9 LEVEL. THIS ELEVATION IS A CRITICAL COMPONENT OF THE REPAIR. A REPAIR PLAN HAS BEEN DEVELOPED, WHICH INCLUDES THE INSTALLATION OF AN ENGINEERED, FULLY-WELDED SLEEVE. THE SLEEVE HAS NOW BEEN RECEIVED. WITH THE ADDITION OF THE SLEEVE, THE EXISTING RISER CLAMP HAS TO BE MODIFIED. FABRICATION OF THE NEW CLAMP WAS COMPLETED. A PRE-JOB WAS HELD WITH THE CONTRACTOR ON MAY 1. THE CONTRACTOR MADE FINAL PREPARATIONS FOR MOBILIZATION. MOBILIZATION WAS TARGETED FOR MAY 7, PENDING FAVORABLE WEATHER CONDITIONS. BECAUSE OF WEATHER DELAYS AND OTHER CONSTRUCTION AND FABRICATION DIFFICULTIES, THE REPAIR OF THE LINE WAS NOT COMPLETED UNTIL JULY 6, 2012.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120040 | 16890 | 2012-04-18 11:10 | SUPPLEMENTAL FINAL | 19570 | WILLIAMS GAS PIPELINE - TRANSCO | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2012-04-02 02:00 | 2012 |  |  | 40.798 | -74.0166 | 1007578 | 2012-04-02 03:00 |  |  |  | 0 | 2677 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-04-02 19:46 | 2012-04-06 13:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-04-02 02:00 | 2012-04-02 02:00 | ONSHORE | NJ | 07047 | NORTH BERGEN | HUDSON | MILEPOST | 2.5 | 72 ND STREET LATERAL | 72 ND STREET LATERAL | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 48 |  | YES |  |  |  |  | YES | BORED/DRILLED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 36 |  | 0.5 | 52000 | API5L | DSAW |  | BETHLEHAM CORP. | ASPHALT | [28 empty] | 1959 | 1959 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | YES | METHOD2 | 647 |  | NO | NO | NO |  | 0 | 0 | 5467 | 6277.7561 | 0 | 0 | 280000 | 321524 | 0 | 0 | 15000 | 17224.5 | FINAL COSTS UPDATED 7-25-12 |  | 300467 | 158376.1557 | 345026.2561 | [8 empty] | 273 |  | 350 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | AUTOMATIC | 19430 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATOR EMPLOYEES WERE ON SITE OF AN INVESTIGATIVE ANAMOLY DIG, AS THE SOIL AROUND THE PIPE WAS BEING REMOVED THE LEAK WAS DISCOVERED.THE LEAK PROMPTED THE OPERATOR TO TAKE THE PIPELINE OUT OF SERVICE FOR REPAIR. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | PREVIOUS MECHANICAL DAMAGE NOT RELATED TO EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | PREVIOUS MECHANICAL DAMAGE | [103 empty] | PREVIOUS MECHANICAL DAMAGE NOT RELATED TO EXCAVATION | [116 empty] | YES | YES |  |  | YES |  |  |  | 2011 | [31 empty] | 2011 | [22 empty] | NO | YES | 1959 | 990 | NO | [13 empty] | YES |  |  | 2012 | 2012 | [5 empty] | YES | YES | [52 empty] | JOHNNY LOPEZ | PIPELIE SAFETY SPECIALIST | johnny.lopez@williams.com | 7132152995 | 7132152222 |  |  |  | MARIE SOTAK | PIPELINE SAFETY MANAGER | 7132152111 | marie.sotak@williams.com | OPERATOR EMPLOYEES AND THIRD PARTY CONTRACTORS WERE ON SITE OF AN ANOMALY INVESTIGATION DIG, OPERATOR EMPLOYEES WERE REMOVING SOIL AROUND THE PIPELINE WHEN OPERATOR EMPLOYEES SMELLED AN ODOR COMING FROM THE ANAMOLY PIE. THE PIPELINE WAS TAKEN OUT OF SERVICE AND AN INVESTIGATION WAS INITIATED . THE RESULTS OF THE LEAK INVESTIGATION SHOWED A DENT ON THE PIPE DUE TO A ROCK UNDERNEATH THE PIPE. THE ROCK UNDERNEATH THE PIPE WAS THE CAUSE OF A SMALL CRACK WHERE THE LEAK INITIATED. THE PIPE ANAMOLY SEGMENT WAS CUTOUT AND REPLACED WITH NEW PIPE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120041 | 33436 | 2012-04-24 18:07 | SUPPLEMENTAL FINAL | 31978 | ATMOS PIPELINE - TEXAS | 5420 LBJ FREEWAY, SUITE 1800 | DALLAS | TX | 75240 | 2012-03-27 10:48 | 2012 | CENTRAL | YES | 31.4849 | -96.9573 | 1007007 | 2012-03-27 11:13 |  | NATURAL GAS |  | 1020 | 1405 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2012-03-27 10:58 |  | YES | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2012-03-27 10:58 | VALVE CLOSURE |  | 2012-03-27 10:58 | 0 | 2012-03-27 10:48 | 2012-03-27 10:48 | ONSHORE | TX | 76682 | RIESEL | MCLENNAN | SURVEY STATION NO. | 466+82 | ATMOS PIPELINE - TEXAS | L8 (3RD) | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12.75 | NO | 0.25 | 36400 | B35 | LAP WELDED |  | UNKNOWN | COAL TAR |  | YES | [26 empty] | 1952 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 40 | 2.5 |  | CLASS 1 LOCATION | NO |  | 197 |  | NO | NO |  |  | 0 | 0 | 2859 | 3282.9897 | 2076 | 1672.21141649049 | 16250 | 18659.875 | 2781 | 3193.4223 | 80000 | 91864 | DAMAGED SMFL + GMFL ILI TOOL | 2.0351 | 103966 | 55439.8765052854 | 118672.49841649 | 0 | 0 | 0 | 0 | NO |  |  |  | 430 | 12 | 500 | 192.619(A)(2) |  | 1952-07-19 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 53377 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATIONS PERSONNEL HAD PIPELINE CONFIGURED FOR PERFORMING PIGGING OPERATIONS AT TIME OF INCIDENT AND WERE ON SITE | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES | [7 empty] | YES | MISALIGNMENT | [17 empty] | YES |  |  |  | 540 | [54 empty] | YES | YES |  |  | YES |  |  |  | 2011 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [27 empty] | 2010 | FREE SWIMMING | HIGH RESOLUTION |  | INSIDE ILI CUPS | [19 empty] | NO |  |  | NO | [13 empty] | NO | [41 empty] | YES | [21 empty] | TOMMY A. CLARK | OPERATIONS SUPERVISOR | tommy.clark@atmosenergy.com | 254-662-7434 | 254-662-7400 |  |  |  | MARLO SUTTON | VP OF TECHNICAL SERVICES | 214-206-2033 | marlo.sutton@atmosenergy.com | ON 3-27-2012, COMPANY AND CONTRACT PERSONNEL WERE ON SITE PERFORMING ILI PIGGING OPERATIONS. DURING PIGGING OPERATIONS, THE PIPELINE FAILED 6,695 FEET DOWNSTREAM FROM RIESEL JUNCTION STATION. NO INJURIES OCCURRED, AND NO CUSTOMERS WERE AFFECTED AS A RESULT OF THE INCIDENT. IT WAS DETERMINED THAT THE FAILURE WAS CAUSED BY THE IMPACT OF THE INLINE INSPECTION TOOL AT THE MISALIGNMENT (HIGH/LOW) ON THE GIRTH WELD ON THE UPSTREAM SIDE. THE LINE WAS SHUT DOWN ON 3-27-2012 AND WAS NEVER PLACED BACK IN SERVICE. IT WAS CAPPED OFF AND ABANDONED ON 10-22-2012.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120042 | 15501 | 2012-04-26 11:06 | ORIGINAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2012-03-29 08:00 | 2012 |  |  | 35.6703 | -108.8119 | 1007239 | 2012-03-29 13:00 |  | NATURAL GAS |  | 266 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | PIPELINE WAS ALREADY ISOLATED AND BLOWN DOWN FOR SCHEDULED MAINTENANCE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-03-29 08:00 | 2012-03-29 08:00 | ONSHORE | NM | 87375 | YAH-TA-HEY | MCKINLEY | MILEPOST | 83+1255 | CROSSOVER PIPING FROM LINE 1208 TO LINE 1204 |  | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | OTHER | ABOVE GROUND VALVE STEM |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [8 empty] | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 619 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 532 | 428.524312896406 | 83600 | 95997.88 | 0 | 0 | 0 | 0 |  |  | 84132 | 44509.8306131078 | 96426.4043128964 | [8 empty] | 729 |  | 894 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 36 | NO | [5 empty] | YES | NOT APPLICABLE SINCE THIS WAS CROSSOVER PIPING. | YES |  |  |  |  | YES | CROSSOVER PIPING. | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURES WERE FAR LOWER THAN OPERATING LIMITS; DID NOT EXCEED MAOP; LEAK WAS FROM VALVE STEM. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [30 empty] | YES | FAILURE OF VALVE THROUGH VALVE STEM PRODUCED SMALL LEAK. | [161 empty] | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | ken.peters@elpaso.com | 2053257554 | 2053253729 |  |  |  | KENNETH C PETERS | MANAGER - DOT COMPLIANCE FIELD SUPPORT | 2053257554 | ken.peters@elpaso.com | EL PASO NATURAL GAS (EPNG) EMPLOYEES WERE PERFORMING INTEGRITY MANAGEMENT REMEDIATION WORK ON LINE 1204. THEY NOTICED A SMALL LEAK FROM A 30-INCH VALVE IN CROSSOVER PIPING WHICH WAS USED TO ISOLATE THE PIPELINE SEGMENT. THE LEAK WAS DUE TO STEM FAILURE IN THE ABOVE GROUND STEM RISER OF THE 30-INCH VALVE AND COULD ONLY BE REPAIRED BY REPLACING THE VALVE. THIS WAS DONE AND THE REMEDIATION WORK CONTINUED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120043 | 15711 | 2012-04-26 16:11 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2012-04-05 13:30 | 2012 |  |  | 28.7337 | -99.0665 | 1007892 | 2012-04-05 14:06 |  | NATURAL GAS |  | 5000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-04-05 13:50 | [5 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-04-05 13:30 | 2012-04-05 13:40 | ONSHORE | TX | 78061 | PEARSALL | FRIO | MILEPOST | 52.3 | DIMMITT COUNTY MAINLINE | 287-1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 42 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.235 | 65000 | API-5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | EPOXY | [28 empty] | 1977 | 1977 | CARBON STEEL |  | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 1 LOCATION | NO |  | 458 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 15000 | 12082.4524312896 | 42790 | 49135.757 | 0 | 0 | 0 | 0 |  |  | 57790 | 35081.0360613108 | 61218.2094312896 | [8 empty] | 1028 |  | 1100 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 63360 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A THIRD PARTY LINE STRIKE WITH MINOR DAMAGE AND A PINHOLE THAT WOULD NOT BE DETECTED. | [12 empty] | YES | 1 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | NO |  |  |  |  | YES | [6 empty] | UTILITY | TRENCHER | NATURAL GAS | YES | 120870859 | DIG-TESS | UNKNOWN/OTHER | NO | NO | NO |  | LOCATING PRACTICES NOT SUFFICIENT |  | FACILITY WAS NOT LOCATED OR MARKED | [264 empty] | MATTHEW STRATMANN | SR. PIPELINE COMPLIANCE SPECIALIST | mstratmann@eprod.com | 713-381-8209 |  |  |  |  | MATTHEW STRATMANN | SR. PIPELINE COMPLIANCE SPECIALIST | 713-381-8209 | mstratmann@eprod.com | LINE 287-1 DIMMIT COUNTY MAINLINE WAS STRUCK BY A THIRD PARTY CONTRACTOR. ENTERPRISE PRODUCTS OPERATING LLC DID NOT MARK THE PIPELINE. THE THIRD PARTY CONTRACTOR DID NOT MAKE A FOUR HOUR FOLLOWUP NOTIFICATION. SUPPLEMENTAL/FINAL- REPAIR COSTS HAVE BEEN FINALIZED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120044 | 15756 | 2012-05-04 10:57 | SUPPLEMENTAL | 31604 | EQT MIDSTREAM | 2200 ENERGY DRIVE | CANONSBURG | PA | 15317 | 2012-04-07 01:48 | 2012 |  |  | 38.9809 | -80.5223 | 1008021 | 2012-04-07 02:43 |  | NATURAL GAS |  | 11200 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-04-07 02:08 | 2012-04-07 03:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-04-07 02:03 | 2012-04-07 02:03 | ONSHORE | WV | 26452-7174 | WESTON | LEWIS | SURVEY STATION NO. | 130+20 GSF943 | COPLEY COMPRESSOR STATION | COPLEY COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | ESD SYSTEM | 1981 |  | CARBON STEEL |  | OTHER | [8 empty] | EXTENDED VENTING OF ESD SYSTEM | CLASS 1 LOCATION | NO |  | 349 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 23408 | 18855.0697674419 | 0 | 0 | 200 | 229.66 | 0 | 0 |  |  | 23608 | 19653.3269767442 | 19084.7297674419 | [8 empty] | 589 |  | 1000 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  | YES | GAS CONTROLLER RECEIVED ALARM ON UNIT #5 SHUTDOWN AND CORRECTLY FOLLOWED PROCEDURE TO CALL OUT COMPRESSOR TECH. ALL OTHER ACTIONS WERE TAKEN LOCALLY AT THE STATION SITE. THE GAS CONTROLLER PERFORMED NO REMOTE OPERATION. |  | YES | [5 empty] | YES | LO PRESSURE ALERTS WERE ADDED TO THE COPLEY STATION AIR SYSTEM ON 4-7-12 | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | LOSS OF AIR SUPPLY TO ESD SYSTEM | [161 empty] | JOE LOMBARDO | MANAGER COMPLIANCE | jlombardo@eqt.com | 412-395-3135 | 412-395-7071 |  |  |  | JOE LOMBARDO | MANAGER COMPLIANCE | 412-395-3135 | jlombardo@eqt.com | AT APPROXIMATELY 1:12 AM APRIL 7, 2012 GAS CONTROL RECEIVED AN ALARM FOR COPLEY COMPRESSOR STATION (544 COPLEY ROAD, WESTON, WV 26452-7174) UNIT #5 COMPRESSOR SHUT DOWN. GAS CONTROL IMMEDIATELY CONTACTED THE ON-CALL EQT COMPRESSOR TECHNICIAN WHO REPORTED TO THE SITE. THE COPLEY STATION ESD TRIPPED AT APPROXIMATELY 1:48 AM WHILE THE COMPRESSOR TECHNICIAN WAS EN ROUTE. THE COMPRESSOR TECHNICIAN ARRIVED AT THE SITE AT APPROXIMATELY 2:03 AM AND DETERMINED ALL ESD VALVES DID NOT CLOSE AND GAS WAS VENTING TO THE ATMOSPHERE. THE COMPRESSOR TECHNICIAN PROCEEDED TO SHUT OFF ONE BLOCK VALVE THAT WAS 100% OPEN AND TWO BLOCK VALVES THAT WERE 20% OPEN. THE VALVES WERE CLOSED AND GAS SHUT OFF AT APPROXIMATELY 2:08 AM. EQT FACILITIES ENGINEERING INVESTIGATED AND DETERMINED TWO OF THREE AIR COMPRESSORS THAT HOLD THE COPLEY AIR SYSTEM PRESSURE UP HAD SHUT DOWN ON HIGH TEMPERATURE. THE THIRD AIR COMPRESSOR COULD NOT HOLD THE SYSTEM UP AND WHEN THE AIR PRESSURE DECLINED BELOW 100 PSIG THE SYSTEM WENT INTO ESD. THERE WAS NOT ENOUGH SUPPLY AIR IN THE SYSTEM TO FULLY SHUT THREE OF THE ESD VALVES. DESIGN ENGINEERING CALCULATED THE GAS LOSS TO BE 11.2 MMCF WHICH REQUIRED AN INCIDENT REPORT FILING.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120045 | 15790 | 2012-05-04 17:03 | SUPPLEMENTAL FINAL | 26330 | ENOGEX LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2012-04-04 02:00 | 2012 |  |  | 36.3123 | -97.4089 | 100781 | 2012-04-04 16:20 |  | NATURAL GAS |  | 3368 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | FACILITY SHUT DOWN DUE TO LOSS OF PURCHASED ELECTRICAL POWER. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-04-04 02:40 | 2012-04-04 03:46 | ONSHORE | OK | 73077 | PERRY | NOBLE | MILEPOST |  | PERRY COMPRESSOR STATION |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | OTHER | ESD VALVE CONTROL LINE |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | TUBING | [38 empty] | 1997 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL TUBING | OTHER | [8 empty] | INADVERTENT GAS RELEASE TO THE ATMOSPHERE THROUGH STAION SUCTION ESD VENT VALVE . | CLASS 1 LOCATION | NO |  | 3 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 6230 | 5018.24524312896 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6230 | 5202.64270613108 | 5018.24524312896 | [8 empty] | 125 |  | 150 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | NO | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INTERVIEW OF GAS CONTROL SUPERVISOR REVEALED THAT SCADA SYSTEM IS NOT CONFIGURED TO MONITOR THE EXHAUST PRESSURE ESCAPING FROM THE ESD VALVE ACTUATOR FOLLOWING ACTIVATION OF A STATION ESD. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | INVESTIGATION DISCOVERED THE ESD ACTUATOR EXHAUST PORT TUBING WAS PLUGGED WITH POLLEN FROM NEARBY CULTIVATED CROP FIELD. BLOCKAGE PREVENTED ESD ACTUATOR FROM OPERATING PROPERLY DURING AN ESD CONDITION. | [147 empty] | MIKE REED | MANAGER EHS ASSESSMENT AND DOT COMPLIANCE | reedmd@oge.com | 4055584685 | 4055578618 |  |  |  | PAUL M BREWER | VP OPERATIONS | 4055257788 | brewerpm@oge.com | ON THE MORNING OF APRIL 3, 2012 A DISRUPTION OF PURCHASED POWER SERVING THE PERRY COMPRESSOR STATION AUTOMATICALLY ACTIVATED THE COMPRESSOR STATION EMERGENCY SHUTDOWN (ESD) SYSTEM, WHICH IS DESIGNED IN ACCORDANCE WITH 49 CFR PART 192.167. THE ESD SYSTEM IS DESIGNED TO ISOLATE THE COMPRESSOR STATION FORM THE INCOMING AND OUTGOING PIPELINES AND VENT ALL GAS INSIDE THE STATION TO A SAFE LOCATION. THE STATION INLET ESD VALVE FAILED TO CLOSE DUE TO A BLOCKAGE IN THE ESD VALVE ACTUATOR EXHAUST TUBING. THE BLOCKAGE, WHICH WAS IDENTIFIED AS POLLEN DEPOSITED BY INSECTS INSIDE THE TUBING, PREVENTED THE OPERATING PRESSURE INSIDE THE SPRING OPERATED VALVE ACTUATOR FROM VENTING TO ATMOSPHERE, THUS PREVENTING THE VALVE FROM OPERATING PROPERLY. THE ESD SYSTEM VENT VALVES DID OPERATE PROPERLY, THEREBY VENTING 3,368 MCF OF NATURAL GAS TO THE ATMOSPHERE UNINTENTIONALLY. GAS CONTROL DISPATCHED COMPANY PERSONNEL TO THE COMRPESSOR STATION. THE COMPRESSOR STATION WAS ISOLATED FORM THE PIPELINE VIA A MANUAL ISOLATION VALVE. THE NATURAL GAS REMAINING INSIDE THE STATION ESD VENT PIPING WAS THEN QUICKLY VENTED TO THE ATMOSPHERE. THE BLOCKAGE WAS REMOVED FROM THE ACTUATOR EXHAUST PORT TUBING AND THE STATION INLET ESD VALVE WAS RETURNED TO NORMAL OPERATION. THERE WAS NO DAMAGE TO THE ACTUATOR OR ESD VALVE. UPDATE MARCH 5, 2013: COMPLETED SECTION E.5.F.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120046 | 30237 | 2012-05-09 10:01 | SUPPLEMENTAL | 19270 | TEXAS GAS TRANSMISSION LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2012-04-09 12:05 | 2012 |  |  | 29.2405 | -91.0263 | 1008161 | 2012-04-09 13:20 |  | NATURAL GAS |  | 21000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-04-09 16:45 |  | YES |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2012-04-09 12:05 | 2012-04-09 14:30 | ONSHORE | LA | 70397 | N/A | TERREBONNE | MILEPOST | 10+9813 | NORTH LAKE PAGIE 16" | N/A | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | IN WATER | 48 |  | YES | [6 empty] | YES | UNCASED | MUDHOLE BAY | 2 | BELOW WATER, PIPE ON OR ABOVE BOTTOM | [11 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.312 | 46000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | YOUNGSTOWN | OTHER | SOMASTIC & CONCRETE | [27 empty] | 1961 | 1961 | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | LONG SPIRAL FRACTURE. SPIRAL INVOLVED MOST OF AN APPROXIMATELY 40' JOINT. SINCE A PORTION OF MATERIAL THAT FAILED WAS LOST IN SHIPMENT, ACTUAL LENGTH OF FRACTURE CANNOT BE DETERMINED. LENGTH IS APPROXIMATED. | 456 | 1 |  | CLASS 1 LOCATION | NO |  | 396 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 43000 | 34636.3636363636 | 1000000 | 1148300 | 75000 | 86122.5 | 0 | 0 | 0 |  | 1118000 | 602541.590909091 | 1269058.86363636 | [8 empty] | 932 |  | 1288 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 57991 | YES | [7 empty] | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | NOTIFICATION FROM PRODUCER |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO CONTROLS WERE UTILIZED IN AREA REMOTELY. LOW FLOW CONDITIONS, OPERATING WELL BELOW MAOP. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | GENERAL CORROSION |  |  | YES | [5 empty] | YES |  |  | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | SHANNON MATTINGLY | PA OQ AND EVENT SUPPORT PROGRAM LEADER | shannon.mattingly@bwpmlp.com | 270-688-6357 | 270-688-6948 |  |  |  | DARRAL WARD | MANAGER PIPELINE SAFETY | 2706886356 | darral.ward@bwpmlp.com | ON APRIL 9, 2012, AT APPROXIMATELY 12:15PM, TEXAS GAS RECEIVED A CALL FROM A PRODUCER INFORMING US OF A FAILURE AND FIRE ON THE NORTH LAKE PAGIE-BAY JUNOP 16" PIPELINE. WE IMMEDIATELY BEGAN DEVELOPING AN ISOLATION PLAN TO IDENTIFY PRODUCERS AND CRITICAL VALVES TO SHUT IN THE PIPELINE AND DISPATCHED PERSONNEL BY BOAT. IT WAS DETERMINED THE APPROXIMATE FAILURE LOCATION WAS AT GPS COORDINATES 29 DEGREES, 14 MINUTES, 22 SECONDS NORTH AND 91 DEGREES, 01 MINUTES, 27 SECONDS WEST IN TERREBONNE PARISH. THE PIPELINE WAS SHUT IN BY 3:50PM. ADDITIONAL NRC REPORTS: 1008151, 1008154, 1008163, & 1008183. PIPELINE REMAINS OUT OF SERVICE PENDING DECISION ON TYPE OF REPAIR. 12-16-13 THIS SEGMENT OF PIPE IS SCHEDULED TO BE ABANONDONED IN 2014. 3-4-15 THE ABANDONMENT IS IN THE PERMITTING PROCESS AND IS NOW EXPECTED TO BE COMPLETE IN 2016 OR 2017. 11-10-15 THIS LINE IS SCHEDULED TO BE ABANDONED IN PLACE IN 2017. BOARDWALK IS PREPARING TO FILE FOR FERC APPROVAL. 4-18-17 TEXAS GAS IS ON SCHEDULE TO ABANDON IN 2017. 4-26-18 FERC APPROVAL FOR ABANDONMENT IS STILL PENDING. THE APPROVAL IS EXPECTED IN OCTOBER 2018; THEREFORE, THE ABANDONMENT PROJECT IS NOW PLANNED FOR 2019.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120047 | 16380 | 2012-05-10 12:18 | SUPPLEMENTAL FINAL | 31613 | ENBRIDGE PIPELINES (EAST TEXAS) L.P. | 1501 MCKINNEY SUITE 600 | HOUSTON | TX | 77010 | 2012-04-13 12:58 | 2012 |  |  | 32.4078 | -95.8752 | 1008612 | 2012-04-13 15:08 |  | NATURAL GAS |  | 1185 | 4447 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-04-13 16:50 | 2012-04-14 16:35 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-04-13 12:58 | 2012-04-13 14:05 | ONSHORE | TX | 75103 | CANTON | VAN ZANDT | MILEPOST | HWY. 17 | AKER RESIDUE | AF-12 AKER FRUITVALE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12.75 |  | 0.219 | 42000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COLD APPLIED TAPE | [28 empty] | 1971 | 1971 | CARBON STEEL |  | MECHANICAL PUNCTURE | 1 | 3 | [7 empty] | CLASS 1 LOCATION | NO |  | 283 |  | NO | NO | NO |  | 0 | 0 | 8895 | 10214.1285 | 2370 | 1909.02748414376 | 15350 | 17626.405 | 1200 | 1377.96 | 0 | 0 |  |  | 27815 | 15391.2349756871 | 31127.5209841438 | [8 empty] | 792 |  | 1039 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 104016 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | DRAINAGE | NO |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | YES | 26 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | JERRY HILL | COMPLIANCE COORDINATOR | jerry.hill@enbridge.com | 903-323-4330 |  |  |  |  | ALFRED GARCIA | COMPLIANCE COORDINATOR | 713-353-5650 | alfred.garcia@enbridge.com | MORROW CONSTRUCTION (DANIEL MORROW 903-780-5658) WAS EXCAVATING ON THE PROPERTY OF A FRIEND. THE EXCAVATOR NOR LANDOWNER HAD CALLED 811 TO REQUEST A LINE LOCATE. DURING THE EXCAVATION MORROW CONSTRUCTION HIT ENBRIDGE'S 12.750' .219 X42 PIPELINE. THE EXCAVATOR CALLED ENBRIDGE'S GAS CONTROL IN HOUSTON AT 12:58 PM. GAS CONTROL DID NOT SEE A DECREASE IN PRESSURE ON LINES IN THE AREA OF DAMAGE. FIELD PERSONNEL WERE NOTIFIED AT 1:05 PM TO INVESTIGATE; FIELD PERSONNEL ARRIVED ON LOCATION AT 2:00 PM AND CONFIRMED THAT THE ENBRIDGE LINE HAD BEEN HIT. THE LINE WAS BLOCKED IN AND BLOWN DOWN BY 4:50 PM. REPAIRS WERE MADE ON 4-14-12 AND THE LINE WAS PUT BACK IN SERVICE 4:35 PM.
2021-02-26 10:37 | YES | YES | GT (Gas Transmission) | 20120048 | 17117 | 2012-05-11 15:12 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION LP (SPECTRA ENERGY CORP) | 5400 WESTHEIMER COURT 77056 | HOUSTON | TX | 77056 | 2012-04-13 13:20 | 2012 |  |  | 40.0641 | -76.5773 | 1008605 | 2012-04-13 15:20 |  |  |  | 0 | 585 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 |  | YES |  | 2012-04-13 13:20 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-04-13 13:20 | 2012-04-13 13:20 | ONSHORE | PA | 17547 | MARIETTA | YORK | MILEPOST | 1203.64 | MARIETTA COMPRESSOR STATION | MARIETTA COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | DRAIN LINES | [38 empty] | 1952 |  | CARBON STEEL |  | OTHER | [8 empty] | STARTING AIR SYSTEM FAILURE | CLASS 1 LOCATION | NO |  | 1 |  | NO | NO | NO |  | 0 | 0 | 1170 | 1343.511 | 0 | 0 | 250000 | 287075 | 0 | 0 | 0 | 0 |  |  | 251170 | 132391.707 | 288418.511 | [8 empty] | 250 |  | 250 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | APPURTENANCE FAILURE | [21 empty] | YES | AIR COMPRESSOR LUBE OIL IN AIR SYSTEM | [161 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | deteschendorf@spectraenergy.com | 713-627-5573 | 713-386-4468 |  |  |  | RICK KIVELA | DIRECTOR OF OPERATIONAL COMPLIANCE | 713-627-6388 | rwkivela@spectraenergy.com | THE EMPLOYEE WAS STARTING THE UNIT. DURING THE START UP 2 OF THE UNIT'S 8 STARTING AIR CHECK VALVES WERE SLUGGISH IN CLOSING WHICH ALLOWED COMBUSTION GASSES TO ENTER THE STARTING AIR SYSTEM. A COMBUSTIBLE MIXTURE OF AIR AND AIR COMPRESSOR LUBE OIL HAD ACCUMULATED IN THE STARTING AIR SYSTEM PIPING AND WAS IGNITED BY THE COMBUSTION GASSES FROM THE UNIT. THERE WAS NO UNINTENTIONAL RELEASE OF NATURAL GAS DURING THE EVENT BUT SPECTRA ENERGY HAS JUDGED THIS TO BE A SIGNIFICANT OCCURRENCE.
2021-02-26 10:37 | YES | YES | GT (Gas Transmission) | 20120049 | 16732 | 2012-05-14 16:12 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2012-04-25 13:45 | 2012 |  |  | 42.5973 | -96.1253 | 1009666 | 2012-04-25 15:37 |  | NATURAL GAS |  | 46285 | 12460 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 2 | 0 | 2 |  | YES |  | 2012-04-25 15:02 | 2012-04-27 19:27 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 0 | 2012-04-25 13:58 | 2012-04-25 14:10 | ONSHORE | IA | 51024-8541 | HINTON | PLYMOUTH | MILEPOST | 20.29 | IAM60802-M560C SOUTH SIOUX CITY TO PAULLINA C-LINE | M560C | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 54 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 |  | 0.281 | 52000 | 5LX | FLASH WELDED |  | A.O.SMITH | COAL TAR | [28 empty] | 1957 | 1957 | CARBON STEEL |  | MECHANICAL PUNCTURE | 10 | 18 | [7 empty] | CLASS 1 LOCATION | NO |  | 468 |  | NO | NO | NO |  | 43000 | 49376.9 | 27051 | 31062.6633 | 100486 | 80941.1543340381 | 218190 | 250547.577 | 83546 | 95935.8718 | 0 | 0 |  |  | 472273 | 279884.297678858 | 507864.166434038 | [8 empty] | 763 |  | 800 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 40128 | NO |  | YES | [5 empty] | YES |  |  |  |  | YES | MISSING 3-MILE SEGMENT | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | AIR PATROL |  | CONTRACTOR WORKING FOR THE OPERATOR | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [7 empty] | CONTRACTOR | TRENCHER | DRAINAGE | NO |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO |  | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | BYRON WOOD | SR PIPELINE SAFETY SPECIALIST | byron.wood@nngco.com | 402-398-7396 |  |  |  |  | THOMAS CORRELL | SR. DIRECTOR PIPELINE SAFETY AND RISK | 402-398-7715 | thomas.correll@nngco.com | ON APRIL 25, 2012, NORTHERN NATURAL GAS' 24-INCH-DIAMETER SOUTH SIOUX CITY-TO-PAULINA M560C MAINLINE (C-LINE) WAS DAMAGED DURING THE INSTALLATION OF FARM DRAINAGE TILE IN A FIELD IN PLYMOUTH COUNTY NEAR HINTON, IOWA. THE TILING WORK WAS BEING PERFORMED BY DEROCHER CONSTRUCTION HEADQUARTERED IN LE MARS, IOWA, ON BEHALF OF RANDY RIEDIGER OF HINTON, IOWA, THE FARM TENANT. THE DAMAGED C-LINE RUPTURED AND THE ESCAPING GAS IGNITED. TWO TILING WORKERS WERE TREATED FOR INJURIES AT A SIOUX CITY HOSPITAL BUT THEIR INJURIES ARE NOT BELIEVED TO BE LIFE THREATENING. NO ONE CALL REQUEST WAS PLACED FOR THE TILING OPERATION. REPAIRS TO THE C-LINE AND INSPECTION OF THE NEARBY 16-INCH-DIAMETER SOUTH SIOUX CITY-TO-PAULINA B-LINE WERE COMPLETED APRIL 27, 2012. NO CUSTOMERS LOST SERVICE DUE TO THE LINE HIT OR THE SUBSEQUENT INVESTIGATION AND REPAIRS. FACILITY PLANNING ESTIMATES THE TOTAL GAS LOST AS A RESULT OF THIS INCIDENT TO BE 57.576 MMCF. THE IOWA ATTORNEY GENERAL OFFICE CONTACTED NORTHERN NATURAL GAS IMMEDIATELY FOLLOWING THE INCIDENT AND HAS OPENED AN INVESTIGATION INTO THE ONE CALL VIOLATION. SUPPLEMENTAL/FINAL REPORT FOR REPORT NO. 20120049-15515 DATED 05/14/2012. UPDATED INFORMATION IN PART A, SECTION 11, PART D, SECTION 7 WITH ESTIMATED FINAL TOTAL COST. APPROXIMATELY 102 FEET OF NEW 24-INCH-DIAMETER TESTED PIPE WAS REPLACED. THE LEGAL DEPARTMENT OF NORTHERN NATURAL GAS COMPANY IS FOLLOWING UP WITH SEEKING REIMBURSEMENT FOR COST INCURRED FROM THE INCIDENT. SUPPLEMENTAL/FINAL UPDATE TO REPORT # 20120049-15648 - IN SECTION C, ITEM 6 WHERE A MECHANICAL PUNTURE WAS INDICATED, ALTHOUGH THERE EXTENSIVE DAMAGE TO THE PIPE, THE SIZE OF THE PUNTURE IS ESTIMATED AS 10 INCHES AXIAL BY A CIRCUMFERENTIAL SIZE OF 18-INCHES. SUPPLEMENTAL/FINAL: REPORT # 20120049, DATED 5/14/2012 - UPDATED PART D ITEM 7A, PART G3 ITEM 10 TO TRENCHER AND ITEM 16. THE TWO TILING WORKERS INJURIES: ONE INCURRED 1ST DEGREE BURNS ON HIS BACK AND THE OTHER INCURRED 1ST AND 2ND DEGREE BURNS ON HIS BACK.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120050 | 15564 | 2012-05-17 11:36 | SUPPLEMENTAL FINAL | 10035 | POSTROCK KPC PIPELINE, LLC | 210 PARK AVE, SUITE 2750 OKLAHOMA CITY, OK 73102 | OKLAHOMA CITY | OK | 73102 | 2011-01-15 08:15 | 2011 |  |  | 37.0951 | -96.6208 |  |  |  | NATURAL GAS |  | 58433 | 3159 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-03-02 09:48 | 2011-03-05 12:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-03-02 08:15 | 2011-03-02 09:48 | ONSHORE | KS | 67024 | CEDAR VALE | COWLEY | MILEPOST | MP 130 | P-30 |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10.75 |  | 0.188 | 46000 | API 5L X46 | LONGITUDINAL ERW - HIGH FREQUENCY |  | STUPP ERW | COLD APPLIED TAPE | [28 empty] | 1964 | 1964 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO | NO |  | 0 | 0 | 13425 | 15708.0981251274 | 248340 | 168059.573712256 | 14595 | 17077.0720399429 | 0 | 0 | 0 | 0 |  |  | 276360 | 189284.249321573 | 200844.743877326 | [8 empty] | 631 |  | 1100 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 102960 | NO | [5 empty] | YES | FABRICATION REQUIRED AT ALL SITES | YES |  |  |  |  | YES | LAUNCHERS & RECIEVERS NEED LENGTHENING | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DUE TO SMALL SIZE OF LEAK, IT WAS FOUND BY THIRD PARTY AND WAS THEN NOTICABLE THROUGH LOSS AND ACCOUNTABLE AUDITING | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | YES | [7 empty] | YES | DENT | [8 empty] | YES |  |  |  | YES | [63 empty] | NO | [63 empty] | YES | 1984 | 1270 | NO | [13 empty] | NO | [63 empty] | JOSEPH M. FOWLER | OPERATIONS MANAGER | jfowler@pstr.com | 913-764-6015 | 913-764-6021 |  |  |  | JOSEPH M. FOWLER | OPERATIONS MANAGER | 913-764-6015 | jfowler@pstr.com | AT THE TIME OF ORIGINAL INSTALLATION, PIPE WAS APPARENTLY LAID OVER AN AREA WITH ROCK AND WAS NOT GIVEN ADEQUATE PADDING TO PROTECT THE PIPE FROM DAMAGE. THIS RESULTED IN A DENT THAT CAUSED THE CRACK IN THE PIPE WALL. THIS REPORT IS REPLACING THE REPORT PREVIOUSLY FILED ON THIS INCIDENT PER GABE HODILL WITH PHMSA KANSAS CITY
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120051 | 16079 | 2012-05-17 15:01 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION LP (SPECTRA ENERGY CORP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2012-04-19 16:30 | 2012 |  |  | 28.4385 | -93.45 | 1009154 | 2012-04-19 18:30 |  | NATURAL GAS |  | 400 | 19194 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | VERY SLOW LEAK IN A REMOTE AREA OF THE GULF OF MEXICO | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-04-19 16:30 | 2012-04-20 10:00 | OFFSHORE | [28 empty] | 170 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST CAMERON | 513 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 20 |  | 0.406 | 52000 | GIRTH WELD SMAW | SEAMLESS |  | US STEEL | OTHER | CONCRETE AND SOMASTIC | [27 empty] | 1975 | 1975 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 524 |  | NO | NO | NO |  | 0 | 0 | 38388 | 44080.9404 | 800 | 644.397463002114 | 300000 | 344490 | 0 | 0 | 0 | 0 |  |  | 339188 | 179032.390909937 | 389215.337863002 | [8 empty] | 885 |  | 1440 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 81629 | NO | [5 empty] | YES | NO PLATFORM FROM WHICH TO LAUNCH/RECEIVE INTERNAL INSPECTION TOOLS | YES |  |  |  |  | YES | NO PLATFORM FROM WHICH TO LAUNCH/RECEIVE | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | THIRD PARTY HELICOPTER OBSERVATION |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS TOO SMALL TO BE IDENTIFIED BY CONTROL ROOM PERSONNEL. A REVIEW OF OPERATING RECORDS FOUND ABNORMAL OPERATING CONDITIONS DID NOT CAUSE OR CONTRIBUTE TO THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  | YES |  |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | deteschendorf@spectraenergy.com | 713-627-5573 | 713-386-4468 |  |  |  | RICK KIVELA | DIRECTOR OF OPERATIONAL COMPLIANCE | 713-627-6388 | rwkivela@spectraenergy.com | BUBBLES WERE OBSERVED BY THE PISCES ENERGY PLATFORM OPERATORS ON APRIL 19, 2012. DIVERS DISCOVERED A PINHOLE LEAK IN THE TEXAS EASTERN 20-INCH LINE 41-A-6 WHICH WAS CAUSED BY INTERNAL CORROSION. TWO LEAK CLAMPS WERE INSTALLED AND THE PIPELINE WAS RETURNED TO FULL SERVICE ON MAY 8, 2012.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20120052 | 15888 | 2012-05-17 15:46 | SUPPLEMENTAL FINAL | 32296 | TARGA RESOURCES OPERATING LP | 811 LOUISIANA ST SUITE 2100 | HOUSTON | TX | 77002 | 2012-04-18 13:00 | 2012 |  |  | 29.32 | -93.4942 | 1009034 | 2012-04-18 14:30 |  | NATURAL GAS |  | 1100 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-04-18 14:00 | 2012-04-23 06:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-04-18 13:00 | 2012-04-19 12:00 | OFFSHORE | [28 empty] | 55 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST CAMERON | 188 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12 |  | 0.312 | 52000 | API 5L | SEAMLESS |  | UNKNOWN | EPOXY | [28 empty] | 1968 | 1968 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 250 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 3500 | 2819.23890063425 | 168000 | 192914.4 | 5500 | 6315.65 | 0 | 0 |  |  | 177000 | 94374.6829809725 | 202049.288900634 | [8 empty] | 950 |  | 1300 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | MANUAL | 355597 | NO | YES |  |  | YES |  |  |  | NO | [6 empty] | OFFSHORE GATHERING | NO |  |  |  |  | OTHER | BSEE AGENT |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | GENERAL CORROSION |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NOT APPLICABLE - NOT MAINLINE PIPE | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | TIM HUFFER | MANAGER REGULATORY COMPLIANCE | thuffer@targaresources.com | 337-583-4642 | 337-583-4630 |  |  |  | TIM HUFFER | MANAGER REGULATORY COMPLIANCE | 337-583-4642 | thuffer@targaresources.com | TARGA RECEIVED NOTIFICATION OF GAS BUBBLES IN WATER SIGHTED NEAR LOCATION OF COMPANY PIPELINE. TARGA RESPONDED BY HELICOPTER AND IDENTIFIED LEAK AS ORIGINATING FROM COMPANY PIPELINE. TARGA DISPATCHED REPAIR DIVE BOAT TO SITE. PIPELINE WAS REPAIRED BY INSTALLATION OF A BELTED REPAIR CLAMP.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120053 | 15752 | 2012-05-22 10:19 | SUPPLEMENTAL FINAL | 12498 | MIDWESTERN GAS TRANSMISSION CO | 100 WEST FIFTH STREET | TULSA | OK | 741034298 | 2012-05-01 06:30 | 2012 |  |  | 38.4414 | -87.176 | 1010206 | 2012-05-01 12:11 |  | NATURAL GAS |  | 5337 | 358 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-05-01 06:36 | 2012-05-03 16:46 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-05-01 06:30 | 2012-05-01 06:30 | ONSHORE | IN | 47598 | WINSLOW | PIKE | MILEPOST | 2110+0.00 | 2100-1 | 2110+0.00 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | WELD/FUSION |  | 2.375 |  | 0.218 | 35000 | ASTM A106 | SEAMLESS |  | UNKNOWN | PAINT | [9 empty] | PIPE GIRTH WELD | [18 empty] | 1979 | 1979 | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 211 |  | NO | NO | NO |  | 0 | 0 | 734 | 842.8522 | 10943 | 8814.55179704017 | 12000 | 13779.6 | 0 | 0 | 0 | 0 |  |  | 23677 | 15850.5374887949 | 23437.0039970402 | [8 empty] | 893 |  | 936 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE GAS CONTROL ALARMS AND COMMANDS DID NOT IMPACT OR PROVIDE ACKNOWLEDGEMENT OF THE FAILURE EVENT. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES |  |  |  | YES | MECHANICAL VIBRATION |  | YES | YES | LACK OF WELD FUSION | [12 empty] | YES | YES | [62 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | MARK MICKELBERG | SR ENGINEER | mark.mickelberg@oneok.com | 651-994-0332 | 651-994-4553 |  |  |  | CRAIG FORSANDER | VP NGP OPERATIONS | 918-588-7414 | craig.forsander@oneok.com | 2" CROSS-OVER LINE FAILED AT GIRTH WELD CONNECTING 2" DIAMETER PIPE NIPPLE TO 2" WELD END VALVE WHICH WAS A BRANCH CONNECTION OFF THE 10" DIAMETER DISCHARGE HEADER. THE 2" CROSS-OVER LINE IS LOCATED ON THE SUCTION/DISCHARGE GAS TURBINE UNIT SKID PIPING. THE ACTUAL GAS TURBINE WAS REMOVED IN 2003. THE 2" CROSS-OVER LINE WAS USED TO PURGE AND LOAD THE COMPRESSOR YARD PIPING, BUT IS NOWBLINDED, CAPPED AND NO LONGER REQUIRED. ONEOK PARTNERS SUPPLIED THE FRACTURED PIPE SECTION TO SHERRY LABORATORIES FOR FAILURE ANALYSIS. BASED ON THE FAILURE ANALYSIS, IT APPEARS FAILURE WAS DUE TO A COMBINATION OF FATIGUE CRACKING AND WELDING DEFECTS IN THE FORMS OF LACK OF FUSION AND INTEGRITY OF THE WELD AND POROSITY IN THE WELD. THE STRESSES RESPONSIBLE FOR THE INITIATION AND PROPAGATION OF THE CRACK WERE A COMBINATION OF APPLIED SERVICE-RELATED CYCLIC LOADING AND RESIDUAL STRESSES FROM THE WELDING FABRICATION. NO MATERIAL DEFECTS IN THE TWO PARENT MATERIALS WERE ASSOCIATED WITH THE PIPE FAILURE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120054 | 15940 | 2012-05-22 18:43 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 717 TEXAS AVE. | HOUSTON | TX | 77002 | 2012-04-25 05:30 | 2012 |  |  | 43.6009 | -88.1311 | 1009599 | 2012-04-25 07:30 |  | NATURAL GAS |  | 31000 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | [7 empty] | NO |  |  |  |  | NO | [9 empty] | ONSHORE | WI | 53001 |  | SHEBOYGAN | MILEPOST | MLV 6-3A-2 | KEWASKUM WI COMPRESSOR STATION | KEWASKUM-GREEN BAY | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | MAINLINE | GATE | [7 empty] | CARBON STEEL |  | OTHER | [8 empty] | THE KEWASKUM COMPRESSOR STATION LOCATED NEAR BEECHWOOD WISCONSIN EXPERIENCED A STATION ESD. THE STATION DID NOT BLOW DOWN AS REQUIRED. TECHNICIANS AND MANAGER REPORTED TO THE STATION AND ISOLATED THE STATION. | CLASS 1 LOCATION | NO |  | 231 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 124000 | 99881.6067653277 | 2000 | 2296.6 | 1000 | 1148.3 | 0 | 0 |  |  | 127000 | 105133.097040169 | 103326.506765328 | [8 empty] | 750 |  | 975 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CAUSE OF THE INCIDENT IS NOT RELATED TO CONTROL ROOM ISSUES. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [7 empty] | YES | [16 empty] | YES | [173 empty] | LOUIS SALINAS | COMPLIANCE ENGINEER | louis_salinas@transcanada.com | 832-320-5305 | 832-320-6305 |  |  |  | LOUIS SALINAS |  | 832-320-5305 | No Email Address | THE KEWASKUM COMPRESSOR STATION LOCATED NEAR BEECHWOOD WISCONSIN EXPERIENCED A STATION ESD. THE STATION DID NOT BLOW DOWN AS REQUIRED. VALVE 350-15-26 STOPPED 3/4 CLOSED. THE VALVE CYCLED NUMEROUS TIMES AS THE ESD SIGNAL AND THE STATION SIGNAL WERE CYCLING. THE VALVE FINALLY STOPPED AT WITHOUT CLOSING COMPLETELY. THE VALVE MALFUNCTIONED BECAUSE A FUSE IN THE 24 VOLT DC RELAY SYSTEM PARTIALLY FAILED. TECHNICIANS AND MANAGER REPORTED TO THE STATION AND PROCEEDED TO ISOLATE THE STATION. SUBSEQUENTLY, STATION TECHNICIANS REPAIRED THE TERMINAL FUSE BLOCKS AND REPLACED WIRING IN THE CONTROL ROOM. INVESTIGATION OF THE MALFUNCTION WAS COMPLETED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120055 | 15534 | 2012-05-25 12:28 | SUPPLEMENTAL FINAL | 30750 | MIDAMERICAN ENERGY COMPANY | 666 GRAND AVENUE, P.O. BOX 657 | DES MOINES | IA | 50309-2580 | 2012-04-27 16:30 | 2012 |  |  | 42.2571 | -90.6472 | 1010092 | 2012-04-30 11:05 |  | NATURAL GAS |  | 6562 | 265 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-04-27 17:30 | 2012-05-03 19:30 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2012-04-27 16:35 | 2012-04-27 17:48 | ONSHORE | IA | 52054-0000 | ZWINGLE | JACKSON | SURVEY STATION NO. | 638+03 | IAQC619 - DUBUQUE TO DAVENPORT PIPELINE | 2.9 MILES SOUTH OF ZWINGLE VALVE STATION | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 49 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.219 | 60000 | API 5L GRADE X60 | LONGITUDINAL ERW - HIGH FREQUENCY |  | GENEVA STEEL | EPOXY | [28 empty] | 1996 | 1995 | CARBON STEEL |  | RUPTURE | [6 empty] | 50.3 | 36 |  | CLASS 1 LOCATION | NO |  | 376 |  | NO | NO | NO |  | 440000 | 505252 | 660 | 757.878 | 16404 | 13213.3699788584 | 135560 | 155663.548 | 37156 | 42666.2348 | 0 | 0 |  |  | 629780 | 337009.390234249 | 717553.030778858 | [8 empty] | 640 |  | 960 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | MANUAL | 236074 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS CAUSED BY THIRD-PARTY DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  |  |  | YES | [6 empty] | CONTRACTOR | FARM EQUIPMENT | AGRICULTURE | NO |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | YES | 21 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | DENNIS C. OLSEN | SUPERVISOR GAS STANDARDS | dcolsen@midamerican.com | 712-277-7941 | 712-252-7369 |  |  |  | THOMAS H. HUTCHINS | VICE PRESIDENT GAS DELIVERY | 515-252-6945 | thhutchins@midamerican.com | SINCE THE INITIAL ELECTRONIC REPORT WAS SUBMITTED TO THE NATIONAL RESPONSE CENTER, THE OFFICIAL ADDRESS WAS CORRECTED FROM 25554 216TH AVENUE, ZWINGLE, IA, 52079 TO 25544. 216TH AVENUE, ZWINGLE, IA, 52054. AT APPROXIMATELY 1630 HOURS ON APRIL 27, 2012, A FIELD TILE INSTALLATION CREW WORKING FOR KUNDE DOZING AND TILING STRUCK AND PUNCTURED A 16-INCH, 960 PSIG MAOP NATURAL GAS TRANSMISSION PIPELINE, OWNED AND OPERATED BY MIDAMERICAN ENERGY COMPANY, IN JACKSON COUNTY, IOWA. THE DAMAGE TO THE PIPELINE RESULTED IN A RUPTURE THAT SUBSEQUENTLY IGNITED. THE PIPELINE WAS OPERATING AT APPROXIMATELY 640 PSIG AT THE TIME OF THE INCIDENT. MIDAMERICAN'S GAS SYSTEM CONTROL CENTER RECEIVED A LOW PRESSURE ALARM AT 1635 HOURS FROM THE SCADA EQUIPMENT LOCATED AT THE PIPELINE TAP LOCATION NEAR DUBUQUE, IOWA. THE MAQUOKETA LAW CENTER RECEIVED A 911 CALL AT 1631 HOURS FROM A RESIDENT REPORTING AN APPARENT PIPELINE BREAK AND FIRE. THE MAQUOKETA LAW CENTER REPORTED THE INCIDENT TO MIDAMERICAN AT 1649 HOURS. MIDAMERICAN WAS ABLE TO ISOLATE THE DAMAGED SEGMENT OF THE PIPELINE BY 1730 HOURS. THE PIPELINE WAS FURTHER ISOLATED BY 1855 HOURS AND THE FIRE EXTINGUISHED AT 1915 HOURS. MIDAMERICAN COMPLETED EMERGENCY WORK TO ISOLATE THE DAMAGED SECTION AND RE-PRESSURIZE THE PIPELINE BY 0600 HOURS ON APRIL 28, 2012. SERVICE WAS RESTORED TO ALL 11 RESIDENTIAL CUSTOMERS AFFECTED BY THE OUTAGE BY 1417 HOURS ON APRIL 28, 2012. PERMANENT REPAIRS WERE COMPLETED AND THE PIPELINE WAS RESTORED TO NORMAL OPERATION AT 1930 HOURS ON MAY 3, 2012. MIDAMERICAN'S INVESTIGATION OF THE INCIDENT DETERMINED THAT THE CONTRACTOR INSTALLING THE DRAIN TILE WAS PERFORMING EXCAVATION ACTIVITIES ON AGRICULTURAL LAND WITHOUT A LOCATE REQUEST. THE TILING CREW HAD CROSSED THE PIPELINE FOUR SEPARATE TIMES DURING THE DAY AND HIT THE LINE DURING THE FIFTH CROSSING. THE OWNER OF THE TILING COMPANY AND IOWA ONE CALL BOTH CONFIRMED THAT NO LOCATE REQUESTS WERE MADE FOR THE INCIDENT LOCATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120056 | 16828 | 2012-05-31 16:21 | SUPPLEMENTAL FINAL | 32296 | TARGA RESOURCES OPERATING LP | 811 LOUISIANA ST SUITE 2100 | HOUSTON | TX | 77002 | 2012-05-01 21:00 | 2012 |  |  | 31.5501 | -101.4607 | 1010358 | 2012-05-02 14:00 |  | NATURAL GAS |  | 26928 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | PIPELINE WAS SHUT DOWN FOR PRESSURE TESTING. | [6 empty] | YES |  |  |  |  | YES | [6 empty] | 0 | 2012-05-01 21:20 | 2012-05-01 21:30 | ONSHORE | TX | 76932 | BIG LAKE | REAGAN | MILEPOST | 506888 | ELDORADO TO SPRABERRY 16" | FM 2600 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.25 | 46000 | 5L | OTHER | UNKNOWN. | YOUNGSTOWN PIPE | COMPOSITE | [28 empty] | 1957 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 60 | 12 |  | CLASS 1 LOCATION | NO |  | 349 |  | NO | NO | NO |  | 2000 | 2296.6 | 0 | 0 | 70500 | 56787.5264270613 | 18000 | 20669.4 | 500 | 574.15 | 0 | 0 |  |  | 91000 | 69679.7571881607 | 80327.6764270613 | [8 empty] | 1136 |  | 1002 | 192.619(A)(2) |  |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 | NO |  |  |  |  | MANUAL | MANUAL | 89760 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE TESTING OF THE PIPELINE WAS IN PROGRESS AT THE TIME OF THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING | [6 empty] | YES | HIGH CHLORIDES IN SOIL. |  |  | YES |  |  |  | YES | YES | 1957 | NO | YES | YES |  |  |  | 2011 |  |  |  | NO | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | WILL BRYANT | SPECIALIST SR ES H | wbryant@targaresources.com | 325-835-8112 | 325-835-8102 |  |  |  | TIM HUFFER | MANAGER REGULATORY COMPLIANCE | 337-583-4642 | thuffer@targaresources.com | INTEGRITY PRESSURE TESTING IN ACCORDANCE WITH TEXAS TITLE 16, CHAPTER 8, SUBCHAPTER B WAS BEING CONDUCTED ON 05/01/2012. THE PRESSURE TEST ON THE PIPELINE WAS TO BE AT 1152 PSIG FOR 8 HRS. AS THE PIPELINE WAS BEING PRESSURED UP, A RUPTURE OF THE LINE OCCURRED AT APPROXIMATELY 1136 PSIG ON THE PIPELINE. THE CAUSE OF THE RUPTURE WAS DUE TO EXTERNAL CORROSION ON THE PIPELINE. A 30' TO 40' AREA OF THE PIPE HAD LOCALIZED PITTING LOCATED ON THE PIPING THAT WAS BLOWN AND REMOVED FROM THE AREA. SOIL SAMPLES FROM NEAR THE PIPE SHOWED HIGH LEVELS OF CHLORIDES. AN OIL WELL LOCATION WAS NEAR THE PIPE WITH THE REMNANTS OF THE BRINE PIT WITHIN 46' TO 50' OF THE PIPE. WHEN THE PIPELINE RUPTURED PERSONNEL WERE IN THE AREA TO ISOLATE VALVES. IT WAS DETERMINED 26,928 MCF WAS LOST IN THE BLOW OUT. WHEN THE RUPTURE OCCURRED A FIRE WAS STARTED, WHICH THEN STARTED A GRASS FIRE. REGAN COUNTY SHERIFF'S OFFICE AND REAGAN COUNTY VOLUNTEER FIRE DEPARTMNET RESPONDED TO THE FIRE AND INCIDENT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120057 | 15872 | 2012-05-31 16:26 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2012-05-01 03:08 | 2012 |  |  | 30.2926 | -90.3972 | 1010173 | 2012-05-01 03:30 |  | NATURAL GAS |  | 12514 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | SYSTEM NOT SHUT DOWN. ISOLATION VALVE CLOSED. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-05-01 03:08 | 2012-05-01 03:20 | ONSHORE | LA | 70744 | MONTPELIER | ST. HELENA |  |  | MONTPELIER COMPRESSOR STATION | INDEX 130 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | OTHER | RELIEF VALVE |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1950 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE PREMATURELY OPENED | CLASS 1 LOCATION | NO |  | 1 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 12664 | 10200.8118393235 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 12664 | 10575.644820296 | 10200.8118393235 | [8 empty] | 882 |  | 930 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO PRESSURE LOSS AT A POINT THAT GAS CONTROL MONITORS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | YES | [33 empty] | YES | LOSS OF PRESSURE DUE TO EQUIPMENT FITTING LEAK. | [161 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 270.688.6357 | 270.688.5871 |  |  |  | JEFF MCMAINE | MANAGER CODES AND STANDARDS | 270-688-6361 | jeffmcmaine@bwpmlp.com | GAS CONTROL RECEIVED A CALL FROM LOCAL POLICE DEPARTMENT REPORTING A SOUND THOUGHT TO BE GAS BLOWING. GAS CONTROL NOTIFIED ON-CALL OPERATOR AND AREA MANAGER. UPON ARRIVAL, OPERATOR IDENTIFIED A RELIEF VALVE BLOWING. OPERATOR CLOSED THE ISOLATION VALVE. AFTER INVESTIGATING, RELIEF VALVE SENSING LINE WAS FOUND TO BE THE CAUSE OF THE RELIEF VALVE ACTIVATING. THE SENSING LINE WAS REPAIRED AND TESTED FOR LEAKS. THE RELIEF VALVE WAS TESTED AND PLACED BACK IN SERVICE. REVISED TO INCLUDE ANSWER TO E.5F PER PHMSA REQUEST.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120058 | 16203 | 2012-06-01 11:09 | SUPPLEMENTAL FINAL | 840 | MOJAVE PIPELINE OPERATING COMPANY | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2012-05-02 08:20 | 2012 |  |  | 35.1616 | -118.8063 | 1010322 | 2012-05-02 09:28 |  | NATURAL GAS |  | 585457 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-05-02 09:06 | 2012-05-04 19:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-05-02 08:30 | 2012-05-02 08:30 | ONSHORE | CA | 93203 | ARVIN | KERN | MILEPOST | 118+1904 | LINE 1901 COMMON, MOJAVE PIPELINE | LINE 1901 BIFURCATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 |  | 0.28 | 35000 | API 5L-B | SEAMLESS |  | NKK CORPORATION | PAINT | [28 empty] | 1992 | 1991 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 6 | 6 |  | CLASS 1 LOCATION | NO |  | 158 |  | NO | NO | NO |  | 16000 | 18372.8 | 0 | 0 | 963643 | 776211.380549683 | 488000 | 560370.4 | 8000 | 9186.4 | 0 | 0 |  |  | 1475643 | 1074608.78350951 | 1364140.98054968 | [8 empty] | 917 |  | 1200 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | REMOTELY CONTROLLED | 100320 | NO | [5 empty] | YES | PIPING INVOLVED WAS FABRICATED STATION TYPE OF A FACILITY SUCH THAT AN ILI DOES NOT APPLY. | YES |  |  |  |  | YES | SEE QUESTION 5(D) ABOVE. | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATIONAL PARAMETERS WERE WITHIN NORMAL LIMITS AND NO REMOTE VALVE COMMANDS HAD BEEN ISSUED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | UNDERSIZED STRUCTURAL SUPPORT MEMBERS DID NOT WITHSTAND VENTING FORCES. |  |  | YES | [175 empty] | KENNETH C PETERS | ENGINEER - PIPELINE SR | ken_peters@kindermorgan.com | 2053257554 | 2053253729 |  |  |  | REJI GEORGE | DIRECTOR COMPLIANCE - CODES AND STANDARDS | 713-420-5433 | reji_george@kindermorgan.com | MOJAVE PIPELINE OPERATING COMPANY GAS CONTROL PERSONAL ENCOUNTERED A PRESSURE DROP VIA SCADA INFORMATION ON THE MOJAVE PIPELINE. LOCAL OPERATING PERSONNEL IN THE VICINITY OF ARVIN, CA, WERE DISPATCHED AND FOUND THAT A FABRICATION OF RELIEF VALVES AND PIPE SUPPORTS HAD FAILED, CAUSING DAMAGE TO THE MOJAVE FACILITY AND SOME SURROUNDING CHERRY TREES. THE INVESTIGATION INTO THE ROOT CAUSE OF REVEALED THE FOLLOWING: THE INADEQUACY OF THE STRUCTURAL SUPPORT PROVIDED AT THIS INSTALLATION AND ITS FAILURE ALLOWED FOR THE FAILURE OF THE PIPING SYSTEMS IT WAS INTENDED TO PROTECT. - UNDERSIZED STRUCTURAL MEMBERS IN SUPPORT TO WITHSTAND PREDICTED FORCES OF VENTING - INCORRECT ORIENTATION OF SUPPORT COLUMNS AND CROSS MEMBER (WEAK AXIS EXPOSED) - CONNECTION BETWEEN PIPE AND SUPPORT DIDNOT INSURE TRANSFER OF FORCES THE RELIEF VALVES WERE FOUND NOT TO HAVE HEIGHTENED THE LIKELIHOOD OF THE GAS RELEASE NOR DID THEY ADD TO THE IMPACT OF THE RELEASE, SO THEY WERE NOT CONTRIBUTING FACTORS AS DEFINED BY PHMSA.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120059 | 16348 | 2012-06-09 13:12 | SUPPLEMENTAL FINAL | 2620 | COLUMBIA GULF TRANSMISSION CO | 700 LOUISIANA ST. SUITE 700 | HOUSTON | TX | 77002 | 2012-05-10 06:32 | 2012 |  |  | 37.31 | -85.0611 | 1011062 | 2012-05-10 08:10 |  | NATURAL GAS |  | 17032 | 17033 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | MALFUNCTIOING RELIEF VALVE. FACILITY LOST SOME PRESSURE BUT REMAINED IN SERVICE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-05-10 07:10 | 2012-05-10 07:10 | ONSHORE | KY | 42539 | LIBERTY | CASEY | MILEPOST | CLEMENTSVILLE | CLEMENTSVILLE COMPRESSOR STATION |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [40 empty] | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE MALFUNCTIONED (LOST SIGNAL GAS) AND OPENED AT PRESSURE BELOW MAOP. RELIEF VALVE SET POINT WAS 1050 PSIG, LINE OPERATING PRESSURE WAS 924 PSIG. LINE MAOP IS 1008 PSIG. THERE IS NO HISTORY OF MAOP EXCEEDENCE IN THIS SEGMENT. | CLASS 1 LOCATION | NO |  | 175 |  | NO | NO | NO |  | 0 | 0 | 2 | 2.2966 | 33723 | 27163.7695560254 | 500 | 574.15 | 500 | 574.15 | 0 | 0 |  |  | 34725 | 28690.0675192389 | 28314.3661560254 | [8 empty] | 924 |  | 1008 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ROOT CAUSE WAS AN EQUIPMENT MALFUNCTION (BROKEN SIGNAL GAS LINE) THAT WAS NOT IN ANY WAY CAUSED BY CONTROL ROOM ACTIONS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | SIGNAL GAS LINE CONNECTION FAILED. FATIGUE POSSIBLE, BUT LITTLE VIBRATION SEEN. | [161 empty] | DAVID ADLER | ENGINEER - SYSTEM INTEGRITY | dadler@nisource.com | 304-357-2378 | 304-357-3804 |  |  |  | PERRY M. HOFFMAN | MANAGER - SYSTEM INTEGRITY | 304-357-2548 | mikehoffman@nisource.com | SHORTLY AFTER 5:30 AM ON 5/10/2012 A COLUMBIA GULF TRANSMISSION EMPLOYEE RECEIVED A CALL FROM A PERSON LIVING NEAR OUR CLEMENTSVILLE COMPRESSOR STATION. THE CALL INFORMED THE EMPLOYEE THAT THE STATION WAS MAKING A NOISE. THE EMPLOYEE ARRIVED ON SITE SHORTLY AFTER 6:00 AM AND HEARD GAS VENTING. BY 6:30 THE PROBLEM HAD BEEN ISOLATED TO A MALFUNCTIONING RELIEF VALVE. A SECOND RELIEF VALVE WAS PRESENT IN THIS SECTION OF PIPING, SO THE MALFUNCTIONING VALVE WAS CLOSED. THE STATION RESUMED NORMAL OPERATIONS. BY 7:00, A QUICK REVIEW OF OPERATING PARAMETERS WAS UNDERWAY. BEFORE 7:30 IT WAS DETERMINED THAT OVER 3000 MCF OF GAS HAD LIKELY BEEN RELEASED. A CALL WAS MADE TO THE NRC BY A FEW MINUTES AFTER 8:00. LATER THAT DAY IT WAS DETERMINED THAT A CONNECTION IN THE TUBING THAT SUPPLIED SIGNAL GAS TO THE RELIEF VALVE HAD FAILED. THIS HAD CAUSED THE RELIEF VALVE TO OPEN AT A PRESSURE SIGNIFICANTLY BELOW THE MAOP. THE CONNECTION WAS REPLACED WITH A DIFFERENT STYLE CONNECTION AT THIS LOCATION AND OTHER SIMILAR LOCATIONS. NOTE ON PART A QUESTION 19A AND 19B: COMPANY PERSONNEL ACTUALLY ARRIVED ON SITE BEFORE IT WAS DETERMINED THAT AN INCIDENT HAD OCCURRED. HOWEVER THE ELECTRONIC VERSION OF THIS FORM DOES NOT SEEM TO ALLOW THAT SEQUENCE OF EVENTS TO BE INPUT. REFERENCE THE ABOVE NARRATIVE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120061 | 15799 | 2012-06-14 16:42 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2012-05-22 13:00 | 2012 |  |  | 40.9003 | -73.84 | 1012478 | 2012-05-24 07:36 |  | NATURAL GAS |  | 7 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-05-24 07:17 | 2012-05-27 10:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-05-22 13:00 | 2012-05-22 13:00 | ONSHORE | NY | 10550-4040 | MT. VERNON | WESTCHESTER |  |  |  |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | FLANGE ASSEMBLY | [38 empty] | 1948 |  | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 4 LOCATION | YES | METHOD1 | 259 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 14 | 11.276955602537 | 20683 | 23750.2889 | 7399 | 8496.2717 | 5000 | 5741.5 | MATERIALS |  | 33096 | 17449.2135319239 | 37999.3375556025 | [8 empty] | 230 |  | 245 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 4278 | NO |  | YES | [5 empty] | YES |  |  |  |  | YES | PLUG VALVES | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SLIGHT LEAK ON VLAVE FLANGE NOT DETECTABLE VIA GAS CONTROL SYSTEMS | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | GASKET | [17 empty] | YES | GASKET LEAK AT FLANGE | [161 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPARTMENT MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | dadariov@coned.com | ON TUESDAY MAY 22, 2012 GAS READINGS WERE RECEIVED IN THE VICINITY OF 24" TRANSMISSION V-25962 LOCATED AT W 5 ST AND MUNDY LANE IN MT. VERNON (WL12004097). THE READINGS WERE RECEIVED DURING REPAIR OPERATIONS OF THE GEARING ASSOCIATED WITH THIS VALVE. IT WAS SUSPECTED A 1949 4" LP STEEL DISTRIBUTION MAIN LOCATED 3' SOUTH OF THE TRANSMISSION MAIN WAS THE SOURCE OF THE READINGS. TRANSMISSION CONTINGENCY CASES 16-C, 16-D WERE IDENTIFIED AND AROUND-THE-CLOCK OPERATIONS CONTINUED TO PREPARE THE DISTRIBUTION MAIN FOR INSERTION TO ELIMINATE THE TRANSMISSION MAIN AS THE SOURCE OF THE LEAK. ON WEDNESDAY MAY 23, 2012, THE DISTRIBUTION MAIN WAS ISOLATED AND THE READINGS DID NOT DISSIPATE. THE CHEMICAL TESTING LAB RESPONDED AND THEIR ANALYSIS CONFIRMED THE PRESENCE OF NATURAL GAS. AN OPERATIONAL PLAN WAS DEVELOPED IDENTIFYING THE STEPS TO BE TAKEN TO ISOLATE THE SECTION OF TRANSMISSION MAIN INVOLVED AND REDUCE PRESSURE TO HIGH PRESSURE IN ORDER TO EXCAVATE AND FURTHER IDENTIFY THE SOURCE OF THE LEAK. OPERATIONS WERE DELAYED DUE TO A SECOND, UNRELATED LEAK ALONG THE ROUTE OF THE 24" TRANSMISSION MAIN IN SCARSDALE, N.Y. WHICH WAS IMMEDIATELY STAFFED AND WORKED AROUND-THE-CLOCK IN ORDER TO ELIMINATE THE POSSIBILITY OF MULTIPLE SECTIONS OF THE TRANSMISSION SYSTEM BEING ISOLATED AT THE SAME TIME. THE SECOND LEAK WAS CONFIRMED ON THE DISTRIBUTION SYSTEM AT 18:00 AND THE OPERATIONAL PLAN ASSOCIATED WITH V-25962 REMAINED IN EFFECT. ON THURSDAY MAY 24, 2012 AT 07:17 ISOLATION OF THE AFFECTED SECTION OF TRANSMISSION MAIN WAS ACHIEVED AND PRESSURE REDUCED FROM 230 PSI TO 67 PSI PER PROCEDURE. AROUND-THE-CLOCK OPERATIONS CONTINUED AND EXCAVATION ACTIVITIES BEGAN FOR REPLACEMENT OF APPROXIMATELY 38' OF TRANSMISSION MAIN. ON SUNDAY MAY 27, 2012, AT 07:22 THE INSTALLATION OF 38' 2" OF 24" PIPE AND ALL WELDING WAS COMPLETED, TESTING PASSED AND PRESSURE RESTORATION BEGAN PER PROCEDURE. LEAK SURVEY MONITORED THE AFFECTED SECTION DURING RESTORATION ACTIVITIES AND NO LEAKS WERE FOUND AT 10:45 THE SECTION OF MAIN WAS FULLY ENERGIZED AND NORMAL SYSTEM CONDITIONS RESUMED (226 PSI). THERE WERE NO INJURIES, EVACUATIONS OR MEDIA ATTENTION ASSOCIATED WITH THIS INCIDENT. THE NYS PSC AND US DOT WERE NOTIFIED AND THE PSC RESPONDED TO LOCATION SEVERAL TIMES DURING THIS PROJECT. THIS WAS A SERIOUS LEVEL INCIDENT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120063 | 16207 | 2012-06-15 12:18 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2012-05-18 17:30 | 2012 |  |  | 31.27 | -103.0836 | 1012322 | 2012-05-22 16:48 |  | NATURAL GAS |  | 9000 | 19 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | DUMP LINE NOT NORMALLY USED, NO GAS BEING PUMPED THRU THE UNITS | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-05-21 08:45 | 2012-05-21 09:00 | ONSHORE | TX | 79730 | COYANOSA | PECOS |  |  | WAHA COMPRESSOR STATION |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1972 |  | CARBON STEEL |  | OTHER | [8 empty] | FAILED CONTROLLER ON DUMP VALVE | CLASS 1 LOCATION | NO |  | 651 |  | NO | NO | NO |  | 0 | 0 | 47 | 53.9701 | 22500 | 18123.6786469345 | 2000 | 2296.6 | 0 | 0 | 0 | 0 |  |  | 24547 | 19868.6142919662 | 20474.2487469345 | [8 empty] | 900 |  | 990 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | YES | [33 empty] | YES | WEAR | [161 empty] | JAMES FRISTOE | PIPELINE COMPLIANCE ENGINEER | mstratmann@eprod.com | 713-381-3824 | 713-381-3824 |  |  |  | JAMES FRISTOE | PIPELINE COMPLIANCE ENGINEER | 713-381-3824 | jpfristoe@eprod.com | THE CONTROLLER FOR THE DUMP VALVE ON THE SOUTH INLET SCRUBBER FOR THE DELAVAL COMPRESSORS (WAHA 2) FAILED. THIS CAUSED THE DUMP VALVE TO GO TO THE OPEN POSITION AND RELEASED SWEET GAS TO THE SLOP TANKS AND VENTED TO THE ATMOSPHERE. ESTIMATED LOSS OF GAS IS 9 MMCF. THE INCIDENT WAS DISCOVERED ON 5-21-12 AT 8:45AM BY AN ENTERPRISE MEASUREMENT TECH AND THE SYSTEM WAS BLOCKED BY 9:00 AM BY THE ENTERPRISE I&E TECH. THE MEASUREMENT TECH ESTIMATED THE LOSS AT 9 MCCF BY 10:00 AM AND IMMEDIATELY NOTIFIED HIS IMMEDIATE SUPERVISOR AND THE PIPELINE MANAGER.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120064 | 15684 | 2012-06-15 15:05 | SUPPLEMENTAL FINAL | 18112 | SAN DIEGO GAS & ELECTRIC CO | 8326 CENTURY PARK COURT | SAN DIEGO | CA | 92123 | 2012-05-23 09:43 | 2012 |  |  | 32.8489 | -117.1846 | 101243 | 2012-05-23 11:30 |  | NATURAL GAS |  | 0 | 40 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | PLANNED BLOWDOWN CONTROLLED BY CLOSING VALVE. PIPELINE STILL ENERGIZED | [6 empty] | YES |  |  |  |  | NO | [6 empty] | 0 | 2012-05-23 09:43 | 2012-05-23 09:43 | ONSHORE | CA | 92122 | SAN DIEGO | SAN DIEGO | MILEPOST | 45.73 | LINE 3010 | LINE 3010 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1979 |  | CARBON STEEL |  | OTHER | [8 empty] | CONTROLLED RELEASE THROUGH OPEN VALVE. | CLASS 3 LOCATION | YES | METHOD2 | 505 |  | NO | NO | NO |  | 32000 | 36745.6 | 240 | 275.592 | 0 | 0 | 36000 | 41338.8 | 1000 | 1148.3 | 0 | 0 |  |  | 69240 | 36496.404 | 79508.292 | [8 empty] | 51 |  | 595 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 1 | NO |  | YES | [5 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT RESULTED FROM PLANNED BLOWDOWN. | [12 empty] | YES | 8 | 0 | YES | 5 | 0 | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [103 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [261 empty] | W. JEFF KOSKIE | SR. PIPELINE SAFETY ADVISOR | wkoskie@semprautilities.com | 213 305-8660 | 213 244-8155 |  |  |  | W. JEFF KOSKIE | SR. PIPELINE SAFETY ADVISOR | 213 305-8660 | wkoskie@semprautilities.com | DURING PLANNED PIPELINE BLOWDOWN, ESCAPING GAS IGNITED AT LOCATION OF OVERHEAD ELECTRICAL FACILITIES. GAS WAS SHUT OFF IMMEDIATELY, STOPPING FIRE. NON-ENERGIZED STATIC LINE DROPPED ACROSS ROADWAY AND WAS STUCK BY 2 VEHICLES. DRUG AND ALCOHOL TESTS WERE PERFORMED ON 8 SDG&E EMPLOYEES AND 5 CONTRACTORS. ALL PASSED. THE IMMEDIATE CORRECTION IS TO TAKE AN ELECTRIC OUTAGE ON ALL OVERHEAD ELECTRIC CIRCUITS NEAR BLOWDOWN SITES. IF THAT IS NOT POSSIBLE, A SITE EVALUATION WILL BE PERFORMED BY A QUALIFIED CONSULTANT TO DETERMINE THE SAFE DISTANCE WHEREBY A BLOWDOWN MAY BE PERFORMED. THE PERMANENT SOLUTION IS TO DEVELOP A SET OF GUIDELINES LISTING THE DISTANCES, VOLTAGES, WEATHER CONDITIONS, ETC., WHEREBY BLOWDOWNS MAY BE SAFELY PERFORMED AT ANY SITE. ANY BLOWDOWN DEVIATING FROM THOSE GUIDELINES WOULD REQUIRE A SITE-SPECIFIC EVALUATION.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20120065 | 16427 | 2012-06-25 09:34 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY, LLC | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2012-06-09 12:00 | 2012 |  |  | 29.0753 | -92.1819 | 1014068 | 2012-06-09 16:30 |  | NATURAL GAS |  | 0.1 | 0 | 200 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | [9 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-06-09 16:20 | 2012-06-09 16:20 | OFFSHORE | [28 empty] | 53 | IN STATE WATERS | LA | VERMILLION | 131 |  |  |  |  | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1964 |  | CARBON STEEL |  | LEAK |  |  | OTHER | GASKET LEAK | [5 empty] | CLASS 1 LOCATION | NO |  | 419 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 2500 | 2013.74207188161 | 100000 | 114830 | 0 | 0 | 0 | 0 |  |  | 102500 | 54797.7378435518 | 116843.742071882 | [8 empty] | 900 |  | 1440 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 113098 | YES | [7 empty] | YES |  |  |  |  | YES | SMART PIG UNDERWATER | OFFSHORE GATHERING | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [5 empty] | YES | [29 empty] | YES | GASKET FAILURE | [161 empty] | EDGAR RODRIGUEZ | PIPELINE SAFETY SPECIALIST III | edgar.x.rodriguez@williams.com | 7132152846 | 7132152222 |  |  |  | MARIE SOTAK | PIPELINE SAFETY MANAGER | 7132152111 | marie.sotak@williams.com | 6/8/12 @ 7:40AM- STONE ENERGY VERM 131 OBSERVED A SHEEN NW OF THEIR PRODUCTION PLATFORM, THE OBSERVED A SHEEN ALONG WITH BUBBLES. STONE ENERGY REPORTED LEAK TO ES&H, THEY MADE NOTIFICATIONS TO USCG, NRC. NRC #1013919. 6/8/12 @ 9:40AM STONE ENERGY NOTIFIED WGP OPERATIONS OF BUBBLES AND SHEEN NW OF VERM 131 PLATFORM. 6/8/12- WGP OPERATIONS NOTIFIED WGP DISTRICT MANAGER OF BUBBLES AND SHEEN NEAR VERM 131 PLATFORM. 6/8/12- WGP OPERATIONS NOTIFIED WGP AREA ENGINEER OF POSSIBLE LEAK AT VERM 131, AREA ENGINEER STARTED LOOKING FOR DIVE BOAT TO RESPOND TO BUBBLES. 6/9/12@2:00AM- DIVE BOAT MOBBED OUT OF CAMERON AT 2:00AM, ARRIVED ON LOCATION AT VERM 131 AT 12:40PM. 6/9/12@ 4:30AM- MADE NOTIFICATION TO WGP GAS CONTROL LEAD OF LEAK ON OUR 16' PIPELINE, WGP GAS CONTROL MADE NOTIFICATIONS TO NRC, USCG AND EXTERNAL NOTIFICATIONS. NEW NRC# 1014068 6/9/12@ 6:30AM- 3 PRODUCERS ON 16' PIPELINE HAVE BEEN NOTIFIED AND SHUT IN. VERM 131, VERM 129 & VERM 87. 6/9/12@ 8:40PM- CONFIRMED THAT LEAK WAS COMING FROM 16' CHECK VALVE ON 16' PIPELINE SEGMENT #1584. LEAK WAS ON FLANGE ON TOP OF CHECK VALVE. CURRENTLY, WGP AREA ENGINEER WORKING ON A REPAIR PLAN TO MAKE REPAIRS TO 16' CHECK VALVE. ***UPDATE 10/30/2012*** PRODUCER STILL WORKING TO FIX LEAK AT CHECK VALVE. PRODUCER HAS GONE TO VALVE SITE TWICE TO TRY TO FIX CHECK VALVE BOTH TIMES VALVE HAS LEAKED. THE PIPE IS FILLED WITH WATER. NEXT OPTION WILL BE REPLACING CHECK VALVE WITH BLIND FLANGE AND BRING THE PIPELINE BACK TO SERVICE BY THE END OF NOVEMBER. ***REPAIR COMPLETED*** THE LEAKING CHECK VALVE WAS REPAIRED BY REPLACING A DAMAGED GASKET. THE LINE RESUMED ACTIVE STATUS ON JANUARY 1, 2013
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120066 | 16273 | 2012-06-27 18:04 | SUPPLEMENTAL FINAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2012-06-06 02:47 | 2012 |  |  | 35.5439 | -100.6785 | 1013669 | 2012-06-06 03:07 |  | NATURAL GAS |  | 34455 | 5000 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-06-06 02:55 | 2012-06-29 12:35 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2012-06-06 02:55 | 2012-06-06 03:00 | ONSHORE | TX | 79065 | PAMPA | GREY | MILEPOST | MILE POST 52 | OE #1 |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 26 |  | 0.25 | 52000 | 5LX 52 | LONGITUDINAL ERW - HIGH FREQUENCY |  | A.O. SMITH | COAL TAR | [28 empty] | 1957 | 1957 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 619.2 |  |  | CLASS 1 LOCATION | NO |  | 67 |  | NO | NO | NO |  | 1000 | 1148.3 | 0 | 0 | 85800 | 69111.6279069767 | 25000 | 28707.5 | 5000 | 5741.5 | 200 | 229.66 | EMERGENCY RESPONDERS COSTS |  | 117000 | 88096.6827906977 | 104938.587906977 | [8 empty] | 694 |  | 720 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | AUTOMATIC | 17424 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLERS ACTIONS DID NOT PARTICIPATE IN THE CAUSAL FACTORS IN THE PIPELINE FAILURE AND OPERATORS PERFORMED THEIR DUTIES AS SPECIFIED BY PROCEDURES. PHMSA INSPECTORS INVESTIGATED CONTROL ROOM AND FOUND NO FAULT IN CONTROLLERS ACTIONS. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) |  | YES | [9 empty] | YES | OTHER | HYDROGEN STRESS CRACKING AT A HARD SPOT | [16 empty] | YES | HARD SPOT CAUSED IN ORIGINAL ROLLING OF THE STEEL | [55 empty] | YES | YES | [6 empty] | 2011 | [55 empty] | YES | 1975 | 929 | NO | [13 empty] | NO | [63 empty] | KRISTIN VAN DER LAAN | COMPLIANCE ENGINEER III | kristin_vanderlaan@kindermorgan.com | 3039147753 | 3039843303 |  |  |  | REJI GEORGE | DIRECTOR COMPLIANCE CODES AND STANDARDS | 7134205433 | reji_george@kindermorgan.com | THE NPS 26 #1 OKLAHOMA EXTENSION FAILED 0.85 MILES DOWNSTREAM (WEST) OF COMPRESSOR STATION 154 IN GRAY COUNTY TEXAS. THE FRACTURE INITIATED NEAR THE OD SURFACE 17 INCHES DOWNSTREAM OF GIRTH WELD 1220 DUE TO HYDROGEN STRESS CRACKING AT A HARD SPOT. THE HARD SPOT WAS A MANUFACTURING DEFECT PRESENT SINCE PLATE ROLLING. THE 3.3 MILES OF PIPELINE (AFFECTED AREA) WAS RETURNED TO SERVICE ON JUNE 29, 2012 AT 80% OF THE OPERATING PRESSURE AT THE TIME OF THE INCIDENT. THE PROCESS TO RETURN IT TO 100% OF MAOP WAS STARTED ON NOVEMBER 16, 2012.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120067 | 15946 | 2012-06-29 12:16 | SUPPLEMENTAL FINAL | 602 | CENTERPOINT ENERGY GAS TRANSMISSION | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2012-06-20 19:22 | 2012 |  |  | 33.2264 | -92.6947 | 1015198 | 2012-06-20 20:16 |  | NATURAL GAS |  | 1 | 3 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | STOPPLE AND BYPASS | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-06-20 19:22 | 2012-06-20 19:22 | ONSHORE | AR | 71730 | EL DORADO | UNION | SURVEY STATION NO. | 117+88 | CEGT KT-1 |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 3 |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1942 |  | CARBON STEEL |  | LEAK |  |  | OTHER | BROKEN THREADS ON TAP VALVE | [5 empty] | CLASS 2 LOCATION | NO |  | 141 |  | NO | NO | NO |  | 0 | 0 | 9 | 10.3347 | 3 | 2.41649048625793 | 90760 | 104219.708 | 1000 | 1148.3 | 0 | 0 |  |  | 91772 | 48373.9451854123 | 105380.759190486 | [8 empty] | 310 |  | 420 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY DAMAGE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  |  |  | YES | [6 empty] | CONTRACTOR | UNKNOWN/OTHER | UNKNOWN/OTHER | NO |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER |  |  | OTHER |  |  |  | THIRD PARTY CONTRACTOR CROSSED ON TO CEGT ROW WHILE CLEANING/CLEARING ANOTHER OPERATOR'S/COMPANY'S PIPELINE ROW | [262 empty] | JIMMY CROSS | DOT WAIVER SPECIALIST | jimmy.cross@centerpointenergy.com | 3184293665 | 3184293927 |  |  |  | JOHNNY L. CAVITT | MANAGER OF DOT COMPLIANCE | 3184293606 | johnny.cavitt@centerpointenergy.com | ON 6/20/12 AT 5:46PM CONNER WILSON/SOUTHERN BRUSH SW INC. CONTACTED CEGT PERSONNEL, FROM THE EL DORADO OFFICE, AND SAID THEY HAD HIT A TAP VALVE ON OUR LINE WITH THEIR ROW EQUIPMENT AND IT WAS LEAKING. AT 6:00PM SYSTEM CONTROL WAS CONTACTED AND NOTIFIED OF A POSSIBLE INCIDENT. AT 6:11PM CEGT PERSONNEL ARRIVED ON SITE AND IDENTIFIED A BROKEN TAP VALVE ON KT-1 OFF OF FOREST LANE. AT 7:00PM PLANS WERE MADE FOR THE CEGT TEAM MEMBERS TO MONITOR THE LEAK UNTIL FIXED. THE DECISION WAS MADE TO INSTALL THREE WAY STOPPLE FITTINGS AND APPROXIMATELY 60' OF PIPE. AT 7:22PM IT WAS DETERMINED THAT THIS EVENT MAY MEET THE DEFINITION OF AN INCIDENT (BASED ON REPAIR COST ESTIMATES) AND NOTIFICATION WAS MADE TO SYSTEM CONTROL. CONFIRMATION OF AN INCIDENT WAS DETERMINED AND AT 8:16PM A REPORT WAS FILED BY SYSTEM CONTROL TO NRC AND THE STATE OF ARKANSAS EMERGENCY MANAGEMENT. AT 8:30PM JERRY THOMAS WITH UNION COUNTY EMERGENCY MANAGEMENT ARRIVED ON SITE TO LOOK AT LEAK AND DISCUSS CEGT'S REPAIR METHODS AND TIMEFRAME FOR REPAIRS. ON 6/21/12 AT 11:16AM CEGT'S REPAIR CONTRACTOR ARRIVED ON SITE. AT 2:35PM SYSTEM CONTROL WAS CONTACTED AND ADVISED THAT THE PIPELINE WAS BEING EXCAVATED. AT 3:58PM CEGT EMPLOYEES DISTRIBUTED THE REPAIR GAS HANDLING PLAN TO SYSTEM CONTROL AND OPERATIONS STAFF. AT 6:01PM THE REPAIR CONTRACTOR BEGAN SANDBLASTING AND PREPARING TO WELD ON STOPPLE FITTINGS. ON 6/22/2012 AT 6:30AM SYSTEM CONTROL WAS NOTIFIED THAT THE PROCESS TO WELD THE FITTINGS WAS GOING TO BEGIN. AT 11:15AM CREWS BEGAN WELDING THE LINE PIPE TO THE FITTINGS ON THE PIPE. AT 2:15PM THE CONTRACTOR BEGAN THE NITROGEN TEST ON THE FITTINGS. ON 6/23/12 AT 6:53AM CEGT PERSONNEL CONTACTED SYSTEM CONTROL AND NOTIFIED THEM WE WERE STARTING WORK. AT 10:49AM CEGT PERSONNEL CONTACTED SYSTEM CONTROL AND NOTIFIED THEM THAT THEY WERE HOT TAPPING AND THEN BLOWING DOWN THE SECTION OF LINE. AT 11:10AM THE LINE SEGMENT WAS BLOWN DOWN AND OUT OF SERVICE. AT 3:01PM CEGT PERSONNEL CONTACTED SYSTEM CONTROL TO NOTIFY THEM WE WERE GETTING READY TO BACKFILL THE SITE. AT 6:30PM CREWS LEFT SITE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120068 | 17148 | 2012-06-29 13:44 | SUPPLEMENTAL FINAL | 15014 | GAS TRANSMISSION NORTHWEST CORPORATION (GTN) | 717 TEXAS STREET | HOUSTON | TX | 77002-2761 | 2012-06-01 11:00 | 2012 |  |  | 48.9666 | -116.1739 | 1013313 | 2012-06-01 12:36 |  | NATURAL GAS |  | 20500 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | COMPRESSOR STATION WAS ISOLATED FROM THE PIPELINE, COMPRESSORS WERE NOT RUNNING. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-06-01 11:00 | 2012-06-01 11:00 | ONSHORE | ID | 83826 | EASTPORT | BOUNDARY | MILEPOST | 2.5 | GTN | COMPRESSOR STATION 3 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1992 |  | CARBON STEEL |  | OTHER | [8 empty] | STATION BLOCK VALVE FAILED TO OPERATE BECAUSE POWER GAS WAS DISABLED. | CLASS 1 LOCATION | NO |  | 875 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 45226 | 36429.399577167 | 0 | 0 | 900 | 1033.47 | 0 | 0 |  |  | 46126 | 38242.4026849894 | 37462.869577167 | [8 empty] | 680 |  | 911 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [204 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | [5 empty] | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | KURT SMITH | PIPE REGULATORY SPECIALIST | kurt_smith@transcanada.com | (509) 533-2848 | (509) 533-2993 |  |  |  | KURT SMITH | PIPE REGULATORY SPECIALIST | (509) 533-2848 | kurt_smith@transcanada.com | ON JUNE 1ST AT APPROXIMATELY 0930 PDT, A COMMUNICATIONS FAILURE WITHIN THE STATION 3 PROGRAMMABLE LOGIC CONTROLLER (PLC) CAUSED A STATION EMERGENCY SHUTDOWN (ESD). THE STATION VALVES IMMEDIATELY ATTEMPTED TO GO TO THEIR FAIL-SAFE POSITIONS. THE STATION B LINE SUCTION VALVE (VALVE 15) FAILED TO CLOSE AND ALLOWED GAS TO VENT THROUGH THE STATION BLOWDOWN SILENCER FOR APPROXIMATELY 90 MINUTES. GAS CONTROL FIRST NOTED AN ESD AT THE STATION AND THEN OBSERVED INDICATIONS THAT THE STATION MAY NOT HAVE BLOWN DOWN PROPERLY AND THAT IT WAS POSSIBLE THAT GAS WAS CONTINUING TO VENT. GAS CONTROL NOTIFIED LOCAL PERSONNEL AT THE SANDPOINT OFFICE AND TWO TECHNICIANS WERE DISPATCHED TO INVESTIGATE. THE TECHNICIANS ARRIVED AT STATION 3 AT APPROXIMATELY 1100 PDT. THEY DETERMINED THAT GAS WAS VENTING OUT THE BLOWDOWN SILENCER AND THAT VALVE 15 HAD NOT CLOSED. POWER GAS WAS RESTORED TO VALVE 15 WHICH ALLOWED THE VALVE TO TRAVEL CLOSED AND STOP THE VENTING OF GAS.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120069 | 16831 | 2012-07-03 10:08 | SUPPLEMENTAL FINAL | 19270 | TEXAS GAS TRANSMISSION LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2012-06-07 08:46 | 2012 |  |  | 29.9535 | -92.7184 | 1013833 | 2012-06-07 10:44 |  | NATURAL GAS |  | 994 | 41 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-06-07 21:00 | 2012-06-13 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-06-07 08:49 | 2012-06-07 11:50 | ONSHORE | LA | 70542-0000 | Not Within a Municipality | CAMERON PARISH | MILEPOST | 6+3720 | LAKESIDE MALLARD BAY LINE | LMB 6" | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | YES | [6 empty] | YES | UNCASED | INTERCOASTAL WATERWAY GRAND LAKE TRAHAN CUT | 7 | BELOW WATER, PIPE BURIED BELOW BOTTOM (NOT IN BORED/DRILLED CROSSING) | [11 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6.625 |  | 0.28 | 42000 | API 5L | SEAMLESS |  | INTERLAKE STEEL CORPORATION | OTHER | REILLY BM | [27 empty] | 1952 | 1952 | CARBON STEEL |  | MECHANICAL PUNCTURE | 2 | 3 | [7 empty] | CLASS 1 LOCATION | NO |  | 58 |  | NO | NO | NO |  | 0 | 0 | 100 | 114.83 | 2375 | 1913.05496828753 | 25000 | 28707.5 | 1000 | 1148.3 | 0 | 0 |  |  | 28475 | 15740.6609513742 | 31883.6849682875 | [8 empty] | 800 |  | 1050 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 14 | NO | YES | [6 empty] | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ROUTINE OR NORMAL FISHING OR OTHER MARITIME ACTIVITY NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | FISHING OR MARITIME ACTIVITY | [103 empty] | ROUTINE OR NORMAL FISHING OR OTHER MARITIME ACTIVITY NOT ENGAGED IN EXCAVATION | [261 empty] | JACK L. ADAMS | SR. CONSULTANT | jack.adams@bwpmlp.com | 713-479-8099 | 713-479-1720 |  |  |  | JACK L. ADAMS | SR. CONSULTANT | 713-479-8099 | jack.adams@bwpmlp.com | TWO 2 IN. X 3 IN. SCRAPES APPROXIMATELY 18" APART WERE DISCOVERED AT NEAR THE 12 :00 POSITION ON THE PIPE. ONE WAS LEAKING. REPAIR WAS MADE BY INSTALLING PLIDCO CLAMPS OVER BOTH AREAS. ADDITIONALLY, THREE BUOYS WERE INSTALLED OVER THE PIPELINE IN THE AREA TO ACT AS A DETERRENT TO BOAT TRAFFIC. 7-24-15 REVISED TO ADD PIPE SPECIFICATION AS REQUESTED BY PHMSA. THE PORTAL REQUIRED ADDITIONAL DATA TO BE POPULATED AS WELL.
2021-02-26 10:37 | NO | NO | GG (Gas Gathering) | 20120070 | 16208 | 2012-07-10 09:20 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2012-06-13 13:00 | 2012 |  |  | 28.4566 | -96.3813 | 1014478 | 2012-06-13 14:30 |  |  |  | 0 | 0 | 0.36 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | LEAK OUT OF THE LAUNCHER BARREL | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-06-13 13:00 | 2012-06-13 13:40 | OFFSHORE | [28 empty] | 11 | IN STATE WATERS | TX | WEST MATAGORDA BAY | 135 | CALHOUN |  |  |  | PLATFORM | INTERSTATE | OFFSHORE PLATFORM, INCLUDING PLATFORM-MOUNTED EQUIPMENT AND PIPING | SCRAPER/PIG TRAP | [40 empty] | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | RUBBER GASKET/ O-RING | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 1 |  | NO | NO | YES |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 2296.6 | 0 | 0 |  |  | 2000 | 1054.2 | 2296.6 | [8 empty] | 800 |  | 1250 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | OFFSHORE GATHERING | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | O-RING | [17 empty] | YES | WEAR | [161 empty] | JAMES P. FRISTOE | PIPELINE COMPLIANCE ENGINEER | jpfristoe@eprod.com | 713-381-3824 |  |  |  |  | JAMES P. FRISTOE | PIPELINE COMPLIANCE ENGINEER | 713-381-3824 | jpfristoe@eprod.com | 1 PM NOTIFIED BY GAS CONTROL POSSIBLE LEAK ON "TOMCAT PLATFORM". DETERMINED THAT ST135 WAS PROBABLE SITE FROM DIRECTIONS. DISPACHED ENTERPRISE EMPLOYEE WORKING AT MI622 TO SCENE BY HELICOPTER. EMPLOYEE DETERMINED WE HAD A CONDENSATE SPILL OF 10-15 GALLONS FROM PIG LAUNCHER ON PLATFORM. LAUNCHER WAS ISOLATED AND BLOWNDOWN AT 1:40 PM. GLO AND COAST GUARD ADVISED NO CLEAN-UP OR USE OF DISPERSANT, LET FILM EVAPORATE. NO RECOVERY, ESTIMATED LOSS AT 10-15 GALLONS OF CONDENSATE. RELEASE WAS DUE TO A FAILED O-RING ON THE PIG TRAP. O-RING WAS REPLACED. THIS IS AN INTERSTATE GATHERING LINE. THERE IS NO HCA OR PIR ASSOCIATED WITH THIS PIPELINE. I ENTERED 1 BECAUSE 0 IS NOT EXCEPTED.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20120071 | 15558 | 2012-07-12 16:57 | ORIGINAL FINAL | 32296 | TARGA RESOURCES OPERATING LP | 811 LOUISIANA ST SUITE 2100 | HOUSTON | TX | 77002 | 2012-06-28 08:00 | 2012 |  |  | 29.131 | -93.4886 | 1016016 | 2012-06-28 08:30 |  | NATURAL GAS |  | 100 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | DIVERS WERE ABLE TO INSTALL CLAMP UNDER PRESSURE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-06-28 08:00 | 2012-06-29 13:00 | OFFSHORE | [28 empty] | 55 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST CAMERON | 188 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12 |  | 0.312 | 52000 | API5LX | SEAMLESS |  | UNKNOWN | EPOXY | [28 empty] | 1968 | 1968 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 300 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 4500 | 3624.73572938689 | 170000 | 195211 | 5500 | 6315.65 | 0 | 0 |  |  | 180000 | 96263.9781183932 | 205151.385729387 | [8 empty] | 950 |  | 1300 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | MANUAL | 101720 | NO | YES | [6 empty] | NO | [6 empty] | TYPE A GATHERING | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | TIM HUFFER | MANAGER REGULATORY COMPLIANCE | thuffer@targaresources.com | 337-583-4642 | 337-583-4630 |  |  |  | TIM HUFFER | MANAGER REGULATORY COMPLIANCE | 337-583-4642 | thuffer@targaresources.cm | GAS BUBBLING DISCOVERED AND IDENTIFIED AS ORIGINATING FROM TARGA'S PIPELINE OFFSHORE LOUISIANA IN WEST CAMERON188. THE PIPELINE WAS REPAIRED BY INSTALLATION OF A BOLTED CLAMP. TH INSTALLATION OF THE CLAMP WAS COMPLETED ON 7/3/2012 AT 900 HOURS. ALTHOUGH THE APPARENT CAUSE SELECTED IN THE REPORT IS MICROBIOLOGICAL, THIS CANNOT BE DETERMINED TO BE THE ACTUAL CAUSE DUE TO THE FACT THAT AN INTERNAL INSPECTION OF THE PIPELINE AT THE LOCATION OF THE INCIDENT WAS NOT COMPLETED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120072 | 16627 | 2012-07-17 15:24 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2012-06-21 16:30 | 2012 |  |  | 35.3425 | -87.6674 | 1015299 | 2012-06-21 17:24 |  | NATURAL GAS |  | 6791 | 1950 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | VALVE SECTION OUT OF SERVICE AND AT MUCH REDUCED PRESSURE DUE TO ANOMALY INVEST | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-06-21 16:30 | 2012-06-21 16:30 | ONSHORE | TN | 38485 | WAYNESVILLE | WAYNE | MILEPOST | 556-1 + 5.78 | 500-1 | 556-1 @ TAP (DELTA PORTLAND) | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 144 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 2 |  | 0.218 | 35000 | API 5L | SEAMLESS |  | US STEEL | EPOXY | [28 empty] | 2009 | 2005 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | YES | METHOD2 | 633 |  | NO | NO | NO |  | 0 | 0 | 4680 | 5374.044 | 16298 | 13127.9873150106 | 175000 | 200952.5 | 0 | 0 | 0 | 0 |  |  | 195978 | 108319.708549683 | 219454.531315011 | [8 empty] | 195 |  | 936 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 96624 | NO | [5 empty] | YES | LEAK WAS IN 2" TAP LINE WHICH IS NOT PIGGABLE. | YES |  |  |  |  | YES | SEE 5D ABOVE. | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LINE WAS OUT OF SERVICE DUE TO ANOMALY INVESTIGATION FOLLOWING A SMART PIG RUN. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [52 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | SUBSIDENCE |  |  |  |  | NO | [306 empty] | KENNETH C. PETERS | ENGINEER PIPELINE - EP | ken_peters@kindermorgan.com | 2053257554 | 2053253729 |  |  |  | KENNETH C. PETERS | ENGINEER PIPELINE - EP | 2053257554 | ken_peters@kindermorgan.com | TENNESSEE GAS PIPELINE (TGP) COMPANY OPERATIONS PERSONNEL DISCOVERED INDICATIONS OF WHAT APPEARED TO BE A NATURAL GAS LEAK DURING THEIR WORK RELATIVE TO ANOMALY DIGS FOLLOWING THE RESULTS OF A SMART PIG RUN ON TGP'S 500-1 PIPELINE IN WAYNE COUNTY, TN. EXCAVATION IN THE VICINITY OF THE SUSPECTED LEAK REVEALED A CRACK FROM WHICH GAS WAS LEAKING IN TGP'S 2" LATERAL LINE NEAR THE TAP OF ITS 500-1 PIPELINE. THE APPARENT CAUSE OF THE LEAK WAS ASSYMETRICAL LOADING (I.E. SETTLEMENT) OF THE SOIL BETWEEN THE CARRIER PIPE AND THE TAP LINE, WHICH RESULTED IN EXCESSIVE STRESSES ON THE 2" PIPE.
2021-02-26 10:37 | NO | NO | GG (Gas Gathering) | 20120073 | 16790 | 2012-07-19 | SUPPLEMENTAL FINAL | 9011 | J - W GATHERING CO | P.O. BOX 226406 | DALLAS | TX | 75222 | 2012-06-20 01:36 | 2012 |  |  | 32.3558 | -93.6778 | 1015293 | 2012-06-21 16:03 |  | NATURAL GAS |  | 7179 | 241 | 1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-06-20 04:15 | 2015-06-22 16:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-06-20 02:20 | 2012-06-20 03:00 | ONSHORE | LA | 71115 | SHREVEPORT | CADDO | MILEPOST | 06+78 | MAIN LINE | CGS2100 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 40 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6.625 |  | 0.156 | 42000 | API 5L X42 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1972 | 1971 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 36 | 6 |  | CLASS 2 LOCATION | NO |  | 143 |  | NO | NO | NO |  | 0 | 0 | 500 | 574.15 | 14000 | 11276.955602537 | 20000 | 22966 | 0 | 0 | 0 | 0 |  |  | 34500 | 22496.8819238901 | 34817.105602537 | [8 empty] | 800 |  | 1187 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 18992 | NO |  | YES |  | YES |  |  |  | NO | [6 empty] | TYPE A GATHERING | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [64 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | [10 empty] | NO |  |  | YES | PRIVATE LANDOWNER | YES | YES | [5 empty] | DATA NOT COLLECTED | DATA NOT COLLECTED | DATA NOT COLLECTED | NO |  |  | DATA NOT COLLECTED | DATA NOT COLLECTED | DATA NOT COLLECTED | DATA NOT COLLECTED |  | PREVIOUS DAMAGE | [121 empty] | NO | [62 empty] | NO | YES | 2011 | 1500 | NO | [13 empty] | NO | [63 empty] | JIM RUMSEY | REGULATORY AFFAIRS MANAGER | jrumsey@jwenergy.com | 9032912811 | 8668403098 |  |  |  | JIM RUMSEY | REGULATORY AFFAIRS MANAGER | 9032912811 | jrumsey@jwenergy.com | A BURIED SIX INCH NATURAL GAS GATHERING PIPELINE RUPTURED. THE RUPTURE CAUSED NATURAL GAS TO ESCAPE THE PIPELINE AND VENT TO ATMOSHPERE. COMPANY PERSONNEL RESPONDED TO SCADA ALARMS AND IDENTIFIED THE FAILURE. THE EFFECTED PIPE SEGMENT WAS ISLOLATED AND DEPRESSURIZED. THE FAILED SEGMENT OF PIPE WAS REPLACED, AND THE PIPELINE WAS PLACED BACK IN SERVICE AT APPROXIMATELY 16:00 THE SAME DATE. THE AFFECTED SEGMENT WAS SENT TO THE LAB FOR ANALYSIS. THERE WAS, WHAT APPEARED TO BE, DAMAGE TO THE OUTSIDE OF THE PIPE FROM A PREVIOUS (THIRD PARTY) EXCAVATION. THERE IS NO RECORD OF THE INCIDENT OR EXCAVATION THAT MAY HAVE CAUSED THE DAMAGE. SUPPLENTAL REPORT: THE LAB ANALYSIS CONCLUDED: 1. THE OUTSIDE OF THE PIPE EXHIBITED TWO LONGITUDINAL BANDS OF GOUGES. THE RUPTURE RAN ALONG THE EDGE OF ONE BAND, AND THEN CONTINUED AT EACH END IN A CIRCUMFERENTIAL DIRECTION. 2. THE WALL THICKNESS WAS SATISFACTORY AWAY FROM THE RUPTURE AND ALONG ONE SIDE OF IT, BUT ON THE OTHER SIDE OF THE RUPTURE, THE WALL THICKNESS WAS 0.010 TO 0.035 INCH THINNER, DUE TO CORROSION AS A RESULT OF DAMAGE TO THE PROTECTIVE COATING AND THE SUBSEQUENT EXPOSURE TO THE ENVIRONMENT. 3. DIAMETER MEASUREMENTS AT THE RUPTURE AND AWAY FROM IT INDICATED THAT THE PIPE HAD NOT SWOLLEN BEFORE RUPTURING. 4. AN API TENSION TEST SHOWED SATISFACTORY YIELD AND TENSILE STRENGTHS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120075 | 15840 | 2012-07-26 08:39 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2012-06-28 08:25 | 2012 |  |  | 29.2983 | -95.9492 | 1016049 | 2012-06-28 11:45 |  | NATURAL GAS |  | 0.5 | 19425 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-06-28 10:45 | 2012-07-03 17:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-06-28 08:25 | 2012-06-28 09:20 | ONSHORE | TX | 77420 | BOLING | WHARTON | MILEPOST | 45.04 | GLEN FLORA- BOLING | GLEN FLORA- BOLING/328-7 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 162 |  | NO | [22 empty] | INTRASTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | PIPE | PIPE BODY | 24 |  | 0.283 | 65000 | X-65 | DSAW |  | UNKNOWN | EPOXY | [28 empty] | 1982 | 1982 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 550 |  | NO | NO | NO |  | 0 | 0 | 58275 | 66917.1825 | 1500 | 1208.24524312896 | 150000 | 172245 | 0 | 0 | 0 | 0 |  |  | 209775 | 111034.395206131 | 240370.427743129 | [8 empty] | 950 |  | 1102 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE AMOUNT OF UNINTENTIONAL GAS LOST WAS SMALL, ONLY .5 MCF | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES | [7 empty] | YES | UNKNOWN | [12 empty] | YES | [63 empty] | YES | YES |  |  | YES |  |  |  | 2008 | [31 empty] | 2008 | [23 empty] | YES | 1982 | 1682 | NO | [13 empty] | NO | [63 empty] | MATT STRATAMNN | SR. PIPELINE COMPLIANCE SPECIALIST | mstratmann@eprod.com | (713)381-8209 |  |  |  |  | MATT STRATMANN | PIPELINE COMPLIANCE SPECIALIST | (713)381-8209 | mstratmann@eprod.com | LANDOWNER IN WHARTON COUNTY DICOVERED LEAK ON PIPELINE RIGHT OF WAY,LANDOWNER NOTIFIED CONTRACT PERSONNEL WORKING ON ROW,CONTRACTOR CONTACTED ENTERPRISE PERSONEL AT 8:25 AM. ENTERPRISE PERSONNEL ARRIVED ON SITE AND DISCOVERED A SMALL LEAK AND VERIFIED THE LEAK TO BE ON OUR 24" PIPELINE AT APPROXIMATELY 9:55 AM. GAS CONTROL WAS NOTIFIED AND THE PIPELINE WAS SHUT-IN AND BLOWN DOWN AT 10:45 AM. NRC AND RAILROAD COMMISSION WERE NOTIFIED. AFTER EXCAVATION, THE PIPELINE WAS FOUND TO HAVE A CRACK IN THE GIRTH WELD. THE SECTION WAS REMOVED AND SENT FOR METALLURGICAL TESTING. THE REPAIR COST AFTER EXCAVATION WAS FOUND TO EXCEED 50,000. METALLURGICAL TESTING HAS BEEN COMPLETED. PLEASE SEE THE ATACHED METALLURGICAL ANALYSIS. ILI DATA WAS REVIEWED BY INTEGRITY TO DETERMINE IF SIMILAR CRACKING WAS PRESENT IN OTHER JOINTS. THEIR REVIEW OF THE ILI DATA INDICATED CRACKING DID NOT APPEAR TO BE PRESENT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120076 | 15572 | 2012-07-31 12:32 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2012-07-15 14:30 | 2012 |  |  | 29.4417 | -92.992 | 1017841 | 2012-07-15 15:00 |  | NATURAL GAS |  | 100 | 1219 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-07-15 16:00 | 2012-07-18 18:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-07-15 14:30 | 2012-07-17 20:30 | OFFSHORE | [28 empty] | 50 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EAST CAMERON | 47 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12.75 |  | 0.375 | 42000 | API 5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | STUPP | OTHER | COAL TAR ENAMEL CONCRETE COASTED | [27 empty] | 1980 | 1979 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 278 |  | NO | NO | NO |  | 0 | 0 | 3047 | 3498.8701 | 250 | 201.374207188161 | 110000 | 126313 | 6000 | 6889.8 | 0 | 0 |  |  | 119297 | 62958.4474843552 | 136903.044307188 | [8 empty] | 800 |  | 999 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 14004 | NO | [5 empty] | YES | SUBSEA TIE-IN | YES |  |  |  |  | YES | SUBSEA TIE-IN | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | OCEANEERING; STONE ENERGY; MMS/BSEE |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATING PRESSURES WERE NORMAL AND UNDER THE MAOP, PLUS THE LEAK WAS A SMALL PIN HOLE. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN | [5 empty] | YES | SUSPECTED MICROBIOLOGICAL DUE TO THE OFFSHORE ENVIRNOMENT |  |  | YES | A VISUAL INSPECTION BY DIVERS ONLY | YES | [5 empty] | YES | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | GARY L TAYLOR | COMPLIANCE SPECIALIST | gary_taylor@kindermorgan.com | 281-592-6436 | 281-592-8705 |  |  |  | GARY L TAYLOR | COMPLIANCE SPECIALIST | 281-592-6436 | gary_taylor@kindermorgan.com | TENNESSEE GAS PIPELINE WAS NOTIFIED OF A 20 FOOT DIAMETER RING OF BUBBLES IN THE VICINTY OF ITS 12 INCH SNG EC 46 LINE. DIVERS CONFIRMED A PINHOLE LEAK AT THE 4 O'CLOCK POSITION, 8 FEET FROM A FIELD JOINT. A REPAIR CLAMP WAS INSTALLED AND THE LINE WAS PLACED BACK INTO SERVICE.
2021-02-26 10:37 | NO | NO | GG (Gas Gathering) | 20120077 | 15843 | 2012-08-07 09:51 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2012-07-09 15:40 | 2012 |  |  | 28.2686 | -96.2792 | 1017226 | 2012-07-09 18:25 |  |  |  | 0 | 0 | 0.4 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE PIPELINE WAS NOT AFFECTED. THE LEAK WAS CAUSED BY AN SUMP THAT OVERFILLED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-07-09 16:45 | 2012-07-09 16:45 | OFFSHORE | [28 empty] | 60 | IN STATE WATERS | TX | MATAGORDA BAY | MI558 | CALHOUN |  |  |  | PLATFORM | INTERSTATE | OFFSHORE PLATFORM, INCLUDING PLATFORM-MOUNTED EQUIPMENT AND PIPING | PULSATION BOTTLE OR DRIP/DRIP COLLECTION DEVICE | [40 empty] | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | SUMP OVERFILLED | OTHER | [8 empty] | THE OSCILLATOR ON A SUMP PUMP FAILED. THIS CAUSED THE SUMP TO OVERFILL AND SMALL AMOUNT OF CONDENSATE TO DRIP OUT OF THE SUMP VENT. | CLASS 1 LOCATION | NO |  | 1 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 2296.6 | 1000 | 1148.3 | 0 | 0 |  |  | 3000 | 1581.3 | 3444.9 | [8 empty] | 1 |  | 1 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | OFFSHORE GATHERING | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE SUMP WAS NOT MONITORED BY SCADA | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | AN OSCILLATOR LIQUID SUMP COLLECTION PUMP FAILED | [15 empty] | YES | NORMAL WEAR | [161 empty] | MATTHEW STRATMANN | SR. PIPELINE COMPLIANCE SPECIALIST | mstratmann@eprod.com | 713-381-8209 |  |  |  |  | MATTHEW STRATMANN | SR. PIPELINE COMPLIANCE SPECIALIST | 713-381-8209 | mstratmann@eprod.com | A FISHERMAN REPORTED A SHEEN TO THE COAST GUARD AT 15:40 IN THE VICINITY OF ENTERPRISE'S X1-400 TOMCAT PLATFORM IN BLOCK MI558 OF MATAGORDA BAY. THE SHEEN WAS REPORTED TO ENTERPRISE BY THE COAST GUARD. AN ENTERPRISE TECHNICIAN WAS DISPATCHED BY HELICOPTER TO THE MI558 PLATFORM WERE HE CONFIRMED THE RELEASE AT 16:45. THE OSCILLATOR ON A LIQUID COLLECTION SUMP PUMP FAILED CAUSING CONDESATED TO DRIP OUT OF THE ATMOSPHERIC VENT. THE TECHNICIAN ISOLATED THE SUMP AND REMOVED THE PUMP FOR REPAIR. THE PUMP WAS REPLACED ON 7-12-2012.
2021-02-26 10:37 | NO | NO | GG (Gas Gathering) | 20120078 | 15839 | 2012-08-07 10:47 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2012-07-13 10:10 | 2012 |  |  | 28.2686 | -96.2792 | 1017619 | 2012-07-13 10:30 |  |  |  | 0 | 0 | 0.1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | A SUPPLY GAS REGULATOR WAS DRIPPING CONDESATE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-07-13 10:10 | 2012-07-13 10:10 | OFFSHORE | [28 empty] | 60 | IN STATE WATERS | TX | MATAGORDA BAY | MI558 | CALHOUN |  |  |  | PLATFORM | INTERSTATE | OFFSHORE PLATFORM, INCLUDING PLATFORM-MOUNTED EQUIPMENT AND PIPING | INSTRUMENTATION | [40 empty] | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | SUPPLY GAS REGULATOR | LEAK |  |  | OTHER | DRIP OFF OF INSTRUMENTATION | [5 empty] | CLASS 1 LOCATION | NO |  | 1 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 574.15 | 0 | 0 | 0 | 0 |  |  | 500 | 263.55 | 574.15 | [8 empty] | 850 |  | 1313 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | OFFSHORE GATHERING | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [25 empty] | YES | NORMAL WEAR | [161 empty] | MATTHEW STRATMANN | SR. PIPELINE COMPLIANCE SPECIALIST | mstratmann@eprod.com | 713-381-8209 |  |  |  |  | MATTHEW STRATMANN | SR. PIPELINE COMPLIANCE SPECIALIST | 713-381-8209 | mstratmann@eprod.com | AN ENTERPRISE TECHNICIAN WAS PERFORMING A PLATFORM CHECK AT MI558 PLATFORM ON ASSOCIATED WITH PIPELINE X1-400 TOMCAT. DURING HIS INSPECTION THE TECHNICIAN NOTICED A SMALL SHEEN ON THE WATER. THE TECHNICIAN FOUND THAT A SUPPLY GAS REGULATOR ON A LEVEL CONTROLLER HAD A SMALL LEAK THAT WAS CAUSING CONDENSATE TO SLOWLY DRIP INTO THE WATER. THE TECHNICIAN WAS AT THE PLATFORM THE DAY BEFORE AND DID NOT NOTICE ANY TYPE OF SHEEN. THE TECHNICIAN REMOVED THE REGULATOR AND PLUGGED THE SUPPY LINE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120079 | 15949 | 2012-08-10 15:14 | SUPPLEMENTAL FINAL | 602 | CENTERPOINT ENERGY GAS TRANSMISSION | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2012-07-14 09:34 | 2012 |  |  | 34.431 | -94.4492 | 1017745 | 2012-07-14 11:11 |  | NATURAL GAS |  | 5500 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELIEF BLOWING | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-07-14 09:48 | 2012-07-14 09:48 | ONSHORE | AR | 71937 | COVE | POLK | SURVEY STATION NO. | 3540+12 | COVE COMPRESSOR STATION | CS208 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | OTHER | RELIEF VALVE |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2008 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF BLOWING | CLASS 2 LOCATION | NO |  | 917 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 15675 | 12626.1627906977 | 0 | 0 | 900 | 1033.47 | 0 | 0 |  |  | 16575 | 13564.5062790698 | 13659.6327906977 | [8 empty] | 827 |  | 1000 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [204 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | [5 empty] | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | JIMMY CROSS | DOT WAIVER SPECIALIST | jimmy.cross@centerpointenergy.com | 3184293664 | 3184293927 |  |  |  | JOHNNY CAVITT | DOT COMPLIANCE MANAGER | 3184293606 | johnny.cavitt@centerpointenergy.com | CEGT COVE COMPRESSOR - ON 7/14/2012, AT APPROXIMATELY 9:34AM, A PRESSURE BLEED-OFF TRIGGERED AN UN-INTENDED EMERGENCY SHUT-DOWN (ESD) AT THE COMPRESSOR STATION. A CEGT TECHNICIAN FAILED TO RETURN ALL VALVES TO THEIR FOUND POSITION UPON COMPLETION OF THE WORK TASK RESULTING IN ACTIVATION OF THE COMPRESSOR ESD SYSTEM. UPON ACTIVATION OF THE COMPRESSOR ESD SYSTEM BOTH THE SUCTION AND DISCHARGE ESD VALVES FAILED TO CLOSE. AN INCIDENT INVESTIGATION FOUND THAT DEBRIS PRESENT IN THE VALVES CAUSED THEM TO BIND OR SEIZE EFFECTIVELY DISABLING OPERATION OF THE VALVES.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20120080 | 16739 | 2012-08-13 10:47 | SUPPLEMENTAL FINAL | 32296 | TARGA RESOURCES OPERATING LP | 811 LOUISIANA ST SUITE 2100 | HOUSTON | TX | 77002 | 2012-07-14 16:00 | 2012 |  |  | 29.319 | -93.4967 | 1017819 | 2012-07-15 10:19 |  | NATURAL GAS |  | 100 | 800 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-07-15 17:00 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-07-15 16:00 | 2012-07-18 10:00 | OFFSHORE | [28 empty] | 55 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST CAMERON | 188 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12 |  | 0.312 | 52000 | API5LX | SEAMLESS |  | UNKNOWN | EPOXY | [28 empty] | 1968 | 1968 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 300 |  | NO | NO | NO |  | 0 | 0 | 2600 | 2985.58 | 320 | 257.758985200846 | 170000 | 195211 | 5500 | 6315.65 | 0 | 0 |  |  | 178420 | 94143.7404439746 | 204769.988985201 | [8 empty] | 950 |  | 1300 | 192.619(A)(4) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | MANUAL | 101720 | NO | YES | [6 empty] | NO | [6 empty] | OFFSHORE GATHERING | NO |  |  |  |  | OTHER | OFFSHORE OPERATOR |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | TIM HUFFER | MANAGER REGULATORY COMPLIANCE | thuffer@targaresources.com | 3375834642 | 3375834630 |  |  |  | TIM HUFFR | MANAGER REGULATORY COMPLIANCE | 3375834642 | thuffer@targaresources.com | THE PRESSURE IN THE LINE SEGMENT WAS REDUCED FROM 950 PSIGTO APPROXIMATELY 300 PSIG AND BLOCKED IN. A BOLTED CLAMP WAS INSTALLED AT THE LOCATION OF THE LEAK. THE LEAK IS ASSUMED TO BE CAUSED BY MIC, BUT PIPELINE WAS NOT INTERNALLY INSPECTED TO CONFIRM CAUSES. PIPELINE SEGMENT REMAINS BLOCKED IN WITH NO GAS FLOW. TARGA PLANS TO SELL THE PIPELINE TO OFFSHORE PRODUCER. IF SELL IS NOT COMPLETED, THE SEGMENT OF THE SYSTEM WILL BE ABANDONED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120081 | 15757 | 2012-08-13 11:49 | SUPPLEMENTAL | 31604 | EQT MIDSTREAM | 625 LIBERTY AVEUNUE | PITTSBURGH | PA | 15222 | 2012-07-15 09:00 | 2012 |  |  | 40.2556 | -79.9611 | 1017814 | 2012-07-15 10:30 |  | NATURAL GAS |  | 22609 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELIEF VALVE VENTING NO NEED TO SHUT DOWN PIPELINE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-07-15 09:00 | 2012-07-15 09:00 | ONSHORE | PA | 15332 | FINLEYVILLE | WASHINGTON | SURVEY STATION NO. | H141 007+72 | H-125 TO H-141/HARTSON COMPRESSOR STATION | HARTSON COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1988 |  | CARBON STEEL |  | OTHER | [8 empty] | EXTENDED VENTING OF RELIEF VALVE | CLASS 3 LOCATION | NO |  | 150 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 63305 | 50991.976744186 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 63305 | 52865.6976744186 | 50991.976744186 | [8 empty] | 260 |  | 328 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  | YES | GAS CONTROLLER FOLLOWED PROPER PROTOCOL. WHEN NOTIFIED OF THE RELIEF VALVE ACTIVATION GAS CONTROLLER OPERATED A CONTROL VALVE TO REROUTE GAS AND LOWER PIPELINE PRESSURE | YES | YES | [7 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | RELIEF VALVE ACTIVATED AT SETPOING AND RELEASED GREATER THAN 3 MILLION CUBIC FEET OF NATURAL GAS | [147 empty] | JOE LOMBARDO | MANAGER COMPLIANCE | jlombardo@eqt.com | 412-395-3135 | 412-395-7071 |  |  |  | JOE LOMBARDO | MANAGER COMPLIANCE | 412-395-3135 | jlombardo@eqt.com | AT 9:00 A.M. ON JULY 15, 2012 AN EQT OPERATIONS EMPLOYEE DISCOVERED A RELIEF VALVE VENTING AT THE HARTSON COMPRESSOR STATION. UPON INVESTIGATION THE EMPLOYEE DETERMINED THE RELIEF VALVE HAD BEEN VENTING APPROXIMATELY TWO HOURS. THE OPERATIONS EMPLOYEE NOTIFIED GAS CONTROL. GAS CONTROL OPERATED A CONTROL VALVE TO REROUTE GAS FLOW AND REDUCE THE PIPELINE PRESSURE. THE RELIEF VALVE CEASED VENTING AT APPROXIMATELY 9:20 A.M. THE MAOP OF THE PIPELINE ON WHICH THE RELIEF VALVE IS LOCATED IS 328 PSIG. THE RELIEF VALVE ACTIVATED AT 286 PSIG AND LEVELED OFF AT 260 PSIG. A CALCULATION WAS PERFORMED THAT DETERMINED THE GAS LOSS EXCEEDED THE 3 MILLION CUBIC FOOT THRESHOLD FOR REPORTING AS PER CFR49 PART 191.3. EQT HAS REVISED THE NORMAL OPERATION OF THIS PIPELINE SYSTEM AS A CORRECTIVE ACTION TO PREVENT A REOCCURENCE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120082 | 16153 | 2012-08-13 12:20 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE CO (EL PASO) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2012-07-20 21:10 | 2012 |  |  | 30.4324 | -92.8752 | 1018458 | 2012-07-20 21:55 |  | NATURAL GAS |  | 11480 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-07-20 21:15 | 2012-07-21 22:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 4 | 2012-07-20 21:10 | 2012-07-20 21:10 | ONSHORE | LA | 70648 | KINDER | JEFFERSON DAVIS | SURVEY STATION NO. | 0+00 | CS 823 KINDER | 507C-100 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | MAINLINE | BALL |  | GROVE |  |  |  | 1977 | 1977 | CARBON STEEL |  | OTHER | [8 empty] | A MAIN LINE BLOCK VALVE FAILED TO FULLY CLOSE | CLASS 1 LOCATION | NO |  | 378 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 28700 | 23117.7589852008 | 16000 | 18372.8 | 2000 | 2296.6 | 0 | 0 |  |  | 46700 | 33455.0304439746 | 43787.1589852008 | [8 empty] | 878 |  | 936 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATING PRESSURES DID NOT EXCEED MAOP; | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [30 empty] | YES | SEVERE WEATHER - VALVE OPERATION NOT REPEATABLE | [161 empty] | MARTIN MULLER | COMPLIANCE SPECIALIST | martin_muller@kindermorgan.com | 205-325-3863 | 205-325-3508 |  |  |  | REJI GEORGE | DIRECTOR COMPLIANCE - CODES AND STANDARDS | 713-420-5433 | reji_george@kindermorgan.com | DUE TO SEVERE WEATHER, TENNESSEE GAS PIPELINE EXPERIENCED AN ESD AT STATION 823 ITS KINDER COMPRESSOR STATION. ONE BLOCK VALVE FAILED TO CLOSE COMPLETELY ALLOWING NATURAL GAS TO VENT AND EXCEED THE REPORTING REQUIREMENT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120083 | 15661 | 2012-08-16 10:02 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2012-07-12 10:20 | 2012 |  |  | 30.4124 | -91.8964 | 1018187 | 2012-07-18 14:37 |  | NATURAL GAS |  | 0 | 27515 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-07-12 16:45 | 2012-07-16 13:10 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-07-12 10:20 | 2012-07-12 12:50 | ONSHORE | LA | 70512 | NEAR ARNAUDVILLE | ST MARTIN | MILEPOST | 38.18 | INDEX 188 | ERATH TO ARNAUDVILLE 36" | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 2.375 |  | 0.218 | 35000 | UNKNOWN | OTHER | UNKNOWN | UNKNOWN | COAL TAR | [28 empty] | 1970 |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 44 |  | NO | NO | NO |  | 0 | 0 | 76800 | 88189.44 | 0 | 0 | 84500 | 97031.35 | 0 | 0 | 38000 | 43635.4 | TEMPORARY GAS SERVICE TO SUPPLY BREAUS BRIDGE TBS |  | 199300 | 105051.03 | 228856.19 | [8 empty] | 830 |  | 1000 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [5 empty] | MANUAL | 65525 | NO | [5 empty] | YES | THE PART THAT FAILED WAS ON A 2" BYPASS | YES |  |  |  |  | YES | 2" PIPING | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS MINOR ON SMALL DIAMETER PIPING AND WOULD NOT SHOW UP ON SCADA | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [7 empty] | YES | [14 empty] | YES | [63 empty] | NO | [63 empty] | YES | 1970 | 2160 | NO | [13 empty] | NO | [63 empty] | SHANNON MATTINGLY | OQ-PA COORDINATOR | shannon.mattingly@bwpmlp.com | 270-688-6357 | 270-688-5871 |  |  |  | JEFF MCMAINE | MANAGER CODES AND STANDARDS | 270-688-6361 | jeff.mcmaine@bwpmlp.com | CRACK IN THE 2" PIPE NEAR A WELD ATTACHING A SADDLE TO THE PIPE. THE 2' IS A BYPASS AROUND A 36" MAINLINE VALVE. INCIDENT INITIALLY WAS NOT THOUGHT TO EXCEED THE $50,000 THRESHOLD FOR REPORTING.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120084 | 16824 | 2012-08-17 08:23 | SUPPLEMENTAL | 602 | CENTERPOINT ENERGY GAS TRANSMISSION | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2012-07-24 13:46 | 2012 |  |  | 33.4348 | -93.6434 | 1018855 | 2012-07-24 16:05 |  | NATURAL GAS |  | 10300 | 1200 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | BLEW DOWN TO 25 PSI | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-07-24 15:23 | 2012-07-24 17:35 | ONSHORE | AR | 71835 | LEWISVILLE | LAFAYETTE | MILEPOST | 2470+45 | CEGT LINE A | 20640 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 6 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 18 |  | 0.25 | 24000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | ASPHALT | [28 empty] | 1948 | 1948 | CARBON STEEL |  | MECHANICAL PUNCTURE | 5.5 | 3 | [7 empty] | CLASS 1 LOCATION | NO |  | 233 |  | NO | NO | NO |  | 0 | 0 | 3636 | 4175.2188 | 30900 | 24889.8520084567 | 24825 | 28506.5475 | 0 | 0 | 0 | 0 |  |  | 59361 | 40806.2328463002 | 57571.6183084567 | [8 empty] | 278 |  | 350 | 192.619(A)(4) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 31606 | NO | YES | YES |  |  |  | YES | COUPLED | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | [8 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | GRADER/SCRAPER | DRAINAGE | NO |  |  | UNKNOWN/OTHER | NO | NO |  |  | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | JIMMY CROSS | DOT WAIVER SPECIALIST | jimmy.cross@centerpointenergy.com | 3184293664 | 3184293927 |  |  |  | JOHNNY CAVITT | DOT COMPLIANCE MANAGER | 3184293606 | johnny.cavitt@centerpointenergy.com | ON 7/24/2012 AT 13:26, CEGT SYSTEM CONTROL WAS NOTIFIED OF A POSSIBLE LEAK ON LINE A. CEGT PERSONNEL WERE DISPATCHED TO INVESTIGATE AND FOUND THAT A CONTRACTOR WAS CLEANING DITCHES FOR A THIRD PARTY AND THEY HIT CEGT'S PIPELINE. CEGT PERSONNEL REDUCED THE PRESSURE ON THE LINE AND INSTALLED A BOLT ON SLEEVE. THE REPAIR WAS MADE AND THE LINE WAS BACK IN SERVICE AT 21:17.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120085 | 15764 | 2012-08-23 10:52 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2012-08-03 10:13 | 2012 |  |  | 43.1487 | -93.1253 | 1019884 | 2012-08-03 13:32 |  | NATURAL GAS |  | 4300 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | PRIMARY REGULATOR SHUT IN AND SECONDARY REGULATOR PLACED IN-SERVICE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 140 | 2012-08-03 10:13 | 2012-08-03 10:35 | ONSHORE | IA | 50401 | MASON CITY | CERRO GORDO | MILEPOST | 14.158 | MASON CITY, IOWA TOWN BORDER STATION | STATION 733041 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1970 |  | CARBON STEEL |  | OTHER | [8 empty] | PRIMARY GAS REGULATOR HAD AN ACCUMULATION OF WELDING SLAG AND PIPELINE DIRT/DEBRIS IN THE SEAT AREA WHICH DID NOT ALLOW THE REGULATOR TO SEAL OFF PROPERLY AT SET PRESSURE. GAS PRESSURE CONTINUED TO RISE UNTIL THE RELIEF VALVE SET POINT WAS REACHED AND THE RELIEF VALVE OPENED DISCHARGING NATURAL GAS TO ATMOSPHERE | CLASS 3 LOCATION | NO |  | 69 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 12479 | 10051.7949260042 | 500 | 574.15 | 1000 | 1148.3 | 0 | 0 | REPAIR MATERIALS FOR REGULATOR & RELIEF VALVE AND LABOR COST. |  | 13979 | 11211.8022198732 | 11774.2449260042 | [8 empty] | 498 |  | 500 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | REGULATOR AND RELIEF VALVE SET POINTS ARE SET LOCALLY AND CONTROLLERS DO HAVE HAVE CAPABILITY TO CHANGE. THERE WAS NO PRIOR INDICATIONS OF PRESSURE FLUCTATIONS OR ALARMS FOR THE STATION. PRESSURE DID NOT EXCEED MAOP. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [25 empty] | YES | PIPELINE DEBRIS/DIRT PREVENTED PROPER CLOSURE OF PRESSURE REGULATOR SEAT | [161 empty] | BYRON H. WOOD | SR. PIPELINE SAFETY SPECIALIST | byron.wood@nngco.com | 402-398-7396 | 402-398-7606 |  |  |  | THOMAS CORRELL | SR DIRECTOR PIPELINE SAFETY AND RISK | 402-398-7715 | thomas.correll@nngco.com | ON AUGUST 3, 2012, AT APPROXIMATELY 10:13 A.M. LOCAL TIME NORTHERN NATURAL GAS COMPANY'S OPERATIONS COMMUNICATION CENTER, IN OMAHA, NE, RECEIVED A REPORT FROM THE CERRO GORDO COUNTY SHERIFF'S DEPARTMENT OF GAS BLOWING TO ATMOSPHERE AT THE MASON CITY, IOWA TOWN BORDER STATION. AT NEARLY THE SAME TIME NORTHERN'S GAS CONTROL RECEIVED A SCADA HIGH, HIGH INLET GAS PRESSURE ALARM FOR THE FACILITY. THE SHERIFF REPORTED THAT LAW AND FIRE DEPARTMENT PERSONNEL WERE ON-SITE AND THAT THEY WERE IN THE PROCESS OF BLOCKING OFF THE ROAD, BUSINESS ROUTE HIGHWAY 18 THAT GOES BY THE TOWN BORDER STATION, AND EVACUATING SEVERAL STORES IN THE IMMEDIATE AREA. APPROXIMATELY 140 PEOPLE WERE EVACUATED FROM BUSINESSES NEAR THE TOWN BORDER STATION. NORTHERN TECHNICIANS ARRIVED ON-SITE AT APPROXIMATELY 10:35 A.M., AND FOUND THE STATIONS INLET 4-INCH FISHER EZ RELIEF VALVE WAS VENTING. NATURAL GAS TO THE TOWN BORDER STATION IS DELIVERED FROM THE MASON CITY IAB72002 PIPELINE, WHICH HAS A MAOP OF 800 PSI. GAS PRESSURE INTO THE TOWN BORDER STATION IS CONTROLLED BY PRESSURE CONTROLLING REGULATORS OF NATURAL GAS FROM IAB72002 AND RELIEF VALVE PROTECTED PIPING, AT A DELIVERY GAS PRESSURE OF APPROXIMATELY 330 PSI INTO THE STATION, WHICH HAS A 500 PSI MAOP. THE STATION INLET RELIEF VALVE IS SET AT 490 PSI TO PROTECT THE STATIONS 500 PSI MAOP. THE STATIONS INLET PRIMARY REGULATOR RUN WAS ISOLATED AND THE SECONDARY REGULATOR INLET RUN WAS PLACED IN-SERVICE. THE RELIEF VALVE CONTINUED TO SEEP AND IT WAS ALSO ISOLATED TO ALLOW INSPECTION. THE STREET WAS REOPENED AT APPROXIMATELY 11:10 A.M. AND BUSINESSES WERE NOTIFIED THAT THE CONDITION HAD BEEN REMEDIATED. ON INSPECTION OF THE PRIMARY REGULATOR IT WAS FOUND THAT SMALL PIECES OF WELDING SLAG AS WELL AS SMALL PIPELINE DIRT AND DEBRIS WERE PREVENTING A POSITIVE SEAL ON THE REGULATOR. THIS ALLOWED THE GAS PRESSURE TO CONTINUE TO INCREASE UNTIL THE RELIEF VALVE SET POINT WAS REACHED AND THE RELIEF OPENED RELEASING GAS TO ATMOSPHERE. IN ADDITION, TO SIMILAR SMALL AMOUNT OF DEBRIS FOUND IN THE RELIEF VALVE, A WASHED OUT AREA ON THE PILOT SEAT WAS FOUND WHICH LIKELY CONTRIBUTED TO THE RELIEF VALVE NOT FULLY SEALING OFF WHICH LIKELY CONTRIBUTED TO THE RELIEF VALVE CONTINUING TO RELEASE GAS TO ATMOSPHERE EVEN WHEN THE PRIMARY REGULATOR WAS SHUT IN AND THE BACK-UP REGULATOR WAS PLACED IN SERVICE. THE PRIMARY REGULATOR AND THE RELIEF VALVE WERE INSPECTED, CLEANED AND REPAIRED, PILOTS REBUILT AND TESTED. REGULATOR STRAINERS DOWNSTREAM OF THE INLET REGULATION WERE ALSO CHECKED AND CLEANED OF MINIMAL DEBRIS. THE REPAIRED REGULATOR AND RELIEF SETUP WAS PLACED BACK IN-SERVICE AROUND 4:25 P.M. RECORDS INDICATE THAT THE LAST DATE OF INSPECTION ON THE REGULATORS AND RELIEF VALVE WAS COMPLETED ON JULY 18, 2012. THIS FACILITY IS NORMALLY A BACK-UP GAS SOURCE TO THE UTILITY AND ONLY FLOWS WHEN NECESSARY IN THE HEATING MONTHS TO SUPPLEMENT GAS SUPPLIES TO THE WEST SIDE OF MASON CITY, IOWA; HOWEVER, THE FACILITY HAD BEEN PLACED INTO FULL SERVICE ON AUGUST 2, 2012, AT THE REQUEST OF ALLIANT ENERGY SO THAT MODIFICATIONS TO THEIR SYSTEM, ELSEWHERE IN THE CITY, COULD BE COMPLETED. NOTIFICATIONS WERE MADE TO THE NATIONAL RESPONSE CENTER, TICKET NUMBER 1019884, TO THE IOWA UTILITY BOARD IN DES MOINES, IOWA AND THE PIPELINE AND HAZARDOUS MATERIALS SAFETY ADMINISTRATION IN KANSAS CITY. THERE WAS NO FIRE, NO EXPLOSION AND NO INJURIES. THIS REPORT IS BEING FILED AS THE QUANTITY OF GAS RELEASED EXCEEDED THE REPORTING LEVEL THRESHOLD AND THE SIGNIFICANT NUMBER OF PEOPLE EVACUATED. 10/09/2012 FILED SUPPLEMENT/FINAL PER JIM BUNN REVIEW WITH MINOR CHANGE TO LONGTIDUE READING AND CHANGING THE APPARENT CAUSE TO EQUIPMENT FAILURE. SUPPLEMENTAL/FINAL - UPDATED REPORT BY INDICATING TRANSMISSION IN E5F PER PHMSA REQUEST ON REPORT 20120085, DATED 8/23/2012.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120086 | 15765 | 2012-08-28 14:59 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2012-08-07 09:26 | 2012 |  |  | 41.6584 | -94.1763 | 1020240 | 2012-08-07 11:11 |  | NATURAL GAS |  | 2369 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-08-07 10:50 | 2012-09-15 13:30 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2012-08-07 09:26 | 2012-08-07 09:30 | ONSHORE | IA | 50233-6037 | REDFIELD | DALLAS | MILEPOST | 0.34 | REDFIELD UNDERGROUND STORAGE FIELD | RDU30801 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 86 |  | NO | [22 empty] | INTERSTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | PIPE | PIPE BODY | 10.75 |  | 0.365 | 42000 | API 5LX | LONGITUDINAL ERW - LOW FREQUENCY |  | UNKNOW | COAL TAR | [28 empty] | 1961 | 1961 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 12 | 48.4 |  | CLASS 1 LOCATION | NO |  | 162 |  | NO | NO | NO |  | 40000 | 45932 | 0 | 0 | 6895 | 5553.90063424947 | 113580 | 130423.914 | 10000 | 11483 | 10417 | 11961.8411 | OUTSIDE LABORATORY ANALYSIS |  | 180892 | 97471.7996725159 | 205354.655734249 | [8 empty] | 1254 |  | 1385 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ALTHOUGH THERE IS SCADA IN PLACE AND IT COVERS REDFIELD UNDERGROUND STORAGE FACILITIES THAT PARTICULAR PART OF THE SYSTEM IS NOT DIRECTLYMONITORED BY SCADA AND/OR A GAS CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | GENERAL CORROSION | [5 empty] | YES | CHEMICAL CORROSION RESULTING FROM H2S AND MOISTURE. |  |  | YES | LABORATORY ANALYSIS. | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | BYRON H. WOOD | SENIOR PIPELINE SAFETY SPECIALIST | byron.wood@nngco.com | 402-398-7396 | 402-398-7606 |  |  |  | THOMAS G. CORRELL | SENIOR DIRECTOR PIPELINE SAFETY AND RISK | 402-398-7715 | thomas.correll@nngco.com | ON AUGUST 7, 2012 AT APPROXIAMTELY 9:15 A.M. LOCAL TIME A SECTION OF 10-INCH DIAMETER PIPELINE IDENTIFIED AS RDU30801 NEAR MILE POST 0.34 AT THE REDFIELD, IOWA UNDERGROUND STORAGE FACILITY RUPTURED. THE PIPELINE FAILURE RESULTED IN A FIRE WHICH WAS EXTINGUISHED AT 10:51 A.M. LOCAL TIME WHEN THE FAILED SECTION OF PIPELINE WAS ISOLATED. EMERGENCY RESPONDERS FROM DALLAS COUNTY IOWA SECURED THE AREA UNTIL THE FIRE WENT OUT. PRESSURE ON THE LINE AT THE TIME OF THE FAILURE WAS APPROXIMATELY 1,254 PSI. THE MAXIMUM ALLOWABLE OPERATING PRESSURE FOR THE PIPELINE IS 1,385 PSI. INTERNAL CORROSION IS BELIEVED TO BE THE ROOT CAUSE OF THE PIPELINE FAILURE. THERE WERE NO INJURIES, NO EVACUATIONS AND NO LOSS OF SERVICE TO CUSTOMERS. TWO MIDAMERICAN ENERGY COMPANY UTILITY POWER POLES WERE DAMAGED. THE RUPTURE MEASURED APPROXIMATELY 48 FEET 4-INCHS IN LENGTH. A SECTION OF THE DAMAGED PIPE WAS IDENTIFIED AS THE RUPTURE ORIGIN. THE LINE OF FRACTURE TRAVELED LONGITUDINALLY THROUGH A SECTION OF CORRODED PIPE APPROXIMATELY 12-INCHS IN LENGTH. THE INTERNAL CORROSION OCCURRED AT THE 6 O'CLOCK POSITION WITH ABOUT 90% WALL LOSS. THE INVESTIGATION INDICATED THE FRACTURE EXTENDING WEST FROM THE RUPTURE SITE STOPPED AT A GIRTH WELD. THE FRACTURE EAST ENDED IN THE MIDDLE OF THE JOINT. NO EXTERNAL CORROSION OR EVIDENCE OF THIRD-PARTY DAMAGE WAS FOUND. THE INCIDENT WAS REPORTED TO THE NATIONAL RESPONSE CENTER (TICKET NUMBER 1020240) DATED 07-AUG-12. THE INCIDENT WAS ALSO REPORTED TO THE IOWA UTILITIES BOARD IN DES MOINES, IOWA AND THE PIPELINE AND HAZARDOUS MATERIALS SAFETY ADMINISTRATION IN KANSAS CITY. ADDITIONAL INVESTIGATION IS IN PROGRESS AS WELL AS FOLLOW UP ANALYSIS BY OUTSIDE LABORATORIES. IN ORDER TO ENSURE THAT THERE ARE NOT SIMILAR ISSUES REMAINING AT THE FACILITY NORTHERN IS NOW CONDUCTING IN-LINE INSPECTION OF SIMILAR PIPELINE SEGMENTS AT THE FACILITY. BAKER HUGHES IS THE INLINE INSPECTION CONTRACTOR. SUPPLEMENTAL/FINAL: SECTION 15 ENTERED DATE AND TIME OF RETURN TO SERVICE, PART B ITEM 11, CORRECTED DEPTH-OF-COVER, PART D ITEM 7 ENTERED FINAL ESTIMATED PROPERTY DAMAGE COSTS (7A THROUGH 7E). PART G ENTERED CAUSE OF INTERNAL CORROSION. APPROXIMATELY 108 FEET OF NEW COATED 10-INCH PIPE WAS INSTALLED AT THE RUPTURE SITE. AN ILI OF THE COMPLETE LINE WAS COMPLETED, WHICH RESULTED IN AN APPROXIMATE REPLACEMENT OF AN ADDITIONAL 100 FEET OF COATED 10-INCH PIPE. THE COMPLETE LINE WAS SUCCESSFULLY HYDRO-TESTED. THE LINE WAS PURGED AND PUT BACK INTO SERVICE AT APPROXIMATELY 13:30 ON SEPTEMBER 15, 2012. SUPPLEMENTAL/FINAL: UPDATED REPORT PER PHMSA REQUEST TO INDICATE TRANSMISSION IN E5F ON REPORT 20120086 DATED 8/28/2012.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120087 | 15914 | 2012-08-30 17:18 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 4720 PIEDMONT ROW DR. | CHARLOTTE | NC | 28210 | 2012-08-02 00:28 | 2012 |  |  | 36.1976 | -86.8363 | 1019694 | 2012-08-02 04:00 |  | NATURAL GAS |  | 441 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-08-02 01:45 | 2012-08-20 14:10 |  |  |  |  | NO |  |  |  |  | YES | [6 empty] | 500 | 2012-08-02 00:28 | 2012-08-02 01:00 | ONSHORE | TN | 37208 | NASHVILLE | DAVIDSON | MILEPOST | 0.76 | LINE M | LINE M | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12.75 |  | 0.25 | 42000 | API-5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | EPOXY | [28 empty] | 1982 | 1982 | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER |  | 30 | 12.7 |  | CLASS 3 LOCATION | YES | METHOD2 | 225 |  | NO | YES | NO |  | 162376 | 186456.3608 | 0 | 0 | 1547 | 1246.10359408034 | 79416 | 91193.3928 | 0 | 0 | 0 | 0 |  |  | 243339 | 128740.45537759 | 278895.85719408 | [8 empty] | 620 |  | 735 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 11377 | NO | [5 empty] | YES | AT THE TIME OF FAILURE LINE M WAS IN THE PROCESS OF BEING CONFIGURED TO ACCOMMODATE INTERNAL INSPECTION. THE INSTALLATION OF LAUNCHERS AND RECEIVERS WAS COMPLETED AND LINE WAS INTERNALLY INSPECTED PRIOR TO RE-COMMISSIONING. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE EVENT OCURRED DURING NORMAL PIPELINE OPERATIONS. THERE WERE NO ALARMS OR ALERTS PRIOR TO THE EVENT. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES | [6 empty] | YES | [10 empty] | YES | YES |  |  | YES | [63 empty] | NO | [63 empty] | NO |  |  | Yes, but the point of the Accident was not identified as a dig site |  | 2005 | [11 empty] | NO | [63 empty] | FARRIS BERRY | MANAGER - OPERATIONS PERFORMANCE | farris.berry@piedmontng.com | 704-731-4618 | 704-731-4098 |  |  |  | NEIL MOSER | DIRECTOR - OPERATIONS COMPLIANCE AND PERFORMANCE | 704-731-4351 | neil.moser@piedmontng.com | IN PIEDMONT NATURAL GAS' NASHVILLE OPERATIONS DISTRICT, AN EVENT OCCURRED ON A 12" TRANSMISSION (LINE M) PIPELINE THAT OPERATES BETWEEN THE BORDEAUX REGULATOR STATION AND COUNTY HOSPITAL REGULATOR STATION AT APPROXIMATELY 12:30 AM LOCAL TIME ON AUGUST 2, 2012. THE EVENT SITE IS NEAR THE INTERSECTION OF CLARKSVILLE HWY AND HWY 12. THERE WERE NO NOTED INJURIES OR FATALITIES FROM THIS EVENT. THE LOCAL FIRE DEPARTMENT EVACUATED AREA RESIDENCES. LANE CLOSURES DID OCCUR DUE TO DEBRIS FROM ESCAPING GAS. DAMAGE WAS SUSTAINED TO AREA STRUCTURES DUE TO DEBRIS FROM THE FORCE OF THE ESCAPING GAS. THE PIPELINE WAS OPERATING AT APPROXIMATELY 620 PSIG AT THE TIME OF THE EVENT. GAS CONTROL NOTED THE EVENT DUE TO SCADA ALARMS. NOTIFICATION WAS ALSO RECEIVED BY THE CALL CENTER FROM LOCAL RESIDENCES. FIRST RESPONDERS WERE DISPATCHED BY BOTH GROUPS. NASHVILLE OPERATIONS PERSONNEL ASSESSED THE SITUATION AND VALVED OFF THIS APPROXIMATE 2.1 MILE SECTION OF PIPELINE WHILE COORDINATING WITH GAS CONTROL TO ENSURE SYSTEM PRESSURE AND FLOW REQUIREMENTS WERE BEING MET. NOTIFICATIONS WERE MADE TO BOTH THE TENNESSEE REGULATORY AUTHORITY (TRA) AND THE NATIONAL RESPONSE CENTER BASED ON INITIAL ESTIMATES THAT COST WOULD EXCEED $50,000 FOR REPAIRS INCLUDING COST OF LOST GAS. SIX RESIDENTIAL CUSTOMER PREMISES WERE IMPACTED BY THE CLOSURE OF THIS SECTION OF PIPELINE. ALL IMPACTED CUSTOMERS WERE CONTACTED TO INFORM THEM OF THE SITUATION AND EXPECTATION OF OUTAGE TIMELINES. THERE WAS ALSO AN IMPACT TO VANDERBILT UNIVERSITY DUE TO THE REDUCTION IN OVERALL SYSTEM PRESSURES UNTIL ALTERNATIVE FLOW PATHS OCCURRED. LINE REPAIRS WERE MADE TO THE DAMAGED SECTION OF PIPELINE. INSTALLATION OF LAUNCHER AND RECEIVER WAS COMPLETED AND THE ENTIRE 2.1 MILES OF PIPELINE WAS SMART PIGGED WITH A CALIPER TOOL AND HYDROTESTED PRIOR TO BEING REINSTATED INTO SERVICE. THIS WORK EFFORT WAS COMPLETED AND LINE M WAS RETURNED TO FULL SERVICE ON AUGUST 20, 2012 AT APPROXIMATELY 2:00 PM LOCAL TIME. DNV, AN INDEPENDENT FORENSICS LABORATORY IN COLUMBUS, OHIO, INVESTIGATED THIS INCIDENT AND DETERMINED THAT MECHANICAL DAMAGE DURING ORIGINAL PIPELINE CONSTRUCTION OCCURRED AND CREATED LINEAR DENTS ON THE BOTTOM SIDE OF A 23-FOOT LENGTH OF THE PIPE. RE-ROUNDING CRACKS FORMED IN THE DENTS, THEN GREW LARGER OVER TIME AND NORMAL OPERATION OF THE PIPELINE, EVENTUALLY RESULTING IN THE FAILURE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120088 | 16411 | 2012-09-04 16:27 | SUPPLEMENTAL FINAL | 32005 | CROSSTEX LIG, LLC | 1722 ROUTH STREET SUITE 1300 | DALLAS | TX | 75201 | 2012-08-04 16:31 | 2012 |  |  | 30.0105 | -91.144 | 1019974 | 2012-08-04 16:31 |  |  |  | 0 | 26554 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-08-04 16:31 | 2014-05-21 22:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-08-04 16:31 | 2012-08-04 16:35 | ONSHORE | LA | 70341 | NAPOLEONVILLE | ASSUMPTION |  |  | P1530 WEEKS ISLAND TO ST.JAMES 36IN | GIBSON DISTRICT | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | THIRD PARTY UNDERGROUND STORAGE LEECHING | 108 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 36 |  | 0.438 | 60000 | API 5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | OTHER | PIPE IS EITHER COAL TAR COATED OR COAL TAR WITH CEMENT COATED. | [27 empty] | 1979 | 1977 | CARBON STEEL |  | OTHER | [8 empty] | NEARBY THIRD PARTY STORAGE CAVERN COLLAPSED CAUSING SINK HOLE TO EVOLVE NEAR PIPELINE SHIFTING THE SOIL AND CAUSING PIPELINE TO MOVE FROM ORIGINAL POSITION. | CLASS 1 LOCATION | NO |  | 786 |  | NO | NO | NO |  | 0 | 0 | 59800 | 68668.34 | 0 | 0 | 25000000 | 28707500 | 0 | 0 | 0 | 0 |  |  | 25059800 | 13209020.58 | 28776168.34 | [8 empty] | 770 |  | 1001 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 70963 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT INVOLVED LINE MOVEMENT ONLY WHICH CAN'T BE DETECTED BY GAS CONTROL. PRESSURE AND FLOW OF SYSTEM INDICATED NO ABNORMAL CHANGE OCCURRED. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [103 empty] | OTHER OUTSIDE FORCE DAMAGE | [9 empty] | NEARBY THIRD PARTY UNDERGROUND STORAGE CAVERN COLLAPSED CAUSING EARTH MOVEMENT ALONG OPERATORS PIPELINE ROW AND SHIFTING PIPELINE FROM ORIGINAL POSITION. | [251 empty] | CHARLES LIONBERGER | PIPELINE INTEGRITY SPECIALIST | charles.lionberger@crosstexenergy.com | 318-619-5681 | 318-619-5719 |  |  |  | WILLIAM WORLEY | DOT COMPLIANCE MANAGER | 214-721-9449 | william.worley@crosstexenergy.com | ON 8-3-12 GAS CONTROL RECEIVED INFORMATION THAT A SINK HOLE HAD FORMED NEAR CROSSTEX'S 36" PIPELINE AT BAYOU CORNE. IT WAS DETERMINED THAT THE SINK HOLE WAS 150 FT FROM CROSSTEX'S FACILITY. AT THIS TIME THE SINK HOLE WAS MONITORED AND NO CHANGES TO THE CROSSTEX FACILITY WERE MADE AND NO ABNORMAL OPERATING CONDITIONS WERE NOTICED. OPERATIONS CONTINUED NORMALLY. ON 8-4-12 CROSSTEX WAS NOTIFIED THAT THE SINK HOLE HAD EXPANDED IN THE DIRECTION OF THE CROSSTEX FACILITY AND AT 3:56PM DECISION WAS MADE TO BLOW DOWN THE FACILITY. ON 8-5-12 LINE PRESSURE WAS DOWN TO ZERO AND THE LINE DECLARED OUT OF SERVICE. THE CROSSTEX FACILITY REMAINS OUT OF SERVICE UNTIL ASSESSMENT OF THIRD PARTY STORAGE CAVERN IS COMPLETE. CROSSTEX BUILT A 5 MILE LOOP AROUND THE SINK HOLE AREA AND ON MAY 21, 2014 AT 22:00 HRS THE PIPELINE WAS PLACED BACK INTO SERVICE. THE ORIGINAL SECTION OF LINE WAS ABANDONED IN PLACE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120089 | 16754 | 2012-09-04 17:33 | SUPPLEMENTAL FINAL | 12696 | CYPRESS GAS PIPELINE COMPANY | 1100 LOUISIANA ST. | HOUSTON | TX | 77002 | 2012-08-06 13:35 | 2012 |  |  | 30.4936 | -91.1968 | 1020164 | 2012-08-06 14:23 |  | NATURAL GAS |  | 12350 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-08-06 14:05 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-08-06 13:37 | 2012-08-06 14:25 | ONSHORE | LA | 70802 | BATON ROUGE | EAST BATON ROUGE, WEST BATON ROUGE | MILEPOST | 232.8 | BRW #1, 580-0100 | MISSISSIPPI RIVER CROSSING #5 (BRW #1) | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | RIVER | 24 |  | YES | [6 empty] | YES | UNCASED | MISSISSIPPI RIVER | 5 | BELOW WATER, PIPE BURIED BELOW BOTTOM (NOT IN BORED/DRILLED CROSSING) | [11 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10 |  | 0.5 |  | UNKNOWN | OTHER | UNKNOWN | UNKNOWN | NONE | [28 empty] | 1949 | 1949 | CARBON STEEL |  | MECHANICAL PUNCTURE | 4 | 6 | [7 empty] | CLASS 1 LOCATION | NO |  | 148 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 24700 | 19895.7716701903 | 50000 | 57415 | 2000 | 2296.6 | 20000 | 22966 | COST OF SIDE SONAR/ COVER SURVEY |  | 96700 | 58578.0498942918 | 102573.37167019 | [8 empty] | 330 |  | 360 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 5000 | NO | [5 empty] | YES | MANIFOLD CROSSING | YES |  |  |  |  | YES | NO FOOTPRINT | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA PERSONNEL AND EQUIPMENT PERFORMED AS REQUIRED | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY BOATS, BARGES, DRILLING RIGS, OR OTHER MARITIME EQUIPMENT OR VESSELS SET ADRIFT OR WHICH HAVE OTHERWISE LOST THEIR MOORING | OTHER OUTSIDE FORCE DAMAGE | MARITIME EQUIPMENT OR VESSEL ADRIFT | [103 empty] | DAMAGE BY BOATS, BARGES, DRILLING RIGS, OR OTHER MARITIME EQUIPMENT OR VESSELS SET ADRIFT OR WHICH HAVE OTHERWISE LOST THEIR MOORING | [5 empty] | YES | LOW WATER LEVEL IN THE MISSISSIPPI RIVER | [254 empty] | NATHAN L. GRAY JR. | SENIOR PIPELINE COMPLIANCE SPECIALIST | ngray@eprod.com | 9854934629 |  |  |  |  | NATHAN L. GRAY JR. | SENIOR PIPELINE COMPLIANCE SPECIALIST | 9854934629 | ngray@eprod.com | RESPONSE GAS CONTROL CALLED OUT TECHNICIAN FOR PRESSURE DROP ON EAST SIDE OF MISSISSIPPI RIVER IN BATON ROUGE. A TECHNICIAN ALONG WITH MEASUREMENT SUPERVISOR FOUND THAT ONE OF THE RIVER CROSSING LINES HAD BLOWN OUT. THEY ISOLATED THE LINE AND LOCKED OUT THE VALVES. APPLICABLE STATE AND FEDERAL AGENCIES WERE CONTACTED. THE LINE(MISSISSIPPI RIVER CROSSING #5) IS CURRENTLY INACTIVE (IDLE). PLANS ARE BEING DEVELOPED TO BORE UNDER THE RIVER AND INSTALL A 24" LINE. THIS PROJECT IS CURRENTLY IN THE BID PROCESS AND SHOULD BE COMPLETED LAST QUARTER OF 2013. THE CAUSE OF THE RELEASE IS A BARGE STRIKING OUR PIPELINE. THE CREW HAVE SINCE BEEN ALERTED TO THE PRESENCE OF PIPELINES IN THE AREA AND PIPELINE SAFETY IS NOW DISCUSSED DURING CREW CHANGE MEETINGS. WE ARE WORKING WITH THE US COAST GUARD TO GET THE AREA BUOYED UNTIL WATER LEVELS RISE. WE PERFORMED A SIDE SCAN SONAR 8/17-8/20. THE RESULTS OF THIS SCAN INDICATED THAT THIS LINE WAS EXPOSED WITHIN 60 FT OF THE WATERS EDGE, BUT NOWHERE ELSE THROUGHOUT THE LINE. PER PHMSA REQUEST, PART C PIPE DATA HAS BEEN UPDATED. ALSO, PART E, PART H, AND PART I HAVE BEEN UPDATED. PLANS ARE BEING DEVELOPED TO BORE UNDER THE MISSISSIPPI RIVER AND INSTALL TWO 16" PIPELINES. THIS PROJECT IS CURRENTLY WAITING ON PERMITS TO BE APPROVED BY THE U.S. ARMY COPRS OF ENGINEERS. THIS PROJECT IS SCHEDULED TO BE COMPLETED BY END OF YEAR 2015. ONCE THE NEW PIPELINE CROSSINGS ARE IN PLACE, WE WILL ABANDON THE BRW #1 MISSISSIPPI RIVER CROSSING #5 PIPELINE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120090 | 15707 | 2012-09-06 14:10 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2012-08-16 16:20 | 2012 |  |  | 35.4602 | -100.9792 | 1021287 | 2012-08-16 17:57 |  | NATURAL GAS |  | 14590 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | [7 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-08-16 16:20 | 2012-08-16 16:20 | ONSHORE | TX | 79065 |  | GRAY | MILEPOST | 68 |  | RELIEF VALVE ON LINE #3044 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | OTHER | RELIEF VALVE |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | RELIEF VALVE | [8 empty] | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 365 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 40560 | 32670.9513742072 | 2747 | 3154.3801 | 262 | 300.8546 | 0 | 0 |  |  | 43569 | 35457.5026737844 | 36126.1860742072 | [8 empty] | 858 |  | 867 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [7 empty] | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS CAUSED BY A MECHANICAL FAILURE ON THE RELIEF VALVE | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | DEFECTIVE OR LOOSE TUBING OR FITTING | MATERIAL/WELD/EQUIP FAILURE | DEFECTIVE OR LOOSE TUBING/FITTING | [166 empty] | DEFECTIVE OR LOOSE TUBING OR FITTING | [35 empty] | YES | IMPROPER ASSEMBLY OR OVERTORQUE OF CONNECTING TUBING FITTING AT THE MANUFACTURER | [161 empty] | KRISTIN VAN DER LAAN | COMPLIANCE ENGINEER III | kristin_vanderlaan@kindermorgan.com | 303-914-7753 |  |  |  |  | JORGE TORRES | VICE PRESIDENT ENGINEERING | 713-369-9232 | No Email Address | GRAY COUNTY SHERIFF REPORTED TO EPNG GAS CONTROL A POSSIBLE RELIEF VALVE RELIEVING. EPNG EMPLOYEE WAS SENT TO INVESTIGATE. TRAFFIC WAS STOPPED ON COUNTY ROAD K UNTIL THE RELIEF VALVE WAS SHUT-IN AND THE AREA MADE SAFE. EPNG EMPLOYEE SHUT THE VALVE IN AT 17:06 CENTRAL TIME.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120091 | 16193 | 2012-09-10 13:13 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION LP (SPECTRA ENERGY CORP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2012-08-13 08:15 | 2012 |  |  | 28.2907 | -93.3531 | 1020906 | 2012-08-13 12:00 |  | NATURAL GAS |  | 400 | 13766 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-08-15 11:45 | 2012-08-17 18:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-08-13 08:15 | 2012-08-13 10:00 | OFFSHORE | [28 empty] | 195 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST CAMERON | 549 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 20 |  | 0.406 | 52000 | API-5L X-52 | SEAMLESS |  | US STEEL | OTHER | CONCRETE AND SOMASTIC | [27 empty] | 1975 | 1975 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 524 |  | NO | NO | NO |  | 0 | 0 | 41298 | 47422.4934 | 1200 | 966.596194503171 | 600000 | 688980 | 0 | 0 | 0 | 0 |  |  | 642498 | 339030.289964905 | 737369.089594503 | [8 empty] | 858 |  | 1440 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 106022 | NO | [5 empty] | YES | NO PLATFORM FROM WHICH TO LAUNCH/RECEIVE | YES |  |  |  |  | YES | NO PLATFORM FROM WHICH TO LAUNCH/RECEIVE | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | THIRD PARTY PLATFORM OPERATOR OBSERVATION |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS TOO SMALL TO BE IDENTIFIED BY CONTROL ROOM PERSONNEL. A REVIEW OF OPERATING RECORDS FOUND ABNORMAL OPERATING CONDITIONS DID NOT CAUSE OR CONTRIBUTE TO THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | deteschendorf@spectraenergy.com | 713-627-5573 | 713-386-4468 |  |  |  | RICK KIVELA | DIRECTOR OF OPERATIONAL COMPLIANCE | 713-627-6388 | rwkivela@spectraenergy.com | INDICATIONS OF BUBBLES ON THE WATER SURFACE IN WEST CAMERON 549 WERE REPORTED BY A PLATFORM OPERATOR ON AUGUST 13, 2012. UPON INVESTIGATION IT WAS DETERMINED THE LEAK WAS CAUSED BY A PINHOLE LEAK RESULTING FROM INTERNAL CORROSION. A LEAK CLAMP WAS INSTALLED FOR PERMANENET REPAIR.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120093 | 16110 | 2012-09-12 14:15 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2012-08-20 15:25 | 2012 |  |  | 29.2563 | -91.1783 | 1021656 | 2012-08-20 15:48 |  | NATURAL GAS |  | 3971 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-08-20 15:50 | 2012-10-01 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-08-20 15:25 | 2012-08-20 15:56 | ONSHORE | LA | 70360 | HOUMA | TERREBONNE | MILEPOST | 1.02 | SELA-I | SELA LINE C- 16" MOSQUITO BAY TO SHORELINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | COASTAL MARSH WETLANDS | 108 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.312 | 52000 | API 5L | SEAMLESS |  | UNKNOWN | OTHER | PART ENAMEL & PART CONCRETE COATING. | [27 empty] | 1963 | 1963 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 418 |  | NO | NO | NO |  | 0 | 0 | 12000 | 13779.6 | 522 | 420.469344608879 | 302000 | 346786.6 | 0 | 0 | 0 | 0 |  |  | 314522 | 165945.319661734 | 360986.669344609 | [8 empty] | 820 |  | 840 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 55440 | NO |  |  | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | AIR PATROL |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS SPOTTED BY A WILLIAMS EMPLOYEE WHILE ON ARIEL PATROL. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  | YES | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | YES | NOT APPLICABLE - NOT MAINLINE PIPE | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | JOHNNY LOPEZ | PIPELINE SAFETY SPECIALIST | johnny.lopez@williams.com | 7132152995 | 7132152222 |  |  |  | MARIE SOTAK | PIPELINE SAFETY MANAGER | 7132152111 | marie.sotak@williams.com | WHILE PERFORMING ARIEL PATROLS, BUBBLES WERE SPOTTED ON A TRANSCO ROW, WHERE TRANSCO OPERATES 4 PIPELINES. IMMEDIATLEY, THE NRC WAS CONTACTED ALONG WITH THE LOUISIANA STATE POLICE. TRANSCO OPERATORS HAVE ISOLATED THE LINE. THE CURRENT STATUS OF THE INCIDENT INVESTIGATION IS IN THE PRELIMINARY STAGE. THIS REPORT WILL BE UPDATED AS MORE DATA IS RECIEVED. SUPLEMENTAL LEAK REPORT UPDATE: - ON 9/27/2012 THE LEAK WAS INVESTIGATED THE LEAK WAS LOCATED ON A PIPELINE LOCATED IN A INLET TO THE GOM. - DIVERS EXPOSED THE LINE AND REMOVED EXTERNAL COATING (MASTIC AND CONCRETE). - WE IDENTIFIED AN ISOLATED PINHOLE LEAK AT THE SIX O'CLOCK POSITION IN A GIRTH WELD, - WE THEN REMOVED COATING AND CLEANED PIPE 3' ON BOTH SIDES OF THE GIRTH WELD - THE PIPE WAS VISUALLY INSPECTED AND A UT INSPECTION OF LEAK AREA WAS ALSO PREFORMENED.THE INSPECTIONS CONFIRMED AN ISOLATED PINHOLE LEAK. - THE DIVERS INSTALLED A MECHANICAL LEAK CLAMP. - THE ARE AFFECTED WAS RECOATED AND CHECKED FOR LEAKS. - THE LINE WAS THEN RETURNED TO SERVICE ON 10-1-2012. WE DETERMINED THAT THE CAUSE OF THE LEAK WAS AN ISOLATED PINHOLE LEAK AT 6'OCLOCK POSITION, ON A GIRTH WELD DUE TO INTERNAL CORROSION. THIS CONCLUSION IS CONSISTANT WITH TGPL'S FIELD TECHNICIANS EXPERIENCE WITH PREVIOUS INCIDENTS OF THIS NATURE.
2021-02-26 10:37 | YES | YES | GT (Gas Transmission) | 20120094 | 15889 | 2012-09-21 14:23 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION CORP | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2012-08-25 06:30 | 2012 |  |  | 41.3315 | -82.1081 | 1022148 | 2012-08-25 06:30 |  | NATURAL GAS |  | 651 |  |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 4 | 4 |  | YES |  | 2012-08-25 11:30 | 2012-08-25 16:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-08-25 07:43 | 2012-08-25 08:30 | ONSHORE | OH | 44035 | ELYRIA | LORAIN | MILEPOST | MS706502 | ELYRIA MEASURING STATION |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | OTHER | MEASURING STATION BUILDING |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | INSTRUMENTATION | [40 empty] | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 2 LOCATION | NO |  | 110 |  | NO | NO | NO |  | 8500 | 9760.55 | 0 | 0 | 1960 | 1578.77378435518 | 45000 | 51673.5 | 0 | 0 | 1500 | 1722.45 | MINOR COSTS WERE ASSOCIATED IN RETURNIG THE FACILITY BACK TO SERVICES. |  | 56960 | 30627.2864693446 | 64735.2737843552 | [8 empty] | 276 |  | 400 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | OTHER | DISTRIBUTION COMPANY PERSONNEL |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [260 empty] | GEORGE HAMATY | ENGINEER | ghamaty@nisource.com | 3043573728 | 3043573804 |  |  |  | MICHAEL HOFFMAN | MANAGER | 3043572548 | mikehoffman@nisource.com | ON THE MORNING OF SATURDAY, AUGUST 25, 2012 AT OR AROUND 06:30 AM, IT WAS REPORTED TO THE COMPANY MONITORING CENTER BY A DISTRIBUTION COMPANY PERSONNEL THAT A VEHICLE HAD DAMAGED THE STRUCTURE OF A MEASURING STATION NAMED ELYRIA DELIVERY POINT. THE VEHICLE WAS DRIVEN BY A TEENAGER AND ACCOMPANIED BY THREE OTHER SAME AGE MALE OCCUPANTS. THE FOUR OCCUPANTS HAD VARIOUS TYPES OF INJURIES THAT VARIED FROM CRITICAL TO MINOR. THAT NECESSITATED THEIR ADMITTANCE TO THE EMERGENCY ROOM. THE VEHICLE WAS IDENTIFIED TO BE STOLEN AND THE POLICE INVESTIGATION CONFIRMED THIS FACT. THE FACILITY WAS SHUT DOWN, THE INJURED OCCUPANTS OF THE VEHICLE WERE EXTRACTED BY LOCAL EMERGENCY RESPONDERS AND TRANSPORTED TO THE NEAREST MEDICAL FACILITY. AFTER EMERGENCY RESPONDERS CLEARED THE FACILITY, COMPANY PERSONNEL INSPECTED THE BUILDING AND CONDUCTED INSPECTIONS TO THE BUILDING AND THE PIPELINES INSIDE AND OUTSIDE THE BUILDING. THE INJURED DRIVER AND OTHER OCCUPANTS WERE RELEASED IN SEQUENCE FROM THE HOSPITAL BASED ON THEIR QUICK RECOVERY. THE BUILDING WAS REBUILT AND THE DAMAGED FENCE AROUND THE FACILITY WAS REPAIRED. THE DAMAGED GAUGES AND OTHER INTRUMENTATION SENSING LINES WERE REPLACED WITH THE DAMAGED 0.5-IN NIPPLE THAT WAS REPLACED. THE ENTIRE FACILITY PIPING WAS INSPECTED BY NDT (6, 8, 10 AND 16 INCH DIAMETER PIPING) FOR ANY EVIDENCE OF CRACKS OR OTHER DAMAGES. NO LEAK OR DAMAGE WAS IDNETIFIED SUBJECT TO THE NDT INSPECTION AND THE FACILITY WAS RETURNED TO SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120095 | 16219 | 2012-09-26 11:22 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION LP (SPECTRA ENERGY CORP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2012-09-01 16:30 | 2012 |  |  | 29.615 | -88.7753 | 1022952 | 2012-09-01 18:40 |  | NATURAL GAS |  | 1335 | 5000 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-09-08 12:00 | 2012-09-14 16:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-09-01 16:30 | 2012-09-04 20:00 | OFFSHORE | [28 empty] | 65 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | MAIN PASS | 94 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 |  | 0.5 | 46000 | API-5L X-46 | SEAMLESS |  | US STEEL | OTHER | CONCRETE AND SOMASTIC | [27 empty] | 1970 | 1970 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 419 |  | NO | NO | NO |  | 0 | 0 | 15000 | 17224.5 | 4005 | 3226.01479915433 | 425908 | 489070.1564 | 0 | 0 | 0 | 0 |  |  | 444913 | 235747.16282537 | 509520.671199154 | [8 empty] | 938 |  | 1440 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 58978 | NO | [5 empty] | YES | NO PLATFORM FROM WHICH TO LAUNCH TOOL | YES |  |  |  |  | YES | NO PLATFORM FROM WHICH TO LAUNCH TOOL | TRANSMISSION SYSTEM | YES | YES | NO | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | deteschendorf@spectraenergy.com | 713-627-5573 | 713-386-4468 |  |  |  | RICK KIVELA | DIRECTOR OF OPERATIONAL COMPLIANCE | 713-627-6388 | rwkivela@spectraenergy.com | INDICATIONS OF BUBBLES ON THE WATER SURFACE IN MAIN PASS BLOCK 94 WERE REPORTED ON SEPTEMBER 1, 2012 BY A HELICOPTER FLYING FOR SPECTRA ENERGY AS PART OF AN INITIAL INVESTIGATION FOLLOWING HURRICANE ISAAC. THE LEAK WAS CAUSED BY A PINHOLE LEAK RESULTING FROM INTERNAL CORROSION. REPAIR WAS COMPLETED BY INSTALLING LEAK CLAMPS. THE HURRICANE CAUSED A TEMPORARY LOSS OF COMMUNICATION TO THE PLATFORMS IN THE AREA OF THE LEAK. AS A RESULT, THE SCADA SYSTEM FOR THIS PIPELINE WAS NOT FULLY FUNCTIONAL AT THE TIME THE LEAK WAS DISCOVERED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120096 | 16220 | 2012-09-26 13:57 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION LP (SPECTRA ENERGY CORP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2012-09-06 17:00 | 2012 |  |  | 28.2888 | -93.3556 | 1023591 | 2012-09-06 18:00 |  | NATURAL GAS |  | 14750 | 9650 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-09-12 15:00 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-09-06 17:00 | 2012-09-07 08:00 | OFFSHORE | [28 empty] | 200 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST CAMERON | 549 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 20 |  | 0.406 | 52000 | API-5L X-52 | SEAMLESS |  | US STEEL | OTHER | CONCRETE AND SOMASTIC | [27 empty] | 1975 | 1975 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 524 |  | NO | NO | NO |  | 0 | 0 | 28950 | 33243.285 | 44250 | 35643.2346723044 | 600000 | 688980 | 0 | 0 | 0 | 0 |  |  | 673200 | 368472.504830867 | 757866.519672304 | [8 empty] | 878 |  | 1440 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 106022 | NO | [5 empty] | YES | NO PLATFORM FROM WHICH TO LAUNCH/RECEIVE TOOLS | YES |  |  |  |  | YES | NO PLATFORM FROM WHICH TO LAUNCH/RECEIVE | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | THIRD PARTY PLATFORM OPERATOR OBSERVATION |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS TOO SMALL TO BE IDENTIFIED BY CONTROL ROOM PERSONNEL. A REVIEW OF OPERATION RECORDS FOUND ABNORMAL OPERATING CONDITIONS DID NOT CAUSE OR CONTRIBUTE TO THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | deteschendorf@spectraenergy.com | 713-627-5573 | 713-386-4468 |  |  |  | RICK KIVELA | DIRECTOR OF OPERATIONAL COMPLIANCE | 713-627-6388 | rwkivela@spectraenergy.com | INDICATIONS OF BUBBLES ON THE WATER SURFACE IN WEST CAMERON BLOCK 549 WERE REPORTED BY A PLATFORM OPERATOR ON SEPTEMBER 6, 2012. THE LEAK WAS CAUSED BY A PINHOLE RESULTING FROM INTERNAL CORROSION. A LEAK CLAMP WAS INSTALLED FOR PERMANENT REPAIR.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120097 | 15878 | 2012-09-26 14:44 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2012-08-28 01:34 | 2012 |  |  | 42.2083 | -83.9684 | 1022457 | 2012-08-28 16:20 |  | NATURAL GAS |  | 34597.47 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | CLOSED BLOWDOWN VALVE TO CEASE UNINTENTIONAL RELEASE OF GAS | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-08-28 01:34 | 2012-08-28 02:30 | ONSHORE | MI | 48158 | MANCHESTER | WASHTENAW |  |  | FREEDOM COMPRESSOR STATION | BLOWDOWN VALVE 613 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 2003 |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENDED OPERATION OF BLOWDOWN VALVE | CLASS 2 LOCATION | NO |  | 312 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 202900 | 163435.306553911 | 448 | 514.4384 | 168 | 192.9144 | 0 | 0 |  |  | 203516 | 169765.496982664 | 164142.659353911 | [8 empty] | 703 |  | 800 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT OCCURRED DUE TO EQUIPMENT MALFUNCTION. CONTROLLER/CONTROL ROOM ISSUES DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES |  |  |  | YES | [24 empty] | YES | VALVE OPERATOR ACTUATED, LIKELY DUE TO SMALL SEAL LEAK AND PLUGGED VENTS | [161 empty] | ALAN M. CHICHESTER | GAS REGULATORY SERVICES ENGINEER | alan.chichester@cmsenergy.com | 989-791-5841 |  |  |  |  | TRACY GOBLE | REGULATORY AND COMPLIANCE MANAGER | 517-768-3187 | tracy.goble@cmsenergy.com | AT APPROXIMATELY 1:34 AM, BLOWDOWN VALVE 613 AT FREEDOM COMPRESSOR STATION TRAVELED OPEN AND VENTED GAS TO ATMOSPHERE THROUGH THE STATION EMERGENCY SHUT-DOWN VENT FOR APPROXIMATELY 1 HOUR AND 23 MINUTES. IN TOTAL, 34 MMCF WAS VENTED TO ATMOSPHERE. AFT THE INCIDENT, THE VALVE OPERATOR MANUFACTURER'S REPRESENTATIVE (WILSON VALVE SPECIALTIES) WAS CONTACTED FOR TESTING METHODS. THE BIFFI 745 PILOT CONTROL VALVE WAS TESTED PER THESE VERBAL INSTRUCTIONS. NO DEFECTS WERE FOUND DURING TESTING, AND THE VALVE WAS PLACED BACK IN SERVICE. AN INVESTIGATION TEAM WAS SUBSEQUENTLY FORMED TO EVALUATE THE INCIDENT; THE TEAM CONVENED SEPTEMBER 5TH, 2012. AS A RESULT OF THIS INVESTIGATION, THE PILOT CONTROL VALVE WAS TO BE REMOVED AND SENT FOR FURTHER TESTING ON SEPTEMBER 7TH, 2012, AT WHICH POINT A SECOND VENTING INCIDENT OCCURRED (NRC REPORT #1023618). THE VENDOR (WILSON VALVE SPECIALTIES) WAS CONTACTED AGAIN BY INVESTIGATION TEAM MEMBERS TO DETERMINE WHETHER THEY WERE AWARE OF SUCH INCIDENTS ON SIMILAR BLOWDOWN VALVES. THEY INDICATED ONE SUCH VENTING INCIDENT IN WISCONSIN, AND INDICATED THAT A MODIFICATION HAD BEEN SUBSEQUENTLY MADE TO THE VALVE IN QUESTION TO HOUSE THE PILOT VALVE IN A WEATHER-TIGHT ENCLOSURE IN ORDER TO PROTECT IT FROM WEATHER CONDITIONS. NEW VALVE ASSEMBLIES, WITH WEATHER ENCLOSURES PROTECTING THE PILOT VALVE AS WELL AS THE CONTROLLER, WERE THEN ORDERED FOR VALVE 613 AND THREE OTHER SIMILAR VALES AT THE STATION. THESE ASSEMBLIES HAVE BEEN INSTALLED AND ALL VALVES APPEAR TO BE FUNCTIONING AS DESIGNED. TESTING OF THE REPLACED VALVE 613 ASSEMBLY BY WILSON HAS SINCE REVEALED A SMALL SEAL LEAK ON THE BIFFI 745 PILOT CONTROL VALVE, AS WELL AS PLUGGED VENTS, WHICH LIKELY CONTRIBUTED TO THE VENTING INCIDENTS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120098 | 16956 | 2012-09-27 16:33 | SUPPLEMENTAL FINAL | 31978 | ATMOS PIPELINE - TEXAS | 5420 LBJ FREEWAY, SUITE 1500 | DALLAS | TX | 75240 | 2012-08-28 08:30 | 2012 |  |  | 33.1651 | -96.6306 | 102241 | 2012-08-28 09:20 |  | NATURAL GAS |  | 1500 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-08-28 09:20 | 2012-08-29 05:55 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2012-08-28 08:30 | 2012-08-28 08:30 | ONSHORE | TX | 75069 | MCKINNEY | COLLIN | SURVEY STATION NO. | 151+98 | D9-2-1-2 | D9-2-1-2 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 72 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 |  | 0.188 | 35000 | B-35 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | A&A COATING | EPOXY | [28 empty] | 1998 | 1998 | CARBON STEEL |  | MECHANICAL PUNCTURE | 2.5 | 9.7 | [7 empty] | CLASS 3 LOCATION | NO |  | 103 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 7500 | 6041.22621564482 | 50000 | 57415 | 75000 | 86122.5 | 500000 | 574150 | DESTROYED CONTRACTOR EQUIPMENT |  | 632500 | 335700.713530655 | 723728.726215645 | [8 empty] | 355 |  | 500 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 15074 | NO |  |  | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | NO | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LOCAL OPERATING PERSONNEL WERE ONSITE AT THE TIME OF THE INCIDENT | [12 empty] | NO |  |  | YES | 4 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [10 empty] | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 122140797 | TEXAS 811 | CONTRACT LOCATOR | NO | UNKNOWN/OTHER | YES | 22 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO VERIFY LOCATION BY TEST-HOLD (POT-HOLING) | [263 empty] | GREGG ELMORE | OPERATIONS SUPERVISOR | gregg.elmore@atmosenergy.com | 214-733-5121 | 214-733-5111 |  |  |  | MARC CHAPMAN | COMPLIANCE DIRECTOR | 214-206-2875 | marcus.chapman@atmosenergy.com | CONTRACTOR WAS USING A CATERPILLAR 324E TRACKHOE TO EXCAVATE A TAIL DITCH TO PULL PIPE THROUGH A BORE AT STATE HWY 5 AT SPUR 339 IN MCKINNEY, TEXAS. DURING THE EXCAVATION, A 6 INCH HIGH PRESSURE STEEL COMPANY MAIN WAS DAMAGED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120099 | 15624 | 2012-09-28 16:41 | SUPPLEMENTAL FINAL | 32296 | TARGA RESOURCES OPERATING LP | 811 LOUISIANA ST SUITE 2100 | HOUSTON | TX | 77002 | 2012-09-04 12:22 | 2012 |  |  | 31.0123 | -100.8748 | 1023290 | 2012-09-04 16:30 |  | NATURAL GAS |  | 7814 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | PIPELINE WAS SHUT DOWN FOR TESTING. | [6 empty] | NO |  |  |  |  | NO | [7 empty] | 2012-09-04 12:22 | 2012-09-04 13:30 | ONSHORE | TX | 76936 | ELDORADO | SCHLEICHER | MILEPOST | 5378 | ELDORADO TO SPRABERRY 16" |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.25 | 46000 | API5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  |  | COAL TAR | [28 empty] | 1957 | 1957 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  |  |  |  | CLASS 1 LOCATION | NO |  | 349 |  | NO | NO | NO |  | 2000 | 2296.6 | 0 | 0 | 27000 | 21748.4143763214 | 2000 | 2296.6 | 500 | 574.15 | 0 | 0 |  |  | 31500 | 24919.5187103594 | 26915.7643763214 | [8 empty] | 952 |  | 1002 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 68640 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE TESTING OF THE PIPELINE WAS IN PROGRESS AT THE TIME OF THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  |  |  |  | YES | [5 empty] | YES |  |  |  | YES | YES | 1957 | YES | YES | YES |  |  |  | 2011 |  |  |  | NO | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | WILL BRYANT | SR. ESANDH SPECIALIST | wbryant@targaresources.com | 325-535-8112 | 325-535-8102 |  |  |  | TIM HUFFER | MANAGER REGULATORY COMPLIANCE | 337-583-4642 | thuffer@targaresources.com | INTEGRITY PRESSURE TESTING IN ACCORDANCE WITH TEXAS TITLE 16, CHAPTER 8, SUBCHAPTER B WAS BEING CONDUCTED ON 9/4/12. THE PRESSURE TEST ON THE PIPELINE WAS TO BE AT 1152 FOR 8 HRS. AS THE PIPELINE WAS BEING PRESSURED UP, A RUPTURE OF THE LINE OCCURRED AT APPROXIMATELY 952 PSIG ON THE PIPELINE. THE CAUSE OF THE RUPTURE WAS DUE TO EXTERNAL CORROSION ON THE PIPELINE. WHEN THE PIPELINE WAS RUPTURED, PERSONNELL WERE IN THE AREA TO ISOLATE VALVES. IT WAS DETERMINED 7,814 MCF WAS LOS IN THE BLOWOUT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120100 | 15625 | 2012-10-03 14:35 | ORIGINAL FINAL | 32296 | TARGA RESOURCES OPERATING LP | 811 LOUISIANA ST SUITE 2100 | HOUSTON | TX | 77002 | 2012-09-07 14:29 | 2012 |  |  | 31.0087 | -100.8711 | 1023695 | 2012-09-27 16:50 |  | NATURAL GAS |  | 6518 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | PIPELINE WAS SHUT DOWN FOR TESTING. | [6 empty] | YES |  |  |  |  | YES | [6 empty] | 0 | 2012-09-07 14:29 | 2012-09-07 14:38 | ONSHORE | TX | 76936 | ELDORADO | SHLEICHER | MILEPOST | 5062 | ELDORADO TO SPRABERRY |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.25 | 46000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1957 | 1957 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  |  |  |  | CLASS 1 LOCATION | NO |  | 349 |  | NO | NO | NO |  | 6900 | 7923.27 | 0 | 0 | 23000 | 18526.4270613108 | 12000 | 13779.6 | 1000 | 1148.3 | 0 | 0 |  |  | 42900 | 29696.4781606765 | 41377.5970613108 | [8 empty] | 1040 |  | 1002 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE EXCEEDED MAOP, BUT DID NOT EXCEED THE APPLICABLE ALLOWANCE IN 192.201 | NO |  |  |  |  | MANUAL | MANUAL | 68640 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE TESTING OF THE PIPELINE WAS IN PROGRESS AT THE TIME OF THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION | [6 empty] | YES | EXTERNAL CORROSION |  |  | YES |  |  |  | YES | YES | 1957 | YES | YES | YES |  |  |  | 2011 |  |  |  | NO | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | WILL BRYANT | SR. ESANDH SPECIALIST | wbryant@targaresources.com | 325-535-8112 | 325-535-8102 |  |  |  | TIM HUFFER | MANAGER REGULATORY COMPLIANCE | 337-583-4642 | thuffer@targaresources.com | INTEGRITY PRESSURE TESTING IN ACCORDANCE WITH TEXAS TITLE 16, CHAPTER 8, SUBCHAPTER B WS BEING CONDUCTED ON 9/7/12. THE PRESSURE TEST ON THE PIPELINE WAS TO BE AT 1152 FOR 8 HRS. AS THE PIPELINE WAS BEING PRESSURED UP, A RUPTURE OF THE LINE OCCURRED (AT APPROXIMATELY 1,040 PSIG ON THE PIPELINE).THE CAUSE OF THE RUPTURE WAS DUE TO EXTERNAL CORROSION ON THE PIPELINE. WHEN THE PIPELINE RUPTURED, PERSONNEL WERE IN THE AREA TO ISOLATE VALVES. AFTER THE EXPLOSION A FIRE WAS STARTED, WHICH THEN STARTED A GRASS FIRE. THE SCHLEICHER COUNTY VFD AND IRION COUNTY VFD RESPONDED TO THE FIRE ALONG WITH THE IRION COUNTY SHERIFF DEPARTMENT. IT WAS CALCULATED THAT 6,518 MCF WAS LOST IN THE BLOW-OUT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120101 | 15877 | 2012-10-04 16:36 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2012-09-07 03:01 | 2012 |  |  | 42.2083 | -83.9684 | 1023618 | 2012-09-07 08:14 |  | NATURAL GAS |  | 15792 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | CLOSED BLOWDOWN VALVE TO CEASE UNINTENTIONAL RELEASE OF GAS | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-09-07 03:05 | 2012-09-07 03:25 | ONSHORE | MI | 48158 | MANCHESTER | WASHTENAW |  |  | FREEDOM COMPRESSOR STATION | BLOWDOWN VALVE 613 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 2003 |  | CARBON STEEL |  | OTHER | [8 empty] | UNITENDED OPERATION OF BLOWDOWN VALVE | CLASS 2 LOCATION | NO |  | 312 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 92614 | 74600.2832980972 | 28996 | 33296.1068 | 168 | 192.9144 | 0 | 0 |  |  | 121778 | 92713.8454570825 | 108089.304498097 | [8 empty] | 709 |  | 800 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT OCCURRED DUE TO EQUIPMENT MALFUNCTION. CONTROLLER/CONTROL ROOM ISSUES DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES |  |  |  | YES | [24 empty] | YES | VALVE OPERATOR ACTUATED, LIKELY DUE TO SMALL SEAL LEAK AND PLUGGED VENTS | [161 empty] | ALAN M. CHICHESTER | GAS REGULATORY SERVICES ENGINEER | alan.chichester@cmsenergy.com | 989-791-5841 |  |  |  |  | TRACY A. GOBLE | REGULATORY AND COMPLIANCE MANAGER | 517-768-3187 | tracy.goble@cmsenergy.com | AT APPROXIMATELY 3:01 AM, BLOWDOWN VALVE 613 AT FREEDOM COMPRESSOR STATION TRAVELED OPEN AND VENTED GAS TO ATMOSPHERE THROUGH THE STATION EMERGENCY SHUT-DOWN VENT FOR APPROXIMATELY 35 MINUTES. IN TOTAL, 15MMCF VENTED TO ATMOSPHERE. CONTACT WITH THE VENDOR (WILSON VALVE SPECIALTIES), PREVIOUSLY INITIATED DUE TO A SIMILAR INCIDENT ABOUT TEN DAYS BEFOREHAND (NRC REPORT #1022457), WAS RESUMED TO DETERMINE WHETHER THEY WERE AWARE OF SUCH INCIDENTS ON SIMILAR BLOWDOWN VALVES. THEY INDICATED ONE SUCH VENTING INCIDENT IN WISCONSIN, AND INDICATED THAT A MODIFICATION HAD BEEN SUBSEQUENTLY MADE TO THE VALVE IN QUESTION TO HOUSE THE PILOT VALVE IN A WEATHER-TIGHT ENCLOSURE IN ORDER TO PROTECT IT FROM WEATHER CONDITIONS. NEW VALVE ASSEMBLIES, WITH WEATHER ENCLOSURES PROTECTING THE PILOT VALVE AS WELL AS THE CONTROLLER, WERE THEN ORDERED FOR VALVE 613 AND THREE OTHER SIMILAR VALES AT THE STATION. THESE ASSEMBLIES HAVE BEEN INSTALLED AND ALL VALVES APPEAR TO BE FUNCTIONING AS DESIGNED. TESTING OF THE REPLACED VALVE 613 ASSEMBLY BY WILSON HAS SINCE REVEALED A SMALL SEAL LEAK ON THE BIFFI 745 PILOT CONTROL VALVE, AS WELL AS PLUGGED VENTS, WHICH LIKELY CONTRIBUTED TO THE VENTING INCIDENTS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120103 | 16351 | 2012-10-05 09:23 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2012-09-14 11:55 | 2012 |  |  | 32.5147 | -90.0841 | 1024433 | 2012-09-14 12:30 |  | NATURAL GAS |  | 0.01 | 131 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | LINE PRESSURE WAS LOWERED UNTIL REPAIRS WERE MADE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-09-14 11:55 | 2012-09-14 11:55 | ONSHORE | MS | 39046 | GLUCKSTADT | MADISON | MILEPOST | 11.01 | CANTON 6" | INDEX 301-18 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | IN OR SPANNING AN OPEN DITCH |  |  |  | YES | [6 empty] | YES | UNCASED | UNNAMED | 4 | BELOW WATER, PIPE ON OR ABOVE BOTTOM | [11 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | REPAIR SLEEVE OR CLAMP | [38 empty] | 2012 |  | CARBON STEEL |  | LEAK |  |  | OTHER | SLEEVE LEAKING | [5 empty] | CLASS 1 LOCATION | NO |  | 83 |  | NO | NO | NO |  | 0 | 0 | 250 | 287.075 | 2500 | 2013.74207188161 | 1100000 | 1263130 | 500 | 574.15 | 0 | 0 |  |  | 1103250 | 582293.062843552 | 1266004.96707188 | [8 empty] | 346 |  | 405 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 3000 | NO |  |  | YES |  |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | BOLT-ON CLAMP | [15 empty] | YES | BOLT ON CLAMP SEAL LEAKED; WAS IN SPAN AT DITCH. BOX SAG REPLACED DITCH XING. | [161 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 2706886361 | jeff.mcmaine@bwpmlp.com | BOLT ON SLEEVE THAT WAS INSTALLED IN FEBRUARY WAS FOUND LEAKING (SMALL LEAK BUBBLING IN WATER). AFTER EXAMINATION IT WAS DETERMINED THAT THE LEAK COULD NOT BE REPAIRED SO A REPLACEMENT OF PIPE WILL BE BE INSTALLED. 12-18-13 REPLACEMENT OF IMPACTED SEGMENT OF PIPE WAS COMPLETED ON JULY 23, 2013. 3-17-14 REVISED SECTION G8 TO CORRECT SUB-CAUSE DESCRIPTION. 4-9-14 REVISED SECTION G8 AT PHMSA'S REQUEST.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120104 | 16239 | 2012-10-05 15:34 | SUPPLEMENTAL FINAL | 207 | ALASKA PIPELINE CO | 3000 SPENARD ROAD P.O. BOX 190288 | ANCHORAGE | AK | 99519 | 2012-09-05 17:45 | 2012 |  |  | 61.2296 | -149.7117 | 1023478 | 2012-09-05 19:57 |  | NATURAL GAS |  | 7950 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | OVERPRESSURE RELIEF OPENED. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-09-05 17:47 | 2012-09-05 18:47 | ONSHORE | AK | 99519 | ANCHORAGE |  | SURVEY STATION NO. | A505 | EAST ANCHORAGE GATE STATION | A24 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [40 empty] | CARBON STEEL |  | OTHER | [8 empty] | APC'S EAG STATION INCLUDES A GAS DELIVERY SALES POINT TO MUNICIPAL LIGHT AND POWER'S STATION NUMBER 2. HIGH WINDS IN THE ANCHORAGE BOWL CAUSED NUMEROUS POWER SYSTEM FAULTS TO OCCUR. THE POWER SYSTEM FED BY MLP 2 WAS INTERRUPTED DUE TO THE FAULT CONDITIONS, INTERRUPTING BOTH GENERATION AND ALSO POWER DELIVERY TO THE APC EAG STATION. ON IMMEDIATE CURTAILMENT OF GAS TO MLP 2, REGULATOR MALFUNCTION CAUSED THE 460 PSI SYSTEM TO OVERPRESSURE FOLLOWED BY OPENING OF THE OVERPRESSURE RELIEF. | CLASS 3 LOCATION | NO |  | 178 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 48000 | 38663.8477801269 | 0 | 0 | 500 | 574.15 | 0 | 0 |  |  | 48500 | 40348.1165961945 | 39237.9977801268 | [8 empty] | 500 |  | 460 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE EXCEEDED MAOP, BUT DID NOT EXCEED THE APPLICABLE ALLOWANCE IN 192.201 | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | NO | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) | [11 empty] | YES | BACK UP BATTERIES AT EAG WERE NOT CAPABLE OF CONTINUED SCADA SURVEILLANCE. | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | [52 empty] | HIGH WINDS | [5 empty] | YES |  |  |  | YES | EXTREME HIGH WINDS IN EXCESS OF 120 MPH. | [301 empty] | PAUL GARDNER | ENGINEER | paul.gardner@enstarnaturalgas.com | 907-334-7755 | 907-334-0053 |  |  |  | JOHN LAU | DIRECTOR OF TRANSMISSION OPERATIONS | 907-264-3736 | john.lau@enstarnaturalgas.com | INCIDENT: RELEASE OF GAS AT APC EAST ANCHORAGE GATE SITE DUE TO OVER PRESSURE ON 460 PSI SYSTEM DATE: SEPTEMBER 5, 2012 VOLUME RELEASED: 7.95 MILLION CUBIC FEET CHRONOLOGY OF EVENTS : WEATHER CONDITIONS: EXTREMELY HIGH WIND CONDITIONS IN EXCESS OF 120 MPH CAUSED NUMEROUS POWER OUTAGES AND SHUT DOWN OF POWER GENERATION STATIONS THROUGHOUT THE COOK INLET. TIMES ARE ESTIMATED +/- 2 MINUTES. 17:42 LOST POWER TO EAST ANCHORAGE GATE STATION ( EAG ) 17:42 SIGNIFICANT LOSS OF LOAD TO MLP POWER PLANT NUMBER 2 DUE TO FAULT CONDITIONS ON POWER SYSTEM 17:45 RELIEF OPENED ON 460 PSI SYSTEM AT EAST ANCHORAGE GATE DUE TO OVERPRESSURE 17:47 RELEASE OF GAS REPORT CALLED INTO ENSTAR (APC) DISPATCH 17:59 TECHNICIANS DISPATCHED TO EAG TO INVESTIGATE CAUSE 18:47 TECHNICIAN ON SITE AND CONTROLLED INCIDENT MITIGATING CIRCUMSTANCES APC'S EAG STATION INCLUDES A GAS DELIVERY SALES POINT TO MUNICIPAL LIGHT AND POWER'S STATION NUMBER 2. HIGH WINDS IN THE ANCHORAGE BOWL ON THE EVENING OF SEPTEMBER 5 CAUSED NUMEROUS POWER SYSTEM FAULTS TO OCCUR. THE POWER SYSTEM FED BY MLP 2 WAS INTERRUPTED DUE TO THE FAULT CONDITIONS, INTERRUPTING BOTH GENERATION AND ALSO POWER DELIVERY TO THE APC EAG STATION. BACK UP BATTERIES AT EAG WERE NOT CAPABLE OF CONTINUED SCADA SURVEILLANCE. ON IMMEDIATE CURTAILMENT OF GAS TO MLP 2, REGULATOR MALFUNCTION CAUSED THE 460 PSI SYSTEM TO OVERPRESSURE FOLLOWED BY OPENING OF THE OVERPRESSURE RELIEF. RESPONSE TIME WAS GREATER THAN WOULD NORMALLY BE EXPECTED DUE TO TRAFFIC CONDITIONS AGAIN CAUSED AGAIN TO LOSS OF POWER GENERATION.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120105 | 16034 | 2012-10-19 13:56 | SUPPLEMENTAL FINAL | 5304 | FLORIDA GAS TRANSMISSION CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2012-09-24 13:50 | 2012 |  |  | 28.5672 | -96.854 | 1025554 | 2012-09-25 16:41 |  | NATURAL GAS |  | 750 | 2486 | 1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-09-24 17:26 | 2012-09-24 19:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-09-24 13:50 | 2012-09-24 15:40 | ONSHORE | TX | 77979 | PORT LAVACA | CALHOUN | MILEPOST | 174.75/2-4 | FGT 20"/TXMWA-2 | 2-4-AA / TXMWA-2-4 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.281 | 52000 | API-5LX | LONGITUDINAL ERW - LOW FREQUENCY |  | A.O. SMITH | COAL TAR | [28 empty] | 1959 | 1959 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 430 |  | NO | NO | NO |  | 0 | 0 | 7806 | 8963.6298 | 2355 | 1896.94503171247 | 80000 | 91864 | 0 | 0 | 0 | 0 |  |  | 90161 | 48249.1916486258 | 102724.574831712 | [8 empty] | 862 |  | 975 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | AUTOMATIC | 73212 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | AIR PATROL |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SMALL LEAK DISCOVERED BY PATROL DURING ROUTINE FLIGHT. LEAK CONFIRMED BY AREA PERSONNEL. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1959 | YES | YES | YES | YES | YES |  | 2012 | 2012 | 2012 |  | NO | [190 empty] | YES | YES | [6 empty] | 1997 | [55 empty] | YES | 1959 | 1227 | NO | [13 empty] | NO | [63 empty] | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 281-714-2231 | 281-714-2176 |  |  |  | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | 281-714-2231 | nathan.hlavaty@energytransfer.com | MONDAY SPETEMBER 24TH, 2012 DURING A ROUTINE AERIAL PATROL, THE PILOT IDENTIFIED AN AREA OF DEAD VEGITATION WITH A SMALL HOLE IN THE GROUND ON THE ROW UPSTREAM OF THE PORT LAVACA STATION. AREA PERSONNEL WERE DISPATCHED TO THE LOCATION, AND CONFIRMATION WAS MADE THAT THE FGT 20" MAINLINE DID HAVE A LEAK. AREA PERSONNEL ISOLATED THE PIPELINE SECTION AND NOTIFICATIONS WERE MADE. PLANS WERE DEVELOPED TO INVESTIGATE AND REPAIR THE PIPELINE. A SECTION OF PIPE WAS REPLACED AND THE PIPELINE SECTION PLACE BACK IN SERVICE SEPTEMBER 28TH, 2012. **THIS REPORT IS BEING SUBMITTED IN RESPONSE TO PHMSA'S REQUEST, (DOCKET ID PHMSA-2013-0028), FOR SUPPLEMENTAL REPORTS FROM OPERATORS WHO SUBMITTED REPORTS FOR INCIDENTS OCCURRING AFTER JANUARY 1, 2010, WITH ANY OF THE FOLLOWING: (1) ``PIPE GIRTH WELD'' WAS SELECTED AS THE ``ITEM INVOLVED IN INCIDENT'' IN PART C3 OF THE REPORT. THE REVISED REPORT COLLECTS DATA ABOUT THE PIPE ADJACENT TO THE GIRTH WELD. (2) ``FUNCTION OF PIPELINE SYSTEM'' IS NULL IN PART E5F OF THE REPORT. THE REVISED REPORT COLLECTS THE FUNCTION OF THE PIPELINE SYSTEM FOR ALL INCIDENTS.** THIS SUPPLEMENTAL REPORT IS TO ACKNOWLEDGE THAT THE TWO RELEVANT SECTIONS IN PHMSA'S REQUEST HAVE BEEN REVIEWED AND NO FURTHER ACTIONS WERE NEEDED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120107 | 16085 | 2012-10-26 13:44 | SUPPLEMENTAL FINAL | 3 | ACADIAN GAS PIPELINE SYSTEM | 1100 LOUISIANA ST. | HOUSTON | TX | 77002 | 2012-09-28 06:50 | 2012 |  |  | 32.2043 | -93.4897 | 102586 | 2012-09-28 07:50 |  | NATURAL GAS |  | 0 | 0.27 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-09-28 06:50 | 2012-10-04 09:33 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2012-09-28 06:50 | 2012-09-28 06:50 | ONSHORE | LA | 71051 | SHREVEPORT | RED RIVER |  |  | RED RIVER COMPRESSOR STATION |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2010 |  | CARBON STEEL |  | OTHER | [8 empty] | FIRE | CLASS 1 LOCATION | NO |  | 419 |  | NO | NO | NO |  | 0 | 0 | 635 | 729.1705 | 0 | 0 | 61000 | 70046.3 | 2500 | 2870.75 | 27000 | 31004.1 | ENVIRONMENTAL REMEDIATION |  | 91135 | 48037.2585 | 104650.3205 | [8 empty] | 1033 |  | 1440 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS A FIRE, WHICH WOULD NOT HAVE BEEN CAUGHT BY SCADA. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | SMALL FIRE CAUSED ESD OF UNIT #302. COMPRESSOR OIL HAD LEAKED INTO STATION BLOW DOWN PIPING, AND WHEN THE STAION BLEW DOWN, THE OIL AND GAS MIXTURE IGNITED. | [147 empty] | NATHAN L. GRAY JR. | SENIOR PIPELINE COMPLIANCE SPECIALIST | ngray@eprod.com | 985-804-1376 |  |  |  |  | NATHAN L. GRAY JR. | SENIOR PIPELINE COMPLIANCE SPECIALIST | 985-804-1376 | ngray@eprod.com | PIPELINE CONTROL RECEIVED A CALL FROM A CENTERPOINT EMPLOYEE OF A POSSIBLE FIRE AT 6:12 AM 9/28/2012. OUR EMPLOYEE ARRIVED ONSITE AT 6:50 AM, AND CONFIRMED THAT THE COMPRESSORS STATION WAS ON FIRE. UNIT #302 HAD ALREADY BEEN SHUTDOWN AT 6:12 AM, THE RESULT OF A SMALL UNRELATED FIRE. COMPRESSOR OIL LEAKED INTO STATION BLOW DOWN PIPING, AS A RESULT OF THE ESD, THE STATION BLOW DOWN VALVES OPENED, WHICH SUBSEQUENTLY SENT GAS TO THE BLOW DOWN STACK. OIL THAT WAS INSIDE THE LINE PUSHED OUT THE TOP OF STACK, CAUSING A MIXTURE OF OIL AND GAS TO SPREAD UNDER COMPRESSOR ROOF LINE BACK TO UNIT #302 WHERE AT THAT TIME IT IGNITED CREATING A FLASH FIRE FROM UNDER ROOF BACK TO BLOW DOWN STACK AND ABOUT 75FT IN DIAMETER, 360 DEGREES AROUND STACK. THE COST OF REPAIR TO THE COMPRESSOR EXCEEDED 50,000 DOLLARS. AS A RESULT OF THIS INVESTIGATION, IT HAS BEEN SUGGESTED THE BLOWDOWN STACK BE RELOCATED. AN AFE IS CURRENTLY BEING BUILT FOR THIS PROJECT WITH AN ESTIMATED COMPLETION OF 1ST QUARTER 2013. A FINAL INVESTIGATION REPORT WILL BE FILED AT THAT TIME.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120109 | 15934 | 2012-10-26 16:51 | SUPPLEMENTAL FINAL | 13769 | NORTHERN BORDER PIPELINE COMPANY | 700 LOUISIANA STREET | HOUSTON | TX | 77002 | 2012-07-31 18:52 | 2012 |  |  | 46.8216 | -101.7598 | 1019579 | 2012-07-31 20:55 |  | NATURAL GAS |  | 19500 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-07-31 18:52 | 2012-07-31 23:50 |  |  |  |  | NO |  |  |  |  | NO | [7 empty] | 2012-07-31 18:52 | 2012-07-31 18:52 | ONSHORE | ND | 58631 | GLEN ULLIN | MORTON | MILEPOST | 149.5 | GLEN ULLIN COMPRESSOR STATION | NORTHERN BORDER MAINLINE VALVE 23 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1982 |  | CARBON STEEL |  | LEAK |  |  | OTHER | UNCONTROLLED OPENING OF VALVE | [5 empty] | CLASS 1 LOCATION | NO |  | 1098 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 79560 | 64085.3276955603 | 500 | 574.15 | 900 | 1033.47 | 0 | 0 |  |  | 80960 | 67178.1091331924 | 65692.9476955603 | [8 empty] | 1210 |  | 1435 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [7 empty] | YES | [16 empty] | YES | [173 empty] | KURT SMITH | PIPE REGULATORY SPECIALIST | kurt_smith@transcanada.com | 509 546-8865 | 509 546-8825 |  |  |  | KURT A. SMITH | PIPE REGULATORY SPECIALIST | 509 546-8865 | kurt_smith@transcanada.com | AT 1728 ON JULY 31, 2012, THE STATION LOST UTILITY POWER WHEN A THUNDERSTORM WENT THROUGH THE AREA. THE FACILITY APU ATTEMPTED TO START AT WHICH TIME THE LEAD ACID BATTERIES EXHIBITED A CATASTROPHIC FAILURE LEAVING THE COMPRESSOR STATION WITHOUT 480 VAC POWER. AT 1742 THE UNIT SHUT DOWN DUE TO THE LACK OF LUBE OIL COOLING FANS WHICH OPERATE ON 480 VAC. AT 1747, WITHOUT OPERATING AIR COMPRESSORS DUE TO THE LACK OF 480 VAC, THE COMPRESSED AIR PRESSURE DECREASED TO A LEVEL WHERE THE UNIT NORMAL VENT VALVE (FAIL OPEN, SPRING ACTUATOR) FAILED ITS CLOSED POSITION AND BEGAN TO OPEN. THE UNIT EMERGENCY VENT VALVE OPENED (AS DESIGNED AND CONFIGURED IN THE UNIT PLC) AS A RESULT OF THE UNIT NORMAL VENT VALVE BEING OUT OF A POSITION. THE UNIT SUCTION AND DISCHARGE VALVES UTILIZE ELECTRIC OPERATORS (480 VAC) AND REMAINED OPEN IN THEIR PRE-EXISTING POSITION. THE STATION SUCTION AND DISCHARGE VALVES REMAINED OPEN AS THE EXISTING CONTROL LOGIC DID NOT ATTEMPT CLOSE THEM. AT 1900 THE STATION SUCTION AND DISCHARGE VALVES WERE CLOSED ON COMMAND BY THE RESPONDING TECHNICIAN. THE APU BATTERY ISSUE WAS ADDRESSED AND AUXILIARY POWER WAS RESTORED TO THE STATION. AT 2350 THE STATION WAS RETURNED TO OPERATIONAL STATUS. UTILITY POWER WAS RESTORED TO THE STATION.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120110 | 15953 | 2012-11-03 00:06 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2012-10-04 17:52 | 2012 |  |  | 37.4014 | -122.0327 | 1027171 | 2012-10-12 |  | NATURAL GAS |  | 3200 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE PIPELINE WAS SHUTDOWN DUE TO A SCHEDULED CLEARANCE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-10-04 17:52 | 2012-10-04 17:52 | ONSHORE | CA | 94089 | SUNNYVALE | SANTA CLARA | MILEPOST | 109 MP 6.7 | LINE 109 | SEGMENT 120 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | TEE OFF MAINLINE | 1936 |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | YES | METHOD2 | 294 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 10800 | 8699.36575052854 | 0 | 0 | 25000 | 28707.5 | 0 | 0 |  |  | 35800 | 22196.5274841438 | 37406.8657505285 | [8 empty] | 280 |  | 375 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | AUTOMATIC | 52219 | NO | YES | [6 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | CONTRACTOR WORKING FOR THE OPERATOR | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | [8 empty] | NO |  |  | YES | 2 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [10 empty] | NO | YES | CITY STREET |  |  | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 364827 | N/A | UTILITY OWNER | YES | YES |  |  | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO USE HAND TOOLS WHERE REQUIRED | [263 empty] | CHERYL DIZON | COMPLIANCE ENGINEER | c1dz@pge.com | 925-974-4378 | 925-974-4232 |  |  |  | FRANCES YEE | ACTING DIRECTOR OF REGULATORY COMPLAINCE | 925-974-4316 | fcs2@pge.com | ON OCTOBER 4, 2012, AT APPROXIMATELY 1752 HOURS, A PACIFIC GAS & ELECTRIC (PG&E) CONTRACTOR, SNELSON, NOTIFIED PG&E OF A GAS RELEASE DUE TO A DIG IN ON LINE 109 IN MOUNTAIN VIEW. PG&E WAS PERFORMING CLEARANCE WORK FOR A HYDROSTATIC PRESSURE TEST ON LINE 109. A CANUS INSPECTOR WAS HIRED TO PERFORM STAND-BY DUTIES AND A SNELSON OPERATOR WAS HIRED TO EXCAVATE A BELL HOLE IN PREPARATION OF INSTALLING A 22-INCH ISOLATION CAP FOR THE 20 MILE CLEARANCE. THE CANUS EMPLOYEE, ALLOWED THE SNELSON OPERATOR TO DIG WITH AN EXCAVATOR, WITHIN TWO FEET OF THE 22-INCH PIPELINE, WHEN THE OPERATOR STRUCK AN ABANDONED 3/4-INCH TEE OFF OF LINE 109. THE CREW HAD PROPERLY IDENTIFIED THE TRANSMISSION PIPELINE, BUT THE CANUS STAND-BY INSPECTOR FAILED TO DIRECT THE OPERATOR TO FULLY EXPOSE AND PROTECT THE PIPE PRIOR TO USING AN EXCAVATOR. THE CANUS EMPLOYEE WAS OPERATOR QUALIFIED TO PERFORMED STAND BY ON THE PIPELINE, BUT VIOLATED PROPER WORK PROCEDURES AND WAS TERMINATED FROM THE JOB. WHEN THE INCIDENT OCCURRED, WORKERS WERE EVACUATED FROM THE SITE AND THE AREA WAS BLOCKED OFF. BECAUSE PG&E WAS IN THE PROCESS OF PREPARING A CLEARANCE TO BLOW THE LINE DOWN, THE AREA WAS MADE SAFE AND PG&E ALLOWED THE GAS TO CONTINUE TO VENT TO THE ATMOSPHERE. PG&E'S LOCAL EMERGENCY OPERATIONS CENTER (EOC) OPENED ON-SITE ON OCTOBER 5, 2012 AND REMAINED NEAR THE SITE OF THE DIG IN WHERE GAS WAS VENTING TO ATMOSPHERE UNTIL THE FLOW OF GAS WAS STOPPED ON OCTOBER 5, 2012 AT 2000 HOURS. AT THAT TIME, THE LINE WAS ISOLATED AND THE END CAPS WERE WELDED ON IN PREPARATION FOR THE HYDROSTATIC PRESSURE TEST. THERE WERE NO INJURIES, NO FATALITIES AND NO IGNITION AS A RESULT OF THIS INCIDENT. NO CUSTOMERS EXPERIENCED SERVICE INTERRUPTION. DAMAGES ARE LESS THAN $50,000. THIS INCIDENT WAS REPORTED TO THE CPUC AND DOT WHEN THE AMOUNT OF GAS RELEASED WAS DETERMINED TO BE UNINTENTIONAL AND GREATER THAN 3 MMCF. PG&E HAS DETERMINED THE ROOT CAUSE OF THE INCIDENT TO BE FAILURE TO VERIFY PROPER OPERATION, TOOLS AND PROCEDURAL DISREGARD. PG&E'S WP 4412P-05 ATTACHMENT 1 STATES THAT POWER EXCAVATION IS NOT PERMITTED WITHIN 12-INCHES OF THE FACILITY. THE POWER EQUIPMENT STRUCK THE AFFECTED TEE FITTING 4-INCHES FROM THE GAS PIPELINE. THE CORRECTIVE ACTION FOR THIS INCIDENT WAS FOR GAS TRANSMISSION CONSTRUCTION AND PSEP (SAFETY) TO DISCUSS THE INCIDNET WITH SNELSON AND CANUS SAFETY SUPERVISION WITH EMPHASIS ON NON-ADHERENCE TO PG&E (WP 4412P-05 AND WP 4412P-05 ATTACHMENT #1) AND USA NORTH'S CONSTRUCTION MANUAL: GENERAL EXCAVATION INFORMATION PROCEDURES. THIS CORRECTIVE ACTION ITEM WAS COMPLETED ON OCTOBER 9, 2012.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120111 | 16221 | 2012-11-06 09:15 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION LP (SPECTRA ENERGY CORP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2012-10-24 08:30 | 2012 |  |  | 29.615 | -88.775 | 1028188 | 2012-10-24 10:05 |  | NATURAL GAS |  | 2074 | 6490 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-11-02 01:00 | 2012-11-05 08:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-10-24 08:30 | 2012-10-24 13:00 | OFFSHORE | [28 empty] | 60 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | MAIN PASS | 94 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 |  | 0.5 | 46000 | API-5L X-46 | SEAMLESS |  | US STEEL | OTHER | CONCRETE AND SOMASTIC | [27 empty] | 1970 | 1970 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 419 |  | NO | NO | NO |  | 0 | 0 | 22715 | 26083.6345 | 7259 | 5847.10147991543 | 240000 | 275592 | 0 | 0 | 0 | 0 |  |  | 269974 | 144539.032102537 | 307522.735979915 | [8 empty] | 931 |  | 1440 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 58978 | NO | [5 empty] | YES | NO PLATFORM FROM WHICH TO LAUNCH TOOL | YES |  |  |  |  | YES | NO PLATFORM FROM WHICH TO LAUNCH TOOL | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS TOO SMALL TO BE IDENTIFIED BY CONTROL ROOM PERSONEL. A REVIEW OF OPERATING RECORDS FOUND ABNORMAL OPERATING CONDITIONS DID NOT CAUSE OR CONTRIBUTE TO THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | deteschendorf@spectraenergy.com | 713-627-5573 | 713-386-4468 |  |  |  | RICK KIVELA | DIRECTOR OF OPERATIONAL COMPLIANCE | 713-627-6388 | rwkivela@spectraenergy.com | INDICATIONS OF BUBBLES ON THE WATER SURFACE IN MAIN PASS BLOCK 94 WERE REPORTED ON OCTOBER 24, 2012 BY SPECTRA ENERGY PERSONNEL CONDUCTING A ROUTINE FLY OVER IN A HELICOPTER. THE LEAK WAS CAUSED BY A PINHOLE LEAK RESULTING FROM INTERNAL CORROSION. REPAIR WAS COMPLETED BY INSTALLING A LEAK CLAMP.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120112 | 16199 | 2012-11-14 18:29 | SUPPLEMENTAL FINAL | 31531 | ONEOK WESTEX TRANSMISSION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2012-10-15 10:15 | 2012 |  |  | 32.0721 | -101.9287 | 1027378 | 2012-10-15 14:54 |  | NATURAL GAS |  | 3649 | 216 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-10-15 14:30 | 2012-10-15 21:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 10 | 2012-10-15 10:15 | 2012-10-15 10:15 | ONSHORE | TX | 79705 | MIDLAND | MIDLAND |  |  | 0420-000 |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 6.625 |  | 0.203 | 24000 | API 5L? | LAP WELDED |  | UNKNOWN | COAL TAR | [28 empty] | 1928 | 1928 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 19 | 0.4 |  | CLASS 2 LOCATION | NO |  | 180 |  | NO | NO | NO |  | 0 | 0 | 771 | 885.3393 | 13027 | 10493.2071881607 | 2000 | 2296.6 | 10000 | 11483 | 0 | 0 |  |  | 25798 | 17610.3784551797 | 25158.1464881607 | [8 empty] | 132 |  | 307 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 92717 | NO | YES | [6 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLERS OR CONTROL ROOM ISSUES DID NOT CONTRIBUTE TO THIS INCIDENT. ONEOK PARTNERS CONTRACTOR PERSONNEL WERE ONSITE AT THE TIME OF THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) |  | YES | YES | SEE PART H NARRATIVE | [11 empty] | YES | SEE PART H NARRATIVE | [13 empty] | YES | SEE PART H NARRATIVE | [55 empty] | NO | [63 empty] | YES | 1971 | 460 | Yes, and an investigative dig was cunducted at the point of the Accident | 2012 | [12 empty] | NO | [63 empty] | PATTI FORD | SENIOR PIPELINE SAFETY ENGINEER | patti.ford@oneok.com | 918 588 7131 | 918 732 1311 |  |  |  | WESLEY R. DUNBAR | VICE PRESIDENT | 918 588 7424 | wes.dunbar@oneok.com | ONEOK WESTEX TRANSMISSION WAS CONDUCTING ECDA CONFIRMATION DIGS ON 6 INCH DIAMETER PIPELINE 0420-000 ON MONDAY OCTOBER 15, 2012 UTILIZING A THIRD PARTY CONTRACTOR. THE CONTRACTOR HAD UNCOVERED THE PIPELINE AND TWO CONTRACTOR PERSONNEL WERE IN THE DITCH REMOVING THE OLD COATING IN PREPARATION FOR RECOATING THE PIPELINE. AT APPROXIMATELY 1015 HOURS, THE PIPELINE SPLIT OPEN LONGITUDINALLY RELEASING NATURAL GAS AND THE CONTRACTOR PERSONNEL IMMEDIATELY LEFT THE DITCH. THERE WAS NO FIRE, NO EXPLOSION, AND NO INJURIES. THE LOCAL SHERIFF WAS NOTIFIED AND THE 5-7 NEARBY STRUCTURES WERE EVACUATED AS A PRECAUTIONARY MEASURE ONLY. LINE PRESSURE AT THE TIME OF THE INCIDENT WAS 132 PSI WHICH WAS REDUCED TO 84 PSI TO MINIMIZE HAZARDS. INITIAL GAS LOSS CALCULATIONS AND ESTIMATED REPAIR COSTS WERE DETERMINED TO BE LESS THAN REPORTABLE LIMITS. THE RAILROAD COMMISSION OF TEXAS WAS PROVIDED A COURTESY CALL AT 1236 HOURS. FURTHER ASSESSMENT OF THE DAMAGED PIPE RESULTED IN A DECISION TO REPAIR VIA PIPE REPLACEMENT. THIS WOULD CAUSE A LOSS OF NATURAL GAS SERVICE DOWNSTREAM OF THE INCIDENT SITE TO THE TOWN OF STANTON WITH AN ESTIMATED 850 CUSTOMERS. THE NATIONAL RESPONSE CENTER WAS PROVIDED A COURTESY CALL AT 1454 HOURS (INCIDENT NUMBER 1027378) BASED ON THE LOSS OF SERVICE TO THE TOWN OF STANTON. THE RAILROAD COMMISSION OF TEXAS WAS NOTIFIED OF THE NRC INCIDENT NUMBER (TEXAS INCIDENT NUMBER 755). THE TOWN OF STANTON WENT DOWN AT 1430 HOURS IN PREPARATION FOR THE PIPE REPLACEMENT. REPAIRS WERE COMPLETED AND EVACUATED STRUCTURES RELEASED FOR OCCUPANCY BY 1900 HOURS THE SAME DAY. FULL SERVICE TO ALL CUSTOMERS AND APPROVAL TO RELIGHT OCCURRED AT 2145 HOURS. THE DELAY BETWEEN THE COMPLETION OF THE PIPE REPAIR AND RELIGHT WAS BECAUSE A SMALL 2 INCH METER HAD TO BE UTILIZED TO PRESSURE UP THE LINE AND IT TOOK SOME TIME TO ACHIEVE FULL LINE PRESSURE. FURTHER REFINED GAS LOSS CALCULATION RESULTS CAUSED THIS INCIDENT TO BECOME REPORTABLE BASED ON GREATER THAN 3 MMCF UNINTENTIONAL RELEASE OF NATURAL GAS. THE ENTIRE JOINT OF PIPE WHERE THE SPLIT OCCURRED WAS REPLACED (TOTAL OF 23.5 FEET). A FAILURE ANALYSIS IS IN PROCESS TO DETERMINE THE CAUSE OF THE RUPTURE. UPDATE: FAILURE ANALYSIS BY EXTERNAL THIRD PARTY WAS INCONCLUSIVE SO THE CAUSE OF THE LONG SEAM WELD FAILURE COULD NOT BE DETERMINED. IN ADDITION TO THE FAILURE ANALYSIS OF THE FAILED LONGITUDINAL SEAM, A SEGMENT FROM THE SAME JOINT OF PIPE ADJACENT TO THE SEAM FAILURE PORTION WAS HYDROTESTED TO FAILURE AT 1500+ PSIG. PART G5 AMENDED TO REFLECT THIS. THE INCIDENT COSTS AND AUTHORIZED SIGNATURE INFORMATION WERE ALSO UPDATED. THIS IS A SUPPLEMENTAL AND FINAL INCIDENT REPORT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120113 | 16294 | 2012-11-15 11:58 | SUPPLEMENTAL FINAL | 602 | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA STREET | HOUSTON | TX | 77002 | 2012-10-30 17:35 | 2012 |  |  | 35.3737 | -91.8375 | 1028860 | 2012-10-30 19:43 |  | NATURAL GAS |  | 4430 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | COMPRESSOR RELIEF | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-10-30 17:35 | 2012-10-30 17:35 | ONSHORE | AR | 72085 | LETONA | WHITE | MILEPOST | SEARCY COMP | SEARCY COMPRESSOR STATION | SEARCY COMPRESSOR STATION UNIT 2 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | NIPPLE |  |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 523 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 14974 | 12061.5095137421 | 0 | 0 | 0 | 0 | 0 | 0 | N/A |  | 14974 | 12504.7145877378 | 12061.5095137421 | [8 empty] | 1020 |  | 1260 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ACTION DID NOT CONTRIBUTE TO THE CAUSE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | PIPE NIPPLE |  |  |  |  | YES | [177 empty] | JIMMY CROSS | DOT WAIVER SPECIALIST | jimmy.cross@centerpointenergy.com | 3184293664 | 3184293927 |  |  |  | JOHNNY L. CAVITT | MANAGER OF DOT COMPLIANCE | 3184293606 | johnny.cavitt@centerpointenergy.com | VIBRATION BROKE A NIPPLE AND CAUSED THE RELIEF TO GO OFF. RELIEF MOVED OFF OF COMPRESSOR SKID TO REMEDIATE THE ISSUE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120114 | 16295 | 2012-11-15 12:01 | SUPPLEMENTAL FINAL | 602 | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA STREET | HOUSTON | TX | 77002 | 2012-11-05 14:06 | 2012 |  |  | 35.3737 | -91.8375 | 1029736 | 2012-11-05 15:35 |  | NATURAL GAS |  | 4266 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | COMPRESSOR STATION RELIEF VALVE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-11-05 14:47 | 2012-11-05 14:47 | ONSHORE | AR | 72085 | LETONA | WHITE | MILEPOST | SEARCY COMP | SEARCY COMPRESSOR STATION | SEARCY COMPRESSOR STATION UNIT 2 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | NIPPLE |  |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 523 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 14069 | 11332.5348837209 | 0 | 0 | 0 | 0 | 0 | 0 | N/A |  | 14069 | 11748.9534883721 | 11332.5348837209 | [8 empty] | 1020 |  | 1260 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER ACTIONS DID NOT CONTRIBUTE TO THE EVENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | PIPE NIPPLE |  |  |  |  | YES | [177 empty] | JIMMY CROSS | DOT WAIVER SPECIALIST | jimmy.cross@centerpointenergy.com | 3184293664 | 3184293927 |  |  |  | JOHNNY L. CAVITT | MANAGER OF DOT COMPLIANCE | 3184293606 | johnny.cavitt@centerpointenergy.com | VIBRATION BROKE A NIPPLE ON TOP OF THE RELIEF VALVE AND CAUSED THE RELIEF TO GO OFF. RELIEF VALVE MOVED OFF OF COMPRESSOR SKID TO REMIDIATE THE ISSUE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120115 | 15658 | 2012-11-16 15:29 | ORIGINAL FINAL | 602 | CENTERPOINT ENERGY GAS TRANSMISSION | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2012-11-08 15:50 | 2012 |  |  | 35.2029 | -90.2314 | 1030086 | 2012-11-08 16:39 |  | NATURAL GAS |  | 3300 | 388 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | APRROXIMATELY 14 MILES SHUT DOWN, HELD UP 6 MILE SEGMENT WITH CNG TRAILERS. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 2 | 2012-11-08 16:28 | 2012-11-08 16:28 | ONSHORE | AR | 72327 | CRAWFORDSVILLE | CRITTENDON | SURVEY STATION NO. | 78+34 | JM-24 |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 14 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 3.5 |  | 0.216 | 35000 | UNKNOWN | OTHER | UNKNOWN | UNKNOWN | COAL TAR | [28 empty] | 1954 | 1954 | CARBON STEEL |  | MECHANICAL PUNCTURE | 0.5 | 4 | [7 empty] | CLASS 3 LOCATION | NO |  | 54 |  | NO | NO | NO |  | 100 | 114.83 | 1259 | 1445.7097 | 10705 | 8622.84355179704 | 23000 | 26410.9 | 2500 | 2870.75 | 47000 | 53970.1 | CNG TRAILERS AND CHARGES FROM DISTRIBUTION COMPANY |  | 84564 | 47870.7723460888 | 93435.133251797 | [8 empty] | 545 |  | 680 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 74000 | NO |  |  |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | LOCAL DISTRIBUTION COMPANY PERSONNEL WERE CONTACTED, THEY CONTACTED CEGT. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | HIT BY THIRD PARTY. CONTROLLER/S DID NOT CONTRIBUTE TO THE CAUSE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  | YES | PRIVATE LANDOWNER | YES | [6 empty] | FARMER | FARM EQUIPMENT | AGRICULTURE | NO |  |  | UNKNOWN/OTHER | NO | UNKNOWN/OTHER |  |  | OTHER |  |  |  | FARMER PLOWING FIELD, PIPE MARKED WITH LINE MARKERS ON EDGES ON FIELD. | [262 empty] | JIMMY CROSS | DOT WAIVER SPECIALIST | jimmy.cross@centerpointenergy.com | 3184293664 | 3184293927 |  |  |  | JOHNNY L. CAVITT | MANAGER OF DOT COMPLIANCE | 3184293606 | johnny.cavitt@centerpointenergy.com | FARMER PERFORMING SUB-MOISTURE PLOWING STRUCK AND PUNCTURED PIPELINE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120116 | 16026 | 2012-11-20 16:23 | SUPPLEMENTAL FINAL | 18152 | SEA ROBIN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2012-10-21 15:30 | 2012 |  |  | 28.2605 | -92.5241 | 1027955 | 2012-10-21 15:30 |  | NATURAL GAS |  | 3286 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-10-21 16:09 | 2012-11-01 17:43 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-10-21 15:40 | 2012-10-22 08:30 | OFFSHORE | [28 empty] | 164 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EAST CAMERON | 265 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12.75 |  | 0.5 | 52000 | API 5L GRADE B | SEAMLESS |  | JONES & LAUGHLIN | OTHER | MASTIC AND CONCRETE | [27 empty] | 1970 | 1970 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 276 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 3600 | 2899.78858350951 | 475000 | 545442.5 | 5000 | 5741.5 | 0 | 0 |  |  | 483600 | 256014.342494715 | 554083.78858351 | [8 empty] | 925 |  | 984 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | CHECK VALVE | 4171 | NO | YES | YES | YES | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | OTHER | PRODUCER PLATFORM EMPLOYEE IDENTIFIED LEAK. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DUE TO THE LOCATION AND KIND OF FAILURE IT APPEARS TO BE CAUSED BY AN INTERNAL DEFECT. CONTROLLERS ACTIONS HAVE NO EFFECT ON THIS EVENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | PIN-HOLE LEAK AT THE 6 O'CLOCK POSITION. |  |  |  |  | YES | LOW FLOW ON DEAD-END LATERAL. |  |  | YES | HISTORICAL DATA |  |  |  |  | YES | DEAD-END LEG OF SUB-SEA LATERAL | YES | NO | NO | NO | [168 empty] | NO | [63 empty] | YES | 2009 | 1941 | NO | [13 empty] | NO | [63 empty] | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | ** THE REASON FOR THIS SUPPLEMENTAL REPORT IS TO CORRECT THE LAT. AND LONG. COORDINANTS PREVIOUSLY SUBMITTED IN THE ORIGINAL/FINAL REPORT. **THIS REPORT IS BEING SUBMITTED IN RESPONSE TO PHMSA'S REQUEST, (DOCKET ID PHMSA-2013-0028), FOR SUPPLEMENTAL REPORTS FROM OPERATORS WHO SUBMITTED REPORTS FOR INCIDENTS OCCURRING AFTER JANUARY 1, 2010, WITH ANY OF THE FOLLOWING: (1) ``PIPE GIRTH WELD'' WAS SELECTED AS THE ``ITEM INVOLVED IN INCIDENT'' IN PART C3 OF THE REPORT. THE REVISED REPORT COLLECTS DATA ABOUT THE PIPE ADJACENT TO THE GIRTH WELD. (2) ``FUNCTION OF PIPELINE SYSTEM'' IS NULL IN PART E5F OF THE REPORT. THE REVISED REPORT COLLECTS THE FUNCTION OF THE PIPELINE SYSTEM FOR ALL INCIDENTS.** THIS SUPPLEMENTAL REPORT IS TO ACKNOWLEDGE THAT THE TWO RELEVANT SECTIONS IN PHMSA'S REQUEST HAVE BEEN REVIEWED AND NO FURTHER ACTIONS WERE NEEDED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120117 | 17118 | 2012-11-28 11:04 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION LP (SPECTRA ENERGY CORP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2012-11-03 12:30 | 2012 |  |  | 28.2907 | -93.3531 | 1029486 | 2012-11-03 14:30 |  | NATURAL GAS |  | 400 | 13089 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-11-03 12:30 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-11-03 12:30 | 2012-11-03 12:30 | OFFSHORE | [28 empty] | 190 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST CAMERON | 549 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 20 |  | 0.406 | 52000 | API -5L X-52 | SEAMLESS |  | US STEEL | OTHER | CONCRETE AND SOMASTIC | [27 empty] | 1975 | 1975 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 524 |  | NO | NO | NO |  | 0 | 0 | 45812 | 52605.9196 | 1400 | 1127.6955602537 | 1131000 | 1298727.3 | 0 | 0 | 0 | 0 |  |  | 1178212 | 621466.738392389 | 1352460.91516025 | [8 empty] | 858 |  | 1440 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 106022 | NO | [5 empty] | YES | NO PLATFORM FROM WHICH TO LAUNCH/RECEIVE | YES |  |  |  |  | YES | NO PLATFORM FROM WHICH TO LAUNCH/RECEIVE | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | THIRD PARTY PLATFORM OPERATOR OBSERVATION |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS TOO SMALL TO BE IDENTIFIED BY CONTROL ROOM PERSONNEL. A REVIEW OF OPERATING RECORDS FOUND ABNORMAL OPERATING CONDITIONS DID NOT CAUSE OR CONTRIBUTE TO THIS INCIDENT/ | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | deteschendorf@spectraenergy.com | 713-627-5573 | 713-386-4468 |  |  |  | RICK KIVELA | DIRECTOR OF OPERATIONAL COMPLIANCE | 713-627-6388 | rwkivela@spectraenergy.com | INDICATIONS OF BUBBLES ON THE WATER SURFACE IN WEST CAMERON 549 WERE REPORTED BY A PLATFORM OPERATOR ON NOVEMBER 3, 2012. A SHEEN ALSO APPEARED ON THE SURFACE. UPON INVESTIGATION IT WAS DETERMINED THE LEAK WAS CAUSED BY A PINHOLE RESULTING FROM INTERNAL CORROSION.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120118 | 17621 | 2012-11-28 12:13 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION CORP | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2012-10-30 13:30 | 2012 |  |  | 37.5885 | -81.0917 | 1028803 | 2012-10-30 14:15 |  | NATURAL GAS |  | 6850 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE FACILITY WAS ALREADY DOWN AT THE TIME OF THE INCIDENT. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-10-30 13:30 | 2012-10-30 13:30 | ONSHORE | WV | 25841 | FLAT TOP | SUMMERS | MILEPOST | BLOWDOWNVLV | FLAT TOP COMPRESSOR STATION | LINE KA AND LINE KA LOOP | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 1998 |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENTIONAL GAS RELEASE THROUGH ESD SYSTEM. | CLASS 1 LOCATION | NO |  | 45 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 20619 | 16608.5391120507 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 20619 | 17218.8266384778 | 16608.5391120507 | [8 empty] | 718 |  | 1000 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | NO | NO | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | COMMUNICATIONS WERE OUT BETWEEN THE CONTROL ROOM AND THE FACILITY. THE CONTROL ROOM COULD NOT SEE THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  | YES | YES |  |  | YES | [16 empty] | YES | [10 empty] | YES | LOSS OF COMMUNICATIONS AND POWER DUE TO MAJOR STORM IN AREA. | [161 empty] | MARK NEWAMN | COMPLIANCE SPECIALIST | mark_newman@transcanada.com | 304-722-8475 |  |  |  |  | LEE ROMACK | MANAGER | 832-320-5315 | lee_romack@transcanada.com | HURRICANE SANDY SIGNIFICANTLY IMPACTED THE WEST VIRGINIA MOUNTAINS ON THE EVENING OF OCTOBER 29, WITH LESSENING IMPACTS FOLLOWING. DAMAGE FROM THIS HEAVY, EARLY SEASON SNOWSTORM IN THE WEST VIRGINIA MOUNTAINS INCLUDED LOSS OF POWER AND COMMUNICATIONS FOR MUCH OF THE REGION. AMONG THE FACILITIES AFFECTED IN THE REGION WAS THE FLAT TOP COMPRESSOR STATION. AT THE TIME THE STORM HIT, THE COMPRESSOR STATION WAS UNATTENDED. WHEN THE COMMUNICATION LOSS WAS RECOGNIZED ON THE MORNING OF OCTOBER 30, AN EMPLOYEE WAS DISPATCHED TO THE LOCATION TO INVESTIGATE. THE EMPLOYEE ARRIVED AT THE STATION AT APPROXIMATELY 9:30 A.M. NOT LONG AFTER ARRIVAL, HE HEARD GAS VENTING. THIS WAS NOT UNUSUAL, AS THE TURBINE UNIT IS DESIGNED TO BLOW DOWN IF IT GOES OFFLINE AS HAD APPARENTLY HAPPENED. A SHORT WHILE LATER, AS THE EMPLOYEE CONTINUED TO RESTORE STATION OPERATION, HE RECOGNIZED THAT GAS WAS STILL VENTING. THIS WAS UNUSUAL, AS THE BLOWDOWN PROCESS SHOULD HAVE BEEN COMPLETE BY THEN, EVEN IF IT HAD BEGUN JUST PRIOR TO THE EMPLOYEE'S ARRIVAL. AFTER CAREFULLY ASSESSING THE SITUATION, THE EMPLOYEE MANUALLY CLOSED THE BLOWDOWN VALVE. FURTHER INVESTIGATION REVEALED THAT A PARTIAL ESD HAD OCCURRED DURING THE COMMUNICATION LOSS / POWER LOSS EVENT, AND THE BLOW DOWN VALVE HAD REMAINED IN THE OPEN POSITION. CORRECTIVE ACTIONS TAKEN ON 10-30-2012 1. THE STATION COMPRESSED AIR SYSTEM WAS RECHARGED USING THE EMERGENCY GASOLINE POWERED AIR COMPRESSOR. 2. THE UNIT SUCTION VALVE WAS MANUALLY CLOSED TO STOP GAS FROM VENTING. 3. THE EMERGENCY BACKUP GENERATOR WAS STARTED AND AC POWER RESTORED. 4. THE 24 VOLT ESD SHUNT TRIP BREAKER WAS RESET AND 24 VOLT DC POWER RESTORED. 5. THE STATION WAS RETURNED TO NORMAL OPERATIONAL STATUS WITH AC POWER BEING SUPPLIED BY THE EMERGENCY BACKUP GENERATOR. COLUMBIA'S ENGINEERING SERVICES COMPLETED AN INVESTIGATION WITH A RECOMMENDATION TO UPGRADE THE SUCTION VALVE ACTUATOR FROM ELECTRIC TO FAIL CLOSED PNEUMATIC.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120119 | 15813 | 2012-12-08 10:32 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2012-11-10 10:44 | 2012 |  |  | 41.0275 | -73.7746 | 1030221 | 2012-11-10 11:24 |  | NATURAL GAS |  | 24 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-11-10 11:15 | 2012-11-21 08:37 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-11-10 10:44 | 2012-11-10 10:44 | ONSHORE | NY | 10602-7504 | WHITE PLAINS | WESTCHESTER |  |  |  |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 65 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | 24" COMPRESSION COUPLING | 1948 |  | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 4 LOCATION | YES | METHOD1 | 259 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 48 | 38.6638477801268 | 1261000 | 1448006.3 | 1000 | 1148.3 | 0 | 0 |  |  | 1262048 | 665240.284566596 | 1449193.26384778 | [8 empty] | 233 |  | 245 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 528 | NO | YES | YES | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | MINOR LEAK ON COMPRESSION COUPLING RESULTING IN NO PRESSURE LOSS OR INCREASED FLOW. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | MECHANICAL COUPLING | [19 empty] | YES | COMPRESSION COUPLING LEAK AT SEAL | [161 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPARTMENT MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | dadariov@coned.com | ON NOVEMBER 5, 2012 WESTCHESTER GAS OPERATIONS PERFORMED A 30-DAY LEAK FOLLOW-UP INSPECTION AT 100 FISHER AVENUE, WHITE PLAINS, NEW YORK AND DETECTED 24% IN THE VALVE BOX 24" 230 PSI TRANSMISSION MAIN VALVE 25971. WESTCHESTER GAS OPERATIONS, GAS ENGINEERING AND GAS CONTROL WERE NOTIFIED. GAS CONSTRUCTION RESPONDED AND INVESTIGATED OVER THE MAIN AND DETECTED 41% OVER THE TRANSMISSION MAIN 4' WEST OF THE VALVE BOX. THE READINGS VENTED TO 5%-10% RANGE AND NO MIGRATION BEYOND THE STREET WAS DETECTED. ALL SUBSURFACE STRUCTURES AND BUILDINGS INVESTIGATED WERE FOUND GAS FREE. CONTINGENCY W12-151, CASE 38B AND 38C WERE PLACED IN EFFECT. GAS ENGINEERING RESPONDED TO LOCATION WITH WESTCHESTER GAS TO DETERMINE A COURSE OF ACTION. AN OPERATIONAL PLAN WAS DEVELOPED AND AROUND-THE-CLOCK OPERATIONS BEGAN FOR THE REPLACEMENT OF APPROX. 320' OF TRANSMISSION MAIN FROM WEST OF V-25971 EAST TO THE INLET OF TRANSMISSION-MEDIUM PRESSURE REGULATOR STATION GR-512. TWO REMOTE OPERATED VALVES (ROVS) WERE OPERATED BY GAS CONTROL TO ENSURE THERE WAS NO IMPACT TO THE GAS SYSTEM. ADDITIONALLY, (5) 24" COMPRESSION COUPLING WERE IDENTIFIED, EXCAVATED AND PREPARED FOR THE WELDED REPAIR SLEEVE INSTALLATION AS A PREEMPTIVE MEASURE. ON NOVEMBER 10, 2012 AT 10:44 A VISIBLE LEAK ON A 24" COMPRESSION COUPLING LOCATED 124' WEST OF V-25971 WAS REPORTED. GAS CONTROL WAS NOTIFIED AND AT 10:59 ORDERED CONTINGENCY V-32715 CLOSED. AT 11:15 THE VALVE WAS REPORTED TO BE IN THE FULLY CLOSED POSITION. THE PRESSURE IN THE AFFECTED SEGMENT OF MAIN AT TIME OF DISCOVERY OF THE LEAK WAS 233 PSI. THE SEGMENT OF MAIN WAS ISOLATED AND THERE WAS NO GAS SYSTEM IMPACT AS A RESULT OF THE ISOLATION. AROUND-THE-CLOCK OPERATIONS CONTINUED UNTIL THE WELDED SLEEVE WAS INSTALLED OVER THE LEAKING COUPLING TO SECURE THE LEAK ON NOVEMBER 12, 2012 AT 15:43. ON 11-20-12 AT 06:21 OPERATIONS ASSOCIATED WITH REPLACEMENT PROCEDURE MPC-12-46 COMMENCED. ON NOVEMBER 21, 2012 AT 07:43 OPERATIONS WERE COMPLETED AND V-32715 WAS OPENED AND PRESSURE WAS RAISED INCREMENTALLY. AT 08:17 THE VALVE WAS REPORTED FULLY OPENED AND PRESSURE IN THE AFFECTED SEGMENT WAS RETURNED TO 230 PSI. LEAK SURVEY CHECKED DURING INCREMENTAL PRESSURE INCREASES DURING THE RESTORATION PROCESS AND NO LEAKS WERE FOUND. GAS CONTROL REPORTED AT 08:37 THE SYSTEM WAS RETURNED TO NORMAL OPERATING CONDITIONS. THE US DOT AND NYS PSC WERE NOTIFIED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120120 | 15814 | 2012-12-10 11:14 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2012-11-14 13:12 | 2012 |  |  | 40.9764 | -73.8076 | 1030677 | 2012-11-15 10:16 |  | NATURAL GAS |  | 11 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-11-15 09:53 | 2012-11-18 11:12 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-11-14 13:12 | 2012-11-14 13:12 | ONSHORE | NY | 10707-0000 | EASTCHESTER | WESTCHESTER |  |  |  |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 48 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | (2) 24" COMPRESSION COUPLINGS | 1948 |  | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 4 LOCATION | YES | METHOD1 | 259 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 22 | 17.7209302325581 | 120000 | 137796 | 2500 | 2870.75 | 0 | 0 |  |  | 122522 | 64588.1220930233 | 140684.470930233 | [8 empty] | 209 |  | 245 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | REMOTELY CONTROLLED | 6566 | NO | YES | YES | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | NO | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | MINOR LEAK ON COMPRESSION COUPLINGS RESULTING IN NO PRESSURE LOSS OR INCREASED FLOW. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | MECHANICAL COUPLING | [19 empty] | YES | COMPRESSION COUPLING LEAK AT SEAL | [161 empty] | KEVIN FAGAN | OPERATIONS MANAGER--GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPTARTMENT MANAGER--GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | dadariov@coned.com | ON NOVEMBER 14, 2012 AT 13:12 HRS. GAS CONSTRUCTION REPORTED A POSSIBLE LEAK ON THE 24" STEEL TRANSMISSION MAIN AT 23 MAPLE STREET, EASTCHESTER, NY TO THE GAS EMERGENCY RESPONSE CENTER (GERC). TWO REPAIRS WERE PREVIOUSLY MADE ON A PARALLEL 4" HIGH PRESSURE 1932 STEEL DISTRIBUTION MAIN AND THE GAS READINGS INDICATED A POSSIBLE LEAK ON THE TRANSMISSION MAIN. A CODE MURRE (MULTIPLE RESOURCE RESPONSE EVENT) WAS INITIATED AND THE GERC DISPATCHED GAS DISTRIBUTION SERVICES (GDS), THE EMERGENCY RESPONSE GROUP (ERG) AND SUPERVISION.GAS ENGINEERING, PRESSURE CONTROL AND GAS CONTROL WERE NOTIFIED. GERC AND GAS CONTROL IDENTIFIED ROV 25934 AND MV 25968 TO ISOLATE THE AREA PER CONTINGENCY CASE 34A. GAS CONTROL CONFIRMED COMMUNICATION WITH ROV 25934 AND GDS INSPECTED AND CONFIRMED ACCESSIBILITY AND POSITION OF MV 27235 (OPEN) AND MV # 36697 (CLOSED). THESE VALVES ARE STRADDLE CONNECTIONS TO REGULATOR STATION GR-425 (TRANSMISSION-HIGH PRESSURE) AND WERE NEEDED FOR MAIN DEPRESSURIZATION AND ISOLATION AS REQUIRED. THE LEAK WAS STAFFED OVERNIGHT AND AN OPERATIONAL PLAN WAS DEVELOPED. AT 09:53 ON NOVEMBER 15, 2012 THE ISOLATION OF THIS SEGMENT OF TRANSMISSION MAIN WAS CONFIRMED. PRESSURE CONTROL WAS ON LOCATION AND THE SEGMENT WAS DEPRESSURIZED VIA GR-425 AND EXCAVATION COMMENCED TO EXPOSE THE SOURCE OF THE LEAK. GAS CONTROL DECLARED A CONDITION YELLOW AND ISSUED A LIMITED WORK ORDER ON THE 245 PSI TRANSMISSION SYSTEM TO ENSURE SYSTEM SUPPLY. CORROSION CONTROL PERFORMED A PATROL OVER THIS SYSTEM TO ENSURE NO UNREGISTERED ACTIVITY IS ONGOING THAT WOULD JEOPARDIZE THE GAS TRANSMISSION SYSTEM. AROUND-THE-CLOCK OPERATIONS CONTINUED AND ON FRIDAY, NOVEMBER 15, 2012 AT 19:15 HRS A CONFIRMED VISUAL LEAK ON A 24" COUPLING APPROXIMATELY 20' SOUTH OF THE SERVICE SUPPLYING # 20 MAPLE ST (TE). A WELDED REPAIR SLEEVE WAS INSTALLED, AND THE ASSOCIATED TESTING WAS SUCCESSFUL. THE AFFECTED SEGMENT OF MAIN WAS RE-ENERGIZED AND DURING THE INCREMENTAL PRESSURE INCREASE AND ASSOCIATED LEAK SURVEILLANCE, A SECOND LEAK WAS DETECTED OVER A COUPLING APPROXIMATELY 40' SOUTH OF THE ORIGINAL REPAIR. THE MAIN WAS DEPRESSURIZED AND A WELDED REPAIR SLEEVE WAS SUCCESSFULLY INSTALLED AND TESTED. THE MAIN WAS RE-ENERGIZED AND NO OTHER LEAKS FOUND. BRONX CONSTRUCTION-CAPITAL, WESTCHESTER GAS OPERATIONS, PRESSURE CONTROL AND TRANSMISSION ENGINEERING-MAJOR PROJECTS WERE ON LOCATION. THE TRANSMISSION SYSTEM WAS RETURNED TO NORMAL OPERATING CONDITIONS ON SUNDAY NOVEMBER 18, 2012 AT 11:12 HRS. THE US DOT, NYS PSC AND TEFD WERE NOTIFIED. THE TEFD AND PSC VISITED THE LOCATION AND WERE KEPT APPRISED. MEDIA RELATIONS WAS UPDATED DUE TO AN INQUIRY FROM BLOOMBERG NEWS. THERE WERE NO EVACUATIONS OR INJURIES ATTRIBUTED TO THIS INCIDENT.THIS WAS A SERIOUS LEVEL INCIDENT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120121 | 15796 | 2012-12-11 12:34 | SUPPLEMENTAL FINAL | 14210 | OKLAHOMA NATURAL GAS CO | 401 N. HARVEY AVE | OKLAHOMA CITY | OK | 73102 | 2012-11-12 05:05 | 2012 |  |  | 36.0349 | -95.8885 | 1030401 | 2012-11-12 14:00 |  | NATURAL GAS |  | 6650 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELIEF VALVE VENTING ONLY | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 200 | 2012-11-12 05:05 | 2012-11-12 06:00 | ONSHORE | OK | 74133 | TULSA | TULSA |  |  | 91ST & MEMORIAL ROAD | LINE C - SOUTH | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2005 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE OPENED BELOW SET POINT | CLASS 3 LOCATION | NO |  | 147 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 34720 | 27966.8498942918 | 0 | 0 | 300 | 344.49 | 0 | 0 |  |  | 35020 | 29152.6331712474 | 28311.3398942918 | [8 empty] | 248 |  | 300 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 1 | 0 | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | NO DEFECTS IDENTIFIED | [161 empty] | ROBERT STAFFORD | REGIONAL OPERATIONS ENGINEER | rstafford@oneok.com | 918-831-8215 |  |  |  |  | BRYAN BREWSTER | DIRECTOR - DIVISION OPERATIONS | 405-551-6653 | bbrewster@ong.com | AT APPROXIMATELY 05:05 ON NOVEMBER 12, 2012, OKLAHOMA NATURAL GAS DISPATCH IN OKLAHOMA CITY RECEIVED NOTIFICATION FROM THE TULSA FIRE DEPARTMENT OF A LOUD NOISE AND ODOR OF GAS IN THE VICINITY OF OUR TRANSMISSION PIPELINE STATION NEAR 91ST & MEMORIAL ROAD IN TULSA, OK. ONG DISPATCH NOTIFIED THE OPERATING AREA, WHICH CONTACTED EMPLOYEES TO INVESTIGATE. THE FIRST ONG PERSONNEL ARRIVED ON SITE AT APPROXIMATELY 06:00 AND BEGAN EVALUATION OF THE CONDITIONS. IT WAS DETERMINED THAT THE GAS RELEASE WAS A RELIEF VALVE THAT WAS VENTING. COMPANY PERSONNEL FURTHER EVALUATED CONDITIONS ON ALL CONNECTING LINES WITHIN THE STATION TO DETERMINE IF ANY OVERPRESSURE SITUATIONS HAD EXISTED DUE TO REGULATOR FAILURE. THERE WAS NO REGULATOR FAILURE OR OVERPRESSURE CONDITION. PERSONNEL ALSO VERIFIED THEIR GAUGE READINGS WITH THE GAS CONTROL SCADA SYSTEM, CONFIRMING NO OVERPRESSURE INDICATIONS HAD OCCURED ON ANY OF THE LINES. THE ONG PERSONNEL DETERMINED IT WOULD BE SAFE TO CLOSE THE ISOLATION VALVE BELOW THE RELIEF VALVE WHICH IMMEDIATELY STOPPED THE VENTING AT 06:40. REDUNDANT PRESSURE REDUCTION AND OVERPRESSURE MONITORING EQUIPMENT WAS IN PLACE, SO THE SETTING IN QUESTION WAS ISOLATED FROM THE SYSTEM INSURING THERE WAS NO POSSIBILITY OF AN OVERPRESSURE DUE TO THE RELIEF VALVE BEING ISOLATED. THE VALVE ASSEMBLY WAS REMOVED AND TESTED AT THE VENDOR'S FACILITY UNDER DIRECTION OF ONG PERSONNEL. TESTING AND DISSASEMBLY PROVIDED NO INDICATION OF THE CAUSE. ANY SUBSEQUENT DETERMINATIONS OF CAUSE WILL BE REPORTED VIA A SUPPLEMENTAL FILING. NOTE REGARDING PART A, QUESTION 18: THE NUMBER OF PERSONS EVACUATED WAS ESTIMATED WITH INFORMATIONAL ASSISTANCE FROM THE TULSA FIRE DEPARTMENT. PART E, 5.F ADDED "FUNCTION OF PIPELINE" INFORMATION AS REQUESTED BY MR. BLAINE KEENER FOR REPORTS SUBMITTED ON OR AFTER 1-1-2010.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120122 | 15957 | 2012-12-11 13:41 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2012-11-10 14:24 | 2012 |  |  | 37.5998 | -121.094 | 1030266 | 2012-11-10 18:49 |  | NATURAL GAS |  | 51000 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | [9 empty] | NO |  |  |  |  | NO | [7 empty] | 2012-11-10 14:24 | 2012-11-10 15:00 | ONSHORE | CA | 95358 | MODESTO | STANISLAUS | MILEPOST | 10.85 | 148 |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8.625 |  | 0.277 | 35000 | GRADE B | SEAMLESS |  | UNKNOWN | ASPHALT | [28 empty] | 1947 | 1947 | CARBON STEEL |  | MECHANICAL PUNCTURE | 4 | 2.5 | [7 empty] | CLASS 1 LOCATION | NO |  | 112 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 20010 | 16117.9915433404 | 85000 | 97605.5 | 0 | 0 | 0 | 0 |  |  | 105010 | 61513.7536997886 | 113723.49154334 | [8 empty] | 318 |  | 408 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | [16 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE DAMAGE WAS NOT DUE TO PG&E OPERATORS, THE DAMAGE WAS CAUSED BY A THIRD PARTY | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  |  |  | YES | [6 empty] | FARMER | FARM EQUIPMENT | AGRICULTURE | NO |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | YES | 12 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO USE HAND TOOLS WHERE REQUIRED | [263 empty] | CHERYL DIZON | GAS ENGINEER | c1dz@pge.com | 925-322-3311 | 925-974-4232 |  |  |  | FRANCES YEE | ACTING DIRECTOR | 925-974-4316 | fsc2@pge.com | AT APPROXIMATELY 1424 HOURS A FARMER RIPPING A FIELD WEST OF MODESTO STRUCK TRANSMISSION PIPELINE L-148 AT MILE POINT 10.85, RESULTING IN A RELEASE OF GAS. THE EXCAVATOR DID NOT COMPLY WITH EXCAVATION DAMAGE PREVENTION REGULATIONS BY FAILING TO CALL USA PRIOR TO PERFORMING FIELD EXCAVATIONS. PIPELINE MARKERS WERE IN PLACE. PG&E PERSONNEL ARRIVED ON SCENE AT 1500 HOURS. THE FLOW OF GAS WAS CONTROLLED AT 1630 HOURS BY REDUCING THE PIPELINE PRESSURE FROM 318 PSIG TO 60 PSIG, AND THE FLOW OF GAS WAS STOPPED AT 2330 HOURS BY CLOSING AN UPSTREAM VALVE AND A DOWNSTREAM VALVE. PG&E REPLACED THIS DAMAGED SECTION OF PIPE WITH 8-INCH, 0.188-INCH WALL THICKNESS, X-52, HFW PIPE; THESE PERMANENT REPAIRS WERE COMPLETED AT 0730 HOURS ON NOVEMBER 11, 2012. PG&E WAS ABLE TO MAINTAIN SERVICE TO THIRTY-FIVE CUSTOMERS WITH THE TEMPORARY INSTALLATION OF COMPRESSED NATURAL GAS. TWENTY-FIVE OTHER CUSTOMERS EXPERIENCED GAS SERVICE INTERRUPTIONS AND ALL TWENTY-FIVE SERVICES WERE RESTORED BY 1200 HOURS ON NOVEMBER 11, 2012. THERE WERE NO INJURIES, NO FATALITIES AND NO IGNITION AS A RESULT OF THIS INCIDENT. THIS INCIDENT WAS REPORTED TO THE DOT AND CPUC DUE TO COST OF DAMAGES GREATER THAN $50,000 AND AN UNINTENTIONAL RELEASE OF GAS GREATER THAN 3 MMCF.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120123 | 15894 | 2012-12-11 18:12 | SUPPLEMENTAL FINAL | 15931 | PUBLIC SERVICE CO OF COLORADO | 1800 LARIMER STREET | DENVER | CO | 80202 | 2012-11-11 15:00 | 2012 |  |  | 36.8507 | -106.0796 | 1030342 | 2012-11-11 22:01 |  | NATURAL GAS |  | 3989 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-11-11 17:00 | 2012-11-12 09:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-11-11 15:00 | 2012-11-11 16:00 | ONSHORE | CO | 80498 | SILVERTHORNE | SUMMIT | SURVEY STATION NO. | 3328+18.55 | 8" FRASER TO FRISCO "A" | PLAT SHEET 82 72012 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8.625 |  | 0.188 | 42000 | UNKNOWN | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | COLD APPLIED TAPE | [28 empty] | 1969 | 1969 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 10.8 | 4.3 |  | CLASS 1 LOCATION | NO |  | 167 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 16000 | 12887.9492600423 | 51786 | 59465.8638 | 0 | 0 | 0 | 0 |  |  | 67786 | 40657.9227987315 | 72353.8130600423 | [8 empty] | 752 |  | 790 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 43824 | NO |  |  | YES | YES |  |  |  | YES |  |  |  |  | YES | VALVE SPACING;NEED FOR LAUNGER/RECEIVER | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLERS DID EVERYTHING CORRECTLY. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [9 empty] | YES |  |  | YES | YES | 1994 | YES | YES |  |  | YES |  |  |  | 1994 |  | YES | [190 empty] | YES |  |  |  | YES | [35 empty] | 1994 | [23 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DIANE JACQUEZ | INVESTIGATOR - CLAIMS SERVICES DEPARTMENT | diane.m.jacquez@xcelenergy.com | 303-294-2552 | 303-294-2311 |  |  |  | ADRIENNE GRANDJEAN FOR JOHN J KARTUS | CLAIMS MANAGER MANAGING INVESTIGATOR | 303-294-2665 | john.j.kartus@xcelenergy.com | ON 11/11/12 AT APPROXIMATELY 15:00 THERE WAS AN UNINTENTIONAL RELEASE OF 3,989 MCF (SEE PART A, #10) OF NATURAL GAS FROM AN 8 INCH STEEL TRANSMISSION LINE, OPERATING AT 752 PSIG. SERVICE WAS SHUT DOWN AT APPROXIMATELY 17:00 ON 11/11/12 AND RESTORED ON 11/12/12 AT APPROXIMATELY 09:00. THE RUPTURE WAS CAUSED BY EXTERNAL GALVANIC CORROSION ATTRIBUTED TO A COATING FLAW (A HOLIDAY OR DISBONDED REGION) THAT ERODED WALL THICKNESS BELOW THRESHOLD TO CONTAIN OPERATION PRESSURE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20120124 | 17113 | 2012-12-12 08:56 | SUPPLEMENTAL FINAL | 288 | ALGONQUIN GAS TRANSMISSION CO (SPECTRA ENERGY CORP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2012-11-21 18:30 | 2012 |  |  | 41.4871 | -72.1263 | 1031300 | 2012-11-21 20:00 |  | NATURAL GAS |  | 200 | 278 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-11-21 18:30 | 2012-11-25 18:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-11-21 18:30 | 2012-11-21 18:30 | ONSHORE | CT | 06353 | MONTVILLE | NEW LONDON | SURVEY STATION NO. | 1213+90 | ALGONQUIN GAS TRANSMISSION | LINE E-1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 72 |  | YES | [6 empty] | YES | UNCASED | STONY BROOK | 1 | BELOW WATER, PIPE BURIED BELOW BOTTOM (NOT IN BORED/DRILLED CROSSING) | [11 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6.625 |  | 0.25 | 35000 | API 5L GRADE B | SEAMLESS |  | SHIN-FUSO METAL INDUSTRIES | OTHER | NO-OX-ID WAX | [27 empty] | 1953 | 1952 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | NO |  | 182 |  | NO | NO | NO |  | 1000 | 1148.3 | 973 | 1117.2959 | 700 | 563.84778012685 | 50000 | 57415 | 0 | 0 | 0 | 0 |  |  | 52673 | 27979.5348961945 | 60244.4436801268 | [8 empty] | 575 |  | 750 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | REMOTELY CONTROLLED | 35075 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS TOO SMALL TO BE IDENTIFIED BY CONTROL ROOM EQUIPMENT | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [8 empty] | YES | POROSITY IN WELD RESULTING IN PINHOLE LEAK | [19 empty] | YES | POROSITY IN WELD RESULTED IN PINHOLE LEAK. | [55 empty] | YES | YES |  |  | YES |  |  |  | 2012 | [31 empty] | 2012 | [23 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | deteschendorf@spectraenergy.com | 713-627-5573 | 713-386-4468 |  |  |  | RICK KIVELA | DIRECTOR OF OPERATIONAL COMPLIANCE | 713-627-6388 | rwkivela@spectraenergy.com | ON NOVEMBER 21, 2012, A LANDOWNER REPORTED A SMELL ASSOCIATED WITH PIEPLINE ODORANT. SPECTRA ENERGY PERSONNEL DISCOVERED NATURAL GAS FROM ALGONQUIN 6-INCH LINE E-1 WAS BUBBLING UP IN STONY BROOK WHICH IS LESS THAN ONE FOOT DEEP. A PINHOLE LEAK IN THE CIRCUMFERENTIAL WELD OF THE PIPE WAS DISCOVERED. REPLACEMENT OF THE PIPE WAS COMPLETED ON NOVEMBER 25, 2012.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120125 | 16387 | 2012-12-14 10:22 | SUPPLEMENTAL FINAL | 2564 | COLORADO INTERSTATE GAS CO | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2012-11-26 03:56 | 2012 |  |  | 41.4339 | -105.9358 | 1031501 | 2012-11-26 06:20 |  | NATURAL GAS |  | 33806 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | STATION WAS OFF-LINE AT TIME OF INCIDENT. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-11-26 03:56 | 2012-11-26 04:20 | ONSHORE | WY | 82070 | LARAMIE | ALBANY | SURVEY STATION NO. | 156+48188 | LARAMIE COMPRESSOR STATION | 5A | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [8 empty] | CARBON STEEL |  | OTHER | [8 empty] | FAILED HAZARDOUS GAS DETECTOR CAUSED PARTIAL STATION ESD. STATION SUCTION ESD VALVE ONLY PARTIALLY CLOSED DUE TO MALFUNCTION IN VALVE ACTUATOR CAUSING CONTINUOUS VENTING. OPERATIONS PERSONNEL SECURED THE AREA AND SHUT-IN THE VENT VALVES. | CLASS 1 LOCATION | NO |  | 483 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 60343 | 48606.0951374207 | 1000 | 1148.3 | 800 | 918.64 | 0 | 0 |  |  | 62143 | 51340.9258773784 | 50673.0351374207 | [8 empty] | 651 |  | 850 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PROBABLE CAUSE WAS CONFINED TO STATION EQUIPMENT AND NOT UNDER CONTROL OF THE CONTROL ROOM. UPON RECEIPT OF ALARM, GAS CONTROLLER EXECUTED NOTIFICATION PROCEDURES AS REQUIRED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [6 empty] | YES | HAZARDOUS GAS DETECTOR AND VALVE ACTUATOR. | [22 empty] | YES | HAZARDOUS GAS DETECTOR REPLACED AND ACTUAUTOR CLEANED AND REPAIRED. | [161 empty] | STEPHEN R. DINES | COMPLIANCE ENGINEER | stephen.dines@kindermorgan.com | 719 481 1271 | 719 329 5673 |  |  |  | REJI GEORGE | DIRECTOR - ENGINEERING CODES AND STANDARDS | 713-420-5433 | george_reji@kindermorgan.com | FAILED HAZARDOUS GAS DETECTOR CAUSED PARTIAL STATION ESD. UNIT SUCTION ESD VALVE ONLY PARTIALLY CLOSED DUE TO MALFUNCTION IN VALVE ACTUATOR CAUSING CONTINUOUS VENTING EXCEEDING REPORTING CRITERIA. OPERATIONS PERSONNEL SECURED THE AREA AND SHUT-IN THE VENT VALVES.
2021-02-26 10:37 | NO | NO | GG (Gas Gathering) | 20120127 | 15720 | 2012-12-20 12:17 | SUPPLEMENTAL FINAL | 32668 | PVR MARCELLUS GAS GATHERING, LLC | 301 COMMERCE, STE 700 | FORT WORTH | TX | 76102 | 2012-11-23 03:00 | 2012 |  |  | 41.3911 | -75.9853 | 1031807 | 2012-11-28 19:17 |  | NATURAL GAS |  | 5400 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-11-23 03:26 | 2012-11-23 04:31 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-11-23 03:05 | 2012-11-23 03:21 | ONSHORE | PA | 18612 | DALLAS | MONROE TOWNSHIP |  |  | WYOMING 24" AT CHAPIN STATION |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2012 |  | CARBON STEEL |  | LEAK |  |  | OTHER | FAULTY RELIEF VALVE | [5 empty] | CLASS 2 LOCATION | NO |  | 637 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 21060 | 16963.7632135307 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 21060 | 17587.1035940803 | 16963.7632135307 | [8 empty] | 1172 |  | 1480 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 1 | YES | [7 empty] | NO | [6 empty] | TYPE A GATHERING | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [16 empty] | YES | [174 empty] | EDWARD SENAVAITIS | SAFETY AND REGULATORY COMPLIANCE MANAGER | esenavaitis@pvrpartners.com | 5705053777 | 5705053798 |  |  |  | EDWARD SENAVAITIS | SAFETY AND REGULATORY COMPLIANCE MANAGER | 5705053777 | esenavaitis@pvrpartners.com | ON FRIDAY, NOVEMBER 23RD AT 3:00 AM, A 4 INCH ANDERSON GREENWOOD PRESSURE RELIEF VALVE ON THE INLET SIDE OF THE CHAPIN DEHYDRATION FACILITY MALFUNCTIONED CAUSING NON-ODORIZED GAS TO BE RELEASED TO THE ATMOSPHERE. A PVR OPERATOR AND THE LOCAL FIRE DEPARTMENT RESPONDED TO THE FACILITY. THE INCIDENT LASTED FOR APPROXIMATELY 30 MINUTES BEFORE THE LOCAL OPERATOR MANUALLY CLOSED THE BLOCK VALVE UNDER THE RELIEF VALVE TO STOP THE GAS FROM VENTING. SINCE NATURAL GAS IS LIGHTER THAN AIR, THE RELEASED VOLUME QUICKLY DISSIPATED WITHOUT ANY RISK TO THE PUBLIC, ENVIRONMENT, OR EMPLOYEES. AN INTERNAL INVESTIGATION TEAM DETERMINED THAT THE PRESENCE OF ICE IN THE PILOT SENSING LINE OF THE VALVE WAS LIKELY THE CAUSE OF THE EQUIPMENT MALFUNCTION. THE VALVE WAS SENT TO A THIRD PARTY FOR FURTHER INSPECTION AND ANALYSIS. THE THIRD PARTY COULD NOT DEFINITIVELY DETERMINE WHETHER ICE RESULTED IN THE MALFUNCTION. HOWEVER, THE REPORT DOES STATE THAT ICE COULD HAVE VERY WELL BEEN THE PRIMARY CAUSAL FACTOR. DUE TO REDUNDANT OVERPRESSURE PROTECTION ON THIS SYSTEM, PVR DOES NOT PLAN TO REINSTALL A VALVE AT THIS LOCATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120128 | 16360 | 2012-12-28 12:08 | SUPPLEMENTAL | 31968 | WTG GAS TRANSMISSION COMPANY | 211 NORTH COLORADO | MIDLAND | TX | 79701 | 2012-12-05 18:00 | 2012 |  |  | 31.9774 | -102.6311 | 1032446 | 2012-12-05 22:40 |  | NATURAL GAS |  | 5212 | 704 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-12-05 18:47 | 2012-12-06 18:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2012-12-05 18:00 | 2012-12-05 18:40 | ONSHORE | TX | 79741 | GOLDSMITH | ECTOR | MILEPOST | MILEPOST | SNYDER 16" @ MILEPOST 0+875 | PIPELINE 1122 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 35 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.25 | 42000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | YOUNGSTON STEEL AND TUBE | COAL TAR | [28 empty] | 1953 | 1952 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 42 | 15.5 |  | CLASS 1 LOCATION | NO |  | 306 |  | NO | NO | NO |  | 400000 | 459320 | 2816 | 3233.6128 | 20848 | 16792.9978858351 | 10000 | 11483 | 20000 | 22966 | 0 | 0 |  |  | 453664 | 245547.377024947 | 513795.610685835 | [8 empty] | 480 |  | 610 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 46844 | NO |  | YES |  | YES |  |  |  | YES |  |  | YES |  | YES | NO ALTERNATE SUPPLY FOR GOLDSMITH | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1953 | NO | YES | YES |  |  |  | 2011 |  |  |  | NO | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | RAY REED | DIRECTORY OF INTEGRITY MANAGEMENT | rreed@wtghugoton.com | 6202713793 | 8063540797 |  |  |  | RICHARD HATCHETT | VP OF OPERATIONS | 4326824349 | rhatchett@westtexasgas.com | DURING PREPARATION FOR AN 8 HOUR INTEGRITY MANAGMENT PRESSURE TEST (REQUIRED BY THE STATE OF TEXAS) SCHEDULED FOR DECEMBER 6, 2012, WTG EMPLOYEES BART BEAN, CHRIS BALTZELL, AND RAY REED WERE IN THE PROCESS OF INCREASING THE PRESSURE PROFILE OF THE SNYDER 16" PIPELINE FROM THE MARTIN COUNTY #3 COMPRESSOR STATION TO THE EL PASO ENERGY TAP WEST OF THE TOWN OF GOLDSMITH, TEXAS. DURING THE MORNING OF DECEMBER 5TH, THE PIPELINE WAS CONFIGURED FOR TEST AND NOTIFICATION WAS MADE TO THE GENERAL PUBLIC WITHIN 660' OF THE PIPELINE. IN ADDITION TO THE PUBLIC, THE CITY OFFICIALS FROM GOLDSMITH WERE NOTIFIED OF THE PENDING TEST. THE PLAN INCLUDED ISOLATION OF THE TEST SEGMENT AND RAISING THE PRESSURE PROFILE OF THE PIPELINE. THE PLAN WAS TO RAISE PRESSURE WITHIN THE PIPELINE TO A POINT JUST BELOW 610 PSIG (MAOP) ON THE DAY PRIOR TO TEST. COMPRESSION AT MARTIN COUNTY #3 WAS THE PRESSURE SOURCE. THE DATA ACQUISITION SYSTEM WAS BEING MONITORED AT MARTIN COUNTY #3, AT APPROXIMATELY 17:45, THE PRESSURE AT A DELIVERY POINT ON THE WEST END OF THE SYSTEM WAS 499 PSIA. THE NEXT CYCLE OF THE DATA AT APPROXIMATELY 18:00, PRESSURE AT THE SAME POINT HAD DECREASED TO 450 PSIA. IMMEDIATELY MARTIN COUNTY 3 COMPRESSION WAS ISOLATED FROM THE SNYDER 16" PIPELINE AND DURING THIS PROCESS CHRIS BALTZELL RECEIVED A CALL AT 18:02 FROM AN EMPLOYEE WITH THE CITY OF GOLDSMITH COMMUNICATING BLOWING GAS WEST OF TOWN. THE FOLLOWING ISOLATION PLAN WAS DEVELOPED AND IMMEDIATELY ENACTED: CHRIS BALTZELL TO SIGHT OF BLOWING GAS RAY REED TO BLOCK VALVE #1 TO ISOLATE (CLOSEST TO BV TO SCENE) BART BEAN TO RE-CONFIGURE MARTIN COUNTY #3, ISOLATE BLOCK VALVE #4, ORGANIZED EMERGENCY RESPONSE, CONTACTED CREWS TO INTIATE REPAIRS AND THEN TO SCENE OF BLOWING GAS DURING TRAVEL TO SCENE, CHRIS WAS INFORMED THE BLOWING GAS HAD BEEN IGNITED; DCP FACILITIES WERE INVOLVED AND EMERGENCY RESPONDERS WERE IN-ROUTE TO SCENE. TRAVEL DISTANCE TO SCENE FROM MARTIN COUNTY #3 WAS APPROXIMATELY 43 MILES. ORDER OF EVENTS AT SCENE: CHRIS ON SITE AT 18:45 RAY AT BLOCK VALVE #1 AT 18:40 AND ISOLATED AT 18:45 RAY ON SITE AT 18:55 FIRE BURNED OUT AT 19:15 BART ON SITE AT 19:30 CONTRACT PERSONAL AND EQUIPMENT ON STANDBY AT SCENE 20:00
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120129 | 16275 | 2012-12-28 18:27 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2012-11-30 09:54 | 2012 |  |  | 36.922 | -120.0193 | 1031956 | 2012-11-30 11:40 |  | NATURAL GAS |  | 7010 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | [9 empty] | NO |  |  |  |  | NO | [7 empty] | 2012-11-30 09:54 | 2012-11-30 10:10 | ONSHORE | CA | 93637 | MADERA | MADERA | MILEPOST | 7.8 | 118B |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 10 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12.75 |  | 0.25 | 42000 | 12.75" OD 0.25" WT X42 ERW | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | NA | ASPHALT | [28 empty] | 1965 | 1965 | CARBON STEEL |  | MECHANICAL PUNCTURE | [9 empty] | CLASS 1 LOCATION | NO |  | 166 |  | NO | NO | NO |  | 450 | 516.735 | 3000 | 3444.9 | 10450 | 8417.44186046512 | 350000 | 401905 | 0 | 0 | 0 | 0 |  |  | 363900 | 195030.239186046 | 414284.076860465 | [8 empty] | 370 |  | 400 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | [16 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT CAUSED BY THIRD PARTY DIG-IN | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  |  |  | YES | [6 empty] | UNKNOWN/OTHER | GRADER/SCRAPER | GRADING | NO |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | YES | 27 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | NICOLE BUNN | ASSOCIATE GAS ENGINEER | neb6@pge.com | 925-322-3311 |  |  |  |  | LAURENCE DENISTON | ACTING MANAGER | 925-328-5756 | lcd1@pge.com | ON NOVEMBER 30, 2012 AT APPROXIMATELY 0954 HOURS A THIRD PARTY EXCAVATOR (MADERA IRRIGATION DISTRICT) STRUCK AND SEVERELY DAMAGED PACIFIC GAS AND ELECTRIC COMPANY'S (PG&E) 12-INCH NATURAL GAS TRANSMISSION LINE 118B AT MILE POINT 7.8, RESULTING IN A RELEASE OF GAS. THE THIRD PARTY EXCAVATOR WAS USING A TRACTOR WITH A BLADE TO CLEAN OUT THE BOTTOM OF A DRY CREEK AND DID NOT COMPLY WITH EXCAVATION DAMAGE PREVENTION REGULATIONS BY FAILING TO CALL USA PRIOR TO EXCAVATION. GAS PIPELINE MARKERS WERE IN PLACE. PG&E REPRESENTATIVES ARRIVED ON-SITE AT 1010 HOURS. PG&E CREWS ISOLATED THE DAMAGED SECTION OF PIPELINE BY CLOSING TAP VALVES AND MAIN LINE VALVES. THE FLOW OF GAS WAS BROUGHT DOWN FROM 370 PSIG TO 4 PSIG AT 1430 HOURS. THE THREE FEET OF DAMAGED PIPELINE WAS REPLACED WITH 12-INCH OD, 0.281 INCH WT, X-42, PRE-TESTED PIPE. THE REPAIR WORK WAS COMPLETED AT APPROXIMATELY 1215 HOURS ON DECEMBER 1, 2012. ELEVEN CUSTOMERS EXPERIENCED GAS SERVICE INTERRUPTION AND ALL ELEVEN SERVICES WERE RESTORED BY 1730 HOURS ON DECEMBER 1, 2012. THE TEMPORARY INSTALLATION OF COMPRESSED NATURAL GAS WAS USED TO MAINTAIN GAS SERVICE TO MANY OF THE SURROUNDING CUSTOMERS. OUT OF AN ABUNDANCE OF CAUTION, NORTHBOUND AND SOUTHBOUND HIGHWAY 99 AND THE ADJACENT RAILROAD WERE SHUT DOWN, AND THE AREA WAS EVACUATED WITHIN A HALF MILE RADIUS. THERE WERE NO INJURIES, NO FATALITIES AND NO IGNITION AS A RESULT OF THIS INCIDENT. THIS INCIDENT WAS REPORTED TO BOTH THE DOT AND THE CPUC BECAUSE THE COST OF DAMAGES EXCEEDED $50,000, AND THE VOLUME OF UNINTENTIONALLY RELEASED GAS WAS GREATER THAN 3 MMCF. IN ADDITION, SACRAMENTO MAJOR TV NEWS MEDIA CHANNELS 30 AND 47 WERE OBSERVED ON-SCENE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20120130 | 16076 | 2012-12-28 19:55 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2012-12-01 08:40 | 2012 |  |  | 37.9652 | -121.2466 | 1032021 | 2012-12-01 10:35 |  | NATURAL GAS |  | 4700 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-12-01 09:56 | 2012-12-02 08:26 |  |  |  |  | NO |  |  |  |  | NO | [7 empty] | 2012-12-01 08:40 | 2012-12-01 09:05 | ONSHORE | CA | 95205-4711 | STOCKTON | SAN JOAQUIN | MILEPOST | 1.64 | DISTRIBUTION FEEDER MAIN 1609-01 |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 54 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 |  | 0.156 | 42000 | 6.625" OD 0.156" WT X-42 ERW | LONGITUDINAL ERW - HIGH FREQUENCY |  | NA | COLD APPLIED TAPE | [28 empty] | 1985 | 1985 | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | LONGITUDINAL, THEN ROTATED TO CIRCUMFERENTIAL | 18 |  |  | CLASS 3 LOCATION | YES | METHOD2 | 111 |  | NO | NO | NO |  | 15000 | 17224.5 | 0 | 0 | 16000 | 12887.9492600423 | 465000 | 533959.5 | 50000 | 57415 | 0 | 0 |  |  | 546000 | 292724.522198731 | 621486.949260042 | [8 empty] | 412 |  | 720 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 6125 | [15 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS APPARENT THAT CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WERE NOT A CONTRIBUTING FACTOR TO THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [64 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | [10 empty] | NO | YES | OTHER |  |  | YES | YES | [5 empty] | UTILITY | AUGER | POLE | NO |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO |  | PREVIOUS DAMAGE | [121 empty] | NO | [62 empty] | NO | NO |  |  | Yes, but the point of the Accident was not identified as a dig site |  | 1985 | [11 empty] | NO | [63 empty] | CHARLES CHANG | ASSOCIATE ENGINEER | cyc8@pge.com | 925-974-4248 |  |  |  |  | FRANCES YEE | ACTING DIRECTOR | 925 974-4207 | fsc2@pge.com | ON DECEMBER 1, 2012 AT APPROXIMATELY 0840 HOURS, PACIFIC GAS AND ELECTRIC COMPANY (PG&E) WAS NOTIFIED OF A RELEASE OF GAS AT 3331 EAST MINER AVENUE IN THE CITY OF STOCKTON ON DISTRIBUTION FEEDER MAIN 1609-01, MILE POINT 1.64. A PG&E REPRESENTATIVE ARRIVED ON SCENE OF THE INCIDENT AT 0905 HOURS AND THE FLOW OF GAS WAS STOPPED AT 0956 HOURS. THE RELEASE OF GAS WAS DETERMINED TO BE THE RESULT OF A PIPELINE RUPTURE. THE SECTION OF RUPTURED PIPELINE WAS REMOVED AND TRANSPORTED TO A LABORATORY FOR FURTHER ANALYSIS. THE REMAINING PIPELINE WAS CAPPED IN THE FIELD. OUT OF AN ABUNDANCE OF CAUTION, APPROXIMATELY SIX BLOCKS SURROUNDING THE RUPTURE SITE WERE EVACUATED AND THE FIRE DEPARTMENT SHUT OFF GAS SERVICES TO THE SURROUNDING AREA. SEVENTY-EIGHT CUSTOMERS EXPERIENCED GAS SERVICE INTERRUPTIONS. SERVICE WAS RESTORED ON 2100 HOURS, DECEMBER 1, 2012, VIA REDUNDANT LINES TO ALL CUSTOMERS WITH THE EXCEPTION OF THE "CAN'T-GET-INS." PG&E CREWS COMPLETED A BYPASS LINE AT THE RUPTURE LOCATION AT 0826 HOURS ON DECEMBER 2, 2012, RESTORING SERVICE TO THE REMAINING CUSTOMERS WHO WERE OUT OF SERVICE. THIS INCIDENT WAS REPORTED TO BOTH THE DOT AND THE CPUC BECAUSE THE COST OF DAMAGES EXCEEDED $50,000, AND THE VOLUME OF UNINTENTIONALLY RELEASED GAS WAS GREATER THAN 3 MMCF. IN ADDITION, SACRAMENTO MAJOR TV NEWS MEDIA CHANNELS 3, 10 AND 4 WERE OBSERVED ON-SCENE. PG&E DETERMINED THAT A ROOT CAUSE OF THE INCIDENT WAS PREVIOUS DAMAGE TO THE PIPE CAUSED BY AN ELECTRIC DEPARTMENT POLE AUGER DURING ELECTRIC POLE INSTALLATIONS IN 1996. PG&E INVESTIGATED THE OTHER SITES ALONG THE LINE WHERE POWER POLES WERE INSTALLED. FOUR ADDITIONAL PIPE LOCATIONS WERE IDENTIFIED AS HAVING SIMILAR DAMAGE; THESE DAMAGED SECTIONS WERE REPLACED AND STRENGTH TESTED TO RE-ESTABLISH AN MAOP OF 720 PSIG.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130001 | 16610 | 2013-01-09 20:49 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION CORP | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2012-12-11 12:41 | 2012 |  |  | 38.5026 | -81.6449 | 1032935 | 2012-12-11 13:20 |  | NATURAL GAS |  | 76000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-12-11 13:37 | 2014-01-15 11:20 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 12 | 2012-12-11 12:53 | 2012-12-11 13:20 | ONSHORE | WV | 25312 | SISSONVILLE | KANAWHA | SURVEY STATION NO. | 237+13 | SM-80 | SM80-230 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 66 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.281 | 60000 | API 5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | EPOXY | [28 empty] | 1967 | 1967 | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | APPROXIMATE 20-FOOT SECTION OF PIPE WAS EJECTED | 240 | 20 |  | CLASS 2 LOCATION | NO |  | 495 |  | NO | NO | NO |  | 3280000 | 3766424 | 0 | 0 | 285760 | 230178.773784355 | 410000 | 470803 | 105458 | 121097.4214 | 295000 | 338748.5 | MULTIPLE EXPENSES INCURRED DUE TO THE LOSS OF THE PIPELINE |  | 4376218 | 2394717.19826934 | 4927251.69518436 | [8 empty] | 929 |  | 1000 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 41870 | NO |  | YES |  | YES |  |  |  | YES |  |  |  |  | YES | INSTALL TEMPORARY LAUNCHER/RECEIVER | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | [8 empty] | YES | 11 | 0 | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [8 empty] | YES | YES |  |  | YES | YES | 1967 | YES | YES | YES | YES |  |  | 2012 | 1995 |  |  | NO | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | GEORGE HAMATY | ENGINEER | ghamaty@nisource.com | 3043573728 | 3073573804 |  |  |  | PERRY MICHAEL HOFFMAN | MANAGER | 3043572548 | mikehoffman@nisource.com | ON DECEMBER 11, 2012, A 20 INCH DIAMETER NATURAL GAS TRANSMISSION PIPELINE RUPTURED IN SISSONVILLE, WEST VIRGINIA. THE NATURAL GAS IGNITED AND SEVERAL NEARBY RESIDENCES WERE DAMAGED AS A RESULT. THE FAILED TRANSMISSION PIPELINE IS OWNED, OPERATED AND MAINTAINED BY COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA). AN INVESTIGATION INTO THE CAUSE OF THE INCIDENT WAS CONDUCTED BY THE NATIONAL TRANSPORTATION SAFETY BOARD (NTSB). COLUMBIA PARTICIPATED IN THIS INVESTIGATION. AREAS OF INVESTIGATION INCLUDE THE TIME OF THE RUPTURE, THE RECOGNITION OF THE RUPTURE, THE RESPONSE TO THE RUPTURE, LABORATORY ANALYSIS OF THE RELEVANT SECTION OF PIPE, AND OTHER AREAS THAT BEAR ON THE INFORMATION COVERED BY THIS FORM. THE PROBABLE CAUSE OF THE FAILURE OF LINE SM-80 AS DETERMINED BY THE NTSB WAS PRESENTED IN THE NTSB INCIDENT REPORT (NTSB/PAR-14/01 PB2014-103977).
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130002 | 16257 | 2013-01-10 12:36 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2013-01-02 03:43 | 2013 |  |  | 30.2397 | -89.4973 | 1034680 | 2013-01-02 18:52 |  | NATURAL GAS |  | 22000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | GAS RELEASE WAS DUE TO A RELIEF VALVE MALFUNCTION SO ONLY THAT DEVICE ISOLATED. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-01-02 03:45 | 2013-01-02 03:45 | ONSHORE | MS | 39520 | BAY SAINT LOUIS | HANCOCK |  |  | BAY SAINT LOUIS COMPRESSOR STATION |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | RELIEF VALVE | 2012 |  | CARBON STEEL |  | OTHER | [8 empty] | GAS RELEASE THROUGH RELIEF VALVE OUTLET STACKS. | CLASS 1 LOCATION | NO |  | 182 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 88000 | 68704.9180327869 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 88000 | 71229.5081967213 | 68704.9180327869 | [8 empty] | 897 |  | 936 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE WAS BELOW MAOP AND THE OCCURRENCE WAS DUE TO A MECHAQNICAL FAILURE OF A RELIEF VALVE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | NOT YET DETERMINED, PENDING ROOT CAUSE ANALYSIS. | [161 empty] | MARTIN MULLER | COMPLIANCE ENGINEER | martin_muller@kindermorgan.com | (205)325-3863 | (205)325-3508 |  |  |  | MARTIN MULLER | COMPLIANCE ENGINEER | (205)325-3863 | martin_muller@kindermorgan.com | ON JANUARY 2, 2013, A 8-INCH X DOUIBLE 8-INCH RELIEF VALVE MALFUNCTIONED AT TENNESSEE GAS PIPELINE'S BAY SAINT LOUIS COMPRESSOR STATION IN BAY SAINT LOUIS, MS. THE RELIEF VALVE RELEASED NATURAL GAS TO THE ATMOSPHERE FOR APPROXIMATELY 25 MINUTES AND EXCEEDED PHMSA'S REPORTABLE QUANTITY THRESHOLD FOR A PIPELINE INCIDENT. THE RELIEF VALVE WAS ISOLATED BY CLOSING A VALVE BENEATH IT. RELIEF VAVLE WAS CLEANED, SET, AND RETURNED TO SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130003 | 16269 | 2013-01-11 16:42 | SUPPLEMENTAL FINAL | 5304 | FLORIDA GAS TRANSMISSION CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2012-12-13 09:38 | 2012 |  |  | 26.6197 | -80.1735 | 1033110 | 2012-12-13 10:08 |  | NATURAL GAS |  | 6004 | 9344 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-12-13 09:38 | 2012-12-17 19:53 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-12-13 09:38 | 2012-12-13 09:38 | ONSHORE | FL | 33467 | LAKE WORTH | PALM BEACH COUNTY | SURVEY STATION NO. | 3156+59 | FLMEA-21 | 18" VALVE SECTION 20-3 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 98 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 18 |  | 0.25 | 52000 | API 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | YOUNGSTOWN SHEET & TUBE | COLD APPLIED TAPE | [28 empty] | 1959 | 1959 | CARBON STEEL |  | LEAK |  |  | OTHER | ROAD FEATURE AND BEND STRESSES | [5 empty] | CLASS 3 LOCATION | YES | METHOD2 | 366 |  | NO | NO | NO |  | 50000 | 57415 | 31453 | 36117.4799 | 20188 | 16261.3699788583 | 483900 | 555662.37 | 4000 | 4593.2 | 0 | 0 |  |  | 589541 | 316964.866934249 | 670049.419878858 | [8 empty] | 840 |  | 866 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | AUTOMATIC | 27456 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO ABNORMAL OPERATING CONDITIONS EXISTED. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [103 empty] | OTHER OUTSIDE FORCE DAMAGE | [9 empty] | CIRCUMFERENTIAL SCC DUE TO ROAD FEATURE AND BEND STRESSES | [251 empty] | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | THIS SUPPLEMENTAL/FINAL HAS UPDATED THE SECTION G4 - CAUSE. DURING A LEAK SURVEY A POSSIBLE LEAK WAS SUSPECTED ON 12/12/2012. AFTER INVESTIGATING, A LEAK WAS CONFIRMED AT 9:38 AM ON 12/13/2012. NOTE THE REASON THERE ARE REPETITIVE (09:38, 12/13/12) DATE ENTRY FOR SECTIONS : A (15.A), A (19.A), A (19.B) IS BECAUSE THE PORTAL DOES NOT ALLOW A DATE PRIOR TO THE "DATE OF THE INCIDENT" TO BE ENTERED. LISTED BELOW ARE THE ACTUAL TIMES AND DATES FOR THESE SECTIONS MENTIONED ABOVE: A (15.A) LOCAL TIME AND DATE OF SHUTDOWN (17:15, 12/12/12) A (19.A) LOCAL TIME OPERATOR IDENTIFIED POTENTIAL INCIDENT (11:30, 12/12/12) A (19.B) LOCAL TIME OPERATOR RESOURCES ARRIVED ON SITE (12:00, 12/12/12)
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130004 | 16490 | 2013-01-14 17:16 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2012-12-23 02:00 | 2012 |  |  | 31.27 | -103.0859 | 1034063 | 2012-12-23 16:10 |  | NATURAL GAS |  | 4230 |  | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE RELIEF VALVE RESET WHEN THE PRESSURE WAS LOWERED. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-12-23 02:00 | 2012-12-23 02:10 | ONSHORE | TX | 79730 | COYANOSA | PECOS |  |  | WAHA COMPRESSOR STATION | UNIT 601 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [8 empty] | CARBON STEEL |  | OTHER | [8 empty] | FACILITY WAS SHUTDOWN AUTOMATICALLY BY A GAS ANALYZER WHICH CAUSED THE PRESSURE TO INCREASE RESULTING IN THE ACTUATION OF A RELIEF VALVE VENTING GAS TO ATMOSPHERE. | CLASS 1 LOCATION | NO |  | 536 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 13536 | 10903.2050739958 | 5000 | 5741.5 | 0 | 0 | 0 | 0 |  |  | 18536 | 13939.3477801268 | 16644.7050739958 | [8 empty] | 1020 |  | 1050 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | YES | [33 empty] | YES | H2S GAS ANALYZER FAILED CAUSING SHUTDOWN AND ACTUATION OF RELIEF VALVE | [161 empty] | ANTHONY BROWN | SR. PIPELINE COMPLIANCE ENGINEER | abrown@eprod.com | 713-381-5757 |  |  |  |  | ANTHONY BROWN | SR. PIPELINE COMPLIANCE ENGINEER | 713-381-5757 | abrown@eprod.com | ON DECEMBER 23, 2012 AT 02:00AM, THE RELIEF VALVE ON WAHA COMPRESSOR #601 DISCHARGED. THIS RESULTED IN A RELEASE OF 4,230 MCF OF NATURAL GAS. THE OPERATING PRESSURE NEVER EXCEEDED 1020PSIG AT THE STATION THUS, NEVER EXCEEDING THE MAOP IS 1050 PSIG. UPON INVESTIGATION, A GAS ANALYZER DESIGNED TO DETECT H2S AT THE DELIVERY POINT FAILED RESULTING IN A SHUTDOWN OF THE COMPRESSOR STATION. THE SHUTDOWN RESULTED IN AN INCREASE OF PRESSURE AND SUBSEQUENT ACTIVATION OF THE RELIEF VALVE CAUSING THE RELEASE OF NATURAL GAS TO ATMOSPHERE. THE RELIEF VALVE FUNCTIONED PROPERLY AS DESIGNED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130005 | 15823 | 2013-01-17 15:36 | SUPPLEMENTAL FINAL | 22655 | WBI ENERGY TRANSMISSION, INC. | 1250 WEST CENTURY AVENUE | BISMARCK | ND | 58503 | 2012-12-25 20:53 | 2012 |  |  | 44.5082 | -105.6298 | 1034718 | 2013-01-03 10:37 |  | NATURAL GAS |  | 4199 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | GAS RELEASED THROUGH VENT PIPE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-12-25 20:53 | 2012-12-25 23:47 | ONSHORE | WY | 82716 | GILLETTE | CAMPBELL | SURVEY STATION NO. | 0+00 | LANDECK COMPRESSOR STATION | ESD VENT LINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | OTHER | COMPRESSOR STATION VENT PIPE |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | EMERGENCY SHUT DOWN (ESD) VENT PIPING | 2001 |  | CARBON STEEL |  | OTHER | [8 empty] | GAS WAS RELEASED THROUGH A 2" VENT LINE AS A RESULT OF A PARTIAL FREEZE OFF OF THE SUPPLY GAS TO THE EMERGENCY SHUTDOWN SYSTEM (ESD). | CLASS 1 LOCATION | NO |  | 386 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 12888 | 10381.2431289641 | 2163 | 2483.7729 | 246 | 282.4818 | 0 | 0 | HEAT TRACE WAS PERMANENTLY INSTALLED TO PREVENT THE LINE FROM FREEZING AGAIN. |  | 15297 | 12032.4900310782 | 13147.4978289641 | [8 empty] | 645 |  | 1120 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  |  | YES | [5 empty] | YES | INFORMATION WAS IDENTIFIED THAT WOULD HAVE BEEN USEFUL FOR THE CONTROLLER TO IDENTIFY THE INCIDENT. COMPRESSOR RUN STATUS AND A GENERAL STATION ALARM HAVE BEEN ADDED TO THE SCADA SYSTEM TO PROVIDE MORE INFORMATION TO CONTROLLERS. | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | NO | [306 empty] | KENT KAHL | DOT COMPLIANCE SUPERVISOR | kent.kahl@wbienergy.com | 406-359-7222 | 406-359-7244 |  |  |  | KENT KAHL | DOT COMPLIANCE SUPERVISOR | 406-359-7222 | kent.kahl@wbienergy.com | A 2" VENT LINE RELEASED NATURAL GAS AS A RESULT OF A PARTIAL FREEZE OFF OF THE SUPPLY GAS TO THE EMERGENCY SHUT DOWN SYSTEM. FREEZING OF THE SUPPLY GAS LINE RESULTED IN THE STATION NOT ISOLATING AND OPENING ONE BLOW DOWN VALVE RELEASING GAS THROUGH THE 2" VENT LINE. SINCE THE FREEZE OFF PREVENTED THE STATION FROM ISOLATING, THE 2" VENT LINE BLEW GAS UNTIL PERSONNEL WERE ABLE TO REACH THE SITE AND RESTORE OPERATION. THIS INCIDENT OCCURRED IN A RURAL LOCATION AT A COMPRESSOR STATION APPROXIMATELY 17 MILES NORTH OF GILLETTE, WY. THE SUPPLEMENTAL REPORT WAS SUBMITTED RESULTING FROM A RECOMMENDATION FROM PHMSA TO CHANGE THE CAUSE OF THE INCIDENT FROM 'G8 ' OTHER INCIDENT CAUSE' TO 'G2 ' NATURAL FORCE DAMAGE.' A SECOND SUPPLEMENTAL REPORT WAS SUBMITTED RESULTING FROM A RECOMMENDATION FROM PHMSA TO UNCHECK THE BOX "INVESTIGATION IDENTIFIED NO CONTROL ROOM ISSUES" IN PART E QUESTION 8. THE BOX WAS UNCHECKED SINCE WBI IDENTIFIED AND ADDED USEFUL SCADA POINTS TO HELP CONTROL ROOM OPERATORS IDENTIFY ABNORMAL CONDITIONS. APPENDED PART E5F TO TRANSMISSION SYSTEM PER DOT EMAIL REQUEST FROM BLAINE KEENER ON 3/4/13.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20130006 | 15981 | 2013-01-18 08:57 | SUPPLEMENTAL FINAL | 32646 | CHESAPEAKE OPERATING INC. | 6100 N. WESTERN AVE. | OKLAHOMA CITY | OK | 73118 | 2012-12-11 08:30 | 2012 |  |  | 32.4606 | -93.549 | 1032918 | 2012-12-11 10:30 |  | NATURAL GAS |  | 250 | 500 | 50 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-12-11 09:30 | 2013-01-02 10:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-12-11 09:00 | 2012-12-11 09:00 | ONSHORE | LA | 71037 |  | BOSSIER |  |  |  | 570431 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 120 |  | YES | [6 empty] | YES | UNCASED |  | 1 | BELOW WATER, PIPE IN BORED/DRILLED CROSSING | [11 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10.75 |  | 0.365 | 42000 | API 5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | COAL TAR | [29 empty] | 1957 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 2 LOCATION | NO |  | 227 |  | NO | NO | NO |  | 5000 | 5741.5 | 2000 | 2296.6 | 1000 | 805.496828752643 | 245000 | 281333.5 | 30000 | 34449 | 0 | 0 |  |  | 283000 | 149477.295137421 | 324626.096828753 | [8 empty] | 50 |  | 1350 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 2800 | YES | [7 empty] | YES |  | YES | YES |  |  |  | TYPE A GATHERING | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  | YES |  |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NOT APPLICABLE - NOT MAINLINE PIPE | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | BRIAN PUTNAM | PIPELINE MANAGER | brian.putnam@chk.com | 405-935-6908 |  |  |  |  | BRIAN PUTNAM | PIPELINE MANAGER | 405-935-6908 | No Email Address | CORROSION-RELATED LEAK ON A LOW FLOW, LOW PRESSURE CLASS 2 GATHERING LINE. THE LEAK WAS IN AN INTERMITTENT CREEK CROSSING. THE PIPELINE WAS ORIGINALLY HDD'D AND WAS 10 PLUS FEET DEEP AT THE LEAK SITE. THE DECISION WAS MADE TO ABANDON IN PLACE AND REPLACE WITH A NEW PIPE CROSSING OF TRENCHED CONSTSRUCTION TO MINIMIZE THE WATER TRAP ASSOCIATED WITH THE CROSSING.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130007 | 16271 | 2013-01-24 16:52 | SUPPLEMENTAL FINAL | 5304 | FLORIDA GAS TRANSMISSION CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2012-12-26 05:55 | 2012 |  |  | 28.0609 | -80.7219 | 1034170 | 2012-12-26 07:41 |  | NATURAL GAS |  | 293976 | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-12-26 05:55 | 2013-04-19 14:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-12-26 05:55 | 2012-12-26 06:30 | ONSHORE | FL | 32904 | MELBOURNE | BREVARD | SURVEY STATION NO. | 1613+22 | FLMEA-18 | VALVE SECTION 18-3 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 20 |  | 0.25 | 52000 | API 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | YOUNGSTOWN SHEET & TUBE | COLD APPLIED TAPE | [28 empty] | 1959 | 1959 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 360 | 54 |  | CLASS 1 LOCATION | NO |  | 422 |  | NO | NO | NO |  | 14000 | 16076.2 | 0 | 0 | 1022154 | 823341.805496829 | 132077 | 151664.0191 | 0 | 0 | 0 | 0 |  |  | 1168231 | 930593.021795137 | 991082.024596829 | [8 empty] | 927 |  | 936 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | MANUAL | 74976 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 3 | 0 | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) |  | YES | [13 empty] | YES | HOOK CRACK, HARD SPOT, LOW TOUGHNESS | [6 empty] | YES | [63 empty] | YES | YES |  |  | YES |  |  | YES | 2007 | [31 empty] | 2007 | [17 empty] | COMBINATION TOOL | 2012 |  |  |  |  | YES | 2000 | 1235 | Yes, but the point of the Accident was not identified as a dig site |  | 2012 | [11 empty] | NO | [63 empty] | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | THIS SUPPLEMENTAL/FINAL BEING SUBMITTED, IS TO UPDATE THE INFORMATION IN SECTION G5 - CAUSE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130008 | 16045 | 2013-01-28 11:07 | SUPPLEMENTAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2013-01-08 10:20 | 2013 |  |  | 30.9953 | -90.0475 | 1035876 | 2013-01-16 15:53 |  | NATURAL GAS |  | 145 | 42339.31 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE AFFECTED PIPE SEGMENT WAS ISOLATED AND THE GAS FLOW BYPASSED. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-01-08 10:23 | 2013-01-08 10:23 | ONSHORE | LA | 70441-5164 | GREENSBURG | SAINT HELENA | MILEPOST | 626.617 | MAINLINE - D | 65D1 - 65D10 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 66 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | FLANGE ASSEMBLY | [38 empty] | 1969 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | MICARTA FLANGE GASKET | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 820 |  | NO | NO | NO |  | 0 | 0 | 147934 | 166803.429104478 | 507 | 395.834016393443 | 174620 | 196893.309112333 | 0 | 0 | 42510 | 47932.2790652003 | LABOR, RENTAL EQUIPMENT AND MATERIAL. |  | 365571 | 189358.959616821 | 412024.851298405 | [8 empty] | 712 |  | 760 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | YES | NO | NOT MANDATED |  |  | AUTOMATIC | AUTOMATIC | 33634 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK OCCURED ON A FLANGE GASKET, TRANSCO'S SCADA SYSTEM DOES NOT HAVE THE CAPABILITIES TO MONITOR FOR THIS TYPE OF LEAK. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | GASKET |  |  |  |  | YES | [175 empty] | JOHNNY LOPEZ | PIPELINE SAFETY SPECIALIST | johnny.lopez@williams.com | 7132152995 | 7132152222 |  |  |  | MARIE SOTAK | MANAGER PIPELINE SAFETY | 7132152111 | marie.sotak@williams.com | PRIMARY CAUSE OF LEAK WAS LOSS OF SUPPORT ON FLANGE RESULTING IN A CRACKED GASKET.TWO CONCRETE SUPPORTS IMMEDIATELY UPSTREAM AND DOWNSTREAM (DISTANCE FROM CENTER OF SUPPORT TO CENTER OF FLANGE APPROXIMATELY 4'-6") OF THE FLANGE WAS INSPECTED AFTER THE LEAK WAS IDENTIFIED AND BOTH WERE FOUND IN GOOD CONDITION WITH NO SOIL SETTLEMENT. HOWEVER, SOIL SETTLEMENT DID OCCUR IN AN AREA 50' TO 60' DOWNSTREAM OF THE FLANGE SET WHICH CONTRIBUTED TO THE FLANGE GASKET CRACK. THE FLANGE GASKET WAS REPLACED AND ONE ADDITIONAL CONCRETE PIPE SUPPORT WAS INSTALLED 50' DOWNSTREAM OF FLANGE TO PROVIDE ADDITIONAL SUPPORT. PLEASE SEE ATTACHED DOCUMENT FOR SEQUENCE OF LEAK INVESTIGATION EVENTS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130009 | 15954 | 2013-02-04 13:46 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2013-01-06 11:43 | 2013 |  |  | 33.961 | -118.437 | 1034954 | 2013-01-06 17:00 |  | NATURAL GAS |  | 1540 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-01-06 11:45 | 2013-04-22 10:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2013-01-06 11:43 | 2013-01-06 11:43 | ONSHORE | CA | 90213 | PLAYA DEL REY | LOS ANGELES |  |  | PLAYA DEL REY STORAGE FACILITY | V-24 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | VALVE | [31 empty] | MAINLINE | PLUG |  | FLOWSERVE NORDSTROM VALVE |  |  |  | 2007 | 2007 | CARBON STEEL |  | OTHER | [8 empty] | UNINTENTONIAL OPENING OF VALVE | CLASS 3 LOCATION | YES | METHOD2 | 435 |  | NO | NO | NO |  | 300000 | 338265.907305577 | 0 | 0 | 9250 | 7221.8237704918 | 650000 | 732909.465828751 | 500 | 563.776512175962 | 0 | 0 |  |  | 959750 | 499443.742112346 | 1078960.973417 | [8 empty] | 763 |  | 520 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  |  |  | YES | [6 empty] | YES | 1 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | VALVE PLACED IN WRONG POSITION, RESULTING IN AN OVERPRESSURE |  |  | YES |  |  | NORMAL OPERATING CONDITIONS | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | W. JEFF KOSKIE | PIPELINE SAFETY AND COMPLIANCE MANAGER | wkoskie@semprautilities.com | 213 305-8660 | 213 244-8223 |  |  |  | W. JEFF KOSKIE | PIPELINE SAFETY AND COMPLIANCE MANAGER | 213 305-8660 | wkoskie@semprautilities.com | ORIGINAL REPORT: AT THE PLAYA DEL REY UNDERGROUND STORAGE FACILITY, AN UNINTENTIONAL AND MOMENTARY OPENING OF A BLOCK VALVE ALLOWED A RELEASE OF HIGH-PRESSURE GAS INTO LOWER-RATED PRESSURE PIPING. THIS RESULTED IN UNPLANNED RELEASE OF GAS THROUGH THE RELIEVING VALVE SYSTEM AND AN OVER PRESSURE OF CERTAIN STATION PIPING. THE GAS EMITTED THROUGH THE RELIEF SYSTEM IGNITED. THE PROBABLE SOURCE OF IGNITION WAS A STATIC CHARGE. THE SYSTEM WAS ISOLATED AND FIRE EXTINGUISHED. THE SOOT FROM THE BURNED GAS CAUSED MIST DAMAGE TO NEIGHBORING HOMES, LANDSCAPING AND VEHICLES. FACILITY IS CURRENTLY SHUTDOWN DURING ON-GOING INVESTIGATION AND INSPECTION OF PIPELINE FACILITIES. THE INCIDENT IS STILL UNDER INVESTIGATION. A SUBSEQUENT REPORT WILL BE FILED WHEN INVESTIGATION IS COMPLETE AND FACILITIES ARE BACK IN SERVICE. NO INJURIES OR EVACUATIONS OCCURRED AS A RESULT OF THIS INCIDENT. SUPPLEMENTAL/FINAL REPORT - INVESTIGATION OF THE INCIDENT IS COMPLETE AND DETERMINED PROBABLE CAUSE OF THE EVENT WAS THE UNINTENTIONAL OPERATION OF A BLOCK VALVE. SINCE THE INCIDENT, ADDITIONAL MEASURES HAVE BEEN IMPLEMENTED TO AVOID A SIMILAR EVENT IN THE FUTURE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130012 | 15845 | 2013-02-07 12:47 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2013-01-04 04:30 | 2013 |  |  | 29.293 | -95.9384 | 1035242 | 2013-01-09 14:30 |  | NATURAL GAS |  | 6 | 6 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-01-04 04:40 | 2013-01-06 16:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-01-04 04:30 | 2013-01-04 04:30 | ONSHORE | TX | 77420-2368 | BOLING | WHARTON |  |  | WILSON STORAGE |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1982 |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 550 |  | NO | NO | NO |  | 0 | 0 | 100 | 112.755302435192 | 100 | 78.0737704918033 | 70000 | 78928.7117046348 | 0 | 0 | 0 | 0 |  |  | 70200 | 36363.0616331629 | 79119.5407775618 | [8 empty] | 1000 |  | 1102 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS MINOR ORIGINATING FROM CRACK. THIS WAS A MANNED FACILITY AND LEAK WAS FOUND BY ONSITE PERSONNEL SHORTLY AFTER IT HAPPENED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [8 empty] | YES | [11 empty] | YES | [177 empty] | MATTHEW STRATMANN | SR. PIPELINE COMPLIANCE SPECIALIST | mstratmann@eprod.com | 713-381-8209 |  |  |  |  | MATTHEW STRATMANN | SR. PIPELINE COMPLIANCE SPECIALIST | 713-381-8209 | mstratmann@eprod.com | AT 04:30AM ON JANUARY 4, 2013 FIELD OPERATIONS FOUND A CRACK ON THE STATION BLOW DOWN LINE AT THE WILSON STORAGE FACILITY. THE SECTION OF THE PIPELINE THAT CONTAINED THE CRACK WAS ISOLATED AND REPAIRS WERE MADE. THE CRACK OCCURRED ON A 24" X 8" SADDLE THAT SUPPORTED THE STATION VENT VALVE AND ACCUATOR. ENGINEERING ANALYZED THE AREA AND CONCLUDED THAT THE CRACK WAS CAUSED BY HARMONIC VIBRATION. TO RESOLVE THE VIBRATION ISSUE, THE SADDLE WAS REMOVED AND A 24" X 12" SPLIT TEE WAS INSTALLED TO SUPPORT THE BLOW LINE, VALVE, AND ACCUATOR. THE BLOWDOWN STACK WAS AS ALSO SHORTENED TO MITIGATE VIBRATION. THE INCIDENT WAS REPORTED ON JANUARY 9, 2013 AFTER IT WAS DETERMINED THAT THE REPAIR COSTS EXCEEDED THE 50 THOUSAND DOLLAR THRESHOLD.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130013 | 15892 | 2013-02-08 18:11 | SUPPLEMENTAL FINAL | 15931 | PUBLIC SERVICE CO OF COLORADO | 1800 LARIMER STREET | DENVER | CO | 80202 | 2013-01-10 08:30 | 2013 |  |  | 39.568 | -105.0542 | 1035317 | 2013-01-10 10:13 |  | NATURAL GAS |  | 676 | 490 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-01-10 10:55 | 2013-01-10 23:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 2500 | 2013-01-10 08:30 | 2013-01-10 08:30 | ONSHORE | CO | 80128 | LITTLETON | JEFFERSON |  |  | 24 INCH SPMS BLAKELAND |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 84 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 |  | 0.25 | 35000 | API 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1969 | 1968 | CARBON STEEL |  | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 1 LOCATION | NO |  | 345 |  | NO | NO | NO |  | 0 | 0 | 1122 | 1265.11449332286 | 1547 | 1207.8012295082 | 38198 | 43070.2704241948 | 12727 | 14350.3673409269 | 137535 | 155078.005204242 | TO ENSURE THAT INTERNAL INSPECTION TOOLS CAN BE UTILIZED IN THE FUTURE. |  | 191129 | 99375.3876009298 | 214971.558692195 | [8 empty] | 340 |  | 350 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 9834 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURES AND FLOWS REMAINED WITHIN EXPECTED VALUES. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | NO | YES | INTERSTATE HIGHWAY | [9 empty] | DEVELOPER | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 234801245 |  | CONTRACT LOCATOR | NO | NO | YES | 14 | LOCATING PRACTICES NOT SUFFICIENT |  | FACILITY WAS NOT LOCATED OR MARKED | [264 empty] | RYAN CHANCE HUTSON | INVESTIGATOR | ryan.c.hutson@xcelenergy.com | 303-294-2667 | 303-294-2311 |  |  |  | JOHN KARTUS | CLAIMS MANAGER MANAGING INVESTIGATOR | 303-294-2665 | john.j.kartus@xcelenergy.com | PINNACLE CONSTRUCTION WAS INSTALLING TELECOMMUNICATION FACILITIES WHEN THEY BORED INTO A 24 INCH HP GAS LINE. THE CONTRACTOR REQUESTED LOCATES; HOWEVER, XCEL ENERGY'S LOCATE CONTRACTOR, SAFE SITE, DID NOT MARK THE GAS FACILITIES WHERE THE DAMAGE OCCURRED. PLEASE NOTE THAT THE RESPONSE TO PART A QUESTION NUMBER 18 WAS DETERMINED DUE TO A REVERSE 911 CALL THAT WAS MADE TO APPROXIMATELY 2,500 PEOPLE; HOWEVER, THE ACTUAL NUMBER OF INDIVIDUALS EVACUATED IS UNKNOWN. PLEASE NOTE THAT THE RESPONSE TO PART C QUESTION NUMBER 3E WAS SELECTED BASED ON THE LIMITED INFORMATION THAT WE HAVE REGARDING THE SEAM TYPE. PLEASE NOTE PART D QUESTION 7B IS THE COST TO MAKE REPAIRS THAT WERE NECESSARY TO PLACE THE PIPELINE LINE BACK IN SERVICE. ADDITIONAL WORK, BOTH ENGINEERING AND FIELD, WILL NEED TO BE PERFORMED TO ENSURE THAT INTERNAL INSPECTION TOOLS CAN BE UTILIZED IN THE FUTURE. THIS WILL RESULT IN ADDITIONAL COSTS TO THE OPERATOR. A SUPPLEMENTAL FINAL REPORT WILL BE SUBMITTED WHEN THE TOTAL COSTS ASSOCIATED WITH THE DAMAGE AND REPAIRS HAVE BEEN COMPILED. PLEASE NOTE PART D QUESTION 7D IS THE ESTIMATED COST NECESSARY TO SAFELY RESTORE THE PIPELINE TO ITS PREDEFINED LEVEL OF SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130014 | 15735 | 2013-02-12 11:34 | ORIGINAL FINAL | 12874 | QUESTAR PIPELINE COMPANY | 333 SOUTH STATE STREET P.O. BOX 45360 | SALT LAKE CITY | UT | 84145-0360 | 2013-01-14 05:00 | 2013 |  |  | 39.9489 | -109.7758 | 1035660 | 2013-01-14 10:54 |  | NATURAL GAS |  | 54400 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | ISOLATION VALVE TO RELIEF VALVE WAS ISOLATED AND RELIEF LINE WAS REPAIRED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-01-14 09:00 | 2013-01-14 09:50 | ONSHORE | UT | 84052-0000 | MYTON | DUCHESNE |  |  | MAIN LINE 40 / GREEN RIVER GATE |  | YES | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2012 |  | CARBON STEEL |  | OTHER | [8 empty] | EXTREME AMBIENT TEMPERATURE CAUSED A FREEZE IN THE SENSING LINE OF THE PILOT-OPERATED RELIEF VALVE, WHICH RESULTED IN THE RELEASE OF GAS APPROXIMATELY 101 PSIG BEFORE ITS SET-POINT. RELIEF VALVE DID NOT RE-SEAT. | CLASS 1 LOCATION | NO |  | 131 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 175730 | 137199.036885246 | 1300 | 1465.8189316575 | 300 | 338.265907305578 | 0 | 0 |  |  | 177330 | 143068.593856644 | 139003.121724209 | [8 empty] | 726 |  | 827 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL |  | 1 | NO | [5 empty] | YES | THE INCIDENT OCCURRED AT A TEE OFF THE MAIN LINE THAT ACCOMODATES A PRESSURE RELIEF VALVE, THUS THE MAIN LINE IS CAPABLE OF ILI INSPECTION, BUT THE RELIEF LINE IS A BRANCH FROM THE MAIN LINE | YES |  |  |  |  | YES | RELIEF LINE IS A BRANCH FROM MAIN LINE | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS DUE TO PHYSICAL FAILURE IN THE RELIEF VALVE SENSING LINE TUBING, NOT OPERATOR ERROR. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | FREEZE IN SENSING LINE TUBING CAUSED RELIEF VALVE TO OPEN BEFORE SET-POINT | [161 empty] | CHAD WILDING | SUPERVISOR OF PIPELINE COMPLIANCE | chad.wilding@questar.com | 801-324-3814 | 801-324-5622 |  |  |  | LARRY CONTI | VICE PRESIDENT OF GAS CONTROL AND OPERATIONS | 801-324-5061 | larry.conti@questar.com | FREEZE IN SENSING LINE TUBING TO PILOT-OPERATED RELIEF VALVE CAUSED THE 6"X8" RELIEF VALVE TO OPEN AND VENT GAS AT APPROXIMATELY 726 PSIG, WHICH IS WELL-BELOW ITS SET-POINT OF 827 PSIG. DURING THE VENTING PROCESS THE TUBING TO THE SENSING LINE FAILED, WHICH PREVENTED THE RELIEF VALVE FROM RE-SEATING AND RESULTED IN VENTING GAS FOR APPROXIMATELY 4 HOURS AND 55 MINUTES. FIELD OPERATIONS ARRIVED ON-SITE AND ISOLATED THE RELIEF VALVE BY CLOSING THE 6" ISOLATION VALVE INSTALLED IMMEDIATELY UPSTREAM OF THE RELIEF VALVE. THE PILOT VALVE AND SENSING LINE TUBING WERE REPAIRED AND THE RELIEF VALVE WAS PLACED BACK INTO SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130015 | 15971 | 2013-02-13 12:46 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2013-01-15 12:45 | 2013 |  |  | 29.4858 | -93.7932 | 1035785 | 2013-01-15 14:45 |  | NATURAL GAS |  | 1000 | 93418.8 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-01-15 12:45 | 2013-04-30 16:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-01-15 12:45 | 2013-01-15 13:00 | OFFSHORE | [28 empty] | 40 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | HIGH ISLAND | 39 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | TAP FITTING(STOPPLE, THREAD-O-RING, WELD-O-LET, ETC.) | [20 empty] | CRACKED WELD ON SADDLE CONNECTION | [19 empty] | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 628 |  | NO | NO | NO |  | 0 | 0 | 351255 | 396058.637568735 | 3760 | 2935.5737704918 | 962206 | 1084938.28534957 | 107816 | 121568.256873527 | 0 | 0 |  |  | 1425037 | 738663.146766706 | 1605500.75356232 | [8 empty] | 1000 |  | 1440 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 24585 | NO | [5 empty] | YES | SUB SEA TIE-IN | YES |  |  |  |  | YES | SUB SEA TIE-IN | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | NOTIFICATION FROM THIRD PARTY PRODUCER |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURES WERE WITHIN NORMAL OPERATING RANGES; NO ABNORMAL EXCURSIONS. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [8 empty] | YES | WELD DEFECT DURING ORIGINAL CONSTRUCTION. | [12 empty] | YES | [63 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KRISTIN VAN DER LAAN | COMPLIANCE ENGINEER III | kristin_vanderlaan@kindermorgan.com | 303-914-7753 |  |  |  |  | REJI GEORGE | DIRECTOR - COMPLIANCE CODES AND STANDARDS | 713-420-5433 | reji_george@kindermorgan.com | THIRD PARTY PRODUCER NOTICED SMALL PRESSURE REDUCTION ISSUES ON PLATFORM. NOTIFIED TGP. TGP SCADA DID NOT SHOW ANY PRESSURES OUTSIDE NORMAL PARAMETERS. PRODUCER SUBSEQUENTLY IDENTIFIED BUBBLES ON SURFACE AND PROVIDED COORDINATES TO TGP. BUBBLES LOCATED BY AIRCRAFT PILOT WITH GPS COORDINATES NEAR THE 821E-100 LINE IN HIGH ISLAND BLOCK 39. INITIAL ACTIONS / REPORT: ISOLATED LINE 821E-100 LINE BY SHUTTING IN TWO FLOWING PRODUCERS AND MAINLINE VALVE AT SABINE PASS 18 CG. SUBSEQUENT INVESTIGATION FOUND A CRACK ON 6" SADDLE AT SUB-SEA TIE-IN. REPAIR PART HAS NINE WEEK LEAD TIME. PROVIDED A NOTICE TO MARINERS WITH THE PORT ARTHUR COAST GUARD ON JANUARY 20TH. GAS BLANKET WILL BE MAINTAINED ON PIPELINE TO PREVENT OIL IN LINE FROM ESCAPING. AS A RESULT GAS WILL CONTINUE TO BE RELEASED UNTIL REPAIR CAN BE MADE. FINAL GAS VOLUME RELEASED WILL BE CALCULATED AT THAT TIME. UPDATE / FINAL REPORT: THE REPAIRS WERE BEEN COMPLETED ON APRIL 25, 2013 AND THE PIPELINE WAS PUT BACK INTO SERVICE ON APRIL 30, 2013.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130016 | 15815 | 2013-02-20 12:35 | SUPPLEMENTAL FINAL | 22655 | WBI ENERGY TRANSMISSION, INC. | 1250 WEST CENTURY AVENUE | BISMARCK | ND | 58503 | 2013-01-26 09:50 | 2013 |  |  | 47.85 | -103.5708 | 1036670 | 2013-01-26 13:51 |  | NATURAL GAS |  | 751 | 104 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-01-26 11:54 | 2013-01-26 19:05 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-01-26 09:55 | 2013-01-26 11:06 | ONSHORE | ND | 58831 | ALEXANDER | MCKENZIE COUNTY | SURVEY STATION NO. | 792+89 | CABIN CREEK - WILLISTON | WATFORD CITY LATERAL | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 24 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 4 |  | 0.237 | 35000 | UNKNOWN | SEAMLESS |  | UNKNOWN | COAL TAR | [28 empty] | 1962 | 1962 | CARBON STEEL |  | MECHANICAL PUNCTURE | 4 | 4 | [7 empty] | CLASS 1 LOCATION | NO |  | 89 |  | NO | NO | NO |  | 0 | 0 | 413 | 465.679399057345 | 2980 | 2326.59836065574 | 15350 | 17307.938923802 | 1250 | 1409.44128043991 | 175000 | 197321.779261587 | THE LDC WAS INVOLVED WITH RESTORING SERVICE TO CUSTOMERS THAT LOST GAS SERVICE. |  | 194993 | 101793.524079881 | 218831.437225542 | [8 empty] | 373 |  | 752 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 55652 | NO |  |  | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | GRADER/SCRAPER | GRADING | YES | 13004270 | NTMS | UTILITY OWNER | YES | YES | YES | 7 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO MAINTAIN CLEARANCE | [263 empty] | KENT KAHL | DOT COMPLIANCE SUPERVISOR | kent.kahl@wbienergy.com | 406-359-7222 | 406-359-7244 |  |  |  | KENT KAHL | DOT COMPLIANCE SUPERVISOR | 406-359-7222 | kent.kahl@wbienergy.com | A DOZER THAT WAS RIPPING FROZEN GROUND PUNCTURED A 4" NATURAL GAS LINE. THE LINE RELEASED NATURAL GAS UNTIL IT WAS SHUT IN AND ISOLATED. THE LINE WAS PROPERLY MARKED BY THE OPERATOR, BUT THE CONTRACTOR FAILED TO MAINTAIN DISTANCE FROM THE PIPELINE WHILE EXCAVATING. THE UNINTENTIONAL RELEASE OF GAS TOTALED 751 MCF WHICH DOES NOT MEET THE REPORTING THRESHOLD OF 3 MILLION CUBIC FEET OF GAS, BUT WBI ENERGY DEEMED IT SIGNIFICANT TO REPORT THE INCIDENT. NATURAL GAS SERVICE WAS LOST TO THE TOWNS OF ARNEGARD, ND AND WATFORD CITY, ND. SUPPLEMENTAL REPORT 3/7/13 REVISED DATA IN QUESTION C.3.A. FROM 4.5 TO 4, REVISED DATA G3.6 FROM NO TO YES, AND MARKED ONE-CALL SYSTEM IN G3.6.A.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130017 | 15816 | 2013-02-20 13:02 | SUPPLEMENTAL FINAL | 22655 | WBI ENERGY TRANSMISSION, INC. | 1250 WEST CENTURY AVENUE | BISMARCK | ND | 58503 | 2013-01-28 16:35 | 2013 |  |  | 46.8475 | -102.4219 | 1036884 | 2013-01-28 19:50 |  | NATURAL GAS |  | 4187 | 5 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-01-28 20:47 | 2013-01-29 00:05 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-01-28 16:40 | 2013-01-28 20:25 | ONSHORE | ND | 58656 | TAYLOR | STARK | SURVEY STATION NO. | 0+65 | CABIN CREEK - BISMARCK | TAYLOR LATERAL | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 24 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 2 |  | 0.154 | 24000 | UNKNOWN | SEAMLESS |  | UNKNOWN | NONE | [28 empty] | 1930 | 1930 | CARBON STEEL |  | MECHANICAL PUNCTURE | 2 | 2.5 | [7 empty] | CLASS 1 LOCATION | NO |  | 49 |  | NO | NO | NO |  | 0 | 0 | 20 | 22.5510604870385 | 15351 | 11985.1045081967 | 9000 | 10147.9772191673 | 250 | 281.888256087981 | 25000 | 28188.8256087981 | THE LDC WAS INVOLVED WITH RESTORING NATURAL GAS SERVICE TO CUSTOMERS. |  | 49621 | 30162.8518135166 | 50626.3466527372 | [8 empty] | 696 |  | 832 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 19964 | NO | [5 empty] | YES | THERE IS NO COMMERCIALLY AVAILABLE INSPECTION TOOL TO ACCOMODATE 2" PIPE. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 1 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | TRENCHER | ELECTRIC | YES | 13004502 | NTMS | UTILITY OWNER | NO | NO | YES | 8 | LOCATING PRACTICES NOT SUFFICIENT |  | FACILITY WAS NOT LOCATED OR MARKED | [264 empty] | KENT KAHL | DOT COMPLIANCE SUPERVISOR | kent.kahl@wbienergy.com | 406-359-7222 | 406-359-7244 |  |  |  | KENT KAHL | DOT COMPLIANCE SUPERVISOR | 406-359-7222 | kent.kahl@wbienergy.com | A TRENCHER PUNCTURED A 2 INCH NATURAL GAS LINE CAUSING GAS TO BE RELEASED TO ATMOSPHERE. THE DAMAGE OCCURRED ON A LATERAL PIPELINE TRANSVERSE OF A MAIN TRANSMISSION LINE. THE MAIN TRANSMISSION LINE WAS MARKED, BUT THE OPERATOR FAILED TO MARK THE LATERAL LINE THAT WAS IN PROXIMITY OF THE EXCAVATION. THE GAS LOST DURING THIS INCIDENT WAS 4,187 MCF WHICH EXCEEDED THE REPORTING THRESHOLD. NATURAL GAS SERVICE WAS LOST TO THE TOWN OF TAYLOR, ND. SUPPLEMENTAL REPORT 3/7/13 REVISED DATA IN QUESTION C.3.A. FROM 2.375 TO 2.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130018 | 16192 | 2013-02-22 14:53 | SUPPLEMENTAL FINAL | 2620 | COLUMBIA GULF TRANSMISSION CO | 700 LOUISIANA ST. SUITE 700 | HOUSTON | TX | 77002 | 2013-01-26 14:30 | 2013 |  |  | 29.5989 | -92.3814 | 1036684 | 2013-01-26 17:14 |  | NATURAL GAS |  | 9.87 |  | 155 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THIS INCIDENT TOOK PLACE ON AN ABANDONED PIPELINE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-01-26 14:30 | 2013-01-26 14:30 | ONSHORE | LA | 70548 | PECAN ISLAND | VERMILLION | MILEPOST | 2.1 | BLUEWATER LINE 200 | BLUEWATER FIELD LINE 200, 26-INCH | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | MARSHLAND | 204 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 36 |  | 0.562 | 60000 | API-5LX-60 | DSAW |  | UNKNOWN | OTHER | SOMASTIC AND 3.75-IN CONCRETE COAT. WELDED AREA COATED WITH COLD TAR AND WAX. | [27 empty] | 1979 | 1979 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 1 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 32 | 24.983606557377 | 316131 | 356454.465141398 | 909384 | 1025378.67949725 | 0 | 0 | THESE COSTS WERE COMPILED AT THE TIME THIS REPORT WAS UPDATED. |  | 1225547 | 634323.777228504 | 1381858.12824521 | [8 empty] | 1 |  | 1 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [7 empty] | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | OTHER | ANOTHER OPERATOR WHO OWNS AND OPERATES ACTIVE PIPELINES N THE SAME AREA. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS IS AN ABANDONED PIPELINE AND IS NOT CONNECTED TO A REMOTE MONITORING SYSTEM. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED | YES | [16 empty] | OTHER | CRACK ON S GIRTH WELD |  |  |  |  | YES | [63 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | GEORGE HAMATY | ENGINEER | ghamaty@nisource.com | (304) 357-3728 | (304) 357-3522 |  |  |  | PERRY M. HOFFMAN | MANAGER | (304) 357-2548 | mikehoffman@nisource.com | ON JANUARY 24, 2013, COLUMBIA GULF TRANSMISSION COMPANY (COLUMBIA) WAS ADVISED THAT SHEEN APPEARED ON THE WATER IN THE AREA OF ITS ABANDONED LINE BW-200. BECAUSE THERE ARE MULTIPLE FOREIGN PIPELINES IN THAT AREA, IT WAS NOT IMMEDIATELY CLEAR TO WHICH LINE THE SHEEN RELATED. NEVERTHELESS, OUT OF CAUTION, COLUMBIA'S ENVIRONMENTAL PERSONNEL REPORTED THE SHEEN TO THE NRC REPORT NO. 1036464 AND CERTAIN LOUISIANA AGENCIES AS APPROPRIATE. COLUMBIA CONTINUED ITS INVESTIGATION TO DETERMINE IF THERE WAS IN FACT A LEAK AND IF SO WHETHER SUCH LEAK WAS IN A COLUMBIA GULF OWNED PIPELINE. ATTENTION FOCUSED ON A SMALL AMOUNT OF BUBBLES REACHING THE SURFACE. FOREIGN PIPELINES WERE BLOWN DOWN BY THEIR RESPECTIVE OPERATORS. FEW BUBBLES REMAINED, ENABLING COLUMBIA TO CONCLUDE THAT ITS ABANDONED LINE BW-200 COULD BE THE SOURCE OF THE BUBBLES. NITROGEN WAS INJECTED INTO THE PIPELINE IN ORDER TO LOCATE PRECISELY IF THERE WAS A LEAK AND WHERE THE LEAK WAS LOCATED. DIVERS WERE MOBILIZED TO EXCAVATE THE PIPELINE, LOCATE THE LEAK ON THE PIPELINE SURFACE AND IMPLEMENT REPAIRS. THIS REPAIR CONSISTED OF INSTALLING A 36-IN PRE-TESTED BOLT-ON CLAMP WHERE COLUMBIA TREATED THIS PIPELINE AS AN ACTIVE LINE RATHER THAN ABANDONED. FOLLOWING THE REPAIR, NO FURTHER BUBBLES WERE PRESENT FROM THIS LOCATION. WHILE TESTING THE REPAIR TO ENSURE ITS EFFECTIVENESS, SOME BUBBLING WAS NOTICED APPROXIMATELY 80 FEET SOUTH OF THE REPAIR LOCATION NEAR BUT NOT NECESSARILY ON THE SAME PIPELINE. THERE WAS NO EVIDENCE OF ANY SUBSTANCE BEING RELEASED WITH THOSE BUBBLES. THIS SECOND AREA WAS EXCAVATED AND NITROGEN INJECTED INTO THE LINE. THE PRESSURE WAS HELD FOR 2 HOURS WITH NO EVIDENCE OF BUBBLING AND NO PRESSURE DROP. THE DIVER DID NOT OBSERVE ANY EVIDENCE OF A LEAK. BOTH EXCAVATION AREAS WERE BACKFILLED. COLUMBIA WILL RE-INSPECT THE AREA AFTER ALLOWING TIME FOR NORMAL SETTLING IN THE EXCAVATED AREAS (AT BOTH SITES) TO ENSURE THERE IS ADEQUATE COVER OVER THE PIPELINE AS WELL AS TO ENSURE THE EFFECTIVENESS OF THE PREVIOUS SHEEN REMOVAL EFFORTS. ORIGINAL PLANS WERE TO PIG THE LINE IN 2013. FOLLOWING ANALYSIS OF THE SITUATION, A DECISION WAS MADE NOT TO PIG AT THAT TIME. THE PIPELINE IS BEING MONITORED TO ENSURE THE CONDITIONS WHICH LED TO THE EMERGENCY RESPONSE ARE NOT REPEATED. IF CONCERNS ARISE BASED ON COLUMBIA GULF INSPECTIONS, PIPELINE OPERATIONS PERSONNEL WILL TAKE NECESSARY ACTIONS TO ADDRESS THE SITUATION, WHICH MAY INCLUDE PIGGING.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130019 | 16448 | 2013-02-22 15:49 | SUPPLEMENTAL FINAL | 602 | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA STREET | HOUSTON | TX | 77002 | 2013-02-10 18:23 | 2013 |  |  | 32.9587 | -94.8391 | 1038101 | 2013-02-10 20:08 |  | NATURAL GAS |  | 6429 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-02-10 21:01 | 2013-02-11 19:25 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-02-10 19:41 | 2013-02-10 19:41 | ONSHORE | TX | 78010 | CENTER POINT | CAMP | SURVEY STATION NO. | 2660+55 | AM-47 |  | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | OTHER | EXPOSED AT CREEK CROSSING |  |  | YES | [6 empty] | YES | UNCASED | UNKNOWN | 1 | SHORELINE/BANK/MARSH CROSSING | [11 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12.75 |  | 0.312 | 35500 | GRADE B | LAP WELDED |  | UNKNOWN | COAL TAR | [28 empty] | 1949 | 1949 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 108 | 8 |  | CLASS 1 LOCATION | NO |  | 185 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 24444 | 19084.3524590164 | 30000 | 33826.5907305577 | 990 | 1116.27749410841 | 12000 | 13530.6362922231 | LABORATORY TESTING |  | 67434 | 42036.232389605 | 67557.8569759057 | [8 empty] | 370 |  | 500 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 33792 | NO | YES | [6 empty] | YES |  |  | YES |  | YES | DRESSER COUPLED | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | MANAGER OF SYSTEM CONTROL EVALUATED THE CONTROLLER'S CONDITION. THERE WAS NO EVIDENCE OR APPEARANCE OF PHYSICAL IMPAIRMENT. HE REVIEWED SCADA HISTORY, LOOKING AT PRESSURES AT THE TIME OF THE RUPTURE. IT WAS DETERMINED; THE CONTROLLER'S ACTIONS DID NOT CONTRIBUTE TO THE RUPTURE. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [9 empty] | YES |  |  | NO | [11 empty] | NO | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | JIMMY CROSS | COMPLIANCE COORDINATOR | jimmy.cross@centerpointenergy.com | 3184293664 | 3184293997 |  |  |  | JOHNNY CAVITT | DOT COMPLIANCE MANAGER | 3184293606 | johnny.cavitt@centerpointenergy.com | A FAILURE OCCURRED AT SURVEY STATION 2660+55 IN A RURAL (CLASS 1) PORTION OF CAMP COUNTY NEAR THE COMMUNITY OF CENTER POINT ON FM 2057. THE PIPE SEGMENT WAS TRANSPORTED TO LABORATORY FACILITIES FOR FAILURE ANALYSIS. LABORATORY TESTING RESULTS - STRESS ENGINEERING SERVICES, INC.: STRESS ENGINEERING EXAMINED THE PIPE SAMPLE CONTAINING THE RUPTURE. THE OUTSIDE SURFACE OF THE PIPE WAS COVERED WITH REDDISH-BROWN OXIDE (RUST) DEPOSITS. THERE WAS ALSO EXTENSIVE WALL LOSS OBSERVED DUE TO GENERAL CORROSION AND PITTING ON THE OUTSIDE OF THE SAMPLE. THE INSIDE SURFACE WAS ALSO COVERED WITH LIGHT RUST, BUT NO MEASURABLE LOSS WAS IDENTIFIED. EXAMINATION OF THE CORROSION MORPHOLOGY INDICATED THAT AQUEOUS CORROSION CAUSED THE DAMAGE OBSERVED. THE SUBJECT FAILURE OCCURRED AFTER CUMULATIVE WALL-THINNING RESULTED IN A DUCTILE OVERLOAD. STRESS DETERMINED THAT THE PIPE WAS LAP-WELDED. BASED ON THE MECHANICAL AND CHEMICAL ANALYSES PERFORMED, THE SAMPLE MATERIAL TESTED MEETS APPLICABLE REQUIREMENTS OF API 5L (1949) FOR LAP-WELD PIPE. IT IS BELIEVED THAT THE CHEMICAL AND MECHANICAL PROPERTIES OF THIS PIPE DID NOT CONTRIBUTE TO ITS FAILURE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130020 | 15743 | 2013-02-25 11:57 | ORIGINAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2013-01-28 04:30 | 2013 |  |  | 38.7881 | -94.2853 | 1036777 | 2013-01-28 08:00 |  | NATURAL GAS |  | 3501 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | GAS WAS DIVERTED TO SECONDARY REGULATOR WHILE REPAIRS WERE MADE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-01-28 05:15 | 2013-01-28 05:44 | ONSHORE | MO | 64080 | PLEASANT HILL | CASS | SURVEY STATION NO. | 110/0+26 | XT-015 | MISSOURI PUBLIC SERVICE POWER | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1995 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE ACTIVATION BECAUSE OF REGULATOR FAILURE. | CLASS 2 LOCATION | NO |  | 138 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 10940 | 8541.27049180328 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 10940 | 8855.12295081967 | 8541.27049180328 | [8 empty] | 490 |  | 535 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [5 empty] | YES | DURING THE INVESTIGATION IT WAS DISCOVERED THAT THE ALARM WAS INHIBITED DUE TO A NO FLOW SITUATION. STATUS OF THE ALARMS BEING ANALYZED FOR SIMILAR SITUATIONS ON THE SYSTEM TO PREVENT FUTURE ISSUES. | YES | 2 | 0 | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [25 empty] | YES | FOUND A CUT IN REGULATOR BOOT AND HARD DEBRIS IN THE MAIN BODY. | [161 empty] | DAVID COOMES | COMPLIANCE ANALYST | david.coomes@sscgp.com | 270.852.4391 |  |  |  |  | DAVID SINCLAIR | PIPELINE COMPLIANCE MANAGER | 270.852.4424 | davidl.sinclair@sscgp.com | AT 5:15 AM ON JANUARY 28, 2013 SSCGP GAS CONTROL WAS CALLED BY A HOMEOWNER NEAR THE PLEASANT HILL SETTING, STATING THAT THE RELIEF WAS BLOWING. GAS CONTROL IMMEDIATELY CALLED JASON JEDLICKA, OPERATIONS, WHO IN TURN CALLED LES JOHNSON, MEASUREMENT TECHNICIAN. LES ARRIVED AT THE PLEASANT HILL SETTING AT APPROXIMATELY 5:44 AM AND WORKED TO STOP THE RELIEF FROM CYCLING GAS. ONCE THE GAS RELEASE WAS MANAGED LES SWITCHED THE REGULATOR TO THE SECONDARY LINE AND INVESTIGATED THE REGULATOR. THE REGULATOR WAS FOUND TO HAVE A CUT IN THE BOOT AND HARD DEBRIS IN THE MAIN BODY. THE REGULATOR BOOT WAS REPLACED AND THE REGULATOR PILOT WAS OVERHAULED. AFTER THE MAIN REGULATOR WAS OVERHAULED THE GAS WAS RETURNED TO NORMAL AND THE SECOND REGULATOR WAS CHECKED AND OVERHAULED AS A PRECAUTIONARY ACTION. THE SECONDARY RUN PASSED LOCKUP AND NO DEBRIS WERE FOUND. THE BOOT WAS REPLACED AS AN EXTRA MEASURE. WHEN THE LOSS OF GAS WAS DISCOVERED BY GAS CONTROL TO BE ABOVE THE THREE MILLION THRESHOLD, THE INCIDENT WAS REPORTED TO NRC.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130021 | 16104 | 2013-03-01 09:32 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 4720 PIEDMONT ROW DR. | CHARLOTTE | NC | 28210 | 2013-02-03 02:50 | 2013 |  |  | 34.4334 | -78.4753 | 1037392 | 2013-02-03 07:16 |  | NATURAL GAS |  | 25895 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | A SECTION OF PIPE WAS ISLOTATED. NO FIRM CUSTOMERS LOST SERVICE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-02-03 02:50 | 2013-02-03 03:45 | ONSHORE | NC | 28434 | COUNCIL | BLADEN | SURVEY STATION NO. | 2481+17 | LINE 2 | 53029353 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | YES | [6 empty] | YES | UNCASED |  |  | SHORELINE/BANK/MARSH CROSSING | [11 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12.75 |  | 0.219 | 42000 | API5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | MANNESMANN | COAL TAR | [28 empty] | 1959 | 1959 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 36 | 12 |  | CLASS 1 LOCATION | NO |  | 249 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 80015 | 62470.7274590164 | 525175 | 592162.659564022 | 1000 | 1127.55302435192 | 0 | 0 |  |  | 606190 | 337102.10238175 | 655760.94004739 | [8 empty] | 631 |  | 704 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 6336 | NO |  |  |  | YES |  | YES | LACK OF LAUNCHERS AND RECEIVERS | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SYSTEM AND LINE WERE OPERATING NORMALLY UNTIL THE DETECTION OF PRESSURE ISSUES. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [64 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | [10 empty] | YES |  |  |  |  | YES | [6 empty] | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO |  |  | UNKNOWN/OTHER | NO | NO |  |  | PREVIOUS DAMAGE | [121 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | FARRIS BERRY | MANAGER - OPERATIONS PERFORMANCE | farris.berry@piedmontng.com | 704-731-4618 |  |  |  |  | NEIL MOSER | DIRECTOR - OPERATIONS COMPLIANCE AND PERFORMANCE | 704-731-4351 | neil.moser@piedmontng.com | AT APPROXIMATELY 2:50 A.M. LOCAL TIME ON SUNDAY FEBURARY 3, 2013, A PIEDMONT NATURAL GAS 12" TRANSMISSION LINE, DENOTED AS LINE 2, RUPTURED. THIS EVENT WAS NEAR THE COMMUNITY OF COUNCIL IN RURAL SOUTHEASTERN NC. PRESSURES BEFORE THE EVENT WERE WITHIN MAOP LIMITS. NO INJURIES OR SIGNIFICANT PROPERTY DAMAGE WAS NOTED FROM THE EVENT. THE FAILURE ANALYSIS PERFORMED BY A THIRD PARTY INVESTIGATOR INDICATES THAT THE RUPTURE "INITIATED AT A GOUGE CONTAINING A RE-ROUNDING CRACK THAT WAS LOCATED ALONG THE TOP OF THE PIPELINE. THE CAUSE OF THE GOUGE IS UNKNOWN. CRACKS PROPAGATED IN A HELICAL PATTERN AROUND THE PIPE AND AWAY FROM THE GOUGE. THE MATERIAL WAS LIKELY OF LOW TOUGHNESS DUE TO THE INHERENT LOW TOUGHNESS OF THE PIPE STEEL AT SERVICE TEMPERATURE AND THE WORK HARDENING EFFECT OF THE GOUGING PROCESS."
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130022 | 16049 | 2013-03-04 12:23 | SUPPLEMENTAL FINAL | 3 | ACADIAN GAS PIPELINE SYSTEM | 1100 LOUISIANA ST. | HOUSTON | TX | 77002 | 2013-01-25 02:30 | 2013 |  |  | 29.8519 | -91.3975 | 1036987 | 2013-01-29 16:10 |  | NATURAL GAS |  | 39 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-02-06 06:57 | 2013-04-10 08:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-02-06 06:57 | 2013-02-06 09:00 | ONSHORE | LA | 70538 | FRANKLIN | ST. MARY | SURVEY STATION NO. | 1320+96 | CHICO B | 307-100 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 246 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.312 | 52000 | 5LX | LONGITUDINAL ERW - HIGH FREQUENCY |  | YOUNGSTOWN SHEET | COAL TAR | [28 empty] | 1966 | 1966 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 430 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 133 | 103.838114754098 | 2157000 | 2432131.8735271 | 0 | 0 | 0 | 0 |  |  | 2157133 | 1116520.35989434 | 2432235.71164186 | [8 empty] | 790 |  | 970 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 87172 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO INVESTIGATION NEEDED DUE TO THE NATURE OF THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  | YES |  |  | YES |  |  | YES |  |  |  | YES | [5 empty] | NO | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | NATHAN L. GRAY JR. | PIPELINE COMPLIANCE SPECIALIST | ngray@eprod.com | 9858041376 |  |  |  |  | NATHAN L. GRAY JR. | PIPELINE COMPLIANCE SPECIALIST | 9858041376 | ngray@eprod.com | ACADIAN CHICO B PIPELINE LEAK; A FISHERMAN DISCOVERED BUBBLES COMING FROM A PIPELINE ROW IN SOUTH LOUISIANA WHICH ACADIAN SHARES WITH OTHER PIPELINE COMPANIES; THE FISHERMAN USED THE INFORMATION ON THE ROW PIPELINE MARKERS AND NOTIFIED ACADIAN PERSONNEL OF THE SUSPECTED LEAK. ACADIAN PERSONNEL WORKED WITH OTHER PIPELINE ROW PERSONNEL TO DETERMINE WHICH PIPELINE WAS THE SOURCE OF THE LEAK; IT WAS DETERMINED THAT ACADIAN WAS THE RESPONSIBLE PARTY FOR THE LEAKING NATURAL GAS. ACADIAN SHUT IN THE PIPELINE SEGMENT AND COMPRESSED OUT THE REMAINING NATURAL GAS. AFTER EXCAVATING SITE TO A DEPTH OF TWENTY FIVE FEET AND MAKING AREAS SAFE, AN EXISTING REPAIR CLAMP WAS DETERMIND TO BE LEAKING. REPAIR CLAMP WAS REMOVED AND DISGARDED. A NINE FEET WELD SLEEVE WAS WELDED OVER PINHOLE AREA, U-T WELDS, AND MAGNA FLUXED WELDS AFTER 12 HOURS TO INVESTIGATE ANY FOR ANY SIGNS OF UNDER BEAD CRACKING. THE 16.6 MILE SECTION OF PIPELINE WAS LEAK TESTED AND NO ISSUES WERE FOUND, PIPELINE WAS RETURNED TO SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130023 | 16000 | 2013-03-19 08:37 | SUPPLEMENTAL FINAL | 12350 | CENTERPOINT ENERGY RESOURCES CORP., DBA CENTERPOINT ENERGY MINNESOTA GAS | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2011-03-17 08:36 | 2011 |  |  | 44.8961 | -93.2806 | 970337 | 2011-03-17 11:45 |  |  |  | 9627 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-03-17 09:49 | 2011-04-05 18:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 522 | 2011-03-17 08:36 | 2011-03-17 08:41 | ONSHORE | MN | 55419-2421 | MINNEAPOLIS | HENNEPIN | SURVEY STATION NO. | MBLSE #1 | MBLSE #1 | MBLSE #1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 60 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | ELECTROSTOP | 1947 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STEEL API 5L | OTHER | [8 empty] | LEAK AT JOINT. | CLASS 3 LOCATION | YES | METHOD2 | 183 |  | YES | NO | NO |  | 0 | 0 | 0 | 0 | 36803 | 24905.7602131439 | 86400 | 101093.458324842 | 16628 | 19455.8104748319 | 21566 | 25233.5824332586 | HEAVY EQUIPMENT, BARRICADES, SUB-CONTRACTORS, SECURITY AND FENCING |  | 161397 | 92739.1079680639 | 170688.611446076 | [8 empty] | 163 |  | 175 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 6600 | NO | [5 empty] | YES | VALVES, PRESSURE, NO LAUNCHERS OR RECEIVERS AND TEE'S. | YES |  |  |  |  | YES | LOSS OF CUSTOMERS | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA WAS NOT A CONTRIBUTING FACTOR TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [103 empty] | OTHER OUTSIDE FORCE DAMAGE | [9 empty] | THE OPENING WAS THE DIRECT RESULTS OF THE DROPPING AND ATTENDANT DOWNWARD BENDING OF THE GAS MAINPIPE BECAUSE OF THE DETERIATION OF ITS FOUNDATIONAL SUPPORT DUE TO THE LOSS OF THE UNDERLYING SOIL. THE LOSS OF SOIL SUPPORT RESULTED FROM A WASHOUT THAT OCCURRED BENEATH THE 60TH STREET ROADWAY. THERE WAS A CONCLUENCE OF UTILITY SERVICE CONDUITS ALMOST DIRECTLY BENEATH THE GAS MAIN, SUCH AS A STORM SEWER AND A WATER MAIN, BOTH OF WHICH WERE FOUND IN A DETERIOTED AND FRACTURED CONDITION. | [251 empty] | STEVE OLINGER | COMPLIANCE SPECIALIST I | steve.olinger@centerpointenergy.com | 612.321.5453 |  |  |  |  | DEAN HEADLEE | MANAGER COMPLIANCE AND PIPELINE SAFETY | 612.321.5366 | dean.headlee@centerpointenergy.com | ON MARCH 17, 2011 AT 8:36 AM, CENTERPOINT ENERGY RESPONDED TO AN INCIDENT IN SOUTH MINNEAPOLIS IVOLVING A 20" GAS LINE. SOME PROPERTY DAMAGE OCCURRED, BUT THERE WERE NO INJURIES. THE CAUSE OF THE INCIDENT IS UNDER INVESTIGATION. CRANE ENGINEERING, THIRD PARTY VENDOR, HAS COMPLETED THEIR ANALYSIS OF THE INCIDENT THAT OCCURRED ON MARCH 17, 2011 JUST EAST OF NICOLLET AVENUE ON 60TH STREET IN MINNEAPOLIS. CRANE ENGINEERING SUBMITTED THAT THE UTILITIES IN THE SURROUNDING AREA "PROVIDED THE MEANS OF WATER INGRESS AND EGRESS THAT CREATED A WASHOUT CAVERN BENEATH THE ROAD, OF WHICH THE FINAL FAILURE WAS THE COLLAPSE OF THE ROADWAY AND THE GAS MAIN WITH THE ENSUING CONFLAGRATION."
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130024 | 16296 | 2013-03-19 14:34 | SUPPLEMENTAL FINAL | 602 | CENTERPOINT ENERGY GAS TRANSMISSION | 1111 LOUISIANA STREET | HOUSTON | TX | 77002 | 2013-02-28 15:08 | 2013 |  |  | 35.0418 | -92.2846 | 1039726 | 2013-02-28 15:40 |  | NATURAL GAS |  | 2689 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELIEF VALVE BLOWING | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 60 | 2013-02-28 16:10 | 2013-02-28 16:10 | ONSHORE | AR | 72034 | CONWAY | FALKNER | MILEPOST | CONWAY TB #2 | LINE B | CONWAY TB #2 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1984 |  | CARBON STEEL |  | OTHER | [8 empty] | TRASH IN SENSING LINE CAUSED A REGULATOR TO OPEN AND POP THE RELIEF VALVE. | CLASS 3 LOCATION | YES | METHOD2 | 62 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 1713 | 1337.40368852459 | 195 | 219.872839748625 | 300 | 338.265907305578 | 0 | 0 |  |  | 2208 | 1642.74754355917 | 1895.54243557879 | [8 empty] | 445 |  | 500 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [25 empty] | YES | TRASH IN SENSING LINE | [161 empty] | JIMMY CROSS | COMPLIANCE COORDINATOR | jimmy.cross@centerpointenergy.com | 3184293664 | 3184293669 |  |  |  | JOHNNY CAVITT | DOT COMPLIANCE MANAGER | 3184293606 | johnny.cavitt@centerpointenergy.com | THIS EVENT WAS REPORTED BECAUSE IT IS CONSIDERED TO BE SIGNIFICANT BY THE OPERATOR. CEGT BELIEVES THE EVENT IS SIGNIFICANT DUE TO EMERGENCY RESPONDERS EVACUATING 60 PEOPLE FROM A NEAR BY BUILDING (DAYCARE) TO ENSURE THEIR SAFETY. THERE WERE NO DEATHS, INJURIES OR A FIRE. THIS EVENT DID NOT HAVE A REPORTABLE LOSS OF GAS VOLUME AND HAD A MINIMAL REPAIR COST. THE METERING FACILITY INVOLVED FUNCTIONED PROPERLY AND AS DESIGNED. TRASH IN A SENSING LINE CAUSED THE REGULATOR TO OPEN AND BUILD PRESSURE IN THE MEASUREMENT STATION. THE SYSTEM RELIEF OPENED/BLEW AS IT WAS DESIGNED TO DO. CEGT TECHNICIANS ARRIVED AT THE LOCATION, CORRECTED THE ISSUES AND MADE THE AREA SAFE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130025 | 15828 | 2013-03-20 10:42 | ORIGINAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2013-02-24 13:30 | 2013 |  |  | 32.9373 | -83.7115 | 1039294 | 2013-02-24 15:06 |  | NATURAL GAS |  | 17000 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | [7 empty] | NO |  |  |  |  | NO | [7 empty] | 2013-02-24 13:30 | 2013-02-24 13:30 | ONSHORE | GA | 31210 | MACON | BIBB | MILEPOST | 380.6 | OCMULGEE STATION |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | SOLENOID VALVE | 2007 |  | CARBON STEEL |  | OTHER | [8 empty] | EQUIPMENT FAILURE - SOLENOID VALVE | CLASS 2 LOCATION | YES | METHOD2 | 717 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 56100 | 43799.3852459016 | 200 | 225.510604870385 | 0 | 0 | 0 | 0 |  |  | 56300 | 45512.3267935559 | 44024.895850772 | [8 empty] | 1177 |  | 1200 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EQUIPMENT FAILURE - SOLENOID VALVE | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | EQUIPMENT FAILURE - SOLENOID VALVE | YES | [177 empty] | THOMAS N MEEK JR | COORDINATOR - OPS SR II | thomas_meekjr@kindermorgan.com | 505-831-7718 | 505-831-7735 |  |  |  | REJI GEORGE | DIRECTOR - ENGINEERING | 713-420-5433 | reji_george@kindermorgan.com | SOLENOID VALVE FAILED CAUSING ENGINE UNIT VENT TO OPEN.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130026 | 16328 | 2013-03-28 12:02 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2013-03-03 00:37 | 2013 |  |  | 32.2465 | -93.2832 | 1039933 | 2013-03-03 08:35 |  | NATURAL GAS |  | 23799 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE MAIN COMPRESSOR STATION WAS NOT SHUT DOWN; BLOW DOWN VALVE WAS CLOSED. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-03-03 00:37 | 2013-03-03 00:37 | ONSHORE | LA | 71068 | RINGGOLD | BIENVILLE | MILEPOST | 62.85 | HALL SUMMIT COMPRESSOR STATION | INDEX 266/INDEX 326 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1991 |  | CARBON STEEL |  | OTHER | [8 empty] | MECHANICAL FAILURE OF ACTUATOR COMPONENT CAUSED VALVE TO OPEN. | CLASS 1 LOCATION | NO |  | 91 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 82107 | 64104.0307377049 | 180 | 202.959544383346 | 0 | 0 | 0 | 0 |  |  | 82287 | 66552.723212561 | 64306.9902820883 | [8 empty] | 884 |  | 1080 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | VALVE OPENED BECAUSE OF ACTUATOR COMPONENT FAILURE ON VALVE; NOT UNDER THE CONTROL OF THE GAS CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | APPURTENANCE FAILURE | [21 empty] | YES | VALVE ACTUATOR COMPONENT FAILURE | [161 empty] | SHANNON MATTINGLY | PA AND OQ COORDINATOR | shannon.mattingly@bwpmlp.com | 270-688-6357 | 270-688-5871 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 270-688-6361 | jeff.mcmaine@bwpmlp.com | FAILED ELECTRICAL WIRING CONNECTION ON VALVE ACCUATOR CONTROLS CAUSED A COIL TO DROP OUT AND CAUSED STATION VALVE TO OPEN WHICH IS THE FAIL SAFE POSITION. THE NRC REPORT INDICATES THAT THE INCIDENT OCCURRED ON A TEXAS GAS TRANSMISSION ASSET; HOWEVER, IT ACTUALLY OCCURRED ON A GULF SOUTH ASSET. ORIGINAL SUBMISSION WAS THE FINAL SUBMISSION. UPDATED COORDINATES AS REQUESTED BY BASIN BACENTY WITH PHMSA. 2-28-14 CORRECTED GAS VOLUME RELEASED UNINTENTIONALLY FROM 23.79 MCF TO 23,799 MCF. 3-17-14
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130027 | 15875 | 2013-04-04 13:48 | ORIGINAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2013-03-17 15:56 | 2013 |  |  | 32.2845 | -93.305 | 1041315 | 2013-03-17 16:55 |  | NATURAL GAS |  | 8446 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELIEF VALVE WAS ISOLATED FOR REPAIR | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 50 | 2013-03-17 15:56 | 2013-03-17 16:33 | ONSHORE | LA | 71037 | HAUGHTON | BOSSIER | MILEPOST | 17.8521 | SHARON-CARTHAGE 20" | SHARON-CARTHAGE AREA | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2007 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE VENTED DUE TO CONTROL TUBING FAILURE. | CLASS 3 LOCATION | YES | METHOD2 | 127 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 25000 | 19518.4426229508 | 0 | 0 | 600 | 676.531814611155 | 0 | 0 |  |  | 25600 | 20546.2016921433 | 20194.974437562 | [8 empty] | 864 |  | 936 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELIEF VALVE VENTED PREMATURELY DUE TO FAILURE OF CONTROL TUBING TO FACILITY. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [13 empty] | YES | [177 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 270.688.6357 | 270.688.5871 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 270.688.6361 | jeff.mcmaine@bwpmlp.com | RELIEF VALVE VENTED PREMATURELY AS A RESULT OF CONTROL TUBING FAILURE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130030 | 16330 | 2013-04-11 14:51 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2013-03-15 17:15 | 2013 |  |  | 28.551 | -91.6792 | 1041182 | 2013-03-15 18:15 |  | NATURAL GAS |  | 100 | 6011 | 1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-03-15 17:30 | 2013-03-29 19:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-03-15 17:15 | 2013-03-16 22:20 | OFFSHORE | [28 empty] | 146 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EUGENE ISLAND | 241 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 24 |  | 0.438 | 60000 | API-5L | DSAW |  | BETHLEHEM | OTHER | CONCRETE | [28 empty] | 1975 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 588 |  | NO | NO | NO |  | 0 | 0 | 22979 | 25910.0409465829 | 382 | 298.241803278689 | 426159 | 480516.869304792 | 0 | 0 | 0 | 0 |  |  | 449520 | 232772.515627214 | 506725.152054654 | [8 empty] | 863 |  | 1260 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 25872 | NO | YES | [6 empty] | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | BUREAU OF SAFETY AND ENVIRONMENTAL ENFORCEMENT NOTIFICATION |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE PRESSURES WERE WITHIN NORMAL OPERATING RANGE WITH NO ABNORMAL PRESSURE EXCURSIONS. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN | [5 empty] | YES | SUSPECTED TO BE MICROBIOLOGICALLY INDUCED BASED UPON COMPANY'S KNOWLEDGE RELATED TO THE ASPECTS OF INTERNAL CORROSION. |  |  | YES | SEE RESPONSE TO ITEM 7. | YES | [5 empty] | YES | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | MERLIN MOSEMAN | ENGINEER PIPELINE | merlin_moseman@kindermorgan.com | 713-420-4614 | 713-420-7464 |  |  |  | MERLIN MOSEMAN | ENGINEER PIPELINE | 713-420-4614 | merlin_moseman@kindermorgan.com | TENNESSEE GAS PIPELINE (TGP) WAS NOTIFIED BY THE BUREAU OF SAFETY AND ENVIRONMENTAL ENFORCEMENT (BSEE) THAT BUBBLES AND ABOUT A 1 MILE LONG SHEEN WERE VISIBLE IN THE VACINITY OF TGP'S 24" LINE 523M-3700 ON THE OCS IN EUGENE ISLAND BLOCK 241. TGP INVESTIGATED AND CONFIRMED THE LOCATION OF THE BUBBLES AND SHEEN. THE ONLY PRODUCER FLOWING INTO THE PIPELINE WAS IMMEDIATELY SHUT-IN. DIVERS WERE SENT CLOSE A 30X24 SUBSEA VALVE IN ORDER TO REDUCE THE PIPELINE PRESSURE BEFORE EVALUATING THE LEAK LOCATION BUT WERE DELAYED BY WEATHER FROM DIVING AND COMPLETING THIS TASK UNTIL MARCH 17. AN ADDITIONAL CHECK VALVE WAS TO BE PINNED BEFORE COMMENCING REPAIR OF THE LEAK BUT THE DIVERS HAD TO RETURN TO SHORE ON MARCH 21 DUE TO BAD WEATHER. ON MARCH 27 THE DIVERS RETURNED TO THE LEAK LOCATION AND WERE ABLE TO EXCAVATE THE PIPE, REMOVE THE COATING AND INSTALL A LEAK CLAMP TO COMPLETE THE REPAIR. THE CLAMP INSTALLATION WAS COMPLETED ON MARCH 29 AND THE PIPELINE THEN RETURNED TO SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130031 | 16178 | 2013-04-12 10:32 | SUPPLEMENTAL FINAL | 18532 | TEXAS GAS SERVICE COMPANY | 1301 S. MOPAC EXPY, SUITE 400 | AUSTIN | TX | 78746 | 2013-03-13 11:38 | 2013 |  |  | 26.1507 | -98.2486 | 1040958 | 2013-03-13 15:45 |  | NATURAL GAS |  | 188 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-03-13 15:35 | 2013-09-27 15:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-03-13 11:38 | 2013-03-13 12:26 | ONSHORE | TX | 78503-5702 | MCALLEN | HIDALGO |  |  | 35 E TRANSVALLEY TO HIDALGO | SEG 1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | YES |  |  |  |  | YES | BORED/DRILLED | [16 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10.75 |  | 0.188 | 24000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1965 | 1965 | CARBON STEEL |  | OTHER | [8 empty] | MECHANICAL PUNCTURE, NOT EXPOSED DUE TO DEPTH. | CLASS 1 LOCATION | NO |  | 201 |  | NO | NO | NO |  | 0 | 0 | 396 | 446.510997643362 | 370 | 288.872950819672 | 132889 | 149839.393853103 | 3271 | 3688.22594265515 | 0 | 0 |  |  | 136926 | 70977.6766287201 | 154263.003744221 | [8 empty] | 337 |  | 604 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 14396 | NO | YES | YES |  | YES |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO NOTICABLE PRESSURE DROP NOTICED, DUE TO THE SMALL AMOUNT OF RELEASED GAS. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | NO | YES | STATE HIGHWAY | [9 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 1355627933 | TEXAS 811 | CONTRACT LOCATOR | YES | NO | NO |  | LOCATING PRACTICES NOT SUFFICIENT |  | FACILITY MARKING OR LOCATION NOT SUFFICIENT | [264 empty] | AMY MARK | REGULATORY COMPLIANCE | amy.mark@oneok.com | 512-370-8378 | 512-370-8400 |  |  |  | DEAN LAFLAMME | MANAGER REGIONAL ENGINEERING | 512-370-8318 | dean.laflamme@txgas.com | AT APPROXIMATELY 11:38 ON WEDNESDAY MARCH 13, 2013, TEXAS GAS SERVICE RECEIVED AN EMERGENCY CALL OF A HIT LINE. THE CALL WAS RECEIVED BY OUR DISPATCH LINE FROM DUDE BENKY OF MASTEC COMPANY; LOCATION 2101 W. MILITARY HWY, MCALLEN. A TEXAS GAS SERVICE FIRST RESPONDER ARRIVED AT 12:26 AND NOTICED THAT THERE WERE FIRE DEPARTMENT PERSONNEL ON SITE AND THAT MILITARY HWY WAS CLOSED TO TRAFFIC. HE ALSO NOTICED DAMAGE TO THE ROADWAY. FURTHER INVESTIGATION REVEALED THAT A BORING UNIT OPERATED BY HERNANDEZ UTILITIES, SUBCONTRACTOR FOR MASTEC, HAD DAMAGED AN UNDERGROUND GAS PIPELINE. DUE TO THE PROXIMITY OF ANOTHER PIPELINE IN THE AREA, TEXAS GAS SERVICE WAS UNCERTAIN IF THE DAMAGED GAS PIPELINE WAS A 10" TRANSMISSION LINE OPERATED BY TEXAS GAS SERVICE. TO DETERMINE IF THE DAMAGED PIPELINE WAS TEXAS GAS SERVICE'S, PERSONNEL ISOLATED THE DAMAGED PORTION OF THE 10" TRANSMISSION LINE VIA OPERATING 2 MANUAL VALVES AND MONITORED THE GAS PRESSURE WITHIN THE ISOLATED SECTION. IT WAS THEN DETERMINED THAT THE DAMAGED PIPELINE WAS THE TEXAS GAS SERVICE PIPELINE. THE LEAKAGE WAS CONTROLLED BY ISOLATING THE SEGMENT. SKILLETS WERE INSTALLED TO THE VALVE SITE FOR ADDITIONAL SAFETY TO PREVENT ANY POSSIBLE LEAK THROUGH WITH THE SHUTDOWN COMPLETED AT 15:35. THE ROADWAY WAS REOPENED AT APPROXIMATELY 18:00.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130032 | 15980 | 2013-04-12 21:48 | SUPPLEMENTAL FINAL | 15014 | GAS TRANSMISSION NORTHWEST LLC | 700 LOUISIANA STREET | HOUSTON | TX | 77002 | 2013-03-14 17:05 | 2013 |  |  | 46.8559 | -117.8096 | 1041089 | 2013-03-14 17:44 |  | NATURAL GAS |  | 1 | 52616 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-03-14 21:15 | 2013-03-21 14:20 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-03-14 17:05 | 2013-03-14 17:05 | ONSHORE | WA | 99143 | LACROSSE | WHITMAN | MILEPOST | 179.3 | B-LINE | MLV 6-2 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 72 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | DRAIN LINES | [38 empty] | 1992 |  | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 935 |  | NO | NO | NO |  | 25000 | 28188.8256087981 | 204007 | 230028.709838963 | 4 | 3.12295081967213 | 313000 | 352924.096622153 | 2019 | 2276.52955616654 | 0 | 0 |  |  | 544030 | 281578.360053701 | 613421.2845769 | [8 empty] | 860 |  | 911 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 99175 | NO | YES | [6 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS A THREADED FITTING NOT AFFECTED BY CONTROL ROOM ACTIVITY. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | THREADED FITTING | [19 empty] | YES | CAUSE OF LEAK PAST THREADS IS UNKNOWN, BUT THE FITTING DID NOT BREAK. | [161 empty] | KURT SMITH | COMPLIANCE SPECIALIST | kurt_smith@transcanada.com | (509) 546-8865 | (509) 546-8825 |  |  |  | KURT SMITH | COMPLIANCE SPECIALIST | (509) 546-8865 | kurt_smith@transcanada.com | THE LANDOWNER REPORTED AN AREA OF DEAD VEGETATION OVER THE PIPELINE. PIPELINE PERSONNEL DETECTED GAS IN A PROBE HOLE OVER THE PIPELINE, BUT NOT IN THE AIR ABOVE GROUND. THE PIPELINE SECTION WAS ISOLATED AND PRESSURE REDUCED TO 125 PSIG. THE AREA WAS EXCAVATED AND A BRANCH CONNECTION WAS FOUND. THE 2" BRANCH CONNECTION HAD A PIPE CAP AND THE LEAK WAS FOUND AT THE THREADS OF THE PIPE CAP. THE CAUSE OF THE LEAKAGE PAST THE THREADS OF THE FITTING IS UNKNOWN, BUT THE FITTING WAS NOT BROKEN. THE PIPELINE WAS VENTED TO NEAR ATMOSPHERIC PRESSURE. THE BRANCH CONNECTION WAS SANDBLASTED AND THREADED CONNECTION WAS SEAL-WELDED. THE PIPELINE WAS PUT BACK IN OPERATION AND THE EXPOSED PIPE WAS RECOATED AND BACKFILLED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130033 | 16048 | 2013-04-16 08:20 | SUPPLEMENTAL FINAL | 3 | ACADIAN GAS PIPELINE SYSTEM | 1100 LOUISIANA ST. | HOUSTON | TX | 77002 | 2013-03-08 03:54 | 2013 |  |  | 29.8963 | -91.3227 | 1041115 | 2013-03-15 09:50 |  | NATURAL GAS |  | 15 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-03-13 10:00 | 2013-04-10 08:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-03-13 10:00 | 2013-03-15 10:00 | ONSHORE | LA | 70538 | BELLE RIVER | ST. MARTIN | SURVEY STATION NO. | 1628+10 | CHICO B |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 312 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.312 | 52000 | 5LX | LONGITUDINAL ERW - HIGH FREQUENCY |  | YOUNGSTOWN SHEET | COAL TAR | [28 empty] | 1966 | 1966 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 430 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 51 | 39.8176229508197 | 334000 | 376602.710133543 | 0 | 0 | 0 | 0 |  |  | 334051 | 172911.862041711 | 376642.527756494 | [8 empty] | 790 |  | 970 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 87172 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLER(S) OR CONTROL ROOM WERE NOT CONTRIBUTING FACTORS IN THIS INCIDENT, THERE FOR AN INVESTIGATION OF ACTIONS WAS NOT NESCESSARY. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  | YES |  |  | YES |  |  | YES |  |  |  | YES | [5 empty] | NO | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | NATHAN L. GRAY JR. | COMPLIANCE SPECIALIST | ngray@eprod.com | 9858041376 |  |  |  |  | NATHAN L. GRAY JR. | COMPLIANCE SPECIALIST | 9858041376 | ngray@eprod.com | ACADIAN CHICO B PIPELINE LEAK; A FISHERMAN DISCOVERED BUBBLES COMING FROM A PIPELINE ROW IN SOUTH LOUISIANA WHICH ACADIAN SHARES WITH OTHER PIPELINE COMPANIES; THE FISHERMAN USED THE INFORMATION ON THE ROW PIPELINE MARKERS AND NOTIFIED ACADIAN PERSONNEL OF THE SUSPECTED LEAK. ACADIAN PERSONNEL WORKED WITH OTHER PIPELINE ROW PERSONNEL TO DETERMINE WHICH PIPELINE WAS THE SOURCE OF THE LEAK; IT WAS DETERMINED THAT ACADIAN WAS THE RESPONSIBLE PARTY FOR LEAKING NATURAL GAS. ACADIAN SHUT IN THE PIPELINE SEGMENT AND COMPRESSED OUT THE REMAINING NATURAL GAS. DIVERS WERE CALLED TO THE SITE TO INVESTIGATE FURTHER AND FOUND AN EXISTING REPAIR CLAMP WAS LEAKING OF WHICH WAS REMOVED AND REPLACED. PIPELINE WAS LEAK TESTED AND NO ISSUES WERE FOUND, PIPELINE WAS RETURNED TO SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130034 | 16100 | 2013-04-16 13:04 | SUPPLEMENTAL FINAL | 8170 | ALLIANT ENERGY - INTERSTATE POWER AND LIGHT COMPANY | 200 1ST STREET SE | CEDAR RAPIDS | IA | 52401 | 2013-03-12 09:15 | 2013 |  |  | 41.801 | -90.3017 | 1041516 | 2013-03-19 13:05 |  | NATURAL GAS |  | 6000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | BYPASS STOPPER FITTINGS WERE WELDED ON TO AVOID AN OUTAGE TO CUSTOMERS. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-03-12 09:15 | 2013-03-12 09:15 | ONSHORE | IA | 52732 | CLINTON | CLINTON |  |  | LOW MOOR LATERAL, P-0616 | PERMIT R1156 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 108 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 4 |  | 0.237 | 30000 | API - 5L, GRADE A | OTHER | UNKNOWN | UNKNOWN | COAL TAR | [28 empty] | 1966 | 1966 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 10.7 | 0.1 |  | CLASS 2 LOCATION | NO |  | 48 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 23500 | 18347.3360655738 | 125851 | 141903.675667714 | 74664 | 84187.6190102121 | 21794 | 24573.8906127259 | COST OF CONTAINING, TESTING, AND DISPOSING OF CONTAMINATED GROUNDWATER. |  | 245809 | 134083.450702162 | 269012.521356226 | [8 empty] | 250 |  | 275 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 2500 | NO | YES |  | YES |  |  | YES | THIS LINE CONTAINS 4 INCH AND 2 INCH DIAMETER STEEL AND WAS INSTALLED IN 1966. AS SUCH, IT WAS NOT DESIGNED FOR THE PASSAGE OF INTERNAL INSPECTION DEVICES. ADDITIONALLY, NO LAUNCHER OR RECEIVER EXISTS ON THIS LINE. | NO | [6 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [64 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | [10 empty] | NO | YES | CITY STREET | [9 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 1119607 |  | CONTRACT LOCATOR | YES | YES |  |  | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO MAINTAIN CLEARANCE | [118 empty] | NO | [62 empty] | NO | NO |  |  | NO | [13 empty] | NO | [63 empty] | RICHARD A. SUBLETT | SR. MANAGER COMPLIANCE AND OPERATIONAL PERFORMANCE | richardsublett@alliantenergy.com | 319-786-4008 |  |  |  |  | RICHARD A. SUBLETT | SR. MANAGER COMPLIANCE AND OPERATIONAL PERFORMANCE | 319-786-4008 | richardsublett@alliantenergy.com | A GAS LEAK WAS DISCOVERED BY AN INTERSTATE POWER & LIGHT (IPL) GAS SERVICE EMPLOYEE ON A 4 INCH STEEL LINE OPERATING AT 250 PSIG AT APPROXIMATELY 9:15 A.M. ON TUESDAY, MARCH 12, 2013 WHEN HE SMELLED A GAS ODOR AND HEARD GAS LEAKING. THIS EMPLOYEE IS A QUALIFIED FIRST RESPONDER AND IMMEDIATELY REQUESTED POLICE, FIRE, AND A GAS CONSTRUCTION CREW BE DISPATCHED TO THE SITE. (DATA FROM A PRESSURE RECORDER ON THE LINE INDICATES THAT THE LINE BREAK OCCURRED AT APPROXIMATELY 8:30 A.M. ON SUNDAY, MARCH 10, 2013.) WHEN AN IPL GAS CREW RESPONDED TO THE LEAK, THEY WERE INFORMED BY THE NEIGHBORING CHEMICAL PLANT PERSONNEL THAT THE PIPELINE HAS BEEN ENCROACHED UPON BY CONTAMINATED SOIL AND GROUNDWATER AND WAS NOW IN AN EPA SUPERFUND SITE. ONLY QUALIFIED HAZWOPER PERSONNEL ARE ALLOWED TO WORK ON THE SITE, REQUIRING IPL TO LOCATE AND MOBILIZE AN OUTSIDE GAS CONTRACTOR WITH THESE SPECIALIZED QUALIFICATIONS TO PERFORM THE REPAIRS. THE LINE IS A RADIAL FEED TO A SMALL TOWN WITH 190 CUSTOMERS AND THE LEAK WAS LOCATED ON A RURAL ROAD IN A RELATIVELY REMOTE LOCATION THAT DID NOT PRESENT AN IMMEDIATE RISK TO THE PUBLIC. IN ORDER TO AVOID AN INTERRUPTION OF SERVICE TO THE ENTIRE TOWN DURING COLD WEATHER, A TEMPORARY, ABOVEGROUND BYPASS LINE WAS INSTALLED. AFTER THE BYPASS STOPPERS WERE WELDED ON IN AN AREA OUTSIDE OF THE CONTAMINATED SOIL, A 2,600 FOOT LONG 2 INCH DIAMETER 100 PSIG HDPE ABOVEGROUND BYPASS LINE WAS CONSTRUCTED AND PLACED INTO SERVICE AT 11:54 P.M. ON WEDNESDAY, MARCH 13, 2013. AT THAT POINT, THE REPAIR CONTRACTOR MOVED IN AND MADE THE REPAIRS TO THE DAMAGED LINE BY CUTTING OUT AND REPLACING A 20 FOOT SECTION OF PIPE. THE LOST GAS CALCULATION FROM SUNDAY AT 8:30 A.M. UNTIL WEDNESDAY AT 11:54 P.M. YIELDED A VALUE OF APPROXIMATELY 6,000 MCF, WHICH EXCEEDED THE INCIDENT REPORTING THRESHOLD. THE LINE APPEARS TO HAVE FAILED FROM STRESS CRACKING AS A RESULT OF DENTS CAUSED BY PREVIOUS THIRD PARTY EXCAVATION DAMAGE. A STORM SEWER IMPROVEMENT PROJECT WAS COMPLETED IN THIS IMMEDIATE AREA DURING SUMMER 2011 AND THE DENTS APPEAR TO HAVE BEEN CAUSED BY THE TEETH OF A BACKHOE/TRACKHOE BUCKET. LEGAL ACTION TO RECOVER THE $245,000 ESTIMATED COST OF EMERGENCY RESPONSE, REPAIR, AND LOST GAS IS PENDING. THE CONTAMINANTS IN THE SOIL AND GROUNDWATER ARE VOLATILE ORGANIC COMPOUNDS (VOCS) AND POLYNUCLEAR AROMATIC HYDROCARBONS (PAHS), BUT DO NOT APPEAR TO HAVE HAD A HARMFUL EFFECT ON EITHER THE COAL TAR ENAMEL COATING OR THE PIPE. CATHODIC PROTECTION READINGS ON THE LINE HAVE HISTORICALLY BEEN VERY GOOD. DISCUSSIONS HAVE TAKEN PLACE REGARDING RE-ROUTING THE PIPELINE AWAY FROM ITS EXISTING LOCATION, BUT NO FIRM PLANS HAVE BEEN DEVELOPED AT THIS TIME. ADDITIONAL CLARIFICATION AS REQUESTED BY OPS CENTRAL REGION OFFICE. WHERE APPROPRIATE, CHANGES WERE MADE TO THE QUESTIONS REFERENCED: C6 - SELECTION IS LEFT AS RUPTURE, RATHER THAN PUNCTURE. INITIAL DAMAGE DID NOT PIERCE THROUGH THE PIPE WALL, BUT CAUSED A DENT THAT CREATED A STRESS CONCENTRATOR THAT EVENTUALLY CAUSED THE PIPE TO FAIL CIRCUMFERENTIALLY. E5A AND E5B - VALVES WERE NOT USED TO ISOLATE THE DAMAGE. HOWEVER, TWO MUELLER ANSI 600 TWO PIECE LINE STOPPERS WERE INSTALLED TO UTILIZE A BYPASS LINE TO AVOID A CUSTOMER OUTAGE. IN ORDER TO PROVIDE AN ANSWER FOR QUESTIONS E5A AND E5B, "MANUAL" VALVE WAS SELECTED. G14 AND G15 - IPL PERSONNEL WERE PRESENT WHEN THE LINE WAS INITIALLY EXPOSED IN 2011 FOR THE SEWER PROJECT, AND THE LOCATE MARKS WERE ACCURATE AT THAT TIME. G16 - DID THE DAMAGE CAUSE AN INTERRUPTION IN SERVICE? THIS QUESTION APPEARS ON THE PRINTED VERSION OF THE REPORT, BUT IS ABSENT ON THE ONLINE ENTRY FORM. THE CORRECT ANSWER IS "NO". G17 - CGA FIRST AND SECOND LEVEL DIRT ROOT CAUSES: RESPONSES WERE REVISED TO MORE ACCURATELY REFLECT THE ROOT CAUSE - EXCAVATION PRACTICES NOT SUFFICIENT AND FAILURE TO MAINTAIN CLEARANCE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130035 | 16768 | 2013-04-17 12:20 | SUPPLEMENTAL FINAL | 21252 | VIKING GAS TRANSMISSION CO | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2013-03-20 00:17 | 2013 |  |  | 47.2393 | -96.5243 | 1041585 | 2013-03-20 08:00 |  | NATURAL GAS |  | 44059 | 30 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | UNIT #1A WAS SHUTDOWN BUT OTHER COMPRESSION REMAINED ONLINE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-03-20 06:29 | 2013-03-20 06:43 | ONSHORE | MN | 56510 | ADA | NORMAN | MILEPOST | MP2207-1+0.0 | ADA COMPRESSOR STATION | MP2207-1+0.0 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | RELIEF VALVE PILOT SENSING LINE FITTING | 1967 |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 315 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 189674 | 148085.643442623 | 100 | 112.755302435192 | 100 | 112.755302435192 | 0 | 0 |  |  | 189874 | 153630.625973884 | 148311.154047493 | [8 empty] | 816 |  | 877 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) | [6 empty] | YES | [6 empty] | YES | 1 | 0 | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | OTHER | 1/2" THREADED CONNECTION ON OEM STEEL CROSS FITTING FOR RELIEF VALVE PILOT SENSING LINE | [6 empty] | YES | [11 empty] | YES | SEE ATTACHED FAILURE ANALYSIS REPORT FROM SHERRY LABS | [161 empty] | PAT VAUGHAN | MANAGER REGULATORY COMPLIANCE - DOT | pat.vaughan@oneok.com | 918-588-7734 | 918-591-5032 |  |  |  | WES DUNBAR | VP NATURAL GAS PIPELINE OPERATIONS | 918-588-7414 | wes.dunbar@oneok.com | AN ORIGINAL EQUIPMENT MANUFACTURER (OEM) FITTING ON A 4X6 ANDERSON-GREENWOOD RELIEF VALVE LOCATED ON A RECIPROCATING NATURAL GAS COMPRESSOR DISCHARGE PIPING, FAILED ON MARCH 20, 2013 AT THE ADA, MN COMPRESSOR STATION, CAUSING THE UNINTENDED RELEASE OF NATURAL GAS. EMPLOYEES FROM THE ADA COMPRESSOR STATION WERE NOTIFIED OF THE BLOWING GAS AT APPROXIMATELY 6:29 A.M. BY A NEIGHBOR TO THE COMPRESSOR STATION. THE RESPONDING EMPLOYEES WERE ABLE TO IDENTIFY THE PROBLEM AND SHUT DOWN THE UNIT AND THE VENTING GAS BY 7:02 A.M. A REVIEW OF THE STATION CONTROLLER LOG AT THE ADA COMPRESSOR STATION INDICATED THAT THE OEM FITTING FAILED AT 00:17 A.M., WHICH ALLOWED GAS TO VENT FOR 6 HOURS AND 45 MINUTES. THE EVENT WAS REPORTED TO THE NRC IN ANTICIPATION OF GAS LOSS EXCEEDING THE 3,000 MCF THRESHOLD LEVEL. A NEW FITTING WAS INSTALLED TO REPLACE THE FAILED FITTING AND THE COMPRESSOR WAS RESTORED TO NORMAL SERVICE THE SAME DAY. THE FAILED FITTING WAS SENT TO SHERRY LABS FOR A FAILURE ANALYSIS. THE FAILURES ANALYSIS CONCLUDED THE RELIEF VALVE FITTING FRACTURED THROUGH THE 1/2" DIAMETER THREADS OF ONE END BY UNIAXIAL BENDING FATIGUE. THE PRIMARY CAUSE OF FAILURE APPREARED TO BE USE OF A MATERIAL WITH INSUFFICIENT FATIGUE RESISTANT FOR THE APPLICATION. THE FAILED FITTING WAS A OEM STANDARD SUPPLIED FITTING, WHICH IS PART OF THE PILOT SENSING SYSTEM. THE OEM HAS DESIGNED A NEW HIGH STRENGTH, STAINLESS STEEL COMPONENT WHICH WILL REPLACE THOSE EXISTING PILOTS WITH SIMILAR RELIEF PILOT INSTALLATIONS. THIS WORK WILL BE COMPLETED IN 2013. OVER-PRESSURE WAS NOT A CONTRIBUTING FACTOR TO THE FITTING FAILURE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130036 | 16222 | 2013-04-23 10:07 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION LP (SPECTRA ENERGY CORP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2013-03-27 16:45 | 2013 |  |  | 28.5417 | -92.9089 | 1042284 | 2013-03-27 19:10 |  | NATURAL GAS |  | 360 | 14663 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-03-28 10:52 | 2013-05-08 10:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-03-27 16:45 | 2013-03-28 09:00 | OFFSHORE | [28 empty] | 150 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EAST CAMERON | BLOCK 246 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 20 |  | 0.406 | 56000 | API-5L X-52 | SEAMLESS |  | US STEEL | OTHER | CONCRETE AND SOMASTIC | [27 empty] | 1971 | 1971 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 524 |  | NO | NO | NO |  | 0 | 0 | 51320 | 57866.0212097408 | 1260 | 983.729508196721 | 500000 | 563776.512175962 | 0 | 0 | 0 | 0 |  |  | 552580 | 286370.203050752 | 622626.2628939 | [8 empty] | 671 |  | 1440 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 100425 | NO | [5 empty] | YES | NO PLATFORM FROM WHICH TO LAUNCH/RECEIVE | YES |  |  |  |  | YES | NO PLATFORM FROM WHICH TO LAUNCH/RECEIVE | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | ANOTHER PIPELINE OPERATOR'S HELICOPTER DISCOVERED THE LEAK |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS TOO SMALL TO BE IDENTIFIED BY CONTROL ROOM PERSONNEL. A REVIEW OF OPERATING RECORDS FOUND ABNORMAL OPERATING CONDITIONS DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | YES | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | deteschendorf@spectraenergy.com | 713-627-5573 | 713-386-4468 |  |  |  | RICK KIVELA | DIRECTOR OF OPERATIONAL COMPLIANCE | 713-627-6388 | rwkivela@spectraenergy.com | INDICATIONS OF BUBBLES ON THE WATER SURFACE IN EAST CAMERON 246 WERE REPORTED BY ANOTHER PIPELINE OPERATOR'S HELICOPTER ON MARCH 27, 2013. UPON INVESTIGATION, IT WAS DETERMINED THE LEAK WAS CAUSED BY A PINHOLE LEAK RESULTING FROM INTERNAL CORROSION ON TEXAS EASTERN TRANSMISSION, L.P. 20-INCH LINE 41-A-2 NATURAL GAS PIPELINE. A SHEEN WAS DISCOVERED ON APRIL 1, 2013 AS THE LINE PRESSURE WAS REDUCED, BUT THE SHEEN DISPERSED WITHIN A FEW HOURS. SUPPLEMENTAL: A LEAK CLAMP WAS INSTALLED BY DIVERS APRIL 24, 2013 AND THE LINE RETURNED TO SERVICE MAY 8, 2013.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130037 | 16087 | 2013-04-30 06:51 | SUPPLEMENTAL FINAL | 2620 | COLUMBIA GULF TRANSMISSION CO | 700 LOUISIANA ST. SUITE 700 | HOUSTON | TX | 77002 | 2013-03-29 08:50 | 2013 |  |  | 34.9616 | -88.419 | 1042402 | 2013-03-29 08:50 |  | NATURAL GAS |  | 4154 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-03-29 08:50 | 2013-03-29 10:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 |  |  | ONSHORE | MS | 38834 | CORINTH | ALCORN | MILEPOST | 506-2 BD | CORINTH COMPRESSOR STATION | 4-IN ESD VALVE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [8 empty] | CARBON STEEL |  | LEAK |  |  | OTHER | SHORT IN ELECTRICAL CONDUIT | [5 empty] | CLASS 1 LOCATION | NO |  | 84 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 14124 | 11027.1393442623 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 14124 | 11432.3360655738 | 11027.1393442623 | [8 empty] | 728 |  | 935 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE FAILURE WAS IDNETIFIED TO BE DUE TO MOISTURE IN THE ELECTRICAL CONDUIT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | OTHER | 4-IN ESD VALVE | [20 empty] | YES | MOISTURE IN THE ELECTRICAL CONDUIT. | [161 empty] | GEORGE HAMATY | ENGINEER | ghamaty@nisource.com | 3043573728 | 3043573522 |  |  |  | PERRY MICHAEL HOFFMAN | MANAGER | 3043572548 | mikehffman@nisource.com | AN INVESTIGATION INTO THIS INCIDENT IDENTIFIED EVIDENCE OF MOISTURE IN AN ELECTRICAL CONDUIT THAT TRIGGERED AN ELECTRICAL SHORT WHICH IN TURN ACTIVATED THE 4 INCH ESD VALVE. ACTIVATION OF THE VALVE RESULTED IN AN UNINTENDED RELEASE OF GAS. AS A FOLLOW-UP ACTION TO THIS INCIDENT, THE DESIGN TEAM CHANGED THE LOCATION OF THE ELECTRICAL CONDUIT SO THAT A RE-OCCURENCE TO A SIMILAR CONDITION IS ELIMINATED. HENCE; NO MOISTURE WILL ENTER INSIDE THE ELECTRICAL CONDUIT LEADING TO SIMILAR COMPONENTS THAT INITIATED THIS INCIDENT. ASIDE: PLEASE NOTE THAT THE INITIAL INCIDENT REPORT FOR CORINTH CS WAS READY FOR SUBMISSION ON APRIL 26, 2013. THE ODES SYSTEM EXPERIENCED AN ISSUE THAT REMOVED ALL PREVIOUSLY SUBMITTED INCIDENT REPORTS (FROM THE THREE OPIDS THAT COLUMBIA HAS) WITH MY DRAFT CORINTH CS INCIDENT REPORT FROM COLUMBIA'S OPID. AS OF TODAY, THE ODES SYSTEM IS RUNNING NORMALLY AND ALL PREVIOUSLY SUBMITTED INCIDENTS WERE RESTORED TO ALL THREE OPIDS. PLEASE REFER TO THE ATTACHED FILE FOR MORE INFORMATION. THANK YOU.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130038 | 15959 | 2013-05-02 11:14 | ORIGINAL FINAL | 31531 | ONEOK WESTEX TRANSMISSION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2013-04-02 12:50 | 2013 |  |  | 32.0969 | -101.5167 | 1042744 | 2013-04-02 15:28 |  | NATURAL GAS |  | 3789 | 11785 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-04-02 16:05 | 2013-04-03 20:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-04-02 14:00 | 2013-04-02 14:50 | ONSHORE | TX | 79720 | BIG SPRING | HOWARD |  |  | 4100-000 |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.25 | 46000 | X-46 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1970 | 1970 | CARBON STEEL |  | MECHANICAL PUNCTURE | 1 | 1.5 | [7 empty] | CLASS 1 LOCATION | NO |  | 442 |  | NO | NO | NO |  | 0 | 0 | 46807 | 52777.3744108406 | 15035 | 11738.3913934426 | 42262 | 47652.6459151611 | 2000 | 2255.10604870385 | 0 | 0 |  |  | 106104 | 59304.9059018969 | 114423.517768148 | [8 empty] | 661 |  | 960 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 174768 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A THIRD PARTY DAMAGE INCIDENT THAT WAS REPORTED BY THE THRID PARTY SO NOT A CONTROL ROOM ISSUE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | TRENCHER | LIQUID PIPELINE | NO |  |  | DATA NOT COLLECTED | NO | DATA NOT COLLECTED | YES | 32 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | PATTI FORD | SENIOR PIPELINE SAFETY ENGINEER | patti.ford@oneok.com | 918 588-7131 | 918 732-1311 |  |  |  | CRAIG A. FORSANDER | VICE PRESIDENT | 918 588-7414 | craig.forsander@oneok.com | ONEOK WESTEX TRANSMISSION RECEIVED A CALL FROM A THIRD PARTY EXCAVATOR AT APPROXIMATELY 1400 HOURS ON APRIL 2, 2013 THAT THE THIRD PARTY HAD HIT THE 4100-000 NATURAL GAS PIPELINE AT APPROXIMATELY 1250 HOURS. THE THIRD PARTY WAS UTILIZING A TRENCHER ALONG CR-2 NEAR THE INTERSECTION OF FM-33 ABOUT 10 MILES SOUTH OF BIG SPRING, TEXAS. ONEOK IMMEDIATELY DISPATCHED PERSONNEL TO HEAD TOWARDS THE SITE AND ARRIVED ONSITE AT 1450 HOURS. THE TRENCHER WAS STILL ON THE PIPELINE WITH BLOWING NATURAL GAS. ONEOK PERSONNEL ONSITE CONFIRMED THE PIPELINE THAT WAS STRUCK WAS THE ONEOK PIPELINE 4100-000. THE INCIDENT WAS REPORTED TO THE NATIONAL RESPONSE CENTER AT 1528 HOURS ON APRIL 2, 2013 UNDER INCIDENT NUMBER 1042744. THE RAILROAD COMMISSION OF TEXAS WAS NOTIFIED OF THE INCIDENT AT 1533 HOURS ON APRIL 2, 2013. THE INCIDENT SITE WAS ISOLATED AND BLOWN DOWN IN ORDER TO REPAIR THE DAMAGE VIA PIPE REPLACEMENT. THERE WAS NO FIRE, NO INJURIES, NO DEATHS, NO MEDIA, AND NO LAW ENFORCEMENT OR FIRE DEPARTMENT ON SITE. THE PIPELINE WAS REPAIRED AND RETURNED TO SERVICE AS OF 2000 HOURS ON APRIL 3, 2013. THERE WERE FOUR CUSTOMERS IMPACTED BY THE INCIDENT. A ONECALL TICKET WAS NOT CALLED IN BY THE THIRD PARTY PRIOR TO TRENCHING.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130039 | 15977 | 2013-05-11 17:10 | ORIGINAL FINAL | 12874 | QUESTAR PIPELINE COMPANY | 333 SOUTH STATE STREET P.O. BOX 45360 | SALT LAKE CITY | UT | 84145-0360 | 2013-04-17 06:00 | 2013 |  |  | 40.9912 | -108.0738 | 1044269 | 2013-04-17 15:06 |  | NATURAL GAS |  | 4500 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | STATION WAS IN STANDBY, BUT SUCTION ESD VALVE DID NOT CLOSE DURING PLANT ESD | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-04-17 06:00 | 2013-04-17 06:00 | ONSHORE | CO | 81625 |  | MOFFAT |  |  | STATELINE COMPRESSOR STATION | EAST FIELDS - MAIN LINE 22 SYSTEM | YES | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | VALVE ACTUATOR | 1972 |  | CARBON STEEL |  | OTHER | [8 empty] | SUCTION ESD VALVE DID NOT CLOSE WHEN PLANT WENT INTO ESD. VALVE ACTUATOR DID NOT FUNCTION PROPERLY. | CLASS 1 LOCATION | NO |  | 218 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 21087 | 16463.4159836066 | 200 | 225.510604870385 | 200 | 225.510604870385 | 0 | 0 | N/A |  | 21487 | 17275.4015379316 | 16914.4371933473 | [8 empty] | 631 |  | 863 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER RESPONDED APPROPRIATELY TO AN ESD ALARM AND DISPATCHED AN OPERATIONS EMPLOYEE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | VALVE ACTUATOR ON SUCTION ESD VALVE | [22 empty] | YES | VALVE OPERATOR DID NOT FUNCTION TO CLOSE SUCTION ESD VALVE WHEN ESD OCCURRED. | [161 empty] | CHAD WILDING | SUPERVISOR OF PIPELINE COMPLIANCE | chad.wilding@questar.com | 801-324-3814 | 801-324-5622 |  |  |  | LARRY CONTI | VICE PRESIDENT OF OPERATIONS AND ENGINEERING | 801-324-5061 | larry.conti@questar.com | ON APRIL 17, 2013 STATELINE COMPRESSOR STATION WENT INTO AN ESD AT 04:05. GAS CONTROL NOTED THE ALARM AND DISPATCHED AN OPERATIONS EMPLOYEE TO THE STATION. WHEN OPERATIONS ARRIVED THEY NOTED THAT THE SUCTION ESD VALVE DID NOT CLOSE. OPERATIONS CLEARED THE ESD AND RESET THE SYSTEM, ENABLING THE ESD VENT VALVE TO CLOSE, WHICH STOPPED THE VENTING GAS. OPERATIONS THEN WORKED ON THE SUCTION ESD VALVE ACTUATOR AND REPAIRED IT, WHICH ENABLED IT TO CLOSE. THE EVENT WAS REPORTED TO THE NRC AT 15:06 ON APRIL 17, 2013. THE WESTERN REGION OF PHMSA AND COLORADO STATE PSC WERE ALSO NOTIFIED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130040 | 16005 | 2013-05-13 15:15 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2013-04-23 04:40 | 2013 |  |  | 44.564 | -91.7664 | 1044767 | 2013-04-23 07:29 |  | NATURAL GAS |  | 4057 | 15 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | STOPPLE BYPASS WAS UTILIZED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-04-23 06:00 | 2013-04-23 08:00 | ONSHORE | WI | 54755 | MONDOVI | BUFFALO | MILEPOST | MP 55.126 | BLACK RIVER FALLS BRANCHLINE | WIB18601 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 120 |  | YES |  |  |  |  | YES | CASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 8 |  | 0.156 | 42000 | 5LX | LONGITUDINAL ERW - LOW FREQUENCY |  | LONE STAR | COAL TAR | [9 empty] | PIPE GIRTH WELD | [18 empty] | 1966 | 1965 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 138 |  | NO | NO | NO |  | 30000 | 33826.5907305577 | 65 | 73.2909465828751 | 17365 | 13557.5102459016 | 58994 | 66518.8631186175 | 123309 | 139037.435879812 | 0 | 0 |  |  | 229733 | 123972.391895677 | 253013.690921471 | [8 empty] | 776 |  | 895 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [7 empty] | NO |  | YES | YES | YES |  |  |  | YES |  |  |  |  | YES | LINE NOT ASSESSED FOR PIGGING YET. | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAKAGE OF NATURAL GAS WAS NOT OF A SUFFICIENT QUANTITY, AT ANY TIME, TO IMPACT OR CREATE FLUCTUATIONS IN PRESSURE THAT WOULD BE IDENTIFIED BY A CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES | [6 empty] | YES | YES | ANALYZED BY OUTSIDE METALLURGICAL LABORATORY, REPORT ATTACHED. | [12 empty] | YES | [63 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | BYRON H. WOOD | SR. PIPELINE SAFETY SPECIALIST | byron.wood@nngco.com | 402-398-7396 |  |  |  |  | THOMAS G. CORRELL | SR. DIRECTOR PIPELINE SAFETY AND INTEGRITY | 402-398-7715 | thomas.correll@nngco.com | ON APRIL 23, 2013, AT APPROXIMATELY 04:27 NORTHERN NATURAL GAS COMPANY'S OMAHA OPERATIONS COMMUNICATIONS CENTER RECEIVED A CALL FROM A DAVID WEISS WITH THE MONDOVI, WISCONSIN FIRE DEPARTMENT REPORTING THAT THERE APPEARED TO BE BLOWING NATURAL GAS 1/2 MILE SOUTH OF COUNTY ROAD A ON STEELE VALLEY ROAD ON PIPELINE NUMBER WIB 18601 AT A MILE POST OF 55.126. MR. WEISS INDICATED THAT EMERGENCY RESPONDERS WERE ON-SITE AND THAT THEY HAD BLOCKED OFF A SECTION OF THE ROAD. HE INDICATED THAT THERE WERE NO RESIDENCES IN THE IMMEDIATE AREA. A REPRENTATIVE FROM MIDWEST NATURAL GAS CALLED TO CONFIRM THAT NATURAL GAS APPEARED TO BE BLOWING FROM VENT CASINGS ON BOTH SIDES OF THE ROAD. THE LOCATION IS APPROXIMATELY FOUR MILES WEST OF THE TOWN OF MONDOVI, WISCONSIN. NORTHERN COMPANY EMPLOYEES WERE DISPATCHED TO THE SITE AND A GAS MANAGEMENT PLAN WAS DEVELOPED TO REDUCE PRESSURE ON THE THE PIPELINE TO APPROXIMATELY 520-550 PSIG FROM A TYPICAL 795 PSIG. PRESSURE WAS REDUCED BY PINCHING BLOCK VALVES AND LETTING CUSTOMER USAGE PULL THE PRESSURE DOWN ON THE LINE THEN CLOSELY MONITORING. EMERGENCY STOPPLE AND BYPASS PIPING WAS BROUGHT ON-SITE TESTED AND PLACED IN-SERVICE. MICHELS CONSTRUCTION, A CONTRACTOR, ASSISTED WITH EXCAVATION ACTIVITIES ON BOTH SIDE OF THE ROAD. UPON COMPLETION OF EXCAVATION A CRACK IN A PIPING GIRTH WELD WAS FOUND ON THE UNDER SIDE (SIX O'CLOCK POSITION) WHICH WENT ENTIRELY THROUGH THE PIPE, THE CRACK WAS APPROXIMATELY 4 1/2 INCHES LONG AND ONE SIXTEENTH OF AN INCH WIDE. THE STEELE COUNTY ROAD DEPARTMENT WAS CONTACTED AND AGREED THAT NORTHERN COULD OPEN CUT THE ROAD FOR INSTALLING NEW TESTED PIPE. NORTHEN WOULD BE RESPONSIBLE FOR RESTORATION OF THE ROAD AND HARD SURFACING. APPROXIMATELY 60-FEET OF NEW TESTED, COATED PIPE WAS INSTALLED. THERE WERE NO INJURIES, NO FIRE, NO EVACUATIONS AND NO LOSS OF SERVICE TO CUSTOMERS. THE PIPE WITH THE CRACKED GIRTH WELD WAS SENT TO AN OUTSIDE METALLURGICAL LABORATORY FOR ANALYSIS. A SUPPLEMENTAL REPORT WILL BE FILED WHEN RESULTS FROM THE METALLURICAL LABORATORY TESTS ARE RECEIVED AND A TOTAL COST OF THE REPAIRS IS COMPLILED. SUPPLEMENTAL/FINAL REPORT (REFERENCE INITIAL REPORT 20130040 - 15978 DATED 05/13/2013 - THE FINAL COST FOR THIS EVENT HAS BEEN UPDATED. A METALLURGICAL ANALYSIS WAS COMPLETED BY BRYAN LABORATORY, INC. WITH FINDINGS OF THAT THE PIPE AT BOTH GIRTH WELDS EXAMINED WERE FOUND TO EXHIBIT MISALIGNMENT AND APPEAR TO BE DISTORTED. EXTRANEOUS WELDING WIRE WAS NOTED PROTRUDING FROM THE INTERNAL PORTIONS OF THE WELD. THE CRACK WAS FOUND TO BE 6-INCHES LONG AND IN THE LOWER QUADRANT OF THE WELD. "NECKING DOWN", TYPICAL OF DUCTILE OVERLOADING FRATURING, WAS NOTED IN THE PIPE ON THE INTERNAL SURFACE OF THE CRACKED AREA. IN THE LABORATORIES OPINION, THE CRACK WAS CAUSED BY BENDING FORCES, AS SHOWN BY THE DISTORTION OF THE PIPE AT THE GIRTH WELD. BLACK DEPOSITS ALONG BOTH SIDES OF THE CRACK AT THE OUTSIDE SURFACE SHOWED THAT A CRACK APPROXIMATELY 0.025 INCHES DEEP PRECEDED FINAL SEPARATION. FINAL SEPARATION INITIATED AT THE PREEXISTING CRACK AND FINAL SEPARATION WAS BY DUCTILE OVERLOAD. A COPY OF THE METALLURICAL REPORT IS ATTACHED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130041 | 16395 | 2013-05-15 16:51 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2013-04-17 10:50 | 2013 |  |  | 33.8003 | -84.281 | 1044257 | 2013-04-17 16:50 |  | NATURAL GAS |  | 365 | 41.6 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-04-17 16:50 | 2013-04-19 01:12 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 31 | 2013-04-17 11:04 | 2013-04-17 11:40 | ONSHORE | GA | 30033 | DECATUR | DEKALB | MILEPOST | INTERSECTION | MEMORIAL DR TO SCOTT BLVD PIPELINE | GIS OBJECT ID #316437 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.25 | 42000 | API 5L X42 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | OTHER | MILLWRAP | [27 empty] | 1971 | 1970 | CARBON STEEL |  | MECHANICAL PUNCTURE | 0.1 | 6 | [7 empty] | CLASS 3 LOCATION | YES | METHOD1 | 191 |  | NO | NO | NO |  | 0 | 0 | 174 | 196.194226237235 | 1522 | 1188.28278688525 | 44000 | 49612.3330714847 | 21000 | 23678.6135113904 | 0 | 0 |  |  | 66696 | 34964.4834455849 | 74675.4235959976 | [8 empty] | 251 |  | 300 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 1400 | NO |  | YES | YES | YES |  |  |  | NO | [6 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTRACTOR WORKING FOR THE COMPANY STRUCK THE 16-INCH PIPE WITH BORE AUGER CAUSING A SMALL HOLE IN PIPE. | [12 empty] | NO |  |  | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [10 empty] | YES | YES | STATE HIGHWAY | [9 empty] | CONTRACTOR | AUGER | NATURAL GAS | NO | 4053400013 |  | CONTRACT LOCATOR | YES | YES | YES | 39 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO MAINTAIN CLEARANCE | [263 empty] | RALPH MCCOLLUM | SR. COMPLIANCE ENGINEER | rmccollu@aglresources.com | (404) 584-3733 | (404) 584-4807 |  |  |  | RICHARD R. LONN | MANAGING DIR COMPLIANCE AND PIPELINE RISK MGNT | (404) 584-3552 | rlonn@aglresources.com | OPERATOR'S CONTRACTOR WAS ATTEMPTING TO INSTALL APPROXIMATELY 200 FEET OF 24-INCH STEEL PIPE VIA CONVENTIONAL JACK & BORE WHERE IT APPEARS THE AUGER STRUCK A ROCK ABOUT 30-FEET INTO THE BORE AND VEERED APPROXIMATELY 3-FEET OFF THE BORE PATH STRIKING THE SIDE OF AN EXISTING 16-INCH HIGH PRESSURE STEEL TRANSMISSION PIPELINE CAUSING A LEAK. THE DAMAGE OCCURRED ON THE VERTICAL PIPE WHERE THE 16-INCH TRANSMISSION PIPELINE MADE A DEPTH CHANGE FROM 5-FEET TO 10-FEET DEEP.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130042 | 15983 | 2013-05-24 10:46 | ORIGINAL FINAL | 12696 | CYPRESS GAS PIPELINE COMPANY | 1100 LOUISIANA ST. | HOUSTON | TX | 77002 | 2013-04-24 18:55 | 2013 |  |  | 30.5279 | -91.7457 | 1045977 | 2013-05-13 20:50 |  | NATURAL GAS |  | 16 | 158 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-04-24 18:55 | 2013-05-03 18:55 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-04-24 18:55 | 2013-04-24 18:55 | ONSHORE | LA | 70750 | KROTZ SPRINGS | ST. LANDRY | SURVEY STATION NO. | 2534+40 | BRW #1 MAIN LNE | 580-0100 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 40 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.375 | 52000 | API 5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | US STEEL | COAL TAR | [28 empty] | 1946 | 1946 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 312 |  | NO | NO | NO |  | 0 | 0 | 539 | 607.751080125688 | 54 | 42.1598360655738 | 60471 | 68184.2589355853 | 0 | 0 | 0 | 0 |  |  | 61064 | 31621.0568168648 | 68834.1698517765 | [8 empty] | 592 |  | 775 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 41942 | NO | [5 empty] | YES | GAS PRESSURE WELDS EXIST ON PIPELINE. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LOCAL OPERATIONS PERSONNEL WAS ONSITE AND SHUT IN PIPELINE. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  | YES | [5 empty] | YES | [5 empty] | YES |  |  |  | NO | YES | NO | NO | [168 empty] | NO | [63 empty] | YES | 1990 | 2000 | NO | [13 empty] | NO | [63 empty] | NATHAN L. GRAY JR. | PIPELINE COMPLIANCE SPECIALIST | ngray@eprod.com | 9858041376 |  |  |  |  | NATHAN L. GRAY JR. | PIPELINE COMPLIANCE SPECIALIST | 9858041376 | ngray@eprod.com | CYPRESS GAS PIPELINE BRW #1 MAIN LINE LEAK; A PIPELINE TECHNICIAN DISCOVERED BUBBLES IN A PUDDLE OF WATER COMING FROM AN UNDERGROUND PIPELINE VALVE SITE IN SOUTH LOUISIANA. CYPRESS GAS PIPELINE PERSONNEL SHUT IN THE PIPELINE SEGMENT AND COMPRESSED OUT THE REMAINING NATURAL GAS. REPAIR WORK CONSISTED OF REPLACING A 23 FOOT SECTION OF PIPELINE WITH PRETESTED PIPE, X-RAYING WELDS, AND LEAK TESTING PIPELINE SECTION TO 590 PSI. NO ISSUES WERE FOUND, PIPELINE WAS RETURNED TO SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130043 | 15984 | 2013-05-24 17:40 | ORIGINAL FINAL | 1007 | TALLGRASS INTERSTATE GAS TRANSMISSION, LLC | 370 VAN GORDON ST | LAKEWOOD | CO | 80228 | 2013-05-04 02:18 | 2013 |  |  | 41.3336 | -103.8849 | 1046014 | 2013-05-04 08:46 |  | NATURAL GAS |  | 75000 | 10000 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-05-04 02:54 | 2013-05-09 18:41 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-05-04 02:31 | 2013-05-04 04:45 | ONSHORE | NE | 69128 | UNINCORPORATED | KIMBALL | SURVEY STATION NO. | 29272+31.20 | 650-001-00-00/PONY EXPRESS PIPELINE (PXP) MAINLINE | LA GRANGE TO STERLING | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.281 | 52000 | API-5L | FLASH WELDED |  | AO SMITH | COAL TAR | [28 empty] | 1954 | 1954 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 4800 | 20 |  | CLASS 1 LOCATION | NO |  | 490 |  | NO | NO | NO |  | 500 | 563.776512175962 | 50000 | 56377.6512175962 | 200000 | 156147.540983607 | 246000 | 277378.043990574 | 0 | 0 | 0 | 0 |  |  | 496500 | 315346.70505325 | 490467.012703952 | [8 empty] | 845 |  | 1052 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 83952 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  | YES | RECORDS INDICATE NORMAL PIPELINE OPERATIONS PRIOR TO INCIDENT WITH APPROPRIATE CONTROL ROOM/CONTROLLER ACTIVITY. RECORDS INDICATE APPROPRIATE CONTROL ROOM/CONTROLLER RESPONSE TO PIPELINE AOC (E.G., UNEXPLAINED BACK FLOW PRESSURES). RECORDS INDICATE APPROPRIATE CONTROL ROOM/CONTROLLER ACTIONS DURING COMPANY INCIDENT RESPONSE. | YES | YES | [7 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) |  | YES | [12 empty] | YES | [15 empty] | YES | MILL DEFECT = HARD SPOT | [55 empty] | YES | YES | YES |  | YES |  |  |  | 2013 | [11 empty] | 2012 | [19 empty] | 2013 | [23 empty] | YES | 1996 | 1329 | NO | [13 empty] | NO | [63 empty] | JOSEPH MOLLOY | SENIOR COMPLIANCE ENGINEER | joe.molloy@tallgrassenergylp.com | 303.763.3434 | 720.452.6610 |  |  |  | DANIEL PRASCHER | MANAGER - COMPLIANCE AND RECORDS | 303.763.3253 | daniel.prascher@tallgrassenergylp.com | AT APPROXIMATELY 02:18 LOCAL TIME ON MAY 4, 2013, A PIPE SECTION OF THE 20" TALLGRASS PONY EXPRESS PIPELINE (PXP) MAINLINE IN UNINCORPORATED (CLASS 1 AREA) KIMBALL COUNTY, NE RUPTURED DUE TO THEN-UNKNOWN CAUSES. THE PIPELINE WAS OPERATING AT 845 PSIG AT THE TIME OF THE INCIDENT, WITH AN ESTABLISHED MAXIMUM ALLOWABLE OPERATING PRESSURE (MAOP) OF 1052 PSIG. THERE WAS NO FIRE, EXPLOSION, INJURY/DEATH, OR MAJOR PRIVATE PROPERTY DAMAGE ASSOCIATED WITH THE RUPTURE. THE RUPTURE WAS IDENTIFIED BY TALLGRASS GAS CONTROL OPERATORS AT 02:31 WHEN A DOWNSTREAM COMPRESSOR STATION ALARMED ON A LOW COMPRESSION RATE. PRESSURE TRENDING INDICATED ABNORMAL OPERATING CONDITIONS (AOC) ON THE 135 MILE-LONG PXP GUERNSEY-STERLING SEGMENT. LOCAL FIELD OPERATORS WERE CONTACTED AND BEGAN SHUTTING IN THE SEGMENT VIA ISOLATION VALVES AT INTERCONNECT POINTS. THE GUERNSEY-ROCKPORT INTERCONNECT POINT (35 MILES UPSTREAM OF STERLING) SEGMENT WAS ISOLATED BY 02:54, 23 MINUTES AFTER AOC IDENTIFICATION. FIELD OPERATIONS CONTINUED SYSTEMATIC VALVE CLOSURES AS THEY MOVED ALONG THE PIPELINE TOWARDS THE RUPTURE; THE LOCAL 15.9 MILE VALVE-TO-VALVE SEGMENT WITH THE RUPTURED SECTION WAS ISOLATED BY 06:29. FIELD OPERATIONS SUPERVISED AN INTENTIONAL AND CONTROLLED BLOWDOWN OF THE LOCAL SEGMENT UNTIL IT WAS SAFE TO APPROACH THE RUPTURE SITE TO BEGIN INVESTIGATION. FIELD INVESTIGATION REVEALED A CATASTROPHIC RUPTURE OF A PIPE SECTION APPROXIMATELY 45 FEET IN LENGTH, WITH COMPLETE SEPARATION OF THE RUPTURED SECTION FROM THE PIPELINE. THE FRAGMENTS OF THE PIPE (API-5L X52, EFW, MANUFACTURED IN 1954 BY AO SMITH) WERE SENT TO A METALLURGICAL FIRM FOR STUDY. METALLOGRAPHY DETERMINED THAT THE RUPTURE ORIGINATED IN A "HARD SPOT" MILL DEFECT IN THE BODY WALL. THE SEAM AND GIRTH WELDS WERE NOT PART OF THE ROOT CAUSE. THE PIPELINE WAS RETURNED TO SERVICE ON MAY 9, 2013 UNDER A TEMPORARY PRESSURE RESTRICTION OF 676 PSIG (80% OF THE OPERATING FAILURE PRESSURE).
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130045 | 16006 | 2013-05-31 15:07 | SUPPLEMENTAL FINAL | 32668 | PVR MARCELLUS GAS GATHERING, LLC | 301 COMMERCE, STE 700 | FORT WORTH | TX | 76102 | 2013-05-05 10:00 | 2013 |  |  | 41.3271 | -77.266 | 1046086 | 2013-05-05 11:47 |  | NATURAL GAS |  | 26350 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | SIMPLY ISOLATED THE RELIEF VALVE TO ISOLATE THE RELEASE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-05-05 10:00 | 2013-05-05 10:15 | ONSHORE | PA | 17740 | CUMMINGS TWP | LYCOMING | MILEPOST | OGONTZ EAST | OGONTZ EAST COMPRESSOR STATION | LYCOMING 30" | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2012 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE RELIEVED AT A PRESSURE LOWER THAN ITS SETTING | CLASS 1 LOCATION | YES | METHOD1 | 750 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 109402 | 85414.2663934426 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 109402 | 88552.8483606557 | 85414.2663934426 | [8 empty] | 1170 |  | 1313 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [25 empty] | YES | [165 empty] | DAVE JONES | REGULATORY COMPLIANCE ADMINISTRATOR | djones@pvrpartners.com | 610-283-1701 |  |  |  |  | DAVE JONES | REGULATORY COMPLIANCE ADMINISTRATOR | 610-283-1701 | djones@pvrpartners.com | AT APPROXIMATELY 10:00 AM ON MAY 5, 2013, PVR DISCOVERED A PRESSURE RELIEF VALVE RELIEVING NATURAL GAS INTO THE ATMOSPHERE. PVR PERSONNEL RESPONDED BY ISOLATING THE VALVE AND MAKING THE APPROPRIATE INTERNAL NOTIFICATIONS. PVR'S ENGINEERING MANAGER CALCULATED THE RELEASE VOLUME AT APPROXIMATELY 26.53 MMCF. AT NO TIME WAS THE PUBLIC, THE ENVIRONMENT, OR PVR EMPLOYEES IN ANY DANGER AS THE NATURAL GAS BEING RELEASED QUICKLY DISSIPATED INTO THE ATMOSPHERE. PVR NOTIFIED THE NRC (PETTY OFFICER HARDY ' CASE # 1046086) AT 11:47 AM AND PROVIDED AN UPDATED VOLUME AT 5:22 PM (PETTY OFFICER LAYMAN). A REVIEW OF THE OPERATIONAL DATA CONFIRMED THAT THE RELIEF VALVE ACTIVATED BEFORE REACHING ITS SET POINT. THE AFFECTED VALVE WAS REMOVED AND A THIRD PARTY FAILURE INVESTIGATION COMPLETED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130046 | 16122 | 2013-06-05 12:36 | SUPPLEMENTAL FINAL | 4900 | KINDER MORGAN TEJAS PIPELINE | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2013-05-08 21:20 | 2013 |  |  | 31.3396 | -95.4011 | 1046522 | 2013-05-09 09:14 |  |  |  | 53 | 82 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-05-08 21:20 |  | YES |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2013-05-08 21:20 | 2013-05-08 21:35 | ONSHORE | TX | 75835 | CROCKETT | HOUSTON | MILEPOST | STATION 7 | KINDER MORGAN TEJAS STATION 7 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE OTHER ENCLOSED SPACE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [40 empty] | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | TURBINE MATERIALS AND LUBE OIL | OTHER | [8 empty] | UNIDENTIFIED LEAK IN LUBE OIL SYSTEM. | CLASS 1 LOCATION | NO |  | 235 |  | NO | NO | NO |  | 0 | 0 | 294 | 331.500589159466 | 189 | 147.559426229508 | 7491705 | 8447294.63030244 | 10000 | 11275.5302435192 | 0 | 0 |  |  | 7502188 | 3883012.04764143 | 8459049.22056135 | [8 empty] | 875 |  | 1001 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [5 empty] | YES | NO CONTROL ISSUES WERE IDENTIFIED. | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | OTHER | FAILURE OF TURBINE ENGINE LUBE OIL COMPONENTS | [20 empty] | YES | FAILURE CAUSE UNDETERMINED | [161 empty] | MERLIN MOSEMAN | ENGINEER-PIPELINE | merlin_moseman@kindermorgan.com | 713-420-4614 | 713-420-1611 |  |  |  | MERLIN MOSEMAN | ENGINEER-PIPELINE | 713-420-4614 | merlin_moseman@kindermorgan.com | AT 21:20 ON MAY 8, 2013, A COMPRESSOR STATION FIRE ALARM WAS LOGGED AT THE TEJAS GAS CONTROL CENTER. EMERGENCY STATION SHUTDOWNS WERE INITIATED AND LOCAL OPERATING PERSONNEL WERE DISPATCHED TO THE SCENE. UPON ARRIVAL AT THE STATION, THE OPERATOR PERSONNEL CONFIRMED THAT A FIRE WAS IN PROGRESS, THAT THE STATION ESD HAD BEEN INITIATED AND THEY NOTIFIED THE LOCAL FIRE DEPARTMENTS. THE FIRE DEPARTMENT PERSONNEL DETERMINED THAT THE SAFEST COURSE OF ACTION WAS TO ALLOW THE FIRE TO BURN DOWN AND EXHAUST THE AVAILABLE FUEL BEFORE STARTING FIRE SUPPRESSION. THE FIRE BURNED APPROXIMATELY TWO HOURS BEFORE IT WAS FULLY EXTINGUISHED. THE FIRE INVOLVED A COVERED COMPRESSOR ENCLOSURE. THE ENCLOSURE IS A ROOFED STRUCTURE WITH OPEN SIDES (NO WALLS). FOUR SOLAR SATURN PACKAGE COMPRESSOR UNITS WERE INSTALLED INSIDE THE ENCLOSURE. UNITS 2 & 3 WERE FULLY INVOLVED IN THE FIRE AND SUSTAINED HEAVY DAMAGE. UNITS 1 & 4 SUSTAINED LIGHT DAMAGE. NO NATURAL GAS PIPING AT THE STATION WAS BREACHED OR DAMAGED BY THIS INCIDENT. THE CAUSE OF THE FIRE WAS INVESTIGATED AND COULD NOT BE DETERMINED DUE TO THE FIRE DAMAGE TO THE PHYSICAL EVIDENCE. BOTH LUBE OIL AND RESIDUAL NATURAL GAS IN THE UNIT PIPING FUELED THE FIRE WHICH WERE ALLOWED TO BE CONSUMED BEFORE THE FIRE DEPARTMENT EXTINGUISHED THE REMAINDER OF THE FIRE. THIS INCIDENT WAS TELEPHONICALLY REPORTED TO THE TEXAS RAILROAD COMMISSION AT 22:40 ON MAY 8, 2013. THE COMMISSION REPORT NUMBER IS 810.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130047 | 16341 | 2013-06-07 12:39 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2013-05-10 13:15 | 2013 |  |  | 35.5392 | -120.5764 | 1046736 | 2013-05-10 15:30 |  | NATURAL GAS |  | 11300 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-05-10 16:33 | 2013-05-12 23:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-05-10 13:15 | 2013-05-10 14:00 | ONSHORE | CA | 93465 | TEMPLETON | SAN LUIS OBISPO | MILEPOST | 53.9 | LINE 44-1008 |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 32 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10 |  | 0.25 | 24000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | NONE | [28 empty] | 1932 | 1932 | CARBON STEEL |  | MECHANICAL PUNCTURE | 8 | 11 | [7 empty] | CLASS 1 LOCATION | NO |  | 148 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 68000 | 53090.1639344262 | 250000 | 281888.256087981 | 1000 | 1127.55302435192 | 0 | 0 |  |  | 319000 | 184952.707879927 | 336105.973046759 | [8 empty] | 362 |  | 400 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [7 empty] | NO |  | YES | [5 empty] | NO | [6 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  | YES | PRIVATE EASEMENT | [7 empty] | FARMER | FARM EQUIPMENT | AGRICULTURE | NO |  |  | UTILITY OWNER | YES | YES | YES | 50 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | W. JEFF KOSKIE | PIPELINE SAFETY AND COMPLIANCE MANAGER | wkoskie@semprautilities.com | 213 305-8660 |  |  |  |  | W. JEFF KOSKIE | PIPELINE SAFETY AND COMPLIANCE MANAGER | 213 305-8660 | wkoskie@semprautilities.com | CONTRACTOR WORKING FOR A RANCHER WAS DEEP RIPPING THE GROUND IN A VINEYARD AND STRUCK 10' HIGH PRESSURE DOT DEFINED TRANSMISSION LINE. LINE MARKERS WERE PRESENT AS WELL AS MARKINGS FROM A PREVIOUS USA REQUEST. THE CONTRACTOR PERFORMING THE RIPPING OPERATION DID NOT HAVE A CURRENT USA TICKET FOR THE WORK BEING PERFORMED. GAS WAS CONTROLLED BY CLOSING MAIN LINE VALVES ISOLATING A 10 MILE SECTION OF THE LINE. THIRTEEN CUSTOMERS WERE LEFT WITHOUT SERVICE. REPAIRS HAVE BEEN COMPLETED, ALL CUSTOMERS PUT BACK IN SERVICE. NO IGNITION, NO INJURIES. INVESTIGATION DETERMINED THAT CONTRACTOR WAS AWARE OF PIPELINE LOCATION, BUT FAILED TO RAISE RIPPER BEFORE CROSSING MARKED LINE. IN ADDITION, NO CURRENT USA TICKET FOR WORK BEING PERFORMED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130048 | 15993 | 2013-06-11 11:30 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2013-05-17 16:55 | 2013 |  |  | 31.7766 | -93.143 | 1047518 | 2013-05-17 18:53 |  | NATURAL GAS |  | 3632 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-05-17 17:04 | 2013-05-17 19:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-05-17 16:55 | 2013-05-17 16:55 | ONSHORE | LA | 71457 | NATCHITOCHES | NATCHITOCHES | MILEPOST | 40 | STATION 40 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1954 |  | CARBON STEEL |  | OTHER | [8 empty] | GAS RELEASE THROUGH RELIEF VALVE VENT STACK | CLASS 3 LOCATION | YES | METHOD2 | 454 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 14400 | 11242.6229508197 | 0 | 0 | 300 | 338.265907305578 | 0 | 0 |  |  | 14700 | 11811.0106821372 | 11580.8888581253 | [8 empty] | 633 |  | 750 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATING PRESSURE WAS WELL BELOW MAOP. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [204 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE |  |  |  | YES |  |  |  |  | OTHER MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | KENNETH C. PETERS | SR. ENGINEER - PIPELINE | ken_peters@kindermorgan.com | 2053257554 | 2053253508 |  |  |  | REJI GEORGE | DIRECTOR - CODES AND STANDARDS | 7134205433 | reji_george@kindermorgan.com | TENNESSEE GAS PIPELINE (TGP) EMPLOYEES WERE TAKING DISCHARGE PIPING OUT OF SERVICE AT THE TGP NATCHITOCHES COMPRESSOR STATION (STATION 40) MAY 17, 2013 IN ORDER TO PREPARE FOR IMP HYDROSTATIC TESTING. THE EMPLOYEES FAILED TO ISOLATE A RELIEF VALVE DURING THE DEPRESSURIZATION SUCH THAT WHEN THE RELIEF VALVE'S SENSING LINE LOST PRESSURE, THE RELIEF VALVE ACTIVATED AS IT WAS DESIGNED TO DO. THE RELIEF VALVE RELEASED NATURAL GAS TO THE ATMOSPHERE IN A VOLUME THAT EXCEEDED THE INCIDENT REPORTABILITY LEVEL OF 3,000 MCF. UPON HEARING THE NOISE OF THE RELEASE, THE RELIEF VALVE'S ISOATION VALVE WAS CLOSED TO STOP THE RELEASE. THE RELIEF WAS RESET FOR NORMAL OPERATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130049 | 15998 | 2013-06-11 15:28 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2013-05-16 19:15 | 2013 |  |  | 29.4485 | -89.4317 | 1047435 | 2013-05-16 20:02 |  | NATURAL GAS |  | 250 | 1405 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-05-16 19:15 | 2013-05-23 08:34 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-05-16 19:15 | 2013-05-18 20:00 | OFFSHORE | [28 empty] | 11 | IN STATE WATERS | LA | MAIN PASS | 34 | PLACQUEMINES |  |  |  | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | REPAIR SLEEVE OR CLAMP | [38 empty] | 1992 |  | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 187 |  | NO | NO | NO |  | 0 | 0 | 5660 | 6381.9501178319 | 1010 | 788.545081967213 | 275000 | 310077.081696779 | 1500 | 1691.32953652789 | 0 | 0 |  |  | 283170 | 146856.931332338 | 318938.906433106 | [8 empty] | 800 |  | 992 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 69274 | NO | [5 empty] | YES | PIPE IS OFFSHORE. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | AIR PATROL |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATING PRESSURE WAS WELL BELOW MAOP. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | SEAL IN OLD REPAIR CLAMP ALLOWED LEAK. | [15 empty] | YES | SEAL FAILED IN OLD REPAIR CLAMP. | [161 empty] | KENNETH C. PETERS | SR. ENGINEER - PIPELINE | ken_peters@kindermorgan.com | 2053257554 | 2053253508 |  |  |  | REJI GEORGE | DIRECTOR - CODES AND STANDARDS | 7134205433 | reji_george@kindermorgan.com | ON MAY 16, 2013, THIRD PARTY AERIAL PATROL IDENTIFIED A SMALL RING OF BUBBLES APPROXIMATELY 5 FEET IN DIAMETER IN THE VICINITY OF TENNESSEE GAS PIPELINE (TGP) COMPANY'S 526A-200 PIPELINE IN LOUISIANA STATE WATERS. UPON INVESTIGATION, THIS SMALL LEAK WAS CONFIRMED TO BE FROM TGP'S PIPELINE. PERSONNEL WERE MOBILIZED BUT PROGRESS WAS LIMITED DUE TO INCLEMENT WEATHER. THE REPAIR TEAM ARRIVED ON SITE MAY 18. THE FAILED REPAIR CLAMP WAS REMOVED AND A NEW CLAMP WAS INSTALLED IN ITS PLACE. THE PIPELINE WAS PLACED BACK INTO SERVICE ON MAY 23, 2013.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130050 | 16001 | 2013-06-17 14:38 | ORIGINAL FINAL | 13769 | NORTHERN BORDER PIPELINE COMPANY | 700 LOUISIANA STREET | HOUSTON | TX | 77002 | 2013-05-19 04:55 | 2013 |  |  | 47.2546 | -102.7171 | 1047618 | 2013-05-19 07:46 |  | NATURAL GAS |  | 49000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-05-19 04:55 | 2013-05-19 06:44 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-05-19 05:30 | 2013-05-19 05:30 | ONSHORE | ND | 58642 | MANNING | DUNN | MILEPOST | 91.5 | MANNING COMPRESSOR STATION | NORTHERN BORDER MAINLINE VALVE 20 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1982 |  | CARBON STEEL |  | OTHER | [8 empty] | INCOMPLETE CLOSING OF A COMPRESSOR STATION ISOLATION VALVE. | CLASS 1 LOCATION | NO |  | 1098 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 206626 | 161320.709016393 | 500 | 563.776512175962 | 1380 | 1556.02317360566 | 0 | 0 |  |  | 208506 | 168221.548088934 | 163440.508702175 | [8 empty] | 755 |  | 1435 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [7 empty] | YES | [23 empty] | YES | [166 empty] | KURT SMITH | COMPLIANCE SPECIALIST | kurt_smith@transcanada.com | (509) 533-2848 | (509) 533-2993 |  |  |  | KURT SMITH | COMPLIANCE SPECIALIST | (509) 533-2848 | kurt_smith@transcanada.com | ON MAY 19, 2013, A COMPONENT IN ONE OF THE TWO 24VDC BATTERY CHARGERS/INVERTERS SUPPLYING POWER TO THE STATION PROGRAMMABLE LOGIC CONTROLLER (PLC) FAILED AND THE CHARGER BEGAN DELIVERING HIGH AND LOW VOLTAGE SPIKES. THE 24VDC BATTERY CHARGERS / INVERTERS AND ARE CONFIGURED TO SHARE THE LOAD UNDER NORMAL CONDITIONS. THE CHARGER THAT SENSES THE LARGEST VOLTAGE REQUIREMENT WILL TAKE OVER TO SUPPLY THE LOAD CONDITIONS. THE BATTERY CHARGER THAT WAS SPIKING HIGH TOOK OVER THE LOAD AND THEN FAULTED LOW RESULTING IN A LOW 24VDC SUPPLY TO THE CONTROL PANEL. THE LOW VOLTAGE AT THE CONTROL PANEL RESULTED IN VARIOUS DIGITAL INPUT AND OUTPUT CARDS TO FAIL WHICH RESULTED IN THE ESD EVENT. ALTHOUGH THE STATION SUCTION AND DISCHARGE VALVES INDICATED CLOSED, THE DISCHARGE VALVE DID NOT FULLY CLOSE AND HAD TO BE MANUALLY ACTUATED TO FULLY CLOSE. THE CLOSED STATUS, WHICH DROPS THE OUTPUT TO THE VALVE, WAS AN INACCURATE INDICATION CREATED DUE TO THE LOW VOLTAGE SUPPLYING THAT DIGITAL INPUT CARD. GAS CONTROL DISPATCHED FIELD PERSONNEL TO INVESTIGATE THE STATION SHUTDOWN AND WHEN PERSONNEL ARRIVED AT THE SITE, THEY DISCOVERED THAT GAS WAS STILL VENTING FROM THE STATION VENT VALVE. TECHNICIANS MANUALLY CLOSED THE STATION DISCHARGE VALVE TO ISOLATE THE STATION FROM THE MAINLINE AND THE STATION THEN VENTED DOWN TO ATMOSPHERIC PRESSURE. AFTER SHUTTING IN THE STATION, THE FIELD TECHNICIANS DETERMINED WHAT CAUSED THE ESD AND WHY THE STATION DISCHARGE VALVE DID NOT FULLY CLOSE. NUMEROUS FAULTY STATUS, ALARM, AND SHUTDOWN INDICATIONS WERE ALL CORRECTED WHEN THE FAULTY BATTERY CHARGER WAS REMOVED FROM SERVICE. THE BATTERY CHARGER WAS REPAIRED AND RETURNED TO SERVICE AND A FUNCTIONAL ESD TEST WAS PERFORMED WITHOUT ANY ISSUES. THE FOLLOWING IS A TIMELINE OF EVENTS WHEN THIS 24-VOLT CHARGER/INVERTER SYSTEM BEGAN TO EXPERIENCE PROBLEMS. ALL TIMES SHOWN ARE CENTRAL DAYLIGHT TIME (CDT): TIME DESCRIPTION 4:47 UNIT SHUTDOWN AND BEGIN STATION ESD 4:48 STATION SUCTION VALVE CLOSED STATION DISCHARGE VALVE CLOSED STATION VENT VALVE OPEN 4:50 GAS CONTROL CONTACTED THE FIELD ON-CALL TECHNICIAN TO INVESTIGATE THE STATION SHUTDOWN 4:54 STATION BYPASS VALVE OPENED 5:00 FIELD ON-CALL EMPLOYEE TECHNICIAN CONTACTED OTHER FIELD TECHNICIANS THAT WERE CLOSER TO STATION 5 FOR ASSISTANCE 5:30 FIRST EMPLOYEES ARRIVED AT STATION 5 5:55 ONSITE EMPLOYEES MANUALLY CLOSED THE STATION DISCHARGE VALVE AFTER DETERMINING THAT IT HAD NOT FULLY CLOSED DURING THE ESD EVENT. 5:57 STATION WAS NOW BLOWDOWN AND FULLY ISOLATED FROM THE PIPELINE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130051 | 16253 | 2013-06-18 13:35 | SUPPLEMENTAL FINAL | 14210 | OKLAHOMA NATURAL GAS CO | 401 N. HARVEY AVE | OKLAHOMA CITY | OK | 73102 | 2013-05-20 14:56 | 2013 |  |  | 35.3032 | -97.5995 | 1047783 | 2013-05-20 19:27 |  |  |  | 29 | 414 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-05-20 15:50 | 2013-10-31 11:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-05-20 15:25 | 2013-05-20 15:30 | ONSHORE | OK | 73065 | NEWCASTLE | MCCLAIN |  |  | F |  | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | OTHER | SUSPENDED ON BRIDGE TRESTLE |  |  | YES | YES | UNCASED | [20 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | DRAIN LINES | [38 empty] | 1946 |  | CARBON STEEL |  | OTHER | [8 empty] | 1" NIPPLE BROKEN OFF PIPE WHEN IT WAS DISLODGED FROM THE BRIDGE TRESTLE SUSPENSION | CLASS 1 LOCATION | NO |  | 250 |  | NO | NO | NO |  | 0 | 0 | 2296 | 2588.86174391202 | 161 | 125.698770491803 | 2334770 | 2632576.97466614 | 2500 | 2818.88256087981 | 0 | 0 |  |  | 2339727 | 1211034.91169208 | 2638110.41774143 | [8 empty] | 400 |  | 500 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 3300 | NO | YES | [6 empty] | NO | [6 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | AT THE ONSET, THE INCIDENT WAS KNOWN TO BE CAUSED BY TORNADO DAMAGE TO SUPPORTING BRIDGE TRESTLES. THE RESULTING GAS LOSS FROM THE 1" NIPPLE WAS NOT ENOUGH TO TRIGGER ALARMS IN THE CONTROL ROOM. THE LOSS MAY HAVE BEEN DETERMINED BY SCADA OVER TIME, BUT WE RECEIVED NOTIFICATION FROM EMERGENCY RESPONDERS AND DISPATCHED PERSONNEL TO CHECK THE SYSTEM. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [52 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | EF5 TORNADO | YES |  |  | YES | [303 empty] | LEE JAMES | MANAGER WEST REGION TRANSMISSION | lee.james@oneok.com | 405-556-6480 | 405-556-6449 |  |  |  | RICHARD LAMIRAND | MANAGER - REGULATORY COMPLIANCE | 918-732-1338 | richard.lamirand@oneok.com | THE PIPELINE SYSTEM (LINE-F) CONSISTED OF A 20" LINE (SOUTH OF THE BRIDGE) THAT SPLIT INTO TWO LINES (12" AND 16" TRAVERSING THE BRIDGE) AND COMBINED INTO A 24" LINE (NORTH OF THE BRIDGE). THE EF5 TORNADO DAMAGED THE TRESTLE BRIDGE AND CAUSED BOTH LINES TO BE DISLODGED FROM THEIR SUSPENSION ON THE BRIDGE. A 1" NIPPLE WAS BROKEN OFF OF THE 16" LINE, WHEN BOTH LINES FELL ONTO RIVERBED, WHICH CAUSED AN INITIAL UNINTENTIONAL RELEASE. A CONTROLLED RELEASE OCCURRED AFTERWARDS WHEN VALVES ON EITHER END OF THE PIPELINE SECTION OVER THE RIVER WERE CLOSED. BOTH LINES WERE REMOVED FROM SERVICE AND WERE REPLACED BY A SINGLE 24" LINE BORED UNDER THE RIVER. THE INITIAL REPORTING OF THE EVENT WAS DELAYED DUE TO CELLULAR AND VEHICULAR CONGESTION, AS WELL AS AN ADDITIONAL PIPELINE SUPPORTED AT THE BRIDGE BY ANOTHER OPERATOR, WHICH DELAYED COMMUNICATION AND CONFIRMATION OF THE EVENT. THIS SUPPLEMENTAL IS BEING SUBMITTED TO CORRECT THE REPORT TYPE DESIGNATION AS "FINAL". NO OTHER CHANGES WERE MADE OR ARE NECESSARY TO THE PREVIOUS SUBMITTAL.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130052 | 16432 | 2013-06-20 12:21 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2013-05-31 19:44 | 2013 |  |  | 40.4404 | -74.4715 | 1048794 | 2013-05-31 19:44 |  |  |  | 0 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | [9 empty] | YES |  |  |  |  | YES | [6 empty] | 0 | 2013-05-31 18:00 | 2013-05-31 18:00 | ONSHORE | NJ | 08853 | NESHANIC STATION | SOMERSET | MILEPOST | 1789.55 | COMPRESSOR STATION 505 | STATION PIPING | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 30 |  | 0.5 | 50000 | API 5L | DSAW |  | UNKNOWN | COAL TAR | [28 empty] | 1960 | 1960 | CARBON STEEL |  | OTHER | [8 empty] | GAS OR LIQUID VAPORS IGNITED DURING WELD INSTALLATION. | CLASS 2 LOCATION | NO |  | 585 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | $2500 FOR LABOR COST TO MAN SITE UNTIL TEMP WELD CAP WAS INSTALLED. |  | 0 | 0 | 0 | [8 empty] | 0 |  | 800 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | NO | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | REDUCING AIR MOVEMENT AT THE TIME OF THE WELD CAP INSTALLATION AND NOT FULLY REMOVING LIQUIDS MAY HAVE ALLOWED VAPOR TO ACCUMULATE AND CAUSE IGNITION. |  |  | YES |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | JOHNNY LOPEZ | PIPELINE SAFETY SPECIALIST | johnny.lopez@williams.com | 7132152995 | 7132152222 |  |  |  | MARIE SOTAK | MANAGER OF PIPELINE SAFETY | 7132152111 | marie.sotak@williams.com | WILLIAMS CONSTRUCTION AND CONTRACTOR HENKELS AND MCCOY WERE PERFORMING CONSTRUCTION WORK AT COMPRESSOR STATION 505 IN NESHANIC STATION, NJ. THE INCIDENT OCCURRED WHILE WORKERS WERE INSTALLING A TEMPORARY WELD CAP ON A 30"OUT OF SERVICE SECTION OF PIPE AT 505 COMPRESSOR STATION YARD PIPING. DURING THE INSTALLATION PROCESS, A CONTRACT WELDER'S HELPER WAS PRE-HEATING THE PIPE WHEN EITHER GAS VAPORS OR LIQUID VAPORS IGNITED CAUSING THE WELD CAP TO DISLODGE FROM THE LINE UP CLAMP BUT NOT FROM THE HARNESS OF THE SIDE BOOM THAT WAS HOLDING IT. NO VISIBLE FIRE WAS WITNESSED NOR NEEDED TO BE EXTINGUISHED. 3 HENKELS AND MCCOY EMPLOYEES WERE TRANSPORTED TO LOCAL HOSPITALS WITH MINOR INJURIES AND WERE RELEASED LATER THE SAME EVENING. NO DAMAGED OCCURRED TO THE FACILITY AND THE PIPE THAT THE CAP WAS BEING INSTALLED ON IS BEING REMOVED AND SCRAPPED AT A LATER DATE AS PART OF THE PROJECT. PHMSA INSPECTED THE JOB SITE, THE GAS HANDLING PLAN, AND THE CONSTRUCTION INSTALLATION PROCEDURES THE FOLLOWING DAY AND GAVE WILLIAMS THE OK TO INSTALL THE TEMPORARY CAP AND CONTINUE WITH THE JOB.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130053 | 16347 | 2013-06-20 13:49 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | ONE ENERGY PLAZA | DETROIT | MI | 48226 | 2013-05-21 12:35 | 2013 |  |  | 43.5401 | -85.2844 | 1047864 | 2013-05-21 14:26 |  | NATURAL GAS |  | 484 | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-05-21 13:25 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 6 | 2013-05-21 12:46 | 2013-05-21 12:46 | ONSHORE | MI | 49336 | HINTON TOWNSHIP | MECOSTA | MILEPOST | MP 7.92 | HINTON 5 RECEIPT METER STATION |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | FILTER/STRAINER/SEPARATOR | [38 empty] | 2006 |  | CARBON STEEL |  | LEAK |  |  | CRACK | PICKUP TRUCK HIT ASSEMBLY | [5 empty] | CLASS 1 LOCATION | NO |  | 43 |  | NO | NO | NO |  | 30000 | 33826.5907305577 | 0 | 0 | 1935 | 1510.72745901639 | 119000 | 134178.809897879 | 1000 | 1127.55302435192 | 0 | 0 |  |  | 151935 | 79202.7283636821 | 170643.681111805 | [8 empty] | 500 |  | 686 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [260 empty] | ROBERT FRECKELTON | MANAGER- CODES AND STANDARDS | freckeltonr@dteenergy.com | 313-389-7755 | 313-389-7757 |  |  |  | ROBERT H FRECKELTON | MANAGER | 313-389-7755 | No Email Address | THE DRIVER OF A PICK-UP TRUCK SUFFERED AN APPARENT MEDICAL CONDITION AND LOST CONTROL OF THE VEHICLE, CAUSING IT TO LEAVE THE WESTBOUND ROADWAY OF 5 MILE ROAD. THE VEHICLE CROSSED 100TH AVENUE, CONTINUING WESTERLY AND CRASHING THROUGH THE GATE SURROUNDING THE HINTON 5 METER/SEPARATOR ASSEMBLY. THE VEHICLE CROSSED THROUGH THE STATION YARD AND STRUCK THE SEPARATOR PIPING, CRACKING THE 2-INCH STEEL PIPE FROM THE SEPARATOR, STARTING A LEAK AT APPROXIMATELY 500 PSIG. THE DRIVER APPEARS TO HAVE BEEN DECEASED PRIOR TO THE VEHICLE STRIKING THE SEPARATOR PIPING. LEAKING GAS DID NOT IGNITE, AND THERE WERE NO OTHER INJURIES. DTE GAS PERSONNEL WERE ABLE TO CLOSE VALVES AT THE SITE AND THE LEAKING GAS WAS STOPPED WITHOUT FURTHER DAMAGE. THE WRECKAGE OF THE VEHICLE AND THE DESTROYED METER/SEPARATOR PIPING WERE REMOVED, AND THE FACILITY REMAINS OUT OF SERVICE. DISCUSSIONS ARE UNDERWAY BETWEEN THE GAS PRODUCER AND DTE GAS AS TO WHETHER THIS FACILITY IS EVEN REQUIRED TO BE REPLACED AND REACTIVATED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130054 | 16009 | 2013-06-20 16:09 | ORIGINAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2013-05-22 16:00 | 2013 |  |  | 28.2746 | -92.1055 | 1048006 | 2013-05-22 17:00 |  | NATURAL GAS |  | 1000 | 2500 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-05-23 08:00 | 2013-06-10 16:14 |  |  |  |  | NO |  |  |  |  | NO | [7 empty] | 2013-05-22 16:00 | 2013-05-23 08:00 | OFFSHORE | [28 empty] | 225 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SOUTH MARSH ISLAND | 137 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12 |  | 0.375 | 52000 | API | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | KAISER STEEL | OTHER | UNKNOWN | [27 empty] | 1979 | 1979 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 347 |  | NO | NO | NO |  | 0 | 0 | 10000 | 11275.5302435192 | 5000 | 3903.68852459016 | 270000 | 304439.31657502 | 5000 | 5637.76512175962 | 0 | 0 |  |  | 290000 | 151556.45950575 | 325256.300464889 | [8 empty] | 846 |  | 1200 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 1127 | NO |  |  |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | AIR PATROL |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM ISSUES WERE NOT IDENTIFIED AS HAVING ANY CONTRIBUTING EFFECT ON THE CAUSE OF THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  | YES |  |  |  |  | YES |  |  |  | YES |  | YES |  |  |  | YES | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | LOUIS SALINAS | COMPLIANCE ENGINEER |  | 832-320-5305 | 832-320-6305 |  |  |  | LOUIS SALINAS |  | 832-320-5305 |  | 05/22/13, RECEIVED A CALL FROM GAS CONTROL STATING THE PRODUCER (APACHE) AT SOUTH MARSH ISLAND 137 CALLED IN A REPORT OF A POSSIBLE LEAK ON TCO FACILITIES. AFTER INVESTIGATING IT WAS DETERMINED, THE LEAK WAS GAS ONLY WITH NO SHEEN VERY NEAR THE 12", LINE 619 TRANSCANADA OFFSHORE LATERAL. EXTERNAL AND INTERNAL NOTIFICATIONS WERE MADE AS WELL AS CONTACT WITH THE PRODUCER AT THE FACILITY. THE PRODUCER HAD ALREADY SHUT-IN GAS PRODUCTION FROM THAT FACILITY WHICH IS THE ONLY PRODUCTION ON THE LATERAL. PLANS ARE IN PLACE TO HAVE A DIVE BOAT CLOSE AN ISOLATION VALVE AND A INVESTIGATION DIVE AT THE LOCATION OF THE LEAK. THE NRC INCIDENT NUMBER IS 1048006. THE PIEPLINE WAS REPAIRED ON 6/14/2013 BY INSTALLING A REPAIR CLAMP OVER THE LEAK AREA. THE PIPELINE WAS SUBSEQUENTLY PLACED BACK INTO SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130055 | 16176 | 2013-06-21 08:15 | SUPPLEMENTAL FINAL | 32005 | CROSSTEX LIG, LLC | 1722 ROUTH STREET SUITE 1300 | DALLAS | TX | 75201 | 2013-05-22 08:34 | 2013 |  |  | 29.6843 | -91.1557 | 1047993 | 2013-05-22 15:35 |  | NATURAL GAS |  | 23 | 10 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-05-22 12:35 | 2013-11-05 06:59 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-05-22 14:15 |  | ONSHORE | LA | 70381 | MORGAN CITY | ST MARY |  |  | GREENWOOD 6 INCH | PIPELINE #1039 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | WATER CANAL - SHIP CHANNEL | 6 |  | YES | [6 empty] | YES | UNCASED | INTRACOASTAL CHANNEL | 9 | BELOW WATER, PIPE BURIED BELOW BOTTOM (NOT IN BORED/DRILLED CROSSING) | [11 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 |  | 0.28 | 35000 | API 5L | SEAMLESS |  | UNITED STATES STEEL | COAL TAR | [28 empty] | 1978 | 1978 | CARBON STEEL |  | RUPTURE | [7 empty] | 42 |  | CLASS 3 LOCATION | NO |  | 87 |  | NO | NO | NO |  | 0 | 0 | 30 | 33.8265907305577 | 90 | 70.266393442623 | 311000 | 350668.990573449 | 0 | 0 | 0 | 0 |  |  | 311120 | 161054.695375581 | 350773.083557622 | [8 empty] | 350 |  | 450 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 2397 | NO |  |  | YES |  |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A LEAK CREATED BY LARGE SHIP OR BARGE OPERATING IN THE INTRACOASTAL CANAL | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ROUTINE OR NORMAL FISHING OR OTHER MARITIME ACTIVITY NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | FISHING OR MARITIME ACTIVITY | [103 empty] | ROUTINE OR NORMAL FISHING OR OTHER MARITIME ACTIVITY NOT ENGAGED IN EXCAVATION | [261 empty] | WILLIAM WORLEY | DOT COMPLIANCE MANAGER | bill.worley@crosstexenergy.com | 214 721 9449 | 214 953 9501 |  |  |  | WILLIAM WORLEY | DOT COMPLIANCE MANAGER | 214 721 9449 | bill.worley@crosstexenergy.com | CROSSTEX WAS NOTIFIED BY THE COAST GUARD THAT BUBBLES WERE SEEN AT THE SURFACE OF THE WATER OF THE INTRACOASTAL CANNAL AND THAT THE BUBBLES MAY BE COMING FROM OUR PIPELINE. CROSSTEX STARTED AN INVESTIGATION TO DETERMINE IF THE LEAK BELONGED TO CROSSTEX. ONCE CROSSTEX DETERMINED IT WAS A CROSSTEX PIPELINE LEAK WE ATTEMPTED TO PLACE ON CLAMP ON THE LEAK WITH DIVERS. THAT ATTEMPT WAS UNSUCCESSFUL AND WAS NOT FEASIBLE DUE TO EXTENT OF THE DAMAGE TO THE PIPELINE. CROSSTEX THEN TOOK THE PIPELINE OUT OF SERVICE. WE ARE NOW EVALUATING THE BEST WAY TO MAKE REPAIRS THAT WOULD HAVE LEST IMPACT TO THE PUBLIC, ENVIRONMENT AND THE END USER. PIPELINE WAS REPAIRED BUT REPLACING 484.6 FEET OF PIPELINE WITH LIKE KIND MATERIAL AND RETURNED PIPELINE TO SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130057 | 16378 | 2013-06-27 16:41 | SUPPLEMENTAL FINAL | 5304 | FLORIDA GAS TRANSMISSION CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2013-05-29 23:26 | 2013 |  |  | 28.0545 | -82.3716 | 1048703 | 2013-05-30 00:07 |  | NATURAL GAS |  | 1443.2 | 2894.25 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-05-30 01:25 | 2013-06-11 18:35 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-05-29 23:26 | 2013-05-29 23:26 | ONSHORE | FL | 33617 | TAMPA | HILLSBOROUGH | SURVEY STATION NO. | 3551+05 | FLORIDA GAS TRANSMISSION | ST. PETE LATERAL | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 72 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 14 |  | 0.25 | 42000 | X-42 | LONGITUDINAL ERW - LOW FREQUENCY |  | REPUBLIC | COLD APPLIED TAPE | [28 empty] | 1959 | 1959 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | YES | METHOD2 | 265 |  | NO | NO | NO |  | 0 | 0 | 10911 | 12302.7310487039 | 6061 | 4732.0512295082 | 130000 | 146581.89316575 | 0 | 0 | 0 | 0 |  |  | 146972 | 77838.1673534828 | 163616.675443962 | [8 empty] | 675 |  | 750 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | YES | NO | NOT MANDATED |  |  | MANUAL | MANUAL | 33264 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS TOO SMALL TO DETECT WITH SCADA DATA. | [12 empty] | YES | 2 | 0 | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [52 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | LIGHTNING STRIKE OCCURED FROM A THIRD PARTY GROUNDING ROD. | NO | [306 empty] | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | AFTER DISCUSSIONS WITH THE PHMSA SOUTHERN REGION, THIS SUPPLEMENTAL FINAL REPORT IS SUBMITTED TO CHANGE THE CAUSE FROM G8 - OTHER INCIDENT CAUSE, TO G2 - OTHER NATURAL FORCE DAMAGE. THIS IS AN INTERACTING FAILURE. THERE WERE TWO CAUSES. LIGHTNING STRIKE ON A THIRD PARTY GROUNDING ROD. A LEAK OCCURRED ON WEDNESDAY MAY 29, 2013 ON THE ST. PETE LATERAL BETWEEN MLV 24-70 AND MLV 24-8. AFTER THE LEAK WAS IDENTIFIED, THIS SECTION OF PIPE WAS ISOLATED AND BLOWNDOWN. THE AFFECTED PIPE HAD A 7.5' SECTION CUT-OUT AND REPLACED ON JUNE 1, 2013.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130058 | 16141 | 2013-06-28 11:46 | SUPPLEMENTAL FINAL | 22435 | WEST TEXAS GAS INC | 211 NORTH COLORADO | MIDLAND | TX | 79701 | 2013-05-31 13:50 | 2013 |  |  | 28.839 | -99.9201 | 1048880 | 2013-05-31 15:12 |  | NATURAL GAS |  | 126.8 | 344.5 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-05-31 14:41 | 2013-05-31 20:30 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2013-05-31 13:50 | 2013-05-31 13:50 | ONSHORE | TX | 78872 | LA PRYOR | ZAVALLA | MILEPOST | 3.21 | TGU SYSTEM 6 / 2 PIPELINE | FRIO JUNCTION TO CHITTIM | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 40 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 |  | 0.203 | 24000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1940 | 1940 | CARBON STEEL |  | MECHANICAL PUNCTURE | 2 | 3.5 | [7 empty] | CLASS 1 LOCATION | NO |  | 102 |  | NO | NO | NO |  | 792000 | 893021.995286725 | 1378 | 1553.76806755695 | 508 | 396.614754098361 | 3886 | 4381.67105263158 | 3200 | 3608.16967792616 | 0 | 0 |  |  | 800972 | 414712.616647136 | 902962.218838938 | [8 empty] | 295 |  | 397 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | CHECK VALVE | 59664 | NO |  |  | YES | YES |  | YES | PIPELINE NOT CONFIGURED FOR PIGGING TRAPS. | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | WEST TEXAS GAS DOES NOT HAVE A CONTROL ROOM THAT MONITORS THIS SYSTEM. SCADA ALARMS ARE SENT VIA CELL PHONE TO EMPLOYEES. | [12 empty] | NO |  |  | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [10 empty] | YES |  |  | YES | PRIVATE LANDOWNER | [7 empty] | CONTRACTOR | TRENCHER | NATURAL GAS | YES | 1364111981 | TEXAS EXCAVATION SAFETY SYSTEM, INC. | UTILITY OWNER | YES | YES | YES | 7 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO MAINTAIN CLEARANCE | [263 empty] | RAY REED | DIRECTOR OF INTEGRITY MANAGMENT | rreed@wtghugoton.com | 806.358.1321 | 806.354.0797 |  |  |  | BART BEAN | OPERATIONS MANAGER | 806.358.1321 | bbean@westtexasgas.com | A SECOND PARTY CONTRACTOR WAS AWARD A CAPITOL PROJECT TO REPLACE 2.5 MILES OF 6.625 INCH PIPELINE IN ZAVALLA COUNTY TEXAS FOR WEST TEXAS GAS (WTG). THE PROJECT WAS ON WTG'S TGU SYSTEM AND THE 6/A SUB-SYSTEM. THE SCOPE OF THE PROJECT INCLUDES THE PARALLEL INSTALLATION OF NEW PIPE APPROXIMATELY SEVEN FOOT FROM THE EXISTING PIPELINE. THE REPLACEMENT PIPELINE WILL BE CONSTRUCTED WHILE THE EXISTING PIPELINE REMAINS IN-SERVICE, THE EXCEPTION WOULD BE FOR THE TIE-IN ON BOTH THE UPSTREAM AND DOWNSTREAM POINTS. WTG EMPLOYEES LOCATED THE EXISTING PIPELINE UTILIZING A CONDUCTIVE PIPELINE LOCATOR AND "POT-HOLED" THE PIPE AT APPROXIMATELY 300 FOOT INTERVALS TO ENSURE THE ACCURACY OF THE PIPE LOCATION. THIS CENTERLINE WAS CLEARLY MARKED. THE CENTERLINE OF THE NEW PIPELINE LOCATION WAS CLEARLY STAKED. IN ADDITION "LINE-UP MARKERS" WAS ALSO IN PLACE FOR THE TRENCHER OPERATOR. APPROXIMATELY 2.25 MILES OF THE PROJECT WAS COMPLETED WITHOUT INCIDENT. ON MAY 31, 2013 PRIOR TO 1:50 PM THE TRENCHER OPERATOR BECAME IN-ATTENTIVE AND ALLOWED THE MACHINE TO START DRIFTING TOWARD THE PIPELINE THAT WAS IN OPERATION. AT APPROXIMATELY 1:50 PM, THE TRENCHER CAME INTO CONTACT WITH THE PRESSURIZED PIPELINE. WHEN THE TRENCHER STRUCK THE PIPELINE, IT PLACED A GOUGE IN THE PIPELINE. THE GOUGE INCLUDED METAL LOSS OF AN AREA APPROXIMATELY 2 INCHES BY 3 INCHES WHICH ALLOWED THE RELEASE OF GAS. THE OPERATOR WAS ABLE TO DISMOUNT THE TRENCHER AND MOVE TO A SAFE DISTANCE PRIOR TO THE GAS BEING IGNITED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130059 | 17119 | 2013-07-02 10:49 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION LP (SPECTRA ENERGY CORP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2013-06-04 13:00 | 2013 |  |  | 28.3455 | -92.7647 | 1049291 | 2013-06-04 16:30 |  | NATURAL GAS |  | 6409 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-06-04 13:00 | 2013-06-07 13:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-06-04 13:00 | 2013-06-04 13:00 | OFFSHORE | [28 empty] | 190 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EAST CAMERON | 293 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 |  | 0.375 | 52000 | API 5LX | SEAMLESS |  | U.S. STEEL | OTHER | CONCRETE AND SOMASTIC | [27 empty] | 1975 | 1975 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 419 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 22432 | 17513.5081967213 | 787000 | 887384.230164965 | 0 | 0 | 0 | 0 |  |  | 809432 | 425489.826085277 | 904897.738361686 | [8 empty] | 964 |  | 1438 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 60334 | NO |  |  |  | YES |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | NOTIFICATION FROM THIRD PARTY THAT SPOTTED THE BUBBLES ON THE SURFACE |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS TOO SMALL TO BE IDENTIFIED BY THE CONTROLL ROOM PERSONNEL. A REVIEW OF OPERATING RECORDS FOUND ABNORMAL OPERATING CONDITIONS DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | deteschendorf@spectraenergy.com | 713-627-5573 | 713-386-4468 |  |  |  | RICK KIVELA | DIRECTOR OF TECHNCIAL OPERATIONS | 713-627-6388 | rwkivela@spectraenergy.com | A SURFACE SHEEN WAS DISCOVERED IN EAST CAMERON 293 ON MAY 27, 2013 BY A PLATFORM OPERATOR. THIS INITIAL OBSERVATION WAS REPORTED AS A SURFACE SHEEN OF UNKNOWN ORIGIN BY THE ENVIRONMENTAL RESPONSE CONTRACTOR O'BRIEN TO THE NATIONAL RESPONSE CENTER (REPORT 1048450). SURFACE BUBBLES, A TYPICAL INDICATOR OF A NATURAL GAS PIPELINE LEAK, WERE NOT OBSERVED. AS A PRECAUTION, TEXAS EASTERN TRANSMISSION SHUT IN THE SEGMENT OF ITS PIPELINE NEAREST THE SHEEN ON MAY 27, 2013 UNTIL THE SOURCE OF THE SHEEN COULD BE DETERMINED. AFTER SHUT IN THERE WAS NO PRESSURE DROP THAT WOULD HAVE INDICATED A LEAK. TEXAS EASTERN TRANSMISSION DISPATCHED A DIVE BOAT MAY 28, 2013 TO THE SITE TO DETERMINE THE CAUSE OF THE SHEEN. DUE TO INCLEMENT CONDITIONS THE DIVE BOAT WAS UNABLE TO REACH THE LOCATION UNTIL JUNE 3, 2013. ONCE THE DIVERS ARRIVED ON LOCATION AND WERE ABLE TO DIVE, THEY DETERMINED THERE WAS A SMALL AMOUNT OF BUBBLES ORIGINATING FROM A PINHOLE LEAK DUE TO INTERNAL CORROSION ON TEXAS EASTERN TRANSMISSION, L.P. 16-INCH LINE 41-A-5 NATURAL GAS PIPELINE. THE METHOD OF REPAIR TO THE PIPELINE WAS INSTALLATION OF CLAMP.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130060 | 16031 | 2013-07-03 13:01 | ORIGINAL | 2714 | DOMINION TRANSMISSION, INC | 925 WHITE OAKS BOULEVARD | BRIDGEPORT | WV | 26330 | 2013-06-10 06:10 | 2013 |  |  | 39.8907 | -77.7191 | 1049844 | 2013-06-10 07:19 |  |  |  | 23856 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-06-10 06:10 | 2013-06-17 17:00 |  |  |  |  | NO |  |  |  |  | NO | [9 empty] | ONSHORE | PA | 17202 | CHAMBERSBURG | FRANKLIN |  |  | CHAMBERSBURG COMPRESSOR STATION |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 1996 |  | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | DURING VENTING OF GAS, THE SILENCER FAILED. |  |  |  | CLASS 2 LOCATION | NO |  | 390 |  | NO | NO | NO |  | 3000 | 3382.65907305577 | 0 | 0 | 102000 | 79635.2459016393 | 350000 | 394643.558523174 | 0 | 0 | 0 | 0 |  |  | 455000 | 265266.011937723 | 477661.463497869 | [8 empty] | 1002 |  | 1250 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | NO | YES | NO | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PURCHASE POWER WAS LOST AT THE SITE. THE EMERGENCY GENERATOR SHUTDOWN ON LOW OIL PRESSURE SOMETIME AFTER 4 AM, 15 MIN LATER THE UPS SYSTEM WAS DRAINED AND THE FACILITY WAS WITHOUT POWER. DURING THIS TIME, GAS VENTED OUT THE SILENCER AND CAUSED THE SILENCER TO RUPTURE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | FAILURE OF EQUIPMENT BODY (EXCEPT COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL | MATERIAL/WELD/EQUIP FAILURE | FAILURE OF EQUIPMENT BODY | [166 empty] | FAILURE OF EQUIPMENT BODY (EXCEPT COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL | [35 empty] | YES | FAILURE DUE TO SLUG OF WATER DURING COMMISSIONING OF THE UNIT | [161 empty] | ERIC TAYLOR | COMPLIANCE ENGINEER III | eric.v.taylor@dom.com | 304-627-3034 |  |  |  |  | ERIC TAYLOR | COMPLIANCE ENGINEER III | 304-627-3034 | eric.v.taylor@dom.com | A REVIEW OF THE CHAMBERSBURG SILENCER DAMAGE APPEARS TO HAVE OCCURRED FROM FATIGUE THAT LIKELY HAD EXISTED FOR QUITE SOME TIME. THE HISTORY OF THIS UNIT INDICATES THAT DAMAGE OCCURRED DURING COMMISSIONING OF THIS UNIT IN 1996 THAT LIKELY TOOK A SLUG OF HYDRO-TEST WATER AND PROBABLY CRACKED/DAMAGED THE INTERNAL 44" DIAMETER FORMED & DISHED HEAD. REPAIRS TO THE UPPER SECTION WERE REPAIRED AND THE ORIFICE PLATE WAS REDESIGNED/REPLACED AT THIS SAME TIME, BUT NO DAMAGE WAS IDENTIFIED TO THE LOWER SECTION. THE SILENCER'S CURRENT DESIGN HAS THE DISHED HEAD ABSORBING THE MAJORITY OF THE DISCHARGE GAS FORCES. THE DISHED HEAD FAILED DURING THE 6/10/2013 VENTING EVENT CAUSING THE ENTIRE EASTERN WALL OF THE VESSEL TO FAIL. THIS ALLOWED ALL THE GAS TO VENT OUT THE SIDE OF THE SILENCER UNIT.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20130061 | 16544 | 2013-07-09 15:44 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2013-06-24 18:52 | 2013 |  |  | 28.9859 | -91.4937 | 1051674 | 2013-06-24 20:01 |  | NATURAL GAS |  | 50 | 10326 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-06-28 15:30 | 2014-02-19 12:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-06-25 13:30 | 2013-06-26 12:30 | OFFSHORE | [28 empty] | 35 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EUGENE ISLAND | 119 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1959 |  | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 434 |  | NO | NO | NO |  | 0 | 0 | 37350 | 42114.1054595444 | 180 | 140.532786885246 | 200000 | 225510.604870385 | 10000 | 11275.5302435192 | 0 | 0 |  |  | 247530 | 128168.266438515 | 279040.773360334 | [8 empty] | 735 |  | 1168 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 169593 | NO | [5 empty] | YES | THIS PIPELINE HAS A LAUNCHER AND RECEIVER DESIGNED FOR CLEANING SPHERES ONLY. | YES |  |  |  |  | YES | DESIGN OF PIPING SYSTEM. | OFFSHORE GATHERING | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS VERY SMALL AND A MINIMAL PRESSURRE LOSS COULD NOT BE DETECTED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | GASKET | [7 empty] | YES | [172 empty] | JOHNNY LOPEZ | PIPELINE SAFETY SPECIALIST |  | 7132152995 | 7132152222 |  |  |  | MARIE SOTAK | PIPELINE SAFETY MANAGER | 7132152111 | marie.sotak@williams.com | LOCATING AND VERIFING THE LEAK (JUNE 24, 2013) - TRANSCO RECEIVED INFORMATION FROM APACHE CORP AT 7:30PM ON THE EVENING THE LEAK WAS IDENTIFIED. APACHE PLOTTED OVER TRANSCO'S 10 " OFFSHORE PIPELINE BETWEEN THE EI 119 - EI 120 PLATFORM, WHICH TIES-IN AT THE 16" SS128 - EI 129A. APACHE'S MESSAGE TO TRANSCO WAS SIGHTING OF BUBBLES, NO SHEEN REPORTED. GAS CONTROL WAS NOTIFIED (APACHE ALREADY HAD NOTIFIED THE NRC # 1051561) AND TRANSCO RESPONDED WITH SCHEDULING THE INVESTIGATION THE NEXT MORNING. FIELD INVESTIGATION AND THE REPAIR OF THE LEAK (FEBURARY 2014) - TRANSCO PLOTTED THE 16" LINE, LOCATED AND IDENTIFIED THE LEAK AS BEING A 16" CHECK VALVE. THE LEAKING VALVE WAS RETRIEVED AND DISASSEMBLED, RESULTS SHOWED THAT DEBRIS WAS FOUND IN THE VALVE FLANGE RING JOINT GROOVES, IDENTIFIED AS THE ORGIN OF THE LEAK. THE VALVE FLANGE RING JOINT GROOVES WERE CLEANED AND THE VALVE REASSEMBLED. IN SUMMARY, THE TRANSCO RCA CONCLUDED THAT THE 16" CHECK VALVE LEAK WAS THE RESULT OF IMPROPER INSTALLATION OF THE 16" CHECK VALVE COVER FLANGE, MORE THAN LIKELY ASSOCIATED WITH THE VALVE CLAPPER REMOVAL DURING A 1980 REPAIR. THE 16" LINE WAS REPESSURED AND THE CHECK VALVE SHOWED NO SIGNS OF LEAKING. THE LINE IS NOW IN FULL OPERATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130062 | 16326 | 2013-07-09 15:52 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2013-06-15 15:43 | 2013 |  |  | 34.9926 | -107.3158 | 1050541 | 2013-06-15 17:05 |  | NATURAL GAS |  | 29163 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | [7 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-06-15 14:12 | 2013-06-15 14:12 | ONSHORE | NM | 87026 | MESITA | CIBOLA | MILEPOST | 300 | LAGUNA COMPRESSOR STATION |  | YES | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 1953 |  | CARBON STEEL |  | OTHER | [8 empty] | COMPRESSOR STATION ESD; PLEASE SEE PART H NARRATIVE; | CLASS 1 LOCATION | YES | METHOD2 | 599 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 89778 | 70093.0696721311 | 0 | 0 | 200 | 225.510604870385 | 0 | 0 | 0 |  | 89978 | 72772.183350933 | 70318.5802770015 | [8 empty] | 791 |  | 836 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM NOT INCIDENT CAUSE; CONTROL ROOM NOT A CONTRIBUTING FACTOR; | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [204 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | [6 empty] | YES | INVESTIGATION COULD NOT DETERMINE REASON FOR POWER GAS ISOLATION VALVE TO BE IN CLOSED POSITION; FOLLOWING INVESTIGATION, ALL BLOCK VALVES, ALL VENT VALVES, AND ALL POWER GAS ISOLATION VALVES WERE CONFIRMED TO BE IN THE CORRECT OPERATING POSITION; | NON-ROUTINE OPERATING CONDITIONS (ABNORMAL OPERATIONS OR EMERGENCIES) | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | WM. MARTIN MULLER | COORDINATOR - OPS SR II | martin_muller@kindermorgan.com | 205 325 3863 | 205 325 3508 |  |  |  | REJI GEORGE | DIRECTOR ENGINEERING COMPLIANCE CODES STANDARDS | 713 420 5433 | reji_george@kindermorgan.com | AMBITROL COOLANT LEAKING FROM ENGINE COMPONENT ON TO TURBO CHARGER INSULATION RESULTED IN FLASH FIRE (BURNING COOLANT, NOT NATURAL GAS); UNIT WAS RUNNING AT THE TIME; FIRE EYE SAW FLASH FIRE; FULL STATION ESD OCCURRED; 30-INCH DISCHARGE VALVE DID NOT CLOSE THEREFORE ALLOWING NATURAL GAS RELEASE THROUGH VENT SYSTEM; INVESTIGATION FOUND CLOSED POWER GAS ISOLATION VALVE RENDERING 30-INCH DISCHARGE VALVE INOPERABLE; NOT AN EQUIPMENT FAILURE; INVESTIGATION COULD NOT DETERMINE REASON FOR ISOLATION VALVE TO BE CLOSED; FOLLOWING INITIAL INVESTIGATION, ALL BLOCK VALVES, VENT VALVES, AND POWER GAS VALES WERE CONFIRMED TO BE IN CORRECT OPERATING POSITION;
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130063 | 16147 | 2013-07-10 09:34 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2013-06-12 00:08 | 2013 |  |  | 33.2325 | -90.5793 | 1050121 | 2013-06-12 05:11 |  | NATURAL GAS |  | 3235 | 314 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-06-12 00:20 | 2013-06-12 05:20 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-06-12 00:10 | 2013-06-12 00:10 | ONSHORE | MS | 38754 | ISOLA | HUMPHREYS | SURVEY STATION NO. | 843-1B - 0+00 | STATION 843 ON 800 PIPELINE SYSTEM | 843-1B | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1950 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE OPENED PREMATURELY; RELIEF VALVE DID NOT SEAT; STATION ESD OCCURRED; | CLASS 1 LOCATION | NO |  | 634 |  | NO | NO | NO |  | 0 | 0 | 1226 | 1382.38000785546 | 29308 | 22881.8606557377 | 0 | 0 | 1800 | 2029.59544383346 | 0 | 0 | 0 |  | 32334 | 25288.8506979769 | 26293.8361074266 | [8 empty] | 931.7 |  | 936 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM WAS NOT EVENT CAUSE; CONTROL ROOM WAS NOT A CONTRIBUTING FACTOR; | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | RELIEF VALVE OPERATED PREMATURELY; RELIEF VALVE DID NOT SEAT; INVESTIGATION FOUND A SMALL AMOUNT OF SLUDGE IN O-RING OF RELIEF VALVE; SLUDGE MAY HAVE CONTRIBUTED TO THE EVENT; |  |  |  | YES | RELIEF VALVE OPERATED PREMATURELY; RELIEF VALVE DID NOT SEAT; ESD OCCURRED; INVESTIGATION FOUND A SMALL AMOUNT OF SLUDGE IN O-RING OF RELIEF VALVE; SLUDGE MAY HAVE CONTRIBUTED TO THE EVENT; | NORMAL OPERATING CONDITIONS | NO | [150 empty] | WM. MARTIN MULLER | COORDINATOR - OPS SR II | martin_muller@kindermorgan.com | 205 325 3863 | 205 325 3508 |  |  |  | REJI GEORGE | DIRECTORENGINEERINGCOMPLIANCECODESANDSTANDARDS | 713 420 5433 | reji_george@kindermorgan.com | TGP COMPRESSOR STATION 843; OPERATOR WAS ON SITE; EVENT OCCURRED AFTER STATION CAME ON LINE; RELIEF VALVE OPERATED PREMATURELY; RELIEF VALVE DID NOT SEAT; STATION ESD OCCURRED; INVESTIGATION AND REPAIR OF RELIEF VALVE FOUND A SMALL AMOUNT OF SLUDGE IN O-RING OF RELIEF VALVE WHICH MAY HAVE CONTRIBUTED TO THE EVENT; PRESSURE TRANSMITTERS WERE INSPECTED AND FOUND TO BE IN CALIBRATION; RELIEF VALVE WAS TESTED AND CONSISTENTLY LIFTED DURING TESTING;
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130064 | 31666 | 2013-07-12 12:34 | SUPPLEMENTAL FINAL | 1007 | TALLGRASS INTERSTATE GAS TRANSMISSION, LLC | 370 VAN GORDON ST | LAKEWOOD | CO | 80228 | 2013-06-13 19:55 | 2013 |  |  | 42.0067 | -104.0537 | 1050393 | 2013-06-13 23:41 |  | NATURAL GAS |  | 6142 | 2141 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-06-13 20:30 | 2013-06-17 15:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-06-13 20:03 | 2013-06-13 20:15 | ONSHORE | WY | 82240 | UNINCORPORATED | GOSHEN | MILEPOST | 798+01.5 | LINGLE TO MITCHELL 12" | 700-003-00-00 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 |  | 0.219 | 42000 | API-5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | REPUBLIC STEEL | COAL TAR | [28 empty] | 1963 | 1963 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 120 | 24 |  | CLASS 1 LOCATION | NO |  | 290 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 29024 | 22660.131147541 | 200 | 225.510604870385 | 5216 | 5881.31657501964 | 226252 | 255111.126865672 | EMPLOYEE & VEHICLE EXPENSES, OT, MATERIALS & SUPPLIES |  | 260692 | 143398.720506613 | 283878.085193103 | [8 empty] | 815 |  | 865 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 42065 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED |  | YES | [15 empty] | STRESS CORROSION CRACKING | [5 empty] | YES | [63 empty] | YES | [6 empty] | YES | [50 empty] | COMBINATION TOOL | 2010 |  |  |  |  | NO |  |  | NO | [13 empty] | NO | [63 empty] | JENNIFER ECKELS | COMPLIANCE MANAGER | jennifer.eckels@tallgrassenergylp.com | 3037633486 |  |  |  |  | CRAIG MEIS | EHS AND COMPLIANCE VICE PRESIDENT | 3037633442 | craig.meis@tallgrassenergylp.com | AT APPROXIMATELY 19:55 LOCAL TIME ON JUNE 13, 2013, A PIPE SECTION OF THE TIGT 12" LINGLE TO MITCHELL MAINLINE IN UNINCORPORATED (CLASS 1 AREA) GOSHERN COUNTY, WY RUPTURED DUE TO THEN-UNKNOWN CAUSES. THE PIPELINE WAS OPERATING AT 815 PSIG AT THE TIME OF THE INCIDENT, WITH AN ESTABLISHED MAXIMUM ALLOWABLE OPERATING PRESSURE (MAOP) OF 865 PSIG. THERE WAS NO FIRE, EXPLOSION, INJURY/DEATH, OR MAJOR PRIVATE PROPERTY DAMAGE ASSOCIATED WITH THE RUPTURE. THE RUPTURE WAS IDENTIFIED BY TALLGRASS GAS CONTROLER USING SCADA AT 20:03 WHEN PRESSURE DROPPED FROM 815 TO 545 PSIG AT THE HENRY-TORRINGTON STATE LINE CHECK METER. GAS CONTROL RECEIVED A CALL AT 20:09 FROM A SOURCEGAS EMPLOYEE WHO STATED THE 12" LINGLE TO MITCHELL PIPELINE HAD RUPTURED. AT 20:15 THE AREA SUPERVISOR WAS CONTACTED AND CONFIRMED THAT A LOCAL OPERATOR WAS ON THE SCENE. HE BEGAN SHUTTING IN THE SEGMENT VIA MAINLINE VALVES. GAS CONTOL CLOSED THE GUERNSEY TO HENRY/TORRINGTON FEED AT THE GUERNSEY COMPRESSOR STATION AT 20:18. AT 20:24 THE DOWNSTREAM MAINLINE VALVE NEAR HENRY HAD BEEN CLOSED. AT 20:30, THE UPSTREAM MANINLINE VALVE NEAR TORRINGTON WAS CLOSED. FIELD OPERATIONS SUPERVISED AN INTENTIONAL AND CONTROLLED BLOWDOWN OF THE LOCAL SEGMENT UNTIL IT WAS SAFE TO APPROACH THE RUPTURE SITE TO BEGIN INVESTIGATION. FIELD INVESTIGATION REVEALED A CATASTROPHIC RUPTURE OF A PIPE SECTION APPROXIMATELY 10 FEET IN LENGTH, WITH COMPLETE SEPARATION OF THE RUPTURED SECTION FROM THE PIPELINE. THE PIPE (API-5L X42, ERW, MANUFACTURED IN 1963 BY REPUBLIC STEEL) WAS SENT TO A METALLURGICAL FIRM FOR STUDY.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130065 | 16051 | 2013-07-16 11:34 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2013-06-19 08:00 | 2013 |  |  | 29.5962 | -92.3106 | 1050938 | 2013-06-19 08:45 |  | NATURAL GAS |  | 13111 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | UNDERGROUND VALVE LEAKING | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-06-19 08:00 | 2013-06-19 08:00 | ONSHORE | LA | 70533 | ERATH | VERMILION | MILEPOST | 2.04 | ERATH 3" | INDEX 205-07-02 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | FARM TAP RISER (ABANDONED) | 1940 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 44 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 50000 | 39036.8852459016 | 50 | 56.3776512175962 | 400 | 451.02120974077 | 0 | 0 |  |  | 50450 | 40704.2209412386 | 39544.28410686 | [8 empty] | 300 |  | 460 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 26000 | NO | [5 empty] | YES | LINE HAS DRESSER COUPLINGS AND CHANGES PIPE DIAMETER | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [260 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 270.688.6357 | 270.688.5871 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 270.688.6361 | jeff.mcmaine@bwpmlp.com | DURING AN EXTENSIVE INVESTIGATION TO IDENTIFY THE CAUSE OF AN UNACCOUNTED FOR GAS DISCREPENCY, THE CAUSE WAS EVENTUALLY IDENTIFIED AS A PIPELINE LEAK. APPARENT CAUSE WAS FROM SURFACE ACTIVITY CONDUCTED IN AN ACTIVE SUGAR CANE FIELD.
2021-02-26 10:37 | YES | YES | GT (Gas Transmission) | 20130066 | 16345 | 2013-07-17 15:41 | SUPPLEMENTAL FINAL | 5304 | FLORIDA GAS TRANSMISSION CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2013-06-18 05:20 | 2013 |  |  | 30.7824 | -90.0515 | 1050774 | 2013-06-18 06:30 |  | NATURAL GAS |  | 86000 | 0 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 |  | YES |  | 2013-06-18 06:10 | 2013-07-19 19:29 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 55 | 2013-06-18 05:23 | 2013-06-18 06:10 | ONSHORE | LA | 70438 | FRANKLINTON | WASHINGTON | SURVEY STATION NO. | 27+55 - 27+93 | FLORIDA GAS TRANSMISSION | LAMEB | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 |  | 0.344 | 60000 | API 5L | DSAW |  | KAISER | OTHER | BUCOTE | [27 empty] | 1966 | 1966 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 897 | 94 |  | CLASS 1 LOCATION | NO |  | 646 |  | YES | NO | YES |  | 246481 | 277920.396995287 | 0 | 0 | 354000 | 276381.147540984 | 2199000 | 2479489.10054988 | 263000 | 296546.445404556 | 0 | 0 |  |  | 3062481 | 1688383.24728439 | 3330337.09049071 | [8 empty] | 952 |  | 975 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 63360 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE MAOP WAS NOT EXCEEDED. | [12 empty] | YES | 3 | 0 | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  |  |  |  | YES | [6 empty] | YES |  |  | YES | YES | 1966 | NO | YES | YES | YES |  |  | 2013 | 2009 |  |  | YES | [190 empty] | YES | [6 empty] | YES | [50 empty] | COMBINATION TOOL | 2010 |  |  |  |  | NO |  |  | NO | [13 empty] | NO | [63 empty] | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | THIS SUPPLEMENTAL/FINAL REPORT IS BEING SUBMITTED TO PROVIDE UPDATES TO PART A, QUESTION 15(B).
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130067 | 16483 | 2013-07-19 08:33 | SUPPLEMENTAL FINAL | 13063 | NATIONAL FUEL GAS SUPPLY CORP | 6363 MAIN STREET | WILLIAMSVILLE | NY | 14221-5887 | 2013-06-22 00:04 | 2013 |  |  | 42.0641 | -78.7248 | 1051310 | 2013-06-22 07:55 |  | NATURAL GAS |  | 6486 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-06-22 06:04 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-06-22 00:10 | 2013-06-22 03:00 | ONSHORE | NY | 14753 | RED HOUSE | CATTARAGUS | MILEPOST | WELL LINE | CONNECTOR LINE FOR WELL 7013 | FW7013 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTERSTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | PIPE | PIPE BODY | 4 |  | 0.237 | 35000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | EXTRUDED POLYEHYLENE | [28 empty] | 1973 | 1973 | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | PIPE WALL RUPTURE. | 3 | 3 |  | CLASS 1 LOCATION | NO |  | 118 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 25000 | 19518.4426229508 | 20000 | 22551.0604870385 | 3000 | 3382.65907305577 | 0 | 0 |  |  | 48000 | 32139.9173245078 | 45452.1621830451 | [8 empty] | 1350 |  | 1440 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS CONTROL ACTIONS WERE NOT A CONTRIBUTOR TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | GENERAL CORROSION | [5 empty] | YES | BRINE WITH EROSION |  | YES | [6 empty] | YES | WELL LINE | NO | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | [313 empty] | JOHN W. SEAGER | INTEGRITY ENGINEER | seagerj@natfuel.com | 7168577899 | 7168577469 |  |  |  | BRIAN A. KEMPSKI | SUPERINTENDENT | 7168272131 | kemskb@natfuel.com | AT APPROXIMATELY 12:04 AM, ON JUNE 22, 2013, THE NATIONAL FUEL GAS CONTROL OPERATIONS CENTER RESPONDED TO AN ALARM ON THE SCADA SYSTEM FOR COMPRESSOR SHUT DOWN AT THE LIMESTONE STORAGE FIELD STATION. GAS CONTROL OPERATIONS STAFF DETERMINED FROM SCADA THAT THE STORAGE FIELD WAS POTENTIALLY EXPERIENCING AN ABNORMAL DECLINE IN PRESSURE AND CONTACTED FIELD OPERATIONS TO INVESTIGATE. A RUPTURE WAS DISCOVERED AT WELL LINE FW 7013 WHICH WAS ISOLATED AND MADE SAFE AT 6:04 AM. FURTHER INVESTIGATION REVEALED THAT NO PERSONAL INJURIES OR PROPERTY DAMAGE BEYOND THE PIPELINE RESULTED FROM THE INCIDENT. A ROOT CAUSE ANALYSIS HAS BEEN COMPLETED BY AN EXPERT LAB IDENTIFYING INTERNAL CORROSION AS THE APPARANT CAUSE. THE COMPANY IS EVALUATING THE REPORT TO DETERMINE A LONG TERM ACTION PLAN. WELL LINE FW 7013 REMAINS OUT OF SERVICE AT THIS TIME.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130068 | 16510 | 2013-07-19 12:20 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2013-06-18 11:00 | 2013 |  |  | 41.4628 | -88.1751 | 1051135 | 2013-06-20 16:00 |  | NATURAL GAS |  | 91400 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | STATION WAS NOT RUNNING | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-06-20 11:00 | 2013-06-20 12:00 | ONSHORE | IL | 60410 | CHANNAHON | WILL | MILEPOST | 819 | JOLIET COMPR STA. |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1959 |  | CARBON STEEL |  | LEAK |  |  | OTHER | VENT | [5 empty] | CLASS 2 LOCATION | YES | METHOD2 | 664 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 40000 | 31229.5081967213 | 5980 | 6742.76708562451 | 12673 | 14289.4794776119 | 0 | 0 | MISC OPERATIONAL ACTIVITIES |  | 58653 | 42031.405327225 | 52261.7547599578 | [8 empty] | 741 |  | 850 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) | [10 empty] | YES |  |  | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [26 empty] | YES | [166 empty] | JERRY PALMER | REGULATORY COMPLIANCE SPECIALIST | jerry_palmer@transcanada.com | 708-342-4730 | 708-342-4731 |  |  |  | JERRY PALMER | REGULATORY COMPLIANCE SPECIALIST | 708-342-4730 | jerry_palmer@transcanada.com | THE GEARHEAD ADAPTOR ON THE STATION BLOCK VALVE DID NOT FULLY CLOSE AND GAS CONTROL SCREEN TEMPLATE DID NOT PICK IT UP. THE AIR COMPRESSOR THAT SUPPLIED THE GAS TO BLOCK VALVE FAILED AND GAS CONTROL DID NOT SEE THAT FUNCTION. A FOLLOW UP INVESTIGATION WAS FORWARDED TO THE PHMSA CENTRAL REGION OFFICE. THE FAILED BLOCK VALVE HAS BEEN REPAIRED AND BOTH AIR COMPRESSORS ARE BACK IN NORMAL SERVICE. ALL OPERATIONS ARE BACK IN NORMAL SERVICE AT THE COMPRESSOR STATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130069 | 16062 | 2013-07-24 11:21 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2013-06-27 18:25 | 2013 |  |  | 35.847 | -87.451 | 1051985 | 2013-06-27 19:39 |  | NATURAL GAS |  | 26151.8 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | [7 empty] | NO |  |  |  |  | NO | [9 empty] | ONSHORE | TN | 37033 | CENTERVILLE | HICKMAN | MILEPOST | STATION 860 | NUNNELLY STATION 860 | VALVE SECTION 558-1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2006 |  | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 578 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 96500 | 75341.1885245902 | 150 | 169.132953652789 | 0 | 0 | 0 | 0 |  |  | 96650 | 78187.2676361506 | 75510.321478243 | [8 empty] | 754.9 |  | 780 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 2 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | MECHANICAL FAILURE OF EQUIPMENT NOT ATTRIBUTED TO OPERATOR ACTIONS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | O-RING FAILURE | [161 empty] | THOMAS N MEEK JR | COORDINATOR - OPS SR II | thomas_meekjr@kindermorgan.com | 505-831-7718 | 505-831-7735 |  |  |  | REJI GEORGE | DIRECTOR - ENGINEERING | 713-420-5433 | reji_george@kindermorgan.com | RELIEF VALVE LIFTED PREMATURELY DUE TO PILOT VALVE O-RING LEAK.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130070 | 16064 | 2013-07-26 09:59 | ORIGINAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2013-07-01 16:45 | 2013 |  |  | 30.3428 | -101.5936 | 1052456 | 2013-07-01 22:33 |  | NATURAL GAS |  | 6195 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-07-01 16:45 | 2013-07-02 15:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-07-01 16:45 | 2013-07-01 18:45 | ONSHORE | TX | 76943 | OZONA | CROCKETT | SURVEY STATION NO. |  | PECOS COMPRESSOR STATION | LINE 146 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | 2" SUCTION HEADER BLOWDOWN VALVE, ETC. |  |  | CARBON STEEL |  | OTHER | [8 empty] | GAS WAS VENTING TO ATMOSPHERE THROUGH 2" FULLY OPENED SUCTION HEADER BLOWDOWN VALVE AND 2" PARTIALLY OPENED DISCHARGED HEADER BLOWDOWN VALVE. | CLASS 1 LOCATION | NO |  | 645 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 21868 | 17073.1721311475 | 8861 | 9991.24734878241 | 0 | 0 | 0 | 0 |  |  | 30729 | 22286.7789573487 | 27064.4194799299 | [8 empty] | 760 |  | 899 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ESD ALARM WAS PERFORMING AS INTENDED. GAS CONTROLLERS PERFORMED DUTIES BY NOTIFYING TECHNICIAN TO INVESTIGATE MATTER AT COMPRESSOR STATION SITE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | OTHER | ESD ALARM ON COMPRESSOR; GAS VENT TO ATMS THRU OPEN 2" SUCTION HEADER, ETC. | [20 empty] | YES | IN FIELD, SUCTION HEADER BLOWDOWN VALVE HAD BAD SOLENOID CAUSING TO FAIL OPEN. | [161 empty] | ANTHONY BROWN | SR. PIPELINE COMPLIANCE ENGINEER | abrown@eprod.com | (713) 381-5757 | (713) 381-6660 |  |  |  | ANTHONY BROWN | SR. PIPELINE COMPLIANCE ENGINEER | (713) 381-5757 | abrown@eprod.com | AT APPROXIMATELY 4:45 PM ON JULY 1,2013 ENTERPRISE GAS CONTROL BECAME AWARE OF AN ESD ALARM LOCATED AT ITS PECOS RIVER COMPRESSOR STATION SITE. GAS CONTROL DISPATCHED A PIPELINE TECHNICIAN TO INVESTIGATE THE SITUATION AND UPON ARRIVAL THE PIPELINE TECHNICIAN DISCOVERED GAS VENTING TO ATMOSPHERE THROUGH A FULLY OPENED 2" SUCTION HEADER BLOWDOWN VALVE AND A PARTIALLY OPENED 2" DISCHARGE HEADER BLOWDOWN VALVE. THIS VENTING OF GAS WAS ON THE COMPRESSOR UNIT AS INDICATED BY THE ESD ALARM. THE PIPELINE TECHNICIAN CLOSED SUCTION AND DISCHARGE VALVES IN ORDER TO STOP GAS FROM VENTING AT THE COMPRESSOR UNIT. THIS ACTION REMEDIED THE NATURAL GAS RELEASE. ADDITIONAL, ACTIONS AND TESTS WERE TAKEN TO ENSURE THAT SYSTEMS ASSOCIATED WITH THE COMPRESSOR UNIT(S) CONTINUE TO OPERATE AS INTENDED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130071 | 16111 | 2013-07-29 12:37 | SUPPLEMENTAL FINAL | 26330 | ENOGEX LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2013-06-29 09:00 | 2013 |  |  | 35.1069 | -95.2878 | 1052427 | 2013-07-01 17:05 |  | NATURAL GAS |  | 18950 | 4500 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-06-29 09:15 | 2013-07-02 16:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-06-29 09:00 | 2013-06-29 09:15 | ONSHORE | OK | 74552 | KINTA | HASKELL | MILEPOST |  | ARCO SNOW LATERAL |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 4.5 |  | 0.125 | 42000 | 4.5 OD | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | VULCAN SUPPLY | COAL TAR | [28 empty] | 1980 | 1980 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 24 | 4 |  | CLASS 1 LOCATION | NO |  | 86 |  | NO | NO | NO |  | 0 | 0 | 8751 | 9867.2165161037 | 36853 | 28772.5266393443 | 32853 | 37043.4995090338 | 8000 | 9020.4241948154 | 0 | 0 |  |  | 86457 | 55503.6540426642 | 84703.6668592972 | [8 empty] | 811 |  | 907 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 39600 | NO | [5 empty] | YES | RUPTURED PIPE IS A 4" GAS GATHERING LINE. | YES |  |  |  |  | YES | PIPELINE IS A 4" INACTIVE LATERAL. | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NOTIFICATION WAS RECEIVED FROM LANDOWNER BEFORE SCADA ALARMS INITIATED. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | GENERAL CORROSION | [5 empty] | YES | WATER | YES |  |  |  | YES | [5 empty] | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | CASEY ROBERTS | DOT COMPLIANCE COORDINATOR | casey.roberts@enogex.com | 405 558-4647 | 405 557-8618 |  |  |  | PAUL M BREWER | VP DIRECTOR OF OPERATIONS | 405 525-7788 | No Email Address | ON THE MORNING OF JUNE 29TH, LOCAL LAND OWNERS NOTIFIED HIGHLAND TO REPORT A POSSIBLE LINE RUPTURE SOUTH OF THE HIGHLAND KINTA YARD. HIGHLAND THEN CONTACTED ENOGEX. ENOGEX RESPONDED TO THE REPORT AND DROVE TO THE SITE FOR CONFIRMATION. AFTER CONFIRMING THE RUPTURE, ENOGEX CLOSED THE UPSTREAM VALVE AT ROBBERS CAVE JUNCTION, AND PROCEEDED TO THE KINTA YARD TO CLOSE THE DOWNSTREAM VALVE ON L-111, AND AT THIS POINT WAS ABLE TO CONFIRM THE RUPTURE. AFTER THE LINE WAS BLOWN DOWN, ENOGEX EVALUATED THE PIPELINE AND IT WAS DETERMINED THAT THE RUPTURE WAS ON AN INACTIVE 4" LATERAL (ARCO SNOW LATERAL) THAT TIES INTO L-111. AT THE TIME OF THE RUPTURE THE LATERAL WAS CAPPED AND INACTIVE. SINCE THE RUPTURE OCCURRED IN AN AREA BETWEEN L-111 AND THE BLIND INSTALLED ON THE ARCO LATERAL, L-111 TRANSMISSION GAS WAS VENTING THROUGH THE RUPTURE ON THE LATERAL. THE DECISION WAS MADE TO REMOVE 44' OF L-111 PIPE, INCLUDING THE ARCO TIE IN, AND REPLACING IT WITH 44' OF NEW PIPE. LINE 111 WAS REPAIRED AND PLACED BACK INTO SERVICE ON 7/2/13.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130072 | 16078 | 2013-07-30 20:23 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2013-06-30 18:18 | 2013 |  |  | 35.1576 | -118.804 | 1052308 |  |  | NATURAL GAS |  | 71596 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | FAILED RELIEF VALVE WAS MANUALLY CLOSED AND PRESSURE REDUCED BUT NOT SHUT DOWN. | [6 empty] | NO |  |  |  |  | NO | [7 empty] | 2013-06-30 18:18 | 2013-06-30 19:44 | ONSHORE | CA | 93203 | ARVIN |  | MILEPOST | 256.64 | 300B |  | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1950 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE STUCK OPEN | CLASS 1 LOCATION | NO |  | 240 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 281157 | 219509.870901639 | 100 | 112.755302435192 | 900 | 1014.79772191673 | 0 | 0 |  |  | 282157 | 228093.427000567 | 220637.423925991 | [8 empty] | 746 |  | 757 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS EVIDENT AT THE TIME OF THE INCIDENT THAT THE CAUSE WAS DUE TO A STUCK VALVE POPPET. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | VALVE POPPET BECAME STUCK DUE TO THE AGING INFRASTRUCTURE | [161 empty] | SONAL PATNI | SENIOR ENGINEER | s1pw@pge.com | 925-974-4104 |  |  |  |  | LARRY DENISTON | INTERIM MANAGER | 925-974-4313 | lcd1@pge.com
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130073 | 16399 | 2013-08-01 13:56 | SUPPLEMENTAL FINAL | 15825 | EAGLE US 2 LLC | 1300 PPG DRIVE | WESTLAKE | LA | 70669 | 2012-10-31 12:43 | 2012 |  |  | 30.0601 | -93.5976 |  |  |  | OTHER GAS | ETHYLENE | 866 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2012-10-31 16:45 | 2012-11-12 00:40 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-10-31 12:45 | 2012-10-31 15:00 | ONSHORE | LA | 70665 | SULPHUR | CALCASIEU | MILEPOST | MILE POST 12 | ORANGE ETHYLENE PIPELINE | ORANGE TO GUM COVE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 85 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8.625 |  | 0.219 | 42000 | API 5LX-42 | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | EXTRUDED POLYEHYLENE | [28 empty] | 1975 | 1974 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 200 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 30769 | 24784.3319238901 | 224000 | 257219.2 | 0 | 0 | 0 | 0 |  |  | 254769 | 143765.442283298 | 282003.53192389 | [8 empty] | 835 |  | 1066 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | MANUAL | 199642 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | AIR PATROL |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS NOT DETECTABLE BY SCADA OR OTHER MEANS WITHIN THE CONTROLLERS ACTIONS OR RESPONSIBILITIES. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING | [6 empty] | YES | INDUCED AC CURRENT. |  |  | YES |  |  |  | YES | YES | 1975 | YES | YES | YES | YES |  |  | 2012 | 1992 |  |  | YES | [190 empty] | YES |  |  | YES | YES | [23 empty] | 2011 | [11 empty] | 2011 | [23 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | JESSIE CASEY | PIPELINE SUPERVISOR | jessie.casey@axiall.com | 337-708-4434 | 337-708-4860 |  |  |  | DENNIS TOOKE | INSPECTION COMPLIANCE TEAM LEADER | 337-708-4457 | dennis.tooke@axiall.com | ON OCTOBER 31, 2012 THE WEEKLY AERIAL PIPELINE PATROL DISCOVERED A POSSIBLE LEAK (AN ICE PATCH ON THE GROUND) ON THE UNDERGROUND PORTION OF THE 8 INCH ORANGE ETHYLENE PIPELINE APPROXIMATELY 300 YARDS WEST OF THE VINTON DRAINAGE DITCH AND APPROXIMATELY 100 YARDS NORTH OF THE INTER COASTAL CANAL. PIPELINE INSPECTORS VISITED THE SITE AS SOON AS POSSIBLE ON 10/31/2012 TO VERIFY THE LEAK AND TO DETERMINE IF IT WAS ON PPG'S ETHYLENE PIPELINE. AT APPROXIMATELY 16:45 ON 10/31/2012 OPERATIONS BEGAN DEPRESSURIZING THE ETHYLENE PIPELINE WHICH CONTINUED UNTIL 11/5/2012 WHEN PURGING WITH NITROGEN BEGAN. PURGING AND DEPRESSURIZATION TO ATMOSPHERIC PRESSURE WAS COMPLETE ON 11/7/2012. THE LEAK SITE WAS THEN EXCAVATED AND THE SECTION OF LEAKING PIPE WAS REMOVED AND REPLACED WITH NEW 8 INCH, 0.219 WT, GRADE B X42, FBE COATED, PRESSURE TESTED PIPE. A ROOT CAUSE ANALYSIS DETERMINED THAT THE LEAK WAS CAUSED BY EXTERNAL CORROSION DUE TO INDUCED AC CURRENT ON THE PIPELINE AND A SMALL AREA OF DAMAGE TO THE PIPE COATING WHICH EXPOSED THE STEEL PIPE. THE DAMAGE TO THE PIPE COATING WAS THEORIZED TO HAVE BEEN CAUSED BY A PROBE STRIKE THAT OCCURRED WHEN SOMEONE WAS LOCATING THE PIPELINE. THE PIPELINE WAS RETURNED TO SERVICE ON 11/11/2012. AT THE TIME OF THE LEAK PPG PIPELINE SUPERVISION DID NOT BELIEVE THAT THE SITUATION MET THE DEFINITION OF AN INCIDENT AS DEFINED BY 49 CFR 191.3; THE LEAK OCCURRED IN A VERY REMOTE AREA IN THE CALCASIEU PARISH MARSH (AT LEAST 5 MILES TO THE NEAREST DWELLING), THERE WERE NO DEATHS OR INJURIES, NO EXPLOSION OR FIRE, AND ACTUAL CALCULATED GAS LOST WAS 866 MCF (WELL BELOW THE 3 MILLION CUBIC FEET DEFINED AS AN INCIDENT). THE ONLY DIRECT PROPERTY DAMAGE WAS TO A SECTION OF 8 INCH UNDERGROUND PIPING AND THAT REPAIR WAS ESTIMATED TO BE LESS THAN $50,000. THEREFORE, BASED ON THIS INFORMATION, IT WAS CONCLUDED BY PPG'S PIPELINE SUPERVISION THAT NOTIFICATION TO THE NRC WAS NOT REQUIRED AND SUBMISSION OF AN ELECTRONIC WRITTEN REPORT TO PHMSA WITHIN 30 DAYS OF THE EVENT WAS NOT REQUIRED. THIS YEAR PPG'S PIPELINE SUPERVISOR ATTENDED A THIRD PARTY DOT PIPELINE COMPLIANCE TRAINING CLASS AND WAS INFORMED THAT PROPERTY DAMAGE INCLUDED ALL COST ASSOCIATED WITH REPAIRING A LEAK; NOT JUST THE COST FOR THE IMMEDIATE REPAIR TO THE PIPE. AFTER RETURNING TO HIS WORK LOCATION, THE PIPELINE SUPERVISOR LOCATED AN ADVISORY BULLETIN (ADB-02-01) RELEVANT TO THE ISSUE. WITH THE BENEFIT OF THIS ADDITIONAL UNDERSTANDING, THE PPG PIPELINE SUPERVISOR RE-EVALUATED ALL COSTS ASSOCIATED WITH THE REPAIR AND REVALUED THE PROPERTY DAMAGE AS EXCEEDING THE $50,000 THRESHOLD.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130074 | 16081 | 2013-08-01 17:22 | ORIGINAL | 13480 | NIAGARA MOHAWK POWER CORP | 300 ERIE BOULEVARD WEST | SYRACUSE | NY | 13202 | 2013-07-03 14:56 | 2013 |  |  | 43.0826 | -75.598 | 1052682 | 2013-07-03 15:50 |  | NATURAL GAS |  | 2900 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-07-03 14:56 | 2013-07-18 17:25 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-07-03 14:56 | 2013-07-03 14:56 | ONSHORE | NY | 13461 | SHERRILL | ONEIDA | SURVEY STATION NO. | SCONONDOA CRK | PIPELINE 61 | N/A | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | BELOW STREAM BED | 48 |  | YES | [6 empty] | YES | UNCASED | SCONONDOA CREEK | 4 | BELOW WATER, PIPE BURIED BELOW BOTTOM (NOT IN BORED/DRILLED CROSSING) | [11 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6.625 |  | 0.188 | 35000 | API-5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | LTV STEEL | EXTRUDED POLYEHYLENE | [28 empty] | 1991 | 1990 | CARBON STEEL |  | OTHER | [8 empty] | EXTREME RAINFALL CAUSED LOCALIZED FLOODING AND STRONG CURRENTS, WHICH ERODED COVER FROM PIPELINE. EROSION LED TO THE PIPE BEING COMPROMISED. | CLASS 2 LOCATION | YES | METHOD2 | 100 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 10473 | 8176.66598360656 | 651500 | 734600.795365279 | 1000 | 1127.55302435192 | 0 | 0 |  |  | 662973 | 346195.846353328 | 743905.014373238 | [8 empty] | 450 |  | 473 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 5000 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | YES | YES | OTHER | POWER PLANT PERSONNEL. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | FLOODING DAMAGE WAS THE ROOT CAUSE OF THE EVENT. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [52 empty] | HEAVY RAINS/FLOODS |  | WASHOUTS/SCOURING |  |  |  | YES |  |  |  | YES | EXCESSIVE LOCALIZED RAINFALL. | [301 empty] | DEBORAH DEBERGALIS | MANAGER UPSTATE DISPATCH AND SCHEDULING | deborah.debergalis@nationalgrid.com | 3154602615 |  |  |  |  | GARY BENNETT | DIRECTOR DISPATCH AND SCHEDULING US | 6178397208 | gary.bennett@nationalgrid.com | EXTREME RAINFALL IN THE MOHAWK VALLEY REGION OF UPSTATE NY CAUSED LOCALIZED FLOODING NEAR THE MOHAWK RIVER AND ASSOCIATED TRIBUTARIES. IN THE TOWNSHIP OF SHERRIL, THE SCONONDOA CREEK OVER-TOPPED IT'S BANKS NEAR THE STERLING POWER GENERATING PLANT. THE ASSOCIATED FLOODING AND STRONG CURRENTS ERODED THE COVER FROM PIPELINE 61, A 6" 473 PSI MAOP PIPELINE SERVING ONLY STERLING POWER. FLOOD WATER INUNDATED THE POWER GENERATING PLANT AND PROMPTED A PRE-EMPTIVE SHUT DOWN OF PIPELINE 61. THE PIPELINE DEPRESSURIZED UNDER THE SUPERVISION OF LOCAL OPERATING PERSONNEL. SUBSEQUENT TO THE WEATHER EVENT, FLOODWATERS RECEDED AND REVEALED THAT PIPELINE 61 HAD BEEN COMPROMISED IN THE MAIN STREAM BED. NOTE: PART A, 15A: PIPELINE WAS SHUT DOWN AS A PRECAUTION ON 06/28/13 DUE TO FLOODING CONDITIONS. PART C, 3G: DATE OF MANUFACTURER IS BASED ON PURCHASE ORDER DATE OF 10/02/90.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130075 | 16083 | 2013-08-02 16:38 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2013-07-05 15:08 | 2013 |  |  | 39.0975 | -95.6903 | 1053312 | 2013-07-10 10:00 |  | NATURAL GAS |  | 0.13 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE METERING FACILITY WAS CAPABLE OF BEING BYPASSED WHILE DAMAGE IS CORRECTED. | [6 empty] | YES |  |  |  |  | NO | [6 empty] | 0 | 2013-07-05 15:08 | 2013-07-05 15:57 | ONSHORE | KS | 66618 | TOPEKA | SHAWNEE | SURVEY STATION NO. | 180/393+27 | LINE EK | SERVICE PIPELINE 10" AND 16" | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | METER | [38 empty] | 1990 |  | CARBON STEEL |  | OTHER | [8 empty] | A TRANSMISSIN LINE NEUTRAL BROKE AND CAME INTO CONTACT WITH THE HIGH VOLTAGE LINES AND OUR SERVICE LINE. | CLASS 1 LOCATION | NO |  | 65 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 4 | 3.12295081967213 | 145000 | 163495.188531029 | 0 | 0 | 0 | 0 |  |  | 145004 | 75051.8433608489 | 163498.311481849 | [8 empty] | 179 |  | 200 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | NO | NO | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | [103 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [261 empty] | DAVID COOMES | PIPELINE COMPLIANCE ENGINEER | david.coomes@sscgp.com | 270.852.4391 |  |  |  |  | DAVID SINCLAIR | PIPELINE COMPLIANCE MANAGER | 270.852.4424 | No Email Address | A HIGH VOLTAGE LINE CAME DOWN ON SOUTHERN STAR'S SERVICE LINE FROM THE TRANSMISSION LINE THIS ALLOWED THE HIGH VOLTAGE TO ENTER THE ELECTRIC METER FOR THE FACILITY. THIS HIGH VOLTAGE DESTROYED THE METER AND ALLOWED THE HIGH VOLTAGE TO FOLLOW THE GROUNDING WIRE FROM THE METER TO THE MEASUREMENT SETTING. THE HIGH VOLTAGE FOLLOWED THE GROUNDING WIRE TO THE GROUND STRAPPING FOR THE MEASUREMENT BUILDING AND EQUIPMENT CAUSING IGNITION. THE IGNITION WAS FUELED OUTSIDE OF THE BUILDING BY A CONTROLLER VENT LINE. THE HEAT FROM THE FIRE IS BELIEVED TO HAVE DAMAGED SEALS CAUSING GAS TO LEAK AND THE FIRE TO SPREAD TO THE INTERIOR OF THE METER BUILDING. THE FIRE AND BLOWING GAS WAS REPORTED TO SOUTHERN STAR GAS CONTROL AT 3:13 PM ON 7/5/2013. GAS CONTROL NOTIFIED OPERATIONS OF THE ISSUE. OPERATIONS ARRIVED ON SCENE AT 3:57 PM. FIRE DEPARTMENT WORKED TO GET FIRED CONTAINED WHILE WESTAR (HIGH VOLTAGE LINE) WORKED TO CUT POWER. THE FIRE WAS EXTINGUISHED AT 4:55 PM AND OPERATIONS BEGAN TO CONTAIN GAS FLOW WHICH WAS STOPPED AT 5:13 PM. ALL FLOW COMPUTERS WERE DAMAGED IN FIRE CAUSING THE METER TO BE BYPASSED UNTIL REPAIRS ARE MADE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130076 | 16090 | 2013-08-09 16:43 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2013-07-18 16:15 | 2013 |  |  | 31.8973 | -92.9651 | 1054330 | 2013-07-18 16:30 |  | NATURAL GAS |  | 0 | 3.03 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-07-18 18:20 | 2013-07-20 04:10 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-07-18 16:15 | 2013-07-18 16:15 | ONSHORE | LA | 71031 | CLARENCE | NATCHITOCHES | MILEPOST | 368.83 | INDEX 129 | WEST 30" | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 41 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 |  | 0.5 | 52000 | API 5L | FLASH WELDED |  | A. O. SMITH | OTHER | ENAMEL PRIMER, FIBERGLASS COATED | [27 empty] | 1952 | 1952 | CARBON STEEL |  | LEAK |  |  | OTHER | LEAK UNDER HARD SPOT SLEEVE | [5 empty] | CLASS 1 LOCATION | NO |  | 578 |  | NO | NO | NO |  | 0 | 0 | 11476 | 12939.7985074627 | 0 | 0 | 80460 | 90722.9163393559 | 0 | 0 | 0 | 0 |  |  | 91936 | 47583.9214454046 | 103662.714846819 | [8 empty] | 657 |  | 780 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | AUTOMATIC | 42240 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SMALL LEAK NOT DETECTED BY SCADA. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | YES |  | YES | SIMILAR TYPES OF LEAKS (HARD SPOTS) | [11 empty] | YES | HARD SPOT | [13 empty] | YES | UNKNOWN SINCE HARD SPOT SLEEVE WAS NOT REMOVED. | [55 empty] | YES | YES | YES |  |  |  |  | YES | 2006 |  | HARD SPOTS | [9 empty] | 2013 | [37 empty] | COMBINATION TOOL | 2013 |  |  |  |  | NO |  |  | NO | [13 empty] | NO | [63 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 270.688.6357 | 270.688.5871 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 270.688.6361 | jeff.mcmaine@bwpmlp.com | GAS LEAK AT SITE OF PREVIOUS HARD SPOT SLEEVE REPAIR AREA ON THE WEST 30-INCH SUCTION LINE (INDEX 129) INSIDE CLARENCE STATION YARD. REPAIR WAS MADE USING A TYPE B SLEEVE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130077 | 16265 | 2013-08-21 10:56 | SUPPLEMENTAL FINAL | 4060 | DOMINION EAST OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2013-07-22 06:01 | 2013 |  |  | 40.9462 | -81.5411 | 1054638 | 2013-07-22 08:15 |  | NATURAL GAS |  | 17700 |  | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-07-22 07:02 | 2013-11-22 12:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 175 | 2013-07-22 06:25 | 2013-07-22 06:30 | ONSHORE | OH | 44319 | NEW FRANKLIN | SUMMIT | SURVEY STATION NO. | 35+16 | L#3362 | 459757672 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 42 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 8.625 |  | 0.375 | 42000 | API 5L X42 | LONGITUDINAL ERW - LOW FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1957 | 1956 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 156 | 15 |  | CLASS 3 LOCATION | NO |  | 258 |  | NO | NO | NO |  | 5000 | 5637.76512175962 | 0 | 0 | 76234 | 59518.7581967213 | 15000 | 16913.2953652789 | 5000 | 5637.76512175962 | 1400000 | 1578574.2340927 | INCLUDES REPLACING 4400 FEET OF LIKE AND SIMILAR PIPE IN THE AREA. |  | 1501234 | 799252.440971373 | 1666281.81789821 | [8 empty] | 1483 |  | 1565 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 2400 | NO | YES | YES |  | YES |  | YES | NO LAUNCHER/RECEIVER INSTALLED | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DEO DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER'S ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE THE COMPLETION OF THE DOMINION CRM PLAN SECTION 9.2 "INCIDENT REVIEW-REPORTABLE INCIDENTS REVIEW TO DETERMINE CONTROL ROOM INVOLVEMENT PROCEDURE" THAT DETERMINED THAT THERE WAS NO CONTROLLER OR CONTROL ROOM ISSUES INVOLVED IN THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | GENERAL CORROSION | [5 empty] | YES | SELECTIVE SEAM WELD CORROSION |  | YES | [6 empty] | YES | IN PIPE SEAM | NO | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | AARON MCCOY | TECHNICAL SPECIALIST | aaron.m.mccoy@dom.com | 3304589186 | 3304783760 |  |  |  | AARON MCCOY | TECHNICAL SPECIALIST | 3304589186 | aaron.m.mccoy@dom.com | ON JULY 22, 2013, AT APPROXIMATELY 6:01 A.M. AN 8" STORAGE LINE OPERATING AT 1,483 PSIG LOCATED IN NEW FRANKLIN, OHIO RUPTURED. AT APPROXIMATELY 6:30 A.M. ON JULY 22, 2013, DOMINION ARRIVED ON SCENE AND ISOLATED THE SECTION OF PIPELINE THAT RUPTURED AT APPROXIMATELY 7:02 A.M. THE SECTION OF PIPE THAT RUPTURED WAS CUT OUT AND SENT TO A THIRD PARTY LABORATORY, KEIFNER & ASSOCIATES, FOR A FAILURE ANALYSIS. THE ANALYSIS CONCLUDED THE CAUSE OF THE FAILURE WAS DETERMINED TO BE INTERNAL SELECTIVE SEAM WELD CORROSION (SSWC) OF THE LOW-FREQUENCY ELECTRIC-RESISTANCE WELDED (LF-ERW) SEAM.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130078 | 16162 | 2013-08-27 18:24 | SUPPLEMENTAL FINAL | 31286 | ONEOK GAS TRANSPORTATION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2013-07-28 01:42 | 2013 |  |  | 35.4936 | -98.5184 | 1055311 | 2013-07-28 08:42 |  | NATURAL GAS |  | 13102 | 3 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-07-28 08:15 | 2013-07-28 15:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-07-28 06:30 | 2013-07-28 07:25 | ONSHORE | OK | 73048 | HYDRO | CADDO |  |  | HYDRO JUNCTION - M-20/A-1100 |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | IN UNDERGROUND ENCLOSED SPACE (E.G. VAULT) |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1975 |  | CARBON STEEL |  | LEAK |  |  | OTHER | VALVE FAILURE | [5 empty] | CLASS 1 LOCATION | NO |  | 273 |  | NO | NO | NO |  | 0 | 0 | 11 | 12.4030832678712 | 51013 | 39827.7725409836 | 1940 | 2187.45286724273 | 500 | 563.776512175962 | 0 | 0 |  |  | 53464 | 42559.8404697822 | 42591.4050036702 | [8 empty] | 834 |  | 960 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | REMOTELY CONTROLLED | 75 | NO | [5 empty] | YES | SETTING PIPE | YES |  |  |  |  | YES | VALVE ON DRIP | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | FAILURE OF EQUIPMENT BODY (EXCEPT COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL | MATERIAL/WELD/EQUIP FAILURE | FAILURE OF EQUIPMENT BODY | [166 empty] | FAILURE OF EQUIPMENT BODY (EXCEPT COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL | [35 empty] | YES | UNDERGROUND BOLTED BODY VALVE FAILURE, SEE PART H FOR FURTHER DETAILS | [161 empty] | PATTI FORD | SENIOR PIPELINE SAFETY ENGINEER | patti.ford@oneok.com | 918 588 7131 | 918 732 1311 |  |  |  | WESLEY R. DUNBAR | VICE PRESIDENT | 918 588 7424 | wesley.dunbar@oneok.com | A LANDOWNER CALLED GAS CONTROL AT APPROXIMATELY 0630 HOURS ON JULY 28, 2013 TO REPORT A NATURAL GAS LEAK AT THE ONEOK GAS TRANSPORTATION'S HYDRO JUNCTION FACILITY IN CADDO COUNTY, OKLAHOMA. OPERATIONS PERSONNEL WERE DISPATCHED AT APPROXIMATELY 0640 HOURS AND VERIFIED THE LEAK TO BE ON ONEOK FACILITIES AT 0725 HOURS. THE HYDRO FIRE DEPARTMENT RESPONDED AND PROVIDED TRAFFIC CONTROL UNTIL THE LEAK COULD BE ISOLATED AT 0840 HOURS. THE LEAK WAS DETERMINED TO HAVE RESULTED FROM A FAILED 2 INCH VALVE ON THE PIPELINE DRIP. THE FAILED VALVE WAS REPLACED WITH A PLUG AND THE PIPELINE RETURNED TO SERVICE AT 1530 HOURS ON JULY 28, 2013. NO CUSTOMERS WERE IMPACTED. A FAILURE ANALYSIS IS BEING CONDUCTED ON THE FAILED 2 INCH VALVE. POST INCIDENT REVIEW OF SCADA DATA INDICATED THAT A SMALL PRESSURE DROP RECORDED AT 0142 HOURS ON JULY 28 WAS PROBABLY WHEN THE DRIP VALVE FAILED. THAT PRESSURE DROP WAS NOT OF SUFFICIENT MAGNITUDE TO BE JUDGED ABNORMAL WHEN IT OCCURRED. IT IS ESTIMATED THE UNINTENTIONAL GAS LOSS EXCEEDED 3 MILLION CUBIC FEET 83 MINUTES LATER THEREFORE MAKING THE LEAK REPORTABLE AT 0305 HOURS. THIS TIME IS USED IN PART A OF THIS INCIDENT REPORT AS THE TIME OF THE INCIDENT. THE OKLAHOMA CORPORATION COMMISSION WAS CONTACTED AT 0832 HOURS AND THE NATIONAL RESPONSE CENTER WAS CONTACTED AT 0842 HOURS - REFERENCE PHMSA INCIDENT NUMBER 1055311. UPDATE: THE FAILURE ANALYSIS CONDUCTED BY A THIRD PARTY STATED THE FAILURE MODE OF THE VALVE BOLTS WAS MOST LIKELY SULFIDE STRESS CRACKING, A FORM OF HYDROGEN EMBRITTLEMENT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130079 | 16288 | 2013-08-29 18:56 | SUPPLEMENTAL FINAL | 11820 | BRIDGELINE HOLDINGS, LP | 1722 ROUTH STREET, SUITE 1300 | DALLAS | TX | 75201 | 2013-07-29 16:28 | 2013 |  |  | 29.2246 | -90.1632 | 1055755 | 2013-08-01 11:10 |  | NATURAL GAS |  | 44 | 504.75 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-07-29 18:00 | 2013-08-04 17:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-07-29 16:28 | 2013-07-29 16:28 | ONSHORE | LA | 70357 | GOLDEN MEADOW | LAFOURCHE | SURVEY STATION NO. | 0+00 | LAFOURCHE NATURAL GAS PIPELINE SYSTEM | 14" SEGMENT - GOLDEN MEADOW TO LAROSE VALVE SITE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | DRAIN LINES | [40 empty] | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO | NO |  | 0 | 0 | 1873 | 2111.90681461116 | 148 | 115.549180327869 | 95000 | 107117.537313433 | 0 | 0 | 0 | 0 |  |  | 97021 | 50258.9921558086 | 109344.993308372 | [8 empty] | 500 |  | 987 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 77563 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PINHOLE SIZE LEAK VOLUME WAS TOO SMALL TO BE DETECTED BY THE CONTROL ROOM SCADA. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  |  | YES | [7 empty] | YES |  |  |  | NO | [11 empty] | YES | YES | [335 empty] | HENRY L. LEGER | DOT PIPELINE SAFETY SPECIALIST | henryleger@chevron.com | (337) 654-8915 | (337) 572-3720 |  |  |  | HENRY L. LEGER | DOT PIPELINE SAFETY SPECIALIST | (337) 654-8915 | henryleger@chevron.com | THE LAFOURCHE NATURAL GAS PIPELINE SYSTEM IS AN INTRASTATE NATURAL GAS TRANSMISSION PIPELINE UNDER THE JURISDICTION OF THE LOUISIANA DEPARTMENT OF NATURAL RESOURCES AND IS OWNED BY BRIDGELINE HOLDINGS, L.P. LA DNR OPID NO. PFPL0317. THE INCIDENT WAS DUE TO A EXTERNAL PINHOLE CAUSED BY ATMOSPHERIC CORROSION. THE LEAK OCCURED ON 1-INCH AUXILLARY PIPING. AT THE LEAK POINT, THE COATING/PAINT WAS DAMAGED, ALLOWING ATMOSPHERIC CORROSION TO SET IN. THE LEAK WAS SO SMALL THAT AN EMERGENCY RESPONSE MODE WAS NOT REQUIRED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130080 | 16102 | 2013-09-06 10:15 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2013-08-13 16:47 | 2013 |  |  | 31.2936 | -90.2396 | 1057014 | 2013-08-13 17:24 |  | NATURAL GAS |  | 107 | 3156 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-08-13 18:15 | 2013-08-14 01:11 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2013-08-13 16:48 | 2013-08-13 17:26 | ONSHORE | MS | 39641 | MCCOMB | WALTALL | MILEPOST | 166 | INDEX 130 | KOSCI 30" | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | ON CENTERPOINT'S ASSETS DOWNSTREAM OF GS |  |  | CARBON STEEL |  | LEAK |  |  | OTHER | ON CENTERPOINT'S ASSETS | [5 empty] | CLASS 1 LOCATION | NO |  | 631 |  | NO | NO | NO |  | 0 | 0 | 11238 | 12671.4408876669 | 381 | 297.46106557377 | 1000 | 1127.55302435192 | 6500 | 7329.09465828751 | 0 | 0 |  |  | 19119 | 10006.7415505518 | 21425.5496358801 | [8 empty] | 850 |  | 930 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [52 empty] | LIGHTNING |  |  | DIRECT HIT |  |  | NO | [306 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 270.688.6357 |  |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 270.688.6361 | jeff.mcmaine@bwpmlp.com | ONSITE INVESTIGATION REVEALED THAT THIS INCIDENT OCCURRED ON CENTERPOINT ENERGY'S ASSETS RATHER THAN GULF SOUTH. GULF SOUTH IS COMPLETING A WRITTEN INCIDENT REPORT BECAUSE IT WAS CONSIDERED A SIGNIFICANT INCIDENT UNDER THE REPORTING CRITERIA.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130081 | 16515 | 2013-09-06 11:23 | SUPPLEMENTAL FINAL | 31130 | DCP MIDSTREAM | 370 17TH STREET SUITE 2500 | DENVER | CO | 80202 | 2013-08-09 19:55 | 2013 |  |  | 32.4039 | -92.7027 | 1056710 | 2013-08-10 15:24 |  | NATURAL GAS |  | 4200 | 0 | 40 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-08-09 23:25 | 2013-09-11 09:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 12 | 2013-08-09 19:55 | 2013-08-09 20:43 | ONSHORE | LA | 71270 | RUSTON | JACKSON | SURVEY STATION NO. | 48793.08 | PELICO | PL-2-1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12.75 |  | 0.219 | 52000 | API 5LX 52 | LONGITUDINAL ERW - HIGH FREQUENCY |  | AMERICAN STEEL | EPOXY | [28 empty] | 1984 | 1984 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 234 | 36 |  | CLASS 1 LOCATION | NO |  | 262 |  | NO | NO | NO |  | 45000 | 50739.8860958366 | 0 | 0 | 14700 | 11476.8442622951 | 97000 | 109372.643362137 | 4700 | 5299.49921445405 | 0 | 0 |  |  | 161400 | 87827.0514339434 | 176888.872934722 | [8 empty] | 815 |  | 1000 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 89760 | NO |  |  |  | YES |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WAS NO ABNORMAL CONDITION AND THE PIPELINE PRESSURES WERE IN NORMAL OPERATING RANGES | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) |  | YES | YES | ENGINEERING ASSESSMENT | [11 empty] | YES | MNS-FES INCLUSIONS ALONG THE 180O PIPE AXIS FROM THE SEAM | [13 empty] | YES | THE PRESENCE OF THE MNS-FES INCLUSIONS ALONG THE 180O PIPE AXIS FROM THE SEAM, AND BECAUSE IT WAS USED AS A BEND, THAT THE MECHANICAL PROPERTIES (TENSILE STRENGTH) WERE COMPROMISED. | [55 empty] | NO | [63 empty] | YES | 2013 | 1650 | NO | [13 empty] | NO | [63 empty] | KEN JOHNSON | SR. PIPELINE COMPLIANCE SPECIALIST | kwjohnson@dcpmidstream.com | 2548359728 | 7209440261 |  |  |  | JIM MCCLAIN | SUPERVISOR OPS II | 3182456718 | jemcclain@dcpmidstream.com | ON FRIDAY, AUGUST 9TH, 2013, AT APPROXIMATELY 7:55PM A DCP OPERATOR RECEIVED A CALL FROM A HOMEOWNER, STATING THAT HE HEARD A LOUD POP AND ROARING. HE THOUGHT THAT THE DCP PIPELINE BEHIND HIS HOME HAD RUPTURED. HIS HOME IS LOCATED AT ANSLEY ROAD 10 MILES SOUTH OF RUSTON. TWO OTHER THIRD PARTY PIPELINES ARE IN THE SAME AREA SO IT WAS UNKNOWN AT THE TIME WHETHER OR NOT THE LINE WAS DCP'S. THE DCP OPERATOR CONTACTED THE DCP FIELD SUPERVISOR CONCERNING A POSSIBLE RUPTURE AND WAS PROCEEDING TO THE SITE. THE DCP OPERATOR ARRIVED ON SITE TO FIND THAT THE SHERIFF DEPUTY AND FIRED DEPARTMENT WERE ON SITE. THE AUTHORITIES HAD THE ROAD BLOCKED AND WERE IN THE PROCESS OF EVACUATING THREE FAMILIES IN THE AREA. AT APPROXIMATELY, 8:30PM, IT WAS CONFIRMED THAT THE LINE WAS DCP'S AND THE FIELD OPERATORS BEGAN TO SHUT IN THE BLOCK VALVES AND THE PRODUCERS WERE CONTACTED TO SHUT IN THEIR WELLS. MOST OF THE WELLS WERE SHUT IN IMMEDIATELY; HOWEVER, EXCO WAS DELAYED IN SHUTTING THEIR WELLS. THE DCP SUPERVISOR WAS WORKING WITH EXCO TO EXPEDITE THEM SHUTTING IN THEIR GAS; HOWEVER, THEY WERE STILL NOT ABLE TO CUT OFF THEIR FLOW TO DCP'S LINE. AT 11:10PM, THE DCP SUPERVISOR MADE THE DECISION TO SHUT IN THE TAP VALVE FOR THE ANADARCO CDP SINCE EXCO COULD NOT SHUT IN THEIR GAS. ONCE THE PIPELINE WAS SHUT IN DCP PERSONNEL AND A REPRESENTATIVE FROM THE LDEQ WALKED INTO THE SITE WITH GAS MONITORING EQUIPMENT TO CONFIRM THAT THE SITE WAS SAFE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130082 | 16322 | 2013-09-10 11:04 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2013-08-29 03:07 | 2013 |  |  | 32.0837 | -94.1558 | 1058608 | 2013-08-29 11:20 |  | NATURAL GAS |  | 4971.2 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | PRESSURES WERE VERIFIED & RVS ISOLATED TO STOP VENTING UNTIL INVESTIGATED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-08-29 03:15 | 2013-08-29 03:33 | ONSHORE | TX | 75633 | CARTHAGE | PANOLA | MILEPOST | 296+67 | CARTHAGE JUNCTION COMPRESSOR STATION | INDEX 59 AND INDEX 266 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1981 |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENTIONAL VENTING OF RELIEF VALVE | CLASS 1 LOCATION | NO |  | 61 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 17200 | 13428.6885245902 | 0 | 0 | 360 | 405.919088766693 | 0 | 0 |  |  | 17560 | 14108.458720204 | 13834.6076133569 | [8 empty] | 728 |  | 875 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLERS WERE THE ENTITY THAT DISCOVERED AND DISPATCHED PERSONNEL TO INVESTIGATE. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | DURING A PLANNED SHUTDOWN AT THE CARTHAGE JUNCTION COMPRESSOR STATION TO INSTALL A FILTER/SEPARATOR, A SECTION OF THE LONGVIEW SUCTION LINE WAS ISOLATED. THIS SECTION OF LINE SUPPLIED GAS TO A RELIEF VALVE AND ESD VALVE VOLUME BOTTLE. OVER THE COURSE OF THE 2 DAY SHUTDOWN, THE PRESSURE IN THE BOTTLE DECREASED CAUSING THE RELIEF VALVES TO DISCHARGE. | YES |  |  |  |  | CONSTRUCTION | NO | [150 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 270.688.6357 | 270.688.6948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 270.688.6361 | jeff.mcmaine@bwpmlp.com | SEE SECTION G7. AN ADDITIONAL RELIEF VALVE ACTUATED ON INDEX 59 WHICH DID NOT EXCEED THE MAOP OF THAT PIPELINE. THE DELAY IN MAKING THE NRC NOTIFICATION WASS DUE TO AN ERROR FOUND IN THE ORIGINAL GAS LOSS ESTIMATE. THE ORIGINAL ESTIMATE WAS MADE USING DATA FROM A CHECK METER. UNFORTUNATELY, PERSONNEL MAKING THE ESTIMATE DID NOT REALIZE THE CHECK METER WAS NOT FULLY MEASURING THE GAS LOSS. A SUBSEQUENT CALCULATION WAS MADE BASED ON THE TIME BOTH BLOW-OFFS WERE VENTING GAS. ONCE THE ERROR WAS RECOGNIZED, THE REPORT WAS MADE TO NRC. 3-11-14
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130083 | 16665 | 2013-09-10 16:12 | SUPPLEMENTAL FINAL | 12180 | MARSHALL COUNTY GAS DISTRICT | 1245 GUNTER AVENUE | GUNTERSVILLE | AL | 35976 | 2013-08-09 10:45 | 2013 |  |  | 34.576 | -86.1232 | 1056616 | 2013-08-09 15:50 |  | NATURAL GAS |  | 1110 | 128 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-08-09 12:10 | 2013-08-09 20:20 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 0 | 2013-08-09 10:55 | 2013-08-09 11:10 | ONSHORE | AL | 35768 | SCOTTSBORO | JACKSON | MILEPOST | MM 83.8 | BIRMINGHAM-SCOTTSBORO | JACKSON COUNTY | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 42 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10 |  | 0.188 | 42000 | API -5LX-42 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | REPUBLIC STEEL | COAL TAR | [28 empty] | 1966 | 1966 | CARBON STEEL |  | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | NO |  | 129 |  | NO | NO | NO |  | 136000 | 153347.211311862 | 714 | 805.072859387274 | 6188 | 4831.20491803279 | 12000 | 13530.6362922231 | 16000 | 18040.8483896308 | 0 | 0 |  |  | 170902 | 90260.8400737898 | 190554.973771136 | [8 empty] | 185 |  | 350 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | CHECK VALVE | 32208 | NO | YES | YES | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 2 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | NO | YES | STATE HIGHWAY | [9 empty] | CONTRACTOR | UNKNOWN/OTHER | UNKNOWN/OTHER | YES | 132200469 |  | UTILITY OWNER | YES | YES | NO |  | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO MAINTAIN CLEARANCE | [263 empty] | RICHARD T LAWSON | CEO | lawson@mcgd.org | 256-582-0324 | 256-582-5694 |  |  |  | RICHARD T LAWSON | CEO | 256-582-0324 | lawson@mcgd.org
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130084 | 16191 | 2013-09-11 06:51 | SUPPLEMENTAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2013-08-19 05:05 | 2013 |  |  | 33.1116 | -98.4053 | 1057525 | 2013-08-19 07:20 |  | NATURAL GAS |  | 26765 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-08-19 05:08 | 2013-08-23 15:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-08-19 05:05 | 2013-08-19 05:05 | ONSHORE | TX | 76427 | BRYSON | JACK | SURVEY STATION NO. | 14+81 | BRYSON LATERALS | SIMPSON HEIRS LATERAL 8" | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8.625 |  | 0.188 | 42000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | PERVIN & GERTZ | COAL TAR | [28 empty] | 1973 | 1973 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 8 | 32 |  | CLASS 1 LOCATION | NO |  | 179 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 95010 | 74177.8893442623 | 49000 | 55250.0981932443 | 0 | 0 | 0 | 0 |  |  | 144010 | 102264.839011371 | 129427.987537507 | [8 empty] | 802 |  | 944 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 2563 | NO | YES | [6 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | GENERAL CORROSION |  |  |  | YES |  |  |  | YES | YES |  |  | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DANNY NICHOLS | DIRECTOR REGULATORY COMPLIANCE | danny.nichols@energytransfer.com | 713-989-7232 | 713-989-1188 |  |  |  | DANNY NICHOLS | DIRECTOR REGULATORY COMPLIANCE | 713-989-7232 | danny.nichols@energytransfer.com | ON AUGUST 19, 2013, AT APPROXIMATELY 5:05 AM ENERGY TRANSFER COMPANY (ETC) EXPERIENCED RUPTURE ON THE SIMPSON HEIRS 8" LATERAL IN THE BRYSON UNDERGROUND STORAGE FACILITY IN JACK COUNTY, NEAR BRYSON, TEXAS. THE PIPELINE IS AN INTRASTATE NATURAL GAS TRANSMISSION PIPELINE LOCATED IN A RURAL (CLASS 1) AREA, UNDER THE JURISDICTION OF THE TEXAS RAILROAD COMMISSION (SYSTEM ID # 960834). THE INCIDENT WAS REPORTED TO THE TRRC UNDER INCIDENT ID: 844 AND ALSO TO THE NRC UNDER ID: 1057525. THERE WERE NO FATALITIES, INJURIES, EVACUATIONS, ROAD CLOSURES, EXPLOSIONS, FIRE, MEDIA INTEREST, SPILLS OR ANY RESPONSE BY AN EMERGENCY OFFICIAL. THERE WERE NO BUILDINGS INTENDED FOR HUMAN OCCUPANCY WITHIN 1/2 MILE. AT 4:31 AM, AN AREA LANDOWNER, CONTACTED AN ETC EMPLOYEE AND ADVISED THAT HE HEARD GAS BLOWING IN THE AREA OF THE BRYSON STORAGE FACILITY. AT 4:37 AM A SECOND AREA LANDOWNER, CONTACTED AN ETC EMPLOYEE AND ADVISED THAT HE HEARD GAS BLOWING IN THE AREA OF CEMENT MOUNTAIN ROAD. AT 4:40 AM, ETC GAS CONTROL WAS CONTACTED, AND ADVISED THERE WAS AN ISSUE AT THE BRYSON COMPRESSOR STATION AND ASKED TO STOP INJECTING, SHUT THE ENGINES DOWN, ISOLATE STATION VALVES & WAIT FOR A CALL BACK. OPERATIONS PERSONNEL RESPONDED ON SCENE AT 5:05 AM AND THE RUPTURE WAS CONFIRMED TO BE ON THE SIMPSON HEIRS 8" LATERAL AND WAS ISOLATED AND DEPRESSURIZED AT 5:08 AM. THE PIPELINE WAS REPAIRED BY REPLACING A SECTION OF LINE PIPE AND WAS MADE READY FOR SERVICE ON 8/23/13 AT 3:30 PM. FINAL UPDATE: NOV. 26, 2013 ALL PERMANENT REPAIRS WERE COMPLETED AND THE LINE WAS BROUGHT BACK IN SERVICE ON OCT. 23, 2013. THE LINE WAS MADE PIGGABLE BY REPLACING PIPE SIZES TO BE SAME. ALL DAMAGES WERE LIMITED TO GAS LOSS AND PIPE REPAIRS. ESTIMATED COST NOTED ON INITIAL REPORT REMAIN ACCURATE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130085 | 16113 | 2013-09-11 15:08 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2013-08-16 12:05 | 2013 |  |  | 29.306 | -93.0253 | 1057320 | 2013-08-16 13:25 |  | NATURAL GAS |  | 576 | 5891 | 4.5 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-08-16 13:00 | 2013-08-28 16:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-08-16 12:05 | 2013-08-16 12:05 | OFFSHORE | [28 empty] | 50 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST CAMERON | 192 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | VALVE | [31 empty] | MAINLINE | CHECK |  | TOM WHEATLEY |  |  |  | 1968 | 1968 | CARBON STEEL |  | LEAK |  |  | OTHER | DAMAGE DURING MAINTENANCE | [5 empty] | CLASS 1 LOCATION | NO |  | 567 |  | NO | NO | NO |  | 0 | 0 | 20935 | 23605.3225648075 | 2017 | 1574.74795081967 | 347000 | 391260.899450118 | 0 | 0 | 0 | 0 |  |  | 369952 | 192067.155615366 | 416440.969965745 | [8 empty] | 830 |  | 999 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL |  | NO |  |  |  | YES |  |  |  | YES |  |  |  |  | YES | OFFSHORE FACILITY, NOT COMPATIBLE | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE WAS BELOW MAOP AT ALL TIMES. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [103 empty] | OTHER OUTSIDE FORCE DAMAGE | [9 empty] | DIVERS PERFORMING A MAINTENANCE OPERATION INADVERTANTLY STRUCK AND BROKE OFF A 1/2" POWER GAS VALVE RESULTING IN GAS RELEASE. | [251 empty] | KENNETH C PETERS | SR. ENGINEER - PIPELINE | ken_peters@kindermorgan.com | 2053257554 | 2053253508 |  |  |  | KENNETH C PETERS | SR. ENGINEER - PIPELINE | 2053257554 | ken_peters@kindermorgan.com | ON AUGUST 16, 2013, CONTRACTED DIVERS PERFORMING WORK IN THE VICINITY OF A CHECK VALVE IN TENNESSEE GAS PIPELINE (TGP) COMPANY'S 26" 507K-100 PIPELINE (ON THE OCS) INADVERTANTLY STRUCK A 1/2 INCH POWER GAS SUPPLY VALVE. THE 1/2 INCH VALVE BROKE OFF THE CHECK VALVE, RELEASING NATURAL GAS AT A WATER DEPTH OF ABOUT 50 FEET. THE LEAK WAS ISOLATED AND REPAIRS WERE MADE WITH THE PIPELINE BEING PLACED BACK INTO SERVICE AUGUST 28, 2013.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130086 | 16116 | 2013-09-12 16:07 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2013-08-16 12:30 | 2013 |  |  | 28.5449 | -91.6884 | 1057328 | 2013-08-16 14:12 |  | NATURAL GAS |  | 2300 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-08-16 14:40 | 2013-08-22 02:14 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-08-16 12:30 | 2013-08-20 02:30 | OFFSHORE | [28 empty] | 160 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EUGENE ISLAND | 241 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 24 |  | 0.438 | 70000 | API 5L | DSAW |  | UNKNOWN | OTHER | CONCRETE | [27 empty] | 1974 | 1974 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 485 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 7590 | 5925.79918032787 | 430000 | 484847.800471328 | 0 | 0 | 0 | 0 |  |  | 437590 | 228701.479096107 | 490773.599651656 | [8 empty] | 889 |  | 1250 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 25872 | NO | [5 empty] | YES | PIPE IS ON THE OCS AND IS NOT SUITABLE FOR SMART PIG APPLICATIONS. | YES |  |  |  |  | YES | SEE 5D ABOVE. | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | 3RD PARTY AIRCRAFT NOT INVOLVED IN PATROL |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE WAS BELOW MAOP AT ALL TIMES. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  |  | YES |  |  |  | YES |  | YES | CONCLUSION BASED ON OPERATING HISTORY OF THE PIPELINE. | YES | [5 empty] | NO | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KENNETH C PETERS | SR. ENGINEER - PIPELINE | ken_peters@kindermorgan.com | 2053257554 | 2053253508 |  |  |  | KENNETH C PETERS | SR. ENGINEER - PIPELINE | 2053257554 | ken_peters@kindermorgan.com | ON AUGUST 16, 2013, TENNESSEE GAS PIPELINE (TGP) COMPANY RECEIVED A REPORT FROM A 3RD PARTY AIRCRAFT OF BUBBLES INDICATING A LEAK IN THE VICINITY OF TGP'S 24" 523M-3700 PIPELINE ON THE OCS, OFFSHORE LOUISIANA. THE LEAK WAS ISOLATED AND CONTRACTED DIVERS RESPONDED TO INVESTIGATE. A PINHOLE LEAK IN THE PIPE BODY AT THE 6 O'CLOCK POSITION NEAR THE GIRTH WELD WAS FOUND. A CLAMP WAS INSTALLED AND THE PIPELINE WAS PLACED BACK INTO SERVICE.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20130087 | 16412 | 2013-09-17 18:46 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2013-08-22 16:20 | 2013 |  |  | 28.36 | -92.5919 | 1057950 | 2013-08-22 17:42 |  | NATURAL GAS |  | 2241 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-08-22 16:30 | 2013-08-28 14:30 |  |  |  |  | NO |  |  |  |  | NO | [7 empty] | 2013-08-22 16:20 | 2013-08-23 04:00 | OFFSHORE | [28 empty] | 130 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | VERMILLION | 241 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PLATFORM, INCLUDING PLATFORM-MOUNTED EQUIPMENT AND PIPING | PIPE | PIPE BODY | 20 |  | 0.406 | 60000 | API-5LX-60 | DSAW |  | BETHLEHEM | OTHER | CONCRETE COATED | [27 empty] | 1979 | 1979 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 488 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 7844 | 6124.10655737705 | 454810 | 512822.391005499 | 0 | 0 | 0 | 0 |  |  | 462654 | 241748.148574427 | 518946.497562876 | [8 empty] | 771 |  | 1250 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | OFFSHORE GATHERING | YES | YES | YES | NO | NO | OTHER | 3RD PARTY AIRCRAFT |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PINHOLE LEAK WAS DETECTED BY 3RD PARTY | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  |  | YES |  | YES | SUSPECTED TO BE MICROBIOLOGICALLY INDUCED BASED UPON COMPANY'S KNOWLEDGE RELATED TO THE ASPECTS OF INTERNAL CORROSION. |  |  | YES | SEE RESPONSE IN ITEM 7 | YES | [5 empty] | NO | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | ZACHARY RAGAIN | ENGINEER - PIPELINE | zachary_ragain@kindermorgan.com | 713-420-6633 |  |  |  |  | REJI GEORGE | DIRECTOR - ENGINEERING | 713-420-5433 | reji_george@kindermorgan.com | A REPORT OF BUBBLES AND RAINBOW SHEEN NEAR VERMILION BLOCK 241 WAS REPORTED TO TGP ON 8/22/2013 AT APPROXIMATELY 4:20PM. A HELICOPTER AND BOAT WERE IMMEDIATELY DISPATCHED TO DETERMINE IF THE LOCATION OF THE REPORTED LEAK WAS NEAR TGP PIPELINES IN THE AREA. CONFIRMATION WAS MADE AT 5:45PM (8/22) BY TGP PERSONNEL. THERE WAS NO SHEEN OBSERVED DURING THE INITIAL CONFIRMATION FLIGHT, AND BUBBLES WERE 20' TO 20' DIAMETER. THE PRODUCER, LOCATED IN VERMILION BLOCK 261 WAS SHUT IN. ON 8/23/2013, A CONTRACT VESSEL WAS MOBILIZED FOR LEAK REPAIR. TGP PERSONNEL WORKED WITH DIVE BOAT PERSONNEL TO DETERMINE WHETHER THE LEAK IS ON A 12" LINE OR AN ADJACENT 20" LINE, IN ORDER TO INITIATE REPAIRS. THE DEPTH OF THIS PIPE IS APPROXIMATELY 130'. THE LEAKING PIPELINE WAS IDENTIFIED AS TGP'S 20" NATURAL GAS LINE (509A-100) IN VERMILION BLK 241. THE LINE WAS RAPAIRED WITH A 20" CLAMP AND WAS RETURNED TO SERVICE AT APPROXIMATELY 2:30 PM ON 8/28/2013.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130088 | 16282 | 2013-09-19 16:05 | SUPPLEMENTAL FINAL | 26330 | ENABLE OKLAHOMA INTRASTATE TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2013-08-20 11:05 | 2013 |  |  | 34.6952 | -95.9195 | 1057718 | 2013-08-20 18:20 |  | NATURAL GAS |  | 5100 | 680 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-08-20 11:22 | 2013-08-22 10:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2013-08-20 11:05 | 2013-08-20 11:25 | ONSHORE | OK | 74553 | KIOWA | PITTSBURG COUNTY | MILEPOST |  | L-263 |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 |  | 0.219 | 52000 | LONGITUDINAL ERW- HIGH FREQUENCY | LONGITUDINAL ERW - HIGH FREQUENCY |  | LONE STAR STEEL | EPOXY | [28 empty] | 2007 | 2007 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 36 | 12 |  | CLASS 1 LOCATION | NO |  | 305 |  | NO | NO | NO |  | 13500 | 15221.965828751 | 2300 | 2593.37195600943 | 17000 | 13272.5409836066 | 40000 | 45102.120974077 | 3000 | 3382.65907305577 | 0 | 0 |  |  | 75800 | 44193.7494365962 | 79572.6588154998 | [8 empty] | 1120 |  | 1200 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 50160 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPE SHOWING SIGNS OF THIRD PARTY DAMAGE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [64 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | [10 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [7 empty] | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO |  |  | UNKNOWN/OTHER | NO | DATA NOT COLLECTED | NO |  | PREVIOUS DAMAGE | [121 empty] | NO | [62 empty] | NO | NO |  |  | NO | [13 empty] | NO | [63 empty] | PATRICK KELLEY | DOT COMPLIANCE COORDINATOR | kenneth.kelley@enogex.com | 9186883330 |  |  |  |  | PAUL M BREWER | V.P. OPERATIONS | 4055257788 | No Email Address | MCALESTER LINE 263 RUPTURED JUST SOUTH OF KIOWA IN A PASTURE CAUSING A GRASS/TIMBER FIRE. LOCAL FIRE DEPARTMENT AND LOCAL AUTHORITIES ARRIVED ON SCENE TO ASSIST. NO INJURIES AND NO STRUCTURES WERE INVOLVED. THE PIPELINE FIRE DISSIPATED FROM SHUTTING THE GAS IN AND FIRE DEPARTMENT WAS ABLE TO CONTROL FIRE AND KEEP IT FROM SPREADING. THE DAMAGED SECTION OF PIPE WAS REMOVED AND SHOWED SIGNS OF THIRD-PARTY DAMAGE. IT HAS BEEN SENT TO A METALLURGIST FOR FURTHER ANALYSIS AND WE ARE AWAITING THE RESULTS. NOTE: THE DAMAGED SECTION OF PIPE WAS REPLACED. A GAUGE PIG WAS RAN ON 8/22/13 BEFORE PIPELINE WAS PLACED BACK INTO SERVICE. SUPPLEMENTAL INFORMATION. THE METALLURGIST REPORT CONCLUDED THAT THE THIRD PARTY DAMAGE RESULTED IN: FRACTURE INITIATED ON A DAMAGED AREA OF THE PIPELINE WHERE DEEP GOUGE MARKS WERE NOTED ON THE OUTSIDE SURFACE. THERE WERE TWO PARALLEL SCRAPE MARKS RUNNING ROUGHLY IN THE LONGITUDINAL DIRECTION AND PRODUCED CONSIDERABLE DEFORMATION OF THE STEEL. FINAL FAILURE OF THE PIPELINE WAS A RESULT OF DUCTILE OVERLOAD. EXTERNAL DAMAGE AND NECKING HAD RESULTED IN A WALL THICKNESS REDUCED TO APPROXIMATELY 0.160" FROM THE MEASURED 0.225" UNDAMAGED WALL NEARBY. THE UNDAMAGED SECTION OF PIPE WAS TESTED AND MET ALL THE REQUIREMENTS OF API SPECIFICATION 5L, PSL 2, GRADE X52.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130089 | 16149 | 2013-09-27 20:10 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2013-08-29 10:29 | 2013 |  |  | 36.8534 | -120.4527 | 1058688 |  |  | NATURAL GAS |  | 3000 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-08-29 15:45 | 2013-08-29 22:15 |  |  |  |  | NO |  |  |  |  | NO | [7 empty] | 2013-08-29 10:29 | 2013-08-29 10:47 | ONSHORE | CA | 93622 | FIREBAUGH | FRESNO | MILEPOST | 32.58 | LINE 134A |  | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | YES | [6 empty] | YES | UNCASED | CALIFORNIA IRRIGATION DISTRICT CANAL |  | SHORELINE/BANK/MARSH CROSSING | [11 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 4 |  | 0.225 | 35000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | ASPHALT | [28 empty] | 1957 | 1957 | CARBON STEEL |  | LEAK |  |  | OTHER | MOWER BLADE STRUCK PIPELINE | [5 empty] | CLASS 3 LOCATION | NO |  | 70 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 10000 | 7807.37704918033 | 195000 | 219872.839748625 | 5000 | 5637.76512175962 | 0 | 0 |  |  | 210000 | 111609.580441194 | 233317.981919565 | [8 empty] | 470 |  | 500 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CAUSE OF THE LEAK IS DUE TO A THIRD PARTY THAT STRUCK THE ABOVE GROUND PIPE WITH AN INDUSTRIAL MOWER BLADE DURING VEGETATION REMOVAL. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [260 empty] | CHERYL DIZON | COMPLIANCE ENGINEER | c1dz@pge.com | 925-328-5721 | 925-329-5591 |  |  |  | FRANCES YEE | MANAGER REGULATORY COMPLIANCE | 925-328-5733 | fsc2@pge.com | ON AUGUST 29, 2013 AT APPROXIMATELY 1029 HOURS, CENTRAL CALIFORNIA IRRIGATION DISTRICT (CCID) STRUCK THE 4-INCH GAS TRANSMISSION LINE 134A WITH THE BLADE OF A MOWER WHILE PERFORMING WEED CONTROL ALONG THE BANK OF AN IRRIGATION CANAL. NOTIFYING USA WAS NOT REQUIRED BECAUSE THE WORK DID NOT INCLUDE EXCAVATION ACTIVITIES. PACIFIC GAS AND ELECTRIC'S (PG&E) GAS SERVICE REPRESENTATIVE ARRIVED ON SCENE AT 1047 HOURS. THE FLOW OF GAS WAS STOPPED AT 1545 HOURS AND REPAIRS TO THE 4-INCH STEEL LINE WERE COMPLETED AT 2215 HOURS. COMPRESSED NATURAL GAS TRUCKS WERE DISPATCHED IN ORDER TO CONTINUE GAS SUPPLY FOR THE CITY OF FIREBAUGH. NO CUSTOMERS EXPERIENCED GAS SERVICE INTERRUPTION. THERE WERE NO FATALITIES, NO INJURIES AND NO IGNITION AS A RESULT OF THIS INCIDENT. OUT OF AN ABUNDANCE OF CAUTION, THE LOCAL POLICE AND FIRE DEPARTMENTS CLOSED HIGHWAY 33. THIS INCIDENT WAS REPORTED TO THE DOT AND CPUC BECAUSE THE COST OF DAMAGES DUE TO THE RELEASE OF GAS IS ESTIMATED ABOVE $50,000 AND THE VOLUME OF GAS RELEASED IS APPROXIMATELY THREE MILLION CUBIC FEET.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130090 | 16174 | 2013-10-03 12:01 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2013-09-09 12:20 | 2013 |  |  | 28.5453 | -91.6732 | 1059668 | 2013-09-09 13:25 |  | NATURAL GAS |  | 2405 | 8120 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-09-11 18:00 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-09-09 12:20 | 2013-09-10 18:00 | OFFSHORE | [28 empty] | 160 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EUGENE ISLAND | 241 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 24 |  | 0.438 | 70000 | API 5L | DSAW |  | UNKNOWN | OTHER | CONCRETE | [27 empty] | 1974 | 1974 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 585 |  | NO | NO | NO |  | 0 | 0 | 36837 | 41535.6707580519 | 8418 | 6572.25 | 500000 | 563776.512175962 | 0 | 0 | 0 | 0 |  |  | 545255 | 284668.014238021 | 611884.432934014 | [8 empty] | 970 |  | 1250 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 25872 | NO | [5 empty] | YES | PIPE IS ON THE OCS AND IS NOT SUITABLE FOR SMART PIG APPLICATIONS. | YES |  |  |  |  | YES | SEE 5D ABOVE. | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | REPORTED BY TRANSPORTER VESSEL OF 3RD PARTY OPERATOR. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE OPERATION WAS NORMAL DUE TO MINIMAL SIZE OF LEAK. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  |  | YES |  |  |  | YES |  | YES | ANALYSIS BASED UPON OPERATING HISTORY OF THE PIPELINE. | YES | [5 empty] | NO | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | MERLIN H MOSEMAN | ENGINEER-PIPELINE | merlin_moseman@kindermorgan.com | 7134204614 | 7134207464 |  |  |  | MERLIN H MOSEMAN | ENGINEER-PIPELINE | 7134204614 | merlin_moseman@kindermorgan.com | ON SEPTEMBER 9, 2013, TENNESSEE GAS PIPELINE (TGP) COMPANY WAS NOTIFIED BY TC OFFSHORE, A THIRD PART VENDOR FOR ANOTHER PIPELINE OPERATOR, OF A POTENTIAL OFFSHORE LEAK. BASED UPON THE LEAK COORDINATES IT WAS SUSPECTED THAT THE SOURCE OF THE LEAK WAS TGP'S 24" LINE 523M-3700 LOCATED ON THE OCS IN EUGENE ISLAND BLOCK 241. AFTER CONFIRMATION THAT THE LEAK WAS INDEED FROM THE TGP PIPELINE, THE PIPELINE SEGMENT WAS ISOLATED AND BLOWN DOWN. THE PIN HOLE SIZED LEAK ON THE BOTTOM QUADRANT OF THE PIPELINE WAS SECURED BY THE INSTALLATION OF A REPAIR CLAMP ON SEPTEMBER 15, 2013. THE PIPELINE SEGMENT HAS NOT BEEN RETURNED TO SERVICE SINCE THE REPAIR AND WILL NOT BE RETURNED TO SERVICE PENDING ABANDONMENT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130091 | 16332 | 2013-10-15 16:07 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2013-09-16 08:15 | 2013 |  |  | 32.3156 | -108.6089 | 1060314 | 2013-09-16 10:25 |  | NATURAL GAS |  | 7800 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | REGULATOR REPAIRED PROMPTLY | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-09-16 08:15 | 2013-09-16 08:15 | ONSHORE | NM | 88045 | LORDSBURG | HIDALGO | MILEPOST | 341 | LORDSBURG COMPRESSOR STATION | 1ST CUT FUEL GAS "B" BUILDING | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1969 |  | CARBON STEEL |  | OTHER | [8 empty] | A MOONEY REGULATOR FAILED BECAUSE OF A DIAPHRAGM THAT RUPTURED DUE TO LOSS OF FLEXIBILITY. THE REGULATOR FAILURE TRIGGERED THE RELIEF VALVE TO OPEN. THE RELIEF VALVE FUNCTIONED PROPERLY BY OPENING. THE MOONEY FLOWGRID REGULATOR IS SIZE 2 INCH WITH A CAPACITY OF 535.956 MCF PER HOUR. THE AGCO RELIEF VALVE INLET SIZE 3 INCHES AND OUTLET SIZE 4 INCHES WITH A CAPACITY OF 611.206 MCF PER HOUR. | CLASS 1 LOCATION | NO |  | 21 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 31200 | 24359.0163934426 | 100 | 112.755302435192 | 0 | 0 | 0 | 0 |  |  | 31300 | 25305.8560197288 | 24471.7716958778 | [8 empty] | 253 |  | 230 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE EXCEEDED MAOP, BUT DID NOT EXCEED THE APPLICABLE ALLOWANCE IN 192.201 | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  |  |  | YES | [6 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [25 empty] | YES | RUBBER BOOT FAILED IN REGULATOR | [161 empty] | ZACHARY RAGAIN | ENGINEER - PIPELINE | zachary_ragain@kindermorgan.com | 713-420-6633 |  |  |  |  | REJI GEORGE | DIRECTOR - ENGINEERING | 713-420-5433 | reji_george@kindermorgan.com | REGULATOR FAILED CAUSING RELIEF VALVE TO OPEN. DID NOT EXCEED MAOP PLUS ALLOWABLE BUILDUP. A MOONEY FLOWGRID REGULATOR FAILED BECAUSE OF A DIAPHRAM THAT RUPTURED DUE TO LOSS OF FLEXIBILITY. THE REGULATOR FAILURE TRIGGERED THE RELIEF VALVE TO OPEN. THE RELIEF VALVE FUNCTIONED PROPERLY. THE MOONEY FLOWGRID REGULATOR IS SIZE 2 INCH WITH A CAPACITY OF 535.956 MCF PER HOUR. THE AGCO RELIEF VALVE HAS AN INLET SIZE 3 INCHES AND OUTLET SIZE 4 INCHES WITH A CAPACITY OF 611.206 MCF PER HOUR. THE REGULATOR WAS REBUILT WITH A NEW DIAPHRAM AND PLACED BACK IN SERVICE 9/16/2013.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130092 | 16229 | 2013-10-17 11:55 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2013-09-21 16:51 | 2013 |  |  | 30.4329 | -92.875 | 1060873 | 2013-09-21 18:04 |  | NATURAL GAS |  | 13000 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | [7 empty] | NO |  |  |  |  | NO | [7 empty] | 2013-09-21 16:51 | 2013-09-21 16:51 | ONSHORE | LA | 70648 | KINDER | JEFF DAVIS | MILEPOST | 823-1 | STATION 823 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2010 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE VENTED PREMATURELY. | CLASS 1 LOCATION | NO |  | 211 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 52000 | 40598.3606557377 | 500 | 563.776512175962 | 0 | 0 | 0 | 0 |  |  | 52500 | 42348.9522297915 | 41162.1371679137 | [8 empty] | 851 |  | 937 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | DEBRIS IN RELIEF VALVE | [161 empty] | THOMAS N. MEEK JR | COORDINATOR - OPS SRII | thomas_meekjr@kindermorgan.com | 505-831-7718 | 505-831-7735 |  |  |  | REJI GEORGE | DIRECTOR - ENGINEERING | 713-420-5433 | reji_george@kindermorgan.com | RELIEF VALVE OPENED PREMATURELY VENTING NATURAL GAS. DID NOT EXCEED MAOP. FOLLOW UP ACTIONS ON THE RELIEF VALVE: 1. INSPECTED AND CLEANED SNAP ACTING PILOT CONTROL VALVE ( SEAT AND VALVE). 2. SNAP ACTING PILOT CONTROL VALVE TOTALLY REBUILT. 3. REPLACED PILOT RANGE SPRING WITH NEW RELEASE SET POINT (601-1001 PSI) TO OPERATE EFFICIENTLY AT PRESSURES IN THIS RANGE. 4. INSPECTED AND CLEAN RELIEF VALVE BODY.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130093 | 16216 | 2013-10-24 08:42 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2013-09-28 20:03 | 2013 |  |  | 36.3214 | -97.3899 | 1061558 | 2013-09-28 21:35 |  | NATURAL GAS |  | 25400 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-09-28 21:51 | 2013-10-08 13:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 1 | 2013-09-28 20:03 | 2013-09-28 21:20 | ONSHORE | OK | 73077 | PERRY | NOBLE | SURVEY STATION NO. | 220/-2427+68 | LINE V | OKLAHOMA CITY-DILWORTH 20" | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 31 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | DRESSER COUPLING FAILURE | 1930 |  | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | PIPE PULLED OUT OF DRESSER COUPLING |  |  |  | CLASS 1 LOCATION | NO |  | 336 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 83875 | 65484.375 | 325000 | 366454.732914376 | 0 | 0 | 0 | 0 |  |  | 408875 | 236103.016987431 | 431939.107914376 | [8 empty] | 545 |  | 594 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 79200 | NO | [5 empty] | YES | LINE IS A COUPLED PIPELINE. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | OTHER | PIPE PULLED OUT OF DRESSER COUPLING | [16 empty] | YES | DRESSER COUPLING IS ONLY KNOWN ISSUE REGARDING THIS FAILURE. | [161 empty] | DAVID COOMES | COMPLIANCE ENGINEER | david.coomes@sscgp.com | 270.852.4391 |  |  |  |  | DAVID SINCLAIR | PIPELINE COMPLIANCE MANAGER | 270.852.4424 | No Email Address | AT APPROXIMATELY 8:03 PM SSCGP GAS CONTROL NOTICE A DROP IN PRESSURE ON LINE V-OKLAHOMA DILLWORTH LINE, AND AT 8:08 PM RECEIVED A CALL FROM A LOCAL RESIDENT NOTIFYING SSCGP OF A POSSIBLE INCIDENT. LOCAL OPERATIONS WERE IMMEDIATELY CALLED TO BE DISPATCHED TO THE SITE TO CONFIRM THE SITUATION AND MAKE ANY NECESSARY CORRECTIONS. EDMOND STATION COMPRESSOR, FEEDS LINE V, WAS SHUTDOWN AT 8:14 PM AND GAS FLOWS WERE BEING DIVERTED AROUND AFFECTED AREA. AT 8:23 SSCGP GAS CONTROL NOTIFIED LOCAL EMERGENCY RESPONDERS OF THE SITUATION OF WHICH THEY WERE ALREADY AWARE. LOCAL OPERATIONS ARRIVED ON SCENE AT 9:20 PM AND AFTER CONFIRMING THAT THE SCENE HAD BEEN MADE SAFE THROUGH EVACUATIONS BEGAN ISOLATING THE FAILED LINE SEGMENT. THE LINE FAILURE WAS COMPLETELY ISOLATED AT 9:51 PM. THERE WAS NO FIRE COMBINED WITH THE BLOWING GAS DURING THIS INCIDENT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130094 | 16449 | 2013-10-28 09:26 | SUPPLEMENTAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 1111 LOUISIANA STREET | HOUSTON | TX | 77002 | 2013-10-01 16:53 | 2013 |  |  | 35.425 | -98.544 | 1061822 | 2013-10-01 18:58 |  | NATURAL GAS |  | 12449 | 14321 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-10-01 22:42 | 2013-10-02 18:17 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-10-01 16:53 | 2013-10-01 17:35 | ONSHORE | OK | 73048 | HYDRO | CADDO | SURVEY STATION NO. | 2133+41 | LINE AD WEST |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 24 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 |  | 0.266 | 65500 | X65 | DSAW |  | REPUBLIC | COAL TAR | [28 empty] | 1973 | 1973 | CARBON STEEL |  | MECHANICAL PUNCTURE | 1.5 | 1 | [7 empty] | CLASS 1 LOCATION | NO |  | 524 |  | NO | NO | NO |  | 0 | 0 | 49551 | 55871.3799096622 | 43074 | 33629.4959016393 | 59000 | 66525.6284367636 | 1000 | 1127.55302435192 | 0 | 0 |  |  | 152625 | 91566.2585009594 | 157154.057272417 | [8 empty] | 770 |  | 1000 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 92294 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY STRUCK THE PIPELINE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  |  |  | YES | [6 empty] | FARMER | UNKNOWN/OTHER | AGRICULTURE | NO |  |  | UNKNOWN/OTHER | NO | UNKNOWN/OTHER | YES | 24 | OTHER |  |  |  | NO ONE-CALL NOTIFICATION WAS MADE. | [262 empty] | JIMMY CROSS | COMPLIANCE COORDINATOR | jimmy.cross@centerpointenergy.com | 3184293664 | 3184293997 |  |  |  | JOHNNY CAVITT | MANAGER OF DOT COMPLIANCE | 3184293606 | johnny.cavitt@centerpointenergy.com | FARMER'S CONTRACTOR WAS LEVELING LAND. NO ONE-CALL WAS MADE BY THE FARMER OR CONTRACTOR. COMPANY EMPLOYEES DISCOVERED THE EXCAVATION IN PROGRESS. COMPANY EMPLOYEES SHUT DOWN THE WORK AND EXPLAINED THAT A PIPELINE WAS IN THE DIRECT VICINITY OF THE WORK. COMPANY EMPLOYEES EXPLAINED THAT THE ONE-CALL CENTER MUST BE NOTIFIED. THE EQUIPMENT OPERATOR SAID HE WAS DONE FOR THE DAY AND WOULD MAKE THE REQUIRED ONE-CALL NOTIFICATION PRIOR TO CONTINUING THE WORK. COMPANY EMPLOYEES LEFT THE LOCATION AND WHERE LATER NOTIFIED OF THE HIT/BLOWING LINE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130095 | 16521 | 2013-10-30 12:52 | SUPPLEMENTAL FINAL | 38987 | KINETICA ENERGY EXPRESS LLC | 1001 MCKINNEY STREET, SUITE 900 | HOUSTON | TX | 77002 | 2013-10-10 12:35 | 2013 |  |  | 28.8047 | -92.1286 | 1062628 | 2013-10-10 13:35 |  | NATURAL GAS |  | 411 | 6331 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-10-10 14:45 | 2013-10-19 10:32 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-10-10 12:35 | 2013-10-10 13:10 | OFFSHORE | [28 empty] | 150 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SMI | 42 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12.75 |  | 0.5 | 52000 | ASTM A106 | SEAMLESS |  | U.S. STEEL | OTHER | UNKNOWN | [27 empty] | 1978 | 1977 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO | NO |  | 0 | 0 | 21906 | 24700.1765514533 | 1422 | 1110.20901639344 | 341700 | 385284.868421053 | 10000 | 11275.5302435192 | 0 | 0 |  |  | 375028 | 194520.723854842 | 422370.784232419 | [8 empty] | 845 |  | 1250 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL |  | NO |  | YES |  | YES |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS LOCATED AT -150 DEPTH IN REMOTE LOCATION. BUBBLE ON WATER SURFACE WAS SPOTTED BY BSEE PERSONNEL. PIPELINE PRESSURE WERE IN NORMAL OPERATING RANGE. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  | YES | [6 empty] | YES | LOW FLOW, NON PIGGABLE SYSTEM. |  |  |  |  | YES | BODY OF PIPE IN 6 O'CLOCK POSITION | NO | YES | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | SUSIE RICHMOND | MANAGER DOT COMPLIANCE AND TRAINING | susie.richmond@kineticallc.com | 985-223-6145 |  |  |  |  | SUSIE RICHMOND | MANAGER DOT COMPLIANCE AND TRAINING | 985-223-6145 | susie.richmond@kineticallc.com | ON 10.9.13 DURING ROUTINE OPERATIONS, A BSEE INSPECTOR IDENTIFIED BUBBLES IN SMI 41. UPON RETURNING TO THE OFFICE THEY LOOKED AT THE PIPELINE DATABASE AND IDENTIFIED THE 523M-1300 AS THE MOST LIKELY SOURCE OF THE RELEASE. UPON NOTIFICATION KINETICA DISPATCHED A HELICOPTER AND CREW TO VERIFY THE LEAK LOCATION AND INITIATE SHUT IN OF THE PIPELINE. CORROSION MONITORING COUPONS ARE IN USE ON THE PIPELINE ALTHOUGH NOT INDICATIONS WERE RECEIVED. KINETICA ACQUIRED THIS PIPELINE AS PART OF THE PURCHASE FROM TENNESSEE GAS PIPELINE COMPANY. AT THIS TIME, THE TGP / EP PROGRAMS FOR CORROSION MONITORING AND PREVENTION PROGRAMS WHICH HAVE BEEN UTILIZED ON THE ASSETS ARE UNDERGOING THIRD PARTY EVALUATION BY TWO ORGANIZATIONS, CORRPRO AND NALCO CHAMPION. NOTE: NO ADDITIONAL INFORMATION, THIS WAS JUST THE ONLY WAY I COULD GET THE SYSTEM TO CREATE A FINAL REPORT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130096 | 16252 | 2013-10-30 20:27 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2013-10-27 14:05 | 2013 |  |  | 43.6734 | -94.5908 | 1064169 | 2013-10-27 16:45 |  | NATURAL GAS |  | 3000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | A RELIEF VALVE RESET | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-10-27 14:05 | 2013-10-27 14:35 | ONSHORE | MN | 56181 | WELCOME | MARTIN | MILEPOST |  | M460B WELCOME TO MINNEAPOLIS 1P MAINLINE |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1982 |  | CARBON STEEL |  | OTHER | [8 empty] | A PILOT OPERATED RELIEF VALVE OPENED UNEXPECTEDLY AND RELEASE OVER 3,000 MCF OF GAS TO ATMOSPHERE IN ABOUT 30 MINUTES. | CLASS 1 LOCATION | YES | METHOD2 | 311 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 18000 | 14053.2786885246 | 100 | 112.755302435192 | 300 | 338.265907305578 | 0 | 0 |  |  | 18400 | 14776.7027674398 | 14504.2998982654 | [8 empty] | 770 |  | 796 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER MADE NO ACTION THAT CAUSED THE PILOT OPERATED RELIEF TO FAIL. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | WATER (CONDENSATE) AND DEBRIS (DIRT) IN PILOT REGULATOR | [161 empty] | JOHN GORMLEY | SR CORROSION SPECIALIST | john.gormley@nngco.com | 402-398-7494 |  |  |  |  | TOM CORRELL | DIRECTOR - PIPELINE SAFETY | 402-398-7715 | thomas.correll@nngco.com | AT 1405 ON SUNDAY, OCTOBER 27, 2013 NORTHERN NATURAL GAS COMPANY'S OPERATION COMMUNICATION CENTER (24 HOUR EMERGENCY) RECEIVED A PHONE CALL FROM A NEIGHBOR STATING THAT THERE WAS A VERY LOUD NOISE COMING FROM THE INTERCONNECT WITH NORTHERN BORDER PIPELINE. LOCAL EMPLOYEES WERE NOTIFIED AND RESPONDED WITHIN 30 MINUTES. THE INTERCONNECT IS ABOUT 1.5 MILES EAST OF WELCOME, MN WHERE EMPLOYEES LIVE. THE LOCAL EMPLOYEES IMMEDIATELY INVESTIGATED THE CAUSE. THE RELIEF IS SET TO RELIEVE AT 830 PSI BUT WAS OPEN AND RELEASING NATURAL GAS TO THE ATMOSPHERE AT 770 PSI. THE RELIEF VALVE RESET AUTOMATICALLY WHEN THE PRESSURE DROPPED TO 740 PSI AFTER NORTHERN BORDER SHUT OFF ITS DELIVERY. THE METER AND REGULATING STATION NORMALLY OPERATES BETWEEN 770 AND 780 PSI. CHANGES TO DELIVERY VOLUMES OCCUR OFTEN. THE GAS CONTROL LOG DID NOT INDICATE A DROP IN PRESSURE FOR THE 30 MINUTES THE RELIEF VALVE WAS OPEN. THE LOCAL EMPLOYEES DISASSEMBLED THE PILOT AND FOUND DIRT AND MOISTURE INSIDE THAT MUST HAVE CAUSED THE RELIEF VALVE TO OPEN AT THE LOWER PRESSURE. THE PILOT WAS REPAIRED, REINSTALLED AND TESTED. THE EMPLOYEES LEFT AFTER THEY VERIFIED THAT EVERYTHING WAS BACK TO NORMAL, AROUND 1800 HOURS. THE ATTACHED PRESSURE LOG SHOWS THAT NORTHERN NATURAL GAS CONTROLLERS CALLED NORTHERN BORDER GAS CONTROLLERS TO CEASE DELIVERIES UNTIL NORTHERN NATURAL EMPLOYEES COULD APPROACH THE RELIEF VALVE AND AFFECT REPAIRS. NORTHERN BORDER RETURNED TO NORMAL OPERATION AFTER THE PILOT WAS REPAIRED AND TESTED. LOCAL EMPLOYEES NOTIFIED NORTHERN NATURAL GAS CONTROL WHO NOTIFIED NORTHERN BORDER GAS CONTROL.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130097 | 16475 | 2013-11-02 15:02 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2013-11-01 16:35 | 2013 |  |  | 41.6218 | -93.2166 | 1064645 | 2013-11-01 17:08 |  | NATURAL GAS |  | 7119 | 19 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-11-01 18:30 | 2013-11-02 09:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 3 | 2013-11-01 16:45 | 2013-11-01 18:00 | ONSHORE | IA | 50228 | PRAIRIE CITY | JASPER | MILEPOST | 5.59 | MONROE 4-INCH BRANCH LINE | IAB42801 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 32 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 4 |  | 0.156 | 35000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | YOUNGSTOWN | EXTRUDED POLYEHYLENE | [28 empty] | 1966 | 1966 | CARBON STEEL |  | MECHANICAL PUNCTURE | 1.5 | 1 | [7 empty] | CLASS 1 LOCATION | NO |  | 78 |  | NO | NO | NO |  | 0 | 0 | 6000 | 6765.31814611155 | 18000 | 14053.2786885246 | 50000 | 56377.6512175962 | 50000 | 56377.6512175962 | 0 | 0 |  |  | 124000 | 69432.7907485867 | 133573.899269829 | [8 empty] | 780 |  | 800 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 52000 | NO |  | YES | [5 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A THIRD PARTY LINE HIT OUT OF THE CONTROLLERS SPHERE OF INFLUENCE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | TRENCHER | DRAINAGE | NO |  |  | DATA NOT COLLECTED | NO | NO | NO |  | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | JOHN GORMLEY | SR CORROSION SPECIALIST | john.gormley@nngco.com | (402) 398-7949 |  |  |  |  | TOM CORRELL | SR DIRECTOR - PIPELINE SAFETY AND RISK | (402) 398-7715 | thomas.correll@nngco.com | AT APPROXIMATELY 4:30 PM (16:30) ON FRIDAY, NOVEMBER 1, 2013, NORM ROZENDAAL TILING, INC WAS INSTALLING DRAIN TILE ON A FARM NEAR PRAIRIE CITY, IOWA WHEN HIS TILE MACHINE IMPACTED AND PUNCTURED A HOLE IN NORTHERN NATURAL GAS COMPANY'S 4-INCH MONROE, IOWA (IAB42801) BRANCH LINE. THE OPERATOR EVACUATED THE TILE MACHINE IN-PLACE WHEN HE HEARD GAS BLOWING AND CALLED 911. NORTHERN PERSONNEL WERE DISPATCHED TO THE SITE TO CONTROL THE EMERGENCY AND BEGIN REPAIRS IMMEDIATELY. THE PIPELINE IS CONNECTED TO 3 IOWA TOWNS THAT NEVER LOST SERVICE WHEN NORTHERN UTILIZED THEIR VOLUME BOTTLE TRAILERS AND WERE ABLE TO CONTINUE SERVICE TO CUSTOMERS WHILE THE PIPELINE WAS BEING REPAIRED. THE REPAIR CONSISTED OF INSTALLING A 10'-4" LENGTH OF PIPE REPLACEMENT. THE DAMAGED SECTION IS BEING HELD FOR FURTHER ANALYSIS. THE PIPELINE WAS RETURNED TO SERVICE AT APPROXIMATELY 9:00 AM (09:00) ON SATURDAY, NOVEMBER 2, 2013. THERE WAS NO ONE-CALL MADE TO THE IOWA ONE-CALL CENTER PRIOR TO THE EXCVATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130099 | 16421 | 2013-11-05 11:42 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2013-10-08 23:45 | 2013 |  |  | 36.9496 | -99.9859 | 1062460 | 2013-10-09 00:30 |  | NATURAL GAS |  | 40000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-10-09 02:00 | [5 empty] | YES |  |  |  |  | NO | [6 empty] | 0 | 2013-10-08 23:45 | 2013-10-09 03:00 | ONSHORE | OK | 73855 | ROSSTON | HARPER | MILEPOST | MP 34.31 | M680C BEAVER TO MULLINVILLE C-LINE | OKM10703-M680C | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 40 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 |  | 0.344 | 52000 | 5LX | DSAW |  | REPUBLIC | COAL TAR | [28 empty] | 1954 | 1954 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 1200 | 90 |  | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 160000 | 124918.032786885 | 55000 | 62015.4163393559 | 70000 | 78928.7117046348 | 0 | 0 |  |  | 285000 | 194205.270562631 | 265862.160830876 | [8 empty] | 806 |  | 860 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL |  | NO |  | YES | [5 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES | YES |  |  | YES | YES | 1954 | YES | YES | YES |  |  |  | 2013 |  |  |  | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | JOHN GORMLEY | SR CORRSION SPECIALIST | john.gormley@nngco.com | 402-398-7494 |  |  |  |  | TOM CORRELL | DIRECTOR PIPELINE SAFETY | (402) 398-7715 | thomas.correll@nngco.com | ON OCTOBER 8, 2013 AT APPROXIMATELY 10:40 PM (22:40) NORTHERN'S 30-INCH BEAVER TO MULLINVILLE (OKM10703-M680C) C-LINE FAILED. THE FAILURE RESULTED IN A RELEASE OF NATURAL GAS AND A SUBSEQUENT FIRE. THE FAILURE OCCURRED IN A CULTIVATED FIELD LOCATED IN HARPER COUNTY, OKLAHOMA NEAR MILE POST 34.22. THE AREA IS WEST OF US HIGHWAY 283 AND SOUTH OF E0040 ROAD. THE FAILURE DID NOT CAUSE ANY INJURIES OR EVACUATIONS. WHILE THE FIRE DESTROYED SOME CROPS, NO OTHER PROPERTY DAMAGE WAS REPORTED. NORTHERN'S SHIFT OPERATOR LOCATED AT THE BEAVER COMPRESSOR STATION DISCOVERED THE PRESSURE ON THE BEAVER TO MULLINVILE M680C LINE WAS DECREASING AT AN ABNORMAL RATE. HE WAS ALSO ABLE TO SEE THE FIRE IN THE DISTANCE. THE FAILED SECTION WAS SUBSEQUENTLY ISOLATED WHEN THE UPSTREAM AND DOWNSTREAM MAINLINE VALVES WERE CLOSED. THE INVESTIGATION TEAM BEGAN TO EXAMINE THE SITE AND COLLECT EVIDENCE ON OCTOBER 9. THE FAILURE HAD OPENED A HOLE ALONG THE RIGHT-OF-WAY ABOUT 45 FEET AT ITS WIDEST AND 200 FEET LONG. SEVERAL SECTIONS OF PIPE HAD BEEN EJECTED FROM THE DITCH. ALL OF THE FAILED PIPE WAS SENT TO STRESS ENGINEERING SERVICES IN HOUSTON, TEXAS FOR EXAMINATION. THE PIPE WAS RECEIVED IN HOUSTON ON OCTOBER 13. STRESS DETERMINED THAT THE FAILURE WAS A DIRECT RESULT OF AN AREA OF EXTERNAL CORROSION ABOUT 9 INCHES LONG BY 3 INCHES CIRCUMFERENTIALLY. ON OCTOBER 16, 2013, NORTHERN RECEIVED APPROVAL FROM THE SW REGION OF PHMSA TO RETURN THE PIPELINE TO SERVICE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130101 | 16438 | 2013-11-15 16:56 | SUPPLEMENTAL FINAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2013-10-22 20:30 | 2013 |  |  | 27.2742 | -98.1552 | 1063752 | 2013-10-22 21:56 |  | NATURAL GAS |  | 8913 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-10-22 20:30 | 2013-10-23 13:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-10-22 20:30 | 2013-10-22 20:30 | ONSHORE | TX | 78355 | FALFURRIAS | JIM WELLS | MILEPOST |  | DCP LA GLORIA PIN 900439 | ROUTE ID 3358 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2009 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE MALFUNCTION | CLASS 1 LOCATION | NO |  | 251 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 33149 | 25880.6741803279 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 33149 | 26831.6700819672 | 25880.6741803279 | [8 empty] | 831 |  | 815 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE EXCEEDED MAOP, BUT DID NOT EXCEED THE APPLICABLE ALLOWANCE IN 192.201 | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | NO | YES | YES | OTHER | NOTIFICATION FROM THIRD PARTY OPERATOR |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL REACTED TO SUSPECTED INCIDENT NOTIFICATION PER PROCEDURES. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | LIQUID IN RELIEF VALVE PILOT OPERATOR CAUSED VALVE TO REMAIN OPEN. | [161 empty] | MERLIN MOSEMAN | ENGINEER - PIPELINE SR | merlin_moseman@kindermorgan.com | 713-420-4614 |  |  |  |  | MERLIN MOSEMAN | ENGINEER - PIPELINE SR | 713-420-4614 | merlin_moseman@kindermorgan.com | INDICATION OF VENTING RELIEF VALVE REPORTED TO NGPL BY A THIRD PARTY PIPELINE OPERATOR WITH PIPELINE FACILITIES CONNECTED TO THE NGPL FACILITIES AT APPROXIMATELY 7:58 PM ON 10/22/2013 AT WHICH TIME THEY CLOSED THEIR ISOLATION VALVE TO THE NGPL FACILITY. AN NGPL TECHNICIAN WAS CALLED OUT AND ARRIVED AT THE DCP LA GLORIA STATION AT APPROXIMATELY 8:30 PM, CONFIRMED THAT IT WAS THE NGPL RELIEF VALVE THAT WAS VENTING AND COMPLETED THE ISOLATION OF THE PIPING TO THE RELIEF VALVE. THE STATION REMAINED OUT OF SERVICE UNTIL THE RELIEF VALVE COULD BE MADE FUNCTIONAL BY REMOVAL OF THE LIQUIDS IN THE PILOT OPERATOR AND WAS RETURNED TO SERVICE AT APPROXIMATELY 1:45 PM ON 10/23/2013. THE RELIEF VALVE PILOT GAS PIPING WAS MODIFIED WITH THE INSTALLATION OF A LIQUID FILTER TO PREVENT A RECURRENCE OF THIS EVENT SINCE THE VALVE DID NOT RESET OR CLOSE WHEN THE INLET PRESSURE DROPPED BELOW THE VALVE SET POINT.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20130102 | 16361 | 2013-11-21 09:40 | SUPPLEMENTAL | 18646 | ENBRIDGE OFFSHORE (GAS TRANSMISSION) LLC | 1100 LOUISIANA ST. SUITE 3300 | HOUSTON | TX | 77002 | 2011-10-25 15:36 | 2011 |  |  | 28.3257 | -93.324 | 993570 | 2011-10-25 18:04 |  | NATURAL GAS |  | 3906 |  | 1.33 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-10-25 17:30 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-10-25 15:36 | 2011-10-25 16:30 | OFFSHORE | [28 empty] | 195 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WC | 543 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 |  | 0.406 | 46000 | API 5L X-46 | SEAMLESS |  | DON'T KNOW | OTHER | CONCRETE | [27 empty] | 1976 | 1976 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 30 |  | NO | NO | NO |  | 0 | 0 | 67900 | 79447.2895863053 | 1000 | 676.731793960924 | 0 | 0 | 314000 | 367399.836967597 | 0 | 0 |  |  | 382900 | 205816.220547657 | 447523.858347863 | [8 empty] | 1090 |  | 1200 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 38648 | NO |  | YES | [5 empty] | YES |  |  |  |  | YES | UNSUITABLE MAINLINE VALVES | OFFSHORE GATHERING | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PLATFORM OPERATOR NOTIFIED GAS CONTROL BY TELEPHONE OF THE LEAK. GAS CONTROL NOTIFIED ENBRIDGE OPERATING PERSONEL. ENBRIDGE OPERATING PERSONEL THEN INVESTIGATED. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING | [5 empty] | YES | DON'T KNOW |  |  | YES | PIPE WAS NOT OPENED. EXTERNAL PIPE CLAMP INSTALLED. |  |  |  |  | YES | 6 O'CLOCK POSITION | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO | [16 empty] | NO | [63 empty] | LESLIE STEVENS | COMPLIANCE COORDINATOR | leslie.stevens@enbridge.com | 832-214-1649 |  |  |  |  | LESLIE STEVENS | COMPLIANCEJ COORDINATOR | 832-214-1649 | leslie.stevens@enbridge.com | GAS CONTROL RECEIVED A CALL FROM THE WC 544 PLATFORM AT APPROXIMATELY 1530, NOTIFYING THEM OF A LEAK APPROXIMATELY 2.5 MILES SE OF THE PLATFORM (IN THE WC 543 BLOCK). THIS BLOCK IS APPROXIMATELY 100 MILES FROM SHORE, IN ABOUT 200 FEET OF WATER. A HELICOPTER OVERFLIGHT CONFIRMED A BUBBLE 30 DIAMETER AND A SHEEN (LIGHT RAINBOW COLOR) OF 2 MILES LONG BY 500 FT WIDE. THE CALCULATED SPILLED VOLUME IS AROUND 1.3 BARRELS.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20130103 | 16362 | 2013-11-21 11:48 | SUPPLEMENTAL | 18646 | ENBRIDGE OFFSHORE (GAS TRANSMISSION) LLC | 1100 LOUISIANA ST. SUITE 3300 | HOUSTON | TX | 77002 | 2011-08-28 14:00 | 2011 |  |  | 29.392 | -93.1737 | 987528 | 2011-08-28 16:06 |  | NATURAL GAS |  | 1100 | 30000 | 0.33 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-08-29 12:10 | 2012-04-10 06:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-08-28 14:00 | 2011-08-29 12:00 | OFFSHORE | [28 empty] | 48 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WC | 173 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 |  | 0.375 | 60000 | API 5L X-60 | SEAMLESS |  | ? | OTHER | SOMASTIC AND 190 PCF CONCRETE | [27 empty] | 1971 | 1971 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 20 |  | NO | NO | NO |  | 0 | 0 | 104000 | 121686.570205828 | 20000 | 13534.6358792185 | 70074 | 81991.0069288771 | 0 | 0 | 0 | 0 |  |  | 194074 | 107525.353891801 | 217212.213013924 | [8 empty] | 900 |  | 1300 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 23806 | NO |  | YES | [5 empty] | YES |  |  |  |  | YES | UNSUITABLE MAINLINE VALVES | OFFSHORE GATHERING | YES | YES | YES | NO | NO | AIR PATROL |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK IN LINE WAS SPOTTED BY OPERATROR WHILE FLYING OVER THE AREA. IT WAS A SMALL LEAK THAT WOULD BE UNDETECED BY SCADA. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING | [5 empty] | YES | DON'T KNOW. PIPE WAS REPAIRED WITH CLAMP. |  |  | YES | PIPE WAS REPAIRED WITH CLAMP. | YES | [5 empty] | YES | NO | NOT APPLICABLE - NOT MAINLINE PIPE | YES | [168 empty] | NO | [66 empty] | NO | [13 empty] | NO | [63 empty] | LESLIE STEVENS | COMPLIANCE COORDINATOR | leslie.stevens@enbridge.com | 832-214-1649 |  |  |  |  | LESLIE STEVENS | COMPLIANCE COORDINATOR | 8322141649 | leslie.steves@enbridge.com | A LEAK WAS DETECTED BY AN ENBRIDGE OPERATOR 8-28-2011 WHILE FLYING OVER THE AREA. THE OPERATOR OF THE PLATFORM THAT TIES INTO THE LINE WAS CONTACTED AND THE OPERTOR WAS ABLE TO FLY TO THE PLATFORM AND SHUT OFF THE FLOW TO THE PIPELINE (ISOLATING THE LINE AT THE SOURCE) ON 8-29-2011. A DIVE BOAT ARRIVED ON LOCATION AND ISOLATED THE PIPELINE BY CLOSING A SUBSEA VALVE AT WC 144 ON 8-30-2011.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20130104 | 16309 | 2013-11-22 09:26 | SUPPLEMENTAL FINAL | 18646 | ENBRIDGE OFFSHORE (GAS TRANSMISSION) LLC | 1100 LOUISIANA ST. SUITE 3300 | HOUSTON | TX | 77002 | 2012-01-09 09:40 | 2012 |  |  | 28.5049 | -93.0827 | 999862 | 2012-01-09 11:06 |  | NATURAL GAS |  | 20 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | VERY SMALL LEAK IN THE OCS, JUST BUBBLE. WE NEED THE BUBBLES TO LOCATE THE LEAK. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-01-09 09:40 | 2012-01-11 09:01 | OFFSHORE | [28 empty] | 86 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST CAMERON | 275 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | FLANGE ASSEMBLY | [38 empty] | 1978 |  | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 20 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 80 | 64.4397463002114 | 1790687 | 2056245.8821 | 0 | 0 | 0 | 0 |  |  | 1790767 | 943937.925310994 | 2056310.3218463 | [8 empty] | 900 |  | 1200 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [7 empty] | YES | [7 empty] | NO | [6 empty] | OFFSHORE GATHERING | YES | YES | NO | NO | NO | AIR PATROL |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | VERY SMALL LEAK OFFSHORE IDENTIFIED BY ANOTHER COMPANY FLYING OVER THE AREA. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | VERY SMALL LEAK (BUBBLE) LOCATED IN FLANGE. FLANGE SEAL LEAK. LINE WAS LEFT IN SERVICE WITH PERMISSION FROM BSEE (ALEX ALVARDAO) UNTIL CLAMP COULD BE BUILT AND INSTALLED. NO POLLUTION. | [147 empty] | LESLIE B. STEVENS | COMPLIANCE COORDINATOR | leslie.stevens@enbridge.com | 832-214-1649 | 985-851-0059 |  |  |  | LESLIE B. STEVENS | COMPLIANCE COORDINATOR | 832-214-0059 | leslie.stevens@enbridge.com | A VERY SMALL LEAK WAS INDENTIFEID AT WC 275 (BUBBLE) WITH NO POLLUTION. THE LEAK WAS A FLANGE SEAL LEAK ON A 36 RTJ FLANGE. THE LINE WAS LEFT IN SERVICE WITH THE PERMISSION OF ALEX ALVARADO WITH BSEE UNTIL A CLAMP COULD BE BUILT AND INSTALLED.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20130105 | 16366 | 2013-11-22 11:04 | SUPPLEMENTAL | 18646 | ENBRIDGE OFFSHORE (GAS TRANSMISSION) LLC | 1100 LOUISIANA ST. SUITE 3300 | HOUSTON | TX | 77002 | 2011-11-22 09:18 | 2011 |  |  | 28.5197 | -92.5636 | 996302 | 2011-11-22 17:11 |  | NATURAL GAS |  | 80 | 28080 | 0.2 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-11-22 17:11 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-11-22 09:18 | 2011-11-22 12:14 | OFFSHORE | [28 empty] | 133 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | VERMILLION | 263 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 20 |  | 0.409 | 60000 | API 5L X-60 | SEAMLESS |  | ? | OTHER | ASPHALT AND CONCRETE | [27 empty] | 1974 | 1974 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 10 |  | NO | NO | NO |  | 0 | 0 | 100000 | 117006.317505604 | 2000 | 1353.46358792185 | 196327 | 229714.992969228 | 0 | 0 | 0 | 0 |  |  | 298327 | 160557.427543246 | 348074.774062754 | [8 empty] | 815 |  | 1200 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 212528 | NO | YES | [13 empty] | OFFSHORE GATHERING | YES | YES | YES | NO | NO | AIR PATROL |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIN HOLE LEAK IDENTIFIED BY HELICOPTER. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING | [5 empty] | YES | DON'T KNOW. CLAMP INSTALLED |  |  | YES | DON'T KNOW. | YES | [5 empty] | YES | [316 empty] | LESLIE B. STEVENS | COMPLIANCE COORDINATOR | leslie.stevens@enbridge.com | 832-214-1649 | 9858514126 |  |  |  | LESLIE B. STEVENS | COMPLIANCE COORDINATOR | 832-214-1649 | leslie.stevens@enbridge.com | PIN HOLE LEAK WAS REPAIRED BY CLAMP INSTALLATION ON 12-29-2011. ANOTHER LEAK DEVELOPED ON 12-29-2011. ANOTHER INCIDENT REPORT WAS INITIATED FOR THIS LINE ON 12-29-2013.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20130106 | 16365 | 2013-11-22 11:22 | SUPPLEMENTAL | 18646 | ENBRIDGE OFFSHORE (GAS TRANSMISSION) LLC | 1100 LOUISIANA ST. SUITE 3300 | HOUSTON | TX | 77002 | 2011-12-29 11:55 | 2011 |  |  | 28.5197 | -92.5636 | 999214 | 2011-12-29 14:18 |  | NATURAL GAS |  | 80 | 28080 | 0.02 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-12-29 12:00 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-12-29 12:00 | 2011-12-29 12:00 | OFFSHORE | [28 empty] | 133 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | VERMILLION | 263 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 20 |  | 0.409 | 60000 | API 5L X-60 | SEAMLESS |  | ? | OTHER | ASPHALT AND CONCRETE | [27 empty] | 1974 | 1974 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 6 |  | NO | NO | NO |  | 0 | 0 | 100000 | 117006.317505604 | 2000 | 1353.46358792185 | 196327 | 229714.992969228 | 0 | 0 | 0 | 0 |  |  | 298327 | 160557.427543246 | 348074.774062754 | [8 empty] | 815 |  | 1200 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 212528 | NO | YES | [13 empty] | OFFSHORE GATHERING | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS DETECTED AFTER CONTRACTORS REPAIRED A LEAK WITH A CLAMP AND WERE PRESSURING UP THE LINE. THE NEW LEAK WAS DETECTED BY THE CONTRACTOR ON LOCATION. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING | [5 empty] | YES | DON'T KNOW. CLAMP INSTALLED. |  |  | YES | DON'T KNOW. CLAMP INSTALLED. | YES | [5 empty] | YES | [316 empty] | LESLIE STEVENS | COMPLIANCE COORDINATOR | leslie.stevens@enbridge.com | 832-214-1649 | 985-851-4126 |  |  |  | LESLIE STEVEND | COMPLIANCE COORDINATOR | 832-214-1649 | leslie.stevens@enbridge.com | A REPAIR ON THE PIPELINE WAS COMPLETED BY INSTALLING A CLAMP ON THE LILNE. WHILE THE PIPE WAS BEING PRESSURED UP TO TEST THE CLAMP, A NEW LEAK WAS DETECTED ABOUT 2000 FEET FROM THE REPAIR. THE PIPELINE WAS SHUT DOWN UNTIL A DECISION CAN BE MADE ON A PLAN FORWARD.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130107 | 16258 | 2013-11-25 14:29 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2013-10-23 14:35 | 2013 |  |  | 39.0099 | -121.423 | 106386 | 2013-10-23 17:22 |  | NATURAL GAS |  | 13798 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | ISOLATED THE DAMAGED SECTION OF PIPE BY CLOSING MAINLINE VALVES | [6 empty] | NO |  |  |  |  | NO | [7 empty] | 2013-10-23 14:35 | 2013-10-23 15:20 | ONSHORE | CA | 95692 | WHEATLAND | YUBA | MILEPOST | 14.49 | L 124A |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 56 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 16 |  | 0.28 | 42000 | X42 | SEAMLESS |  | UNKNOWN | ASPHALT | [28 empty] | 1955 | 1955 | CARBON STEEL |  | OTHER | [8 empty] | FARMER STRUCK TRANSMISSION GAS LINE WITH FIELD RIPPER | CLASS 1 LOCATION | NO |  | 270 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 40000 | 31229.5081967213 | 100000 | 112755.302435192 | 10000 | 11275.5302435192 | 0 | 0 |  |  | 150000 | 89310.4741606893 | 155260.340875433 | [8 empty] | 585 |  | 600 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 5 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CAUSE OF THE INCIDENT WAS DUE TO A THIRD PARTY CONTRACTOR THAT STRUCK PG&E'S GAS TRANSMISSION LINE WITH A FIELD RIPPER | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  | YES |  |  | YES | [5 empty] | CONTRACTOR | FARM EQUIPMENT | AGRICULTURE | NO |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER |  |  | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | CHERYL DIZON | COMPLIANCE ENGINEER | c1dz@pge.com | 925-328-5721 | 925-328-5591 |  |  |  | FRANCES YEE | MANAGER REGULATORY COMPLIANCE | 925-328-5733 | fsc2@pge.com | ON OCTOBER 23, 2013 PACIFIC GAS AND ELECTRIC (PG&E) WAS NOTIFIED THAT A THIRD PARTY CONTRACTOR, WESTERN CONSTRUCTION AND MINING, WAS RIPPING A FIELD WITH A CAT D-10 FOR THE PROPERTY OWNER, TOLLENCREST DAIRY, WHEN THE CONTRACTOR STRUCK PG&E'S 16-INCH STEEL TRANSMISSION LINE L-124A RESULTING IN A RELEASE OF GAS. THE CONTRACTOR DID NOT CONTACT USA AND DID NOT HAND DIG, EXPOSE AND PROTECT THE LINE PRIOR TO USING MECHANICAL EQUIPMENT, AS REQUIRED. PG&E'S GAS SERVICE REPRESENTATIVE ARRIVED ON SITE AT 1520 HOURS AND THE FLOW OF GAS WAS STOPPED AT 1645 HOURS BY CLOSING THE MAIN LINE VALVES. NO CUSTOMERS EXPERIENCED GAS SERVICE INTERRUPTION. THERE WERE NO INJURIES, NO FATALITIES AND NO IGNITION AS A RESULT OF THIS INCIDENT. MEDIA WAS NOT OBSERVED ON SCENE. THE DAMAGED SECTION OF 16-INCH STEEL PIPE ON L-124A WAS REPAIRED BY 0327 HOURS ON OCTOBER 24, 2013 AND THE OPERATING PRESSURE WAS LIMITED TO 526 PSI (10% BELOW DISCOVERY PRESSURE). AT THE TIME THE DIG IN WAS OBSERVED, THE CONTRACTOR HAD DUG A SIGNIFICANT DISTANCE OVER LINE-124A; THEREFORE, PG&E PERFORMED ADDITIONAL ASSESSMENT ON THE PIPELINE PRIOR TO RESTORING THE PIPELINE TO NORMAL OPERATING PRESSURE. AFTER AN EXPLORATORY DIG CONFIRMED THAT NO ADDITIONAL DAMAGE WAS MADE TO THE PIPE AS A RESULT OF THIS INCIDENT, THE PRESSURE IN LINE-124A WAS RESTORED TO 585 PSIG, WHICH IS THE OPERATING PRESSURE PRIOR TO THE INCIDENT. THIS INCIDENT WAS REPORTED TO THE DOT AT 1722 HOURS AND CPUC AT 1724 HOURS BECAUSE THE VOLUME OF GAS RELEASED IS IN EXCESS OF 3 MILLION CUBIC FEET AND DAMAGES ARE GREATER THAN $50,000.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130108 | 16536 | 2013-11-25 14:36 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2013-10-29 12:15 | 2013 |  |  | 38.1473 | -97.454 | 1064450 | 2013-10-30 17:02 |  | NATURAL GAS |  | 0 | 24654 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-10-29 20:00 | 2013-11-01 20:39 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-10-29 12:15 | 2013-10-29 12:15 | ONSHORE | KS | 67062 | HESSTON | HARVEY | SURVEY STATION NO. | 105/10972+27 | LINE Q | HUGOTON 26" | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 54 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 26 |  | 0.344 | 60000 | API 5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | KAISER | COAL TAR | [9 empty] | PIPE GIRTH WELD | [18 empty] | 1968 | 1967 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 538 |  | NO | NO | NO |  | 0 | 0 | 85549 | 96461.0336802828 | 0 | 0 | 384285 | 433301.713963079 | 7200 | 8118.38177533386 | 0 | 0 |  |  | 477034 | 246901.631382561 | 537881.129418696 | [8 empty] | 817 |  | 900 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 137175 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [8 empty] | YES | CRACK IN PIPE BEGAN TO LEAK | [12 empty] | YES | [63 empty] | YES |  | YES |  | YES |  |  | YES | [12 empty] | 2013 | [19 empty] | 2013 | [17 empty] | COMBINATION TOOL | 2013 |  |  |  |  | NO |  |  | NO | [13 empty] | NO | [63 empty] | DAVID COOMES | PIPELINE COMPLIANCE ENGINEER | david.coomes@sscgp.com | 2708524391 | 2708525016 |  |  |  | DAVID SINCLAIR | PIPELINE COMPLIANCE MANAGER | 2708524424 | david.l.sinclair@sscgp.com | AT 12:15 PM ON 10/29/2013 AN SSCGP OPERATOR WAS DOING FIELD CHECKS OF THE HESSTON COMPRESSOR STATION. AN ICE BALL AND AUDIO SOUNDS WERE FOUND INDICATING A LEAK AND GAS CONTROL WAS IMMEDIATELY NOTIFIED. ONCE NOTIFIED, PIPELINE SAFETY ISSUED A 20% REDUCTION IN PRESSURE, GAS CONTROL BEGAN THE PROCESS OF BRINGING THE LINE DOWN TO THE 20% REDUCTION LEVEL. WHILE PRESSURE WAS DROPPING OPERATIONS BEGAN DIGGING THE LEAKING AREA AND DECIDED THE LINE NEEDED TO BE BLOWN DOWN. THE LINE SEGMENT WAS BLOWN DOWN AT 20:00 10/29/2013. BEGINNING ON 10/30/2013 THE SEGMENT WAS COMPLETELY UNCOVERED AND THE CORRECTIVE ACTION OF CUTTING AND CAPPING THE LEAKING SECTION WAS MADE. THE LINE WAS BROUGHT BACK UP TO NORMAL OPERATING PRESSURE AT 20:39 ON 11/1/2013.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130109 | 16363 | 2013-12-03 09:23 | SUPPLEMENTAL | 18646 | ENBRIDGE OFFSHORE (GAS TRANSMISSION) LLC | 1100 LOUISIANA ST. SUITE 3300 | HOUSTON | TX | 77002 | 2011-03-30 20:28 | 2011 |  |  | 29.6314 | -93.3208 | 971591 | 2011-03-31 00:42 |  | NATURAL GAS |  | 4093 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2011-03-30 23:30 | 2011-12-09 06:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2011-03-30 20:28 | 2011-03-31 14:16 | OFFSHORE | [28 empty] | 40 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WC | 62 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12.75 |  | 0.562 | 52000 | API-5L X-52 | SEAMLESS |  | ? | EPOXY | [28 empty] | 2006 | 2006 | CARBON STEEL |  | MECHANICAL PUNCTURE | [9 empty] | CLASS 1 LOCATION | NO |  | 1000 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 17064 | 11547.7513321492 | 8116085 | 9496332.18412472 | 0 | 0 | 0 | 0 |  |  | 8133149 | 4371039.12879469 | 9507879.93545687 | [8 empty] | 900 |  | 1349 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | MANUAL | 73374 | [15 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY DAMAGE TO PIPELINE WAS REPORTED BY THE CONTRACTOR WHEN THE LINE WAS STRUCK. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  |  |  | YES | [6 empty] | UNKNOWN/OTHER | UNKNOWN/OTHER | WATERWAY IMPROVEMENTS | NO |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | YES | 6048 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO MAINTAIN CLEARANCE | [263 empty] | LESLIE STEVENS | COMPLIANCE COORDINATOR | leslie.stevens@enbridge.com | 832-214-1649 | 985-851-4126 |  |  |  | LESLIE STEVENS | COMPLIANCE COORDINATOR | 832-214-1649 | leslie.stevens@enbridge.com | THE PIPELINE WAS DAMAGED BY A DREDGE OPERATING IN THE CALCASIEU CHANNEL WHERE IT CROSSES THE CHANNEL IN WC BLOCK 62.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20130110 | 16364 | 2013-12-03 11:59 | SUPPLEMENTAL | 18646 | ENBRIDGE OFFSHORE (GAS TRANSMISSION) LLC | 1100 LOUISIANA ST. SUITE 3300 | HOUSTON | TX | 77002 | 2012-09-05 16:38 | 2012 |  |  | 29.2151 | -93.12 | 1023474 | 2012-09-05 20:29 |  | NATURAL GAS |  | 124 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE LINE WAS ALREADY SHUT IN. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2012-09-05 16:38 | 2012-11-05 18:03 | OFFSHORE | [28 empty] | 42 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST CAMERON | 181 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 |  | 0.375 | 60000 | API 5L X-60 | SEAMLESS |  | ? | OTHER | CONCRETE | [27 empty] | 1971 | 1971 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 8 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 500 | 402.748414376321 | 164574 | 188980.3242 | 0 | 0 | 0 | 0 |  |  | 165074 | 87164.5029687103 | 189383.072614376 | [8 empty] | 500 |  | 1300 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 160 | NO | [7 empty] | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | NO |  |  |  |  | OTHER | THIRD PARTY FLYING OVER AREA NOTIFIED ENBRIDGE OF THE LEAK. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LINE HAD BEEN ISOLATED BEFORE THE INCIDENT. THE LEAK WAS REPORTED TO ENBRIDGE BY A THIRD PARTY FLYING OVER THE AREA. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING | [5 empty] | YES | DON'T KNOW |  |  | YES | DON'T KNOW | YES | [5 empty] | YES | NO | [315 empty] | LESLIE B. STEVENS | COMPLIANCE COORDINATOR | leslie.stevens@enbridge.com | 832-214-1649 | 985-851-4126 |  |  |  | LESLIE B. STEVENS | COMPLIANCE COORDINATOR | 832-214-1649 | leslie.stevens@enbridge.com | A GAS LEAK WITH NO SHEEN WAS DISCOVERD BY THIRD PARTY FLYING OVER THE AREA ON SEPTEMBER 5TH, 2012 AND REPORTED TO ENBRIDGE. ENBRIDGE SENT A HELICOPTER TO THE AREA TO INVESTIGATE AND GET LAT/LONG COORDINATES. THE LAT/LONG COORDINATES WERE SENT TO DRAFTING TO PLOT THE LOCATION AND OUR LINE LOCATION. ENBRIDGE HAS A LINE IN THE AREA, SO A DIVE BOAT WAS HIRED TO INVESTIGATE. THE DIVERS ARRIVED ON LOCATION AND DISCOVERED A PIN HOLE LEAK AT THE 6 O'CLOCK POSTION ON LINE SEGMENT 2814. THIS INCIDENT WAS REPORTED LATE DUE TO THE CHANGE IN THE REPORTING SYSTEM. I CONTACTED TOM BRAVO BY PHONE AND E-MAIL SEVERAL TIMES UNTIL I WAS APPROVED TO USE THE NEW SYSTEM. L. B. STEVENS
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130111 | 16707 | 2013-12-05 18:14 | SUPPLEMENTAL FINAL | 18273 | SHELL PIPELINE CORP | 150 NORTH DAIRY ASHFORD ROAD WCK BLDG. A | HOUSTON | TX | 77079 | 2013-11-07 10:28 | 2013 |  |  | 30.1313 | -90.7775 | 1065160 | 2013-11-07 12:58 |  | OTHER GAS | DRY GAS | 56 | 715 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-11-07 10:40 | 2013-11-14 16:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-11-07 10:28 | 2013-11-07 10:28 | ONSHORE | LA | 70052 | GRAMERCY | ST. JAMES | SURVEY STATION NO. | 530+08.00 | CONVENT TO GARYVILLE 12" DRY GAS | CONVENT TO GARYVILLE 12" | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 54 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 12.75 |  | 0.281 | 42000 | 5L-X | LONGITUDINAL ERW - LOW FREQUENCY |  | REPUBLIC | COAL TAR | [28 empty] | 1954 | 1954 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 285 |  | NO | NO | NO |  | 0 | 0 | 7844 | 8844.5259230165 | 619 | 483.276639344262 | 460000 | 518674.391201886 | 100000 | 112755.302435192 | 0 | 0 |  |  | 568463 | 294403.796422869 | 640757.496199439 | [8 empty] | 940 |  | 1233 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | AUTOMATIC | 47793 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LOOKED AT THE SCADA LINE BALANCE AND PRESSURE TRENDS - NO ANOMALIES WERE DETECTED. ALSO THE CONTROLLER FOLLOWED CONTROL CENTER PROCEDURE WHEN SHUTTING DOWN THE LINE AND PERFORMING THE ISOLATION. THEREFORE NO INVESTIGATION WILL BE CONDUCTED. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) |  | YES | [13 empty] | YES | ERW LONG SEAM WELD PROCESS AT MANUFACTURER, LACK OF FUSION | [7 empty] | YES | [62 empty] | YES | YES | YES |  | YES |  |  |  | 2013 | [11 empty] | 2010 | [19 empty] | 2013 | [23 empty] | YES | 2011 | 1632 | NO | [13 empty] | NO | [63 empty] | RICHARD KLASEN | REGULATORY SPECIALIST | richard.klasen@shell.com | 713 241 1064 |  |  |  |  | BRIAN SITTERLY | MANAGER INTEGRITY REGULATORY SRVC | 713 241 3620 | brian.sitterly@shell.com | DETERMINED BY METALLURGICAL INVESTIGATION THAT THE ERW LONG SEAM HAD SOME EVIDENCE OF AN IRREGULAR COIL EDGE THAT CHANGED THE WELDING GEOMETRY. THE EFFECT OF THE IRREGULAR COIL EDGE WAS TO WEAKEN THE WELD. LACK OF FUSION / LONG SEAM
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130112 | 16279 | 2013-12-09 15:20 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2013-12-03 14:06 | 2013 |  |  | 40.9287 | -96.517 | 1067478 | 2013-12-03 18:00 |  | NATURAL GAS |  | 1000 | 2000 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-12-03 20:00 | 2013-12-03 21:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 1 | 2013-12-03 15:06 | 2013-12-03 16:00 | ONSHORE | NE | 68462 | WAVERLY | LANCASTER | MILEPOST | 16.94 | PALMYRA TO HOOPER A-LINE | NEM50101-M581A | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 1 |  | 0.179 | 25000 | A106 | SEAMLESS |  | AO SMITH | ASPHALT | [28 empty] | 1954 | 1954 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 12 |  | NO | NO | NO |  | 0 | 0 | 15000 | 16913.2953652789 | 1000 | 780.737704918033 | 2500 | 2818.88256087981 | 3000 | 3382.65907305577 | 0 | 0 |  |  | 21500 | 11419.7463394846 | 23895.5747041325 | [8 empty] | 368 |  | 500 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [260 empty] | JOHN GORMLEY | SR CORROSION SPECIALIST | john.gormley@nngco.com | 402-398-7494 |  |  |  |  | JOHN GORMLEY | SR CORROSION SPECIALIST | 402-398-7494 | john.gormley@nngco.com | A LANDOWNER/FARMER STRUCK AND DAMAGED A FARM TAP SETTING WITH HIS DISKING EQUIPMENT. THE FARM EQUIPMENT DESTROYED THE FARM TAP FENCE AND SIGNAGE, STRUCK THE FARM TAP SETTING, AND CRACKED A 1-INCH NIPPLE ON THE HIGH PRESSURE SIDE OF THE FARM TAP NEAR GROUND LEVEL. HE IMMEDIATELY NOTIFIED 911 AND EMERGENCY PERSONNEL RESPONDED. THE 20-INCH MAINLINE PIPING WAS BLOWN DOWN TO 75 PSI SO EMPLOYEES COULD APPROACH SAFELY. THE SHUT OFF VALVE, BELOW THE CRACKED NIPPLE, WAS SHUT OFF AND THE EMERGENCY WAS UNDER CONTROL. THE MAINLINE WAS RETURNED TO NORMAL AND THE FARM TAP WAS REPAIRED THE NEXT DAY.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130113 | 16205 | 2013-12-12 16:40 | ORIGINAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2013-11-27 05:30 | 2013 |  |  | 32.2471 | -93.2822 | 1066962 | 2013-11-27 05:52 |  | NATURAL GAS |  | 11365.44 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | VALVE TO HP BLOWDOWN STACK OPENED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-11-27 05:30 | 2013-11-27 05:30 | ONSHORE | LA | 71068 | RINGGOLD | BIENVILLE | MILEPOST | 62.85 | HALL SUMMIT COMPRESSOR STATION | INDEX 266 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1991 |  | CARBON STEEL |  | OTHER | [8 empty] | SENSING LINE TO VALVE FROZE CAUSING VALVE TO OPEN | CLASS 1 LOCATION | NO |  | 88 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 40137 | 31336.4692622951 | 100 | 112.755302435192 | 180 | 202.959544383346 | 0 | 0 |  |  | 40417 | 32632.862019175 | 31652.1841091136 | [8 empty] | 800 |  | 1012 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA SYSTEM DID NOT HAVE ANY EVENT ALARMS THAT WOULD REQUIRE CONTROLLER INTERACTION. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | NO | [306 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 270.688.6357 | 270.688.6948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 270.688.6361 | jeff.mcmaine@bwpmlp.com | VALVE ACTUATOR CONTROL SUPPLY LINE FROZE WHICH CAUSED STATION BLOWDOWN VALVE TO "FAIL" IN THE "OPEN" POSITION, WHICH IS THE FAIL SAFE POSITION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130114 | 16708 | 2013-12-13 11:06 | SUPPLEMENTAL FINAL | 18273 | SHELL PIPELINE CORP | 150 NORTH DAIRY ASHFORD ROAD WCK BLDG. A | HOUSTON | TX | 77079 | 2013-11-15 08:22 | 2013 |  |  | 30.0943 | -90.7297 | 1065831 | 2013-11-15 09:24 |  | OTHER GAS | DRY GAS | 302 | 1790 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-11-15 08:22 | 2014-02-21 22:22 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-11-15 08:22 | 2013-11-15 08:22 | ONSHORE | LA | 70052 | GRAMERCY | ASCENSION, ST. JAMES AND ST. JOHN THE BAPTIST | SURVEY STATION NO. | 37047-110524 | CONVENT TO NORCO 12" DRY GAS | CONVENT TO GARYVILLE 12" | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 55 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 12.75 |  | 0.281 | 42000 | 5L-X | LONGITUDINAL ERW - LOW FREQUENCY |  | REPUBLIC | COAL TAR | [28 empty] | 1954 | 1954 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 280 |  | NO | NO | NO |  | 0 | 0 | 19635 | 22139.50363315 | 3308 | 2582.68032786885 | 6100000 | 6878073.44854674 | 400000 | 451021.20974077 | 0 | 0 |  |  | 6522943 | 3377088.03807483 | 7353816.84224853 | [8 empty] | 704 |  | 1233 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | REMOTELY CONTROLLED | 119654 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER FOLLOWED CONTROL CENTER PROCEDURE WHEN SHUTTING DOWN THE LINE AND PERFORMING THE ISOLATION. THEREFORE NO INVESTIGATION WAS CONDUCTED. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | YES | [14 empty] | YES | MILL MANUFACTURING PROCESS LACK OF FUSION IN THE PIPE LONG SEAM | [7 empty] | YES | [62 empty] | NO | [63 empty] | YES | 2011 | 1632 | NO | [13 empty] | NO | [63 empty] | RICHARD KLASEN | REGULATORY SPECIALIST | richard.klasen@shell.com | 713 241 1064 |  |  |  |  | BRIAN SITTERLY | MANAGER INTEGRITY AND REGULATORY SERVICES | 713 241 3620 | brian.sitterly@shell.com | A MANUAL SURVEY OF THE DRY GAS ROW WAS BEING CONDUCTED AS DRY GAS WAS BEING RE-INTRODUCED TO THE PIPELINE. DURING THIS ASSESSMENT MULTIPLE LOCATION WERE REPORTED BY THE MAINTENANCE CREW ALONG THE ROW. PIPELINE WAS SHUTDOWN, ISOLATED AND BEGAN TO FLARE THE CONTENTS OF THE PIPELINE. THE PIPELINE WAS EVACUATED BY FLARING, FILLED WITH NITROGEN TO DETERMINE LOCATIONS WHICH INDICATE LOSS OF PRIMARY CONTAINMENT OF THE PIPELINE. PLAN OF ACTION TO TEST THE PIPELINE WITH NITROGEN, THEN WATER, THEN NITROGEN. ALL IDENTIFIED LOCATIONS WILL BE REMEDIATED. LINE WILL REMAIN DOWN UNTIL TESTS, REPAIRS ARE COMPLETED. IN TOTAL 11 LOCATIONS WERE IDENTIFIED. REPAIR METHOD WAS ONE CUT OUT AND 10 LOCATIONS WITH REPAIRS BY FULL ENCIRCLEMENT SLEEVES. THE PIPELINE WAS THEN HYRDOTESTED WITH WATER AND ESTABLISHED A NEW MOP OF 1052 PSI. THE LINE WAS THEN PRESSURED WITH NITROGEN TO 1052 PSI AND HELD FOR 8 HOURS TO VERIFY INTEGRITY OF PIPELINE. BOTH TESTS WERE SUCCESSFULL. PIPELINE WAS RETURNED TO SERVICE ON FEB. 21, 2014.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20130115 | 16595 | 2013-12-18 17:03 | SUPPLEMENTAL FINAL | 32296 | TARGA RESOURCES OPERATING LLC | 811 LOUISIANA ST SUITE 2100 | HOUSTON | TX | 77002 | 2013-11-15 15:20 | 2013 |  |  | 29.5464 | -93.2222 | 1066154 | 2013-11-18 16:00 |  | NATURAL GAS |  | 750 | 3439 | 0.2 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-11-17 08:00 | 2013-11-23 15:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-11-18 15:42 | 2013-11-19 06:00 | OFFSHORE | [28 empty] | 49 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST CAMERON | 109 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12.75 |  | 0.375 | 52000 | API5L | SEAMLESS |  | UNKNOWN | EPOXY | [28 empty] | 1970 | 1969 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 200 |  | NO | NO | NO |  | 0 | 0 | 13000 | 14658.189316575 | 3000 | 2342.2131147541 | 160000 | 180408.483896308 | 7000 | 7892.87117046348 | 0 | 0 |  |  | 183000 | 95592.065020025 | 205301.757498101 | [8 empty] | 500 |  | 1240 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | CHECK VALVE | 110544 | NO |  |  | YES |  |  |  |  | NO | [6 empty] | OFFSHORE GATHERING | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  |  | YES | [5 empty] | YES | FIELD EXPERIENCE | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | TIM HUFFER | MANAGER REGULATORY COMPLIANCE | thuffer@targaresources.com | 337-583-4642 | 337-583-4630 |  |  |  | TIM HUFFER | MANAGER REGULATORY COMPLIANCE | 337-583-4642 | thuffer@targaresources.com | TARGA RECEIVED REPORT OF A GAS LEAK NEAR TARGA'S OFFSHORE GAS GATHERING PIPELINE ON 11/15/2013. TARGA BEGAN STEPS TO IDENTIFY IF THE LEAK ORIGINATED FROM TARGA'S PIPELINE. PRODUCTION INTO PIPELINE WAS SHUT IN. TARGA CONFIRMED ON 11/18/2013 THAT LEAK WAS FROM TARGA'S PIPELINE. CLAMP WAS INSTALLED TO REPAIR LEAKING SEGMENT AND PIPELINE RE-STARTED ON 11/23/2013.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130116 | 16408 | 2013-12-19 16:17 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2013-11-25 11:10 | 2013 |  |  | 32.302 | -90.0924 | 1066795 | 2013-11-25 12:05 |  | NATURAL GAS |  | 812 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | COMPRESSOR STATION NOT SHUTDOWN; PIPING SECTION ISOLATED. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-11-25 11:15 | 2013-11-25 11:15 | ONSHORE | MS | 39232 | FLOWOOD | RANKIN | MILEPOST | 124.527 | JACKSON COMPRESSOR STATION | INDEX 381 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 50 |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | WELD/FUSION |  | 18 |  | 0.25 | 35000 | API 5L | SEAMLESS |  | NATIONAL PIPE | COAL TAR | [9 empty] | PIPE GIRTH WELD | [18 empty] | 1939 | 1939 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 20 | 1 |  | CLASS 1 LOCATION | NO |  | 271 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 2842 | 2218.85655737705 | 100000 | 112755.302435192 | 9000 | 10147.9772191673 | 0 | 0 |  |  | 111842 | 58716.2377338931 | 125122.136211737 | [8 empty] | 420 |  | 475 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | AREA EMPLOYEE WAS AT THE SITE WHEN INCIDENT OCCURRED. NO CHANGE WAS MADE TO CAUSE EVENT. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES | [7 empty] | YES | WELD FAILURE FROM A ONE TIME EXTERNAL LOAD EVENT | [19 empty] | YES | A CRITICAL SECONDARY FACTOR WAS THE PRE-EXISTING WELD FLAWS, WHICH REDUCED THE STRENGTH OF THE GIRTH WELD. | [55 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | YES | [5 empty] | FULL METALLURGICAL EXAMINATION OF THE FAILURE | 2013 | [5 empty] | YES | [50 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 270.688.6357 | 270.688.6948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 270.688.6361 | jeff.mcmaine@bwpmlp.com | PIPE FAILED IN AREA OF GIRTH WELD IN PIPELINE LOCATED INSIDE COMPRESSOR STATION YARD. CAUSE STILL UNDER INVESTIGATION. 5-23-14 CAUSE WAS WELD FAILURE FROM A ONE-TIME LOAD EVENT. APPROXIMATELY AN 800' SECTION OF PIPELINE, WHICH INCLUDED THE AREA WHERE THE PIPE FAILED, WAS ABANDONED AND WILL NOT BE REPLACED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130117 | 16376 | 2013-12-19 16:54 | SUPPLEMENTAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2013-11-21 02:17 | 2013 |  |  | 33.4071 | -88.6233 | 1066418 | 2013-11-21 06:21 |  | NATURAL GAS |  | 25938 | 403 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-11-21 05:00 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 200 | 2013-11-21 04:50 | 2013-11-21 05:03 | ONSHORE | MS | 39736 | ARTESIA | LOWNDES | MILEPOST | MP 11.09 | WEST POINT MAIN LINE | T18N R16E | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 8 |  | 0.188 | 25000 | API 5L | LAP WELDED |  | NATIONAL TUBE | NONE | [28 empty] | 1929 | 1929 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 50 | 12 |  | CLASS 1 LOCATION | NO |  | 158 |  | NO | NO | NO |  | 500 | 563.776512175962 | 1465 | 1651.86518067557 | 942670 | 735978.012295082 | 40000 | 45102.120974077 | 2500 | 2818.88256087981 | 0 | 0 |  |  | 987135 | 786035.866877326 | 786114.65752289 | [8 empty] | 460 |  | 500 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 52766 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLERS ACTIONS DID NOT CAUSE OR CONTRIBUTE NEGATIVELY TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) |  | YES | [13 empty] | YES | NONFUSION IN THE LAP WELDED LONGITUDINAL SEAM | [6 empty] | YES | YES | [5 empty] | YES | EXTERNAL CORROSION | [55 empty] | YES | YES | [6 empty] | 2005 | [55 empty] | YES | 1967 | 840 | NO | [13 empty] | NO | [63 empty] | KRISTIN VAN DER LAAN | COMPLIANCE ENGINEER III | kristin_vanderlaan@kindermorgan.com | 303-914-7753 |  |  |  |  | REJI GEORGE | DIRECTOR-COMPLIANCE CODES AND STANDARDS | 713-420-5433 | reji_george@kindermorgan.com | AT 3:40AM SNG GAS CONTROL RECEIVED NOTIFICATION OF SMELL OF GAS (LATER DETERMINED TO BE CAUSED BY PREVIOUS ATMOS ODORANT MAINTENANCE ACTIVITIES) AND A LOUD NOISE FROM THE LOWNDES COUNTY 911. LOWNDES COUNTY EMERGENCY RESPONDERS WERE ONSITE AND BELIEVED THE NOISE AND SMELL ORIGINATED FROM THE SNG PIPELINE. SNG PERSONNEL WERE DEPLOYED TO THE LOCATION, AN UNCULTIVATED AREA, WHERE THEY SECURED THE AREA AND ISOLATED THE PIPELINE. AS A PRECAUTIONARY MEASURE, EMERGENCY RESPONDERS TEMPORARILY EVACUATED APPROXIMATELY 200 RESIDENTS TO THE LOCAL HIGH SCHOOL. AT 5:12AM SNG PERSONNEL NOTIFIED THE LOWNDES COUNTY 911 PERSONNEL THAT THE EVACUATED PEOPLE COULD RETURN HOME. EVACUATION WAS NOT NECESSARY SINCE THE ESCAPING GAS VENTED DIRECTLY TO THE ATMOSPHERE. THE 8-INCH WEST POINT LINE SEGMENT WILL REMAIN ISOLATED, WILL NOT BE RETURNED TO SERVICE AND WILL BE ABANDONED PENDING FERC APPROVAL.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130118 | 16218 | 2013-12-20 23:49 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2013-11-22 12:56 | 2013 |  |  | 36.0251 | -120.9215 | 1066618 | 2013-11-22 14:53 |  | NATURAL GAS |  | 1166 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-11-22 16:02 | 2013-11-23 17:00 |  |  |  |  | NO |  |  |  |  | NO | [7 empty] | 2013-11-22 12:56 | 2013-11-22 13:55 | ONSHORE | CA | 93450 | SAN ARDO | MONTEREY | MILEPOST | 5.35 | L-187 |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 18 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 |  | 0.188 | 42000 | API5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | OTHER | DOUBLE WRAP | [27 empty] | 1957 | 1957 | CARBON STEEL |  | OTHER | [8 empty] | FARMER PLOWING FIELD STRUCK THE GAS LINE WITH HEAVY FARMING EQUIPMENT | CLASS 1 LOCATION | NO |  | 74 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 3300 | 2576.43442622951 | 200000 | 225510.604870385 | 200000 | 225510.604870385 | 0 | 0 |  |  | 403300 | 209701.7428496 | 453597.644166999 | [8 empty] | 300 |  | 313 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL |  | 44352 | [15 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CAUSE OF THE INCIDENT WAS A THIRD PARTY WHO STRUCK THE PIPELINE WITH HEAVY FARMING EQUIPMENT | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  | YES | PRIVATE LANDOWNER | [7 empty] | FARMER | FARM EQUIPMENT | AGRICULTURE | NO |  |  | DATA NOT COLLECTED | DATA NOT COLLECTED | DATA NOT COLLECTED | YES | 25 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | CHERYL DIZON | GAS COMPLIANCE ENGINEER | c1dz@pge.com | 925-328-5721 | 925-328-5591 |  |  |  | FRANCES YEE | MANAGER REGULATORY COMPLIANCE | 925-328-5733 | fsc2@pge.com | ON NOVEMBER 22, 2013, AT APPROXIMATELY 1256 HOURS, PACIFIC GAS AND ELECTRIC (PG&E) GAS CONTROL TRANSMISSION OBSERVED A SUDDEN PRESSURE DROP ON SCADA ON TRANSMISSION LINE L-187. PG&E CALLED 9-1-1 AT 1311 HOURS TO REPORT A POSSIBLE GAS LINE BREAK. PG&E'S GAS SERVICE REPRESENTATIVE ARRIVED ON SCENE AT 1355 HOURS. A THIRD PARTY EXCAVATOR, EB FARMS, STRUCK PG&E'S 6-INCH STEEL GAS TRANSMISSION LINE, L-187, RESULTING IN A RELEASE OF GAS. THE EXCAVATOR WAS PLOWING A FIELD AT 62910 CATTLEMEN ROAD, NEAR HIGHWAY 101 IN THE TOWN OF SAN ARDO. THE EXCAVATOR DID NOT CALL USA AND DID NOT HAND DIG TO LOCATE THE GAS LINE PRIOR TO USING MECHANICAL EQUIPMENT. PG&E'S FIELD CREWS ARRIVED AT 1425 HOURS AND THE FLOW OF GAS WAS STOPPED AT 1602 HOURS BY CLOSING A MAIN LINE VALVE. ONE HUNDRED FORTY CUSTOMERS EXPERIENCED GAS SERVICE INTERRUPTION. AT 1700 HOURS ON NOVEMBER 23, 2013, 114 OF THE AVAILABLE CUSTOMERS WERE RELIT. THE REMAINING 26 CUSTOMERS WERE RESTORED BY NOVEMBER 24, 2013. THERE WERE NO INJURIES, NO FATALITIES, NO IGNITION AND NO MEDIA ASSOCIATED WITH THIS INCIDENT. THE VOLUME OF GAS UNINTENTIALLY RELEASED IS LESS THAN 3 MILLION CUBIC FEET. THIS INCIDENT WAS REPORTED TO THE DOT AT 1453 HOURS AND TO THE CPUC AT 1514 HOURS BECAUSE THE COST OF DAMAGES DUE TO THE RELEASE OF GAS IS MORE THAN $50,000.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130119 | 16223 | 2013-12-24 09:42 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2013-11-27 22:19 | 2013 |  |  | 42.9403 | -76.1175 | 1067048 | 2013-11-28 00:07 |  | NATURAL GAS |  | 25230 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | GAS RELEASE WAS DUE TO A RELIEF VALVE MALFUNCTION. ONLY THAT DEVICE WAS ISOLATED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-11-27 22:24 | 2013-11-27 23:25 | ONSHORE | NY | 13084 | LA FAYETTE | ONONDAGA |  |  | STATION 241 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1960 |  | CARBON STEEL |  | OTHER | [8 empty] | THE AD-1 RELIEF VALVE PREMATURELY LIFTED, RELEASING NATURAL GAS. | CLASS 1 LOCATION | NO |  | 482 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 88817 | 69342.7807377049 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 88817 | 71890.8094262295 | 69342.7807377049 | [8 empty] | 682 |  | 760 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NEITHER CONTROL ROOM ACTIONS OR CONTROL ROOM ISSUES CONTRIBUTED TO THE PREMATURE LIFTING OF THE RELIEF VALVE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | EQUIPMENT MALFUNCTION | [161 empty] | KRISTIN VAN DER LAAN | COMPLIANCE ENGINEER III | kristin_vanderlaan@kindermorgan.com | 303-914-7753 |  |  |  |  | REJI GEORGE | DIRECTOR - COMPLIANCE CODES AND STANDARDS | 713-420-5433 | reji_george@kindermorgan.com | LA FAYETTE FIRE DEPARTMENT NOTIFIED TENNESEE GAS PIPELINE (TGP) GAS CONTROL OF A POSSIBLE RELEASE IN THE STATION 241 FACILITY. TGP OPERATIONS PERSONNEL WERE DEPLOYED TO THE LOCATION AND SHUT-IN THE RELIEF VALVE AT 23:25 EASTERN TIME. THE RELIEF VALVE HAS BEEN INSPECTED AND TESTED AND IS OPERATIONAL. THE CAUSE IS UNKNOWN BUT THE RAIN / ICE STORM THAT OCCUR THAT EVENING IS SUSPECTED AS THE CAUSE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20130120 | 16394 | 2013-12-27 16:05 | SUPPLEMENTAL FINAL | 15105 | PANHANDLE EASTERN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2013-11-28 23:57 | 2013 |  |  | 38.8634 | -93.2812 | 1067081 | 2013-11-29 00:58 |  | NATURAL GAS |  | 150000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-11-29 01:25 | 2014-01-02 13:55 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 9 | 2013-11-29 00:02 | 2013-11-29 00:10 | ONSHORE | MO | 65334 | HUGHESVILLE | PETTIS | SURVEY STATION NO. | 250+21 | PANHANDLE EASTERN PIPE LINE COMPANY | HOUSTONIA 400 LINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 |  | 0.312 | 60000 | API 5LX | DSAW |  | KAISER | COAL TAR | [28 empty] | 1962 | 1962 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 43 | 16 |  | CLASS 1 LOCATION | NO |  | 621 |  | NO | NO | NO |  | 450000 | 507398.860958366 | 0 | 0 | 544000 | 424721.31147541 | 929500 | 1048060.53613511 | 8740 | 9854.81343283582 | 73535 | 82914.6116457188 | METALLURGICAL ANALYSIS. |  | 2005775 | 1196908.38976762 | 2072950.13364744 | [8 empty] | 894 |  | 900 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 69447 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE MAOP WAS NOT EXCEEDED. | [12 empty] | YES | 3 | 0 | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [9 empty] | YES |  |  | YES | YES | 1962 | NO | YES | YES | YES |  |  | 2013 | 2013 |  |  | YES | [190 empty] | YES | YES |  |  | YES |  |  | YES | 2005 | [31 empty] | 2000 | [17 empty] | COMBINATION TOOL | 2012 |  |  |  |  | NO |  |  | NO | [13 empty] | NO | [63 empty] | NATHAN HLAVATY | DIRECTOR REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 7138575479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR REGULATORY COMPLIANCE | 7138575479 | nathan.hlavaty@energytransfer.com | THIS SUPPLEMENTAL/FINAL REPORT DATED 05/09/14, IS BEING SUBMITTED TO PROVIDE UPDATES TO PART D.7D, THE COSTS FOR THE METALLURGICAL ANALYSIS. ON 11/28/13 AT 11:57 P.M. THE PANHANDLE EASTERN PIPE LINE COMPANY 30-INCH HOUSTONIA 400 LINE EXPERIENCED AND IN-SERVICE RELEASE WHICH SUBSEQUENTLY IGNITED IN PETTIS COUNTY, MISSOURI JUST NORTH OF THE RURAL COMMUNITY OF HUGHESVILLE. THERE WERE NO INJURIES; HOWEVER, THERE WERE EVACUATIONS OF LOCAL RESIDENTS AS A PRECAUTIONARY MEASURE. THE RELEASE OCCURRED IN A RURAL AREA AND WITHIN A CULTIVATED FIELD. THE PIPE SEGMENT INVOLVED DOES NOT CONTAIN AN HCA. THE INCIDENT WAS INITIALLY REPORTED BY A PEPL COMPANY EMPLOYEE WHO WAS AT A RESIDENCE IN CLOSE PROXIMITY TO THE SITE AND HE CALLED THE OPERATIONS MANAGER FOR THE LOCATION. THE PRESSURE LOSS WAS ALSO ALARMED IN THE GAS CONTROL CENTER. THE PRESSURE AT THE TIME OF THE RELEASE WAS 894 PSIG AT THE HOUSTONIA COMPRESSOR STATION; THE MAOP OF THIS SEGMENT IS 900 PSIG. THE REPORT BY THE PEPL COMPANY EMPLOYEE AND GAS CONTROL ALARMS SET IN MOTION A RESPONSE BY LOCAL EMPLOYEES WHICH HAD THE AFFECTED SEGMENT ISOLATED ON THE UPSTREAM AND DOWNSTREAM SIDES BY 1:25 A.M. LOCAL LAW ENFORCEMENT AND FIRE FIGHTERS RESPONDED TO THE EVENT AND ASSISTED WITH EVACUATIONS, SECURING THE INCIDENT SITE, AND CONTROLLING GROUND FIRES.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20130121 | 16303 | 2013-12-30 19:30 | SUPPLEMENTAL FINAL | 13769 | NORTHERN BORDER PIPELINE COMPANY | 700 LOUISIANA STREET | HOUSTON | TX | 77002 | 2013-11-30 14:30 | 2013 |  |  | 47.769 | -103.4997 | 1067182 | 2013-11-30 18:13 |  | NATURAL GAS |  | 11450 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-11-30 14:30 | 2013-12-01 01:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-11-30 16:15 | 2013-11-30 16:15 | ONSHORE | ND | 58835 | ARNEGARD | MCKENZIE | MILEPOST | 36.2 | CS04 ARNEGARD COMPRESSOR STATION | NORTHERN BORDER MAINLINE VALVE 15 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1982 |  | CARBON STEEL |  | OTHER | [8 empty] | INCOMPLETE CLOSING OF COMPRESSOR STATION FUEL GAS SUPPLY ISOLATION VALVES | CLASS 1 LOCATION | NO |  | 1098 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 45494 | 35518.881147541 | 1508 | 1700.3499607227 | 300 | 338.265907305578 | 0 | 0 |  |  | 47302 | 37759.8153612868 | 37557.4970155693 | [8 empty] | 1235 |  | 1445 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | NO | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | YES | YES | [33 empty] | YES | DEBRIS IN CONTROL VALVE | [161 empty] | KURT SMITH | COMPLIANCE SPECIALIST | kurt_smith@transcanada.com | (509) 533-2848 | (509) 533-2993 |  |  |  | KURT SMITH | COMPLIANCE SPECIALIST | (509) 533-2848 | kurt_smith@transcanada.com | AT 13:51 ON 11/30/2013 THE STATION CONTROL PANEL PROGRAMMABLE LOGIC CONTROLLER (PLC) FAILED DUE TO A DIGITAL INPUT CARD FAILURE. THE PLC FAILURE CAUSED THE STATION TO SHUT DOWN AND BLOW DOWN. THE STATION ISOLATION VALVES AND BLOWDOWN VALVE OPERATED CORRECTLY AND VENTED THE STATION MAIN GAS PIPING. AT THE SAME TIME, THE FUEL GAS VENT VALVES OPENED, BUT THE FUEL GAS ISOLATION VALVES, HV-1014 AND HV-1036 FAILED TO CLOSE. THE ON-CALL TECHNICIAN ARRIVED AT THE STATION AT 16:15 AND DISCOVERED GAS VENTING THROUGH THE FUEL GAS VENT VALVES. AT 16:25 THE FUEL GAS VENT VALVES WERE MANUALLY CLOSED. THE STATION WAS RESTORED TO SERVICE AT 01:15 12/01/2013.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140001 | 16557 | 2014-01-02 16:11 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2013-12-02 13:05 | 2013 |  |  | 40.9292 | -91.3464 | 1067374 | 2013-12-02 23:45 |  | NATURAL GAS |  | 110000 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-12-12 15:48 | 2013-12-14 10:38 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-12-02 13:05 | 2013-12-02 13:45 | ONSHORE | IA | 52645 | NEW LONDON | DES MOINES | MILEPOST | 0.01 | NEW LONDON LATERAL - LINE 356 |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 4 |  | 0.237 | 35000 | API5L | LONGITUDINAL ERW - LOW FREQUENCY |  | NEWPORT STEEL | COAL TAR | [28 empty] | 1960 | 1960 | CARBON STEEL |  | MECHANICAL PUNCTURE | 0.5 | 0.1 | [7 empty] | CLASS 1 LOCATION | NO |  | 200 |  | NO | NO | NO |  | 50000 | 56377.6512175962 | 10000 | 11275.5302435192 | 15000 | 11711.0655737705 | 255000 | 287526.021209741 | 50000 | 56377.6512175962 | 20000 | 22551.0604870385 | EMPLOYEES AT SITE 24 HOURS |  | 400000 | 211408.380873888 | 445818.979949262 | [8 empty] | 817 |  | 975 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 14256 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NOTIFIED BY THIRD PARTY | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES |  | YES | [6 empty] | NO |  |  | YES | PRIVATE EASEMENT | YES | [6 empty] | CONTRACTOR | TRENCHER | DRAINAGE | YES | 133250500 |  | UTILITY OWNER | NO | NO | NO |  | LOCATING PRACTICES NOT SUFFICIENT |  | FACILITY MARKING OR LOCATION NOT SUFFICIENT | [264 empty] | JERRY PALMER | REGULATORY COMPLIANCE SPECIALIST | jerry_palmer@transcanada.com | 708-342-4730 | 708-342-4731 |  |  |  | ROBERT LATIMER | MANAGER - U.S. REGULATORY COMPLIANCE | 402-492-7454 | rob_latimer@transcanada.com | A CONTRACTOR HIT THE ANR PIPELINE WHILE TILING IN THE FARMFIELD. ACCORDING THE INCIDENT ANALYSIS REPORT SUBMITTED EARLIER THIS YEAR THE CONTRACTOR DID UTILIZE THE ONE CALL SYSTEM BUT ALL THE LINES IN THE AREA WERE NOT MARKED. AT 13:05 THE CONTRACTOR CONTACTED ANR AND A TECHNICIAN ARRIVED AT THE SITE AROUND 13:45. THE SITE WAS SECURED BY WORKING WITH LOCAL EMERGENCY RESPONDERS AND ANR PERSONNEL. THE INVESTIGATION PROCESS BEGAN WHICH UTILIZED INFORMATION FROM GAS CONTROL AND A DECISION WAS MADE TO DROP THE PRESSURE TO 400 PSI. AFTER IT WAS SAFE TO APPROACH WHERE THE SOURCE OF THE RELEASE WAS LOCATED IT WAS CONFIRMED AT 22:40. PRESSURE WAS MAINTAINED AND SERVICE WAS CONTINUED ON THE PIPELINE. A SMALL HOLE/PUNCTURE 1/8" X 1/2" WAS DISCOVERED IN THE PIPELINE. SERVICE WAS MAINTAINED BY LNG DURING THE REPAIR PROCESS WHICH WAS A PIPE CUT OUT AND REPLACEMENT. REPAIR WAS MADE AND PIPE WAS PLACED BACK IN FULL SERVICE ON DECEMBER 14, 2013.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140002 | 16228 | 2014-01-04 19:56 | ORIGINAL | 2616 | COLUMBIA GAS TRANSMISSION CORP | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2013-12-06 10:05 | 2013 |  |  | 41.8823 | -75.141 | 1067741 | 2013-12-06 10:51 |  | NATURAL GAS |  | 1 | 11909 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | [7 empty] | NO |  |  |  |  | NO | [6 empty] | 0 |  |  | ONSHORE | NY | 12760 | LONG EDDY | HANCOCK | SURVEY STATION NO. | MLV-1018 | MILLENNIUM 30-IN PIPELINE |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | IN AN OPEN DITCH | 72 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION | [19 empty] | FILLET WELD | [18 empty] | 2013 |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 638 |  | NO | NO | NO |  | 0 | 0 | 44659 | 50355.3905145326 | 3 | 2.3422131147541 | 50000 | 56377.6512175962 | 0 | 0 | 0 | 0 | THE TOTAL COST OF REPAIRS IS NOT AVAILABLE AT THIS TIME. |  | 94662 | 48995.7107806524 | 106735.383945244 | [8 empty] | 950 |  | 1200 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 55387 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE NUISANCE LEAK THAT WAS IDENTIFIED AT THE CRACKED WELD WAS VERY MINUTE AND WOULD HAVE NEVER BE IDENTIFIED BY THE SCADA OR THE CONTROLLER DUE TO ITS INSIGNIFICANT VALUE (LEAK THROUGH A HAIRLINE CRACKED WELD). | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | [9 empty] | YES | CRACKED WELD | [12 empty] | YES | [63 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | GEORGE HAMATY | ENGINEER | ghamaty@nisource.com | (304) 357-3728 | (304) 357-3804 |  |  |  | PERRY MICHAEL HOFFMAN | MANAGER | (304) 357-2548 | mikehoffman@nisource.com | ON DECEMBER 5, 2013, A MILLENNIUM PIPELINE COMPANY (MPC) CONTRACTOR WAS INSTALLING A STOPPLE ON A 30-IN PIPELINE TO ENABLE THE NEWLY CONSTRUCTED COMPRESSOR STATION (HANCOCK) TO TIE-IN TO THE 30-IN MAINLINE PIPE. A NUISANCE LEAK WAS IDENTIFIED AT THE WEST STOPPLE WELDED TEE BY A CONTRACTOR EMPLOYEE. COLUMBIA GAS TRANSMISSION (COLUMBIA) WHO OPERATES AND MAINTAINS MPC'S PIPELINE, INVESTIGATED THE LEAK. PLANS BY ENGINEERING AND FIELD OPERATIONS PERSONNEL WERE SET IN MOTION TO RECTIFY THE NUISANCE LEAK. A DECISION BY COLUMBIA ENGINEERING SERVICES AND FIELD OPERATIONS PERSONNEL WAS MADE TO REDUCE THE OPERATING PRESSURE TO A SAFE VALUE TO 20% OF ITS CURRENT OPERATING PRESSURE AND PERFORM FOLLOW-UP NON-DESTRUCTIVE TESTING (NDT) TO THE IDENTIFIED LOCATION OF THE LEAK. LINE OPERATING PRESSURE WAS 950 PSIG WHEN THE LEAK WAS DETECTED. A NDT WAS NOT PERFORMED UNTIL A SAFE ENVIRONMENT FOR THE CONTRACTOR'S EMPLOYEES WAS ESTABLISHED. AN ADDITIONAL PRESSURE REDUCTION WAS MADE AND THE AREA AROUND THE LEAK WAS RE-EVALUATED. THEREAFTER, A DECISION WAS MADE TO ISOLATE THE LINE IN ORDER TO FURTHER ADDRESS THE IDENTIFIED LEAK LOCATION. THE LINE WAS PURGED AND ISOLATED. COURTESY NOTIFICATIONS WERE MADE TO LOCAL AUTHORITIES AND THE NEAR-BY RESIDENCE ABOUT THE ONGOING ACTIVITY AND THE NOISE ASSOCIATED WITH THE REQUIRED BLOWDOWN. THE NEIGHBOR DECLINED THE OFFER TO MOVE TO A LODGING ACCOMMODATION AND ELECTED TO VISIT A NEAR-BY RELATIVE. AFTER MIDNIGHT, THE LINE WAS ISOLATED. ON JANUARY 6, 2013, THE AREA OF INTEREST WAS TESTED BY THE NDT TEAM AFTER SECURING THE AREA TO BE SAFE TO OPERATE. PRELIMINARY NDT FINDINGS INDICATED THREE TRANSVERSE CRACKS; CIRCUMFERENTIALLY AT THE 09:00, 11:30 AND 12:00 O'CLOCK POSITIONS. THOSE FINDINGS INDICATED THE NEED TO FURTHER INVESTIGATE THE CRACKS FOR DEPTH AND WELD CONDITION OF THE WEST STOPPLE FITTING. THE NEED TO NDT THE SURFACE OF THE REMAINING WELDS OF THE WEST FITTING AS WELL AS THE EAST FITTING WAS DISCUSSED AND ACTED UPON. A CRACK IN A CIRCUMFERENTIAL WELD ON THE EAST STOPPLE FITTING WAS DISCOVERED AT THE 3 O'CLOCK POSITION. THE INSTALLED STOPPLE FITTINGS WITH THE ASSOCIATED WELDS WERE CUT OUT AND REMOVED. A REPLACEMENT OF THE CUT OUT SECTION OF THE PIPE WAS COMPLETED WITH A PRE-TESTED 30-IN PIPING. THIS REPAIR METHOD WAS DETERMINED TO BE THE APPROPRIATE PERMANENT REPAIR. A FOLLOW-UP REVIEW WITH THE HELP OF AN OUTSIDE CONSULTANT WAS UNDERTAKEN. ON DECEMBER 7, 2013, NDT WAS PERFORMED ON THE NEW WELDS AND THE ISOLATED SECTION WAS PURGED WITH A LEAK SURVEY PERFORMED IN AND AROUND THE EXCAVATED AREA. THE LINE WAS LOADED INCREMENTALLY AND RESURVEYED FOR ANY LEVELS OF LEL.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20140003 | 16594 | 2014-01-08 11:45 | SUPPLEMENTAL FINAL | 32296 | TARGA RESOURCES OPERATING LLC | 811 LOUISIANA ST SUITE 2100 | HOUSTON | TX | 77002 | 2013-12-11 12:00 | 2013 |  |  | 29.5192 | -93.2189 | 1068197 | 2013-12-11 12:29 |  | NATURAL GAS |  | 750 | 3439 | 11.4 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-12-11 12:30 | 2013-12-16 06:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-12-11 12:16 | 2013-12-13 06:00 | OFFSHORE | [28 empty] | 49 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST CAMERON | 109 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12.75 |  | 0.375 | 52000 | API5L | SEAMLESS |  | UNKNOWN | EPOXY | [28 empty] | 1970 | 1969 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 200 |  | NO | NO | NO |  | 0 | 0 | 13000 | 14658.189316575 | 3000 | 2342.2131147541 | 182500 | 205778.426944226 | 10000 | 11275.5302435192 | 0 | 0 |  |  | 208500 | 108790.268083654 | 234054.359619075 | [8 empty] | 500 |  | 1240 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | CHECK VALVE | 110544 | NO |  |  | YES |  |  |  |  | NO | [6 empty] | OFFSHORE GATHERING | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  |  | YES | [5 empty] | YES | FIELD EXPERIENCE. | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | TIM HUFFER | MANAGER REGULATORY COMPLIANCE | thuffer@targaresources.com | 337-583-4642 | 337-583-4630 |  |  |  | TIM HUFFER | MANAGER REGULATORY COMPLIANCE | 337-583-4642 | thuffer@targaresources.com | TARGA RECEIVED REPORT OF A GAS LEAK NEAR TARGA'S OFFSHORE GAS GATHERING PIPELINE ON 12/11/2013. TARGA RESPONDEDE BY SHUTTING IN PRODUCTION TO THE LINE AND REDUCING OPERATING PRESSURE. A CLAMP WAS INSTALLED TO REPAIR LEAKING SEGMENT AND PIPELINE RE-STARTED ON 12/16/2013.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140004 | 17345 | 2014-01-09 09:03 | SUPPLEMENTAL FINAL | 2620 | COLUMBIA GULF TRANSMISSION CO | 700 LOUISIANA ST. SUITE 700 | HOUSTON | TX | 77002 | 2013-12-12 13:49 | 2013 |  |  | 34.962 | -88.42 | 1068318 | 2013-12-12 14:11 |  | NATURAL GAS |  | 4320 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | NO ENGINES WERE RUNNING. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-12-12 09:01 | 2013-12-12 09:06 | ONSHORE | MS | 38834-9664 | CORINTH | ALCORN | MILEPOST | 5SH-2U | CORINTH COMPRESSOR STATION | BLOCK CONTROLLER I/O MODULE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | INSTRUMENTATION | [38 empty] | UNKNOWN |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | ELECTRIC CIRCUIT BOARD MATERIAL | OTHER | [8 empty] | OUTPUT BLOCK, CAT#1794-OB8EP FAILURE. | CLASS 1 LOCATION | NO |  | 164 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 17058 | 13317.8237704918 | 250 | 281.888256087981 | 0 | 0 | 0 | 0 |  |  | 17308 | 13936.5867706335 | 13599.7120265798 | [8 empty] | 891 |  | 1008 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | AN OUTPUT BLOCK CONTROLLER FOR THE ISOLATION VALVE FAILED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | YES | [33 empty] | YES | FAULTY ALLEN BRADLEY FLEX I/O 1794-OB8EP RELAY OUTPUT MODULE | [161 empty] | GEORGE HMATY | ENGINEER | george_hamaty@transcanada.com | (304)357-3728 |  |  |  |  | LEE ROMACK | US REGULATORY COMPLIANCE MANAGER | (832)320-5315 | lee_romack@transcanada.com | ON DECEMBER 12, 2013, A COLUMBIA GULF TRANSMISSION, LLC (COLUMBIA) COMPRESSOR STATION (CS) WAS SUBJECT TO AN UNINTENDED EMERGENCY SHUTDOWN (ESD). THIS ESD EVENT TOOK PLACE AT COLUMBIAS CORINTH CS WHICH IS LOCATED IN ALCORN COUNTY, NEAR THE CITY OF CORINTH, MISSISSIPPI. AN OUTPUT BLOCK CONTROLLER FOR THE ISOLATION VALVE FAILED ON THE ESD SYSTEM WHICH LED TO THE CONTINUED FLOW OF NATURAL GAS TO THE ISOLATION BLOW-OFF VALVE THAT EXCEEDED 3,000 MCF (4,320 MCF). AFTER A THOROUGH INVESTIGATION, THIS OUTPUT BLOCK CONTROLLER WAS FOUND FAULTY AND WAS REPLACED. FULL FUNCTIONAL CHECK AND TEST WERE PERFORMED TO THE REPLACED COMPONENTS BEFORE RETURNING THE ESD SYSTEM AND THE CS BACK TO NORMAL SERVICE.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20140005 | 16520 | 2014-01-10 12:43 | SUPPLEMENTAL FINAL | 38987 | KINETICA ENERGY EXPRESS LLC | 1001 MCKINNEY STREET, SUITE 900 | HOUSTON | TX | 77002 | 2013-12-15 10:30 | 2013 |  |  | 29.5039 | -93.7894 | 1068572 | 2013-12-15 12:14 |  | NATURAL GAS |  | 1000 | 35000 | 0.1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-12-15 12:45 | 2014-03-04 09:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-12-15 12:00 | 2013-12-15 12:00 | OFFSHORE | [28 empty] | 85 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SABINE PASS | 10 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | FLANGE ASSEMBLY | [38 empty] | 1981 |  | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO | NO |  | 0 | 0 | 14000 | 15785.742340927 | 700 | 546.516393442623 | 100 | 112.755302435192 | 40000 | 45102.120974077 | 538490 | 607176.028083268 | VESSEL AND DIVER EXPENSES |  | 593290 | 307277.310261677 | 668723.16309415 | [8 empty] | 945 |  | 1440 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 4500 | NO |  |  |  | YES |  |  |  | NO | [6 empty] | OFFSHORE GATHERING | YES | YES | YES | NO | NO | OTHER | LEAK WAS LOCATED APPX. 300' FROM THE PLATFORM. PLATFORM OPERATORS SAW IT. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PINHOLE LEAK IN SUBSEA LOCATION, IN NO WAY COULD CONTROL ROOM OPERATORS CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | [204 empty] | EQUIPMENT NOT INSTALLED PROPERLY |  |  |  | YES |  |  |  |  | CONSTRUCTION | NO | [150 empty] | SUSIE RICHMOND | MANAGER DOT COMPLIANCE AND TRAINING | susie.richmond@kineticallc.com | 985-223-6145 |  |  |  |  | SUSIE RICHMOND | MANAGER DOT COMPLIANCE AND TRAINING | 985-209-4263 | susie.richmond@kineticallc.com | ON 12/15/2013 KINETICA GAS CONTROL WAS NOTIFIED BY FIELDWOOD OPERATIONS PERSONNEL ON THE SABINE PASS PLATFORM. THEY IDENTIFIED A LIGHT SHEEN IN THE WATER ABOUT 300' FROM THE PLATFORM. THEY HAD ALREADY SHUT IN THEIR PIPELINE TO DETERMINE IF THEY WERE THE SOURCE OF THE SHEEN. THEIR SHUT IN DID NOT ELIMINATE THE PROBLEM SO THEY MADE CONTACT WITH KINETICA. WE DISPATCHED OUR PERSONNEL TO THE SCENE, THEY COMMUNICATE MORE ACCURATE COORDINATES TO OUR PIPELINE DIRECTOR WHO ADVISED THEM TO ISOLATE THE PIPELINE SECTION FOR FURTHER INVESTIGATION. A DIVE VESSEL WAS DISPATCHED TO THE LOCATION TO INVESTIGATE AND IDENTIFIED TINY BUBBLES WERE BEING EMITTED FROM A FLANGED SUBSEA CONNECTION. DUE TO POOR WEATHER CONDITIONS THEY RETURNED TO THE DOCK AND ARE SCHEDULED TO RETURN TO THE LOCATION AND COMPLETE AN O-RING REPLACEMENT. ON 3/3/2014 REPLACEMENT OF THE FLANGE GASKET AND O-RING WAS COMPLETED. AN INSPECTION OF THE MATERIALS INDICATED THAT DAMAGE OCCURRED DURING THE ORIGINAL INSTALLATION, WHICH OVER TIME ALLOWED FOR THE O-RING TO FLATTEN AND ALLOW THE PASSAGE OF NATURAL GAS. ALTHOUGH ORIGINAL INSTALLATION OCCURRED IN 1981, WE WILL USE THIS AS A LESSONS LEARNED FOR FUTURE INSTALLATIONS AND REVIEW OUR CONSTRUCTION PROCURES FOR POTENTIAL AREA OF IMPROVEMENT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140006 | 16431 | 2014-01-14 13:14 | SUPPLEMENTAL FINAL | 13845 | NORTHWEST PIPELINE LLC | 295 CHIPETA WAY | SALT LAKE CITY | UT | 84108 | 2013-12-16 17:00 | 2013 |  |  | 47.3147 | -120.118 | 1068710 | 2013-12-16 18:00 |  | NATURAL GAS |  | 155.42 | 14 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | A STOPPLE BY-PASS WAS COMPLETED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-12-16 17:00 | 2013-12-16 17:00 | ONSHORE | WA | 98828 | MALAGA (WENATCHEE) | CHELAN | MILEPOST | 131 | WENATCHEE LATERAL | 2417 | YES | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | FLASH FLOOD EXPOSURE (SEE NARATIVE) | 1 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8.625 |  | 0.188 | 42000 | API 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | KAISER | COAL TAR | [28 empty] | 1956 | 1956 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 174 |  | NO | NO | NO |  | 0 | 0 | 70 | 78.9287117046348 | 777 | 606.633196721311 | 100000 | 112755.302435192 | 150000 | 169132.953652789 | 0 | 0 |  |  | 250847 | 130059.302224319 | 282573.817996407 | [8 empty] | 730 |  | 850 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 104597 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS FOUND WHILE INSPECTING A DENT CAUSED BY A FLASH FLOOD. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [52 empty] | HEAVY RAINS/FLOODS |  | WASHOUTS/SCOURING |  |  |  | YES |  |  |  | YES | FLASH FLOODS | [301 empty] | DANIELLE HUDSON | ENGINEER II | danielle.hudson@williams.com | 801-803-8962 | 801-584-6344 |  |  |  | JARED ELLSWORTH | MANAGER OF PIPELINE SAFETY | 801-584-6539 | jared.ellsworth@williams.com | PRIOR TO THIS INCIDENT THERE WAS A FIRE THAT CLEARED THE AREA OF GROUND VEGETATION. HEAVY RAIN THEN CAUSED A FLASH FLOOD. THE PIPELINE WAS BEING INSPECTED AFTER A FLASH FLOOD EVENT. SEVERAL DENTS WERE DISCOVERED, IN A DRY WASH, WHILE INSPECTING THE PIPELINE. THE PIPE WAS UT INSPECTED IN A FEW AREAS SHOWED 0.185 WT PIPE. WHILE CLEANING THE PIPELINE FOR FURTHER INSPECTION A PIN HOLE LEAK WAS DISCOVERED. THE PIPELINE PRESSURE WAS LOWERED, AND STOPPLE BYPASS WAS COMPLETED TO REMOVE THE DAMAGED SECTION OF PIPELINE. APPROXIMATELY 27' OF PIPE WAS REPLACED. *NOTE: IN PART B #11 OF THIS FORM IT ASKS FOR THE DEPTH-OF-COVER. AFTER THE FLASH FLOOD, THE TOP OF THE PIPE WAS JUST BARELY VISIBLE. THE FORM DIDN'T ALLOW FOR A DEPTH-OF-COVER VALUE OF LESS THAN 1 INCH. TO ANSWER THIS QUESTION AS BEST WE COULD WE STATED THAT THE DEPTH-OF-COVER WAS 1 INCH.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140007 | 16243 | 2014-01-16 15:52 | ORIGINAL | 22655 | WBI ENERGY TRANSMISSION, INC. | 1250 WEST CENTURY AVENUE | BISMARCK | ND | 58503 | 2013-12-23 00:56 | 2013 |  |  | 46.8473 | -101.7828 | 1069327 | 2013-12-23 13:50 |  | NATURAL GAS |  | 3609 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | GAS RELEASED THROUGH VENT PIPING. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-12-23 00:56 | 2013-12-23 01:30 | ONSHORE | ND | 58631-9743 | GLEN ULLIN | MORTON COUNTY | SURVEY STATION NO. | 6814+73 | GLEN ULLIN COMPRESSOR STATION | ESD VENT LINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 2010 |  | CARBON STEEL |  | OTHER | [8 empty] | THE REGULATOR SUPPLYING GAS TO THE ESD SYSTEM FROZE OFF AND CAUSED THE ESD BLOW DOWN VALVES TO OPEN AND RELEASE GAS TO THE ATMOSPHERE THROUGH ESD VENT PIPING. | CLASS 1 LOCATION | NO |  | 332 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 16970 | 13249.118852459 | 0 | 0 | 555 | 625.791928515318 | 1035 | 1167.01738020424 | INSTALLED HEAT TRACE AND A HEAT BLANKET TO PREVENT A SIMILAR INCIDENT. |  | 18560 | 14558.9098940157 | 15041.9281611786 | [8 empty] | 572 |  | 832 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | YES |  |  |  | YES | A SUBZERO OPERATING TEMPERATURE THAT WAS APPROXIMATELY -30 DEGF AMBIENT, WITH A WINDCHILL APPROACHING -50 DEGF. | [301 empty] | KENT KAHL | DOT COMPLIANCE SUPERVISOR | kent.kahl@wbienergy.com | (406) 359-7222 | (406) 359-7244 |  |  |  | KENT KAHL | DOT COMPLIANCE SUPERVISOR | 406-359-7222 | kent.kahl@wbienergy.com | NATURAL GAS WAS VENTED THROUGH EMERGENCY SHUTDOWN (ESD) VALVES AS A RESULT OF A PARTIAL FREEZE OFF OF THE ESD SYSTEM. THE SUPPLY GAS REGULATOR FROZE OFF WHICH RESULTED IN THE SUPPLY GAS SYSTEM PRESSURE DROPPING TO 0 PSIG. THE LOSS OF PRESSURE TO THE SUPPLY GAS SYSTEM CAUSED THE ESD BLOW DOWN VALVES TO OPEN AS DESIGNED AND VENT NATURAL GAS TO THE ATMOSPHERE. THE NATURAL GAS WAS VENTED FOR APPROXIMATELY 54 MINUTES UNTIL PERSONNEL WERE ABLE TO REACH THE SITE AND RESTORE NORMAL OPERATION. DURING A FOLLOW UP INVESTIGATION, A SMALL LEAK WAS FOUND ON A 3/8" TUBING UNION DOWNSTREAM OF THE SUPPLY GAS REGULATOR WHICH WOULD HAVE CAUSED GAS TO FLOW THROUGH THE SUPPLY GAS REGULATOR. THE FLOWING CONDITIONS THROUGH THE SUPPLY GAS REGULATOR IN CONJUNCTION WITH THE AMBIENT TEMPERATURE OF -30 DEGF WOULD HAVE ALLOWED THE SUPPLY GAS REGULATOR TO FREEZE OFF WITH SUBSEQUENT LEAKING THROUGH THE TUBING UNION CAUSING THE LOSS OF PRESSURE TO THE SUPPLY GAS SYSTEM. THE LEAK IN THE 3/8" TUBING UNION HAS BEEN FIXED; AND HEAT TRACE AND AN INSULATION BLANKET HAVE BEEN INSTALLED ON THE SUPPLY GAS REGULATOR TO PREVENT THIS SITUATION FROM REOCCURRING. THIS INCIDENT OCCURRED IN A RURAL LOCATION AT A COMPRESSOR STATION APPROXIMATELY 4 MILES NORTH OF GLEN ULLIN, ND.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140008 | 16464 | 2014-01-17 13:11 | SUPPLEMENTAL FINAL | 12874 | QUESTAR PIPELINE COMPANY | 333 SOUTH STATE STREET P.O. BOX 45360 | SALT LAKE CITY | UT | 84145-0360 | 2013-12-18 01:50 | 2013 |  |  | 39.9083 | -108.2944 | 1068887 | 2013-12-18 08:41 |  | NATURAL GAS |  | 4980 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | ABOVE GROUND PIPING ISOLATED AND REPAIRED. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-12-18 08:21 | 2013-12-18 08:21 | ONSHORE | CO | 81641 | MEEKER | RIO BLANCO | SURVEY STATION NO. | 206+60 | ML 126, HATCH GULCH |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | 1" X 3/4" BUSHING |  |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 27 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 21165 | 16524.3135245902 | 100 | 112.755302435192 | 300 | 338.265907305578 | 0 | 0 | *BASIS FOR 7.F WAS $4.25 PER MCF |  | 21565 | 17338.5367838332 | 16975.3347343309 | [8 empty] | 1081 |  | 1480 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 15 | NO |  |  |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | OTHER | ADJACENT FOREIGN PIPELINE OPERATOR EMPLOYEE |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL ROOM WAS MANNED WHEN THE INCIDENT OCCURED. STAFF IN THE CONTROL ROOM HAD NO WAY OF KNOWING THAT A LEAK OCCURED AT THE 1" X 3/4" THREADED BUSHING AS THERE WAS NO ALARM SET AT THE PRESSURE TRANSDUCER. THEREFORE, THE CONTROL ROOM HAD NO DIRECT WAY OF KNOWING THAT THERE WAS A LEAK OCCURING UNTIL CONFIRMED ON-SITE. A CONTROL ROOM ALARM HAS NOW BEEN ADDED TO THAT PRESSURE TRANSDUCER. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | THREADED FITTING | [19 empty] | YES | FATIGUE CRACK IN 1" X 3/4 "STEEL BUSHING | [161 empty] | CHAD WILDING | SUPERVISOR PIPELINE COMPLIANCE | chad.wilding@questar.com | 801-324-3814 |  |  |  |  | RON JORGENSEN | VICE PRESIDENT GAS CONTROL AND OPERATIONS | 801-324-5145 | ron.jorgensen@questar.com | CREATED SUPPLEMENTAL TO INDICATE THAT THE REPORT IS FINAL. AT 01:50 A BROKEN 1" X 3/4" THREADED BUSHING TO A PRESSURE TRANSDUCER RESULTED IN AN UNINTENDED NATURAL GAS LOSS OF APPROXIMATELY 4.98 MMSCF. A QUESTAR EMPLOYEE ARRIVED ON SITE AT 08:21 AND CONFIRMED THAT THE BUSHING LEADING TO THE PRESSURE TRANSDUCER WAS BROKEN AND ISOLATED THE AREA BY CLOSING 2 MANUAL BLOCK VALVES. THE BUSHING AND VALVE WERE REPLACED SHORTLY THEREAFTER. AFTER THIS INCIDENT QUESTAR PIPELINE ADDED AN ALARM ON THE SCADA SYSTEM FOR THIS PRESSURE TRANSDUCER.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140009 | 16381 | 2014-01-20 14:56 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2013-12-21 22:33 | 2013 |  |  | 42.6979 | -85.9503 | 1069244 | 2013-12-22 14:58 |  | NATURAL GAS |  | 6648 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | CLOSED BLOWDOWN VALVE TO CEASE UNINTENTIONAL RELEASE OF GAS. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-12-21 22:34 | 2013-12-21 23:00 | ONSHORE | MI | 49419-9116 | HAMILTON | ALLEGAN |  |  | OVERISEL COMPRESSOR STATION | BLOWDOWN VALVE 614 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 2001 |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENDED OPERATION OF BLOWDOWN VALVE. | CLASS 2 LOCATION | NO |  | 468 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 31645 | 24706.4446721311 | 500 | 563.776512175962 | 250 | 281.888256087981 | 0 | 0 |  |  | 32395 | 26002.4754758348 | 25552.1094403951 | [8 empty] | 541 |  | 1800 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT OCCURRED DUE TO EQUIPMENT MALFUNCTION. CONTROLLER/CONTROL ROOM ISSUES DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES |  |  |  | YES | [24 empty] | YES | VALVE OPERATOR ACTUATED, LIKELY DUE TO ICE BUILD-UP ON OUTSIDE OF PILOT ASSEMBLY | [161 empty] | ALAN M. CHICHESTER | GAS REGULATORY SERVICES ENGINEER | alan.chichester@cmsenergy.com | 989-791-5841 |  |  |  |  | TRACY A. GOBLE | REGULATORY AND COMPLIANCE MANAGER | 517-768-3187 | tracy.goble@cmsenergy.com | AT APPROXIMATELY 10:33 PM ON DECEMBER 21, 2013, BLOWDOWN VALVE 614 AT OVERISEL COMPRESSOR STATION TRAVELED OPEN AND VENTED GAS TO ATMOSPHERE THROUGH THE STATION EMERGENCY SHUT-DOWN VENT FOR APPROXIMATELY 57 MINUTES. IN TOTAL, ABOUT 6.65 MMCF WAS VENTED TO ATMOSPHERE. PER MANUFACTURER'S RECOMMENDATION, CONSUMERS ENERGY IS PURSUING PLANS TO INSTALL WEATHER-TIGHT ENCLOSURES AND/OR NEW PILOT ASSEMBLIES FOR ALL BIFFI-STYLE VALVES IDENTIFIED AT ITS COMPRESSOR STATIONS. WHERE IMPLEMENTED, THE ENCLOSURES WILL HOUSE THE PILOT VALVE AS WELL AS THE CONTROLLER. AS A NEAR-TERM MEASURE, VALVES ARE BEING MONITORED REGULARLY FOR ICE BUILD-UP TO PREVENT RE-OCCURRENCE. ADDITIONALLY, VENT REPLACEMENT IS IN PROGRESS FOR ALL IDENTIFIED BIFFI VALVES AND IS SCHEDULED FOR COMPLETION BY JANUARY 31, 2014. IN THE EVENT OF A LEAKING SHAFT SEAL, UNRESTRICTED VENTS WILL HELP PREVENT PRESSURE BUILD-UP AT THE VALVE ACTUATOR, THUS PREVENTING THE BLOWDOWN VALVE FROM IMPROPER OPERATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140010 | 16388 | 2014-01-20 16:38 | SUPPLEMENTAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2013-12-26 21:00 | 2013 |  |  | 36.3602 | -97.39 | 1069501 | 2013-12-26 21:32 |  | NATURAL GAS |  | 20073 | 5431 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | LEAK WAS AT A COUPLING AND COULD BE CONTAINED WHILE PUMPKIN WAS PLACED. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-12-26 17:50 | 2013-12-26 18:42 | ONSHORE | OK | 73077 | PERRY | NOBLE | SURVEY STATION NO. | 220/-2286+68 | LINE V | OKLAHOMA CITY-DILWORTH 20" | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 46 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | COUPLING | 1930 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 336 |  | NO | NO | NO |  | 0 | 0 | 18791 | 21187.848880597 | 70771 | 55253.5881147541 | 15772 | 17783.7663000786 | 0 | 0 | 0 | 0 |  |  | 105334 | 75172.9033939449 | 94225.2032954297 | [8 empty] | 525 |  | 594 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 74439 | NO | [5 empty] | YES | ACETYLENE WELDED PIPE. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | MECHANICAL COUPLING | [19 empty] | YES | NO OTHER ISSUES FOUND. COUPLINGS HAVE HISTORY OF LEAKS. | [161 empty] | DAVID COOMES | PIPELINE COMPIANCE ENGINEER | david.coomes@sscgp.com | 270.852.4391 |  |  |  |  | DAVID SINCLAIR | PIPELINE COMPLIANCE MANAGER | 270.852.4424 | david.l.sinclair@sscgp.com | SSCGP RECEIVED A CALL AT 5:50 PM ON 12/26/2013 FROM LOCAL RESIDENT ABOUT GAS BLOWING FROM A PIPE NEAR PERRY, OK IN NOBLE COUNTY. GAS CONTROL CONTACTED OPERATIONS AND NARROWED THE ADDRESS TO THE PERRY STATION. OPERATIONS ARRIVED ON SCENE AT 6:42 PM ON 12/26/2013, CONFIRMING THE LEAK BUT WAS UNABLE TO CONFIRM WHETHER IT WAS A SSCGP LINE OR MUSTANG GAS FACILITY; CONTACT WAS MADE WITH MUSTANG AND SSCGP WAITED FOR THEIR OPERATIONS FOR HELP WITH CONFIRMATION. AT 8:45 PM ON 12/26/2013 CUSTOMERS WERE NOTIFIED AND SSCGP BEGAN TO LOWER GAS FLOW FOR A SHUT IN. AT 9:00 PM THE LEAK WAS VERIFIED TO BE A SSCGP FACILITY AND AT 9:17 PM ON 12/26/13 THE NRC WAS NOTIFIED. THE SEGMENT WAS COMPLETELY SHUT IN AT 10:00 PM ON 12/26/2013. ALL WORK TO INSTALL A HOUSING OVER THE LEAKING COUPLING WAS COMPLETED AND LINE RETURNED TO NORMAL SERVICE AT 8:14 PM ON 12/27/2013.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20140011 | 16426 | 2014-01-21 09:56 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2013-12-31 10:30 | 2013 |  |  | 28.3161 | -91.9971 | 1070176 | 2014-01-06 09:50 |  | NATURAL GAS |  | 25 | 3.14 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-01-06 07:55 | 2014-01-30 21:22 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-01-06 07:55 | 2014-01-06 07:55 | OFFSHORE | [28 empty] | 200 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SOUTH MARSH ISLAND | 130 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1978 |  | CARBON STEEL |  | LEAK |  |  | OTHER | 1/2-INCH THREADED COMPONENT | [5 empty] | CLASS 1 LOCATION | NO |  | 418 |  | NO | NO | NO |  | 0 | 0 | 13575 | 15306.5323055774 | 108 | 84.3196721311475 | 250000 | 281888.256087981 | 4000 | 4510.2120974077 | 15000 | 16913.2953652789 | INSPECTION |  | 282683 | 146341.623158474 | 318702.615528376 | [8 empty] | 728 |  | 1440 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 76454 | NO | YES |  |  | YES |  | YES | PIG TRAPS ARE NOT DESIGNED TO ACCOMODATE INTERNAL INSPECTION TOOLS. | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | YES | YES | YES | NO | NO | OTHER | THIRD PARTY PRODUCER WHO HAS PLATFORM IN THE AREA. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS SO SMALL, PRESSURE INDICATED BY SCADA AND/OR CONTROL ROOM WOULD NOT HAVE BEEN AFFECTED DUE TO PRODUCERS PUTTING IN MORE GAS THAN WAS LEAKING. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | THREADED FITTING | [9 empty] | YES | [172 empty] | JOHNNY LOPEZ | REGULATORY COMPLIANCE SPECIALIST | johnny.lopez@williams.com | 713-215-2995 | 713-215-2222 |  |  |  | MARIE SOTAK | PIPELINE SAFETY MANAGER | 713-215-2111 | marie.sotak@williams.com | ON 12-31-13, AT 10:30 AM CST, AN OFFSHORE VESSEL CONTRACTED BY PRODUCER, ERT, STATIONED AT NEARBY SMI 130-A PLATFORM REPORTED TO WILLIAMS SCHRIEVER DISTRICT OFFICE THAT THEY SITED BUBBLES WITH NO SHEEN ON THE SURFACE OF THE WATER. WILLIAMS OPERATIONS DISPATCHED A HELICOPTER TO INVESTIGATE THE REPORT. THE HELICOPTER CONFIRMED BUBBLES AT THE SAME COORDINATES GIVEN BY THE VESSEL. THE COORDINATES WERE PLOTTED ON ALIGNMENTS SHEETS, THE SUPPORTING DATA SOURCE WAS BSEE'S OWL PROGRAM. AS INDICATED, THERE WERE BUBBLES IN THE VICINITY OF THE WILLIAMS PIPELINE AND A PRODUCER LINE. DUE TO ROUGH SEAS AND WEATHER CONDITIONS WILLIAMS COULD NOT SEND A DIVE BOAT TO CONFIRM THAT THE BUBBLES WERE COMING FROM ITS PIPELINE. IN THE MEANTIME, OPERATIONS MADE A DECISION TO ISOLATE THE WILLIAMS PIPELINE, SUSPEND GAS RECEIPTS INTO THE LINE AND LOWER THE PRESSURE ON THE PIPELINE. AT 7:55 AM CST, ON 1-6-14, EVENTUALLY WEATHER CONDITIONS PERMITTED THE FLYOVER OF THE LEAK AREA AND OPERATIONS WAS ABLE TO CONFIRM THAT THE LEAK WAS COMING FROM THE WILLIAMS PIPELINE. AT 9:50 AM CST GAS CONTROL NOTIFIED THE NRC. A DIVE BOAT WAS SENT TO THE LEAK LOCATION AND THE SOURCE OF THE GAS LEAK WAS IDENTIFIED AS A 1/2-INCH THREADED SWIVEL CONNECTOR ON A SUBSEA ASSEMBLY. THE CONNECTOR WAS REPLACED, THE PIPELINE WAS PRESSURED UP AND PUT BACK INTO SERVICE ON 1-30-14 AT 9:22 PM CST.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140012 | 16991 | 2014-01-22 08:49 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2013-12-27 19:52 | 2013 |  |  | 38.9297 | -99.7415 | 1069577 | 2013-12-27 20:51 |  |  |  | 17.17 | 137.82 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-12-27 19:52 | 2014-11-14 16:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-12-27 19:45 | 2013-12-27 20:01 | ONSHORE | KS | 67656 | OGALLAH | TREGO | SURVEY STATION NO. | 210/3872+86 | LINE W | RAWLINS TO HESSTON | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | COMPRESSOR STATION AUXILARY ROOM | 1979 |  | CARBON STEEL |  | OTHER | [8 empty] | COMPRESSOR BUILDING FIRE. FIRE WAS CONTAINED TO AUXILARY ROOM OF COMPRESSOR BUILDING. | CLASS 1 LOCATION | NO |  | 428 |  | NO | NO | NO |  | 0 | 0 | 585 | 659.618519245876 | 73 | 56.9938524590164 | 2659055 | 2998225.50716811 | 8000 | 9020.4241948154 | 0 | 0 |  |  | 2667713 | 1380767.10461122 | 3007962.54373463 | [8 empty] | 288 |  | 960 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | YES | 3 | 0 | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [146 empty] | DAVID COOMES | PIPELINE COMPLIANCE ENGINEER | david.coomes@sscgp.com | 270.852.4391 |  |  |  |  | DAVID SINCLAIR | PIPELINE COMPLIANCE MANAGER | 270.852.4424 | david.l.sinclair@sscgp.com | AT APPROXIMATELY 19:45 ON 12/27/2013 SSCGP GAS CONTROL BEGAN RECEIVING ALARMS FOR AC POWER, WATER TANK LEVEL, AND STATION FUEL AT THE OGALLAH COMPRESSOR STATION. AT THIS TIME OPERATIONS WAS CALLED AND GAVE AND ETA OF 30 MINUTES TO ARRIVE ON SCENE. THE ESD ALARM CAME INTO GAS CONTROL AT 19:52. OPERATIONS ARRIVED ON SCENE AT 20:01 AND SAW FLAMES COMING FROM THE BOILER ROOM WINDOWS, AT THIS TIME THE ESD VALVE WAS PULLED (STATION WAS ALREADY IN AN ESD STATE). OPERATIONS CALLED THE FIRE DEPARTMENT AT 20:08 AND THEN ADDITIONAL OPERATIONS AND GAS CONTROL TO CONFIRM THE INCIDENT. THE FIRE DEPARTMENT ARRIVED AT APPROXIMATELY 20:25 AND BEGAN APPLYING FOAM TO THE FIRE. BY 20:54 THE FIRE WAS STILL BURNING BUT CONTAINED. OPERATIONS CALLED AT 22:20 ON 12/27/2013 NOTING THAT THE FIRE WAS OUT EXCEPT FOR A COUPLE HOT SPOTS. AN INVESTIGATION BEEN DONE TO DETERMINE WHAT CAUSED THE FIRE, BUT BECAUSE OF THE EXTENSIVE DAMAGE THE ORIGIN OF THE FIRE COULD NOT BE DETERMINED. THE FIRE DESTROYED THE AUXILIARY ROOM. THE ENGINE, WHICH IS SEPERATED BY A FIREWALL FROM THE AUXILARY ROM, WAS NOT DAMAGED BY THE FIRE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140013 | 17024 | 2014-02-02 16:58 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2014-01-03 00:45 | 2014 |  |  | 38.4773 | -81.7111 | 1069991 | 2014-01-03 03:09 |  | NATURAL GAS |  | 15321.18 | 11.52 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-01-03 01:45 | 2014-01-03 11:52 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-01-03 00:45 | 2014-01-03 01:35 | ONSHORE | WV | 25159 | LANHAM | KANAWHA COUNTY | MILEPOST | C9-150 | LANHAM COMPRESSOR STATION | LINE SM-81 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2003 |  | CARBON STEEL |  | OTHER | [8 empty] | BLOW-OFF VALVE MALFUNCTIONED | CLASS 2 LOCATION | NO |  | 175 |  | NO | NO | NO |  | 0 | 0 | 409 | 452.41758982757 | 64809 | 43243.8336252189 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 65218 | 45040.5174960114 | 43696.2512150465 | [8 empty] | 400 |  | 1000 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 501 | NO | [5 empty] | YES | NO LAUNCHER AND RECEIVER CURRENTLY INSTALLED ON LINE TO ALLOW THE USE OF INLINE INSPECTION TOOLS. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS CONTROL HAD NO INVOLVEMENT IN THE INCIDENT AND DID NOT CONTRIBUTE TO THE INCIDENT BY OPERATING ANY VALVES OR STARTING/STOPPING ANY COMPRESSORS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | OTHER | 8-IN BLOW-OFF VALVE | [20 empty] | YES | PAINT RESTRICTED OPERATIONAL FUNCTIONALITY OF THE BO VALVE | [161 empty] | GEORGE HAMATY | ENGINEER | ghamaty@cpg.com | (304) 357-2184 |  |  |  |  | PERRY M. HOFFMAN | MANAGER | (304) 357-2548 | mikehoffman@cpg.com | ON JANUARY 3, 2014 AT 12:45 EST, AN 8-IN BLOW-OFF (BO) VALVE ON PIPELINE SM-81 INADVERTENTLY ACTIVATED. LINE SM-81 IS LOCATED AND IS FED FROM LANHAM COMPRESSOR STATION YARD THROUGH A REGULATION RUN THAT CUTS THE PRESSURE TO APPROXIMATELY 400 PSIG. THIS BO VALVE REMAINED OPEN FOR APPROXIMATELY 70 MINUTES AND CONTINUALLY VENTED GAS AS THE LINE AND THE OPEN BO WERE FED BY THE REGULATORS. IT WAS IDENTIFIED THAT A VENT CAP ON A TRIGGER VALVE WAS HELD CLOSED RENDERING IT INOPERABLE DUE TO PAINT WHICH RESTRICTED ITS NORMAL FUNCTIONALITY. AN INTERNAL COMMUNICATIONS MEMORANDUM WAS ISSUED COMPANY-WIDE TO INSPECT SIMILAR INSTALLATIONS (AFTER RECONDITIONING) AND TO AVOID A SIMILAR RE-OCCURRENCE DUE TO THE IDENTIFIED CAUSAL FACTOR. INITIAL INCIDENT REPOT WAS SUBMITTED ON FEBRUARY 02, 2014
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140014 | 16261 | 2014-02-03 15:02 | ORIGINAL FINAL | 12408 | DTE GAS COMPANY | ONE ENERGY PLAZA | DETROIT | MI | 48226 | 2014-01-06 14:05 | 2014 |  |  | 43.4436 | -85.141 | 1070373 | 2014-01-07 17:44 |  | NATURAL GAS |  | 18400 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-01-06 14:59 | 2014-01-06 17:10 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-01-06 14:05 | 2014-01-06 14:05 | ONSHORE | MI | 48886-8721 | SIX LAKES | MONTCALM |  |  | W C TAGGART COMPRESSOR STATION | PLANT 1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2002 |  | CARBON STEEL |  | LEAK |  |  | OTHER | VALVE OPER DIDNT CLOSE VALVE | [5 empty] | CLASS 1 LOCATION | NO |  | 129 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 86664 | 57826.591943958 | 2250 | 2488.84982178981 | 970 | 1072.9708120605 | 0 | 0 |  |  | 89884 | 61586.4232462951 | 61388.4125778083 | [8 empty] | 367 |  | 970 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ACTIONS BY LOCAL OPERATING PERSONNEL WERE APPROPRIATE IN RESPONSE TO THE EVENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [28 empty] | YES | [164 empty] | JOHN D LUEDERS PE | COMPLIANCE ENGINEER | luedersj@dteenergy.com | 6166322646 | 6166322687 |  |  |  | ROBERT H FRECKELTON | MANAGER CODES AND STANDARDS | 3133897755 | freckeltonr@dteenergy.com | AT APPROXIMATELY 14:05 A FLAME SENSOR NEAR COMPRESSOR UNIT 109 IN PLANT 1 ACTIVATED THE EMERGANCY SHUTDOWN (ESD) SYSTEM FOR PLANT 1. FOUR RELIEF VALVE OPERATORS PROPERLY ACTUATED TO OPEN, RELEASING NATURAL GAS TO THE ATMOSPHERE IN ACCORDANCE WITH THE ESD SYSTEM DESIGN. THE ESD ALSO TRIGGERED FOUR BLOCK VALVE OPERATORS INTENDED TO ISOLATE PLANT 1 FROM THE INLET (SUCTION) AND OUTLET (DISCHARGE) PIPELINES; HOWEVER, ONLY ONE OF THE FOUR BLOCK VALVES ACTUALLY CLOSED. LOCAL OPERATING PERSONNEL DETERMINED THAT EXTREME WEATHER OVER THE PAST DAYS (TEMPERATURES AS LOW AS -15 DEGREES F, WINDY AND SNOW CONDITIONS) MAY HAVE PREVENTED THE HYDRAULIC ACTUATING SYSTEMS FOR THE REMAINING THREE BLOCK VALVE OPERATORS FROM CLOSING THOSE THREE VALVES. LOCAL OPERATING PERSONNEL MANUALLY OPERATED THE REMAINING THREE BLOCK VALVES, CLOSING THE LAST ONE AT APPROXIMATELY 14:59. ONCE THE LAST OF THE THREE REMAINING BLOCK VALVES WERE CLOSED, THE PIPING TO PLANT 1 CONTINUED TO BLOW DOWN TO ATMOSPHERIC PRESSURE IN UNDER A MINUTE. AT NO TIME WAS MAOP OF THE COMPRESSOR STATION PIPING EXCEEDED. INVESTIGATION REVEALED THERE WAS NO FIRE OR IGNITION INSIDE THE BUILDING AT PLANT 1. INVESTIGATION CONTINUES INTO WHETHER THE FLAME SENSOR MAY HAVE BEEN FAULTY AND NEEDS TO BE REPLACED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140015 | 16346 | 2014-02-05 10:52 | SUPPLEMENTAL FINAL | 31286 | ONEOK GAS TRANSPORTATION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2014-01-06 10:57 | 2014 |  |  | 35.7346 | -96.5618 | 1070197 | 2014-01-06 11:48 |  | NATURAL GAS |  | 39400 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-01-06 11:58 | 2014-01-09 20:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2014-01-06 11:03 | 2014-01-06 11:20 | ONSHORE | OK | 74028 | DEPEW | CREEK |  |  | A-26 |  | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | IN OR SPANNING AN OPEN DITCH |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 26 |  | 0.25 | 52000 | X-52 API-5XL | LONGITUDINAL ERW - LOW FREQUENCY |  | A. O. SMITH | COLD APPLIED TAPE | [28 empty] | 1951 | 1950 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 334 | 44 |  | CLASS 1 LOCATION | NO |  | 517 |  | NO | NO | NO |  | 70000 | 77430.8833445718 | 0 | 0 | 165165 | 110206.418563923 | 180000 | 199107.985743185 | 3000 | 3318.46642905308 | 0 | 0 |  |  | 418165 | 242717.899799597 | 390063.754080733 | [8 empty] | 585 |  | 600 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 56496 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) | [5 empty] | YES | [7 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION | [6 empty] | YES | PENDING THIRD PARTY FAILURE ANALYSIS UPDATE: THIRD PARTY FAILURE ANALYSIS DETERMINED THE FAILURE WAS CAUSED BY GENERAL AND INTERGRANULAR EXTERNAL CORROSION THAT OCCURRED UNDER COLD APPLIED TAPE COATING |  |  |  |  | YES | PENDING THIRD PARTY FAILURE ANALYSIS UPDATE: THIRD PARTY FAILURE ANALYSIS | NO | [11 empty] | YES | NO | [190 empty] | YES | YES | YES |  | YES |  |  |  | 2003 | [11 empty] | 2010 | [19 empty] | 2010 | [23 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | PATTI FORD | SENIOR PIPELINE SAFETY ENGINEER | patti.ford@oneok.com | 918 588 7131 | 918 732 1311 |  |  |  | WESLEY R. DUNBAR | VICE PRESIDENT | 918 588 7424 | wes.dunbar@oneok.com | THE ONEOK GAS TRANSPORTATION (OGT) LINE A-26 PIPELINE FAILED AND ESCAPING GAS IGNITED APPROXIMATELY 1.5 MILES SOUTH OF MILFAY, OK AT 1057 HOURS ON JANUARY 6, 2014. OGT FIELD OPERATIONS PERSONNEL WORKING AT THE ONEOK GAS STORAGE DEPEW STORAGE FACILITY WERE THE FIRST TO RECOGNIZE THE EVENT AND NOTIFIED GAS CONTROL WITHIN FIVE MINUTES. GAS CONTROL CONFIRMED THIS ALSO WITH THE DATA COMING IN ON THEIR SCADA SCREENS. OGT PERSONNEL WERE DISPATCHED TO THE SITE ARRIVING AT 1120 HOURS. LOCAL LAW ENFORCEMENT AND FIRE DEPARTMENT ALSO RESPONDED. THERE WERE NO FATALITIES OR INJURIES. THE 10.7 MILE PIPE SEGMENT WAS ISOLATED AT 1155 HOURS. NATURAL GAS SERVICE WAS DISRUPTED TO 48 UTILITY CUSTOMERS IN MILFAY AND 13 RURAL FARM TAP CUSTOMERS WERE ALSO IMPACTED. A NEW SECTION OF PIPE WAS INSTALLED AND THE PIPELINE RETURNED TO SERVICE ON JANUARY 9, 2014. UPDATE: THIRD PARTY FAILURE ANALYSIS DETERMINED THE FAILURE WAS CAUSED BY GENERAL AND INTERGRANULAR EXTERNAL CORROSION THAT OCCURRED UNDER COLD APPLIED TAPE COATING. THIS CAUSED A REDUCTION IN THE PIPELINE WALL THICKNESS TO THE POINT THE MATERIAL WAS NO LONGER CAPABLE OF CONTAINING THE GAS PRESSURE AND FAILURE OCCURRED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140016 | 16266 | 2014-02-10 12:00 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2014-01-23 00:30 | 2014 |  |  | 41.8702 | -77.9939 | 1071875 | 2014-01-23 01:05 |  | NATURAL GAS |  | 8370 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | INCIDENT INVOLVED ONLY A RELIEF VALVE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-01-23 00:30 | 2014-01-23 00:30 | ONSHORE | PA | 16915 | COUDERSPORT | POTTER |  |  | 313C 103 RELIEF | HEBRON STORAGE LITTLE ACRE METER STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ABOVEGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | OTHER | [37 empty] | RELIEF VALVE | 2007 |  | CARBON STEEL |  | OTHER | [8 empty] | RELEASE FROM A RELIEF VALVE | CLASS 1 LOCATION | NO |  | 488 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 33480 | 22339.5446584939 | 144 | 159.286388594548 | 204 | 225.655717175609 | 0 | 0 |  |  | 33828 | 23337.1188991879 | 22724.486764264 | [8 empty] | 811 |  | 1250 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | NOTIFICATION BY ANOTHER OPERATOR'S PERSONNEL (A WELL TENDER) |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | AT NO TIME WAS PRESSURE OUTSIDE OF NORMAL LIMITS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | YES |  |  |  |  | YES | [28 empty] | YES | EXTREMELY COLD WEATHER | [161 empty] | KENNETH C PETERS | SENIOR ENGINEER - PIPELINE | ken_peters@kindermorgan.com | 2053257554 | 2053253508 |  |  |  | KENNETH C PETERS | SENIOR ENGINEER - PIPELINE | 2053257554 | ken_peters@kindermorgan.com | EXTREMELY COLD TEMPERATURES (0 DEGREES F) FROZE OFF INSTRUMENTATION/SUPPLY EQUIPMENT FOR A RELIEF VALVE AT THE TENNESSEE GAS PIPELINE HEBRON STORAGE LITTLE ACRE METER STATION, CAUSING THE RELIEF VALVE TO ACTIVATE PREMATURELY. NATURAL GAS WAS RELEASED THROUGH THE RELIEF VALVE'S OUTLET PORT OF A QUANTITY SUFFICIENT TO REQUIRE 49 CFR 191 INCIDENT REPORTING.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140017 | 17624 | 2014-02-10 14:18 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2014-01-12 19:57 | 2014 |  |  | 37.5423 | -82.7643 | 1070935 | 2014-01-12 21:19 |  | NATURAL GAS |  | 7200 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-01-12 20:30 | 2014-01-12 20:40 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-01-12 19:57 | 2014-01-12 20:15 | ONSHORE | KY | 41649 | Not Within a Municipality | FLOYD | MILEPOST | 27+51 - 56+16 | PM-83 | VS-7077 BEAVER CREEK TO LITTLE MUD CREEK | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 |  | 0.25 | 52000 | API-5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | TENARIS TUBULAR TECHNOLOGIES | EPOXY | [28 empty] | 2012 | 2012 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 33 | 1 |  | CLASS 1 LOCATION | NO |  | 184 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 30456 | 20321.7793345009 | 10000 | 11061.5547635103 | 2000 | 2212.31095270205 | 0 | 0 |  |  | 42456 | 27161.5660025532 | 33595.6450507132 | [8 empty] | 221 |  | 438 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL |  | NO | YES | YES |  | YES |  |  |  | YES |  | YES |  |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PROPER RESPONSE TO ALARMS BY THE CONTROLLER AND THERE WAS NO HUMAN INTERVENTION OR ISSUED COMMANDS (REMOTE) TO INITIATE THE FAILURE | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [52 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | SUBSIDENCE |  |  |  |  | NO | [306 empty] | MARK NEWMAN | COMPLIANCE SPECIALIST SR ENGINEER | mark_newman@transcanada.com | (304) 722-8475 | (304) 722-8420 |  |  |  | LEE ROMACK | MANAGER | (832) 320-5315 | lee_romack@transcanada.com | ON JANUARY 12, 2014, A PIPELINE FAILURE OCCURRED ON LINE PM-83, A COLUMBIA GAS TRANSMISSION, LLC LINE. THE PIPELINE FAILURE OCCURRED IN A REMOTE CLASS 1 LOCATION, APPROXIMATELY ONE MILE EAST OF THE SMALL VILLAGE OF WARCO, NEAR MARTIN KENTUCKY IN FLOYD COUNTY. OPERATIONS PERSONNEL ACTED PROMPTLY TO CLOSE VALVE PM-83-100 TO ISOLATE THE LINE. THE OTHER END WAS CAPPED DUE TO THE STRIP MINING ACTIVITIES. THE LINE FAILED CIRCUMFERENTIALLY AND PARTIALLY PULLED APART BUT DID NOT SEPARATE. THE LINE IS CURRENTLY BLOWN DOWN AND OUT OF SERVICE. THIS LINE WILL REMAIN OUT OF SERVICE UNTIL THE INTEGRITY OF THE PIPE IN THE AREA OF THE FAILURE CAN BE CONFIRMED AND THE AREA REPAIRED. A SCADA SYSTEM IS IN PLACE ON A COMMON PIPELINE SUPPLYING THE LINE IN QUESTION WHERE THIS SYSTEM WAS USED FOR IDENTIFICATION AND VERIFICATION OF THE INCIDENT. INITIAL INCIDENT REPOT WAS SUBMITTED ON FEBRUARY 10, 2014 7/26/2017 - RESULTS FROM THE METALLURGICAL ANALYSIS INDICATE THE RUPTURE INITIATED AT A FIELD GIRTH WELD WHICH WAS LOCATED BETWEEN PIPE AND ELBOW FITTING. THE RUPTURE OCCURRED DUE TO OVERLOAD FROM AN AXIAL STRESS SUCH AS THOSE CAUSED BY LAND/SOIL MOVEMENT. THE LINE REMAINS OUT OF SERVICE PENDING REPAIRS. A 3-5 YEAR ESTIMATE IS PREDICTED BEFORE REPAIRS ARE MADE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140018 | 16658 | 2014-02-10 15:35 | SUPPLEMENTAL FINAL | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 800 GASTON ROAD | GASTONIA | NC | 28056 | 2014-01-10 15:51 | 2014 |  |  | 35.5415 | -82.6435 | 1070739 | 2014-01-10 17:10 |  | NATURAL GAS |  | 2786 | 92 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-01-10 17:26 | 2014-01-11 02:13 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 20 | 2014-01-10 15:53 | 2014-01-10 16:05 | ONSHORE | NC | 28715 | CANDLER (NEAR ASHEVILLE) | BUNCOMBE | MILEPOST | T-33 MP-9.90 | T-033 | T-033-A375 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 48 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12.75 |  | 0.219 | 42000 | API 5LX | SEAMLESS |  | US STEEL | COAL TAR | [28 empty] | 1963 | 1963 | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | ALONG A GOUGE | 26.8 | 9 |  | CLASS 3 LOCATION | NO |  | 160 |  | YES | YES | NO |  | 446367 | 493751.301512378 | 375 | 414.808303631635 | 11345 | 7569.95621716287 | 235193 | 260160.024949427 | 84007 | 92924.8031018206 | 0 | 0 |  |  | 777287 | 396758.654087835 | 854820.89408442 | [8 empty] | 345 |  | 375 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 29245 | NO |  | YES | YES | YES |  |  |  | YES |  | YES |  |  |  |  | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA EQUIPMENT INDICATED A PRESSURE ALARM WHICH WAS ESCALATED PROPERLY AND PROMPTLY. NO CONTROLS ON SYSTEM IN AREA-MONITOR ONLY. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [64 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | [10 empty] | NO | YES | STATE HIGHWAY | [9 empty] | UTILITY | DIRECTIONAL DRILLING | NATURAL GAS | YES | 361097 |  | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | YES | 9 | PREVIOUS DAMAGE | [121 empty] | NO | [62 empty] | YES | NO |  |  | Yes, but the point of the Accident was not identified as a dig site |  | 2005 | [11 empty] | NO | [63 empty] | DANIA H POOL | SR. ANALYST-ENGINEERING | dpool@scana.com | 704-810-3257 | 704-810-3220 |  |  |  | MILTON S. SWINDLER | GENERAL MGR-CONSTRUCTION AND MAINTENANCE | 704-810-3230 | sswindler@scana.com | PSNC ENERGY SAND HILL T-33 PIPELINE RUPTURE JANUARY 10, 2014 THE FOLLOWING INFORMATION UPDATES THE NARRATIVE PROVIDED IN THE ORIGINAL INCIDENT AND INCLUDED ATTACHMENTS. CAUSE OF RUPTURE PSNC ENERGY DETERMINED FROM THE INVESTIGATION OF THE REMOVED SECTION OF T-33 AND OBSERVATIONS MADE DURING THE EMERGENCY RESPONSE / RESTORATION EFFORTS THAT THE RUPTURE WAS CAUSED BY MECHANICAL DAMAGES THAT OCCURRED DURING THE 2003 INSTALLATION OF THE 4-INCH PLASTIC DISTRIBUTION. THE DISTRIBUTION PIPE WAS INSTALLED BY PSNC ENERGY'S CONTRACTOR USING A HORIZONTAL DIRECTIONAL BORE METHOD. AT THE TIME OF THE 2003 CONSTRUCTION, SAND HILL ROAD HAD NOT BEEN WIDENED TO THE POINT WHERE IT EXTENDED OVER T-33. THE LOCATION OF T-33 WAS NOT PROPERLY IDENTIFIED AND THE BORE PATH FOR THE DISTRIBUTION LINE WAS ESSENTIALLY THE SAME AS T-33. WHILE FOLLOWING THE T-33 DITCH LINE THE BORING HEAD CREATED SHALLOW SCRATCHES ALONG T-33. THE DIRECTIONAL BORING HEAD HIT THE 18-INCH CULVERT AND CREATED DEEP GOUGES AS THE HEAD WAS ROTATED TO CLEAR THE OBSTRUCTION. THE DEEP GOUGES CREATED SHEAR CRACKS WHICH SET UP CONDITIONS THAT ULTIMATELY LED TO THE RUPTURE OF THE PIPELINE. THIS WAS CONFIRMED BY METALLURGICAL TECHNOLOGIES, INC. P.A. REPORT 2014141 (3/20/2014). THIS REPORT DISCOUNTED ANY ADDITIONAL STRESSES CREATED BY THE CULVERT. REMEDIAL ACTIONS PRESSURE ON T-33 WAS LIMITED TO 175 PSIG FROM THE TIME OF THE TEMPORARY REPAIR UNTIL PERMANENT REPAIRS COULD BE MADE. PSNC ENERGY FILED A SAFETY RELATED CONDITION REPORT IN ACCORDANCE WITH 49 CFR PART 191.25 ON JANUARY 15, 2014. PSNC ENERGY MADE THE DECISION TO REPLACE THE 1,000 FOOT SECTION OF T-33 THAT RAN PARALLEL TO THE 4-INCH DISTRIBUTION LINE. ONSITE CONSTRUCTION BEGAN ON JANUARY 16, 2014 AND THE NEW SEGMENT WAS IN SERVICE ON FEBRUARY 1, 2014 WHICH CORRECTED THE PIPELINE ISSUES WHICH CREATED THE SAFETY RELATED CONDITION REPORT. SYSTEM PRESSURE HAS BEEN RESTORED TO 350 PSIG AND THE SCADA ALARMS HAVE BEEN RESET. AN UPDATE OF THE STATUS OF THE SAFETY RELATED CONDITION REPORT WAS PROVIDED TO CHRIS TAYLOR, PIPELINE AND HAZARDOUS MATERIALS SAFETY ADMINISTRATION - SOUTHERN REGION, BY EMAIL FROM SCOTT SWINDLER ON MARCH 3, 2014. DAMAGE ESTIMATES THE FIRE AND RUPTURE CAUSED DAMAGE TO SEVERAL CARS, HOMES AND COMMERCIAL BUILDINGS IN THE AREA. IN ADDITION, THE ROAD, AND SEVERAL OTHER UTILITIES WERE DAMAGED. ALL DAMAGE ESTIMATES WITHIN THE INCIDENT REPORT HAVE BEEN UPDATED WITH ACTUAL VALUES AS OF FEBRUARY 13, 2015.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140019 | 16270 | 2014-02-12 08:44 | ORIGINAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2014-01-13 04:13 | 2014 |  |  | 29.0649 | -98.1741 | 1071030 | 2014-01-13 16:20 |  | NATURAL GAS |  | 0 | 3470 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | GAS CONTROL REDIRECTED NATURAL GAS AND SUPPLIERS WERE CURTAILED. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-01-13 04:13 | 2014-01-13 05:36 | ONSHORE | TX | 78114 | FLORESVILLE | WILSON | MILEPOST | STATION 536 | DIMMIT COUNTY MAINLINE 20" | 287-1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [8 empty] | CARBON STEEL |  | OTHER | [8 empty] | DUE TO YOAKUM PLANT PROCESS UPSET AND SUBSEQUENT SHUT DOWN, THE OPERATING PRESSURE ROSE UNTIL THE STATION 536 RELIEF VALVE OPERATED AS DESIGNED VENTING APPROXIMATELY 3.47 MMCF. DURING THIS EVENT, THE WILSON COUNTY SHERIFF'S DEPARTMENT CLOSED HIGHWAY 536. | CLASS 1 LOCATION | NO |  | 457 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 17350 | 11576.7950963222 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 17350 | 12002.1891418564 | 11576.7950963222 | [8 empty] | 1092 |  | 1100 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | DUE TO YOAKUM PLANT PROCESS UPSET AND SUBSEQUENT SHUT DOWN, THE OPERATING PRESSURE ROSE UNTIL THE STATION 536 RELIEF VALVE OPERATED AS DESIGNED VENTING APPROXIMATELY 3.47 MMCF. DURING THIS EVENT, THE WILSON COUNTY SHERIFF'S DEPARTMENT CLOSED HIGHWAY 536. | [147 empty] | MICHAEL D. SMITH | PIPELINE COMPLIANCE SPECIALIST | mdsmith@eprod.com | 713-381-5650 | 713-381-7995 |  |  |  | MICHAEL D. SMITH | PIPELINE COMPLIANCE SPECIALIST | 713-381-5650 | mdsmith@eprod.com | ON MONDAY, JANUARY 13, 2014 AT APPROXIMATELY 12:30 AM THE YOAKUM PLANT SHUT DOWN. GAS CONTROL MONITORED PIPELINE PRESSURE/LINE PACK FOR LINE 287-1, HAVING AN MAOP OF 1100 PSIG. AT 4:13 AM, GAS CONTROL RECEIVED A CALL FROM THE WILSON COUNTY SHERRIFF'S DEPARTMENT, REPORTING A POPPING SOUND AT STATION 536 AND THAT THEY HAD CLOSED HIGHWAY 536 DUE TO VENTING OF NATURAL GAS. THE RELIEF VALVE WAS SET TO RELIEVE AT 1100 PSIG. GAS CONTROL WAS ABLE TO LOWER THE OPERATING PRESSURE BY DIVERTING GAS SUPPLIES. WHEN OPERATIONS ARRIVED ON THE SCENE AT 5:36 AM, THE PRESSURE WAS REDUCED SUCH THAT THE INCIDENT HAD ENDED. THE GAS RELEASE VOLUME WAS CALCULATED TO BE APPROXIMATELY 3.47 MSCF. THE RELIEF VALVE FUNCTIONED AS DESIGNED TO INTENTIONALLY RELEASE EXCESS PRESSURE INTO A SAFE ENVIRONMENT TO AVOID AN OVERPRESSURE SITUATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140020 | 16383 | 2014-02-16 22:36 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2014-01-17 09:15 | 2014 |  |  | 28.9816 | -90.3312 | 1071414 | 2014-01-17 09:40 |  | NATURAL GAS |  | 5000 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | SMALL BUBBLES OBSERVED INDICATE A SMALL NON-HAZARDOUS LEAK OCCURRRED. | [6 empty] | NO |  |  |  |  | NO | [7 empty] | 2014-01-17 09:11 | 2014-01-17 12:30 | OFFSHORE | [28 empty] | 50 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EUGENE ISLAND | 115 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | FLANGE ASSEMBLY | [38 empty] | 1968 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 312 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 40000 | 26690.0175131349 | 135000 | 149330.989307389 | 20000 | 22123.1095270205 | 0 | 0 | NONE |  | 195000 | 106372.708560416 | 198144.116347544 | [8 empty] | 1050 |  | 1300 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 50000 | NO |  |  |  | YES |  |  |  | YES |  |  |  |  | YES | PIPELINE IS A LATERAL LINE, NOT PIGABE | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO CRM ISSUES WERE IDENTIFIED AS CONTRIBUTING TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | GASKET | [7 empty] | YES | [172 empty] | LOUIS SALINAS | CIVIL ENGINEER | louis_salinas@transcanada.com | 832-320-5305 | 832-320-6305 |  |  |  | LOUIS SALINAS | CIVIL ENGINEER | 832-320-5305 | No Email Address | AT ABOUT 9:11 A.M. CST ON FRIDAY (JANUARY 17), A POTENTIAL LEAK WAS DETECTED ON THE TC OFFSHORE SYSTEM'S SOUTHEAST AREA EAST LEG, LOCATED IN EUGENE ISLAND BLOCK 115, ABOUT 70 MILES WEST OF PATTERSON, LA. AN EXPERIENCED DIVE TEAM DISPATCHED TO THE SITE ON FRIDAY CONFIRMED THERE IS A MINOR LEAK ON THE TIE-IN ASSEMBLY THAT CONNECTS TCO"S 12-INCH DIAMETER PIPELINE SYSTEM WITH THE COMPANY'S 20-INCH DIAMETER PIPELINE SYSTEM. BECAUSE OF THE LOCATION OF THE LEAK, A LATERAL PIPELINE CONNECTED TO THE TIE-IN ASSEMBLY WILL HAVE TO BE ISOLATED AND BLOWN DOWN IN ORDER TO MAKE THE REPAIRS. ONCE THE LEAK WAS CONFIRMED AND INITIAL REPAIR ASSESSMENTS MADE, TCO PERSONNEL IMMEDIATELY BEGAN WORKING ON A PLAN TO REPAIR THE LINE. THE PIPELINE WAS SUBSEQUENTLY REPAIRED DURING THE WEEK OF FEB. 17. 2014. DIVERS WERE ABLE TO REPALCE A DAMAGED GASKET ON THE FLANGE IN THE SS VALVE ASSEMBY AND PLACED THE PIPELINE BACK INTO SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140021 | 16277 | 2014-02-18 12:34 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2014-01-24 20:35 | 2014 |  |  | 28.6618 | -96.9965 | 1072055 | 2014-01-24 22:07 |  | NATURAL GAS |  | 2356 | 9600 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-01-24 21:20 | 2014-02-04 12:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-01-24 21:20 | 2014-01-24 21:20 | ONSHORE | TX | 77905 | VICTORIA | VICTORIA | MILEPOST | 8-1 + 9.07 | TGP 100-1 LINE | 8-1 TO 9-1S | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 40 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 24 |  | 0.25 | 50000 | API 5L OR EQUIVALENT | FLASH WELDED |  | A.O. SMITH | COAL TAR | [9 empty] | PIPE GIRTH WELD | [18 empty] | 1944 | 1944 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 454 |  | NO | NO | NO |  | 0 | 0 | 38400 | 42476.3702918794 | 9424 | 6288.16812609457 | 81000 | 89598.5935844331 | 2160 | 2389.29582891822 | 1650 | 1825.15653597919 | HYDRO-VAC TRUCK ON STANDBY. |  | 132634 | 69079.6677228083 | 142577.584367304 | [8 empty] | 617 |  | 750 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 69074 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE PRESSURE WAS NEVER OUTSIDE OF NORMAL OPERATING LIMITS. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | YES | [7 empty] | YES | LACK OF FUSION DUE TO MISALIGNMENT. | [12 empty] | YES | YES |  |  |  | YES | [58 empty] | YES | YES | [6 empty] | 2004 | [55 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KENNETH C PETERS | SENIOR ENGINEER - PIPELINE | ken_peters@kindermorgan.com | 2053257554 | 2053253508 |  |  |  | REJI GEORGE | DIRECTOR - COMPLIANCE CODES AND STANDARDS | 7134205433 | reji_george@kindermorgan.com | A LAND OWNER REPORTED HEARING A LOUD NOISE IN THE VICINITY OF TENNESSEE GAS PIPELINE'S (TGP) 100 PIPELINE SYSTEM ON JANUARY 24, 2014 NEAR VICTORIA, TX. TGP PERSONNEL WERE DISPATCHED AND DISCOVERED NATURAL GAS BEING RELEASED FROM TGP'S 24" 100-1 PIPELINE. VALVES WERE CLOSED TO ISOLATE THE SEGMENT WHICH BLEW DOWN TO ATMOSPHERIC PRESSURE. VISUAL EXAMINATION REVEALED ABOUT A 10" LONG X 0.25" CRACK IN THE GIRTH WELD ON THE BOTTOM OF THE PIPE. METALLURGICAL TESTING DETERMINED LACK OF FUSION IN THE GIRTH WELD DUE TO PIPE MISALIGNMENT DURING WELDING TO BE THE CAUSE OF THE CRACK.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140022 | 16616 | 2014-02-21 11:44 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2014-01-29 10:59 | 2014 |  |  | 31.5857 | -89.5424 | 1072401 | 2014-01-29 11:57 |  | NATURAL GAS |  | 20 | 25 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-01-29 12:07 | 2014-01-29 17:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 20 | 2014-01-29 10:59 | 2014-01-29 12:07 | ONSHORE | MS | 39044 | D'LO | SIMPSON | MILEPOST | 24.2 | HATTIESBURG 8" | INDEX 387 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | PIPING, REGULATORS & METER | 1947 |  | CARBON STEEL |  | OTHER | [8 empty] | THIRD PARTY DAMAGE BY VEHICLE | CLASS 1 LOCATION | NO |  | 71 |  | NO | NO | NO |  | 0 | 0 | 110 | 121.677102398613 | 88 | 58.7180385288967 | 74000 | 81855.5052499759 | 1500 | 1659.23321452654 | 0 | 0 |  |  | 75698 | 38452.1973020561 | 83695.13360543 | [8 empty] | 145 |  | 165 | 192.619(A)(4) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [260 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 270.688.6357 | 270.688.6948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 270.688.6361 | jeff.mcmaine@bwpmlp.com | LOCAL LAW ENFORCEMENT BELIEVES THAT AN SUV HIT ICE ON THE ROAD, RAN OFF THE ROAD, AND HIT THE REGULATOR STATION CAUSING DAMAGE TO THE FACILITY AND THE GAS IGNITED. 1-20-15 UPDATED COST TO SUBMIT FINAL REPORT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140023 | 16525 | 2014-02-25 15:01 | SUPPLEMENTAL FINAL | 31613 | ENBRIDGE PIPELINES (EAST TEXAS) L.P. | 1501 MCKINNEY SUITE 600 | HOUSTON | TX | 77010 | 2014-01-26 08:45 | 2014 |  |  | 30.6072 | -94.9397 | 1072170 | 2014-01-26 14:46 |  | NATURAL GAS |  | 78042 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | [7 empty] | NO |  |  |  |  | NO | [7 empty] | 2014-01-26 08:45 | 2014-01-26 09:35 | ONSHORE | TX | 77335 | GOODRICH | POLK |  |  | GOODRICH COMPRESSOR STATION | TXCG-36 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2008 |  | CARBON STEEL |  | OTHER | [8 empty] | STATION ESD DUE TO POWER OUTAGE. | CLASS 1 LOCATION | NO |  | 829 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 390210 | 260367.793345009 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 390210 | 269935.113835377 | 260367.793345009 | [8 empty] | 865 |  | 1050 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM INITIALLY DETECTED A PRESSURE DROP AND NOTIFIED OPERATIONS. OPERATIONS CONFIRMED THE INCIDENT AND INTERNAL COMMUNICATIONS VERIFIED THE ALARMS/ALERTS THE CONTROLLER EXPERIENCED. ONCE OPERATIONS SECURED THE STATION, THE CONTROL CENTER VERIFIED THE RETURN TO NORMAL OPERATING PRESSURE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | YES | [6 empty] | YES | [16 empty] | YES | [173 empty] | GREGG JOHNSON | INTEGRITY COMPLIANCE SUPERVISOR | gregg.johnson@enbridge.com | 713-353-6369 |  |  |  |  | GREGG JOHNSON | INTEGRITY COMPLIANCE SUPERVISOR | 713-353-6369 | gregg.johnson@enbridge.com | AT 8:45 THE CONTROL CENTER NOTIFIED OPERATIONS THAT A PRESSURE DROP WAS INDICATED ON THE DD AND CLARITY SYSTEM. OPERATIONS WAS DISPACHED AND ARRIVED AT THE GOODRICH COMPRESSOR STATION AT 09:15. OPERATIONS FOUND THE COMPRESSOR STATION HAD EXPERIENCED A POWER FAILURE CAUSING AN ESD OF THE STATION. A 20" SUCTION VALVE FAILED TO CLOSE DURING THE ESD ALLOWING ADDITIONAL GAS TO BE BLOWN DOWN. THE VALVE WAS MANUALLY SHUT AT 09:35 AND PRESSURE BEGAN TO INCREASE TO NORMAL OPERATING PRESSURE. REPORTED DUE TO UNINTENIONAL GAS LOSS EXCEEDING THE 3 MMCF LIMIT AND THE COST OF GAS LOSS EXCEEDING $50,000.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140024 | 16290 | 2014-02-27 08:31 | SUPPLEMENTAL FINAL | 12576 | ENABLE MISSISSIPPI RIVER TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2014-02-04 19:27 | 2014 |  |  | 38.1693 | -90.3221 | 1073027 | 2014-02-04 21:16 |  | NATURAL GAS |  | 3405 | 138 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | SMALL LEAK, SEVERVE WEATHER, KEEPING SERVICE TO CUSTOMERS | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-02-04 20:29 | 2014-02-04 20:29 | ONSHORE | MO | 63028 | FESTUS | JEFFERSON | MILEPOST | 248+19 | A-151 | A-151 STATION | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 4 |  | 0.235 | 24000 | UNKNOWN | OTHER | UNKNOWN | UNKNOWN | PAINT | [28 empty] | 1955 | 1955 | CARBON STEEL |  | LEAK |  |  | OTHER | BULLET HOLE, GUN SHOT | [5 empty] | CLASS 1 LOCATION | NO |  | 155 |  | NO | NO | NO |  | 1000 | 1106.15547635103 | 725 | 801.962720354494 | 17878 | 11929.1033274956 | 50000 | 55307.7738175513 | 13000 | 14380.0211925633 | 0 | 0 |  |  | 82603 | 45231.8564336266 | 83525.0165343158 | [8 empty] | 313 |  | 350 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY DAMAGED PIPELINE, SHOT BY UNKNOWN PARTY | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [103 empty] | INTENTIONAL DAMAGE | [7 empty] | VANDALISM | [253 empty] | JIMMY CROSS | COMPLIANCE COORDINATOR | jimmy.cross@enablemidstream.com | 3184293664 | 3184293927 |  |  |  | JOHNNY CAVITT | DOT COMPLIANCE MANAGER | 3184293606 | johnny.cavitt@enablemidstream.com | ABOVEGROUND PIPING INTENTIONALLY SHOT BY UNKNOWN PARTY. INSTALLED STOPPALL ON LINE AT 176+73 (7,146') UPSTREAM OF DAMAGED ABOVEGROUND PIPING. CUT AND CAPPED PIPELINE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140025 | 16434 | 2014-02-27 10:11 | SUPPLEMENTAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2014-02-12 12:10 | 2014 |  |  | 31.2978 | -92.3328 | 1073703 | 2014-02-12 12:50 |  | NATURAL GAS |  | 45600 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | COMPRESSOR STATION WAS ALREADY OFFLINE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-02-12 12:10 | 2014-02-12 12:35 | ONSHORE | LA | 71360 | PINEVILLE | RAPIDES | MILEPOST | 122.5044 | PINEVILLE COMPRESSOR STATION | BAE SYSTEM | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2012 |  | CARBON STEEL |  | OTHER | [8 empty] | ICE AFFECTED SENSORS TO ESD VALVE (RELIEF VALVE) CAUSING VALVE TO OPEN. | CLASS 2 LOCATION | NO |  | 200 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 253536 | 169172.007005254 | 0 | 0 | 1000 | 1106.15547635103 | 0 | 0 |  |  | 254536 | 175896.055777504 | 170278.162481605 | [8 empty] | 735 |  | 838 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | STATION WAS OFFLINE AND IN BYPASS MODE. WEATHER CONDITIONS CAUSED ICING WHICH AFFECTED SENSING DEVICES. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | NO | [306 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 270.688.6357 | 270.688.6948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 270.688.6361 | jeff.mcmaine@bwpmlp.com | FREEZING RAIN CONDITIONS CAUSED ICING ON THE POPPET BLOCK CAUSING THE VALVE TO OPEN. CORRECTED CAUSE SINCE DEVICE WAS A VALVE AND NOT A RELIEF VALVE. 2-28-14 CORRECTED CAUSE AS SUGGESTED BY PHMSA. 6-24-14
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140026 | 16377 | 2014-03-06 21:25 | SUPPLEMENTAL FINAL | 15105 | PANHANDLE EASTERN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2014-02-10 23:45 | 2014 |  |  | 39.7897 | -88.3581 | 1073610 | 2014-02-11 09:11 |  | NATURAL GAS |  | 11852 | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | [7 empty] | NO |  |  |  |  | NO | [7 empty] | 2014-02-10 23:50 | 2014-02-11 00:05 | ONSHORE | IL | 61953-7586 | TUSCOLA | DOUGLAS | MILEPOST | TUSCOLA STA. | TUSCOLA COMPRESSOR STSTION |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | ESD/RELIEF AUTOMATIC BLOWDOWN |  |  | CARBON STEEL |  | OTHER | [8 empty] | ORIFICE IN VALVE FROZE OFF, LETTING THE DOME PRESSURE BLEED OFF AND THE VALVE TO OPEN. | CLASS 1 LOCATION | NO |  | 745 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 45567 | 30404.6007005254 | 0 | 0 | 300 | 331.846642905308 | 0 | 0 |  |  | 45867 | 31674.1564880673 | 30736.4473434307 | [8 empty] | 803 |  | 900 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CAUSE WAS SUB ZERO TEMPERATURE WEATHER RELATED. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | YES |  |  |  | YES | SUB ZERO TEMPERATURES | [301 empty] | NATHAN HLAVATY | DIRECTOR REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 7138575479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR REGULATORY COMPLIANCE | 7138575479 | nathan.hlavaty@energytransfer.com | THIS SUPPLEMENTAL FINAL REPORT IS SUBMITTED TO CORRECT THE PART A 5. LOCATION OF INCIDENT: LATITUDE TO 39.7897 AND THE LONGITUDE TO -88.3581.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140027 | 16447 | 2014-03-12 06:22 | SUPPLEMENTAL FINAL | 2620 | COLUMBIA GULF TRANSMISSION CO | 700 LOUISIANA ST. SUITE 700 | HOUSTON | TX | 77002 | 2014-02-13 02:04 | 2014 |  |  | 37.2529 | -85.1953 | 1073825 | 2014-02-13 02:49 |  | NATURAL GAS |  | 26300 | 14900 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-02-13 02:11 |  | YES |  |  |  | YES |  |  |  |  | YES | [7 empty] | 2014-02-13 02:05 | 2014-02-13 03:45 | ONSHORE | KY | 42753 | KNIFLEY | ADAIR | SURVEY STATION NO. | 4164+02 | LINE 200 | VALVE 313 TO CLEMENTSVILLE CMP. STATION | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 104 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 30 |  | 0.323 | 65000 | API5L | DSAW |  | US STEEL CORP | OTHER | MODIFIED PRIMER & ENAMEL WITH FIBERGLASS AND KRAFT PAPER | [8 empty] | PIPE GIRTH WELD | [18 empty] | 1965 | 1965 | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | PIPE RUPTURE. APPROXIMATELY 80 FEET OF PIPE EXPELLED. | 960 | 30 |  | CLASS 2 LOCATION | NO |  | 657 |  | NO | YES | NO |  | 550000 | 608385.511993064 | 86204 | 95355.0266833638 | 152158 | 101527.492119089 | 492056 | 544290.43907138 | 39084 | 43232.9806377035 | 480511 | 531519.874096908 | INCIDENT INVESTIGATION |  | 1800013 | 941964.037722324 | 1924311.32460151 | [8 empty] | 964 |  | 1008 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 73550 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 2 | 0 | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [52 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | OTHER |  |  |  | ROOT CAUSE FAILURE ANALYSIS INCLUDING GEOTECHNICAL SURVEY INDICATES MOST LIKELY CAUSE OF FAILURE WAS EXTERNAL LOADING ACTING ON THE PIPE AND LAND MOVEMENT WAS THE PROBABLE CAUSE OF THE EXTERNAL LOADING LEADING TO THE INCIDENT. | NO | [306 empty] | GREGORY LAGO | PRINCIPAL ENGINEER | glago@nisource.com | (304) 357-2465 | (304) 357-3804 |  |  |  | PERRY M. HOFFMAN | MANAGER OF SYSTEM INTEGRITY | (304) 357-2548 | mikehoffman@nisource.com | ROOT CAUSE FAILURE ANALYSIS SUBMITTED TO PHMSA SOUTHERN REGIONAL OFFICE ON 5/9/2014. ALL TIMES SHOWN IN EASTERN STANDARD TIME.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140028 | 16533 | 2014-03-12 15:00 | SUPPLEMENTAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2014-02-13 04:40 | 2014 |  |  | 33.4215 | -91.0231 | 1073885 | 2014-02-13 13:17 |  | NATURAL GAS |  | 3501 | 4378 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-02-13 09:29 | 2014-08-08 10:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-02-13 04:40 | 2014-02-13 05:30 | ONSHORE | MS | 38704 | GREENVILLE | WASHINGTON | MILEPOST | 79.57 | EIS SYSTEM | EIS 18-2 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 18 |  | 0.25 | 35000 | API-5L | OTHER | ERW DIRECT CURRENT | YOUNGSTOWN | COAL TAR | [28 empty] | 1940 | 1940 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 290 |  | NO | NO | NO |  | 0 | 0 | 44224 | 48918.6197861478 | 30185 | 20140.9544658494 | 46000 | 50883.1519121472 | 1000 | 1106.15547635103 | 0 | 0 |  |  | 121409 | 67200.4432452796 | 121048.881640495 | [8 empty] | 518 |  | 545 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 65803 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS NOT OF A MAGNITUDE THAT WOULD HAVE BEEN IDENTIFIED ON SCADA | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES |  |  |  |  | YES | OTHER | FATIGUE IN A WRINKLE BEND, LOCATED IN A FARM FIELD | [19 empty] | YES | [59 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 270.688.6357 | 270.688.6948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 270.688.6361 | jeff.mcmaine@bwpmlp.com | LEAK RESULTED FROM A CRACK IN A WRINKLE BEND. CAUSE IS STILL UNDER INVESTIGATION. THE REPAIR WAS COMPLETED ON FEBRUARY 14, 2014 BUT THE LINE HAS NOT BEEN RETURNED TO SERVICE DUE TO OTHER PLANNED WORK. 11-10-14 UPDATED FOR FINAL REPORT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140029 | 17085 | 2014-03-15 09:08 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | ONE ENERGY PLAZA | DETROIT | MI | 48226 | 2014-02-13 23:48 | 2014 |  |  | 44.7719 | -84.8503 | 1073944 | 2014-02-14 02:42 |  | NATURAL GAS |  | 15400 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-02-14 01:25 | 2014-02-14 02:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-02-13 23:48 | 2014-02-14 01:25 | ONSHORE | MI | 49733 | FREDERIC | KALKASKA | MILEPOST | GOOSE CREEK | GOOSE CREEK COMPRESSOR STATION | GOOSE CREEK COMPRESSOR STATION BYPASS | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | TUBING | [38 empty] | 1999 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL | OTHER | [8 empty] | THE PILOT SENSING TUBING FROZE SHUT CAUSING THE AXELSON 3"X4"RELIEF VALVE TO OPEN AND RELEASE GAS TO ATMOSPHERE | CLASS 1 LOCATION | NO |  | 84 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 71333 | 47596.9754816112 | 378 | 418.126770060688 | 504 | 557.502360080917 | 0 | 0 |  |  | 72215 | 49793.7852237796 | 48572.6046117528 | [8 empty] | 879 |  | 1200 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS CONTROLLER WAS CONTACTED BY AN OPERATOR EMPLOYEE PRIOR TO A SCADA LOW ALARM SET POINT. GAS CONTROLLER DISPATCHED A TECHNICIAN TO THE SITE AND FOLLOWED PROCEDURES. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | YES |  |  |  | YES | SEVERE COLD WEATHER OVER EXTENDED PERIOD OF TIME. | [301 empty] | ROBERT FRECKELTON | MANAGER - CODES AND STANDARDS | freckeltonr@dteenergy.com | 313-389-7755 | 313-389-7757 |  |  |  | JOHN D LUEDERS | COMPLIANCE ENGINEER - CODES AND STANDARDS | 616.632.2646 | luedersj@dteenergy.com | AT 00:13 ON FEBRUARY 14, 2014, A DTE KALKASKA COMPRESSOR OPERATOR NOTIFIED DTE GAS CONTROL OF A PRESSURE DROP OF 25 PSIG IN AN HOUR ON THE KALKASKA ANTRIM 20" PIPELINE AT THE GOOSE CREEK COMPRESSOR STATION. AT 00:30, THE KALKASKA COMPRESSOR OPERATOR CONTACTED GAS CONTROL AND DISPATCHED A TRANSMISSION TECHNICIAN TO THE GOOSE CREEK COMPRESSOR STATION. AT 00:45 DTE GAS CONTROL RECEIVED A CALL FROM A GREAT LAKES GAS CONTROLLER STATING THAT THEY HAD RECEIVED A 911 CALL FROM THE KALKASKA FIRE DEPARTMENT OF GAS BLOWING AT A STATION ON COUNTY ROAD 612. AT 01:25, THE DTE TECHNICIAN ARRIVED AND DETERMINED THE PILOT SENSING LINE TO THE 3"X 4" AXELSON RELIEF VALVE WAS FROZEN SHUT CAUSING THE RELIEF VALVE TO OPEN AS DESIGNED. THE TECHNICIAN CLOSED VALVE #GC1 AND VALVE #GC2 TO ISOLATE THE STATION FROM THE KALKASKA ANTRIM 20" PIPELINE. THE TECHNICIAN THEN CLOSED THE RELIEF VALVE TO ELIMINATE THE GAS RELEASE. AT 01:45 THE TECHNICIAN OPENED BYPASS VALVE #GC3 AND GAS FLOW WAS RESTORED TO GREAT LAKES AND CMS ENERGY AT APPROXIMATELY 02:00.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140030 | 16401 | 2014-03-17 17:09 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2014-02-18 16:30 | 2014 |  |  | 28.9783 | -91.8558 | 1074396 | 2014-02-18 18:00 |  | NATURAL GAS |  | 2500 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | LEAK WAS MONITORED UNTIL DIVERS COULD CLOSE VALVES TO BEGIN VENTING | [6 empty] | NO |  |  |  |  | NO | [7 empty] | 2014-02-18 16:30 | 2014-02-19 12:00 | OFFSHORE | [28 empty] | 75 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SOUTH MARSH ISLAND | 287 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2012 |  | CARBON STEEL |  | LEAK |  |  | OTHER | GREASE FITTING ON AUXILIARY VA | [5 empty] | CLASS 1 LOCATION | NO |  | 312 |  | NO | NO | NO |  | 0 | 0 | 25000 | 27653.8869087757 | 25000 | 16681.2609457093 | 100000 | 110615.547635103 | 20000 | 22123.1095270205 | 0 | 0 |  |  | 170000 | 90918.6306452699 | 177073.805016608 | [8 empty] | 849 |  | 1300 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 20000 | NO | YES | YES | [5 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS EVENT WAS DUE TO PIPELINE COMPONENTS OR EQUIPMENT AND NOT ATTRIBUTABLE TO CONTROL ROOM ISSUES. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | THREADED FITTING | [19 empty] | YES | GREASE FITTING ON AUXILIARY SUB-SEA VALVE BEGAN LEAKING. | [161 empty] | LOUIS SALINAS | ENGINEER | louis_salinas@transcanada.com | 832-320-5305 | 832-320-6305 |  |  |  | LOUIS SALINAS |  | 832-320-5305 | No Email Address | A LEAK WAS DISCOVERED AT SOUTH MARSH ISLAND BLOCK 287 AS WORK WAS BEGINNING ON THE REPAIR OF A LEAK AT EUGENE ISLAND BLOCK 115. THE LEAK WAS APPARENTLY FOUND NEAR A SUB-SEA AUXILIARY VALVE ON ANR LINE 747. IT WAS TRACED BY A DIVING CREW TO A GREASE FITTING ON THE VALVE. FOLLOWING THE INVESTIGATION, THE REPAIR OF THE VALVE ASSEMBLY WAS PLANNED; THE DE-PRESSURIZATION OF THE PIPELINE WAS CONDUCTED BY VENTING THE GAS FROM THE SMI BLOCK 10 PLATFORM. THE VENTING BEGAN WITH 849 PSIG. ONCE THE PRESSURE ON THE LINE REACHED 23 PSIG., THE LEAKING FITTING ON THE VALVE WAS REPLACED. THE REPAIR WAS COMPLETED ON 2-22-14.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140031 | 16713 | 2014-03-25 11:00 | SUPPLEMENTAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2014-03-02 23:21 | 2014 |  |  | 34.9011 | -90.1663 | 1075572 | 2014-03-03 00:13 |  | NATURAL GAS |  | 48864 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE STATION CONTINUED TO OPERATE NORMALLY | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-03-02 23:21 | 2014-03-03 00:10 | ONSHORE | MS | 38641 | LAKE CORMORANT | DESOTO | MILEPOST | 229.8752 | MAIN LINE SYSTEM | LAKE CORMORANT COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1950 |  | CARBON STEEL |  | OTHER | [8 empty] | ESD VALVE OPENED DUE TO FREEZING WEATHER CONDITIONS. | CLASS 1 LOCATION | YES | METHOD2 | 200 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 237479 | 158457.966725044 | 0 | 0 | 500 | 553.077738175513 | 0 | 0 |  |  | 237979 | 164534.446452675 | 159011.044463219 | [8 empty] | 830 |  | 840 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | NO | [306 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlpl.com | 270.688.6357 | 270.688.6948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 270.688.6361 | jeff.mcmaine@bwpmlp.com | FREEZING WEATHER CAUSED THE VENT ON THE CONTROL PILOT TO FREEZE WHICH CAUSED THE VALVE TO OPERATE WHEN THE PRESSURE EQUALIZED WITH THE STATION DISCHARGE PRESSURE. 3-27-14 CORRECTED LAT/LONG COORDINATES 4-7-15 CORRECTED PART A, QUESTION 19A TIME TO REFLECT TIME BASED ON 24 HOUR CLOCK (CHANGED FROM 11:21 TO 23:21).
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140032 | 16468 | 2014-03-28 11:24 | SUPPLEMENTAL FINAL | 22655 | WBI ENERGY TRANSMISSION, INC. | 1250 WEST CENTURY AVENUE | BISMARCK | ND | 58503 | 2014-02-28 09:40 | 2014 |  |  | 44.9919 | -108.8671 | 1075387 | 2014-02-28 11:20 |  | NATURAL GAS |  | 224 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE DAMAGED FACILITY WAS SAFETLY ISOLATED WITHOUT SHUTTING DOWN THE STATION. | [6 empty] | YES |  |  |  |  | YES | [6 empty] | 0 | 2014-02-28 09:40 | 2014-02-28 09:40 | ONSHORE | WY | 82435-1164 | POWELL | PARK | SURVEY STATION NO. | 0+00 | ELK BASIN COMPRESSOR STATION | GAS FIRED HEATER | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2012 |  | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 11 | 4 |  | CLASS 1 LOCATION | NO |  | 161 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 1231 | 821.385288966725 | 521243 | 576575.798959638 | 900 | 995.539928715923 | 0 | 0 |  |  | 523374 | 265972.052253621 | 578392.72417732 | [8 empty] | 594 |  | 1137 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 3 | 0 | NO |  |  | EQUIPMENT FAILURE | FAILURE OF EQUIPMENT BODY (EXCEPT COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL | MATERIAL/WELD/EQUIP FAILURE | FAILURE OF EQUIPMENT BODY | [166 empty] | FAILURE OF EQUIPMENT BODY (EXCEPT COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL | [35 empty] | YES | SEE PART H, NARRATIVE DESCRIPTION. | [161 empty] | KENT KAHL | DOT COMPLIANCE SUPERVISOR | kent.kahl@wbienergy.com | 406-359-7222 | 406-359-7244 |  |  |  | KENT KAHL | DOT COMPLIANCE SUPERVISOR | 406-359-7222 | kent.kahl@wbienergy.com | ***SUPPLEMENTAL REPORT*** UNIFIED INVESTIGATIONS & SCIENCES, INC. (UIS) WAS CONTRACTED TO DIRECT AND COMPLETE AN INVESTIGATION ON THE GAS FIRED HEATER INCIDENT THAT OCCURRED ON 2/28/14. UIS COORDINATED THE REMOVAL OF THE FAILED SECTION OF PIPING FROM THE GAS FIRED HEATER ON 4/1/14. AN INTACT EXEMPLAR PIPE SECTION FROM A LOWER ELEVATION WITHIN THE GAS FIRED HEATER WAS ALSO REMOVED AT THE SAME TIME TO BE ANALYZED WITH THE FAILED SECTION. THE SAMPLES WERE SENT TO FORENSIC CONSULTANTS GROUP, LLC (FCG) IN DENVER, CO TO EVALUATE THE FAILED PIPE SECTION AND TO DETERMINE WHETHER OR NOT MATERIAL SELECTION, PRE-EXISTING DAMAGE, USER ERROR, OPERATING CONDITIONS, AND/OR DESIGN/MANUFACTURING DEFECTS CAUSED OR CONTRIBUTED TO THE OBSERVED FAILURE. FCG FINDING: - THE "FISHMOUTH" TYPE RUPTURE IN THE SPOOL PIECE SHOWED EXTENSIVE DEFORMATION AND THINNING TYPICAL OF A RELATIVELY SHORT-TERM OVERHEAT FAILURE. - EXTENSIVE SECONDARY CRACKING WAS NOTED IN BOTH THE CIRCUMFERENTIAL WELDS ON EITHER SIDE OF THE SPOOL PIECE AND IN THE SPOOL PIECE MATERIAL ITSELF. THE PRESENCE OF THE EXTENSIVE SECONDARY CRACKING ALONG WITH THE CRACKING THAT LED TO THE FAILURE SHOWS THAT THE FAILURE WAS DUE TO A UNIFORM CONDITION IN THE PIPING SUCH AS EXCESSIVE TEMPERATURE, PRESSURE, OR INADEQUATE WALL THICKNESS RATHER THAN AN ISOLATED DEFECT. - THE ULTIMATE FAILURE OF THE SPOOL PIECE WAS CAUSED BY ELEVATED-TEMPERATURE THINNING OF THE TUBE WALL AND THE INITIATION AND GROWTH OF CREEP CRACKS TO THE POINT WHERE THE REMAINING CROSS SECTION COULD NO LONGER SUPPORT THE INTERNAL GAS PRESSURE. - THE RESULTS OF THE OPTICAL EMISSION SPECTROSCOPY (OES) OF THE MATERIAL SHOWED THAT THE CHEMICAL COMPOSITION WAS WITHIN THE REQUIREMENTS FOR THE SA106 GRADE B MATERIAL. - THE RESULTS OF THE TENSILE TESTS INDICATE THAT THE SPOOL PIECE AND THE ADJACENT PIPING MATERIAL MET THE MECHANICAL PROPERTY REQUIREMENTS OF SA106 GRADE B MATERIAL. WBI HAS ANALYZED THE FINDINGS IN THE FCG REPORT AND HAVE INITIATED TAKING SEVERAL STEPS TO PREVENT THIS INCIDENT FROM HAPPENING AGAIN ON THE REPLACEMENT UNIT AND ON EXISTING UNITS. DURING THE INSTALLATION OF THE NEW GAS FIRED HEATER, WBI WILL REQUIRE THE MANUFACTURE OF THE GAS FIRED HEATER TO BE ONSITE FOR THE STARTUP/COMMISSIONING AND VERIFICATION OF ALL LOGIC, SYSTEM INTERLOCKS, AND SHUTDOWNS. ADDITIONAL SHUTDOWNS WILL BE ADDED TO THE LOGIC INCLUDING A SHUTDOWN REQUIRING THE REGEN COMPRESSOR TO BE IN A RUN STATE FOR THE GAS FIRED HEATER TO BE IN OPERATION AND A SECONDARY DIFFERENTIAL PRESSURE SHUTDOWN DEVICE WILL BE ADDED TO MEASURE FLOW GOING INTO THE GAS FIRED HEATER AND SHUTDOWN ON LOW FLOW CONDITIONS. IN ADDITION TO THE STEPS WBI WILL TAKE ON THE REPLACEMENT GAS FIRED HEATER UNIT, WBI WILL ALSO TAKE ADDITIONAL STEPS WITH OUR EXISTING UNITS TO CONFIRM THEY ARE IN SATISFACTORY OPERATIONAL CONDITION. PRIOR TO THE END OF 2014 WBI WILL: - DEVELOP A PLAN TO VERIFY THE INTEGRITY OF THE TUBING BUNDLES TO IDENTIFY AREAS OF TUBE SWELLING AND CRACKING AND FULLY IMPLEMENT THIS PLAN WITHIN 12 MONTHS, - ESTABLISH CRITERIA AND VERIFY THAT SYSTEM SHUTDOWNS OCCUR QUICKLY ENOUGH TO PREVENT ANY DAMAGE FROM OCCURRING IN THE CASE OF A UNIT MALFUNCTION, AND - INSPECT AND CALIBRATE ALL GAS FIRED HEATER EQUIPMENT. WBI WILL STANDARDIZE THE INSPECTION AND CALIBRATION FORM AND REQUIRE THAT ALL STATIONS INSPECT AND CALIBRATE ALL GAS FIRED HEATER EQUIPMENT ANNUALLY; AND WBI WILL IMPLEMENT THE DEVELOPED INSPECTION PLAN OF THE TUBING BUNDLES TO BE DONE EVERY THREE YEARS. WBI FEELS IMPLEMENTING THE ABOVE DESCRIBED PROCESSES IS A PRUDENT APPROACH TO MITIGATING SAFETY CONCERNS ASSOCIATED WITH THIS INCIDENT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140033 | 16415 | 2014-03-28 16:13 | SUPPLEMENTAL FINAL | 3 | ACADIAN GAS PIPELINE SYSTEM | 1100 LOUISIANA ST. | HOUSTON | TX | 77002 | 2014-02-27 09:25 | 2014 |  |  | 30.0198 | -91.1379 | 1075268 | 2014-02-27 11:12 |  | NATURAL GAS |  | 0 | 5335 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELIEF VALVE RELIEVED TO ATMOSPHERE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-02-27 09:25 | 2014-02-27 09:25 | ONSHORE | LA | 70341 | GRAND BAYOU | ASSUMPTION PARISH | MILEPOST | 2436+21 | CHICO B | 307-0100 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | RELIEF VALVE |  |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE OPENED TO ATMOSPHERE. | CLASS 1 LOCATION | NO |  | 430 |  | NO | NO | NO |  | 0 | 0 | 29769 | 32929.1423754937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 29769 | 15115.3452461227 | 32929.1423754937 | [8 empty] | 902 |  | 909 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) | [6 empty] | YES | [6 empty] | YES | 1 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | CONTROLLER FAILING TO RESPOND TO HIGH PRESSURE ALARM. |  |  | YES |  |  | NORMAL OPERATING CONDITIONS | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | NATHAN L. GRAY JR. | SENIOR PIPELINE COMPLIANCE SPECIALIST | ngray@eprod.com | 9854934629 |  |  |  |  | NATHAN L. GRAY JR. | SENIOR PIPELINE COMPLIANCE SPECIALIST | 9854934629 | ngray@eprod.com | THE 6 INCH CHICO B PIPELINE RELIEF VALVE OPENED TO ATMOSPHERE DUE TO THE CONTROLLER FAILING TO RESPOND TO HIGH PRESSURE ALARM. PIPELINE CONTROL FOLLOWED ESTABLISHED PROCEDURES TO EVALUATE THE CONTROLLER RESPONSE; THE CONTROLLER WAS RE-TRAINED AND RE-QUALIFIED TO PREVENT REOCCURRENCE. THE RELIEF VALVE FUNCTIONED PROPERLY OF WHICH RESULTED IN THE INTENTIONAL RELEASE TO THE ATMOSPHERE. PURSUANT TO OPERATOR JUDGMENT THAT IT WAS A SIGNIFICANT EVENT DUE TO THE SENSITIVITY OF THE CIRCUMSTANCE WHERE INCIDENT OCCURRED, THE NRC WAS NOTIFIED BASED ON THE INFORMATION AVAILABLE AT THE TIME.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140034 | 16846 | 2014-03-29 23:00 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | ONE ENERGY PLAZA | DETROIT | MI | 48226 | 2014-02-27 03:30 | 2014 |  |  | 42.8515 | -82.6757 | 1075691 | 2014-03-04 11:01 |  | NATURAL GAS |  | 171.8 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-02-27 07:30 | 2014-03-10 11:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2014-02-27 02:57 | 2014-02-27 02:57 | ONSHORE | MI | 48062 | RICHMOND | ST. CLAIR | MILEPOST | PROP ID #6328 | COLUMBUS COMPRESSOR STATION | DEHYDRATION PLANT | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | DEHYDRATOR/DRIER/TREATER/SCRUBBER | [38 empty] | 1998 |  | CARBON STEEL |  | OTHER | [8 empty] | CHECK VALVE DID NOT HOLD DUE TO SALT AND OTHER MATERIALS; | CLASS 1 LOCATION | NO |  | 5 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 794 | 529.796847635727 | 66805 | 73896.7165976303 | 6624 | 7327.1738753492 | 0 | 0 |  |  | 74223 | 37833.1734166438 | 81753.6873206152 | [8 empty] | 5 |  | 1440 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS CONTROLLER WAS CONTACTED BY OPERATOR PRIOR TO ANY ALERT FROM SCADA SYSTEM. GAS CONTROLLER FOLLOWED ALL APPLICABLE PROCEDURES. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | YES |  |  |  | YES | [14 empty] | YES | [9 empty] | YES | YES | [166 empty] | ROBERT FRECKELTON | MANAGER | freckeltonr@dteenergy.com | 313-389-7755 | 313-389-7757 |  |  |  | ROBERT FRECKELTON | MANAGER | 313-389-7755 | freckeltonr@dteenergy.com | ON FEBRUARY 27, 2014, AT 01:30 A DTE GAS OPERATOR AT BELLE RIVER MILLS (BRM) COMPRESSOR STATION RECEIVED A HIGH DIFFERENTIAL PRESSURE ALARM FOR THE PARTICULATE FILTERS ON THE GLYCOL REGENERATION SKID AND A PLANT SHUTDOWN INDICATION AT THE REMOTE COLUMBUS DEHYDRATION PLANT. AT 02:00, THE BRM OPERATOR DIRECTED A TRANSMISSION TECH TO REPORT TO COLUMBUS COMPRESSOR STATION(CCS)TO INVESTIGATE AND CORRECT THE CAUSE OF THE SHUTDOWN, AND THE HIGH DIFFERENTIAL FOR THE PARTICULATE FILTERS. TECH ARRIVED AT THE CCS AT 02:45. TECH DETERMINED THE PARTICULATE FILTERS ON THE GLYCOL SKID AT THE DEHYDRATION PLANT WERE PLUGGED (CAUSE NOT CLEAR AT THE TIME BUT ASSUMED TO BE BY SALT) CAUSING THE INCREASE IN PRESSURE DIFFERENTIAL. TECH NOTICED THAT THE LOCAL CONTROL PANEL INDICATED THE CAUSE OF PLANT SHUTDOWN TO BE HIGH LIQUID LEVEL IN THE FLASH TANK. TECH DRAINED THE CAGE FOR THE FLASH TANK LEVEL SWITCH TO RESET THE SWITCH AND THIS CAUSED THE PUMPS TO RESTART AUTOMATICALLY IN ACCORDANCE WITH THE CONTROL LOGIC FOR THE PLANT. TECH PROCEEDED IN ACCORDANCE WITH NORMAL PROCEDURE TO BYPASS AND DRAIN THE FILTER CASING TO REMOVE AND REPLACE THE FILTER ELEMENTS. WHILE CHANGING THE FILTERS, TECH HEARD THE LIQUID LEVEL CONTROL VALVE ON CONTACTOR A GO WIDE OPEN. TECH OBSERVED A HIGH LEVEL OF GLYCOL IN THE CONTACTOR SIGHT GLASS. TO SHUT OFF THE FLOW OF GLYCOL TO CONTACTOR A, THE TECH OPENED THE PUMP BYPASS VALVE. THE PUMPS STARTED CAVITATING, SO THE TECH OPENED ALL PUMP BYPASS VALVES WHICH IS STANDARD PROCEDURE WHEN PUMP CAVITATION OCCURS. THE TECH OBSERVED THE LEVEL OF GLYCOL IN THE REBOILER WAS HIGH. AT THIS SAME INSTANT, THE TECH OBSERVED THE EMISSION CONTROL SYSTEM (ECS) FLARE STACK IGNITE WITH A LARGE FLAME. TECH ATTEMPTED TO OPEN THE REBOILER DRAIN VALVE TO DRAIN GLYCOL FROM THE REBOILER TO THE SURGE TANK AND STABILIZE LEVELS IN THE SYSTEM.TECH THEN HEARD THE CREAKING NOISE OF WHAT APPEARED TO BE EXPANDING PIPE AND IMMEDIATELY EVACUATED THE BUILDING. TECH CONTACTED THE BRM OPERATORS TO INFORM THEM OF THE FIRE AND TO DISCONTINUE FLOW THROUGH THE CCS. AFTER THE TECH LEFT THE BUILDING THE SIGHT GLASS ON THE REBOILER BROKE SPILLING 1200 GALLONS OF GLYCOL IN THE BUILDING. TECH DID NOT ACTIVATE THE MANUAL PULL STATION FOR THE SAFETY SHUTDOWN SYSTEM (SSD) FOR THE DEHYDRATION PLANT SINCE THE GAS RELIEF STACKS WERE IN CLOSE PROXIMITY TO THE FIRE IN THE ECS FLARE STACK. INSTEAD,THE TECH MANUALLY OPENED THE CONTACTOR BLOW-DOWN VALVES TO EVACUATE GAS FROM THE PLANT BUILDING AND DIRECT THE GAS TO THE BLOW-DOWN SILENCER AT A SAFE DISTANCE FROM THE FIRE. THE BLOW-DOWN OF CONTACTOR A AND THE COMPRESSOR FUEL GAS SYSTEM WAS FOLLOWED BY THE BLOW-DOWN OF CONTACTOR B AT APPROXIMATELY 04:00. ADDITIONAL TECHNICIANS ARRIVED AT THE CCS AT APPROXIMATELY 04:00 AND 04:30. SUPERVISOR ARRIVED AT 05:30. TEAM ATTEMPTED TO USE THE 150# FIRE EXTINGUISHER TO QUENCH THE FIRE ON TOP OF THE FLARE STACK WITHOUT SUCCESS. THE FIRE IN THE ECS FLARE STAKE CONTINUED TO BURN, AND THE TECHS OBSERVED RED LIGHT FOR LEL ALARM AND REALIZED THE CONCENTRATION OF GAS WAS BUILDING UP INSIDE THE DEHYDRATION BUILDING. THE TECHS AND THE SUPERVISOR WERE UNABLE TO DETERMINE THE SOURCE OF THE LEAKING GAS INSIDE THE BUILDING SINCE THE BUILDING WAS FILLED WITH STEAM FROM THE SPILLED GLYCOL. ONCE THE GLYCOL COOLED, THE TECHS ENTERED THE BUILDING AND OBSERVED GAS WAS LEAKING AT THE BROKEN SIGHT GLASS ON THE REBOILER. INITIALLY THE TECHS AND SUPERVISOR BELIEVED THAT THE SOURCE OF FUEL TO THE ECS WAS GLYCOL AND HYDROCARBON AND NOT NATURAL GAS. THE TEAM FOUND OUT IT WAS NATURAL GAS THAT WAS FEEDING THE FIRE WHEN THEY TURNED OFF THE VALVES TO THE SIGHT GLASS ON THE REBOILER AND THE FLAME OUTSIDE ON THE OUTSIDE ON THE ECS FLARE INCREASED. UPON OPENING THE VALVES THE ECS FLAME DECREASED. THE TEAM THEN DETERMINED THE GAS WAS COMING THROUGH THE CHECK VALVES FROM THE CONTACTORS AND PUMPS OUT TO THE ECS.THEY SHUT THE MANUAL VALVES DOWNSTREAM OF THE CHECK VALVES AT CONTACTORS A&B AND THE FLAME TO THE ECS EXTINGUISHED AT 07:30.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140035 | 16589 | 2014-03-31 14:08 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2014-03-10 13:00 | 2014 |  |  | 40.8083 | -74.0622 | 1076265 | 2014-03-10 15:40 |  | NATURAL GAS |  | 423 | 1246 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-03-10 16:31 | 2014-03-13 11:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-03-10 13:00 | 2014-03-10 13:08 | ONSHORE | NJ | 07073 | EAST RUTHERFORD | BERGEN | MILEPOST | 1824.9 | EAST RUTHERFORD METER STATION | MAINLINE A STATION PIPING | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 25 |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 30 |  | 0.375 | 52000 | API 5L | DSAW |  | KAISER | ASPHALT | [28 empty] | 1950 | 1950 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 523 |  | NO | NO | NO |  | 0 | 0 | 5582 | 6174.55986899143 | 1895 | 1264.43957968476 | 200000 | 221231.095270205 | 0 | 0 | 0 | 0 |  |  | 207477 | 105696.098150315 | 228670.094718881 | [8 empty] | 587 |  | 638 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS TOO SMALL TO BE FOUND REMOTELY | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES | [7 empty] | YES | HIC CAUSED BY FIELD WELDING PROCEDURES. | [12 empty] | YES | [63 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | JOHNNY LOPEZ | SAFETY REGULATORY COMPLIANCE SPECIALIST | johnny.lopez@williams.com | 713.215.2995 | 713.215.2222 |  |  |  | MARIE SOTAK | MANAGER SAFETY REGULATORY COMPLIANCE | 713.215.2111 | marie.sotak@williams.com | MEASUREMENT PERSONEL DETECTED A STRONG GAS ODOR WHILE AT THE EAST RUTHERFORD M&R ON 3/10/2014. IT WAS DETERMINED THAT THE LEAK WAS COMING FROM BELOW GROUND NEAR A MAIN LINE "A" TAP VALVE FEED FOR THE M&R STATION. MANAGEMENT WAS NOTIFIED AND BEGAN THE INVESTIGATION. SOIL WAS REMOVED FROM THE LEAK AREA AND A GAS DETECTOR WAS USED TO DETERMINE THAT A LEAK WAS INFACT PRESENT. THE LINE WAS DRAWN DOWN TO 150 PSIG THROUGH THE EAST RUTHERFORD M&R AND THEN BLOWN DOWN TO 0 PSIG . A CONTRACTOR WAS BROUGHT IN TO FULLY EXCAVATE AND MAKE THE NECESSARY REPAIRS (LEAKING PIPE SECTION WAS CUT-OUT AND REPLACED WITH NEW PIPE). IT WAS DETERMINED THAT A CRACK HAD FORMED ON THE MAIN LINE PIPE IN THE AREA WHERE THE HOT TAP NIPPLE WAS ATTACHED TO THE MAIN LINE PIPING. ONCE THE REPAIR WAS COMPLETE, THE LINE WAS PURGED OF AIR, PACKED TO LINE PRESSURE AND RETURNED TO SERVICE ON 3/13/2014. FINAL LEAK (METALLLURGICAL) EVALUATION - THE TOE CRACK OBSERVED IN THE MAIN LINE PIPE WAS DETERMINED TO BE A HYDROGEN INDUCED CRACK, OR COLD CRACK.THE HYDROGEN WOULD HAVE BEEN INTRODUCED DURING THE WELDING PROCESS, ALTHOUGH LOW-HYDROGEN ELECTRODES CAN HELP REDUCE THE POTENTIAL FOR HYDROGEN ENTRAPMENT. HARDENED MICROSTRUCTURES IN THE HEAT-AFFECTED ZONE OF A WELD CAN BE PRODUCED BY EXCESSIVE COOLING RATES AND THE ABSENCE OF EFFECTIVE PRE- AND POST-HEAT WELD PROCEDURES. THE AMOUNT OF PRE- AND POST-HEAT DEPENDS ON MULTIPLE FACTORS, INCLUDING BUT NOT LIMITED TO, THE WALL THICKNESS AND THE CARBON EQUIVALENT OF THE PIPE. RESIDUAL STRESSES CAUSED BY RESTRAINT INDUCED DURING WELDING ARE ALSO A CONTRIBUTING FACTOR TO HYDROGEN CRACKING.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140036 | 16405 | 2014-04-10 20:41 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2014-03-14 09:01 | 2014 |  |  | 37.4933 | -122.2364 | 1076668 | 2014-03-14 09:40 |  | NATURAL GAS |  | 20 | 650 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-03-14 10:40 | 2014-03-14 13:33 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-03-13 13:38 | 2014-03-13 13:38 | ONSHORE | CA | 94063 | REDWOOD CITY | SAN MATEO COUNTY | MILEPOST | MP 20.19 | L101 | 142 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND |  |  | 138 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | HOT TAP EQUIPMENT | [38 empty] | 2014 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | YES | METHOD2 | 316 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80000 | 88492.4381080821 | 0 | 0 |  |  | 80000 | 40620.3641267701 | 88492.4381080821 | [8 empty] | 311 |  | 365 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | REMOTELY CONTROLLED | 11141 | NO | YES |  |  | YES |  | YES | RECEIVER STILL UNDER CONSTRUCTION | YES |  | YES | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONSTRUCTION ISSUE, NOT OPERATIONS ISSUE. | [12 empty] | NO |  |  | YES | 2 | 0 | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | [204 empty] | EQUIPMENT NOT INSTALLED PROPERLY | [5 empty] | YES |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | LAWRENCE KANG | COMPLIANCE ANALYST | lxkw@pge.com | 925-328-5760 |  |  |  |  | LAURENCE DENISTON | INTERIM MANAGER | 9253285756 | lcd1@pge.com | ON MARCH 13, 2014, AT APPROXIMATELY 1330 HOURS, A PACIFIC GAS AND ELECTRIC (PG&E) CONTRACTOR INSTALLING A COMPLETION PLUG ON A 2-INCH DIAMETER SAVE-A-VALVE NIPPLE OBSERVED A SMALL-VOLUME LEAK. THE NIPPLE HAD BEEN WELDED ONTO PG&E'S NATURAL GAS TRANSMISSION LINE L-101 IN REDWOOD CITY NEAR 640 WHIPPLE AVENUE AS PART OF WORK TO FACILITATE THE UPGRADE OF L-101 FOR PIGGING. ATTEMPTS TO PROPERLY SEAT THE COMPLETION PLUG AND STOP THE LEAKAGE FAILED. THE PG&E PIPELINE ENGINEER WAS MADE AWARE OF THE SITUATION AND BEGAN MAKING PLANS TO INITIATE THE SHUTDOWN OF L-101 AND SAFELY MAKE REPAIRS TO THE SAVE-A-VALVE NIPPLE. MEDIA ARRIVED ON-SCENE AT APPROXIMATELY 0244 HOURS ON MARCH 14, 2014. AT 0828 HOURS ON MARCH 14, 2014, PG&E DETERMINED THAT THE CRITERIA FOR REPORTING THIS INCIDENT TO THE CPUC HAD BEEN REACHED, AND THE CPUC WAS NOTIFIED. AT 0901 HOURS, THE COST TO MAKE REPAIRS WAS ESTIMATED TO EXCEED $50,000, AND THE DOT WAS NOTIFIED (NRC# 1076668) TELEPHONICALLY AT 0940 HOURS. DUE TO THE HEIGHTENED SENSITIVITY OF PIPELINE WORK ALONG THE PENINSULA, AND PRIOR TO STARTING WORK, PG&E HAD NOTIFIED MEDIA OUTLETS OF THE PLANNED WORK ON L-101. WHEN THE MEDIA ARRIVED AT 0244 HOURS ON MARCH 14, PG&E'S FIELD PERSONNEL DID NOT MAKE THE IMMEDIATE CONNECTION THAT THE MEDIA PRESENCE WAS RELATED TO THE RELEASE OF GAS THAT STARTED AT 1330 HOURS ON MARCH 13. THIS RESULTED IN DELAYED INTERNAL COMMUNICATION THAT IN TURN CAUSED THE REPORT TO BE FILED OUTSIDE OF THE REPORTING WINDOW.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140037 | 16355 | 2014-04-11 11:31 | ORIGINAL FINAL | 32005 | ENLINK LIG, LLC | 1722 ROUTH STREET SUITE 1300 | DALLAS | TX | 75201 | 2014-03-13 14:15 | 2014 |  |  | 30.5679 | -92.0636 | 1076606 | 2014-03-13 15:42 |  | NATURAL GAS |  | 7425 | 7.83 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-03-13 15:39 | 2014-03-14 01:44 |  |  |  |  | NO |  |  |  |  | NO | [7 empty] | 2014-03-13 14:15 | 2014-03-13 14:40 | ONSHORE | LA | 70570 | OPELOUSAS | ST LANDRY |  |  | OPELOUSAS 8 INCH LINE # 1164 |  | YES | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 |  | 0.188 | 42000 | API 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1960 | 1960 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  |  |  |  | CLASS 3 LOCATION | NO |  | 165 |  | NO | NO | NO |  | 69130 | 76468.5280801464 | 35 | 38.7154416722859 | 32670 | 21799.0718038529 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 101835 | 57718.9311260249 | 98306.3153256716 | [8 empty] | 753 |  | 800 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | YES | NO | NOT MANDATED |  |  | MANUAL | MANUAL | 20592 | YES | [7 empty] | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLERS DID NOT HAVE ANY DIRECT ENVOLVEMENT OF INCIDENT BESIDES ASSITING WITH DEPRESSURING PIPELINE UNTIL PIPE WAS TOTALLY ISOLATED. DOT COMPLIANCE MANAGER AND GAS CONTROL MANAGER DISCUSSED THIS ISSUE JUST AFTER THE INCIDENT WAS MADE SAFE AND BOTH AGREED NOT OTHER ACTIONS ARE NECESSARY FOR GAS CONTROLLER ENVOVELMENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES | YES |  |  | YES | YES | 1960 | YES | YES | YES | YES |  |  | 2014 | 2014 |  |  | YES | [190 empty] | NO | [63 empty] | YES | 2014 | 521 | NO | [13 empty] | NO | [63 empty] | WILLLIAM L WORLEY | DOT COMPLIANCE MANAGER | bill.worley@enlink.com | 2147219449 | 2149539501 |  |  |  | WILLIAM L WORLEY | DOT COMPLIANCE MANAGER | 2147219449 | bill.worley@enlink.com | THE ENLINK OPELOUSAS 8" PIPELINE (PIPELINE #1164) ON MARCH 13, 2014 HAD TOTALLY SEPARATED. EMERGENCY RESPONDERS REPORTED A GAS RELEASE TO OUR GAS CONTROL CENTER IN PINEVILLE LA. ONCE THE CALL WAS RECEIVED AT OUR GAS CONTROL THEY CALLED FIELD PERSONNEL TO EVALUATE AND BEGAN ISOLATING THE PIPELINE. ONCE THE PIPELINE WAS ISOLATED AND EVALUATED THAT NO ONE WAS HURT OR INJURED; OPERATIONS BEGAN TO REPLACE THE SEPARATED SECTION WITH NEW PIPE. THE PIPELINE WAS RETURNED TO SERVICE AT 0144 HRS. THE MORNING OF THE 14TH AT SIGNIFICANT LOWER PRESSURE TO RESTORE THE DISTRIBUTION SUPPLIER WITH NEEDED GAS TO THEIR CUSTOMERS. ENLINK EVALUATED WHETHER OR NOT THE EXISTING MAOP OF 800 PSI WAS JUSTIFIED. ONCE THE EVALUATION WAS COMPLETED THE PIPELINES MAOP WAS REDUCED TO 347. THE PIPELINE NOW HAS AN ESTABLISHED MAOP AT LESS THAN 30% SMYS.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20140038 | 16481 | 2014-04-14 14:13 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2014-03-18 14:50 | 2014 |  |  | 28.6539 | -91.0014 | 1077084 | 2014-03-19 08:40 |  | NATURAL GAS |  | 241 | 299 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-03-19 08:00 | 2014-03-22 10:05 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-03-19 08:00 | 2014-03-19 08:00 | OFFSHORE | [28 empty] | 64 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SHIP SHOAL | 169 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 10.75 |  | 0.365 | 42000 | API-5L | SEAMLESS |  | YOUNGSTOWN | OTHER | CONCRETE | [27 empty] | 1966 | 1966 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 281 |  | NO | NO | NO |  | 0 | 0 | 1338 | 1480.03602735767 | 1077 | 718.628721541156 | 175000 | 193577.20836143 | 0 | 0 | 2500 | 2765.38869087756 | HELICOPTOR TRANSPORT AND MISC LABOR. |  | 179915 | 91550.843522561 | 198541.261801206 | [8 empty] | 690 |  | 1440 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | CHECK VALVE | 14823 | NO | [5 empty] | YES | PIPELINE DOES NOT HAVE A LAUNCHER/RECIEVER TRAP, ONLY SUBSEA VALVE WITH BLIND FLANGE. | YES |  |  | YES |  | YES | NOT DESIGNED FOR SMART PIG INSPECTION | OFFSHORE GATHERING | YES | YES | YES | YES | NO | OTHER | PRODUCER EMPLOYEES NEAR THE LEAK SITE. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS VERY SMALL, THERFORE THE CONTROL ROOM WOULD NOT HAVE DETECTED THE LEAK. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN | [5 empty] | YES | THIS OCCURRENCE SUPPORTS THE LEAK IS DUE TO INTERNAL CORROSION; THIS CONCLUSION IS CONSISTENT WITH OUR EXPERIENCE WITHPREVIOUS INCIDENTS OF THIS NATURE. PLEASE SEE PART H OF REPORT, NARRATIVE (RCA) FOR MORE DETAILS. |  |  | YES | ULTRASONIC TEST PREFORMED BY DIVERS RESULTED IN NO WALL LOSS ONLY A PINHOLE. | YES | [5 empty] | YES |  | NO | [169 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | JOHNNY LOPEZ | REGULATORY COMPLIANCE SPECIALIST | johnny.lopez@williams.com | 7132152995 | 7132152222 |  |  |  | MARIE SOTAK | MANAGER OF PIPELINE SAFETY | 7132152111 | marie.sotak@willliams.com | RCA : WE (TRANSCO) RECEIVED A CALL FROM PRODUCER (FIELDWOOD) AT APPROXIMATELY 2:50PM ON 3-18-14 REPORTING THAT THEY SPOTTED BUBBLES COMING FROM PLATFORM SS 182. A HELICOPTER IS DISPATCHED TO LEAK SITE AND THEY PLOT GIVEN COORDINATES. THE LEAK LOCATION IS VERY CONGESTED WITH PRODUCER GATHERING PIPELINES WHICH COMPLICATE OUR INVESTIGATION. WITH THE INFORMATION GATHERED WE DETERMINE THAT IT IS OUR 10" (SELA) OFFSHORE GATHERING LINE THAT COULD BE LEAKING. A DIVE BOAT IS DISPACHED TO THE LEAK LOCATION. MULTIPLE PRODUCER LINES ARE ISOLATED. 03-21-2014. EXAMINATION BY DIVERS IDENTIFIED AN ISOLATED PINHOLE LEAK AT THE 7 O'CLOCK POSITION ON THE 10" GATHERING LINE. THE ISOLATED PINHOLE LEAK WITH NO WALL LOSS IS CONFIRMED BY ULTRASONIC TEST READINGS . 03-22-2014 REPAIR CLAMP IS INSTALLED AND THE 10" GATHERING LINE IS PUT BACK INTO SERVICE. THIS OCCURRENCE SUPPORTS THE LEAK CAUSE IS DUE TO INTERNAL CORROSION; THIS CONCLUSION IS CONSISTENT WITH OUR EXPERIENCE WITH PREVIOUS INCIDENTS OF THIS NATURE. THE LINE IS UN-PIGGABLE, AND IS IN TWO-PHASE WET GAS GATHERING SERVICE. THE LINE IS TREATED WITH CHEMICAL INHIBITORS AND BIOCIDES THROUGH CONTINUOUS INJECTION AND BATCH TREATING. THIS LINE AND SEVERAL OTHERS COMINGLE FLOW TO OUR FACILITY AT MOSQUITO BAY, WHERE WE COLLECT SAMPLES AND MONITOR RESIDUALS. THE CHEMICAL INJECTION EQUIPMENT OPERATION AND CHEMICAL QUANTITIES ARE CHECKED MONTHLY BY OUR FIELD TECHNICIANS. THESE ACTIONS ARE CONSISTENT WITH OUR SOP 20.11.03, WILLIAMS GENERAL INTERNAL CORROSION POLICY
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140039 | 16493 | 2014-04-14 17:33 | SUPPLEMENTAL FINAL | 15014 | GAS TRANSMISSION NORTHWEST LLC | 700 LOUISIANA STREET | HOUSTON | TX | 77002 | 2014-03-12 14:08 | 2014 |  |  | 48.7293 | -116.2018 | 1076523 | 2014-03-12 14:40 |  | NATURAL GAS |  | 1 | 29316 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-03-12 14:55 | 2014-05-05 18:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-03-12 13:00 | 2014-03-12 13:00 | ONSHORE | ID | 83845 | MOYIE SPRINGS | BOUNDARY | MILEPOST | 20.8 | GTN | A-LINE MLV 3-0 TO MLV 3-1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 50 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 36 |  | 0.438 | 52000 | API 5L X52 | SINGLE SAW |  | CONSOLIDATED WESTERN STEEL | ASPHALT | [28 empty] | 1961 | 1960 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 2 LOCATION | NO |  | 810 |  | NO | NO | NO |  | 0 | 0 | 135220 | 149574.343512186 | 5 | 3.33625218914186 | 420000 | 464585.300067431 | 3500 | 3871.54416722859 | 0 | 0 |  |  | 558725 | 283696.081905495 | 618034.523999034 | [8 empty] | 710 |  | 911 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | AUTOMATIC | 96270 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM ACTIONS COULD NOT HVE AFFECTED THIS EVENT. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | YES | [6 empty] | YES | [10 empty] | YES |  |  |  | YES | [63 empty] | YES | [6 empty] | YES | [50 empty] | COMBINATION TOOL | 2013 |  |  |  |  | NO |  |  | NO | [13 empty] | NO | [63 empty] | KURT SMITH | COMPLIANCE SPECIALIST | kurt_smith@transcanada.com | (509) 533-2848 | (509) 533-2993 |  |  |  | KURT SMITH | COMPLIANCE SPECIALIST | (509) 533-2848 | kurt_smith@transcanada.com | ANALYSIS OF ILI DATA SHOWED AN INDICATION OF A DENT IN THE BOTTOM QUADRANT OF THE GTN A-LINE PIPELINE 447 FEET UPSTREAM OF MAINLINE VALVE MLV 3-1. A GROUND BASED LEAKAGE SURVEY WAS CONDUCTED AT THE SITE AND UPSTREAM AND DOWNSTREAM FOR A DISTANCE OF 300 FEET IN BOTH DIRECTIONS. GAS WAS DETECTED AT THE GROUND SURFACE NEAR THE LOCATION OF THE SUSPECTED DENT. THE PIPELINE PRESSURE WAS REDUCED AND THE PIPELINE SEGMENT WAS ISOLATED. PRESSURE REDUCTION WAS HELD BELOW 80% OF THE HIGHEST PRESSURE RECORDED DURING THE PREVIOUS 60 DAYS WHILE THE INVESTIGATION CONTINUED TO LOCATE THE POSITION OF THE LEAK. AFTER THE LOCATION OF THE LEAK WAS FURTHER LOCALIZED, THE PIPELINE SECTION WAS VENTED TO NEAR ATMOSPHERIC PRESSURE AND WAS HELD THERE UNTIL THE REPAIR PROCESS WAS BEGUN. FURTHER INVESTIGATION CONFIRMED A DENT WITH A CRACK NEAR THE BOTTOM OF THE PIPE. THE PIPE SECTION WAS CUT OUT AND REPLACED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140040 | 17101 | 2014-04-14 19:45 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2014-03-15 09:45 | 2014 |  |  | 42.736 | -85.9659 | 1076766 | 2014-03-15 13:52 |  | NATURAL GAS |  | 97.8 | 169.6 | 1.6 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-03-15 11:00 | 2015-01-16 07:55 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-03-15 09:47 | 2014-03-15 10:20 | ONSHORE | MI | 49419-9768 | HAMILTON | ALLEGAN | MILEPOST | OVERISEL S F | LATERAL #6 | 90 YARDS WEST OF STORAGE WELL O-119 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 38 |  | NO | [22 empty] | INTRASTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | WELD/FUSION |  | 10 |  | 0.5 | 46000 | API 5L | SEAMLESS |  | JONES & LAUGHLIN STEEL COMPANY | OTHER | 6X TAR WITH NO. 7 WRAP LAYER AND THIN PLASTIC LAYER (25% CHRYSOTILE ASBESTOS) | [8 empty] | PIPE GIRTH WELD | [18 empty] | 1957 | 1956 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 2 LOCATION | NO |  | 293 |  | NO | NO | NO |  | 86978 | 96211.1910220595 | 1433 | 1585.12079761102 | 826 | 551.148861646235 | 0 | 0 | 1445 | 1598.39466332723 | 0 | 0 |  |  | 90682 | 46196.1940379762 | 99945.855344644 | [8 empty] | 417 |  | 1580 | OTHER | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS NOT CAUSED BY AND THERE WAS NO CONTRIBUTION TO THE INCIDENT BY CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  | YES |  |  |  |  | YES | [7 empty] | YES | GIRTH WELD | NO | NO | YES | YES | [168 empty] | YES | YES | [6 empty] | 2002 | [55 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 734-513-6256 |  |  |  |  | AMANDA L. WARD | GAS REGULATORY SERVICES LEAD | 517-545-8746 | amanda.ward@cmsenergy | AT APPROXIMATELY 9:45 AM ON MARCH 15, 2014 NEAR WELL O-119 AT OVERISEL STORAGE FIELD IN HAMILTON, MI, A NEARBY PROPERTY OWNER REPORTED A SUSPECTED NATURAL GAS LEAK. CONSUMERS ENERGY'S GAS CONTROL WAS NOTIFIED AT 9:47 AM OF THE LEAK. CONSUMERS ENERGY CREWS ARRIVED ON SITE AND DISCOVERED A NATURAL GAS LEAK ON LATERAL #6, APPROXIMATELY 90 YARDS FROM WELL O-119. LATERAL #6 WAS ISOLATED BY CLOSING ALL VALVES AFFECTING GAS FLOW TO THE LATERAL. THE LATERAL WAS SUBSEQUENTLY BLOWN DOWN AND TAKEN OUT OF SERVICE. THE CONTROLLED BLOWDOWN WAS COMPLETED AT 3:20 PM ON MARCH 15. PRELIMINARY INCIDENT INVESTIGATION REVEALED A 7/32" DIAMETER HOLE IN THE GIRTH WELD OF THE 10" STEEL PIPE, APPARENTLY DUE TO INTERNAL CORROSION PITTING. THE LATERAL CURRENTLY REMAINS OUT OF SERVICE UNTIL INVESTIGATION AND REMEDIATION HAS BEEN COMPLETED. A TELEPHONIC REPORT WAS INITIALLY FILED WITH NRC DUE TO A POTENTIAL FOR GAS LOSSES IN EXCESS OF 3 MMCF (MILLION CUBIC FEET). EXPOSURE OF THE LEAK AND SUBSEQUENT CALCULATIONS DETERMINED THAT THE VOLUME OF GAS RELEASED WAS MUCH SMALLER; HOWEVER AN INCIDENT REPORT IS STILL BEING FILED DUE TO INCURRED COSTS IN EXCESS OF $50,000. NO FIRE DEPARTMENT, POLICE, BLOCKED TRAFFIC OR MEDIA PRESENCE WAS NOTED ON SITE AT THE TIME OF THE INCIDENT. THE DAMAGE SECTION OF THE PIPELINE WAS TRANSPORTED TO THE CONSUMERS ENERGY TRAIL STREET LABORATORY FOR FURTHER EXAMINATION. THE LABORATORY EVALUATION AND THE HISTORICAL EVIDENCE CONFIRMED THE LEAK WAS DUE TO EFFECTS OF INTERNAL CORROSION. IN ADDITION TO COMPREHENSIVE METALLURGICAL TESTING, CONSUMERS ENERGY CONTRACTED IN-LINE INSPECTION VENDOR, INLINE DEVICES TO INSPECT THE LATERAL AND SYSTEM INTEGRITY EMPLOYEES CONDUCTED A THOROUGH REVIEW OF THE FINDINGS; IDENTIFYING MULTIPLE DIG LOCATIONS TO VALIDATE TOOL DATA AND DEVELOP A REMEDIATION PLAN. SEVEN SECTIONS OF PIPE WERE REPLACED ( APPROXIMATELY 400') WHERE THE TOOL PREDICTED METAL LOSS IN OR NEAR THE GIRTH WELD. REMEDIATION WORK WAS COMPLETED AND THE LATERAL WAS PLACED BACK IN SERVICE ON JANUARY 16, 2015.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140041 | 16607 | 2014-04-17 13:45 | SUPPLEMENTAL FINAL | 12350 | CENTERPOINT ENERGY RESOURCES CORP., DBA CENTERPOINT ENERGY MINNESOTA GAS | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2014-03-02 20:50 | 2014 |  |  | 44.8877 | -93.3626 | 1075578 | 2014-03-03 05:16 |  | NATURAL GAS |  | 1 | 23.3 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | LOWERED PRESSURE TO MITIGATE RISK TO FAILITATE THE REPAIR. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-03-02 20:50 | 2014-03-02 22:33 | ONSHORE | MN | 55439-1227 | EDINA | HENNEPIN | SURVEY STATION NO. | STATION 16+44 | MBLSW | MBLSW | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 264 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | DRESSER STYLE 38 COUPLING | 1952 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | NO |  | 216 |  | NO | NO | NO |  | 50000 | 55307.7738175513 | 203 | 224.549561699258 | 8 | 5.33800350262697 | 300000 | 331846.642905308 | 5000 | 5530.77738175513 | 10000 | 11061.5547635103 | MISCELLANEOUS EQUIPMENT |  | 365211 | 185439.019652973 | 403976.636433326 | [8 empty] | 169 |  | 175 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 4500 | NO |  | YES | YES |  |  |  |  | YES |  |  |  |  | YES | WEATHER OTHER TRANSMISSION LINE PROJECTS | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS DUE TO EQUIPMENT FAILURE NOT ASSOCIATED WITH THE CONTROL ROOM. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | OTHER | DRESSER STYLE 38 COUPLING | [16 empty] | YES | TRANSIENT EARTH STRESS/ LOADING | [161 empty] | STEVE OLINGER | OPERATIONS SPECIALIST | steve.olinger@centerpointenergy.com | 6123215453 |  |  |  |  | DEAN HEADLEE | PIPELINE SAFETY AND COMPLIANCE MANAGER | 6123215366 | dean.headlee@centerpointenergy.com | CENTERPOINT ENERGY RESPONDED TO AN ODOR COMPLAINT ON MARCH 2, 2014. INVESTIGATION REVEALED THE SOURCE TO BE A 24" DRESSER STYLE 38 COUPLING. DURING EXCAVATION THE COUPLING STOPPED LEAKING. A 24" COVER SLEEVE WAS INSTALLED OVER THE COUPLING. THERE WAS NO CORROSION EVIDENT ON THE PIPE AND CORROSION WAS RULED OUT BY X-RAYS AND ULTRASONIC TESTING. THE PIPE WAS IN GOOD CONDITION. GAS WAS MIGRATING. EXCAVATED TO SECOND COUPLING BUT FOUND NO LEAK. COVER SLEEVE WAS INSTALLED ON SECOND COUPLING PER AGREEMENT WITH MNOPS TO INSTALL COVER SLEEVES ON EXPOSED COUPLINGS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140042 | 16880 | 2014-04-22 18:59 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2014-03-14 08:29 | 2014 |  |  | 41.5389 | -96.5364 | 1076651 | 2014-03-14 09:44 |  | NATURAL GAS |  | 37500 | 7000 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-03-14 10:04 | 2014-04-11 12:00 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 3 | 2014-03-14 08:45 | 2014-03-14 09:30 | ONSHORE | NE | 68044 | NICKERSON | DODGE | MILEPOST | 58.04 | PALMYRA TO HOOPER B-LINE | NEM50102-M581B | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 40 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 18 |  | 0.25 | 35000 | 5L | FLASH WELDED |  | AO SMITH | COAL TAR | [28 empty] | 1946 | 1946 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 144 | 42 |  | CLASS 1 LOCATION | NO |  | 329 |  | NO | NO | NO |  | 2200 | 2433.54204797226 | 31400 | 34733.2819574222 | 168000 | 112098.073555166 | 3000000 | 3318466.42905308 | 32973 | 36473.2645217224 | 169642 | 187650.427319141 | EQUIPMENT TO MAINTAIN SERVICE DURING REPAIRS |  | 3404215 | 1759420.05902859 | 3691855.0184545 | [8 empty] | 646 |  | 700 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 45000 | NO |  | YES | [5 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS IDENTIFIED BY A LOCAL UTILITY (NATURAL GAS) EMPLOYEE ON HIS WAY TO WORK. THE GAS CONTROL CENTER VERIFIED HIS INFORMATION ALMOST SIMULTANEOUSLY. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES | [6 empty] | YES | [14 empty] | YES | [6 empty] | YES | THE FAILURE INITIATION POINT IS NEAR A 12-INCH TIE-OVER LINE AND SADDLE WELDED ON TO THE 18-INCH B-LILNE | [55 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | JOHN A. GORMLEY | SR CORROSION SPECIALIST | john.gormley@nngco.com | 402-398-7494 |  |  |  |  | THOMAS CORRELL | DIRECTOR OF PIPELINE SAFETY | 402-398-7715 | thomas.correll@nngco.com | AT 8:30 AM ON MARCH 14, 2014 THE PALMYRA TO HOOPER B-LINE, ALSO KNOWN AS NEM50102-M581B, RUPTURED AND CAUGHT FIRE. THE RUPTURE INITIATED NEAR A 12-INCH TIE-OVER LINE BETWEEN THE 1ST LINE (A-LINE) AND THE SECOND LINE (B-LINE). THE RUPTURE AND FIRE DAMAGED TWO MAINLINE VALVE SETTINGS AND A BRANCH LINE TAKE-OFF. THREE HOMES WERE EVACUATED BY THE THE LOCAL EMERGENCY RESPONDERS BUT HOMEOWNERS WERE ALLOWED TO RETURN LATER IN THE DAY. AT THIS TIME, THE CAUSE HAS NOT BEEN DETERMINED. THE PIPE FAILURE PIECE WAS SENT TO STRESS ENGINEERING IN HOUSTON FOR TESTING. METALLURGICAL ANALYSIS COULD NOT PRECISELY DETERMINE THE ROOT CAUSE OF THE RUPTURE. IT IS BELIEVED THAT INTERACTING DEFECTS FROM ORIGINAL CONSTRUCTION WITH SOME GROUND MOVEMENT MAY HAVE CAUSED A CRACK IN THE FILLET WELD OF A REINFORCING SADDLE TO FAIL. COST UPDATE INFORMATION: NORTHERN'S EMERGENCY RESPONSE WAS ACTUALLY ON THE ORDER OF ABOUT $200,000. HOWEVER, WHEN WE BEGAN TO REMOVE 2 MAINLINE BLOCK VALVE SETTINGS AND PIPE, 4 CROSSOVERS AND THEIR VALVES, REBUILT THE BLAIR LOOP (CARGILL) BRANCHLINE TAKE-OFF, REROUTED ABOUT 600 FEET OF 6-INCH PIPE ALL WHILE MAINTAINING SERVICE TO BLACK HILLS ENERGY. OUR CONTRACTOR WAS ON THIS PROJECT FOR NEARLY ONE MONTH.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140043 | 16907 | 2014-04-22 19:05 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2014-03-19 18:30 | 2014 |  |  | 44.8272 | -93.1867 | 1077174 | 2014-03-19 22:41 |  | NATURAL GAS |  | 4000 | 8000 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-03-20 03:00 | 2014-03-24 08:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 18 | 2014-03-19 20:29 | 2014-03-19 21:10 | ONSHORE | MN | 55122 | EAGAN | DAKOTA | MILEPOST | 2.17 | MINNEAPOLIS 1 TO EAGAN 1 | MNM80801-M464A | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 96 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12.75 |  | 0.25 | 35000 | 5L | FLASH WELDED |  | A.O.SMITH | COAL TAR | [28 empty] | 1942 | 1942 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | YES | METHOD2 | 171 |  | NO | NO | NO |  | 100 | 110.615547635103 | 8000 | 8849.24381080821 | 4000 | 2669.00175131349 | 40000 | 44246.219054041 | 20000 | 22123.1095270205 | 0 | 0 |  |  | 72100 | 37345.1602693929 | 77998.1896908184 | [8 empty] | 316 |  | 380 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 13093 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE ODORIZED NATURAL GAS WAS DETECTED BY THE PUBLIC AND REPORTED TO LOCAL 911 EMERGENCY RESPONDERS. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED | YES | YES | [15 empty] | OTHER | THE CRACK APPEARS TO BE CAUSED BY BENDING FORCES ON THE PIPELINE AND DORMANT SCC CRACKS. SEE PART H FOR DETAILS OF THE LABORATORY REPORT. |  |  | YES |  | YES | [63 empty] | YES | YES | [6 empty] | 2011 | [55 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | JOHN A. GORMLEY | SR CORROSION SPECIALIST | john.gormley@nngco.com | 402-398-7494 |  |  |  |  | THOMAS CORRELL | DIRECTOR OF PIPELINE SAFETY | 402-398-7715 | thomas.correll@nngco.com | AT APPROXIMATELY 6:30 PM ON MARCH 19, 2014, RESIDENTS AND LOCAL EMERGENCY RESPONDERS REPORTED A STRONG GAS ODOR NEAR THE INTERSECTION OF ASHBURY AND TERRA GLENN COURT IN EAGAN, MN. FURTHER INVESTIGATON BY OPERATOR PERSONNEL DETECTED NATURAL GAS ALONG CURB LINES AND IN MANHOLES. NORTHERN NATURAL GAS WORKED WITH LOCAL DISTRIBUTION COMPANIES TO RE-ROUTE GAS AROUND THE 12-INCH PIPELINE WHILE REPAIRS WERE COMPLETED. NINE HOMES AND ABOUT 18 PEOPLE IN THE NEIGHBORHOOD WERE EVACUATED AND 5 OF THOSE HOMES HAD THE ELECTRICITY SHUT OFF. THE HOMEOWNERS WERE AWAY FROM THEIR HOMES OVERNIGHT WHILE PIPELINE CREWS RE-ROUTED GAS. THE PIPELINE WAS REPAIRED WITH A CYLINDER OF PIPE AND RETURNED TO SERVICE WITHOUT INCIDENT ON MARCH 23, 2014. THE PIPELINE HAD AN 8-INCH LONG CIRCUMFERENTIAL CRACK NEAR A GIRTH WELD. THE CRACK RESEMBLED A TEAR IN THE PIPE BODY. THE SECTION WAS SENT TO A LAB FOR ANALYSIS. THE PIPE JUMPED WHEN CUT TO BEGIN REPAIRS SO WE BELIEVE THE PIPE WAS IN A BIND. THAT IS, THE PIPE WAS BEING FORCED TO CHANGE DIRECTION (SLIGHTLY) WITHOUT A FITTING OR BEND. UPDATE: LABORATORY ANALYSIS: THE CRACK APPEARS TO BE CAUSED BY BENDING FORCES ON THE PIPELINE. THE LAB REPORT INDICATED THAT THE FAILURE OCCURRED AT DORMANT CIRCUMFERENTIAL SCC CRACKS. IN THIS CASE, IT WAS NOT THE GROWTH OF CIRCUMFERENTIAL SCC THAT RESULTED IN FAILURE. IT WAS HIGH BENDING/TENSILE STRESSES THAT CAUSED OVERLAOD WHERE THE CRACKS WERE PRESENT. THE LAB SITED LOWER THAN NORMAL TEMPERATURES (LOWER PIPE TOUGHNESS DUE TO LOWER TEMPS AND HIGH TENSILE STRESS DUE TO PIPE CONTRACTION) CONTRIBUTING TO THE FAILURE. SCC WAS NOT THE ROOT CAUSE OF FAILURE. IT WAS HIGH BENDING/TENSILE STRESS COUPLED WITH LOWER THAN NORMAL TEMPERATURES.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140044 | 17040 | 2014-04-24 10:12 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2014-03-30 17:40 | 2014 |  |  | 30.799 | -93.9292 | 1078275 | 2014-03-30 17:45 |  | NATURAL GAS |  | 415 | 1480 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | LINE PRESSURE WAS LOWERED UNTIL TEMPORARY REPAIRS WERE MADE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-03-30 16:00 | 2014-03-30 17:40 | ONSHORE | TX | 75951 | JASPER | JASPER | SURVEY STATION NO. | 5771+04 | CALL JUNCTION TO MAGASCO 16", 14", 12" | INDEX 64 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 26 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.25 | 30000 | VINTAGE | LAP WELDED |  | UNKNOWN | ASPHALT | [28 empty] | 1924 | 1924 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 189 |  | NO | NO | NO |  | 3500 | 3871.54416722859 | 3057 | 3381.51729120509 | 2090 | 1394.5534150613 | 778931 | 861618.791349581 | 8500 | 9402.32154898372 | 0 | 0 |  |  | 796078 | 404596.81775121 | 879668.72777206 | [8 empty] | 195 |  | 292 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 653764 | NO | YES | YES | YES | YES |  | YES | DRESSER COUPLINGS AND SIPHONS | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SMALL LEAK DID NOT SHOW UP ON SCADA. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1955 | NO | YES | YES | YES |  |  | 2013 | 2012 |  |  | NO | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 2706886361 | jeff.mcmaine@bwpmlp.com | HUNTERS IN THE FOREST CAME UPON BUBBLES IN A PIPELINE RIGHT OF WAY CORRIDOR WHERE MULTIPLE PIPELINES EXISTED. AFTER INVESTIGATION, A LEAK WAS FOUND TO BE ON A GULF SOUTH ASSET. THE PRESSURE WAS REDUCED BY CLOSING THE UPSTREAM VALVE ALLOWING THE DOWNSTREAM CUSTOMER TO REMAIN IN SERVICE. A BAND CLAMP WAS INSTALLED UNTIL PERMANENT REPAIRS ARE MADE. 3-2-16 REVISED TO FINALIZE REPORT WITH TOTAL COSTS AND GAS LOSS AMOUNTS FOLLOWING PIPE REPLACEMENT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140045 | 16973 | 2014-04-24 20:33 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2014-03-25 15:10 | 2014 |  |  | 38.5776 | -121.5556 | 1077759 | 2014-03-26 00:20 |  | NATURAL GAS |  | 0 | 617 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-03-25 22:45 | 2014-03-26 02:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-03-25 15:10 | 2014-04-24 15:10 | ONSHORE | CA | 95691 | WEST SACRAMENTO | YOLO | MILEPOST | 10.1536 | TRANSMISSION LINE 116 | 122 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 60 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.375 | 42000 | X42 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | OTHER | POLYETHYLENE TAPE | [27 empty] | 1991 | 1991 | CARBON STEEL |  | OTHER | [8 empty] | CUTTING TORCH BURN-THROUGH | CLASS 3 LOCATION | YES | METHOD2 | 297 |  | NO | NO | NO |  | 0 | 0 | 3125 | 3456.73586359696 | 0 | 0 | 0 | 0 | 50000 | 55307.7738175513 | 0 | 0 |  |  | 53125 | 26974.4605529333 | 58764.5096811483 | [8 empty] | 680 |  | 720 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 16000 | NO |  |  |  | YES |  | YES | PIG LAUNCHER AND RECEIVER NEED TO BE INSTALLED. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS REPORTED BY ON-SCENE CONTRACTOR; ALSO, GAS LOSS THROUGH PINHOLE WAS NEGLIGIBLE AND DID NOT REGISTER ON SCADA. | [12 empty] | NO |  |  | YES | 8 | 0 | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | THE CONTRACTOR HAD A VALID USA TICKET, HOWEVER THE EXCAVATION AREA WAS NOT DELINEATED, THEREFORE, THERE WAS NOT AN OPPORTUNITY TO LOCATE AND MARK THE GAS FACILITIES WERE NOT PROPERLY IDENTIFIED AND MARKED. THE CONTRACTOR PROCEEDED TO PERFORM WORK ON THE ACTIVE LINE WITHOUT PROPERLY IDENTIFYING IF THE LINE WAS DEACTIVATED. |  |  | YES |  |  | DECOMMISSIONING | NO | [150 empty] | STEPHEN RAMOS | COMPLIANCE ENGINEER | s3rc@pge.com | 925-328-6107 |  |  |  |  | LAURENCE DENISTON | MANAGER REGULATORY COMPLIANCE | 925-328-5756 | lcd1@pge.com | A PACIFIC GAS & ELECTRIC (PG&E) CONTRACTOR WAS PERFORMING WORK TO CUT AND CAP THE PREVIOUSLY DEACTIVATED LINE 172A PIPELINE. AT 1510 HOURS, THE CONTRACTOR'S EMPLOYEE BURNED A SMALL HOLE INTO WHAT HE THOUGHT WAS THE DEACTIVATED PIPE, AND OBSERVED A HISSING NOISE. WORK WAS HALTED AND A PG&E SUPERVISOR WAS CALLED TO THE SITE. IT WAS DETERMINED THAT THE PIPE BEING WORKED ON WAS THE PRESSURIZED 16-INCH TRANSMISSION LINE L-116. THERE WERE NO INJURIES, NO IGNITION, AND NO MEDIA ON SITE. PG&E INITIATED EMERGENCY RESPONSE OPERATIONS, L-116 WAS DEPRESSURIZED AT 2245 HOURS ON 3/25/14 AND REPAIRS WERE COMPLETED BY WELDING A 2-INCH SAVE-A-VALVE TEE OVER THE SMALL HOLE. PRESSURE IN THE PIPELINE WAS RESTORED AT 0200 HOURS ON 3/26/14. SERVICE TO ONE CUSTOMER WAS INTERRUPTED. THE CONTRACTOR HAD A VALID USA TICKET, HOWEVER THE EXCAVATION AREA WAS NOT DELINEATED, THEREFORE, THERE WAS NOT AN OPPORTUNITY TO LOCATE AND MARK THE GAS FACILITIES WERE NOT PROPERLY IDENTIFIED AND MARKED. THE CONTRACTOR PROCEEDED TO PERFORM WORK ON THE ACTIVE LINE WITHOUT PROPERLY IDENTIFYING IF THE LINE WAS DEACTIVATED. COSTS TO MAKE REPAIRS WERE ESTIMATED TO EXCEED $50000 AT 0008 HOURS ON 3/26/14.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20140047 | 16633 | 2014-05-06 14:44 | SUPPLEMENTAL FINAL | 1472 | BLACK MARLIN PIPELINE CO | ONE WILLIAMS CENTER P.O. BOX 645 | TULSA | OK | 74172 | 2014-04-11 09:15 | 2014 |  |  | 29.2597 | -94.1219 | 1079470 | 2014-04-11 11:16 |  | NATURAL GAS |  | 47 | 11953 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-04-11 12:00 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-04-11 09:15 | 2014-04-11 09:15 | OFFSHORE | [28 empty] | 60 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | HGH ISLAND | 136 | PLATFORM | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | VALVE | [31 empty] | MAINLINE | BALL |  | NORDSTROM HYPRESPHERE |  |  |  | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO | NO |  | 0 | 0 | 9500 | 10508.4770253347 | 0 | 0 | 160000 | 176984.876216164 | 0 | 0 | 0 | 0 |  |  | 169500 | 86064.3964935941 | 187493.353241499 | [8 empty] | 640 |  | 1367 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 195360 | NO | YES | YES |  |  |  | YES | NO PIG LAUNCHING FACILITIES. | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | MAINTENANCE WAS BEING PERFORMED ON THE VALVE WHEN INCIDENT OCCURRED. PIPELINE CONTROL WAS NOT INVOLVED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | FAILURE OF EQUIPMENT BODY (EXCEPT COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL | MATERIAL/WELD/EQUIP FAILURE | FAILURE OF EQUIPMENT BODY | [166 empty] | FAILURE OF EQUIPMENT BODY (EXCEPT COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL | [30 empty] | YES |  |  |  |  | YES | VALVE BODY DRAIN PLUG | [161 empty] | SHANE FRASIER | PIPELINE SAFETY ENGINEER | shane.frasier@williams.com | 713-215-3051 |  |  |  |  | SHANE FRASIER | PIPELINE SAFETY ENGINEER | 713-215-3051 | shane.frasier@williams.com | WHILE CLOSING THIS VALVE FOR UPSTREAM MAINTENANCE, A CORRODED BODY DRAIN FAILED WHEN PRESSURE WAS INTRODUCED TO THE VALVE BODY THAT HAD BLED OFF.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140048 | 16593 | 2014-05-06 21:43 | SUPPLEMENTAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 200 CIVIC CENTER DR | COLUMBUS | OH | 43215 | 2014-01-23 15:09 | 2014 |  |  | 39.8037 | -83.0298 | 1079396 | 2014-04-10 14:45 |  | NATURAL GAS |  | 30 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | VEHICLE STRUCT AN ABOVE GROUND VALVE OPERATOR RESULTING IN A NON HAZARDOUS LEAK | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-01-23 15:21 | 2014-01-23 15:56 | ONSHORE | OH | 43146 | ORIENT | PICKAWAY | MILEPOST | VALVE C-2996 | SOUTHERN SUPPLY LINE | SOUTHERN SUPPLY LINE VALVE | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | MAINLINE | BALL |  | GROVE |  |  |  | 1988 | 1988 | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 3 LOCATION | NO |  | 283 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 128 | 85.4080560420315 | 300000 | 331846.642905308 | 1000 | 1106.15547635103 | 0 | 0 |  |  | 301128 | 152922.66643678 | 333038.206437701 | [8 empty] | 137.8 |  | 656 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 44143 | NO |  |  |  | YES |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELEASE OF NATURAL GAS WAS A VERY SMALL QUANTITY AND WOULD NOT HAVE BEEN DETECTED BY CONTROLLER | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [260 empty] | ROB R. SMITH | OPERATION COMPLIANCE MANAGER | rrsmith@nisource.com | 614-818-2110 | 614-818-2151 |  |  |  | ROB SMITH | OPERATION COMPLIANCE MANAGER | 614-818-2110 | rrsmith@nisource.com | ON 1/23/14, COLUMBIA GAS OF OHIO, INC. ( COLUMBIA) RECEIVED A CALL FROM THE PICKAWAY COUNTY SHERIFF'S DEPARTMENT NOTIFYING COLUMBIA THAT A CAR WHICH HAD LOST CONTROL AND VEERED OFF THE ROADWAY, HAD STRUCK THE ABOVE GROUND OPERATOR FOR A VALVE ON THE COLUMBIA SOUTHERN SUPPLY LINE IN ORIENT, OHIO. COLUMBIA FIELD PERSONNEL PROMPTLY RESPONDED TO THE SCENE AND FOUND THE VALVE OPERATOR DAMAGED AND A SMALL NON-HAZARDOUS LEAK ON VALVE C2996. SINCE THE TIME OF THE DAMAGE, COLUMBIA HAS EXCAVATED THE VALVE AND HAS WORKED WITH INTERNAL AND EXTERNAL VALVE EXPERTS TO DETERMINE IF REPAIRING THE VALVE IS POSSIBLE. COLUMBIA HAD BEEN MONITORING THE COSTS ASSOCIATED WITH THIS VALVE REPAIR OR REPLACEMENT AND DETERMINED ON APRIL 10, 2014 THAT VALVE COULD NOT BE REPAIRED AND THAT THE REPLACEMENT COSTS WOULD EXCEED CRITERIA IN 191.3. PLEASE CONSIDER THIS REPORT FINAL.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140049 | 16569 | 2014-05-09 10:36 | SUPPLEMENTAL FINAL | 31531 | ONEOK WESTEX TRANSMISSION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2014-04-10 04:45 | 2014 |  |  | 31.7093 | -102.5717 | 1079337 | 2014-04-10 07:10 |  | NATURAL GAS |  | 45792 | 832 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-04-10 07:25 | 2014-04-12 12:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-04-10 06:30 | 2014-04-10 06:45 | ONSHORE | TX | 79766 | ODESSA | ECTOR | MILEPOST | 44.49 | JOINT VENTURE | 4000-000 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 20 |  | 0.25 | 56000 | API 5LX | LONGITUDINAL ERW - HIGH FREQUENCY |  | AMERICAN STEEL PIPE | COAL TAR | [28 empty] | 1967 | 1967 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 588 | 20 |  | CLASS 1 LOCATION | NO |  | 426 |  | NO | NO | NO |  | 0 | 0 | 3843 | 4250.95549561699 | 213388 | 142383.23642732 | 82800 | 91589.673441865 | 0 | 0 | 0 | 0 |  |  | 300031 | 191608.543987728 | 238223.865364802 | [8 empty] | 943 |  | 953 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 103963 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL ROOM WAS MONITORING AN INLINE INSPECTION FOR AN APPROXIMATELY 66 MILE SEGMENT AND THE RUN WAS APPROXIMATELY 3 MILES FROM COMPLETION. THE CONTROL ROOM RECOGNIZED A PROBLEM AND WAS WORKING WITH FIELD PERSONNEL TO IDENTIFY THE CAUSE WHEN A CALL FROM THE PUBLIC WAS RECEIVED. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  |  | YES | THIRD PARTY FAILURE ANALYSIS | [5 empty] | YES | GIRTH WELD ANOMALY | [13 empty] | YES | [5 empty] | YES | FATIGUE | [55 empty] | YES | YES |  |  | YES |  |  |  | 2005 | [31 empty] | 2005 | [23 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | PATTI FORD | SENIOR PIPELINE SAFETY ENGINEER | patti.ford@oneok.com | 918 588 7131 | 918 732 1311 |  |  |  | WESLEY R. DUNBAR | VICE PRESIDENT | 918 588 7424 | wesley.dunbar@oneok.com | AT APPROXIMATELY 0450 HOURS ON APRIL 10, 2014, ONEOK WESTEX TRANSMISSION (OWT) GAS CONTROL NOTICED A DROP IN LINE PRESSURE AT THE DORA ROBERTS COMPRESSOR STATION. OPERATIONS PERSONNEL WERE DISPATCHED AT 0500 HOURS TO LOCATE THE POSSIBLE LEAK. GAS CONTROL DID RECEIVE A CALL AT 0630 HOURS FROM THE PUBLIC REPORTING BLOWING GAS IN A RURAL AREA APPROXIMATELY 6 MILES SOUTH OF PENWELL, TX AND 1/2 MILE EAST OF ROAD FM 1601 IN ECTOR COUNTY. OWT PERSONNEL WERE DIRECTED TO THIS SITE AND WERE ABLE TO IDENTIFY THE SOURCE OF BLOWING GAS AS OWT LINE 4000-000, COMMONLY KNOWN AS THE JV OR JOINT VENTURE LINE. BLOCK VALVES UPSTREAM AND DOWNSTREAM OF THE SITE WERE MANUALLY CLOSED BY 0725 HOURS AND THE ISOLATED SECTION OF THE PIPELINE WAS ALLOWED TO BLOW DOWN TO ATMOSPHERIC PRESSURE. THE SITE IS RURAL AND THERE WERE NO BUILDINGS INTENDED FOR HUMAN OCCUPANCY WITHIN 1/2 MILE OF THE SITE. LOCAL EMERGENCY RESPONDERS WERE ON SITE WHEN OWT PERSONNEL ARRIVED AT 0645 HOURS. THERE WAS NO FIRE OR EXPLOSION DUE TO THE RELEASE. THE PIPE THAT FAILED WAS SECURED AND SENT TO A LAB IN TULSA, OK TO DETERMINE THE CAUSE OF THE FAILURE. UPDATE: THE FAILURE ANALYSIS PERFORMED BY ELEMENT LABS IN TULSA, OK CONCLUDED THAT THE CAUSE OF THE FAILURE WAS AN INITIAL DUCTILE FAILURE OF A FIELD MADE GIRTH WELD WHICH INITIATED THE FAILURE OF THE ADJOINING PIPE JOINT LONG SEAM. THE THIRD PARTY FAILURE ANALYSIS INDICATED THE CAUSE OF THE GIRTH WELD FAILURE WAS AN APPROXIMATELY ONE QUARTER INCH DIAMETER VOID LOCATED AT THE LOCATION OF AN ADJOINING LONGITUDINAL PIPE JOINT SEAM. THIS GIRTH WELD ALSO HAD AREAS OF INCOMPLETE FUSION AND FAILED DUE TO DUCTILE OVERLOAD IN THE VICINITY OF THE VOID. SIGNS OF FATIGUE WERE ALSO OBSERVED ON THE GIRTH WELD FAILURE SURFACES ALONG AREAS OF INCOMPLETE FUSION. WHEN THE GIRTH WELD FAILED, THE CRACK PROPAGATED INTO THE LONGITUDINAL SEAM AND THEN BY RAPID BRITTLE FRACTURE, IT PROCEEDED DOWN THE LENGTH OF THE LONGITUDINAL PIPE SEAM CAUSING THE PIPELINE RUPTURE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140050 | 16522 | 2014-05-09 13:02 | SUPPLEMENTAL FINAL | 38987 | KINETICA ENERGY EXPRESS LLC | 1001 MCKINNEY STREET, SUITE 900 | HOUSTON | TX | 77002 | 2014-04-29 16:45 | 2014 |  |  | 28.5778 | -91.8711 | 1081256 | 2014-04-29 18:00 |  | NATURAL GAS |  | 34 | 700 | 734 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-04-29 17:00 | 2014-05-05 14:50 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-04-30 07:00 | 2014-04-30 07:00 | OFFSHORE | [28 empty] | 145 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SOUTH MARSH ISLAND | 78 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 |  | 0.5 | 52000 | L5 | DSAW |  | NIPPON | EPOXY | [28 empty] | 1991 | 1988 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO | NO |  | 0 | 0 | 3000 | 3318.46642905308 | 461 | 307.602451838879 | 0 | 0 | 1600 | 1769.84876216164 | 215000 | 237823.427415471 | COST OF REPAIR CLAMP, DIVE VESSEL, DIVERS AND COMPANY PERSONNEL |  | 220061 | 111821.804957056 | 243219.345058524 | [8 empty] | 910 |  | 1250 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 8622 | NO | [5 empty] | YES | SUBSEA TIE-IN CONFIGURATION WILL NOT ALLOW FOR THE PASSAGE OF INSPECTION TOOLS. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | PLATFROM OPERATOR IDENTIFED BUBBLE ON SEA SURFACE |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | REMOTE LOCATION OFFSHORE WITH PRESSURES WELL BELOW ESTABLISHED MAOP. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | PINHOLE IDENTIED |  | YES |  |  |  |  | YES |  |  |  | YES | [5 empty] | YES | YES | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | SUSIE RICHMOND | MANAGER OF PIPELINE COMPLIANCE AND TRAINING | susie.richmond@kineticallc.com | 9852236145 |  |  |  |  | SUSIE RICHMOND | MANAGER OF PIPELINE COMPLIANCE AND TRAINING | 9852236145 | susie.richmond@kineticallc.com | NO ADDITIONAL INFORMATION - THIS IS THE ONLY WAY I AM ABLE TO TAKE THE REPORT TO "FINAL" STATUS PLATFORM OPERATOR FOR ENERGY PARTNERS CONTACTED THE KINETICA ENERGY EXPRESS PIPELINE DIRECTOR AT 16:45 ON 4.29.14 STATING THAT A BUBBLE HAD BEEN IDENTIFIED ON THE WATER'S SURFACE ABOUT 1/2 MILE FROM THEIR PLATFORM. THEY HAD SHUT IN THEIR PIPELINE, NO REDUCTION IN THE SIZE OF THE BUBBLE WAS APPARENT. THEY WERE ASKED TO CLOSE THE SUPPLY VALVE TO THE 523M-7500 KINETICA PIPELINE LINE AT THAT TIME. FOGGY CONDITIONS WERE REPORTED AT THE LOCATION SO PERSONNEL COULD NOT BE DISPATCHED TO THE LOCATION AT THAT TIME FROM THE BEACH. ON THE MORNING OF 4.30.14 KINETICA PERSONNEL FLEW TO THE LOCATION TO VERIFY THE COORDINATES. AFTER VERIFICATION THIS WAS A KINETICA PIPELINE, PERSONNEL LOCKED AND TAGGED ALL VALVES AT THE PLATFORM LOCATION AND MADE ARRANGEMENTS TO RELIEVE PRESSURE FROM THE PIPELINE TO 70 PSIG. A DIVE VESSEL WAS DISPATCHED TO THE LOCATION TO CLOSE SUBSEA VALVES AND PREPARE TO MAKE THE PIPELINE REPAIR. AFTER EXCAVATING THE LOCATION AND REMOVING THE CONCRETE COATING, THE DIVER WAS ABLE TO IDENTIFY A SMALL PINHOLE LEAK. THE GENERAL AREA HAD A UT INSPECTION PERFORMED, NO INDICATIONS OF GENERALIZED CORROSION WERE IDENTIFIED. THE REPAIR CLAMP WAS INSTALLED, THE OPERATOR WAS ASKED TO RAISE THE PRESSURE A SMALL TO LOOK FOR ANY INDICATION OF A RELEASE OF PRESSURE. AFTER THE INITIAL PRESSURIZATION, THE PIPELINE TO SERVICE IN INCREMENTAL STEPS WHILE BEING MONITORED FOR LEAKS. AFTER THE DETERMINATION WAS MADE THE REPAIR WAS SUCCESSFUL, THE VESSEL DEPARTED THE LOCATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140051 | 16755 | 2014-05-12 13:58 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2014-04-11 05:30 | 2014 |  |  | 31.3641 | -101.7763 | 1079525 | 2014-04-11 15:46 |  | NATURAL GAS |  | 6800 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | A RELIEF VALVE WAS SLIGHTLY OPEN | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-04-11 05:30 | 2014-04-11 06:32 | ONSHORE | TX | 79778 | RANKIN | REAGAN | MILEPOST | 14.77 | PLYMOUTH COMPRESSOR STATION | TXM15501-M880B | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1977 |  | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 388 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 360000 | 240210.157618214 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 360000 | 249036.777583187 | 240210.157618214 | [8 empty] | 545 |  | 550 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE RELIEF VALVE VENTING WAS SO SMALL THAT ANY PRESSURE DROP WAS UNDETECTABLE BY SCADA EQUIPMENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | A HIGH VOLUME RECEIPT POINT CONTINUED DELIVERIES | [161 empty] | JOHN A GORMLEY | SR CORROSION SPECIALIST | john.gormley@nngco.com | 402-398-7494 |  |  |  |  | TOM CORRELL | DIRECTOR OF PIPELINE SAFETY | 402-398-7715 | thomas.correll@nngco.com | WE BELIEVE THAT ON APRIL 9, 2014 AT ABOUT 10:00 A 3-INCH RELIEF VALVE ON THE TXM15501-M880B PLYMOUTH TO SPRABERRY MAINLINE BEGAN VENTING GAS. THE RELIEF VALVE IS LOCATED ON MAINLINE BLOCK VALVE IDENTIFIED AS BBB01 BETWEEN TWO MAINLINES; M880B AND M883B. THE PIPELINES ARE ALSO PROTECTED BY A CONTROL VALVE WITH PRESSURE OVERRIDE AND SLAM VALVES THAT THE ATLAS PIPELINE MIDKIFF AND WEST TEXAS GAS (WTG) SONORA / BENEDUM RECEIPT POINTS. THIS IS A VERY REMOTE AND UNATTENDED LOCATION. ON APRIL 11, 2014 AT 05:30 THE RELIEF VALVE VENTING WAS IDENTIFIED BY AN ATLAS EMPLOYEE WHILE PERFORMING ROUTINE MAINTENANCE ON THEIR EQUIPMENT NEARBY. THE VENTING WAS SO SMALL THAT SCADA DID NOT DETECT ANY NOTICABLE DROP IN PRESSURES. THE NATURAL GAS VENTING OVER A 3 DAY PERIOD MADE THIS EVENT A REPORTABLE INCIDENT. THE PIPELINE HAS A 550 MAOP AND THE RELIEF VENTED AT 545 AND NEVER COMPLETELY RESET. THE CAUSE OF THE RELIEF VALVE VENTING HAS NOT BEEN DETERMINED. **UPDATE** THE DOWNSTREAM COMPRESSOR STATION (SPRABERRY) HAD CONDUCTED ITS' ANNUAL ESD TESTING AND WAS NOT COMPRESSING. DELIVERIES WERE STILL BEING MADE TO THE PIPELINE SYSTEM AND THE PRESSURE BEGAN TO RISE. FORTUNATELY, THE 30-INCH PIPELINE IS NEARLY 100 MILES LONG SO PRESSURES INCREASED SLOWLY. AS MENTIONED ABOVE, THE RELIEF WAS SET BELOW THE PIPELINE MAOP AND BEGAN TO WEEP. FURTHERMORE, THE RELIEF VALVE IS AN OLD STYLE AND DID NOT RESET IMMEDIATELY, THEREBY CAUSING GAS TO EXPEL TO ATMOSPHERE FOR SOME TIME. ***ADDITIONAL INFO*** AFTER DISCOVERY, THE RELIEF VALVE WAS TESTED AND RESET. IT IS STILL SET BELOW THE ACTUAL MAOP OF THE PIPELINE. THE MAOP IS "GRANDFATHERED". THE PIPELINE IS UNDER A SELF-IMPOSED PRESSURE RESTRICTION CONSIDERING OPERATING HISTORY AND KNOWN CORROSION. THE RELIEF WAS LAST INSPECTED AND TESTED BY MORRIS FIELD SERVICES, LLC ON MARCH 25, 2014. NORTHERN PERSONNEL WILL VERIFY SCHEDULED COMPRESSOR STATION OUTAGES AND CUSTOMER SHUT-INS DO NOT ADVERSELY AFFECT PIPELINE FLOWS. ***UPDATE***THE PIPELINE WAS NOT OPERATING UNDER A SELF-IMPOSED PRESSURE RESTRICTION. THE MAOP HAS BEEN 550 SINCE 2004. UPDATED PART E. ***MORE INFO***THE PRESSURE OVERRIDE SET POINTS FOR FLOW AND PRESSURE CONTROL VALVES WERE RESET TO SLIGHTLY UNDER MAOP. THE SLAM VALVES WERE ADJUSTED TOO. NORTHERN HAS NOT EXPERIENCED ANY FURTHER PROBLEMS OR ISSUES AT THIS RECEIPT POINT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140052 | 16971 | 2014-05-14 13:46 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2014-04-27 20:00 | 2014 |  |  | 41.9462 | -91.2248 | 1081038 | 2014-04-27 23:30 |  | NATURAL GAS |  | 198000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-04-30 13:44 | 2014-04-30 20:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2014-04-27 20:15 | 2014-04-27 23:15 | ONSHORE | IA | 52306 | MECHANICSVILLE | CEDAR | MILEPOST | 14.41 | TIPTON BRANCHLINE | IAB79501 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 4 |  | 0.156 | 35000 | API 5L - GRADE B | LONGITUDINAL ERW - LOW FREQUENCY |  | BETHLEHEM | EXTRUDED POLYEHYLENE | [28 empty] | 1964 | 1964 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 96 |  | NO | NO | NO |  | 35000 | 38715.4416722859 | 0 | 0 | 280000 | 186830.122591944 | 7700 | 8517.3971679029 | 173000 | 191364.897408727 | 0 | 0 |  |  | 495700 | 303217.928230394 | 425427.85884086 | [8 empty] | 800 |  | 960 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 11000 | NO |  | YES |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS TO SMALL TO BE DETECTED BY SCADA EQUIPMENT | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [52 empty] | LIGHTNING |  |  | DIRECT HIT |  |  | YES |  |  |  | YES | SEVERE THUNDERSTORM | [301 empty] | J. DAVID CULLISON | PIPELINE SAFETY ENGINEER | j.cullison@nngco.com | 402-398-7439 | 402-548-5267 |  |  |  | THOMAS CORRELL | SR. DIRECTOR PIPELINE SAFETY AND RISK | 402-398-7715 | thomas.correll@nngco.com | ON APRIL 27, 2014, A FARMER NEAR MECHANICSVILLE, IOWA, OBSERVED A LIGHTNING STRIKE AT APPROXIMATELY 8 P.M., THEN NOTICED A BURNING FLAME APPROXIMATELY 5-6 FEET HIGH IN A NEARBY FIELD. THE WITNESS CALLED AREA EMERGENCY RESPONDERS TO REPORT THE FIRE AND EMERGENCY RESPONDERS REPORTED TO THE SITE TO INVESTIGATE. NORTHERN NATURAL GAS' GAS CONTROL DEPARTMENT DID NOT REGISTER A PRESSURE DROP; ONCE NOTIFIED OF THE FIRE, LOCAL PERSONNEL WERE DISPATCHED TO THE SITE. ONCE LOCAL EMPLOYEES CONFIRMED THE GAS WAS COMING FROM NORTHERN NATURAL GAS' LINE, NORTHERN NATURAL GAS NOTIFIED THE NRC WAS NOTIFIED AND LOWERED PRESSURE IN THE LINE TO 80% OF THE PRESSURE AT THE TIME OF INCIDENT. UPON CONFIRMATION OF THE LOAD REQUIRED TO MAINTAIN SERVICE TO FIVE NEARBY TOWNS, PRESSURE WAS LOWERED TO 400 POUNDS. BOTTLE TRUCKS WERE BROUGHT IN AS A CONTINGENCY AND WERE USED DURING REPAIRS TO MAINTAIN SERVICE TO THE TOWNS. ONCE THE TOWNS WERE SUPPLIED BY THE BOTTLE TRUCKS, THE PRESSURE IN THE LINE WAS REDUCED TO EXTINGUISH THE FIRE AND THE SEGEMENT WAS EXCAVATED. THE SUBSEQUENT INVESTIGATION IDENTIFIED A PINHOLE-SIZED LEAK ATTRIBUTED TO AN APPARENT LIGHTNING STRIKE. THE DAMAGED PIPE WAS REPARIED BY A PRESSURIZED SLEEVE. THE PRESSURE IN THE LINE WAS RETURNED TO 80% OF THE OPERATING PRESSURE AT THE TIME OF INCIDENT, MONITORED FOR APPROXIMATELY 4 HOURS, THEN RESTORED TO NORMAL PRESSURE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140053 | 16402 | 2014-05-16 13:20 | ORIGINAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2014-04-15 06:51 | 2014 |  |  | 45.6513 | -88.3841 | 1079785 | 2014-04-15 08:30 |  | NATURAL GAS |  | 62150 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-04-15 06:55 | 2014-04-21 12:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-04-15 06:51 | 2014-04-15 06:51 | ONSHORE | WI | 54112 | GOODMAN | MARINETTE | MILEPOST | 32.6 | GOODMAN COMPRESSOR STATION |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2006 |  | CARBON STEEL |  | OTHER | [8 empty] | STATION SUCTION BLOWDOWN VALVE UNINTENTIONALLY OPENED DURING UNMANNED HOURS RESULTING IN GAS RELEASE. | CLASS 1 LOCATION | NO |  | 706 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 291500 | 194503.50262697 | 5000 | 5530.77738175513 | 0 | 0 | 0 | 0 |  |  | 296500 | 204189.385717643 | 200034.280008725 | [8 empty] | 530 |  | 975 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | NO | [306 empty] | ROBERT CADORIN | COMPLIANCE SPECIALIST | robert_cadorin@transcanada.com | 248-205-7669 |  |  |  |  | ROBERT CADORIN | COMPLIANCE SPECIALIST | 248-205-7669 | robert_cadorin@transcanada.com | ON THE MORNING OF APRIL 15, 2014, THE STATION TECHNICIAN ARRIVED AT GOODMAN COMPRESSOR STATION TO FIND GAS VENTING FROM THE STATION BLOWDOWN SILENCER. UPON FURTHER INVESTIGATION IT WAS FOUND THAT THE 8-INCH SUCTION BLOWDOWN VALVE WAS OPEN WITH NO ALARM OR SHUTDOWN INDICATION. THE 8" SUCTION BLOWDOWN VALVE VENTED THE GAS INTO THE STATION BLOWDOWN SILENCER, WHICH LIMITS NOISE AND RESTRICTS FLOW VOLUME. IN ADDITION, THE STATION SUCTION AND DISCHARGE VALVES REMAINED OPEN, AS THE STATION HAD NOT SHUT IN. THE STATION TECHNICIAN IMMEDIATELY SHUT IN THE STATION, WHICH WAS NOT OPERATING AT THE TIME, AND ISOLATED IT FROM THE PIPELINE BY CLOSING THE STATION SUCTION AND DISCHARGE VALVES. GAS CONTROL WAS THEN NOTIFIED OF THE SITUATION. INVESTIGATION FOUND THAT THE STATION SUCTION BLOWDOWN VALVE PNEUMATIC PILOT PRESSURE SWITCH HAD ACTIVATED BECAUSE WATER HAD ACCUMULATED AND FROZE IN THE SWITCH AND PILOT GAS SENSING LINES RESULTING IN A LOSS OF PRESSURE TO THE SWITCH. THE LOSS OF PILOT GAS CAUSED THE PILOT PRESSURE SWITCH TO CHANGE STATE AND TO PNEUMATICALLY COMMAND THE BLOWDOWN VALVE TO ITS FAILSAFE POSITION, WHICH IS OPEN. LIQUIDS AND ICE WERE REMOVED FROM THE AFFECTED TUBING AND SWITCH, AS WELL AS FROM SIMILAR COMPONENTS ELSEWHERE AT THE STATION, THE AFFECTED BLOWDOWN VALVE WAS TESTED, AND STATION WAS PLACED BACK INTO SERVICE THE FOLLOWING WEEK. RECOMMENDATIONS HAVE BEEN MADE TO MODIFY THE TUBING TO THE AFFECTED SWITCHES TO ELIMINATE THE ACCUMULATION OF LIQUIDS. IN ADDITION, IT HAS BEEN RECOMMENDED TO MODIFY STATION CONTROL LOGIC TO SHUT DOWN THE STATION AND CLOSE THE STATION SUCTION AND DISCHARGE VALVES WHEN ANY BLOWDOWN VALVE INDICATES OPEN AND TO ANNUNCIATE AN ALARM TO GAS CONTROL.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140054 | 16404 | 2014-05-16 16:00 | SUPPLEMENTAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 1111 LOUISIANA STREET | HOUSTON | TX | 77002 | 2014-04-27 19:58 | 2014 |  |  | 35.0951 | -92.1896 | 1081032 | 2014-04-27 20:58 |  | NATURAL GAS |  | 13041 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | MANUAL OPERATION AND VALVE MANIPULATION | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 500 | 2014-04-27 19:58 | 2014-04-27 21:11 | ONSHORE | AR | 72173 | VILONIA | FAULKNER | SURVEY STATION NO. | 932+67 | LINE BT-14 EOL AT JM-30 VILONIA INTERCONNECT |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 2002 |  | CARBON STEEL |  | OTHER | [8 empty] | TORNADO DEBRIS STRIPPED CONTROL LINES AND SMALL PIPING OFF REGULATOR STATION | CLASS 2 LOCATION | NO |  | 214 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 45600 | 30426.6199649737 | 200000 | 221231.095270205 | 5000 | 5530.77738175513 | 0 | 0 |  |  | 250600 | 135634.341568719 | 257188.492616934 | [8 empty] | 749 |  | 965 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NATURAL FORCE DAMAGE EVENT | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [52 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | TORNADO | YES |  |  | YES | [303 empty] | JIMMY CROSS | COMPLIANCE COORDINATOR | jimmy.cross@enablemidstream.com | 3184293664 | 3184293996 |  |  |  | JOHNNY CAVITT | DOT COMPLIANCE MANAGER | 3184293606 | johnny.cavitt@enablemidstream.com | ON APRIL 27TH, SYSTEM CONTROL CALLED OUT PERSONNEL TO INVESTIGATE HIGH GAS PRESSURE ALARMS RECEIVED FROM THE LINE JM-30 METERING FACILITY AT GRAVEL RIDGE, AR. GAS FLOW RATE WAS ALSO OBSERVED TO INCREASE FROM LINE J INTO LINE JM-30. SYSTEM CONTROL RECEIVED REPORTS FROM LOCAL EMERGENCY PERSONNEL THAT GAS WAS BLOWING NEAR FOXGROVE AND BOBBIT LANES IN GRAVEL RIDGE AND RESIDENTS WERE BEING EVACUATED. NEIGHBORHOOD ROADS WERE BEING CLOSED. SYSTEM CONTROL ALSO RECEIVED CALLS FROM LOCAL OPERATING PERSONNEL REPORTING TORNADO ACTIVITY NEAR MAYFLOWER, ARKANSAS. AT THE JM-30 VILONIA INTERCONNECT FACILITY, COMPANY PERSONNEL FOUND SEVERE DAMAGE TO CONTROL VALVES, METERS AND ESPECIALLY TO INSTRUMENT TUBING FROM FLYING DEBRIS CAUSED BY A TORNADO. THE INSTRUMENT / RTU BUILDING WAS DEMOLISHED. LARGE PORTIONS OF THE FACILITY FENCE WERE MISSING. ELECTRIC POWER SERVICE WAS INTERRUPTED. THE DAMAGE TO THE AREA WAS SO WIDESPREAD THAT INITIALLY OPERATIONS PERSONNEL HAD TO WALK INTO THE SITE DUE TO DEBRIS. THE DAMAGE TO THE VILONIA INTERCONNECT FACILITY DISABLED THE PRESSURE REGULATION AND CONTROL FOR THE SOUTHERN SEGMENT OF JM-30. JM-30 LINE PRESSURE HAD INCREASED AT THE END OF LINE JM-30 AT GRAVEL RIDGE UNTIL THE RELIEF VALVE OPENED TO PREVENT OVER PRESSURING OF THE METERS. NO DIRECT TORNADO DAMAGE WAS OBSERVED AT THE GRAVEL RIDGE FACILITY. HOWEVER, THE ESCAPING GAS AND WINDY CONDITIONS PROMPTED THE GRAVEL RIDGE FIRE DEPARTMENT TO MAKE EVACUATIONS AS A PRUDENT PRECAUTION TO THE SITUATION. LOCAL OPERATING PERSONNEL ARRIVED AT THE INLET TO JM-30 FROM LINE J AND WERE INSTRUCTED TO CLOSE LINE J VALVE J-6 TO REDUCE PRESSURE INTO JM-30 AND TO STOP THE RELIEVING OF GAS AT GRAVEL RIDGE. AFTER THE LINE PRESSURE DECREASED AND THE RELIEF VALVE HAD BEEN RESET, THE AREA AT GRAVEL RIDGE WAS CHECKED AND FOUND TO BE CLEAR OF GAS. THE EVACUATED GRAVEL RIDGE RESIDENTS WERE ALLOWED TO RETURN HOME AT 10:20 PM. IT WAS ESTIMATED THAT AS MANY AS 500 PEOPLE HAD BEEN EVACUATED FROM ALMOST 170 HOMES. ROADS WERE OPENED FOR TRAFFIC. OPERATIONS AND SYSTEM CONTROL PERSONNEL DEVISED A PLAN TO RESUME JM-30 OPERATIONS.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140055 | 16406 | 2014-05-20 15:10 | ORIGINAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2014-04-25 09:30 | 2014 |  |  | 30.3553 | -88.4939 | 1080803 | 2014-04-25 10:29 |  | NATURAL GAS |  | 15 | 90 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | LOWERED LINE PRESSURE WHILE REPAIRS WERE MADE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-04-25 09:30 | 2014-04-25 09:30 | ONSHORE | MS | 39581 | PASCAGOULA | JACKSON | MILEPOST | 15.85 | BAYOU CASOTTE | INDEX 300-11 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION | [19 empty] | FILLET WELD | [18 empty] | 2014 |  | CARBON STEEL |  | LEAK |  |  | OTHER | INADEQUATE FUSION OF WELD | [5 empty] | CLASS 1 LOCATION | NO |  | 249 |  | NO | NO | NO |  | 0 | 0 | 414 | 457.948367209325 | 69 | 46.0402802101576 | 78688 | 87041.1621231095 | 1142 | 1263.22955399287 | 0 | 0 |  |  | 80313 | 40791.9882863935 | 88808.3803245219 | [8 empty] | 649 |  | 902 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 2000 | NO | [5 empty] | YES | BRANCH CONNECTION | YES |  |  |  |  | YES | FABRICATED PIPING | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SMALL LEAK WAS DISCOVERED BY EMPLOYEE PERFORMING FOOT PATROL. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [8 empty] | YES | INCOMPLETE FUSION OF THE WELD | [13 empty] | YES | [62 empty] | NO | [63 empty] | YES | 2014 | 780 | NO | [13 empty] | YES |  |  |  | 2014 |  | DYE PENATRANT AFTER INCIDENT OCCURRED | 2014 |  |  |  | YES |  | YES | [50 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmp.com | 270.688.6357 | 270.688.6948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 270.688.6361 | jeff.mcmaine@bwpmlp.com | DURING LINE PATROL, TECHNICIAN DISCOVERED LEAK. IT WAS REPORTED TO MANAGEMENT, THE PRESSURE WAS LOWERED BY 20% AND PERSONNEL TOOK APPROPRIATE ACTIONS TO ISOLATE THE AREA. PLANS WERE MADE AND EXECUTED TO TO REPAIR LEAK AND LINE WAS RETURNED TO NORMAL OPERATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140056 | 16998 | 2014-05-22 17:16 | SUPPLEMENTAL FINAL | 2620 | COLUMBIA GULF TRANSMISSION, LLC | 700 LOUISIANA ST. SUITE 700 | HOUSTON | TX | 77002 | 2014-04-25 11:00 | 2014 |  |  | 32.457 | -91.4592 | 1080822 | 2014-04-25 12:00 |  | NATURAL GAS |  | 1302.91 | 16667 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-04-25 11:45 | 2014-04-27 15:20 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-04-25 11:10 | 2014-04-25 11:30 | ONSHORE | LA | 71232 | DELHI | MADISON | MILEPOST | 3.24 | ML300 | ML300 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 108 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION | [19 empty] | FILLET WELD | [18 empty] | 2009 |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 789 |  | NO | NO | NO |  | 0 | 0 | 79452 | 87886.2649070417 | 6207 | 4141.6234676007 | 203791 | 225424.530681052 | 0 | 0 | 0 | 0 |  |  | 289450 | 148111.731561314 | 317452.419055694 | [8 empty] | 811 |  | 1008 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | AUTOMATIC | 45725 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK IDENTIFIED BY OPERATIONS PERSONNEL WHILE ON-SITE. LEAK WAS OF SMALL MAGNITUDE AND WOULD NOT HAVE BEEN DETECTABLE BY SCADA. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | YES |  |  |  | YES | OTHER | PROBABLE FAILURE CRACK WAS DUE TO SETTLEMENT OF THE 2-IN PIPE SUPPORT | [15 empty] | YES | [63 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | GEORGE HAMATY | ENGINEER | ghamaty@cpg.com | (304)357-3728 |  |  |  |  | P. MICHAEL HOFFMAN | MANAGER SYSTEM INTEGRITY | 304-357-2548 | mikehoffman@cpg.com | COMPANY PERSONNEL WERE PERFORMING A REPAIR ON A GRADE 2 LEAK ON A NEARBY LINE WHEN THEY DISCOVERED A CRACK IN THE WELD OF A 2 INCH TAP ON LINE 300. THE SECTION OF LINE 300 CONTAINING THE LEAK WAS ISOLATED BETWEEN THE COMPRESSOR STATION AND VALVE 808-3; APPROXIMATELY 8.66 MILES AND THE LINE WAS BLOWN DOWN. THE TOTAL ESTIMATED AMOUNT OF UNINTENTIONAL MATERIAL THAT VENTED INTO ATMOSPHERE DURING THIS EVENT THIS LEAK DID NOT EXCEED 3,000 MCF. FURTHER EVALUATION BY THE COMPANY'S ENGINEERING AND PROJECT MANAGEMENT GROUPS DETERMINED THE COST OF REPAIR AND WORK NECESSARY TO BRING THE ISOLATED SECTION OF LINE 300 BACK INTO SERVICE, WOULD EXCEED $50,000. BASED UPON THIS DETERMINATION THE NATIONAL RESPONSE CENTER WAS NOTIFIED. OVER THE COURSE OF THE NEXT 2 DAYS, THE CRACK WAS INVESTIGATED AND REPAIRED. ON APRIL 27, THE LINE WAS PURGED AND RETURNED BACK INTO SERVICE. BASED ON VISUAL EXAMINATION, METALLURGICAL ANALYSES AND MATERIAL ANALYSES, THE METALLURGICAL FAILURE INVESTIGATION PERSONNEL CONCLUDED THAT THE LEAK WAS CAUSED BY A CRACK THROUGH THE WALL OF A 2-IN WELD-O-LET ON THE 36-INCH DIAMETER PIPE CAUSED BY FATIGUE. AS SHOWN ON PAGE 1 OF THIS REPORT, THE INITIAL INCIDENT REPORT WAS SUBMITTED ON MAY 22, 2014 AND THE ASSIGNED REPORT NUMBER WAS: 20140056 - 16407
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140058 | 16983 | 2014-05-27 23:04 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2014-04-27 09:20 | 2014 |  |  | 42.5146 | -83.3393 | 1081243 | 2014-04-29 17:48 |  | NATURAL GAS |  | 170.1 | 0 | 0.05 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | MAOP EXCEEDANCE OF APPROXIMATELY 67 MINUTES, NOT REQUIRING PIPELINE SHUTDOWN. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-04-27 09:24 | 2014-04-27 10:22 | ONSHORE | MI | 48334-2201 | FARMINGTON HILLS | OAKLAND | MILEPOST | W. WAYNE CG | WEST WAYNE CITY GATE (13 MILE AND MIDDLEBELT) | 1019 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 2010 |  | CARBON STEEL |  | OTHER | [8 empty] | OVERPRESSURE EVENT RESULTING IN MAOP EXCEEDANCE OF STEEL PIPELINE (INCLUDING 10" STEEL OPERATING AT > 20% SMYS) AND VENTING DOWNSTREAM RELIEF VALVE. | CLASS 3 LOCATION | YES | METHOD2 | 127 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 810 | 540.472854640981 | 2841 | 3142.58770831327 | 99987 | 110601.16761391 | 0 | 0 |  |  | 103638 | 52771.7177799061 | 114284.228176864 | [8 empty] | 455 |  | 340 | OTHER | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 | NO | [22 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT OCCURRED DUE TO EQUIPMENT MALFUNCTION. CONTROLLER/CONTROL ROOM ISSUES DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [25 empty] | YES | MONITOR REGULATOR FAILED DUE TO LIQUIDS IN REG, PILOTS, AND PILOT FILTER. | [161 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST I | carmella.king@cmsenergy.com | 571-788-0509 |  |  |  |  | AMANDA L. WARD | GAS REGULATORY SERVICES LEAD | 517-545-8746 | amanda.ward@cmsenergy | AT APPROXIMATELY 9:20 AM ON APRIL 27, 2014, OILY LIQUIDS CAUSED THE PRIMARY WORKER AND MONITOR REGULATORS AT WEST WAYNE CITY GATE (29380 W. 13 MILE ROAD; FARMINGTON HILLS, MI) TO FAIL. LIQUIDS WERE FOUND IN THE REGULATORS, PILOTS, AND PILOT FILTERS OF THE PRIMARY REGULATOR RUN, AS WELL AS IN AND AROUND THE CITY GATE HEATER. A WORN DIAPHRAGM WAS ALSO OBSERVED ON THE PRIMARY WORKER REGULATOR. THE DOUBLE REGULATOR FAILURE RESULTED IN AN OVERPRESSURE OF THE 340 PSIG MAOP DOWNSTREAM SYSTEM. THE OVERPRESSURE EVENT WAS ORIGINALLY IDENTIFIED VIA SCADA ALARMS BY CONSUMERS ENERGY'S GAS CONTROL AT APPROXIMATELY 9:24 AM, WHEN AN OUTLET PRESSURE OF 426 PSIG WAS MEASURED. FIELD PERSONNEL WERE DISPATCHED TO WEST WAYNE CITY GATE AT 9:25 AM. PERSONNEL ARRIVED AT 10:15 AM, AND THE DOWNSTREAM SYSTEM PRESSURE WAS REDUCED TO BELOW 340 PSIG AT 10:27 AM. THE MAX PRESSURE REACHED DURING THE OVERPRESSURE EVENT WAS 455 PSIG (134% MAOP) AT APPROXIMATELY 9:48 AM. FURTHER DOWNSTREAM OF WEST WAYNE CITY GATE, A SLUG OF LIQUIDS ALSO CAUSED A DOUBLE REGULATOR FAILURE AT A WORKER-MONITOR HIGH PRESSURE DISTRIBUTION REG STATION AT 12 MILE AND FRANKLIN ROADS, CAUSING THE MAOP OF THE MEDIUM PRESSURE SYSTEM (60 PSIG MAOP) DOWNSTREAM OF THAT FACILITY TO BE EXCEEDED AS WELL. PRESSURES ON THIS SYSTEM REACHED 104 PSIG (173% MAOP) ACCORDING TO PRESSURE RECORDING CHARTS AT 12 MILE AND FRANKLIN. THIS RESULTED IN A VENTING RELIEF VALVE AT ANOTHER NEARBY REGULATOR STAND (LOCATED AT 29257 CHATEAU COURT, FARMINGTON HILLS AND FEEDING THE SAME 60 PSIG MAOP SYSTEM) DUE TO BACKPRESSURE. THE BLOWING RELIEF WAS DISCOVERED AT 6:10 PM ON APRIL 27, AND VENTED FOR APPROXIMATELY 90 MINUTES. IN SUMMARY, THREE DOWNSTREAM SYSTEMS WERE IMPACTED BY THE OVERPRESSURE EVENT: - APPROXIMATELY 5.25 MILES OF 10" STEEL PIPING (340 PSIG MAOP) OPERATING AT > 20% SMYS (AND THEREFORE CLASSIFIED AS TRANSMISSION PIPE, THOUGH OPERATED BY GAS DISTRIBUTION) RUNNING SOUTH OF WEST WAYNE CITY GATE ALONG MIDDLEBELT ROAD TO 8 MILE ROAD - APPROXIMATELY 1.25 MILES OF 8" STEEL HIGH PRESSURE DISTRIBUTION PIPING (340 PSIG MAOP) RUNNING EAST OF WEST WAYNE CITY GATE ALONG 13 MILE ROAD AND THEN SOUTHEAST ALONG NORTHWESTERN HIGHWAY, TO REGULATOR STATION AT 12 MILE & FRANKLIN ROADS - APPROXIMATELY 87 MILES OF STEEL AND PLASTIC MEDIUM PRESSURE MAIN AS WELL AS 2,944 SERVICES (60 PSIG MAOP) IN FARMINGTON AND SOUTHFIELD TOWNSHIPS, DOWNSTREAM OF THE REGULATOR STATION AT 12 MILE & FRANKLIN ROADS MOBILE AND WALKING LEAK SURVEY WAS PERFORMED ON THE OVERPRESSURED FACILITIES BETWEEN APRIL 28TH AND APRIL 30TH. ADDITIONALLY, OVER 20 GALLONS OF LIQUIDS WERE COLLECTED FROM SURROUNDING DRIP SITES, WITH THE MAJORITY COLLECTED AT THE REGULATOR STATION AT 12 MILE & FRANKLIN. FOLLOW-UP LABORATORY ANALYSIS REVEALED THAT THE COMPOSITION OF LIQUIDS COLLECTED AT WEST WAYNE CITY GATE AND 12 MILE & FRANKLIN WAS CONSISTENT WITH COMPRESSOR ENGINE OIL UTILIZED AT CONSUMERS ENERGY COMPRESSOR STATIONS. AN PROGRAM OF ACCELERATED INSTALLATION OF FILTERS/SEPARATORS AT CONSUMERS ENERGY CITY GATE AND REGULATOR STATION FACILITIES IS CURRENTLY UNDERWAY TO HELP PREVENT RECURRENCE OF SIMILAR DAMAGE BY DEBRIS/LIQUIDS TO REGULATORS AND OVERPRESSURE PROTECTION DEVICES.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140059 | 16413 | 2014-05-29 11:10 | ORIGINAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2014-05-03 11:38 | 2014 |  |  | 37.7447 | -95.4674 | 1081650 | 2014-05-03 13:41 |  | NATURAL GAS |  | 17115 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | A FAILED RELIEF VALVE BLEW. THE RELIEF WAS CLOSED AND MONITORED. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-05-03 11:38 | 2014-05-03 13:12 | ONSHORE | KS | 66748 | PETROLIA | ALLEN |  |  | YJ | FT. SCOTT LINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1966 |  | CARBON STEEL |  | OTHER | [8 empty] | INADVERTANT RELEASE FROM A RELIEF VALVE. | CLASS 1 LOCATION | NO |  | 187 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 76504 | 51047.3274956217 | 119000 | 131632.501685772 | 0 | 0 | 0 | 0 |  |  | 195504 | 113345.873950304 | 182679.829181394 | [8 empty] | 370 |  | 450 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES |  | YES | [6 empty] | YES | 1 | 0 | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | RELIEF VALVE FAILURE. EXCESSIVE GAS LOSS DUE TO VALVE BEING OVERSIZED. | [161 empty] | DAVID COOMES | PIPELINE COMPLIANCE ENGINEER | david.coomes@sscgp.com | [5 empty] | DAVID SINCLAIR | PIPLEINE COMPLIANCE MANAGER | 270.852.4424 | david.sinclair@sscgp.com | GAS CONTROL RECEIVED FIRST ALARM AT 11:38 ON 5/3/2014 SHOWING PRESSURE DROPPED 17 PSI IN 1.5 MINUTES AND THEN BEGAN TO SLOWLY CLIMB. A SECOND ALARM CAME IN AT 12:00 THAT SHOWED PRESSURE WAS RAPIDLY DROPPING. A THIRD ALARM CAM IN AT 12:06 WITH PRESSURES TRENDING AT 30 PSI BELOW NORMAL. GAS CONTROL CONTACTED THE MEASUREMENT TECHNICIAN AT 12:15 AND WAS NOTIFIED OF AN ETA OF 90 MINUTES. ON CALL PERSONEL WERE NOTIFIED AT 12:39 WHO IMMEDIATELY CALLED THE CLOSEST OPERATOR. PSAP AND ALLEN COUNTY SHERIFF WERE NOTIFIED AT 12:42. OPERATIONS WERE ON SCENE AT 13:12 AND NOTIFIED GAS CONTROL OF THE RELIEF VALVE BLOWING. THE RELIEF WAS SHUT-IN AND MONITORED AT THIS TIME UNTIL MEASUREMENT COULD ARRIVE TO SERVICE THE RELIEF VALVE. THE RELIEF VALVE WAS REPLACED AND BACK IN SERVICE BY 22:46 ON 5/3/2014.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140061 | 16597 | 2014-06-04 10:13 | SUPPLEMENTAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2014-05-07 11:35 | 2014 |  |  | 29.995 | -93.9896 | 1082036 | 2014-05-07 14:20 |  | NATURAL GAS |  | 1890 | 3780 | 7 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-05-07 12:10 | 2014-05-07 16:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-05-07 14:00 | 2014-05-07 14:00 | ONSHORE | TX | 77627 | NEDERLAND | JEFFERSON | MILEPOST | MLV #1 | TEXOMA, 30" PIG RECEIVER | ACCOUNT 3080 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | OTHER | TEMPORARY PIPING |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | TEMPORARY PIPING FOR PIGGING | 2014 |  | CARBON STEEL |  | LEAK |  |  | OTHER | MECHANICAL FITTING | [5 empty] | CLASS 1 LOCATION | NO |  | 594 |  | NO | NO | NO |  | 0 | 0 | 17877 | 19774.7414507273 | 8469 | 5650.94395796848 | 0 | 0 | 7500 | 8296.1660726327 | 75000 | 82961.660726327 | ENVIRONMENTAL CLEANUP |  | 108846 | 56825.4688170545 | 116683.512207655 | [8 empty] | 824 |  | 973 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 42976 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DUE TO THE NATURE OF INCIDENT, THE ONGOING INVESTIGATION DOES NOT INCLUDE ANY CONTROL ROOM ISSUES | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | WRONG EQUIPMENT SPECIFIED OR INSTALLED | INCORRECT OPERATION | INCORRECT EQUIPMENT | [204 empty] | WRONG EQUIPMENT SPECIFIED OR INSTALLED | [6 empty] | YES | CONTRACTOR FAILED TO FOLLOW DESIGN BY INSTALLING INFERIOR FITTINGS, TO TEMPORARY PIPING, DURING DEWATERING PROCESS. | OTHER MAINTENANCE | NO | [150 empty] | DANNY NICHOLS | DIRECTOR OF REGULATORY COMPLIANCE | danny.nichols@energytransfer.com | 7139897232 | 7139891188 |  |  |  | DANNY NICHOLS | DIRECTOR OF REGULATORY COMPLIANCE | 7139897232 | danny.nichols@energytransfer.com | AT APPROXIMATELY 11:35 AM ON 5/7/2014, DURING AN INTEGRITY ASSESSMENT ON THE ENERGY TRANSFER ACCT: 3080 TEXOMA 30" PIPELINE, A TEMPORARY FILTER VESSEL WAS INSTALLED TO FILTER PIPELINE PIGGING PARTICULATES. AN UNEXPECTED GAS RELEASE, FROM ONE OF ITS INTERCONNECTING PIPING SEGMENTS, RESULTED IN THIS INCIDENT. THE ROOT CAUSE OF THIS INCIDENT IS STILL UNDER INVESTIGATION. DAMAGES ATTRIBUTED TO THIS INCIDENT ARE PRIMARILY ASSOCIATED WITH ENVIRONMENTAL CLEANUP. EVACUATION WAS LIMITED TO FACILITY PERSONNEL ONLY, DURING INITIAL RELEASE. THIS PIPELINE IS IDENTIFIED AS SYSTEM ID: 530737, TEXOMA 30" (SUNOCO-HWY 69), WITHIN THE TRRC'S DATABASE AND WAS REPORTED RESPECTFULLY. UPDATE DEC. 22, 2014: A ROOT CAUSE ANALYSIS OF THE TEXOMA 3080 INCIDENT WAS COMPLETED AND DETERMINED THAT THE TEMPORARY PIPING, PROVIDED BY THIRD PARTY VENDOR, DID NOT MEET SPECIFICATIONS FOR INTENDED WORK. THE RESULTING CAUSE OF THE INCIDENT WAS THE FAILURE OF THE SERIES 4170 WEBSTONE 4' 600 WOG BRASS BALL VALVES INSTALLED IN THE AUXILIARY PIPING SYSTEM. ALTHOUGH THE CASTING OF THE VALVE BODY IDENTIFIES THE VALVE IS RATED FOR 600 PSI WOG SMALL PRINT IN THE VALVE LITERATURE STATES THAT 4" SERIES 4170 WEBSTONE VALVES ARE ONLY RATED AT 400 PSI WOG.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140062 | 17369 | 2014-06-06 16:22 | SUPPLEMENTAL FINAL | 2620 | COLUMBIA GULF TRANSMISSION, LLC | 700 LOUISIANA ST. SUITE 700 | HOUSTON | TX | 77002 | 2014-05-10 09:14 | 2014 |  |  | 34.9619 | -88.4191 | 1082348 | 2014-05-10 09:57 |  | NATURAL GAS |  | 25228 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE CS WAS NOT SHUTDOWN SINCE IT WAS ALREADY SHUTDOWN | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-05-10 07:00 | 2014-05-10 07:00 | ONSHORE | MS | 38834 | CORINTH | ALCORN | MILEPOST | 5SG-33 | CORINTH COMPRESSOR STATION | CORINTH COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1954 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE ACTUATED UNINTENTIONALLY. | CLASS 3 LOCATION | NO |  | 634 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 119076 | 79453.5131348511 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 119076 | 82373.064798599 | 79453.5131348511 | [8 empty] | 902 |  | 1008 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA WAS WORKING AT THE TIME OF THE GAS RELEASE. GAS CONTROL RECEIVED NO ALERTS OR ALARMS. THERE WAS NO PRESSURE CHANGE DETECTABLE BY GAS CONTROL. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | RV PRESSURE SENSING LINE IN WRONG LOCATION FOR PARTICULAR OPERATIONAL MODE | [161 empty] | GEORGE HAMATY | ENGINEER | george_hamaty@transcanada.com | (304) 357-3728 |  |  |  |  | LEE ROMACK | MANAGER US REGULATORY COMPLIANCE | (832) 320-5315 | lee_romack@transcanada.com | ON MAY 10TH, 2014, A COLUMBIA GULF TRANSMISSION, LLC (COLUMBIA) CORINTH COMPRESSOR STATION (CS) PERSONNEL ARRIVED ON SITE AND NOTICED THAT A RELIEF VALVE (RV) WAS UNINTENTIONALLY RELIEVING A MINUTE AMOUNT OF NATURAL GAS INTO ATMOSPHERE. THE COLUMBIA PERSONNEL INVESTIGATED THE AREA AND ISOLATED THE RV FOR FURTHER INVESTIGATION INTO THE REASON BEHIND THIS UNINTENDED RELEASE. AFTER ENGAGING ENGINEERING PERSONNEL INTO THE INVESTIGATION, IT WAS IDENTIFIED THAT AT THE TIME THE CS WAS REMOTELY SHUTDOWN, ALL BLOWDOWN VALVES FUNCTIONED AS THEY WERE DESIGNED TO. HOWEVER THE SUBJECT RV WAS MODULATING THE FLOW AND ACTING SIMILAR TO A REGULATOR VALVE RATHER THAN A RV. IT WAS IDENTIFIED THAT THE PRESSURE DIFFERENTIAL WAS SO MINUTE TO AN EXTENT THAT IT ALLOWED TO UNSEAT THE VALVE AND UNINTENTIONALLY RELEASING MATERIAL INTO ATMOSPHERE. THE PILOT CONTROL PRESSURE WAS NOT REQUIRED TO BE INSTALLED ON THE UPSTREAM SIDE OF THE INSTALLATION OF THE CS UNIT SUCTION HEADER. HENCE, IT WAS RELOCATED AND A RECONFIGURATION TO SUCH INSTALLATION WAS EXECUTED ALONG THIS FACILITY. FURTHERMORE, A RECOMMENDED APPROACH WAS SHARED AMONG OTHER CS WITH SIMILAR INSTALLATIONS TO INSPECT AND RELOCATE THE PILOT CONTROLS SENSORS TO AVOID SIMILAR SITUATIONS THAT MAY LEAD TO SIMILAR EVENTS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140064 | 17116 | 2014-06-11 12:15 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION LP (SPECTRA ENERGY CORP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2014-05-16 11:15 | 2014 |  |  | 39.9163 | -79.9576 | 1082994 | 2014-05-16 13:00 |  | NATURAL GAS |  | 1 | 28480 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-05-16 14:59 | 2014-05-24 12:46 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2014-05-16 11:15 | 2014-05-16 11:15 | ONSHORE | PA | 15320 | CARMICHAEL | GREENE | MILEPOST | 751.61 | LINE 10 | HOLBROOK DISCHARGE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 144 |  | YES |  |  |  |  | YES | CASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 |  | 0.375 | 52000 | API-5L X-52 | DSAW |  | NATIONAL TUBE | COAL TAR | [28 empty] | 1952 | 1952 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 602 |  | NO | NO | NO |  | 6300 | 6968.77950101146 | 137560 | 152162.747326847 | 6 | 4.00350262697023 | 180137 | 199259.529043445 | 0 | 0 | 0 | 0 |  |  | 324003 | 164515.102062724 | 358395.05937393 | [8 empty] | 846 |  | 936 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 86328 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE TO THE PIPE WAS CAUSED BY EVENTS AT THE INCIDENT SITE WHICH COMPANY PERSONNEL PRESENT AT THE TIME KNEW WERE NOT RELATED TO CONTROLLER ACTIVITY. | [12 empty] | YES | 7 | 0 | NO |  |  | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | [204 empty] | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | [5 empty] | YES |  |  | OTHER MAINTENANCE | NO | [150 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | deteschendorf@spectraenergy.com | 713-627-5573 | 713-386-4468 |  |  |  | RICK KIVELA | DIRECTOR OF OPERATIONAL COMPLIANCE | 713-627-6388 | rwkivela@spectraenergy.com | A SPECTRA ENERGY WELDER WAS REMOVING A PORTION OF ROAD CASING ENCIRCLING THE 30-INCH CARRIER PIPE USING A HOT CUT METHOD WHEN A PIN HOLE LEAK OCCURRED DUE TO THE TORCH COMING IN CONTACT WITH TH CARRIER PIPE. NATURAL GAS WAS RELEASED THROUGH THE PIN HOLE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140065 | 16517 | 2014-06-13 10:22 | SUPPLEMENTAL FINAL | 840 | MOJAVE PIPELINE OPERATING COMPANY | 1001 LOUISIANA STREET | HOUSTON | TX | 77002-5089 | 2014-05-20 10:45 | 2014 |  |  | 34.4881 | -115.4767 | 1083378 | 2014-05-20 14:22 |  | NATURAL GAS |  | 18725 | 0.03 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-05-20 10:50 | 2014-05-20 11:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-05-20 10:45 | 2014-05-20 10:45 | ONSHORE | CA | 92277 | CADIZ | SAN BERNARDINO | MILEPOST | 209 | LINE 1903 | 209 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | DRAIN LINES | [38 empty] | 2014 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 262 |  | NO | NO | NO |  | 0 | 0 | 1 | 1.10615547635103 | 73963 | 49351.8441330998 | 100 | 110.615547635103 | 0 | 0 | 0 | 0 |  |  | 74064 | 51216.5809330025 | 49463.5658362113 | [8 empty] | 643 |  | 1000 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS FROM A BROKEN PIPE NIPPLE FOUND BY LOCAL EMPLOYEES PERFORMING VALVE MAINTENANCE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | PIPE NIPPLE |  |  |  |  | YES | [177 empty] | WILLIAM MARTIN MULLER | COORDINATOR-OPS SR II | martin_muller@kindermorgan.com | 205 325 3863 | 205 325 3508 |  |  |  | REJI GEORGE | DIRECTOR OF ENGINEERING COMPLIANCE CODES | 713 420 5433 | reji_george@kindermorgan.com | TWO KINDER MORGAN (MOJAVE) TECHNICIANS PERFORMING VALVE MAINTENANCE ARRIVED AT CADIZ METER STATION AT 10:45 AM; TECHNICIANS DISCOVERED 1/2-INCH PIPE NIPPLE HAD BROKEN THUS LEAKING NATURAL GAS; TECHNICIANS CONTACTED GAS CONTROL AT 10:55 AM AND BEGAN ISOLATING METER STATION; WITH METER STATION ISOLATED AT 11:05 AM, BROKEN PIPE NIPPLE WAS REMOVED AND 1/2-INCH PLUG WAS INSTALLED; TECHNICIANS RETURNED METER STATION TO SERVICE AT 11:30 AM; THE 1/2-INCH PIPE NIPPLE HAD BEEN INSTALLED TO HOLD AN OPTIONAL 1/2-INCH BALL VALVE WHICH WAS CLOSED AND PLUGGED; NO OTHER APPURTENANCES WERE ATTACHED. TECHNICIANS WERE ON SITE FOR OTHER REASONS, THEREFORE NO COST FOR EMERGENCY RESPONSE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140066 | 16524 | 2014-06-13 17:08 | SUPPLEMENTAL FINAL | 5304 | FLORIDA GAS TRANSMISSION CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2014-05-17 06:07 | 2014 |  |  | 28.463 | -80.7773 | 1083061 | 2014-05-17 08:00 |  | NATURAL GAS |  | 39797 | 3268 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-05-17 07:10 | 2014-10-21 13:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 6 | 2014-05-17 06:30 | 2014-05-17 06:55 | ONSHORE | FL | 32927 | PORT ST. JOHN | BREVARD | MILEPOST | 30.7 | FLBQA - 8" OUC LATERAL | VALVE SECTION 18-41E | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 8.625 |  | 0.203 | 52000 | API 5LX | LONGITUDINAL ERW - LOW FREQUENCY |  | LONESTAR | COAL TAR | [28 empty] | 1962 | 1962 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 118 | 21 |  | CLASS 1 LOCATION | NO |  | 186 |  | NO | NO | NO |  | 0 | 0 | 14722 | 16284.8209228398 | 179285 | 119627.99474606 | 8000 | 8849.24381080821 | 12000 | 13273.8657162123 | 1280000 | 1415879.00972931 | RETURN TO SERVICE COSTS. |  | 1494007 | 791579.853649003 | 1573914.93492523 | [8 empty] | 938 |  | 975 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 17533 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PRESSURE DID NOT EXCEED MAOP. | [12 empty] | YES | 1 | 0 | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) |  | YES | [13 empty] | YES | SKELP | [13 empty] | YES | SKELP | [55 empty] | YES | YES |  |  | YES |  |  |  | 2012 | [31 empty] | 2012 | [23 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | NATHAN HLAVATY | DIRECTOR - REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 7138575479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - REGULATORY COMPLIANCE | 7138575479 | nathan.hlavaty@energytransfer.com | THE 8" DIAMETER FLBQA-8 RUPTURED AT MP 30.7 AT ABOUT 6:00AM EST ON MAY 17, 2014. THE MAOP OF THE SEGMENT IS 975 PSIG, THE ESTIMATED PRESSURE AT THE TIME OF THE FAILURE WAS 938 PSIG. THERE WAS NO IGNITION OF THE ESCAPING GAS. NO INJURIES OR PROPERTY DAMAGE OCCURED. THE SEGMENT CONTAINING THE FAILURE WAS ISOLATED AND BLOWN FLAT. FOLLOWING THE FAILURE, FGT PERSONNEL SHUT IN AND ISOLATED THE SEGMENT BY CLOSING THE UPSTREAM LATERAL BLOCK VALVE, THE DOWNSTREAM LATERAL BLOCK VALVE AND FOUR CROSSOVER VALVES. THERE WERE NO INTERRUPTIONS TO CUSTOMERS BEING SERVED IN THIS AREA DUE TO PARALLEL PIPELINES. THE SUPPLEMENTAL REPORT SUBMITTED ON 07/17/14, CORRECTED THE LONGITUDE LOCATION ENTRY, CORRECTED THE HEADQUARTER ADDRESS, UPDATED THE PART D: 7(D) ESTIMATED OTHER COSTS, AND UPDATED THE PART G5: CAUSE, BASED ON THE METALLURGICAL ANALYSIS REPORT. THE SUPPLEMENTAL/FINAL INCLUDES THE UPDATES BASED ON THE RETURN TO SERVICE PLAN.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140067 | 16729 | 2014-06-17 05:47 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2014-05-19 16:45 | 2014 |  |  | 36.1614 | -97.3893 | 1083286 | 2014-05-19 18:16 |  | NATURAL GAS |  | 0 | 5161 | 0.5 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-05-20 11:28 | 2014-05-22 23:26 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-05-17 18:48 | 2014-05-17 22:21 | ONSHORE | OK | 73073 | Not Within a Municipality | NOBLE COUNTY | SURVEY STATION NO. | 210/-2972+86 | LINE V | OKLAHOMA DILWORTH | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.25 | 33000 | NON-STANDARD | FLASH WELDED |  | A.O. SMITH | COAL TAR | [28 empty] | 1930 | 1930 | CARBON STEEL |  | LEAK |  |  | OTHER | A PIT THAT PENETRATED THE WALL | [5 empty] | CLASS 1 LOCATION | NO |  | 336 |  | NO | NO | NO |  | 42000 | 46458.5300067431 | 27821 | 30774.3515075619 | 0 | 0 | 151000 | 167029.476929005 | 0 | 0 | 0 | 0 |  |  | 220821 | 112122.867835469 | 244262.35844331 | [8 empty] | 586 |  | 594 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 68814 | NO | [5 empty] | YES | COUPLED PIPELINE | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1930 | YES | YES |  |  | YES |  |  |  | 2011 |  | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DAVID COOMES | PIPELINE COMPLIANCE ENGINEER | david.coomes@sscgp.com | 2708524391 |  |  |  |  | DAVID SINCLAIR | PIPELINE COMPLIANCE MANAGER | 270-852-4124 | david.l.sinclair@sscgp.com | SSCGP GAS CONTROL RECEIVED A CALL FROM A THIRD PARTY AT 18:48 ON 5/17/2014 STATING THERE WAS AN OIL PATCH WITH AN AUDIBLE LEAK AND A SECOND NOTIFICATION FROM A LAND OWNER AT 19:11. ON-CALL PERSONAL WERE CONTACTED AND EDMOND OPERATIONS WERE ABLE TO BE NOTIFIED BY 17:23. AT 22:21 OPERATIONS NOTIFIED THAT THERE WAS NOT BLOWING GAS BUT A LEAK COULD BE DETECTED OVER AN OILY PATCH. SSCGP LINE IS ADJACENT TO AN OIL LINE WITH AN UNKNOWN OPERATOR. THE SITE WAS CONSIDERED WAS AWAY FROM ALL ROADS AND HOUSES AND UNTIL THE OIL LINE OPERATOR COULD BE CONTACTED SSCGP PERSONNEL DECIDED TO WAIT TO EXCAVATE THE LINE. ON 5/18/2014 A PRESSURE REDUCTION OF 20% WAS PUT IN PLACE WHILE AN OPERATOR FOR THE OIL LINE WAS TRACKED DOWN TO HELP WITH CONTAINMENT OF THE OIL. AFTER NO OPERATOR COULD BE FOUND, SSCGP BEGAN EXCAVATION ON 5/19/2014. AS EXCAVATION BEGAN IT WAS DETERMINED THAT THE OIL MAY HAVE BEEN FROM THE SSCGP LINE AND IT WAS DECIDED TO BLOW-DOWN THE LINE SO A PERMANENT REPAIR OF THE LEAK AND OIL CLEAN UP COULD BE DONE. GAS FLOW WAS DETERMINED TO BE SHUT IN ON 5/20/14 AT 11:28 AM.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140068 | 16523 | 2014-06-24 09:49 | SUPPLEMENTAL FINAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2014-05-26 23:05 | 2014 |  |  | 29.3996 | -96.1293 | 1083982 | 2014-05-27 00:57 |  | NATURAL GAS |  | 10311 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | STATION WAS IDLE AT THE TIME OF THE INCIDENT. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-05-26 23:05 | 2014-05-26 23:05 | ONSHORE | TX | 77488 | HUNGERFORD | WHARTON |  |  | GULF COAST LINE | COMPRESSOR STATION 301 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1990 |  | CARBON STEEL |  | OTHER | [8 empty] | ACTUACTOR CONTROL FAILED TO CLOSE VALVE. | CLASS 1 LOCATION | NO |  | 729 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 50000 | 33362.5218914186 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 50000 | 34588.4413309982 | 33362.5218914186 | [8 empty] | 688 |  | 900 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | YES | NO | NOT MANDATED | [20 empty] | TRANSMISSION SYSTEM | YES | YES | NO | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM HAD LOST COMMUNICATION AT THE TIME OF THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | UNIT DISCHARGE ISOLATION VALVE | [22 empty] | YES | UNIT DISCHARGE VALVE ACTUATOR DID NOT FUNCTION PROPERLY | [161 empty] | ZACHARY RAGAIN | ENGINEER - PIPELINE | zachary_ragain@kindermorgan.com | 713-420-6633 |  |  |  |  | ZACHARY RAGAIN | ENGINEER - PIPELINE | 713-420-6633 | zachary_ragain@kindermorgan.com | LIGHTING TRIPPED A BREAKER, CAUSING A LOSS OF STATION AIR SUPPLY. THE LOSS OF AIR SUPPLY ALLOWED A FAIL OPEN ACTUATOR TO OPERATE AND VENT THE NATURAL GAS FROM A COMPRESSOR UNIT AS DESIGNED. THE EXCESSIVE RELEASE OF NATURAL GAS WAS CAUSED BY THE 12" UNIT DISCHARGE VALVE NOT BEING 100% CLOSED. THE ROOT CAUSE OF UNIT DISCHARGE VALVE NOT BEING CLOSED WAS INADEQUATE PROCEDURES FOR PERFORMING THE STATION ANNUAL ESD TEST. THIS STATION HAS NOT BEEN IN OPERATION FOR SEVERAL YEARS, BUT IS HOOKED TO THE PIPELINE AND IS TESTED ANNUALLY. IN THE STEPS OF THE PROCEDURE, IT WAS WORDED AS "UNIT DISCHARGE VALVES SHOULD CLOSE". THE UNIT DISCHARGE VALVES ARE ACTUATED. AT THE LAST ANNUAL ESD TEST PRIOR TO THIS INCIDENT, THE ACTUATOR FAILED TO CLOSE THE VALVE 100%. THE ANNUAL ESD TEST PROCEDURE WAS WRITTEN DURING A TIME PERIOD WHEN THE STATION WAS RUNNING, AND IF A UNIT DESHARGE VALVE WAS NOT CLOSED IT WOULD BEEN KNOWN IMMEDIATELY. SINCE THE STATION IS NOT RUNNING IT WAS NOT VERIFIED AS CLOSED AT THE LAST ANNUAL ESD TEST. A STEP WAS ADDED TO THE PROCEDURE WORDED - "VERIFY EACH UNIT DESHARGE VALVE IS CLOSED" TO MAKE SURE THIS ISSUE DOES NOT ARISE IN THE FUTURE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140069 | 16770 | 2014-06-25 23:40 | SUPPLEMENTAL FINAL | 21252 | VIKING GAS TRANSMISSION CO | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2014-05-26 06:18 | 2014 |  |  | 48.2386 | -96.8271 | 1083928 | 2014-05-26 08:11 |  | NATURAL GAS |  | 66500 | 13500 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-05-26 08:41 | 2014-05-28 18:29 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2014-05-26 06:23 | 2014-05-26 06:47 | ONSHORE | MN | 56762 | WARREN | MARSHALL | SURVEY STATION NO. | 489+06 | 2201-1 | MLV 2203 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 |  | YES |  |  |  |  | YES | UNCASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 |  | 0.281 | 52000 | API 5LX | DSAW |  | CONSOLIDATED WESTERN | COLD APPLIED TAPE | [28 empty] | 1960 | 1959 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 468 | 24 |  | CLASS 1 LOCATION | NO |  | 490 |  | NO | NO | NO |  | 0 | 0 | 60750 | 67198.9451883248 | 299250 | 199674.69352014 | 265779 | 293992.896349099 | 1000 | 1106.15547635103 | 0 | 0 |  |  | 626779 | 373316.161891986 | 561972.690533915 | [8 empty] | 828 |  | 877 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | MANUAL | 106128 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED |  | YES | [15 empty] | HYDROGEN STRESS CRACKING | [12 empty] | YES | CRACK OCCURRED IN AN HARD SPOT WITH HARDNESS MEASURED 30 - 46 ROCKWELL C. CRACK APPEARED TO ORIGINATE IN A SMALL SURFACE CORROSION PIT. SURFACE DISCOLORATION SUGGESTED COATING DISBONDMENT. | [55 empty] | YES | YES | [6 empty] | 2001 | [55 empty] | YES | 1960 | 1069 | Yes, but the point of the Accident was not identified as a dig site |  | 2001 | [11 empty] | NO | [63 empty] | PAT VAUGHAN | MANAGER REGULATORY COMPLIANCE | pat.vaughan@oneok.com | 918 588 7734 | 918 732 1311 |  |  |  | WESLEY R. DUNBAR | VICE PRESIDENT | 918 588 7424 | wesley.dunbar@oneok.com | THE VIKING GAS TRANSMISSION PIPELINE 2201-1 RUPTURED AND IGNITED AT APPROXIMATELY 0618 HOURS ON MAY 26, 2014. GAS CONTROL DISPATCHED VIKING OPERATIONS PERSONNEL. THE RUPTURE WAS VERIFIED BY ON SITE VIKING PERSONNEL AT 0647 HOURS. LOCAL LAW ENFORCEMENT AND FIRE DEPARTMENTS RESPONDED AND ISOLATED THE AREA FROM TRAFFIC. THERE WERE NO INJURIES OR DEATHS. PHMSA AND MNOPS WERE NOTIFIED OF THE INCIDENT WITH NRC NUMBER 1083928 AND MNOPS INCIDENT NUMBER 141932. MEDIA FROM GRAND FORKS WERE ON SCENE. THE SEGMENT OF PIPE WHERE THE FAILURE OCCURRED WAS COMPLETELY ISOLATED AT 0841 HOURS. THE COMMUNITIES OF WARREN AND ARGYLE LOST NATURAL GAS SERVICE IMPACTING APPROXIMATELY 900 CUSTOMERS. ON MAY 28, 2014, THE PIPELINE SEGMENT WAS REPAIRED AND RESTORED TO 80 PERCENT OF THE OPERATING PRESSURE AT THE TIME OF FAILURE. THE RUPTURED PIPE SEGMENT WAS SENT TO KIEFNER AND ASSOCIATES IN OHIO FOR FAILURE ANALYSIS. A FINAL INCIDENT REPORT WILL BE FILED ONCE THE FAILURE ANALYSIS IS COMPLETED. UPDATE - METALLURGICAL TESTING DETERMINED THAT THE FAILURE WAS DUE TO ENVIRONMENTAL (HYDROGEN INDUCED) CRACKING WHICH OCCURRED IN A LOCALIZED (3.5 INCHES X 4.4 INCHES) HARD SPOT (30-46 RC) IN THE PIPE WALL. UPDATE - CORRECTED NRC REPORT NUMBER
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140070 | 16895 | 2014-06-30 14:31 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2014-06-05 08:15 | 2014 |  |  | 41.6465 | -93.674 | 1084957 | 2014-06-05 12:30 |  | NATURAL GAS |  | 6392 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-06-05 14:53 | 2014-09-07 12:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-06-05 08:15 | 2014-06-05 08:50 | ONSHORE | IA | 50310 | DES MOINES | POLK | SURVEY STATION NO. | 2777 | DES MOINES 1A METER STATION | 736000 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2014 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE VENTED DUE TO THE SET POINT HAVING BEEN CHANGED DURING THE INSTALLATION OF THE RELIEF VALVE. | CLASS 3 LOCATION | NO |  | 79 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 29873 | 19932.7723292469 | 0 | 0 | 4356 | 4818.41325498507 | 0 | 0 |  |  | 34229 | 22876.9889843208 | 24751.185584232 | [8 empty] | 140 |  | 178 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT DID NOT OCCUR DUE TO OPERATIONS, THE INCIDENT OCCURED DUE TO THE NEW INSTALLATION OF A RELIEF VALVE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | RELIEF SET POINT HAD BEEN LOWERED NON-INTENTIONALLY DURING CONSTRUCTION | [161 empty] | JEFFREY CULLISON | PIPELINE SAFETY ENGINEER | j.cullison@nngco.com | 402-398-7439 |  |  |  |  | THOMAS CORRELL | SR. DIRECTOR OF PIPELINE SAFETY AND RISK | 402-398-7715 | thomas.correll@nngco.com | DURING A CONSTRUCTION PROJECT TO REPLACE A RELIEF VALVE, THE NEW VALVE VENTED APPROXIMATELY 6.4 MMCF IN NATURAL GAS. THE INVESTIGATION CONCLUDED THAT THERE WAS GAS SEEPAGE BY THE CONTROL VALVES THAT CAUSED THE DOWNSTREAM PRESSURE TO REACH 130 PSIG, RESULTING IN THE ACTIVATION OF THE NEW RELIEF VALVE. THIS BUILDUP IN PRESSURE WAS CONCLUDED TO OCCUR BETWEEN THE FIVE MINUTE SCANS BEFORE 0820 HOURS ON JUNE 5, 2014. IT WAS CONCLUDED THAT THE SEATS ON THE CONTROL VALVES WERE THE CAUSE OF THE VALVES NOT HOLDING, WHICH HAVE SINCE BEEN REPLACED. ADDITIONAL OUTSIDE CONDITIONS MAY HAVE CONTRIBUTED TO THE EVENT, BUT ARE NOT THE ROOT CAUSE. DURING THE INSTALLATION OF A RELIEF STACK TO THE NEW RELIEF VALVE, VIBRATION OF THE INSTALLATION MAY HAVE ADJUSTED THE SET POINT OF THE RELIEF VALVE. IT WAS CONCLUDED THAT THE VIBRATION OF THE RELIEF VALVE POPPING OPEN AND CLOSED DID WALK THE SET SCREW OUT FROM 0820 TO 1100 HOURS WHEN THE INVESTIGATIVE TEAM HEARD A DISTINCTIVE SOUND DIFFERENCE IN THE RELIEF VALVE VENTING. AFTER THE SOUND OF GAS VENTING CHANGED, A TECHNICIAN NOTICED THE SET SCREW FOR THE RELIEF VALVE ON THE GROUND AT 1100 HOURS. THE INVESTIGATIVE TEAM RE-INSERTED THE SET SCREW AND REPAIRED THE CONTROL VALVES BEFORE RETURNING THE DELIVERY POINT BACK INTO SERVICE.
2021-02-26 10:37 | YES | YES | GT (Gas Transmission) | 20140071 | 16460 | 2014-06-30 14:48 | SUPPLEMENTAL FINAL | 31968 | WTG GAS TRANSMISSION COMPANY | 211 NORTH COLORADO | MIDLAND | TX | 79701 | 2014-06-01 19:45 | 2014 |  |  | 32.2204 | -102.1047 | 1084567 | 2014-06-01 21:45 |  | NATURAL GAS |  | 0 | 906.6 | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | NO | [5 empty] | 0 |  | YES |  | 2014-06-01 22:05 | 2014-06-03 14:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-06-01 21:35 | 2014-06-01 22:05 | ONSHORE | TX | 79701 | MIDLAND | MARTIN | MILEPOST |  | SNYDER MAINLINE | MARTIN COUNTY 3 COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | DRAIN LINES | [38 empty] | 2013 |  | CARBON STEEL |  | OTHER | [8 empty] | COMPRESSOR BLOW DOWN VENT PIPING WAS CONNECTED BY THREADED FITTINGS. DURING AN INTENTIONAL BLOW DOWN OF THE COMPRESSOR, A THREADED CONNECTION BETWEEN A STRAIGHT RUN OF PIPE AND A 90 DEGREE FAILED. | CLASS 1 LOCATION | NO |  | 235 |  | NO | NO | NO |  | 0 | 0 | 4570 | 5055.13052692419 | 0 | 0 | 1400 | 1548.61766689144 | 2000 | 2212.31095270205 | 0 | 0 |  |  | 7970 | 4046.80377612947 | 8816.05914651768 | [8 empty] | 525 |  | 800 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT OCCURRED DURING A MAINTENANCE ACTIVITY. THE CONTROL ROOM DID NOT HAVE A ROLE WITH THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | THREADED FITTING | [6 empty] | YES | [175 empty] | RAY RED | DIRECTOR OF INTEGRITY MANAGEMENT | rreed@westtexasgas.com | 806.358.1321 | 806.354.0797 |  |  |  | BART BEAN | OPERATIONS MANAGER | 432.682.4349 | bbean@westtexasgas.com | WTG GAS TRANSMISSION COMPANY WAS IN THE PROCESS OF DE-PRESSURING COMPRESSOR UNIT #7 TO PERFORM MAINTENANCE ON THE UNIT. AN EMPLOYEE BEGAN OPENING THE 2' BLOW-DOWN, RELEASING GAS TO THE ATMOSPHERE. DURING THE VENTING PROCESS, A SCREWED FITTING SEPARATED, WITH A PART OF THE LOOSE VENT PIPING FATALLY STRIKING THE EMPLOYEE. THE VENT VALVE WAS CLOSED SECURING THE RELEASE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140072 | 17035 | 2014-07-01 16:39 | SUPPLEMENTAL FINAL | 32262 | PAA NATURAL GAS STORAGE, LLC | 333 CLAY STREET, SUITE 1500 | HOUSTON | TX | 77002 | 2014-06-03 13:00 | 2014 |  |  | 42.8152 | -82.821 | 1084738 | 2014-06-03 15:19 |  | NATURAL GAS |  | 3964 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-06-03 13:00 | 2014-06-25 14:00 |  |  |  |  | NO |  |  |  |  | YES | [6 empty] | 0 | 2014-06-03 13:00 | 2014-06-03 13:30 | ONSHORE | MI | 48062 | RICHMOND TOWNSHIP | MACOMB | MILEPOST | 2300 LINE | BLUEWATER | 20" MARYSVILLE TO RAY | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 42 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.267 | 80000 | API 5LX 17THED | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | OTHER | ENCOR. | [27 empty] | 1972 | 1972 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 120 | 15 |  | CLASS 2 LOCATION | NO |  | 428 |  | NO | NO | NO |  | 25000 | 27653.8869087757 | 0 | 0 | 45000 | 30026.2697022767 | 250000 | 276538.869087756 | 5000 | 5530.77738175513 | 0 | 0 |  |  | 325000 | 173300.871641594 | 339749.803080564 | [8 empty] | 750 |  | 960 | OTHER | UNKNOWN. |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | REMOTELY CONTROLLED | 69168 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | YES |  |  | YES | PRIVATE LANDOWNER | [7 empty] | CONTRACTOR | TRENCHER | AGRICULTURE | YES | 41492654 |  | UTILITY OWNER | NO | NO | YES | 96 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | EXCAVATION PRACTICES NOT SUFFICIENT (OTHER) | [263 empty] | CHRYSTAH CARTER | COMPLIANCE SPECIALIST | crcarter@paalp.com | 7139935080 | 7136464310 |  |  |  | THOMAS MCLANE | SR DIR ENVIRONMENTAL AND REGULATORY COMPLIANCE | 7136464109 | tjmclane@paalp.com | APPROXIMATELY 3,964 MCF WERE RELEASED WHEN A THIRD PARTY CONTRACTOR HIT AND RUPTURED A 20-INCH TRANSMISSION PIPELINE, WHILE OPERATING A TILE TRENCHER. THROUGH THE 8-1-1 DIG ALERT SYSTEM, THE CONTRACTOR NOTIFIED BLUEWATER GAS STORAGE, LLC ON MAY 29TH THAT THEY WERE GOING TO BEGIN EXCAVATION ON WEDNESDAY, JUNE 4TH BUT BEGAN EARLY ON TUESDAY, JUNE 3RD, BEFORE BLUEWATER HAD AN OPPORTUNITY TO MARK THE LINES. BLUEWATER OPERATORS OBSERVED THE LINE PRESSURE DROPPING AND ISOLATED THE SEGMENT OF PIPELINE. THE SEGMENT WAS REPLACED AND EXCAVATION WAS BACK-FILLED. THE LINE IS NOW AVAILABLE FOR SERVICE. THE MISS DIG SYSTEM WAS CALLED AND ASSIGNED TICKET NUMBER B41492654. THE NATIONAL RESPONSE CENTER (NRC) WAS ALSO CONTACTED AND ASSIGNED REPORT NUMBER 1084738. SUPPLEMENTAL NARRATIVE: THIS REPORT WAS UPDATED PER INSTRUCTIONS RECEIVED FROM KYLE FRISKE WITH THE STATE OF MICHIGAN.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140073 | 17029 | 2014-07-02 09:18 | SUPPLEMENTAL FINAL | 32262 | PAA NATURAL GAS STORAGE, LLC | 333 CLAY STREET, SUITE 1500 | HOUSTON | TX | 77002 | 2014-06-07 18:30 | 2014 |  |  | 42.765 | -82.8671 | 1085180 | 2014-06-07 21:55 |  | NATURAL GAS |  | 2484 | 3864 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-06-07 19:00 | 2014-10-30 10:30 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 0 | 2014-06-07 18:30 | 2014-06-07 19:00 | ONSHORE | MI | 48096 | RAY TOWNSHIP | MACOMB | MILEPOST | VECTOR/MICHCO | BLUEWATER | INTERCONNECT | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 42 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.375 | 60000 | API 5L X-60 | LONGITUDINAL ERW - HIGH FREQUENCY |  | PIONEER STEEL AND TUBE CORP | EPOXY | [28 empty] | 2008 | 2008 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 96 | 180 |  | CLASS 2 LOCATION | NO |  | 463 |  | NO | NO | NO |  | 10000 | 11061.5547635103 | 15456 | 17096.7390424815 | 10000 | 6672.50437828371 | 4300000 | 4756468.54830941 | 10000 | 11061.5547635103 | 0 | 0 |  |  | 4345456 | 2208265.20546108 | 4802360.9012572 | [8 empty] | 450 |  | 1125 | OTHER | UNKNOWN. |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | REMOTELY CONTROLLED | 69168 | NO |  |  | YES |  |  | YES | STATION PIPING, NOT PIGABLE | YES |  |  |  |  | YES | STATION PIPING | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 5 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | THE COMBINATION OF AIR AND GAS RESULTED IN INTERNAL DETONATION. | YES |  |  |  |  | COMMISSIONING | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | CHRYSTAH CARTER | COMPLIANCE SPECIALIST | crcarter@paalp.com | 7139935080 | 7136464310 |  |  |  | THOMAS MCLANE | SR DIR OF ENVIRONMENTAL AND REGULATORY COMPLIANCE | 7136464109 | tjmclane@paalp.com | APPROXIMATELY 2,484 MCF OF NATURAL GAS WERE RELEASED DUE TO A RUPTURE OF UNDERGROUND, COMPRESSOR STATION PIPING, WHILE PURGING. BLUEWATER GAS STORAGE, LLC OPERATORS REMOTELY SHUT-IN THE STATION. PERSONNEL ARRIVED ON SITE TO ASSESS DAMAGE AND PROPERLY ISOLATE THE STATION FOR CLEAN-UP AND REPAIRS. THE INCIDENT IS STILL UNDER INVESTIGATION TO DETERMINE THE ROOT CAUSE OF THE FAILURE. PIECES OF THE PIPING HAVE BEEN SENT FOR METALLURGICAL ANALYSIS. A SUPPLEMENTAL REPORT WILL BE SUBMITTED ONCE THE LAB RESULTS ARE RECEIVED. THE NATIONAL RESPONSE CENTER WAS NOTIFIED AND ASSIGNED REPORT NUMBER 1085180. SUPPLEMENTAL NARRATIVE: BASED ON THE RESULTS OF THE METALLURGICAL ANALYSIS, PLAINS HAS CONCLUDED THAT THE FAILURE WAS THE RESULT OF INTERNAL DETONATION THAT RESULTED IN SUDDEN OVER-PRESSURE OF THE PIPING AND OTHER COMPONENTS. AIR MOVERS HAD BEEN USED TO DE-ENERGIZE A PREVIOUSLY DAMAGED SECTION OF PIPELINE PRIOR TO THE INCIDENT OF JUNE 7, 2014. AS THE PIPELINE WAS BROUGHT BACK INTO SERVICE, THE AIR WAS DISPLACED BY FLOWING PIPELINE GAS TO AND THROUGH THE VECTOR STATION TO A SILENCER EQUIPPED VENT AT THE BOOSTER STATION. THIS WAS DONE TO MINIMIZE NOISE AND DISTURBANCE TO NEARBY RESIDENCES AND LIVESTOCK. IT APPEARS THAT THE AIR HAD NOT BEEN COMPLETELY ELIMINATED FROM ALL OF THE PIPING DURING THE STATION PURGING. AS THE VECTOR STATION WAS BEING PRESSURIZED TO THE NORMAL OPERATING CONDITIONS (PIPELINE PRESSURE), THE HEAT OF COMPRESSION COMBINED WITH THE RESIDUAL AIR INCREASED THE TEMPERATURE OF THE GAS TO AUTO IGNITE. THE SUBSEQUENT IGNITION OF THE FLAMMABLE GAS RESULTED IN A DETONATION/OVERPRESSURE INSIDE THE PIPE. THE PURGING PROCEDURES FOR THE PNGS PIPELINE AND THE BOOSTER STATION HAVE BEEN MODIFIED TO ADDRESS THE REMOVAL OF ALL AIR/OXYGEN FROM THE PIPELINE AND THE BOOSTER STATION EQUIPMENT PRIOR TO THE EQUIPMENTS RETURN TO SERVICE, WITH PARTICULAR ATTENTION FOCUSED IN ELIMINATING AIR FROM DEAD LEGS OF PIPING AND EQUIPMENT. THE STATION PIPING HAS BEEN REPLACED AND THE FACILITY WAS RESTARTED ON OCTOBER 28, 2014. THIS REPORT WAS UPDATED BASED ON INSTRUCTIONS RECEIVED FROM KYLE FRISKE WITH THE STATE OF MICHIGAN.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140074 | 16873 | 2014-07-15 09:52 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2014-06-15 07:58 | 2014 |  |  | 39.4805 | -80.5383 | 1085958 | 2014-06-15 08:45 |  | NATURAL GAS |  | 4664 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | OTHER THAN UNIT #1, SMITHFIELD C/S REMAINED IN ITS INTENDED SERVICE STATE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-06-15 02:20 | 2014-06-15 02:20 | ONSHORE | WV | 26437 | SMITHFIELD | WETZEL COUNTY | MILEPOST | RV-1 | SMITHFIELD COMPRESSOR STATION | UNIT NO. 1 DISCHARGE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | UNKNOWN |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL | OTHER | [8 empty] | FAILURE IN PILOT LINE CAUSED RELIEF VALVE TO OPEN. | CLASS 1 LOCATION | NO |  | 147 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 22429 | 14965.7600700525 | 500 | 553.077738175513 | 200 | 221.231095270205 | 0 | 0 |  |  | 23129 | 15871.1111983684 | 15740.0689034983 | [8 empty] | 895 |  | 920 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS CLEARLY A LOCALIZED EVENT OVER WHICH THE CONTROLLERS HAD NO INFLUENCE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [13 empty] | YES |  | YES | [175 empty] | GEORGE HAMATY | ENGINEER | ghamaty@cpg.com | (304) 357-3728 |  |  |  |  | MICHAEL HOFFMAN | MANAGER | 304-357-2548 | mikehoffman@cpg.com | ON JUNE 15, 2014 AT 01:07 EASTERN STANDARD TIME, UNIT NO. 1 FAULTED AND BEGAN SHUTTING DOWN A COMPRESSOR STATION (CS) FACILITY. THE CS FACILITY IS OPERATED AND MAINTAINED BY COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA) LOCATED IN WETZEL COUNTY, WV. COLUMBIA'S GAS CONTROL PERSONNEL NOTIFIED THE CS OPERATOR TO INVESTIGATE THIS EVENT. UPON ARRIVAL, THE CS OPERATOR OBSERVED GAS VENTING BEHIND THE CS BUILDING. THE GAS DETECTORS FOR UNIT #1 WERE ACTIVE INDICATING PRESENCE OF NATURAL GAS. UNIT #1 DISCHARGE RELIEF VALVE (RV) WAS FOUND TO BE VENTING. THE RV HAD VENTED FOR 77 MINUTES WITH GAS LOST ESTIMATED AT 4,664 MSCF. FURTHER INVESTIGATION BY THE CS OPERATOR SUPPORTED BY THE MEASUREMENT AND REGULATION MECHANIC IDENTIFIED THAT THE TUBING CONNECTING THE PILOT TO THE MAIN BODY OF THE RELIEF VALVE HAD CRACKED AND FAILED. THE TUBING WAS REPLACED AND THE UNIT WAS RETURNED TO OPERATION. THE UNIT WAS THEN TAKEN BACK OUT OF OPERATION BECAUSE OF OBSERVED MOVEMENT OF THE RV DUE TO UNUSUALLY HIGH VIBRATION. INVESTIGATION INTO THIS INCIDENT BY THE ENGINEERING DEPARTMENT, IDENTIFIED THAT EXCESSIVE VIBRATION INITIATED THE SEPARATION OF THE SENSING LINE THAT ACTIVATED THIS RV. INSUFFICIENT PIPE SUPPORT WITH THE OPERATING CONDITIONS OF THE ENGINES, ASSISTED IN ELEVATING THE VIBRATION LEVELS WITHIN THE FACILITY. A CORRECTIVE ACTION WAS TAKEN WHERE BASED ON THE EXPERIMENTAL DATA COLLECTED BY ENGINEERING SERVICES, IT WAS DETERMINED THE RVS WILL BE REMOVED AND ELECTRONIC SHUT DOWN DEVICES WILL BE INSTALLED TO PREVENT REOCCURRENCE OF THE RELIEF VALVE TUBING FAILURES. THIS ACTION WAS IMPLEMENTED ON UNITS NO. 1 AND 2. PIPELINE SUPPORTS WERE INSTALLED WITH A CLOSE MONITORING TO SMALL DIAMETER (SENSING LINES) WITHIN THE CS FACILITY WITH A CONSIDERATION TO PULSATION STUDY TO RECIPROCATING UNITS IN A CS IN PARTICULAR TO ABOVE GRADE PIPELINES. NO FURTHER ISSUES WERE NOTED IN THIS FACILITY AFTER THE CORRECTIVE ACTIONS WERE IMPLEMENTED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140075 | 16489 | 2014-07-15 10:12 | SUPPLEMENTAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2014-06-17 09:45 | 2014 |  |  | 30.1757 | -91.6032 | 1086163 | 2014-06-17 10:46 |  | NATURAL GAS |  | 1 | 177 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-06-18 12:30 | 2014-08-24 10:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-06-17 09:45 | 2014-06-17 09:45 | ONSHORE | LA | 70582 | CATAHOULA | ST. MARTIN | MILEPOST | 11.688 | SOUTH SECTION 28 PIPELINE |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1948 |  | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | UNKNOWN (SEE NARRATIVE) | [5 empty] | CLASS 1 LOCATION | NO |  | 447 |  | NO | NO | NO |  | 0 | 0 | 771 | 852.845872266641 | 90 | 60.0525394045534 | 1010000 | 1117217.03111454 | 4000 | 4424.6219054041 | 0 | 0 |  |  | 1014861 | 515316.853260478 | 1122554.55143161 | [8 empty] | 885 |  | 1085 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 1800 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATING PRESSURES WERE NEVER ABOVE MAOP OR OUTSIDE NORMAL OPERATING LIMITS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [5 empty] | YES | [29 empty] | YES | CHECK VALVE LEAKING AT O-RING DUE TO WEAR OR LOOSE CAP. | [161 empty] | KENNETH C PETERS | SR. ENGINEER CODES AND STANDARDS | ken_peters@kindermorgan.com | 2053257554 | 2053253508 |  |  |  | REJI GEORGE | DIRECTOR CODES AND STANDARDS | 7134205433 | reji_george@kindermorgan.com | AT 9:45 AM ON JUNE 17, 2014, A LEAK WAS DISCOVERED ON SOUTHERN NATURAL GAS COMPANY'S 20-INCH SOUTH SECTION 28 PIPELINE. THE LEAK IS LOCATED IN THE ATCHAFALAYA BASIN, ST. MARTIN PARISH, LOUISIANA, AND IS LOCATED IN A LAND LOCKED POND APPROXIMATELY 750 FEET FROM BAYOU L'EMBARRAS. TECHNICIANS WERE AT THE LOCATION, PERFORMING VALVE MAINTENANCE, WHEN THEY NOTICED BUBBLES COMING FROM THE WATER BENEATH THE PLATFORM WHERE A 20-INCH MAIN LINE VALVE OPERATOR IS LOCATED. THE LEAK WAS ISOLATED AND THE PIPING WAS DEPRESSURIZED. EXCAVATION TO EXPOSE THE LEAK SITE WAS DIFFICULT DUE TO THE FACILITY'S DEPTH AND THE PRESENCE OF WATER. AFTER A COFFER DAM WAS CONSTRUCTED IN ORDER TO GAIN ACCESS, THE LEAK WAS FOUND TO BE COMING FROM AROUND THE O-RING IN A CHECK VALVE IMMEDIATELY UPSTREAM OF THE MAIN LINE VALVE. THE LEAKING CHECK VALVE WAS REPAIRED AND THE LINE WAS PLACED BACK INTO SERVICE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140076 | 16458 | 2014-07-18 09:21 | ORIGINAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 4720 PIEDMONT ROW DR. | CHARLOTTE | NC | 28210 | 2014-02-03 17:42 | 2014 |  |  | 34.6409 | -79.0736 | 1072916 | 2014-02-03 22:50 |  | NATURAL GAS |  | 6700 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-02-04 05:02 | 2014-02-04 12:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-02-03 17:42 | 2014-02-03 18:15 | ONSHORE | NC | 28360-0458 | LUMBERTON | ROBESON |  |  | SERVICE LINE OFF LINE 87 | N/A | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | YES |  |  |  |  | YES | UNCASED | [16 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 4.5 |  | 0.188 | 35000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | EPOXY | [29 empty] | 1986 | CARBON STEEL |  | MECHANICAL PUNCTURE | 8 | 3 | [7 empty] | CLASS 3 LOCATION | YES | METHOD2 | 85 |  | NO | NO | NO |  | 14738 | 16302.5194104614 | 0 | 0 | 24000 | 16014.0105078809 | 10342 | 11439.8599364223 | 31919 | 35307.3766496484 | 0 | 0 |  |  | 80999 | 45543.9535246513 | 79063.766504413 | [8 empty] | 575 |  | 704 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 150 | NO |  |  | YES | YES |  |  |  | YES |  |  | YES |  | YES | SMALL DIAMETER MEANS LIMITED TOOLS | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATING PARAMETERS WERE ALL NORMAL | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | NO | YES | STATE HIGHWAY | [9 empty] | UTILITY | BORING | TELECOMMUNICATIONS | YES | 140133224 |  | UTILITY OWNER | YES | YES | YES | 17 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO VERIFY LOCATION BY TEST-HOLD (POT-HOLING) | [263 empty] | ROB FRIESEN | PRINCIPAL ENGINEER | robert.friesen@piedmontng.com | 704-731-4113 |  |  |  |  | NEIL MOSER | DIRECTOR - OPERATIONS COMPLIANCE AND PERFORMANCE | 704-731-4351 | neil.moser@piedmontng.com | CONTRACTOR CALLED FOR CLEARANCES. FACILITIES WERE LOCATED. SINCE IT WAS A HIGH PRESSURE FACLITY A STANDBY WAS SCHEDULED. CONTRACTOR ELECTED TO PROCEED THE DAY BEFORE THE SCHEDULED STANDBY AND ALSO ELECTED TO CROSS THE LINE WITHOUT EXPOSING IT. CONTRACTOR BORED INTO THE SIDE OF THE LINE. OPERATOR RESPONDED WITH MAKE SAFE, REPAIR, RESTORATION OF SERVICE AND CLEANUP ACTIVITIES AS REQUIRED. OPERATOR NOTIFIED NATIONAL RESPONSE CENTER AT TIME OF INCIDENT DUE TO PRELIMINARY REPORT OF AN INJURY. THERE WAS NO REPORTABLE INJURY. OPERATOR DID NOT FILE INCIDENT REPORT AT THE TIME BECAUSE IT WAS NOT BELIEVED ANY OTHER REPORTING CRITERIA WAS MET. DURING CALCULATION OF PROPERTY DAMAGES IN ORDER TO BILL CONTRACTOR, OPERATOR DISCOVERED TOTAL PROPERTY DAMAGE DID EXCEED THE $50,000 REPORTING THRESHOLD.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140077 | 16459 | 2014-07-19 13:05 | ORIGINAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2014-06-20 10:15 | 2014 |  |  | 28.5306 | -90.98 | 1086531 | 2014-06-20 12:10 |  | NATURAL GAS |  | 1200 | 35000 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-06-20 10:15 | 2014-06-28 17:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-06-20 10:15 | 2014-06-20 11:30 | OFFSHORE | [28 empty] | 95 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SHIP SHOAL | 207 | PLATFORM | INTERSTATE | OFFSHORE PLATFORM, INCLUDING PLATFORM-MOUNTED EQUIPMENT AND PIPING | SCRAPER/PIG TRAP | [40 empty] | CARBON STEEL |  | OTHER | [8 empty] | UNINTENTIONAL PRESSURIZING OF PIG TRAP CAUSED TRAP VENT VALVE ASSEMBLY TO BREAK OFF. | CLASS 1 LOCATION | NO |  | 668 |  | NO | NO | NO |  | 0 | 0 | 158550 | 175380.950775455 | 5440 | 3629.84238178634 | 250000 | 276538.869087756 | 0 | 0 | 0 | 0 |  |  | 413990 | 211206.344466712 | 455549.662244998 | [8 empty] | 860 |  | 1350 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT, WHICH WAS LOCAL IN NATURE AND CONTROLLED AT THE POINT OF RELEASE, WAS CAUSED BY THIRD PARTY PERSONNEL WHICH DID NOT AFFECT FACILITIES THAT COULD BE DIRECTLY MONITORED OR OPERATED BY CONTROLLERS. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | SEE PART H - NARRATIVE DESCRIPTION OF THE INCIDENT |  |  |  | YES | UNAUTHORIZED OPERATION | OTHER MAINTENANCE | YES | NO, THEY WERE NOT QUALIFIED FOR THE TASK(S) NOR WERE THEY PERFORMING THE TASK(S) UNDER THE DIRECTION AND OBSERVATION OF A QUALIFIED INDIVIDUAL | [149 empty] | ROBERT CADORIN | REGIONAL COMPLIANCE SPECIALIST | robert_cadorin@transcanada.com | 248-205-7669 | 248-205-5369 |  |  |  | ROBERT CADORIN | REGIONAL COMPLIANCE SPECIALIST | 248-205-7669 | robert_cadorin@transcanada.com | ON JUNE 20, 2014, PRODUCER PERSONNEL NOT UNDER THE DIRECT SUPERVISION OF ANR PERSONNEL WERE IN THE PROCESS OF REMOVING A PORTION OF THE MEASUREMENT PIPING FACILITIES ON THE OFFSHORE SHIP SHOAL 207 PLATFORM TO COMPLY WITH CERTAIN REQUIREMENTS STIPULATED BY THE DOI/BSEE. THE PRODUCER WAS TO REMOVE TWO METER RUNS. THE VALVES AT THE ENDS OF EACH METER RUN HAD BEEN CLOSED AND LOCKED AT SOME EARLIER DATE BY ANR PERSONNEL. AT THE TIME OF PLANNED FACILITY DISCONNECTION AND REMOVAL, THE PRODUCER PERSONNEL DETERMINED THAT THE METER RUN ISOLATION VALVES WERE LEAKING AND DECIDED TO ISOLATE ADDITIONAL PIPING ON THE PLATFORM IN ORDER TO ASSURE THAT NO GAS COULD MIGRATE TO THE MEASUREMENT PIPING. TO FACILITATE THIS ADDITIONAL ISOLATION ACTIVITY, WHICH WAS NOT PART OF THE PROJECT SCOPE AND HAD NOT BEEN AUTHORIZED BY ANR MANAGEMENT, PRODUCER PERSONNEL CLOSED VALVES TO GAS SOURCES, OPENED THE PIG TRAP KICKER LINE VALVE, AND THEN OPENED THE 4' PIG TRAP VENT VALVE THROUGH WHICH THIS ISOLATED PIPING WAS EVACUATED. AS THE PIPING AND PIG TRAP WERE BLOWING DOWN, IT WAS DETERMINED THAT THE PRESSURE IN THE PIG TRAP AND ASSOCIATED PIPING WOULD NOT DROP TO ATMOSPHERIC. PRODUCER PERSONNEL PRESUMED THAT ONE OF THE VALVES THEY HAD CLOSED TO ISOLATED THE PIPING FROM A GAS SOURCE MUST NOT HAVE COMPLETELY CLOSED. IT WAS DECIDED TO ATTEMPT TO FURTHER CLOSE THE VALVE. HOWEVER, RATHER THAN USING THE HAND PUMP TO OPERATE THE VALVE, PRODUCER PERSONNEL USED THE POWER GAS OPERATOR AND MISTAKENLY PARTLY OPENED THE VALVE. THIS ALLOWED HIGH PRESSURE GAS (APPROXIMATELY 860 PSIG) TO ENTER THE PARTIALLY BLOWN DOWN PIPING WITH A HIGH DIFFERENTIAL PRESSURE ACROSS THE OPENED VENT VALVE. IT SHOULD BE NOTED THAT THE PIG TRAP VENT ASSEMBLY, WHICH WAS MOUNTED AT THE 12 O'CLOCK POSITION ON THE TRAP BOTTLE, INCLUDED A VENT STACK THAT WAS CONFIGURED WITH A 90 DEGREE BEND INTENDED TO VENT GAS AWAY FROM THE PLATFORM. DUE TO THE SUDDEN INCREASE IN GAS PRESSURE AND FLOW THROUGH THE VENT VALVE ASSEMBLY AND THE RESULTANT HIGH VELOCITY GAS EXITING THE 90 DEGREE VENT STACK, ENOUGH FORCE WAS PRODUCED TO CAUSE THE ENTIRE VENT ASSEMBLY TO FAIL AND DISCONNECT NEAR THE PIG TRAP BOTTLE. FOLLOWING THE FAILURE, THE VENT VALVE ASSEMBLY HAS BEEN REBUILT AND REINSTALLED ON THE PIG TRAP. THE SYSTEM WAS THEN PLACED BACK INTO SERVICE ON JUNE 28, 2014.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140078 | 31479 | 2014-07-25 13:49 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2014-07-01 07:45 | 2014 |  |  | 39.4805 | -80.5383 | 1087669 | 2014-07-01 11:43 |  | NATURAL GAS |  | 3731 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-07-01 06:45 | 2014-07-01 08:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-07-01 05:18 | 2014-07-01 06:20 | ONSHORE | WV | 26437 | SMITHFIELD | WETZEL | MILEPOST | CS LOT | SMITHFIELD COMPRESSOR STATION | SMITHFIELD COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | ESD SYSTEM | UNKNOWN |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | ESD SYSTEM | OTHER | [8 empty] | UNINTENDED GAS RELEASE FROM ESD SYSTEM | CLASS 1 LOCATION | NO |  | 100 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 16963 | 11318.5691768827 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 16963 | 11734.4746059545 | 11318.5691768827 | [8 empty] | 628 |  | 920 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | UNIT CONTROL PANEL ISSUE, UNINTENDED ACTIVATION OF AN ESD SYSTEM. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | CONTROL SYSTEM WIRING ERROR CAUSED STATION COMPRESSED AIR SYSTEM PRESSURE TO SLOWLY DECLINE CAUSING ESD SYSTEM TO ACTIVATE DUE TO SHUNT FAULT TRIP IN COMPRESSOR CONTROL PANEL. |  |  | YES |  |  | OTHER MAINTENANCE | NO | [150 empty] | ROBERT PRICE | COMPLIANCE SPECIALIST | bob_price@transcanada.com | 304.357.2339 |  |  |  |  | GEORGE HAMATY | US REGULATORY COMPLIANCE MANAGER EAST | 304.357.3728 | george_hamaty@transcanada.com | ON JULY 1, 2014, A COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA) COMPRESSOR STATION (CS) LOCATED IN WETZEL COUNTY, WV UNDERWENT AN UNINTENDED RELEASE OF NATURAL GAS. THE CS IS SMITHFIELD, A TRANSMISSION FACILITY THAT IS OPERATED AND MAINTAINED BY COLUMBIA. THE FACILITY WAS SUBJECT TO AN EMERGENCY SHUTDOWN (ESD) DUE TO AN INADVERTENT ACTIVATION OF A SWITCH ON THE STATION CONTROL PANEL. THIS TOOK PLACE WHEN AN ELECTRICIAN WAS PERFORMING AN UPDATE TO THE PANEL. TRIPPING THE ESD SYSTEM, WITH AN EMERGENCY VALVE STUCK IN THE OPEN POSITION, LEADING TO AN UNINTENTIONAL RELEASE OF NATURAL GAS THAT VENTED INTO ATMOSPHERE. AN INSPECTION IDENTIFIED THE PROBABLE CAUSE LEADING TO THIS REPORTABLE INCIDENT WAS THE INADVERTENT ACTIVATION OF THE ESD. A DETAILED INVESTIGATION REVEALED THE INADVERTENT ACTIVATION OF THE ESD WAS CAUSED BY TWO APPARENT FACTORS. THERE WAS AN INTERRUPTION TO THE CONTROL CIRCUIT TO THE STATION AIR PRESSURE TRANSMITTER CAUSED BY AN ELECTRICAL CONTRACTOR WORKING IN THE STATION AIR COMPRESSOR CONTROL PANEL. A WIRE WAS INCORRECTLY REMOVED BETWEEN THE AIR PRESSURE TRANSMITTER AND THE PROGRAMMABLE LOGIC CONTROLLER CAUSING A LOSS OF PRESSURE DATA TO THE COMPRESSOR STATION CONTROL PANEL. DUE TO THE LOSS OF A PRESSURE READING, THE COMPRESSOR STATION AIR COMPRESSORS DID NOT OPERATE ALLOWING THE STATION AIR PRESSURE TO SLOWLY DECLINE TRIGGERING THE STATION ESD SYSTEM TO OPERATE. LOSS OF THE PILOT AIR PRESSURE CAUSED THE VENT VALVES TO PARTIALLY OR FULLY OPEN WITHOUT THE ESD BLOCK VALVES CHANGING POSITION AS DESIGNED. LEARNINGS FROM THIS INCIDENT INCLUDE HAVING STATION PERSONNEL CLOSELY REVIEW ANY FAULTS ON THE STATION CONTROL PANEL BEFORE CLEARING A STATION ALARM. ANY FAULTS OBSERVED WILL BE FULLY INVESTIGATED. STATION AIR PRESSURE SHOULD BE ROUTINELY CHECKED AND RECORDED. IN ADDITION, CERTAIN STATION FAULTS SHOULD NOT BE ALLOWED TO BE CLEARED WITHOUT A CAUSE OF THE FAULT BEING CORRECTED. FOR PART E, #1 ESTIMATED PRESSURE AT THE POINT AND TIME OF THE INCIDENT, THERE WERE TWO PRESSURES DUE TO THE VALVES VENTING INTO ATMOSPHERE. THE PRESSURES WERE 628 PSIG AND 836 PSIG.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140079 | 16462 | 2014-07-28 10:54 | ORIGINAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2014-06-30 10:20 | 2014 |  |  | 32.3356 | -88.2856 | 1087614 | 2014-06-30 18:20 |  | NATURAL GAS |  | 48546 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | [7 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-06-30 10:05 | 2014-06-30 10:05 | ONSHORE | AL | 36922 | YORK | SUMTER | MILEPOST | MILEPOST 102 | YORK COMPRESSOR STATION |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [8 empty] | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE RELEASE | CLASS 1 LOCATION | NO |  | 47 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 209719 | 139935.094570928 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 209719 | 145077.066549912 | 139935.094570928 | [8 empty] | 550 |  | 1200 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | WEAR & TEAR FAILURE OF PILOT SEAT | [161 empty] | ZACHARY RAGAIN | ENGINEER - PIPELINE | zachary_ragain@kindermorgan.com | 713-420-6633 |  |  |  |  | ZACHARY RAGAIN | ENGINEER - PIPELINE | 713-420-6633 | zachary_ragain@kindermorgan.com | UPON ARRIVING ON JUNE 30TH AT APPROXIMATELY 10AM CENTRAL TIME TO PERFORM DAILY COMPRESSOR STATION OPERATOR DUTIES AT THE YORK COMPRESSOR STATION, AN OPERATIONS SPECIALIST DISCOVERED THAT THE PRIMARY FUEL GAS RELIEF VALVE WAS VENTING GAS. AFTER APPROXIMATELY 5 MINUTES, THE SPECIALIST WAS ABLE TO STOP THE VENTING BUT DID NOT INFORM SUPERVISION OF THE ABNORMAL OPERATING CONDITION. THE OPERATIONS SPECIALIST, THINKING THAT THE REPORTABLE GAS LOSS FROM THE TIME HE NOTED IT UNTIL THE TIME HE ADDRESSED IT WAS UNDER THE PHMSA LIMIT OF 3000 MCF, DID NOT REPORT THE EVENT TO SUPERVISION. SEPARATELY, AND ALSO ON THE MORNING OF JUNE 30TH, THE MEASUREMENT TECHNICIAN RESPONSIBLE FOR THE YORK FUEL GAS METER RECEIVED A CALL FROM DATA INTEGRITY INFORMING HIM THAT THE DIFFERENTIAL PRESSURE TRANSMITTER FOR THE YORK FUEL GAS METER HAD OVER-RANGED OVER THE WEEKEND AND NEEDED TO BE INVESTIGATED. THE MEASUREMENT TECHNICIAN DROVE TO THE YORK C/S, ARRIVING AT 13:30 PM, BUT DID NOT FIND ANYTHING OUT OF THE ORDINARY. FURTHER INVESTIGATION AND DISCUSSION WITH DATA INTEGRITY, AS WELL AS A REVIEW OF SCADA DATA, DETERMINED THAT THE RELIEF VALVE HAD BEGUN VENTING ON FRIDAY, JUNE 27TH AT APPROXIMATELY 11 PM AND CONTINUED UNTIL THE OPERATIONS SPECIALIST ADDRESSED IT ON MONDAY, JUNE 30TH AT 10AM. IT WAS DETERMINED TO BE REPORTABLE AT 17:45 PM ON JUNE 30, 2014. EXAMINATION OF THE RELIEF VALVE AND REGULATOR DETERMINED THAT THE REGULATOR PILOT SEAT HAD BECOME WORN TO THE POINT WHERE IT ALLOWED GAS TO SEEP PAST IT UNTIL PRESSURE BUILT UP HIGH ENOUGH TO LIFT THE RELIEF VALVE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140080 | 16913 | 2014-07-28 13:01 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2014-07-02 14:12 | 2014 |  |  | 41.8837 | -75.1423 | 1087876 | 2014-07-02 16:05 |  | NATURAL GAS |  | 8038 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-07-02 14:12 | 2014-07-02 14:16 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-07-02 14:12 | 2014-07-02 14:12 | ONSHORE | NY | 12760 | LONG EDDY | SULLIVAN COUNTY | MILEPOST | ESD VALVE | HANCOCK COMPRESSOR STATION | 7C4174 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | ESD SYSTEM | 2013 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | ESD SYSTEM | OTHER | [8 empty] | UNINTENDED GAS RELEASE FROM A RELIEF VALVE AFTER ESD SYSTEM ACTIVATION. | CLASS 1 LOCATION | NO |  | 215 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 36545 | 24384.6672504378 | 0 | 0 | 0 | 0 | 0 | 0 | NOT APPLICABLE |  | 36545 | 25280.6917688266 | 24384.6672504378 | [8 empty] | 905 |  | 1350 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LOCALIZED EVENT AT THE COMPRESSOR STATION AND THERE WAS NO INDICATION TO ANY ONSITE OR REMOTE MANIPULATION TO ANY CONTROLS THAT MAY HAVE LED OR CONTRIBUTED TO THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | YES |  |  | YES | YES | LOSS OF COMMERCIAL POWER | [11 empty] | YES | [5 empty] | YES | [167 empty] | GEORGE HAMATY | ENGINEER | ghamaty@cpg.com | (304) 357-3728 | (304) 357-3522 |  |  |  | PERRY M. HOFFMAN | MANAGER - SYSTEM INTEGRITY | (304) 357-2548 | mikehoffman@cpg.com | ON JULY 2, 2014, A MILLENNIUM COMPANY COMPRESSOR STATION (CS) LOCATED IN SULLIVAN COUNTY, NY WAS SUBJECT TO AN UN-INTENDED RELEASE OF NATURAL GAS (MATERIAL). THE CS IS HANCOCK, A TRANSMISSION FACILITY THAT IS OPERATED AND MAINTAINED BY COLUMBIA GAS TRANSMISSION, LLC. (COLUMBIA). IT WAS IDENTIFIED THAT THE CS EXPERIENCED AN EMERGENCY SHUTDOWN (ESD) AND BASED ON THE INVESTIGATIONS, THIS ESD WAS DUE TO LOW PNEUMATIC PRESSURE. EMERGENCY VALVES WERE FOUND PARTIALLY OPEN, LEADING TO AN UNINTENTIONAL RELEASE OF MATERIAL ADDING UP TO 8,038 MCF. THE ROOT CAUSE ANALYSIS INVESTIGATION REPORT IDENTIFIED THE PROBABLE CAUSE THAT TRIGGERED THE CHAIN OF EVENTS WHICH LED TO AN INCIDENT. RECOMMENDATIONS WERE INITIATED IN ORDER TO PREVENT THE SAME EVENTS FROM RE-OCCURRING IN THE FUTURE. THEY WERE; AN INTRODUCTION TO A LOW-LOW PNEUMATIC PRESSURE SWITCH (80 PSIG SET POINT) AND STATION PNEUMATIC PRESSURE TRANSMITTER HAS BEEN ADDED TO TRIGGER A STATION ESD ON THE LOSS OF STATION PNEUMATIC PRESSURE (IF THE PRESSURE DROPS BELOW 80 PSIG). THIS PROGRAMMING CHANGE WAS IMPLEMENTED ON JULY 2ND, 2014; A FEW HOURS AFTER THE INCIDENT TOOK PLACE. THEN, CONFIRMED PROPER OPERATION OF THE EMERGENCY BACK-UP GENERATOR TO SWITCH TO BACK-UP POWER ON LOSS OF COMMERCIAL POWER TO THE FACILITY. NOTE: INITIAL INCIDENT REPORT NO: 20140080-16463, SUBMITTED ON JULY 28, 2014
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140081 | 16465 | 2014-07-31 10:45 | ORIGINAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2014-07-11 18:55 | 2014 |  |  | 36.014 | -97.3888 | 1088798 | 2014-07-11 22:05 |  | NATURAL GAS |  | 4875 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELIEF VALVE MALFUNCTIONED. RELIEF WAS CLOSED AND LINE WAS LEFT IN SERVICE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-07-11 20:42 | 2014-07-11 21:09 | ONSHORE | OK | 73063 | MULHALL | LOGAN | SURVEY STATION NO. | 100/203 | LINE V-196 | PVR MIDSTREAM | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2013 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE MALFUNCTIONED. RELIEF OPEND BELOW MAOP. | CLASS 1 LOCATION | NO |  | 145 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 19331 | 12898.6182136602 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 19331 | 13372.5831873905 | 12898.6182136602 | [8 empty] | 550 |  | 594 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES |  |  |  |  | YES | RELIEF VALVE DID NOT FUNCTION PROPERLY. THE VALVE BEGAN RELIEVING PRESSURE AT 550 PSI WHEN THE LINE MAOP IS 594. THE RELIEF VALVE HAD POPPED 3 DAYS PRIOR TO THIS INCIDENT WHILE THE MAINLINE V PRESSURE WAS REDUCED FOR AN INTEGRITY EVENT. AT THIS TIME THE SET POINTS WERE NOT CHECKED. IT WAS DETERMINED THAT THIS POP OF THE VALVE CAUSE THE SET POINT TO MOVE. SSCGP HAS SINCE UPDATED THE O&M PROCEDURES TO VERIFY SET POINTS OF ALL RELIEF VALVES AFTER ANY ACTIVATION. | [22 empty] | YES | RELIEF VALVE DID NOT FUNCTION PROPERLY. THE VALVE BEGAN RELIEVING BELOW MAOP | [161 empty] | DAVID COOMES | COMPLIANCE ENGINEER | [6 empty] | DAVID SINCLAIR | COMPLIANCE MANAGER | 270-852-4424 |  | SSCGP GAS CONTROL RECEIVED A CALL FROM A THIRD PARTY DRIVING ALONG THE SSCGP RIGHT-OF-WAY SOUTH OF MULHALL AT 20:42 ON JULY 11, 2014. THE THIRD PARTY STATED HE SMELLED SOMETHING UNUSUAL AND COULD HEAR A LOUD NOISE AT A SMALL BUILDING, NO SPECIFIC LOCATION WAS DETERMINED AT THIS TIME. GAS CONTROL NOTIFIED THE ON-CALL OPERATOR WHO STATED HE HAD AN ETA OF ONE HOUR. AS A PRECAUTIONARY MEASURE GAS CONTROL NOTIFIED LOGAN COUNTY PSAP. AT 20:52 GAS CONTROL RECEIVED A CALL FROM PVR LOGAN THAT THERE WAS A RELIEF VALVE BLOWING AT SSCGP SETTING #16999. GAS CONTROL NOTIFIED THE MEASUREMENT TECH WHO HAD AN ETA OF 40 MINUTES. THE OPERATOR ARRIVED ON SCENE AND SHUT IN THE RELIEF VALVE AT 21:09 AND WAITED FOR THE MEASUREMENT TECH TO ARRIVE. THE LINE PRESSURE WAS MANUALLY MONITORED WHILE THE RELIEF VALVE WAS OUT OF SERVICE. THE RELIEF VALVE WAS REPAIRED AND RETURNED TO SERVICE AT 23:04 ON JULY 11, 2014.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140082 | 16573 | 2014-08-01 10:23 | SUPPLEMENTAL FINAL | 18156 | SEADRIFT PIPELINE CORP | 1000 COUNTY ROAD 340 | ANGLETON | TX | 77515 | 2014-07-05 02:27 | 2014 |  |  | 28.6136 | -97.5781 | 1088128 | 2014-07-05 14:40 |  | NATURAL GAS |  | 3554 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-07-05 09:57 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-07-05 13:10 | 2014-07-05 13:10 | ONSHORE | TX | 78107 | BERCLAIR | GOLIAD | MILEPOST | 13.8/722+34 | BURNELL 8 IN | BURNELL/0.5 MILES EAST OF FM 1351 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 72 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 |  | 0.25 | 42000 | API 5LX | SEAMLESS |  | UNKNOWN | COLD APPLIED TAPE | [28 empty] | 1968 | 1910 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 16.3 | 0.2 |  | CLASS 1 LOCATION | NO |  | 216 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 15000 | 10008.7565674256 | 75000 | 82961.660726327 | 0 | 0 | 0 | 0 |  |  | 90000 | 48458.1237681464 | 92970.4172937525 | [8 empty] | 769 |  | 1320 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | AUTOMATIC | 75202 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS INCIDENT WAS THE RESULT OF A CIRCUMVENTIAL RUPTURE, NOT DUE TO ACTIONS TAKEN BY CONTROLLERS. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | YES | YES | [13 empty] | YES | HYDROGEN-INDUCED CRACKING IN INDUCTION BEND DUE TO HIGH HARDNESS FROM NOT BEING |  |  |  |  | YES | [65 empty] | YES | YES |  |  | YES |  |  |  | 1998 | [31 empty] | 1998 | [23 empty] | YES | 1987 | 2047 | NO | [13 empty] | NO | [63 empty] | JENNIFER ASHCRAFT | REGULATORY COMPLIANCE SPECIALIST | joashcraft@dow.com | 979-238-0361 | 979-238-5685 |  |  |  | CURTIS JOHNSON | PRESIDENT | 713-654-3621 | cmjohnson@dow.com | ON JULY 5TH A RUPTURE OCCURRED ON AN 8 INCH FUEL GAS PIPELINE IN A REMOTE AREA OF SOUTH TEXAS RESULTING IN A RELEASE OF METHANE. A CHANGE IN PRESSURE ON THE PIPELINE WAS NOTICED AT THE CONTROL ROOM, AND TECHNICIANS WERE DISPATCHED TO DETERMINE IF A LEAK OCCURRED. EMERGENCY RESPONDERS WERE ALERTED AS A PRECAUTION. THE PIPELINE SECTION WAS ISOLATED. THE LEAK WAS SECURED. THERE WERE NO PUBLIC CALLS OR IMPACT. LOCATION WAS IN A RURAL AREA. THE INVESTIGATION INCLUDED A METALLURGICAL ANALYSIS CONDUCTED ON THE SECTION OF PIPE THAT RUPTURED. BASED ON THE RESULTS OF THAT ANALYSIS, IT WAS DETERMINED THAT THE CAUSE OF THE RUPTURE WAS DUE TO HYDROGEN-INDUCED CRACKING CAUSED BY THE INDUCTION BEND NOT BEING TEMPERED AFTER IT WAS QUENCHED DURING ORIGINAL MANUFACTURE. THE SECTION OF PIPE THAT CONTAINED THE RUPTURE HAS BEEN REPAIRED, BUT REMAINS OUT OF SERVICE. AN INSPECTION WILL BE COMPLETE PRIOR TO PUTTING THE LINE BACK IN SERVICE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140083 | 17519 | 2014-08-08 13:29 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2014-07-09 08:23 | 2014 |  |  | 39.4804 | -80.5382 | 1088470 | 2014-07-09 11:00 |  | NATURAL GAS |  | 10952 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-07-09 05:33 | 2014-07-10 14:25 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-07-09 05:26 | 2014-07-09 08:23 | ONSHORE | WV | 26437 | SMITHFIELD | WETZEL | SURVEY STATION NO. | CS-7C6620 | SMITHFIELD COMPRESSOR STATION DISCHARGE LINE | UNIT NO. 2 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | SEPARATED RELIEF VALVE STAINLESS STEEL SENSING LINE | CLASS 1 LOCATION | NO |  | 150 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 47422 | 31642.350262697 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 47422 | 32805.061295972 | 31642.350262697 | [8 empty] | 682 |  | 975 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE FAILED SENSING PIPE ON THE RELIEF VALVE WAS IDENTIFIED TO BE THE PROBABLE CAUSE TO INITIATE THE FAILURE OF THE RELEIF VALVE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [13 empty] | YES | [177 empty] | GEORGE HAMATY | ENGINEER | george_hamaty@transcanada.com | (304) 357-3728 |  |  |  |  | LEE ROMACK | USRC MANAGER | (832) 320-5315 | lee_romack@transcanada.com | A RELIEF VALVE (RV) SITUATED ON UNIT NO. 2 DISCHARGE LINE IN SMITHFIELD COMPRESSOR STATION (CS) , WAS INADVERTENTLY ACTIVATED, RELEASING AN AMOUNT OF NATURAL GAS (MATERIAL) EXCEEDING 3,000 MCF. SMITHFIELD CS IS A TRANSMISSION CS THAT IS OPERATED AND MAINTAINED BY COLUMBIA GAS TRANSMISSION, LLC. THE CS IS LOCATED IN WETZEL COUNTY, NEAR THE TOWN OF SMITHFIELD, WEST VIRGINIA. THE STAINLESS-STEEL SENSING LINE ON THE RV HAD FAILED LEADING TO A FALSE INDICATION OF A PRESSURE DIFFERENTIAL AND ACTIVATING THE RV. THE UNINTENDED RELEASE OF MATERIAL WAS CALCULATED TO REACH 10,952 MCF. THE AUTOMATION AND ELECTRICAL ENGINEERING DEPARTMENT WITH THE COMPRESSION GROUP HAD ASSESSED THE EVENT AND IDENTIFIED THAT THE SENSING LINE HAD FAILED ON THE RV DUE TO EXCESSIVE VIBRATION TRANSMITTED BY THE OPERATING RECIPROCATING UNIT. A CORRECTIVE ACTION WAS ISSUED TO THE CS OPERATING PERSONNEL TO ALTER (REDUCE) THE SPEED ON THE RUNNING RECIPROCATING UNITS, TO REDUCE THE VIBRATION TO ACCEPTABLE LEVELS. IN ADDITION, THE EXISTING RVS IN SMITHFIELD CS ON THE DISCHARGE LINES OF UNITS 1 & 2, WERE RELOCATED TO ANOTHER LOCATION. IMPROVED PIPELINE PIER SUPPORTS, WERE ALSO INSTALLED THROUGHOUT INSTALLATION ACROSS THE FACILITY. A CONTINUED VIBRATION MONITORING SURVEY WAS ALSO INTRODUCED TO THE CS' TWO RECIPROCATING UNITS. CURRENTLY, THE TWO RECIPROCATING UNITS ARE IN IDLE SERVICE AND HAVE NOT BEEN OPERATING FOR AN EXTENDED PERIOD OF TIME. THE TWO TURBINE UNITS ARE PROVIDING THE REQUIRED COMPRESSION SERVICE FOR THE PIPELINE SYSTEM. A SAFETY ALERT WAS ISSUED TO CS OPERATORS TO BE ALERT FOR SIMILAR CIRCUMSTANCES SO THAT CORRECTIVE MEASURES CAN BE IMPLEMENTED TO PREVENT SIMILAR SENSING TUBE FAILURES FROM RE-OCCURRING.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140084 | 16637 | 2014-08-10 19:31 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2014-07-12 03:15 | 2014 |  |  | 29.6927 | -91.3436 | 1089078 | 2014-07-14 20:58 |  | NATURAL GAS |  | 18390 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | UNINTENTIONAL TEMPORARY BLOWDOWN DID NOT AFFECT OPERATIONS | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-07-12 03:15 | 2014-07-12 03:15 | ONSHORE | LA | 70392 | PATTERSON | ST. MARY | MILEPOST | PATTERSON CS | PATTERSON COMPRESSOR STATION | STATION YARD | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | STATION SUCTION BLOWDOWN VALVE UNINTENTIONALLY OPENED | CLASS 2 LOCATION | NO |  | 252 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 75950 | 50677.6707530648 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 75950 | 52539.8423817863 | 50677.6707530648 | [8 empty] | 770 |  | 1050 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | BLOWDOWN VALVE INVOLVED IS NOT INDIVIDUALLY MONITORED BY CONTROLLER | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [204 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | [5 empty] | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | ROBERT CADORIN | COMPLIANCE SPECIALIST | robert_cadorin@transcanada.com | 248-205-7669 |  |  |  |  | ROBERT CADORIN | COMPLIANCE SPECIALIST | 248-205-7669 | robert_cadorin@transcanada.com | ON JULY 9, 2014, OPERATOR PERSONNEL CONDUCTED THE ANNUAL TEST OF THE EMERGENCY SHUTDOWN (ESD) SYSTEM AT THE ANR PIPELINE COMPANY (ANR) PATTERSON COMPRESSOR STATION. THOUGH THE ESD SYSTEM TEST WAS CONSIDERED SUCCESSFUL WITH ALL VALVES AND ELECTRONICS OPERATING AS REQUIRED, THE STATION TECHNICIAN DECIDED THAT THE ACTIVATION PISTON OF THE ESD POPPET VALVE MOUNTED ON TOP OF THE VALVE ACTUATOR OF THE 8-INCH STATION SUCTION BLOWDOWN VALVE NEEDED ADDITIONAL LUBRICATION. THIS MAINTENANCE WAS PERFORMED ON JULY 11, 2014, THE DAY PREVIOUS TO THE REPORTED INCIDENT. TO PREVENT THE 8-INCH BLOWDOWN VALVE FROM ACCIDENTALLY OPERATING DURING THIS MAINTENANCE, THE PILOT GAS AND POWER GAS SOURCES TO THE BLOWDOWN VALVE OPERATOR WERE DISABLED BY CLOSING 1/2-INCH VALVES ON THE POWER GAS AND PILOT GAS TUBING LINES AT THE VALVE OPERATOR. AT THE COMPLETION OF THE VALVE OPERATOR MAINTENANCE, THE POWER GAS VALVE WAS REOPENED TO THE VALVE OPERATOR BUT THE PILOT GAS VALVE INADVERTENTLY REMAINED CLOSED WHEN THE BLOWDOWN VALVE AND OPERATOR WERE PUT BACK INTO SERVICE. BETWEEN COMPLETION OF THE VALVE OPERATOR MAINTENANCE ON JULY 11 AND 3:15 AM CDT ON JULY 12, 2014, THE PRESSURIZED GAS IN THE PILOT GAS TUBING, LOCATED BETWEEN THE PILOT GAS VALVE AND THE 8-INCH STATION SUCTION BLOWDOWN VALVE OPERATOR, MORE THAN LIKELY LEAKED FROM A FITTING. THIS RESULTED IN A LOSS OF PILOT GAS LINE PRESSURE AT THE OPERATOR, ALLOWED POWER GAS TO ACTIVATE THE ESD POPPET VALVE COMPONENT OF THE VALVE OPERATOR, AND RESULTED IN THE OPENING OF THE 8-INCH STATION SUCTION BLOWDOWN VALVE. THIS BLOWDOWN VALVE REMAINED OPEN UNTIL AN ON-DUTY STATION EMPLOYEE DISCOVERED THE OPEN VALVE AND MANUALLY CLOSED IT AT APPROXIMATELY 3:40 AM CDT. FOLLOWING CLOSURE OF THE BLOWDOWN VALVE, TRANSCANADA PERSONNEL CALCULATED THE ESTIMATED GAS LOST DURING THE EVENT TO BE APPROXIMATELY 1.84 MMCF, WHICH WOULD HAVE PUT THE EVENT BELOW THE REPORTING THRESHOLD OF 3.0 MMCF AS STATED IN 191.3 DEFINITIONS OF AN 'INCIDENT' (THE EVENT ALSO DID NOT MEET ANY OF THE OTHER REPORTING REQUIREMENT CRITERIA IN THE DEFINITION OF AN 'INCIDENT'). HOWEVER, UPON FURTHER REVIEW OF THE EVENT THE FOLLOWING MONDAY, JULY 14, 2014, IT WAS DISCOVERED THAT THE GAS LOSS CALCULATION HAD BEEN MISINTERPRETED, I.E., THE DECIMAL POINT WAS PLACED INCORRECTLY IN THE GAS LOSS RESULT. UPON DETERMINING THE CORRECT GAS VOLUME LOST TO BE 18.39 MMCF, THE INCIDENT WAS REPORTED TO THE NATIONAL RESPONSE CENTER (NRC) AS REQUIRED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140085 | 16561 | 2014-08-11 13:02 | SUPPLEMENTAL FINAL | 4900 | KINDER MORGAN TEJAS PIPELINE | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2014-07-12 08:10 | 2014 |  |  | 29.7206 | -95.1128 | 1088858 | 2014-07-12 14:00 |  | NATURAL GAS |  | 5 | 290 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-07-12 16:35 | 2014-07-28 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-07-12 08:10 | 2014-07-12 08:35 | ONSHORE | TX | 77536 | DEER PARK | HARRIS |  |  |  | LINE 202-412 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 100 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION | [19 empty] | FILLET WELD | [20 empty] | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | YES | METHOD2 | 263 |  | NO | NO | NO |  | 0 | 0 | 1174 | 1298.6265292361 | 20 | 13.3450087565674 | 61970 | 68548.4548694731 | 0 | 0 | 0 | 0 |  |  | 63164 | 32075.488781792 | 69860.4264074658 | [8 empty] | 635 |  | 831 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | YES | NO | NOT MANDATED |  |  | MANUAL | MANUAL | 23232 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLERS DID NOT CONTRIBUTE TO INCIDENT | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [7 empty] | YES | [14 empty] | YES | [63 empty] | YES | YES | [6 empty] | 2014 | [55 empty] | YES | 2007 | 1768 | NO | [13 empty] | NO | [63 empty] | ZACHARY RAGAIN | ENGINEER - PIPELINE | zachary_ragain@kindermorgan.com | 713-420-6633 |  |  |  |  | ZACHARY RAGAIN | ENGINEER - PIPELINE | 713-420-6633 | zachary_ragain@kindermorgan.com | INTEGRITY WORK HAD BEEN EXECUTED FOR THE PREVIOUS FEW WEEKS ON THIS SYSTEM. DURING EXECUTION OF THE WORK, IT WAS DETERMINED THAT A TAP VALVE ON 8 INCH PIPING BRANCHING OFF THE 12 INCH 202-412 LINE WAS LEAKING BY. THE VALVE WAS REPLACED DURING THIS TIME. AS PART OF THAT EFFORT, IT WAS NOTED BY THE PROJECT MANAGEMENT TEAM THAT THE PIPE IN THIS AREA WAS LEANING/SAGGING CAUSING THE TAP VALVE TO BE POSITIONED AT AN ANGLE. BECAUSE OF THIS, ADDITIONAL SUPPORTS WERE INSTALLED UNDER THE NEW TAP VALVE, TO HELP RELIEVE STRESS ON THE PIPE. NOTE, THE ORIGINAL TAP VALVE DID HAVE 12X12 4INCH CONCRETE SUPPORTS. AFTER EXECUTING THE COMPLIANCE REQUIRED PIPELINE INTEGRITY WORK, THE PIPELINE HAD BEEN PUT BACK IN SERVICE ON 7/11/2014. AT APPROXIMATELY 8:00 AM, ON 7/12/2014, A CONTRACTOR ARRIVED AT THE SITE TO COMPLETE BACKFILL AND CLEANUP OF WORK LOCATION. WHILE BACKFILLING DIRT, THE CONTRACTOR NOTICED FUMES FROM THE GROUND IN THE AREA OF THE TAP VALVE. ANOTHER CONTRACTOR STOPPED THE WORK ACTIVITY AND CONTACTED KINDER MORGAN OPERATIONS PERSONNEL. AT 13:00, THE LEAK WAS CONFIRMED BY VISUAL INSPECTION TO BE IN THE AREA OF THE MAIN PIPE SLEEVE UPSTREAM OF THE TAP VALVE WHERE IT CONNECTED WITH THE 12 INCH 202-412 LINE. AT 16:35 THE PIPELINE WAS SHUTDOWN. UPON FURTHER VISUAL EXAMINATION, THE LEAK APPEARED TO BE AT THE WELD POINT OF THE TRANSITION BRANCH OF THE 12 INCH 202-412 TO THE 8 INCH PIPING. THE DEFECT WAS REMOVED AND SENT TO BE ANALYZED BY A METALLURGICAL LAB. THE METALLURGICAL LAB ANALYZED THE SAMPLE AND CAME BACK WITH 4 CONCLUSIONS. 1. THE BRANCH CONNECTION FAILED DUE TO AN OVERLOAD FRACTURE, LIKELY INCDUCED BY EXTERNAL BENDING LOADS. 2. EVIDENCE OF TIME DEPENDENT CRACKING MECHANISMS, SUCH AS HIGH OR LOW CYCLE FATIGUE WAS NOT OBSERVED. 3. INSUFFICIENT STRUCTURAL SUPPORT OF THE BRANCH CONNECTION COULD HAVE CONTRIBUTED TO THE WELD FAILURE. 4. THE WELD CONTAINED DEFECTS SUCH AS LACK OF FUSION; HOWEVER, THIS DOD NOT CONTRIBUTE TO THE FAILURE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140086 | 16472 | 2014-08-13 10:39 | ORIGINAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2014-07-23 12:40 | 2014 |  |  | 33.0168 | -83.2267 | 1090006 | 2014-07-23 02:30 |  | NATURAL GAS |  | 0.2 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-07-23 13:40 | 2014-07-24 10:45 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2014-07-23 12:40 | 2014-07-23 13:30 | ONSHORE | GA | 31061 | MILLEDGEVILLE | BALDWIN |  |  | DUBLIN #1 METER STATION |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1954 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | YES | METHOD2 | 518 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 50 | 33.3625218914186 | 10000 | 11061.5547635103 | 1500 | 1659.23321452654 | 0 | 0 |  |  | 11550 | 5873.7657845542 | 12754.1504999282 | [8 empty] | 295 |  | 400 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATING PRESSURE WAS WITHIN NORMAL RANGE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | DEFECTIVE OR LOOSE TUBING OR FITTING | MATERIAL/WELD/EQUIP FAILURE | DEFECTIVE OR LOOSE TUBING/FITTING | [166 empty] | DEFECTIVE OR LOOSE TUBING OR FITTING | [35 empty] | YES | BREAK DOWN OF DIELECTRIC INSULATION IN TUBING UNION | [161 empty] | KENNETH C. PETERS | SR. ENGINEER COMPLIANCE | ken_peters@kindermorgan.com | 2053257554 | 2053253508 |  |  |  | REJI GEORGE | DIRECTOR COMPLIANCE | 7134205433 | reji_george@kindermorgan.com | THE UPPER SECTION OF A RUN SWITCHING VALVE, THE ACTUATOR, CAUGHT FIRE AT SOUTHERN NATURAL GAS COMPANY'S DUBLIN #1 METER STATION ON JULY 23, 2014. THE FLAME REACHED A HEIGHT OF ABOUT FOUR FEET BUT NEVER SPREAD TO CAUSE DAMAGE ANYWHERE OTHER THAN INSIDE THE METER STATION FENCE. AS A PRECAUTION, THE HIGHWAY (HIGHWAY 441) NEAR THE METER STATION WAS CLOSED UNTIL THE FIRE WAS EXTINGUISHED. INVESTIGATION REVEALED THAT DIELECTRIC INSULATION IN A TUBING UNION BROKE DOWN OVER TIME RESULTING IN AN ELECTRICAL ARC THAT IGNITED RESIDUAL NATURAL GAS PRESENT IN TUBING FITTINGS AND THE VALVE ACTUATOR. THE AREA OF THE FIRE WAS ISOLATED TO CUT OFF FUEL AND THE FIRE EXTINGUISHED. REPAIRS WERE MADE TO ALL DAMAGED COMPONENTS AND THE METER STATION WAS PLACED BACK INTO SERVICE JULY 24, 2014.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140087 | 17201 | 2014-08-15 11:03 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2014-07-18 08:00 | 2014 |  |  | 33.0511 | -115.5122 | 1089480 | 2014-07-18 10:40 |  | NATURAL GAS |  | 26280 | 470 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-07-19 01:54 | 2014-07-19 18:21 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-07-18 08:00 | 2014-07-18 08:12 | ONSHORE | CA | 92227 | BRAWLEY | IMPERIAL | SURVEY STATION NO. | 241889 | 6000 | 6000-2 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 40 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10 |  | 0.25 | 32700 | GRADE B | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | ASPHALT | [28 empty] | 1948 | 1948 | CARBON STEEL |  | MECHANICAL PUNCTURE | 3 | 2.3 | [7 empty] | CLASS 1 LOCATION | NO |  | 188 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 153112 | 102164.049036778 | 103375 | 114348.822367787 | 168960 | 186896.029284269 | 0 | 0 |  |  | 425447 | 244197.444387235 | 403408.900688834 | [8 empty] | 381 |  | 400 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 36960 | NO | YES | YES | YES | YES |  |  |  | YES |  |  |  |  | YES | ONE-WAY FEED | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | NO |  |  | YES | PRIVATE BUSINESS | [7 empty] | CONTRACTOR | GRADER/SCRAPER | GRADING | YES | 41920171 | N/A | UTILITY OWNER | NO | NO | YES | 17 | LOCATING PRACTICES NOT SUFFICIENT |  | INCORRECT FACILITY RECORDS/MAPS | [264 empty] | TROY A. BAUER | PIPELINE SAFETY AND COMPLIANCE MANAGER | tbauer@semprautilities.com | 909-376-7208 | 909-885-6270 |  |  |  | TROY A. BAUER | PIPELINE SAFETY AND COMPLIANCE MANAGER | 909-376-7208 | tbauer@semprautilities.com | ON JULY 18TH, 2014 A CONTRACTOR STRUCK A 10 INCH TRANSMISSION LINE WHILE GRADING, CAUSING A LEAK. NO INJURIES OR PUBLIC PROPERTY DAMAGE RESULTED FROM THIS INCIDENT. DUE TO THE ISOLATED LOCATION OF THE DAMAGE, IT WAS DETERMINED THAT THE LINE WAS SAFELY VENTING TO ATMOSPHERE WITH NO IMPACTS TO PUBLIC SAFETY OR PROPERTY. A REVIEW OF THE SYSTEM REVEALED THAT CLOSING 2 MAIN LINE VALVES UPSTREAM AND DOWNSTREAM OF THE DAMAGE WOULD HAVE IMPACTED MORE THAN 5 CITIES WITH LARGE INDUSTRIAL CUSTOMERS AND A MILITARY BASE WITH LOSS OF SERVICE. AN ALTERNATIVE PLAN WAS MADE TO BACK FEED THE SYSTEM FROM AN ADJACENT ONE IN ORDER TO MAINTAIN PRESSURE AND SERVICE DOWNSTREAM OF THE DAMAGE. ONCE THIS OPERATION WAS ACCOMPLISHED THE MAIN LINE VALVES WERE CLOSED AND GAS CONTROLLED AT 01:54 ON JULY 19TH. ALL REPAIRS WERE COMPLETED AND THE DAMAGED SECTION OF PIPE WAS REPLACED. THE SINGLE CUSTOMER WHOSE SERVICE WAS INTERRUPTED WAS RESTORED. INVESTIGATION OF THE INCIDENT SHOWED THE CONTRACTOR HAD CONTACTED USA BUT THE DAMAGE LINE WAS NOT MARKED. THE MAPPING SYSTEM INDICATED THREE PIPELINES IN THE VICINITY AND THE EMPLOYEE SUCCESSFULLY LOCATED AND MARKED THREE LINES. THE EMPLOYEE WAS UNAWARE OF A FOURTH LINE THAT WAS NOT MAPPED. THIS INCIDENT WAS REPORTED TO DOT AND THE CPUC DUE TO THE ESTIMATED COSTS WOULD EXCEED $50,000 AND THE GAS LOSS WOULD EXCEED THREE MILLION CUBIC FEET.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140088 | 16477 | 2014-08-21 16:49 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2014-07-28 11:12 | 2014 |  |  | 35.0346 | -88.8916 | 1090467 | 2014-07-28 13:10 |  | NATURAL GAS |  | 16606 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE COMPRESSOR STATION WAS NOT IN OPERATION AT THE TIME OF THE EVENT | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-07-28 11:12 | 2014-07-28 11:12 | ONSHORE | TN | 38052 | MIDDLETON | HARDEMAN |  |  | STATION 71 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | BPS PANEL AND TWO ESD BLOCK VALVES |  |  | CARBON STEEL |  | OTHER | [8 empty] | UNPLANNED STATION ESD. | CLASS 1 LOCATION | NO |  | 607 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 63767 | 42548.5586690018 | 400 | 442.46219054041 | 0 | 0 | 0 | 0 |  |  | 64167 | 44315.1245877092 | 42991.0208595422 | [8 empty] | 590 |  | 750 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS INITIATED LOCALLY BY THE STATION ESD. THE CONTROL ROOM AND CONTROLLERS WERE NOT A CONTRIBUTING FACTOR TO THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | A LOOSE WIRE IN THE BUILDING PROTECTION SYSTEM CAUSED A POWER INTERRUPTION. THE ESD SYSTEM OPERATED WHEN THE INTERRUPTION WAS DETECTED, OPERATING AS DESIGNED. DURING THE ESD, TWO AUTOMATIC GAS-OPERATED BLOCK VALVE OPERATORS FAILED TO CLOSE CAUSING THE LOSS OF 16,606 MCF OF NATURAL GAS. | [15 empty] | YES | LOOSE WIRE ON BPS. FAILED BEARINGS ON THE BLOCK VALVE OPERATORS. | [161 empty] | KRISTIN VAN DER LAAN | COMPLIANCE ENGINEER III | kristin_vanderlaan@kindermorgan.com | 303-914-7753 |  |  |  |  | REJI GEORGE | DIRECTOR - COMPLIANCE - CODES AND STANDARDS | 713-420-5433 | reji_george@kindermorgan.com | A LOOSE WIRE IN THE "B" COMPRESSOR BUILDING BPS (BUILDING PROTECTION SYSTEM) CABINET CAUSED THE STATION'S EMERGENCY SHUTDOWN SYSTEM TO ACTIVATE. THE ASSOCIATED UNINTENTIONAL GAS FROM THE BLOWDOWN WAS 16,606 MCF (GREATER THAN THE 3,000 MCF REPORTING THRESHOLD). DURING THE ESD TWO AUTOMATIC GAS-OPERATED BLOCK VALVE OPERATORS FAILED TO CLOSE THE BLOCK VALVES DUE TO A FAILED BEARING IN EACH OPERATOR. THIS RESULTED IN A LARGER AMOUNT OF GAS TO RELEASE, IN A CONTROLLED MANNER, THROUGH THE BLOWDOWNS. OPERATING PERSONNEL WERE ON SITE AND RESPONDED IMMEDIATELY. NOTE THAT DUE TO LOW DEMAND AT THE TIME OF THE EVENT THE COMPRESSOR STATION WAS NOT IN OPERATION. FOLLOWING REPAIRS, THE ESD SYSTEM WAS PLACED BACK IN SERVICE. ADDITIONALLY, EACH ESD VALVE HAS BEEN INSPECTED, TESTED AND FUNCTIONALLY VERIFIED. ALSO NOTE THAT PART D, QUESTION 3 ASKS FOR THE PIR AT THE LOCATION OF THE INCIDENT. THE PIR HAS BEEN CALCULATED BASED ON THE LARGEST DIAMETER PIPELINE WITHIN THE COMPRESSOR STATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140091 | 16480 | 2014-08-25 15:34 | ORIGINAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2014-07-26 17:38 | 2014 |  |  | 29.3726 | -93.5413 | 1090355 | 2014-07-26 18:20 |  | NATURAL GAS |  | 1 | 2261 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-07-26 17:38 | 2014-07-31 06:55 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-07-26 17:38 | 2014-07-29 08:10 | OFFSHORE | [28 empty] | 49 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST CAMERON | 165 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 10.75 |  | 0.365 | 42000 | API-5L | SEAMLESS |  | UNKNOWN | EPOXY | [28 empty] | 2006 | 2005 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 327 |  | NO | NO | NO |  | 0 | 0 | 8730 | 9656.73730854446 | 4 | 2.66900175131348 | 235000 | 259946.536942491 | 0 | 0 | 0 | 0 |  |  | 243734 | 123757.783933027 | 269605.943252787 | [8 empty] | 775 |  | 1300 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | AUTOMATIC | 45725 | NO | [5 empty] | YES | LATERAL LINE HOT TAPS INTO ANOTHER LATERAL | YES |  |  |  |  | YES | HOT TAPS INTO ANOTHER LINE | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE SMALL SIZE OF THE DEFECT AND THE AMOUNT OF GAS LEAKING | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | NO | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | ROGER R. STREET | FIELD COMPLIANCE SPECIALIST | roger_street@transcanada.com | 8325702966 |  |  |  |  | ROGER STREET | FIELD COMPLIANCE SPECIALIST | 832-570-2966 | roger_street@transcanada.com | ON 26 JULY 2014, A THIRD-PARTY HELICOPTER PATROL OBSERVED A RELEASE OF GAS LOCATED IN WEST CAMERON BLOCK 165 (29.37260800, -93.54129500) SOUTH OF CAMERON PARISH IN THE GULF OF MEXICO. THE LEAK WAS REPORTED TO ANR PIPELINE COMPANY, OPERATOR FOR TC OFFSHORE, AS AN APPROXIMATELY TEN FOOT IN DIAMETER BUBBLING OVER THE LOCATION OF TC OFFSHORE'S 687 TRANSMISSION PIPELINE. THE SECTION OF 687 LINE CONTAINING THE LEAK WAS SHUT IN BY A CHECK VALVE ON THE DOWNSTREAM SIDE AND BY CLOSING A VALVE ON THE UPSTREAM SIDE. NO SHEEN OR PRODUCT WAS REPORTED AT THE SURFACE OF THE WATER. FOLLOWING THE SECTION BEING SHUT IN, CONTRACT EMPLOYEES WERE DEPLOYED TO THE SITE TO INVESTIGATE AND REPAIR THE LEAK. PRIOR TO THE ARRIVAL OF THE CONTRACTORS, HELICOPTER PATROLS WERE CONDUCTED IN THE AREA TO MONITOR THE LEAK AND CONDITIONS OF THE SITE. NO SHEEN OR PRODUCT WAS REPORTED FOR THE DURATION OF AERIAL MONITORING WHILE THE PIPELINE WAS BEING REPAIRED. ON 29 JULY, ANR AND CONTRACT PERSONNEL FROM CAL-DIVE INTERNATIONAL ARRIVED AT THE LEAK LOCATION IN WEST CAMERON BLOCK 165 TO INSPECT THE PIPE AND REPAIR THE LEAK. AT APPROXIMATELY 12:00 CDT, DIVERS ENTERED THE WATER AND DETERMINED THE LOCATION OF THE LEAK. AFTER DETERMINING THE APPROXIMATE LOCATION OF THE LEAK, PIPELINE PRESSURE WAS REDUCED TO 80 PSIG WATER, AND WATER BLASTING WAS USED TO REMOVE THE CONCRETE COATING FROM THE PIPE TO PREPARE FOR THE INSTALLATION OF A PLIDCO TEN INCH BOLT-ON CLAMP OVER THE LEAK. THE CLAMP WAS THEN INSTALLED ACCORDING TO MANUFACTURER SPECIFICATIONS, THE EXPOSED PIPE WRAPPED IN SYNTHO-GLASS, AND PIPELINE BACKFILLED. FINALLY, THE PIPELINE WAS MONITORED DURING REPRESSURIZATION TO CONFIRM THAT THE LEAK WAS SUCESSFULLY REPAIRED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140092 | 16827 | 2014-08-28 09:12 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2014-08-07 18:15 | 2014 |  |  | 31.3782 | -102.8903 | 1091667 | 2014-08-07 19:04 |  |  |  | 17.62 | 35881.99 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-08-07 20:51 | 2014-08-11 12:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-08-07 16:30 | 2014-08-07 17:53 | ONSHORE | TX | 79756 | ROYALTY | WARD | MILEPOST | MLBV NO. 1 | NORTH TEXAS GAS SYSTEM - SOUTH TEXAS-TX150 | LINE 225 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 36 |  | 0.406 | 65000 | API-5L | DSAW |  | UNKNOWN | EPOXY | [28 empty] | 1970 | 1970 | CARBON STEEL |  | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 1 LOCATION | NO |  | 805 |  | NO | NO | NO |  | 0 | 0 | 143000 | 158180.233118197 | 70 | 46.707530647986 | 269000 | 297555.823138426 | 0 | 0 | 0 | 0 |  |  | 412070 | 209243.299070729 | 455782.763787271 | [8 empty] | 904 |  | 1051 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 79728 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY CALLED AND REPORTED INCIDENT TO ENTERPRISE PIPELINE CONTROL ROOM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  |  |  | YES | [6 empty] | CONTRACTOR | AUGER | UNKNOWN/OTHER | NO |  |  | CONTRACT LOCATOR | UNKNOWN/OTHER | UNKNOWN/OTHER | NO |  | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | MICHAEL D. SMITH | PIPELINE COMPLIANCE SPECIALIST | mdsmith@eprod.com | (713) 381-5650 |  |  |  |  | MICHAEL D. SMITH | PIPELINE COMPLIANCE SPECIALIST | (713) 381-5650 | No Email Address | ON 8/7/14 AT APPROXIMATELY 4:30 PM, GAS CONTROL RECEIVED A CALL ABOUT A POSSIBLE LEAK ON THE NORTH TEXAS (NT) 36" LINE. A PIPELINE TECHNICIAN RESPONDED AND VERIFIED THAT AN ELECTRIC CONTRACTOR HAD STRUCK EPCO'S LINE WHILE SETTING ANCHORS FOR THE PULLING UNIT. THERE WAS A SMALL AMOUNT OF GAS LEAKING FROM THE PIPELINE; HOWEVER, THERE WAS NO LIQUIDS RELEASED, NO FIRE, AND NO INJURIES. THE LOCATION OF THE PIPELINE STRIKE WAS NORTHWEST OF GRANDFALLS, TX., WEST OF CR 1219 IN WARD COUNTY, TX. THE PIPELINE WAS IMMEDIATELY ISOLATED AND VENTED. THE DAMAGED PIPE WAS REPLACED AND RETURNED TO SERVICE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140093 | 16498 | 2014-09-05 14:01 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2014-08-21 15:50 | 2014 |  |  | 31.9499 | -89.7537 | 1093037 | 2014-08-21 16:44 |  | NATURAL GAS |  | 7238 | 1000 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-08-21 15:50 | 2014-08-21 22:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-08-21 15:50 | 2014-08-21 16:10 | ONSHORE | MS | 39114 | MINDENHALL | SIMPSON | MILEPOST | 70 | JACKSON MOBILE 16" | INDEX 301 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 20 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.25 | 33000 | API 5L | FLASH WELDED |  | AO SMITH | COAL TAR | [28 empty] | 1930 | 1930 | CARBON STEEL |  | LEAK |  |  | OTHER | HOLE GOUGED IN PIPE BODY | [5 empty] | CLASS 1 LOCATION | NO |  | 227 |  | NO | NO | NO |  | 0 | 0 | 11007 | 12175.4533281957 | 31859 | 21257.9316987741 | 18000 | 19910.7985743185 | 1000 | 1106.15547635103 | 0 | 0 |  |  | 61866 | 37275.2538766853 | 54450.3390776393 | [8 empty] | 265 |  | 423 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 568128 | NO |  | YES | YES | YES |  | YES | DRESSER COUPLING PIPELINE | YES |  | YES |  |  | YES | THIS SEGMENT BEING REMOVED FROM SERVICE | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | YES | [6 empty] | CONTRACTOR | UNKNOWN/OTHER | GRADING | NO |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | YES | 6 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 2706886361 | jeff.mcmaine@bwpmlp.com | A THIRD PARTY CONTRACTOR OPERATING A BULLDOZER HIT THE PIPELINE. AREA PERSONNEL WERE DISPATCHED AND LINE WAS ISOLATED. REPAIRS WERE MADE AND LINE RETURNED TO SERVICE THE SAME DAY. NO ONE CALL NOTIFICATION WAS MADE. 9-23-14 REVISED LAT/LONG PER PHMSA REQUEST.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140094 | 17034 | 2014-09-09 08:39 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2014-08-12 02:59 | 2014 |  |  | 39.0083 | -94.6972 | 1092452 | 2014-08-13 16:21 |  | NATURAL GAS |  | 0 | 202 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-08-13 09:02 | 2014-09-05 17:11 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-08-12 02:59 | 2014-08-12 02:59 | ONSHORE | KS | 66203 | MERRIAM | JOHNSON | SURVEY STATION NO. | 100/88+38 | LINE CH | KANSAS CITY | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 288 |  | YES |  |  |  |  | YES | BORED/DRILLED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.344 | 60000 | API 5LX | LONGITUDINAL ERW - HIGH FREQUENCY |  | STUPP CORPORATION | COLD APPLIED TAPE | [28 empty] | 1989 | 1988 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | YES | METHOD2 | 195 |  | NO | NO | NO |  | 20000 | 22123.1095270205 | 770 | 851.73971679029 | 0 | 0 | 972011 | 1075195.29072344 | 5000 | 5530.77738175513 | 0 | 0 |  |  | 997781 | 506627.84423466 | 1103700.917349 | [8 empty] | 185 |  | 200 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 11375 | NO | YES | [6 empty] | YES |  | YES | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS CONTROL DATA DID NOT SHOW ANY ABNORMAL TRENDING DURING TIME OF INCIDENT. INCIDENT WAS CAUSED BY THE REPAIR COST OF A SMALL LEAK DUE TO LOCATION OF LEAK FALLING UNDER I-35. LEAK WAS DETERMINED DURING ONE CALL DISPATCH | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | OTHER | DUE TO LOCATION AND LACK OF WORKSPACE THIS PIPE COULD NOT BE REMOVED TO INVESTIGATE THE LEAK. SSC DETERMINED THE PIPE WAS INSTALLED BY PULLING THROUGH AN HDD HOLE BORED IN SOLID ROCK AND PIPE DIDN'T CONTAIN ABRASION RESISTANT COATING. SSC BELIEVES EXTERNAL CORROSION, CAUSED BY DAMAGE TO COATING DURING INSTALL, IS THE MOST LIKELY CAUSE OF THE LEAK. SSC IS RESEARCHING ANY SIMILARLY INSTALLED PIPE TO DETERMINE WHETHER OTHER LEAKS CAN OCCUR AND WHAT SSCGP CAN DO TO ELIMINATE THESE POSSIBLE THREAT | [5 empty] | YES | UNKNOWN |  |  |  |  | YES | UNKNOWN | YES | YES |  |  | YES | YES |  |  |  | 2014 |  |  |  | NO | [190 empty] | NO | [63 empty] | YES | 2011 | 344 | NO | [13 empty] | NO | [63 empty] | DAVID COOMES | COMPLIANCE ENGINEER | david.coomes@sscgp.com | 2708524391 |  |  |  |  | DAVID SINCLAIR | COMPLIANCE MANAGER | 2708524424 | david.l.sinclair@sscgp.com | ON 8/12/2014 AT 01:15 SSC OPERATIONS WERE DISPATCHED THROUGH A KANSAS ONE-CALL TICKET. AT 02:59 ON 8/12/2014 SSC OPERATOR CONTACTED GAS CONTROL NOTIFYING OF A POSSIBLE LEAK ON A SSC LINE. THE LEAK WAS AT THE I-35 AND 67TH STREET EXIT WHERE SSC AND KGS HAD LINES LOCATED. KGS COMPLETED THEIR EXCAVATION AT 16:34 ON 8/12/2014. KGS STATED THE GAS DETECTION WAS STRONGER AS THEY MOVED CLOSER TO THE SSC LINE . SSC OPERATIONS BEGAN EXCAVATION AFTER THIS DETERMINATION. SSC BEGAN BLOW-DOWN TO DETERMINE OWNERSHIP OF THE LEAK AT 19:37 ON 8/12/2014. SSC OPERATIONS COMPLETED THE BLOWDOWN AND CONFIRMED THE LEAK AT 09:03 ON 8/13/2014. SSC CONTINUED TO EXCAVATE THE AREA TO TRY AND DETERMINE THE LOCATION OF THE LEAK. AT 16:21 ON 8/13/2014 THE PIPE WAS UNCOVERED AND IT WAS DETERMINED THAT THE LEAK WAS BELIEVED TO BE UNDER THE I-35 ROADWAY. AT THIS TIME THE NATIONAL RESPONSE CENTER WAS NOTIFIED BASED ON THE EXPECTED REPAIR COST TO EXCEED $50,000. DUE TO LOCATION AND LACK OF WORKSPACE THIS PIPE COULD NOT BE REMOVED TO INVESTIGATE THE LEAK. SSCGP DETERMINED THE PIPE WAS INSTALLED BY PULLING THROUGH AN HDD HOLE AND PIPE DID NOT CONTAIN ABRASION RESISTANT COATING. THE HOLE HAD BEEN BORED THROUGH SOLID ROCK. SSCGP BELIEVES EXTERNAL CORROSION CAUSED BY DAMAGE TO COATING DURING INSTALL, BY SCRAPING THE SIDES OF THE BORE HOLE, TO BE THE MOST LIKELY CAUSE OF THE LEAK. SSCGP IS RESEARCHING ANY SIMILARLY INSTALLED PIPE TO DETERMINE WHETHER OTHER LEAKS CAN OCCUR AND WHAT SSCGP CAN DO TO ELIMINATE THESE POSSIBLE THREATS. SSC HAS COMPLETED THE REPLACEMENT OF THE ROAD CROSSING BY PULLING A 16" PIPE INTO THE EXISTING 20" LINE. THE EXISTING LINE WILL BE USED AS A CASING. THE REPLACEMENT WAS COMPLETED ON 9/3/2014. THE LINE WAS PURGED, PACKED, AND BACK IN SERVICE ON 9/5/2014. ALL REPAIRS TO THE I-35 RAMP AND R/W WILL BE REPAIRED AND COMPLETED BY 9/10/2014.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140095 | 16491 | 2014-09-16 16:49 | ORIGINAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 1111 LOUISIANA STREET | HOUSTON | TX | 77002 | 2014-08-29 16:40 | 2014 |  |  | 33.0362 | -94.7129 | 1093891 | 2014-08-29 17:38 |  | NATURAL GAS |  | 812 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | ABOVE GROUND METER STATION WITH VALVES TO SHUT GAS OFF | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 10 | 2014-08-29 15:55 | 2014-08-29 16:40 | ONSHORE | TX | 75638 | DAINGERFIELD | MORRIS | MILEPOST | CY-02-05-10 | DAINGERFIELD TOWN BORDER STATION | 355+11 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | UNION | 1970 |  | CARBON STEEL |  | LEAK |  |  | OTHER | OUTSIDE FORCE BROKE PIPE UNION | [5 empty] | CLASS 3 LOCATION | NO |  | 46 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 3003 | 2003.7530647986 | 950 | 1050.84770253347 | 0 | 0 | 0 | 0 |  |  | 3953 | 2559.74861034515 | 3054.60076733207 | [8 empty] | 355 |  | 500 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | DISTRIBUTION OPERATOR |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NATURAL FORCE DAMAGE CAUSED THE EVENT | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [52 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | TREE FELL ON METER STATION | NO | [306 empty] | JIMMY CROSS | COMPLIANCE MANAGER | jimmy.cross@enablemidstream.com | 3184293664 | 3184293997 |  |  |  | JOHNNY CAVITT | MANAGER OF COMPLIANCE PROGRAMS | 3184293606 | johnny.cavitt@enablemidstream.com | A TREE FELL ON AN ABOVEGROUND TOWN BORDER STATION IN DAINGERFIELD, TX. THE TREE BROKE A UNION FITTING ON THE INLET SIDE OF A 2 INCH U-SHAPE ON THE STATION. THIS EVENT IS CONSIDERED SIGNIFICANT TO THE OPERATOR AS FOUR HOMES WERE EVACUATED BY EMERGENCY RESPONDERS AND THE HIGHWAY WAS CLOSED FOR APPROXIMATELY 1 1/2 HOURS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140096 | 16535 | 2014-09-17 17:13 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2014-08-20 12:30 | 2014 |  |  | 34.072 | -113.6121 | 1092921 | 2014-08-20 13:40 |  | NATURAL GAS |  | 2174 | 18152 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-08-20 14:20 | 2014-08-21 20:05 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-08-20 12:30 | 2014-08-20 13:54 | ONSHORE | AZ | 85357 | WENDEN | LA PAZ | MILEPOST | MP 38+3130 |  | LINE 1104 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 30 |  | 0.335 | 52000 | API5LX52 | DSAW |  | CONSOLIDATED WESTERN STEEL COMPANY | COAL TAR | [28 empty] | 1950 | 1950 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 589 |  | NO | NO | NO |  | 0 | 0 | 72669 | 80383.2123109527 | 8702 | 5806.41330998249 | 50305 | 55645.1512378384 | 0 | 0 | 0 | 0 |  |  | 131676 | 68460.3805558147 | 141834.776858774 | [8 empty] | 670 |  | 809 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 79100 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS CAUSED BY A CRACK IN THE LONG SEAM OF THE PIPE. THE CONTROL ROOM AND CONTROLLERS WERE NOT A CONTRIBUTING FACTOR TO THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) |  | YES | [13 empty] | YES | SOLIDIFICATION CRACK IN THE WELD PRESENT SINCE PIPE MANUFACTURE | [6 empty] | YES | [63 empty] | YES | YES |  |  | YES |  |  | YES | 2006 | [31 empty] | 2006 | [17 empty] | COMBINATION TOOL | 2013 |  |  |  |  | NO |  |  | NO | [13 empty] | NO | [63 empty] | KRISTIN VAN DER LAAN | COMPLIANCE ENGINEER III - CODES AND STANDARDS | kristin_vanderlaan@kindermorgan.com | 303-914-7753 |  |  |  |  | REJI GEORGE | DIRECTOR - COMPLIANCE CODES AND STANDARDS | 713-420-5433 | reji_george@kindermorgan.com | A LOCAL RANCHER NOTIFIED EL PASO NATURAL GAS COMPANY (EPNG) GAS CONTROL THAT HE SAW BLOWING GAS IN THE AREA OF THE EPNG NATURAL GAS PIPELINE. EPNG EMERGENCY PROCEDURES WERE INITIATED AND LOCAL OPERATIONS PERSONNEL WERE DEPLOYED TO THE LOCATION TO BOTH VERIFY THE LEAK AND TO SHUT IN THE PIPELINE ONCE THE LEAK WAS CONFIRMED. AFTER THE LEAK LOCATION WAS CONFIRMED, THE PIPELINE SECTION WAS ISOLATED AND BLOWN DOWN. THE JOINT WHERE THE LEAK EXISTED WAS CUT OUT AND REPLACED. THE METALLURGICAL REPORT OF THE CUTOUT JOINT CONCLUDED THAT THE EPNG NPS 30 LINE L1104 LEAKED DUE TO A SOLIDIFICATION CRACK IN THE CENTERLINE OF THE WELD WHICH HAS BEEN PRESENT SINCE THE PIPE MANUFACTURING.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140097 | 16494 | 2014-09-18 20:48 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2014-08-19 08:30 | 2014 |  |  | 38.896 | -121.0956 | 1092822 | 2014-08-19 |  | NATURAL GAS |  | 1258.3 | 138.2 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | LINE PRESSURE WAS REDUCED TO 125 PSIG. BYPASS CARRIED FLOW. | [6 empty] | NO |  |  |  |  | NO | [7 empty] | 2014-08-19 08:30 | 2014-08-19 08:30 | ONSHORE | CA | 95603 | AUBURN | PLACER | MILEPOST | 16.5 | TRANSMISSION LINE 173 | 113.5 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 30 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 |  | 0.188 | 42000 | API 5LX-X42 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | NOT AVAILABLE | ASPHALT | [28 empty] | 1962 | 1962 | CARBON STEEL |  | OTHER | [8 empty] | LINE 173 HAD BEEN STRUCK BY AN EXCAVATOR DURING WORK TO TRANSFER HIGH PRESSURE REGULATORS (HPR) FROM THE 6-INCH TRANSMISSION LINE TO A NEWLY INSTALLED PARALLEL DISTRIBUTION LINE. THE SERVICE TEE TO THE HPR WAS STRUCK, SEVERING IT DIRECTLY ABOVE THE BASE WELD TO THE MAIN, CAUSING GAS TO ESCAPE. | CLASS 3 LOCATION | NO |  | 103 |  | NO | NO | NO |  | 0 | 0 | 537 | 594.005490800501 | 4890 | 3262.85464098074 | 60000 | 66369.3285810616 | 0 | 0 | 0 | 0 |  |  | 65427 | 34120.6868514501 | 70226.1887128428 | [8 empty] | 475 |  | 500 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 125 | NO | YES | YES | YES | YES |  | YES | MULTIPLE BOTTOM-OUT PRESSURE CONTROL FITTINGS | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS REPORTED BY ON-SITE OPERATOR | [12 empty] | YES | 3 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | [10 empty] | YES |  |  |  |  | YES | [6 empty] | UTILITY | BACKHOE/TRACKHOE | NATURAL GAS | YES | 219694 | USAN | UTILITY OWNER | YES | YES |  |  | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO USE HAND TOOLS WHERE REQUIRED | [263 empty] | WINI CHEN | PROGRAM MANAGER | wcce@pge.com | 925-328-5798 |  |  |  |  | LARRY DENISTON | ACTING MANAGER REGULATORY COMPLIANCE | 925-328-5756 | lcd1@pge.com | A PG&E GAS CREW, EXCAVATING TO CUT OFF A 3/4-INCH TEE ON TRANSMISSION LINE L-173, STRUCK THE 3/4-INCH PIPE WITH A BACKHOE. THE 3/4-INCH TEE PARTIALLY PULLED OFF OF THE 6-INCH STEEL TRANSMISSION MAIN RESULTING IN AN UNINTENTIONAL RELEASE OF NATURAL GAS. PRIOR TO THE INCIDENT, PG&E HAD CALLED USA AND THE GAS FACILITIES WERE PROPERLY LOCATED AND MARKED. PG&E GAS CREW FAILED TO HAND DIG, EXPOSE AND PROPERLY PROTECT THE FACILITIES PRIOR TO USING A BACKHOE. THERE WERE NO INJURIES, FATALITIES, OR IGNITION. NO MEDIA WAS PRESENT. PG&E RESPONDED BY LOWERING PRESSURE IN L-173 TO 125 PSIG AND MOBILIZED PERSONNEL TO INSTALL TWO 6-INCH PRESSURE CONTROL FITTINGS AND A 2-INCH BYPASS. NO GAS SERVICE TO CUSTOMERS WAS AFFECTED. THE DAMAGED PORTION OF THE 6-INCH TRANSMISSION MAIN WAS REPLACED. THE VOLUME OF NATURAL GAS UNINTENTIONALLY RELEASED IS ESTIMATED TO BE 1,258 THOUSAND CUBIC FEET (MCF). THE COST OF THE REPAIRS IS ESTIMATED TO BE OVER $50,000. THREE PG&E EMPLOYEES INVOLVED IN THE INCIDENT WERE TESTED FOR DRUG AND ALCOHOL; ALL THREE TESTED NEGATIVE. WHILE CONDUCTING AN INVESTIGATION OF THE INCIDENT, PG&E IDENTIFIED A VIOLATION WITH REGARDS TO THE CLEARANCE EXECUTED DURING THE EMERGENCY RESPONSE. ALTHOUGH ALL OPERATIONS WERE PERFORMED SAFELY AND CORRECTLY, THE INTERIM SUPERVISOR WHO SUPERVISED THE CLEARANCE WAS NOT PROPERLY QUALIFIED TO ACT AS A CLEARANCE SUPERVISOR. AS OF SEPTEMBER 4, 2014, THE INTERIM SUPERVISOR HAS UNDERGONE TRAINING AND NOW POSSESSES THE PROPER QUALIFICATIONS TO ACT AS A CLEARANCE SUPERVISOR PER PG&E UTILITY PROCEDURE TD-4100P-10, "GAS CLEARANCE PROCEDURES FOR FACILITIES OPERATING OVER 60 PSIG."
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140098 | 16980 | 2014-09-23 22:44 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2014-08-24 03:20 | 2014 |  |  | 38.1763 | -122.3026 | 1093289 | 2014-08-24 |  |  |  | 0 | 1099 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | NOT APPLICABLE (THIS REPORT SUMMARIZES PG&E'S RESPONSE TO THE QUAKE) | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-08-24 04:50 | 2014-08-24 05:05 | ONSHORE | CA | 94559 | MULTIPLE | MULTIPLE | MILEPOST | MULTIPLE | MULTIPLE | MULTIPLE | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | OTHER | MORE THAN ONE RESPONSE APPLIES |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | MORE THAN ONE RESPONSE APPLIES | 1968 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | MORE THAN ONE RESPONSE APPLIES | OTHER | [8 empty] | EARTHQUAKE | CLASS 3 LOCATION | NO |  | 1 |  | NO | YES | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 7500000 | 8296166.0726327 | 0 | 0 | 0 | 0 | PLEASE NOTE THAT EARTHQUAKE-RELATED GAS WORK IS ONGOING |  | 7500000 | 3808159.1368847 | 8296166.0726327 | [8 empty] | 0 |  | 0 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 1 | NO | [5 empty] | YES | NOT APPLICABLE AS THIS REPORT IS ON THE REPAIR AND RESPONSE WORK PERFORMED ON PG&E'S GAS TRANSMISSION SYSTEM (AND NOT A SPECIFIC LOCATION). | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS THE EARTHQUAKE. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [52 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | EARTHQUAKE |  |  |  |  | NO | [306 empty] | STEPHEN RAMOS | COMPLIANCE ENGINEER | s3rc@pge.com | 925-328-6107 |  |  |  |  | LARRY DENISTON | MANAGER REGULATORY COMPLIANCE | 925-328-5756 | lcd1@pge.com | AT APPROXIMATELY 0320 HOURS ON AUGUST 24, 2014, A MAGNITUDE 6.0 EARTHQUAKE STRUCK THE NAPA COUNTY REGION. PG&E CONDUCTED SPECIAL AERIAL PATROLS ON OVER 150 MILES OF TRANSMISSION PIPELINE. OVER 250 MILES OF TRANSMISSION PIPELINE UNDERWENT LEAK SURVEYS. PG&E IDENTIFIED FOUR LEAKS (ONE HAZARDOUS; THREE NON-HAZARDOUS) ON ITS GAS TRANSMISSION SYSTEM THROUGHOUT THE COUNTIES OF NAPA, SOLANO, AND SONOMA. THE FOUR LEAKS WERE FOUND ON VALVES (INSTALLED IN 1968, 1981, 1992, & 2004) AND WERE REPAIRED ON OR BEFORE SEPT. 5, 2014. SEVENTY-SIX REGULATOR STATIONS UNDERWENT SPECIAL LEAK SURVEYS AND NO LEAKS WERE DETECTED. FOLLOWING THE NAPA EARTHQUAKE, SURFACE CRACKS WERE DISCOVERED IN THE GROUND AT AN APPROXIMATE 74 DEGREE ANGLE ABOVE TRANSMISSION LINE L-21A, AND AS A PRECAUTION, THE PRESSURE IN L-21A WAS LOWERED FROM 325 PSIG TO 300 PSIG. LEAK SURVEYS AND AERIAL PATROLS HAVE INDICATED NO ANOMALIES WITH THIS LINE OTHER THAN THE GROUND DISPLACEMENT OVER IT. PG&E HAS REPLACED APPROXIMATELY 210 FEET OF 26-INCH PIPE ACROSS THE FAULT CROSSING. L-21A WAS PLACED BACK INTO SERVICE ON SEPTEMBER 13, 2014 AT THE TEMPORARILY REDUCED PRESSURE OF 300 PSIG. PENDING FINAL APPROVAL OF ITS FITNESS FOR SERVICE EVALUATION, L-21A WILL RETURN TO NORMAL OPERATING PRESSURE. L-21B WILL BE ISOLATED BETWEEN MLV 2.31 (NAPA RIVER CROSSING) AND MLV 6.05 AND TAKEN OUT OF SERVICE SO AN INSPECTION CAN BE PERFORMED. RESULTS OF INVESTIGATION WILL DETERMINE THE EXTENT OF L-21B PIPELINE REPLACEMENT AT THE FAULT CROSSING. L-21H PRESSURE WAS REDUCED FROM 250 PSIG TO 140 PSIG AS A PRECAUTIONARY MEASURE. THE FITNESS FOR SERVICE EVALUATION HAS BEEN COMPLETED AND L-21H WILL TO BE RETURNED TO NORMAL OPERATING PRESSURE SHORTLY. SAFETY-RELATED CONDITION REPORTS WERE SUBMITTED FOR L-21A AND L-21H. A SAFETY-RELATED CONDITION REPORT WILL BE SUBMITTED FOR L-21B IF REQUIRED. THERE ARE NO KNOWN INJURIES OR DEATHS RELATING TO PG&E'S GAS FACILITIES. PG&E REPORTED THIS INCIDENT TO THE DOT AND THE CPUC BASED ON OPERATOR JUDGMENT OF THE SIGNIFICANCE OF THIS EVENT. PLEASE NOTE THAT PG&E'S RESPONSES TO PARTICULAR SECTIONS OF THIS REPORT MAY NOT APPLY AS OUR REPORTING IS ON THE REPAIR AND RESPONSE WORK PERFORMED ON PG&E'S GAS TRANSMISSION SYSTEM AND NOT A SPECIFIC LOCATION. (NOTE: THE EARTHQUAKE MAGNITUDE HAS BEEN CORRECTED FROM 6.1 TO 6.0 IN THIS PHMSA 7100 SUPPLEMENTAL REPORT.) PLEASE NOTE THAT FOR PART A, QUESTION 11, "ESTIMATED VOLUME OF INTENTIONAL AND CONTROLLED RELEASE/BLOWDOWN." IS 1,099,000 MCF. PLEASE NOTE THAT FOR PART C, QUESTION 4, "YEAR ITEM INVOLVED IN ACCIDENT WAS INSTALLED," THERE ARE FOUR ITEMS TOTAL AND THAT THE EARLIEST YEAR WAS INPUTTED WITHIN THE BOX (1968).
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140099 | 16500 | 2014-09-25 16:41 | ORIGINAL FINAL | 18408 | SOUTH CAROLINA ELECTRIC & GAS CO | 220 OPERATION WAY MAIL CODE J48 | CAYCE | SC | 29033 | 2014-08-27 04:33 | 2014 |  |  | 33.794 | -80.951 | 1093594 | 2014-08-27 11:30 |  | NATURAL GAS |  | 1027 | 350 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-08-27 08:15 | 2014-08-27 23:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 100 | 2014-08-27 04:54 | 2014-08-27 05:57 | ONSHORE | SC | 29160 | SWANSEA | CALHOUN | MILEPOST | 1999 | DEVRO TAKE OFF @ HWY 176 VALVE STATION 25-82 | ST. MATTHEWS | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 3 |  | 0.216 | 35000 | API 5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | PAINT | [28 empty] | 1993 | 1992 | CARBON STEEL |  | OTHER | [8 empty] | 3RD PARTY DUMP TRUCK DROVE INTO VALVE STATION | CLASS 1 LOCATION | NO |  | 63 |  | NO | NO | NO |  | 10000 | 11061.5547635103 | 1970 | 2179.12628841152 | 5782 | 3858.04203152364 | 84657 | 93643.8041614488 | 8567 | 9476.43396589924 | 0 | 0 |  |  | 110976 | 57412.5396549098 | 120218.961210793 | [8 empty] | 600 |  | 946 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 69000 | YES | [7 empty] | YES |  | YES |  |  | YES | SMALL DIAMETER | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CAUSE OF INCIDENT WAS OBVIOUS TO BE AN OUTSIDE PARTY CAUSING VEHICULAR DAMAGE TO AN ABOVE GROUND VALVE STATION. CONTROL ROOM OPERATORS DISCOVERED ISSUES IN THE SYSTEM AND COMMUNICATED APPROPRIATELY. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [260 empty] | MELANIE MILLER | MANAGER OF REGULATORY ENGINEERING | melanie.miller@scana.com | 803-217-8996 | 803-733-4055 |  |  |  | MICHAEL GREENE | GENERAL MANAGER OF ENGINEERING SERVICES | (803)217-9191 | mgreene@scana.com | THE "DEVRO TAKE OFF @ HWY 176 VALVE STATION" IS A TRANSMISSION VALVE STATION IN CALHOUN COUNTY IN SOUTH CAROLINA, LOCATED APPROXIMATELY 13.5 MILES FROM THE TOWN OF ST. MATTHEWS. THE STATION PROVIDES SERVICE TO A TRANSMISSION LATERAL SERVING THE DEVRO INDUSTRIAL PLANT AS WELL AS THE DOWNSTREAM PORTION OF THE ST. MATTHEWS TRANSMISSION PIPELINE. THE STATION ITSELF RESIDES IN A PRIVATE EASEMENT WHILE THE PIPELINE THAT FEEDS IT RESIDES IN ROAD RIGHT-OF-WAY. THE STATION FOOTPRINT IS LOCATED APPROXIMATELY 30' FROM THE HWY 176 TRAVEL LANE. THE STATION HAD A GUARDRAIL IN PLACE TO PROTECT THE PIPELINE FACILITIES FROM VEHICLE DAMAGE. ON AUGUST 28, 2014 AT APPROXIMATELY 4:33 AM (AS DETERMINED BY POST-INCIDENT REVIEW OF SCADA LOGS), A DUMP TRUCK LEFT THE ROADWAY AND STRUCK THE VALVE STATION CAUSING A MAJOR LEAK ON THE ST. MATTHEWS TRANSMISSION PIPELINE. SCE&G'S SCADA SYSTEM REACHED ALARM CONDITIONS AT APPROXIMATELY 4:54 AM, AND SCE&G RECEIVED A CONFIRMING CALL FROM THE LOCAL FIRE DEPARTMENT REPORTING THE INCIDENT AT APPROXIMATELY 4:58 AM. COMPANY FIRST RESPONDERS WERE NOTIFIED AND DISPATCHED AT APPROXIMATELY 5:02 AM AND ARRIVED ON SITE AT APPROXIMATELY 5:57 AM. THE FIRE DEPARTMENT AIDED IN CLOSING THE ROAD TO TRAFFIC, EVACUATING NEARBY RESIDENTS WITHIN 500 FT OF THE INCIDENT, AND INFORMING THE SCHOOL DISTRICT OF THE INCIDENT. ONE SCHOOL, LOCATED APPROXIMATELY 3 MILES AWAY, ELECTED TO CLOSE FOR THE DAY DUE TO THE DISRUPTION OF TRAFFIC THAT WOULD RESULT FROM THE ROAD CLOSURE. WITHIN THE 500 FT RADIUS OF EVACUATION, CONDUCTED BY THE LOCAL EMERGENCY TEAMS, THERE ARE APPROXIMATELY 8 HOMES. IN REFERENCE TO PART A QUESTION 18 OF THE INCIDENT REPORT, THE NUMBER OF PERSONS EVACUATED WAS PROVIDED BY THE LOCAL FIRE DEPARTMENT WHO CONDUCTED THE EVACUATIONS; HOWEVER, FIRE SERVICES PERSONNEL DID NOT HAVE AN EXACT COUNT OF EVACUEES BUT CONSERVATIVELY ESTIMATED THE NUMBER TO BE 100. AT APPROXIMATELY 8:15 AM, SCE&G VALVED THE PIPELINE OUT OF SERVICE TO SHUT OFF THE ESCAPING GAS. ALSO, AS A RESULT OF THE INCIDENT AND VALVING THE LINE OUT OF SERVICE, TWO INDUSTRIAL CUSTOMERS LOST SERVICE. SCE&G WAS ABLE TO UTILIZE DOWNSTREAM LINEPACK AND A COMPRESSED NATURAL GAS (CNG) TRAILER TO MAINTAIN SERVICE TO TWO SMALL DISTRIBUTION SYSTEMS FEEDING THE TOWNS OF ST. MATTHEWS AND CAMERON. SCE&G COMPLETED REPAIRS TO THE MAINLINE PORTION OF THE VALVE STATION BY 7:30 PM, REESTABLISHING THE FEED TO THE TOWNS OF ST. MATTHEWS AND CAMERON. SCE&G COMPLETED THE REMAINING REPAIRS TO THE DEVRO LATERAL TAKE-OFF PORTION OF THE STATION BY 11:30 PM, RESTORING SERVICE TO THE DEVRO PLANT. THE REPAIRS MADE AT THE TIME OF THE INCIDENT WERE TEMPORARY WITH PLANS TO REBUILD THE STATION AT A LATER DATE. NOTE: PART C QUESTION 3.G (YEAR OF MANUFACTURE) FOR THE PIPE INVOLVED IN THE INCIDENT IS UNKNOWN. - AN ESTIMATE DATE OF 1992 WAS USED - ESTIMATED BY A MATERIAL RECORD FOR ELBOWS USED IN THE STATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140100 | 16503 | 2014-09-30 09:34 | ORIGINAL FINAL | 31286 | ONEOK GAS TRANSPORTATION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2014-09-03 09:52 | 2014 |  |  | 36.2327 | -95.7579 | 1094357 | 2014-09-04 12:24 |  | NATURAL GAS |  | 8662 | 7769 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-09-03 20:10 | 2014-09-06 22:10 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-09-03 10:31 | 2014-09-03 10:31 | ONSHORE | OK | 74015 | CATOOSA | ROGERS |  |  | A-1170 |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 164 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 |  | 0.281 | 60000 | API-5LX | DSAW |  | KAISER STEEL | COAL TAR | [28 empty] | 1974 | 1974 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | YES | METHOD2 | 370 |  | NO | NO | NO |  | 5000 | 5530.77738175513 | 27192 | 30078.5797129371 | 30317 | 20229.0315236427 | 60800 | 67254.2529621424 | 40000 | 44246.219054041 | 0 | 0 |  |  | 163309 | 88499.6488409801 | 167338.860634518 | [8 empty] | 430 |  | 500 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 36220 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS VERY SMALL AND COULD NOT HAVE BEEN DISCOVERED THROUGH THE SCADA SYSTEM. CONTROLLER RESPONDED QUICKLY ONCE NOTIFIED BY PUBLIC SOURCES. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [7 empty] | YES | [14 empty] | YES | [63 empty] | YES | YES |  |  | YES |  |  |  | 2012 | [31 empty] | 2012 | [23 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | PATTI FORD | SENIOR PIPELINE SAFETY ENGINEER | patti.ford@oneok.com | 918 588 7131 | 918 732 1311 |  |  |  | WESLEY R. DUNBAR | VICE PRESIDENT | 918 588 7424 | wesley.dunbar@oneok.com | ON WEDNESDAY, SEPTEMBER 3, 2014, A ONEOK GAS TRANSPORTATION (OGT) CUSTOMER REPORTED VENTING GAS FROM A VALVE EXTENSION CAN ON OGT'S 24-INCH, LINE A-1170 MAINLINE AT THE MAIN ENTRANCE TO THE PORT OF CATOOSA NEAR CATOOSA, OKLAHOMA. THE ENTRANCE TO THE PORT WAS CLOSED TO TRAFFIC BY PORT AUTHORITIES AS A PRECAUTIONARY MEASURE. THE PIPELINE PRESSURE WAS REDUCED FROM 430 PSIG TO 300 PSIG UNTIL CUSTOMERS COULD SAFELY SHUT DOWN THEIR PROCESSES, AND THE PIPELINE WAS THEN BLOWN DOWN. THERE WERE NO INJURIES OR DEATHS, NOR WAS THERE ANY FIRE ASSOCIATED WITH THIS INCIDENT. THERE WAS SOME LOCAL MEDIA COVERAGE. THE LEAK WAS DETERMINED TO BE A CRACK LOCATED ON AN 8-INCH SADDLE FOR A SIDE TAP OFF THE A-1170 MAINLINE. THE LEAK WAS REPAIRED BY INSTALLING A NEW BRANCH CONNECTION. REPAIRS WERE COMPLETED SATURDAY, SEPTEMBER 6, 2014, AND THE MAINLINE WAS RETURNED TO SERVICE SATURDAY EVENING.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140101 | 16504 | 2014-10-01 08:20 | ORIGINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2014-09-02 22:10 | 2014 |  |  | 41.8837 | -75.1423 | 1094204 | 2014-09-03 02:02 |  | NATURAL GAS |  | 9060 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES | [7 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-09-02 22:10 | 2014-09-02 23:25 | ONSHORE | NY | 12760 | LONG EDDY | DELAWARE COUNTY |  |  | HANCOCK COMPRESSOR STATION |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [8 empty] | CARBON STEEL |  | OTHER | [8 empty] | ESD VALVE FAILED TO CLOSE | CLASS 1 LOCATION | NO |  | 215 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 35696 | 23818.1716287215 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 35696 | 24693.3800350263 | 23818.1716287215 | [8 empty] | 905 |  | 1350 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INVESTIGATION OF THE CONTROLLER OR THE CONTROL ROOM SINCE THIS INCIDENT WAS INITIATED BY AN EXTERNAL FACTOR (LOSS OF COMMERCIAL POWER TO THE FACILITY). | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [52 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | A LINE OF SEVERE THUNDERSTORMS WAS TRAVERSING THE AREA GENERATED A FLOW OF LIGHTENING STRIKES INTERRUPTING COMMERCIAL POWER TO THE FACILITY. | YES |  |  |  | YES | SEVERE THUNDERSTORMS ASSOCIATED WITH LIGHTENING STRIKES. | [301 empty] | GEORGE HAMATY | ENGINEER | ghamaty@nisource.com | 3043573728 | 3043573522 |  |  |  | PERRY MICHAEL HOFFMAN | MANAGER | 3043572548 | mikehoffman@nisource.com | ON TUESDAY, SEPTEMBER 2, 2014, MILLENNIUM PIPELINE COMPANY, LLC'S HANCOCK COMPRESSOR STATION (CS) LOCATED IN DELWARE COUNTY, NY WAS IN THE PATH OF A LINE OF SEVERE THUNDERSTORMS TRAVELING THROUGH THE REGION. A LIGHTNING STRIKE DAMAGED AN ELECTRIC TRANSFORMER THAT FEEDS THE HANCOCK CS AREA CAUSING LOSS OF COMMERCIAL ELECTRICAL POWER. DURING THE POWER OUTAGE, THE STATION'S EMERGENCY GENERATOR STARTED BUT POWER FAILED TO FULLY TRANSFER TO THE STATION'S RESERVE POWER IN AN AMOUNT OF TIME CAUSING STATION'S PNEUMATIC COMPRESSORS TO FAULT (AND NOT RESTART). THE LOSS OF PNEUMATIC PRESSURE CAUSED THE STATION EMERGENCY SHUTDOWN VENT VALVES TO OPEN (A FAIL-SAFE POSITION). HOWEVER, DUE TO THE STATION'S LOW PNEUMATIC PRESSURE SWITCH FAILING TO TRIGGER A STATION EMERGENCY SHUTDOWN, THE STATION ISOLATION (BLOCK) VALVES REMAINED IN THE OPEN POSITION CAUSING THE UNINTENDED RELEASE OF NATURAL GAS INTO THE ATMOSPHERE. ADJUSTMENTS WERE MADE TO THE GENERATOR'S RESPONSE SETTINGS AND THE STATION'S LOW PNEUMATIC PRESSURE SWITCH TO PREVENT A SIMILAR FAULT FROM RE-OCCURRING. THE DAYS FOLLOWING THIS INCIDENT, SEVERAL TESTS WERE CONDUCTED TO ASSURE THE SUCCESSFUL START OF THE BACK-UP GENERATOR IN THE EVENT OF THE COMMERCIAL ELECTRIC POWER LOSS AS WELL AS THE CORRECT OPERATION OF THE LOW PNEUMATIC PRESSURE SWITCH. DURING THE TESTING, THE BACK-UP GENERATOR STARTED SUCCESSFULLY WHENEVER THE COMMERCIAL ELECTRIC POWER WAS DISCONNECTED FROM THE MAIN BUS POWER SYSTEM AND THE LOW PRESSURE SWITCH FUNCTIONED WITH NO FAILURES BEING NOTED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140102 | 16601 | 2014-10-01 23:17 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2014-09-01 11:50 | 2014 |  |  | 29.583 | -95.163 | 1094150 | 2014-09-02 12:05 |  | NATURAL GAS |  | 18645 | 17.2 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-09-01 15:35 | 2014-09-02 10:35 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-09-02 09:30 | 2014-09-02 10:25 | ONSHORE | TX | 77598 | WEBSTER | HARRIS |  |  | ELLINGTON COMPRESSOR STATION | LINE 15 TEXAS CITY EXTENSION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2008 |  | CARBON STEEL |  | OTHER | [8 empty] | 2" BYPASS VALVE AROUND THE ESD ISOLATION VALVE WAS INADVERTENTLY LEFT PARTIALLY OPEN THUS, ALLOWING GAS TO VENT TO ATMOSPHERE. | CLASS 1 LOCATION | NO |  | 373 |  | NO | NO | NO |  | 0 | 0 | 68 | 75.2185723918698 | 73368 | 48954.8301225919 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 73436 | 50788.2225809613 | 49030.0486949838 | [8 empty] | 663 |  | 731 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) | [11 empty] | YES | SIGNALS WERE NOT CONFIGURED TO ALARM IN CONTROL ROOM. | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [204 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | [5 empty] | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | MICHAEL D. SMITH | COMPLIANCE SPECIALIST | mdsmith@eprod.com | 713-381-5650 |  |  |  |  | MICHAEL D. SMITH | COMPLIANCE SPECIALIST | 713-381-5650 | mdsmith@eprod.com | ON 9/1/2014, TWO INSTRUMENT AIR COMPRESSORS SHUT DOWN CAUSING A LOW-LOW INSTRUMENT AIR SIGNAL; AS A RESULT, THE EMERGENCY SHUTDOWN (ESD) WAS INITIATED. AN ENTERPRISE EMPLOYEE DISCOVERED THE INCIDENT AND IDENTIFIED THAT A 2" BYPASS VALVE AROUND THE ESD ISOLATION VALVE WAS INADVERTENTLY LEFT PARTIALLY OPEN, THUS ALLOWING GAS TO BYPASS THE ISOLATION VALVE AND VENT GAS TO THE ATMOSPHERE. OPERATIONS PERSONNEL CLOSED THE VALVE TO END THE EVENT. INVESTIGATION IDENTIFIED THAT THE ESD SIGNAL DID NOT ALARM IN THE CONTROL ROOM; THE SIGNAL WAS CONFIGURED TO ALARM IN THE CONTROL ROOM AND POINT-TO-POINT VERIFICATIONS WERE COMPLETED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140103 | 17033 | 2014-10-07 17:00 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2014-09-09 18:40 | 2014 |  |  | 37.3086 | -97.1146 | 1094871 | 2014-09-09 20:26 |  | NATURAL GAS |  | 1760 | 205 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-09-09 20:05 | 2014-09-10 04:44 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-09-09 18:40 | 2014-09-09 20:05 | ONSHORE | KS | 67156 | VERNON | COWLEY | SURVEY STATION NO. | 100/72+81 | AH-001 | UDALL 3" | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 40 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 3 |  | 0.156 | 35000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1977 | 1977 | CARBON STEEL |  | MECHANICAL PUNCTURE | 1.5 | 11 | [7 empty] | CLASS 1 LOCATION | NO |  | 30 |  | NO | NO | NO |  | 1120 | 1238.89413351315 | 756 | 836.253540121376 | 6494 | 4333.12434325744 | 9000 | 9955.39928715923 | 3000 | 3318.46642905308 | 0 | 0 |  |  | 20370 | 11537.9489178583 | 19682.1377331043 | [8 empty] | 139 |  | 150 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 35040 | NO | YES |  | YES |  |  |  |  | YES |  | YES |  |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ALL SCADA ALARMS WERE HANDLED CORRECTLY AND CONTROLLERS FOLLOWED PROCEDURES. THE INCIDENT WAS DISCOVERED BY THE SYSTEM AND ALL APPROPRIATE PARTIES WERE NOTIFIED. THE CAUSE OF THE INCIDENT WAS THE RESULT OF A MISS MARKED LINE. | [12 empty] | YES | 1 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | NO |  |  | YES | PRIVATE LANDOWNER | YES | [6 empty] | CONTRACTOR | TRENCHER | TELECOMMUNICATIONS | YES | 14381628 |  | UNKNOWN/OTHER | NO | NO | YES | 9 | OTHER |  |  |  | LOCATING PROCEDURES WERE NOT FOLLOWED. PIPE FACILITIES WERE NOT MARKED. | [262 empty] | DAVID COOMES | PIPELINE COMPLIANCE ENGINEER | david.coomes@sscgp.com | [5 empty] | DAVID SINCLAIR | PIPELINE COMPLIANCE MANAGER | 270.852.4424 | david.l.sinclair@sscgp.com | SSCGP GAS CONTROL NOTIFIED MEASUREMENT ON 9/9/14 AT 18:40 OF A "LOW LOW" PRESSURE ALARM AT THE UDALL TOWNBORDER. MEASUREMENT BEGAN LOOKING FOR ANOTHER EMPLOYEE THAT WOULD BE CLOSER TO THE SITE. AT 18:55 GAS CONTROL RECEIVED A CALL FROM DISPATCH STATING THAT A CONTRACTOR INSTALLING FIBER OPTIC LINE HAD HIT THE SSC LINE AT 21ST ROAD AND 118TH. AT THIS TIME THE FIRE DEPARTMENT AND HIGHWAY PATROL WERE IN ROUTE AND NO FIRES OR INJURIES WERE REPORTED. GAS CONTROL MADE A SECOND CALL TO MEASUREMENT GIVING AN ETA OF 1 HOUR. MEASUREMENT AND OPERATIONS ARRIVED ON SITE AND SHUT IN THE SEGMENT AT THE MAINLINE GATE VALVE AT 20:05 ON 9/9/2014. THE LINE WAS EXCAVATED AND REPAIRED BY PIPE REPLACEMENT. THE LINE WAS RETURNED TO SERVICE AT 4:44 ON 9/10/2014.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140104 | 16626 | 2014-10-07 17:11 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2014-09-22 15:00 | 2014 |  |  | 42.8058 | -93.296 | 1096143 | 2014-09-22 18:09 |  | NATURAL GAS |  | 407 | 253 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-09-23 11:00 | 2014-09-24 17:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-09-22 15:00 | 2014-09-22 16:45 | ONSHORE | IA | 50475 | SHEFFIELD | FRANKLIN | MILEPOST | 2.5 | SHEFFIELD 4-INCH BRANCH LINE | IAB54101 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 4 |  | 0.188 | 35000 | 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | REPUBLIC | COAL TAR | [28 empty] | 1961 | 1961 | CARBON STEEL |  | MECHANICAL PUNCTURE | 2 | 1 | [7 empty] | CLASS 1 LOCATION | NO |  | 78 |  | NO | NO | NO |  | 1500 | 1659.23321452654 | 971 | 1074.07696753685 | 1562 | 1042.24518388792 | 32544 | 35998.7238223678 | 22517 | 24907.3028609961 | 42383 | 46882.1875541855 | EMPLOYEE EXPENSES AND OUTSIDE SERVICES |  | 101477 | 51812.8389287583 | 111563.769603501 | [8 empty] | 650 |  | 800 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 47000 | NO | [5 empty] | YES | SMALL PIPELINE DIAMETER | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE WAS STRUCK BY A TILING MACHINE INSTALLING AGRICULTURAL DRAIN TILE WITHOUT A ONE-CALL TICKET | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | YES | [6 empty] | FARMER | TRENCHER | DRAINAGE | NO | [5 empty] | NO |  | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | JOHN GORMLEY | SR. CORROSION SPECIALIST | john.gormley@nngco.com | 402-398-7494 |  |  |  |  | TOM CORRELL | DIRECTOR OF PIPELINE SAFETY AND RISK | 402-398-7715 | thomas.correll@nngco.com | ON SEPTEMBER 22, 2014 AT APPROXIMATELY 15:56 NORTHERN'S OPERATIONS COMMUNICATION CENTER RECEIVED A CALL FROM FRANKLIN COUNTY EMERGENCY RESPONSE CENTER THAT THERE WAS BLOWING GAS FROM THE SHEFFIELD 4-INCH (IAB54101) BRANCH LINE. PROPERTY OWNER ROY PLAGGE HAD BEEN INSTALLING AGRICULTURAL DRAINAGE TILE IN AN UNHARVESTED CORN FIELD. PLAGGE IMMEDIATELY CALLED 911 AFTER THE BLOWING GAS WAS DETECTED. PLAGGE DID NOT HAVE A ONE-CALL TICKET AND NO UNDERGROUND UTILITIES WERE MARKED. THE TILING MACHINE PUNCTURED THE 4-INCH CREATING A HOLE ABOUT 2 INCHES LONG BY 1 INCH WIDE. THE PLOW TOOTH STUCK IN THE PIPE PROVIDED SOME LEAK STOPPAGE EFFECTS. THIS ALLOWED NORTHERN TO PROCEED SLOWLY AND DELIBERATELY WITH THE REPAIRS WITHOUT THE THREAT OF LOSING SERVICE. NORTHERN REPLACED 29 FEET OF 4-INCH PIPE AT THE PUNCTURE SITE. THE REPLACEMENT PIPE WAS PRETESTED 4-INCH, 0.250-INCH WALL THICKNESS PIPE. NORTHERN ALSO FOUND ANOTHER SPOT ABOUT 80 FEET DOWNSTREAM WHERE THE TILING MACHINE HAD CAUSED A GREATER THAN 6% DENT WITH METAL LOSS. TWENTY FIVE FEET OF PIPE WAS INSTALLED AT THIS LOCATION. MR PLAGGE HAS RECEIVED MAILINGS AND BROCHURES FROM NORTHERN'S PUBLIC AWARENESS PROGRAM FOR SEVERAL YEARS. HE IS AWARE OF THE ONE CALL SYTEM AND EVEN USED IT IN THE PAST ON THIS PROPERTY. NO CUSTOMERS LOST NATURAL GAS SERVICE DURING THE REPAIRS. EVEN FARM TAP CUSTOMERS NEVER LOST SERVICE THANKS TO NORTHERN'S VOLUME BOTTLE TRAILERS AND WARMER WEATHER.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20140105 | 16566 | 2014-10-13 08:47 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2014-09-15 12:00 | 2014 |  |  | 29.0177 | -90.898 | 1095398 | 2014-09-15 15:35 |  | NATURAL GAS |  | 0.1 | 14000 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-09-15 16:22 | 2014-09-29 16:03 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-09-15 12:10 | 2014-09-15 12:10 | OFFSHORE | [28 empty] | 20 | IN STATE WATERS | LA | SHIP SHOAL | SS47/STATE LEASE 147922 | TERREBONNE |  |  |  | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | WELD/FUSION |  | 26 |  | 0.5 | 52000 | API 5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | U.S. STEEL CORP | OTHER | EXTERNAL COATING TYPE - ASPHALT WITH 3 INCH OF CONCRETE. | [8 empty] | PIPE GIRTH WELD | [18 empty] | 1969 | 1969 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 474 |  | NO | NO | NO |  | 0 | 0 | 56546 | 62548.6675657451 | 404 | 269.569176882662 | 475000 | 525423.851266737 | 75000 | 82961.660726327 | 0 | 0 |  |  | 606950 | 308255.966851403 | 671203.748735692 | [8 empty] | 697 |  | 1440 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 91661 | NO | [5 empty] | YES | PIG TRAPS WERE NOT DESIGNED TO ACCOMMODATE INTERNAL INSPECTION TOOLS. | YES |  |  | YES |  | YES | PIPLINE DESIGN. | OFFSHORE GATHERING | YES | YES | YES | NO | NO | OTHER | BY OTHER PRODUCER EMPLOYEES WORKING NEAR THE LEAK LOCATION. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS VERY SMALL, MINIMAL PRESSURE CHANGE, THEREFORE CONTROLLERS WOULD NOT HAVE DETECTED LEAK. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN | [5 empty] | YES | THIS PIPELINE TRANSPORTS UNPROCESSED UNDEHYDRATED GAS, SINCE 1990. | YES |  | YES | UT INSPECTION BY DIVERS RESULTED IN NO EXTERNAL CORROSION. | YES | [5 empty] | YES | NO | YES | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | JOHNNY LOPEZ | REGULATORY COMPLIANCE SPECIALIST | johnny.lopez@williams.com | 7132152995 | 713-215-2222 |  |  |  | MARIE SOTAK | MANAGER PIPELINE AND PROCESS SAFETY | 7132152111 | marie.sotak@williams.com | WILLIAMS - TRANSCO DISTRICT MANAGER WARREN TOUPS WAS NOTIFIED BY DAN MCKNIGHT FROM HELIS ON 9-15-14 AT 9:15AM THAT THEY WERE INVESTIGATING SOME BUBBLES IN THE SS 47 AREA, NEAR WHERE THEIR 4" PIPELINE CROSSED OVER TRANSCO'S 26" LINE. DAN STATED THEY FIRST NOTICED THE BUBBLES ABOUT 3:30PM ON 9-13-14. THE BARELY VISIBLE SHEEN COVERED APPROXIMATELY 300 FEET WIDE BY 2600 FEET LONG WITH 50% COVERAGE. THEY REPORTED THE LEAK & SHEEN TO NRC AT 6:10PM, NRC #1095249. TRANSCO WAS INFORMED THAT HELIS HAD SHUT-IN AND BLOWN DOWN THEIR WELLS. THIS LED THEM TO BELIEVE THE BUBBLES WERE POSSIBLY COMING FROM THE TRANSCO 26" LINE. HELIS ALSO UTILIZED THE SERVICES OF OIL MOPS(OSRO) TO CONTAIN THE SHEEN AND THE SERVICES OF BLACKWATER DIVERS WHO HAD ARRIVED AT THE LOCATION EARLIER THAT MORNING. WE (TRANSCO) PLOTTED COORDINATES ON OUR ALIGNMENT SHEETS, BUT IT PLOTTED OUT ABOUT 1500 FEET FROM TRANSCO 26". OUR TECHNICIANS, WERE SENT OUT BY HELICOPTER TO FLY OVER LEAK SITE AND LAND AT SS 45 PLATFORM(HELIS OWNED). AT 11:35AM, OUR TECHNICIAN CALLED WITH DETAILS OF THE SHEEN WHICH WAS VERY LIGHT AND MEASURED 5 MILES LONG AND 300 FEET WIDE WITH ABOUT 30% COVERAGE. OUR TECHNICIAN RELAYED TO US UPDATED COORDINATES TAKEN BY THE HELICOPTER. HE TOOK A FIELD BOAT TO LEAK SITE AND WAS INFORMED BY BLACKWATER DIVERS THEY SUSPECTED THAT THE BUBBLES WERE COMING FROM TRANSCO 26" LINE. AT 1:35PM, TRANSCO SCHRIEVER OFFICE WAS INFORMED THAT BUBBLES WERE COMING FROM THE TRANSCO 26" PIPELINE. HELIS CALLED O'BRIENS AT 12 NOON ON 9-15-14 TO INFORM THEM THAT THE LEAK DID NOT BELONG TO HELIS. SCHRIEVER OFFICE ASSUMED THE ORIGINAL NRC #1095249 THAT HELIS HAD CALLED IN WOULD ALSO APPLY TO TRANSCO LEAK ON THE 26" PIPELINE. AFTER CONFIRMING WITH BUD KLINE AND WITH O'BRIEN'S THAT ANOTHER NRC # WAS NECESSARY, TOUPS CONTACTED O'BRIEN'S AT 3:13PM AND WILLIAMS (TRANSCO) GAS CONTROL AT 3:20PM. O'BRIENS CONTACTED NRC AT 3:35PM AND RECEIVED NRC #1095398. O'BRIEN'S ALSO CONTACTED LA. STATE POLICE AT 3:42PM AND RECEIVED #14-04128. SCHRIEVER DISTRICT PERSONNEL ISOLATED THE 26" PIPELINE SEGMENT 5103 AT SHIP SHOAL 70 PLATFORM AND AT DOG LAKE GENERATOR PLATFORM AT 4:22PM. NEGOTIATIONS CONTINUED BETWEEN TRANSCO & HELIS TO UTILIZE THE OSRO (OIL MOPS) AND BLACKWATER DIVERS AS WELL AS THE LIFT BOAT ON LOCATION THE DIVERS WERE USING. TRANSCO WAS ABLE TO UTILIZE OIL MOPS PERSONNEL AND EQUIPMENT, BUT NOT BLACKWATER DIVERS AND LIFT BOAT. SCHRIEVER THEN REQUESTED OIL MOPS PERSONNEL TO USE ABSORBENT BOOM TO ENCIRCLE THE BUBBLES, CAPTURING ANY SHEENING WITHIN THE BOOM. A DIVE VESSEL THAT WAS BEING USED BY TRANSCO ON ANOTHER JOB, WAS REQUESTED TO RELOCATE TO LEAK LOCATION AS SOON AS POSSIBLE. INCLEMENT WEATHER CAUSED SOME DELAYS WITH THE PIPELINE BLOWDOWN AND THE REPAIR. SUMMARY OF LEAK INVESTIGATION & REPAIR OF THE LEAK: DIVERS WERE SENT DOWN TO THE LEAKING PIPE, THEY PERFORMED A UT SCAN ON ALL SIDES OF THE LEAKING PIPE AND VERIFIED THAT THE THE LEAK WAS NOT EXTERNAL. THE LEAK OCCURRED ON THE LOW POINT OF THE PIPE, NEAR THE 6 O'CLOCK POSITION. A CLAMP WAS USED TO REPAIR THE LEAK AND THE LINE WAS GRADUALLY PRESSURED BACK UP TO MAOP ON 9-29-2014 AT 3:15 PM; NO LEAKS WERE DETECTED. THE HISTORY OF THIS GATHERING PIPELINE SYSTEM HAS BEEN THE TRANSPORTATION OF UNPROCESSED UNDEHYDRATED NATURAL GAS SINCE 1990. TRANSCO FOLLOWS HAS A STRICT INTERNAL CORROSION MONITORING AND CONTROL POLICY, THIS LINE HAS BEEN TREATED SINCE 1990 WITH CORROSION INHIBITORS AND BIOCIDES. SAMPLES ARE COLLECTED AND RESIDUALS ARE MONITORED MONTHLY. FIELD TECHNICIANS MEASURE CHEMICAL QUANTITIES AND CHEMICAL INJECTION PUMP OPERATIONS MONTHLY. INTERNAL CORROSION LEAK DOCUMENTATION IS PROVIDED TO ASSET INTEGRITY INTERNAL CORROSION ENGINEERS FOR RECOMMENDATIONS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140106 | 17057 | 2014-10-16 14:30 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2014-09-16 01:59 | 2014 |  |  | 42.1163 | -86.3651 | 1095426 | 2014-09-16 05:09 |  | NATURAL GAS |  | 99800 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-09-16 05:10 | 2014-12-13 12:55 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 550 | 2014-09-16 02:25 | 2014-09-16 03:59 | ONSHORE | MI | 49022 | BENTON HARBOR | BERRIEN | MILEPOST | MP 933.6 | ANR 0-100 LINE | MLV 61 - MLV 62 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 54 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 22 |  | 0.25 | 52000 | API-5L | FLASH WELDED |  | AO SMITH | COAL TAR | [28 empty] | 1960 | 1949 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 600 | 12 |  | CLASS 1 LOCATION | NO |  | 503 |  | NO | NO | NO |  | 80000 | 88492.4381080821 | 0 | 0 | 445000 | 296926.444833625 | 4280000 | 4734345.43878239 | 10000 | 11061.5547635103 | 0 | 0 |  |  | 4815000 | 2526724.5182707 | 5130825.87648761 | [8 empty] | 805 |  | 850 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | AUTOMATIC | 80419 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  |  |  | YES |  |  |  |  | YES | 1. ENHANCEMENT OF INFORMATION AVAILABLE TO THE CONTROL ROOM. 2. IMPROVEMENTS AND CLARIFICATIONS TO PROCEDURES. 3. BENEFIT OF ADDITIONAL TRAINING. | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED |  | YES | [15 empty] | STRESS CORROSION CRACKING | [5 empty] | YES | [63 empty] | YES | YES |  |  | YES |  |  | YES | 2009 | [31 empty] | 2009 | [17 empty] | COMBINATION TOOL | 2009 |  |  |  |  | YES | 1968 | 1173 | NO | [13 empty] | NO | [63 empty] | ROBERT CADORIN | REGULATORY COMPLIANCE SPECIALIST | robert_cadorin@transcanada.com | 248-205-7669 | 248-205-5369 |  |  |  | ROBERT CADORIN | REGULATORY COMPLIANCE SPECIALIST | 248-205-7669 | robert_cadorin@transcanada.com | ON SEPTEMBER 16, 2014, ANR PIPELINE COMPANY EXPERIENCED A PIPELINE BREAK AT APPROXIMATE MILEPOST 933.6 ON THE 22-INCH 100 LINE NEAR BENTON HARBOR, BERRIEN COUNTY, MICHIGAN. THE PIPELINE BREAK HAS BEEN REPAIRED AND RETURNED TO SERVICE PER PHMSA APPROVAL ON DECEMBER 13, 2014.
2021-02-26 10:37 | YES | YES | GT (Gas Transmission) | 20140107 | 30781 | 2014-10-17 10:46 | SUPPLEMENTAL FINAL | 11824 | LOUISVILLE GAS & ELECTRIC CO | 220 W MAIN ST, PO BOX 32010 | LOUISVILLE | KY | 40202 | 2014-09-17 16:51 | 2014 |  |  | 38.3708 | -85.5905 | 1095646 | 2014-09-17 19:10 |  | NATURAL GAS |  | 7000 | 0 | 0 | NO | [5 empty] | 0 | YES | 0 | 1 | 0 | 0 | 0 | 1 |  | YES |  | 2014-09-17 20:29 | 2014-09-19 03:35 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 100 | 2014-09-17 16:51 | 2014-09-17 16:51 | ONSHORE | KY | 40059 | PROSPECT | OLDHAM COUNTY | SURVEY STATION NO. | 69872 | BALLARDSVILLE | SEGMENT 14.0 (HWY 42) | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 48 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | MECHANICAL COUPLING | 1998 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | YES | METHOD2 | 165 |  | NO | NO | NO |  | 52000 | 57520.0847702534 | 0 | 0 | 30709 | 20490.5936952715 | 262000 | 289812.734803969 | 60000 | 66369.3285810616 | 950000 | 1050847.70253347 | RESTORATION/RE-LIGHT EFFORT |  | 1354709 | 693510.555194717 | 1485040.44438403 | [8 empty] | 250 |  | 400 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 35500 | NO |  | YES |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS A RESULT OF A MECHANICAL COUPLING FAILURE AND NOT ANY CONTROL ROOM ISSUES. | [12 empty] | YES | 4 | 0 | YES | 4 | 0 | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | OTHER | MECHANICAL COUPLING |  |  |  | YES |  |  | YES | [6 empty] | YES | [165 empty] | PETER CLYDE | MANAGER GAS REGULATORY COMPLIANCE | peter.clyde@lge-ku.com | 502-364-8715 | 502-217-2535 |  |  |  | GREG CORNETT | ASSOCIATE GENERAL COUNSEL | 502-627-2756 | greg.cornett@lge-ku.com | THE PIPELINE WAS EXCAVATED SO MODIFICATIONS COULD BE MADE TO ALLOW PASSAGE OF IN LINE INSPECTION TOOLS. WITHIN THE EXCAVATION, A MECHANICAL COUPLING WAS EXPOSED. SHORTLY THEREAFTER, THE PIPELINE SEPARATED FROM THE MECHANICAL COUPLING, WHICH RESULTED IN A RELEASE OF GAS. NO IGNITION OR EXPLOSION OCCURRED. REPAIRS WERE MADE PROMPTLY AND THE PIPELINE WAS RETURNED TO SERVICE ON SEPTEMBER 19, 2014.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140108 | 16613 | 2014-10-21 08:18 | SUPPLEMENTAL FINAL | 15105 | PANHANDLE EASTERN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2014-09-23 00:45 | 2014 |  |  | 40.2258 | -85.8425 | 1096161 | 2014-09-23 02:43 |  | NATURAL GAS |  | 3164 | 13490 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-09-23 03:45 | 2014-09-25 14:37 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 2 | 2014-09-23 02:02 | 2014-09-23 02:02 | ONSHORE | IN | 46036 | ELWOOD | MADISON | SURVEY STATION NO. | 1602+39 | ZIONSVILLE 100 | ZIONSVILLE 100 BTW 103 & 105 GATE VALVE | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | FARM TAP RISER | 1936 |  | CARBON STEEL |  | OTHER | [8 empty] | VEHICLE ACCIDENT INVOLVING FARM TAP RESULTING IN RELEASE AND FIRE. | CLASS 1 LOCATION | NO |  | 418 |  | NO | NO | NO |  | 3200 | 3539.69752432328 | 41324 | 45710.7689047298 | 12370 | 8253.88791593695 | 5525 | 6111.50900683942 | 3953 | 4372.63259801561 | 11417 | 12628.9770734997 | RETURN TO SERVICE. |  | 77789 | 41773.9753954036 | 80617.4730233447 | [8 empty] | 578 |  | 760 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 98155 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A THIRD PARTY VECHICLE STRUCK AN ABOVE GROUND FACILITY. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [260 empty] | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713.857.5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | 713.857.5479 | nathan.hlavaty@energytransfer.com | THIS SUPPLEMENTAL REPORT DATED 01/13/15, IS TO UPDATE THIS NARRATIVE SECTION PER A REQUEST BY THE PHMSA CENTRAL REGION. A VEHICLE ACCIDENT AFFECTING A FARM TAP RESULTING IN A RELEASE AND SUBSEQUENT FIRE WAS REPORTED BY MADISON CO SHERIFF'S OFFICE TO PEPL GAS CONTROL AT 12:47PM EDT ON 9/23/2014. THE LIST BELOW IDENTIFIES THE ACTIONS FOLLOWING INITIAL NOTIFICATION IN CHRONOLOGICAL ORDER. NO INJURIES WERE REPORTED AS A RESULT OF THE INCIDENT. PROPERTY DAMAGE CONSISTED OF THE THIRD-PARTY VEHICLE (ESTIMATED AT $3,200) AND OPERATOR PROPERTY DAMAGE AND REPAIRS OF $5,525. 12:45 AM EDT: LOCAL RESIDENT CONTACTED MADISON COUNTY 911 CALL CENTER REPORTING "BLOWING GAS AND FIRE" 12:46 AM EDT: MADISON COUNTY SHERIFF DISPATCHED THE FOLLOWING AGENCIES/EMERGENCY RESPONDERS O PIKE CREEK FIRE DEPT., MADISON CO. SHERIFF, ELWOOD AMBULANCE, MADISON CO. EMA, FRANKTON POLICE, AND ELWOOD POLICE 12:47 AM EDT: MADISON CO. SHERIFF CONTACTED PANHANDLE EASTERN (PEPL) GAS CONTROL 12:50 AM EDT: PEPL GAS CONTROL NOTIFIED AREA TECHNICIAN (ON-CALL/STAND-BY) OF EVENT AND PROVIDED THE SITE ADDRESS AND MADISON CO. SHERIFFS CONTACT NUMBER 1:00 AM EDT: POLICE & FIRE DEPT. SHUT DOWN N CR900 W FROM NORTH AND SOUTH ACCESS ROADS. 1:26 AM EDT: SMALL FIELD FIRE WAS REPORTED BY FIRE DEPT. ON SITE. 2:02 AM EDT: PEPL PERSONNEL ARRIVED AT EVENT SITE AND CONFIRMED AFFECTED FACILITIES TO BE A FARM TAP ON THE ZIONSVILLE 100 MAINLINE. 2:08 AM EDT: SMALL FIELD FIRE PREVIOUSLY REPORTED BURNT ITSELF OUT ACCORDING TO PIKE CREEK FIRE DEPT. 2:25 AM EDT: ALL PEPL PERSONNEL IN-PLACE TO BEGIN BLOW-DOWN SEQUENCE 2:40 AM EDT: NOBLESVILLE M&R STATION; VERIFIED R-2 VALVE OPEN, CLOSED R-1 VALVE. 2:45 AM EDT: ELWOOD M&R STATION; VERIFIED R-2 VALVE OPEN, CLOSED R-1 VALVE. 2:47 AM EDT: ZIONSVILLE 103 GATE - PEPL PERSONNEL ON-SITE MONITORING PRESSURES; VERIFIED 103-L CLOSED. 3:00 AM EDT: ZIONSVILLE 105 GATE - PEPL PERSONNEL ON-SITE MONITORING PRESSURES; OPEN VALVE 205-SE, OPEN VALVE 205-E, OPEN VALVE 105-E, VALVE 105-W VERIFIED CLOSED, CLOSED GATE VALVE 105. 3:13 AM EDT: ZIONSVILLE 103 GATE - PEPL PERSONNEL ON-SITE MONITORING PRESSURES; CLOSED GATE VALVE 103. 3:15 AM EDT: ANDERSON LATERAL TAKE-OFF; VERIFIED R-2 VALVE OPEN, CLOSED R-1 VALVE. 3:43 AM EDT: TIPTON LATERAL TAKE-OFF; VERIFIED R-2 VALVE OPEN, CLOSED R-1 VALVE. 3:45 AM EDT: ZIONSVILLE 105 GATE-PEPL PERSONNEL ON-SITE MONITORING PRESSURES; OPEN VALVE 105-UB AND BEGAN BLOW-DOWN FROM 578 PSIG. 4:00 AM EDT: FIRE AT ACCIDENT SITE WAS EXTINGUISHED. 5:00 AM EDT: AFFECTED SECTION OF ZIONSVILLE 100 MAINLINE WAS COMPLETELY BLOWN-DOWN (0 PSIG). 6:24 AM EDT: AFFECTED RESIDENTS RETURNED HOME. 6:30 AM EDT: VEHICLE THAT STRUCK FARM TAP WAS REMOVED FROM SCENE AND THE ROAD WAS RE-OPENED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140109 | 16604 | 2014-10-21 09:42 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION LP (SPECTRA ENERGY CORP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2014-09-22 19:00 | 2014 |  |  | 39.1539 | -85.5551 | 1096240 | 2014-09-23 15:00 |  | NATURAL GAS |  | 6200 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELIEF VALVE WAS CLOSED FOR 4 HOURS TO REPAIR. GAS FLOW IN PIPELINE CONTINUED. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-09-23 09:00 | 2014-09-23 10:00 | ONSHORE | IN | 47283 | WESTPORT | DECATUR | MILEPOST | 707.4 | M&R 70940 | WESTPORT INDIANA METER STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | RELIEF VALVE | 1963 |  | CARBON STEEL |  | OTHER | [8 empty] | FAILURE OF RELIEF VALVE O-RING. | CLASS 1 LOCATION | NO |  | 469 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 21700 | 14479.3345008757 | 1000 | 1106.15547635103 | 0 | 0 | 0 | 0 |  |  | 22700 | 15519.1380892379 | 15585.4899772267 | [8 empty] | 125 |  | 800 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LOW FLOW THROUGH THE METER SYSTEM WOULD NOT HAVE BEEN DETECTABLE BY THE CONTROL ROOM OPERATOR. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | O-RING FAILURE | [161 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | deteschendorf@spectraenergy.com | 713-627-5573 | 713-386-4468 |  |  |  | RICK KIVELA | DIRECTOR OF OPERATIONAL COMPLIANCE | 713-627-6388 | rwkivela@spectraenergy.com | THE RELIEF VALVE OPENED AT 125 PSIG (BELOW ITS SET PRESSURE OF 180 PSIG) AT THE TEXAS EASTERN M&R 70940 NEAR WESTPORT, INDIANA AT 7PM ON SEPTEMBER 22, 2014. DUE TO LOW FLOW AT THE METER STATION, GAS CONTROL SCADA DID NOT DETECT THE GAS RELEASE AND THE EVENT WAS REPORTED BY THE PUBLIC TO SPECTRA ENERGY CONTROL ROOM AT 9AM SEPTEMBER 23, 2014. THE RELIEF WAS SHUT IN BY SPECTRA ENERGY PERSONNEL AT 10AM. THE CAUSE OF THE INCIDENT WAS AN O-RING FAILURE. THE RELIEF VALVE WAS REPAIRED AND RETURNED TO SEVICE AT 2PM.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140110 | 16634 | 2014-11-03 14:53 | SUPPLEMENTAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2014-10-06 16:58 | 2014 |  |  | 33.3081 | -97.8803 | 1097551 | 2014-10-06 18:00 |  | NATURAL GAS |  | 35648 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-10-06 17:00 | 2014-10-09 10:50 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-10-06 16:58 | 2014-10-06 16:58 | ONSHORE | TX | 76431 | NEAR CHICO | WISE | SURVEY STATION NO. | 19+99 | WISE JACK COUNTY EXTENSION | CHICO 8" | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 24 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8.625 |  | 0.188 | 42000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | STUPP CRPORATION | COAL TAR | [28 empty] | 1974 | 1974 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 8 | 8 |  | CLASS 1 LOCATION | NO |  | 194 |  | NO | NO | NO |  | 500 | 553.077738175513 | 0 | 0 | 143385 | 95673.704028021 | 35000 | 38715.4416722859 | 500 | 553.077738175513 | 0 | 0 |  |  | 179385 | 117468.43706195 | 135495.301176658 | [8 empty] | 870 |  | 945 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | MANUAL | 46092 | NO | [5 empty] | YES | NO CONNECTINS FOR LUANCHERS / RECEIVERSE | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | OTHER | OPERATIONS PERSONNEL AT TARGA PLANT CONTACT ETC GAS CONTROL |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING | [6 empty] | YES | LOCALIZED CORROSION |  |  | YES |  |  |  | YES | YES | 1974 | NO | YES | YES |  |  |  | 2014 |  |  |  | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DANNY NICHOLS | DIRECTOR REGULATORY COMPLIANCE | danny.nichols@energytransfer.com | 713-989-7232 | 713-989-1188 |  |  |  | DANNY NICHOLS | DIRECTOR REGULATORY COMPLIANCE | 713-989-7232 | danny.nichols@energytransfer.com | ON OCTOBER 6, 2014, AT APPROXIMATELY 4:58 PM ENERGY TRANSFER COMPANY (ETC) CONFIRMED A RELEASE ON THE WISE JACK COUNTY EXTENSION, 8" IN WISE COUNTY, NEAR CHICO, TEXAS. THE PIPELINE IS AN INTRASTATE NATURAL GAS TRANSMISSION PIPELINE LOCATED IN A RURAL AREA (CLASS 1), UNDER THE JURISDICTION OF THE TEXAS RAILROAD COMMISSION (SYSTEM ID# 630262). THE INCIDENT WAS REPORTED TO THE TRRC AND ALSO TO THE NRC UNDER ID: 1097551. THERE WERE NO FATALITIES, INJURIES, EVACUATIONS, ROAD CLOSURES, EXPLOSIONS, FIRE, MEDIA INTEREST, SPILLS OR ANY RESPONSE BY AN EMERGENCY OFFICIAL. THE NEAREST STRUCTURE INTENDED FOR HUMAN OCCUPANCY IS 0.25 MILES FROM THE INCIDENT SITE. AT 3:31 PM, ETC GAS CONTROL RECEIVED NOTIFICATION FROM A TARGA- CHICO PLANT EMPLOYEE THAT THERE WAS A POSSIBLE LINE RUPTURE SOUTH OF THEIR FACILITY. PRESSURE INDICATED A LEAK AND UPSTREAM TARGA AUTOMATIC VALVE WAS CLOSED AT 3:40 PM. AT 4:22 PM, ETC BVS15 WAS CLOSED DOWNSTREAM. THIS ISOLATED THE SITE OF THE POSSIBLE RUPTURE TO ALLOW FURTHER EVALUATION. AT 4:58 PM, ETC EMPLOYEES ARRIVED ON SCENE OF THE RUPTURE AND CONFIRMED THAT THE LEAK WAS ON THE CHICO 8" PIPELINE AND WAS DEPRESSURIZED. THE SCENE WAS SECURED UNTIL REPAIRS COULD BE MADE. THE PIPELINE WAS REPAIRED BY REPLACING THE SECTION OF PIPE THAT WAS AFFECTED AND PLACED BACK IN SERVICE ON 10/9/14 AT 10:50 AM. UPDATE: 02/02/2015: ALL DAMAGES WERE LIMITED TO LOSS OF GAS AND PIPE REPLACEMENT. ESTIMATED COST NOTED DURING INITIAL REPORT REMAIN ACCURATE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140111 | 16661 | 2014-11-06 09:28 | SUPPLEMENTAL FINAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2014-10-12 13:56 | 2014 |  |  | 32.5975 | -94.6656 | 1098087 | 2014-10-12 16:09 |  | NATURAL GAS |  | 3147 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-10-12 13:56 | 2014-10-12 19:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-10-12 13:56 | 2014-10-12 14:05 | ONSHORE | TX | 75605 | LONGVIEW | HARRISON | MILEPOST | 22.2 | STATION 388 | NORTH LANSING STORAGE FIELD | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | UV/IR SENSOR | UNKNOWN |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | VARIOUS | OTHER | [8 empty] | LIGHTNING TRIPPED UV/IR SENSTOR AND ACTIVATED THE FACILITY EMERGENCY SHUTDOWN SYSTEM. | CLASS 1 LOCATION | NO |  | 681 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 12110 | 8080.40280210158 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 12110 | 8377.32049036778 | 8080.40280210158 | [8 empty] | 751 |  | 960 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | YES | YES | OTHER | COMPANY AUTOMATED CALLOUT SYSTEM. LOCAL OPERATING EMPLOYEE RESPONDED. |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | [8 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | A FACILITY EMERGENCY SHUTDOWN (ESD) OCCURRED DUE TO EXCESSIVE ELECTRICAL STORMS (I.E., LIGHTNING) TRIPPING THE STATION UV/IR SENSORS DUE TO SENSITIVITY TO LIGHT FLASHES WITH HIGH IR OR UV RADIATION. | [147 empty] | STEPHEN R. DINES | ENGINEER | stephen_dines@kindermorgan.com | 719.329-5633 |  |  |  |  | REJI GEORGE | DIRECTOR OF ENGINEERING CODE AND STANDARDS | 713.420.5433 | reji_george@kindermorgan.com | THE STATION EMERGENCY SHUT-DOWN (ESD) WAS DETERMINED TO BE CAUSED BY LIGHTNING STORMS IN THE AREA. THE ELECTROMAGNET (EM) DISTURBANCES IN THE UV AND IR RANGE TRIPPED THE HEAT AND LIGHT FLASH SENSORS AT THE STATION RESULTING IN THE ESD. THE MANUFACTURE OF THE UV/IR SENSOR WAS CONTACTED TO DETERMINE IF THE SENSORS CAN BE ADJUSTED TO AVOID EM DISTURBANCES FROM LIGHTNING EVENTS AS DISCUSSED BELOW. NGPL OPERATIONS INSPECTED AND INVESTIGATED OPTIONS TO REDUCE THE SENSITIVITY OF THE STATION UV/IR SENSORS THAT CAUSED THE STATION 388 EMERGENCY SHUTDOWN (ESD) BACK ON OCTOBER 12, 2014. AFTER SUBMITTAL OF THE INITIAL REPORT, NGPL DETERMINED THE DIP SWITCH SETTINGS HAVE A FACTORY DEFAULT 4 SECOND DELAY BETWEEN THE WARNING AND ALARM. IN ADDITION, NGPL DETERMINED THAT NO OTHER EQUIPMENT INSTALLED ON THIS SYSTEM WOULD IMPACT THE FACTORY-DEFAULT DELAY SETTINGS AND, UPON VERIFYING THE UV/IR SYSTEM DID NOT EXPERIENCE ANY TYPE OF POWER OUTAGE OR SURGE, THE SENSOR SIGNAL DELAY SETTINGS WERE INCREASED FROM FOUR (4) SECONDS TO EIGHT (8) SECONDS. NGPL BELIEVES THAT INCREASING THE TIME DELAY SETTING WILL REDUCE FALSE ALARMS AND SHUTDOWNS CAUSED BY SEVERE LIGHTNING STORMS GOING FORWARD. NGPL'S NORTH LANSING STORAGE FIELD HAS A MAXIMUM PEAK-DAY WITHDRAWAL RATE OF 1,240 MMCF PER DAY AND THE COMPRESSOR STATION NO. 388 NEAR LONGVIEW, TEXAS IS COMPRISED OF SEVEN COMPRESSOR UNITS TOTALING 36,000 HP, TWO CO2 EXTRACTION PLANTS AND FOUR DEHYDRATOR SKIDS. THE NORMAL ESD RESTORATION PROCESS CAN TAKE UP TO THREE (3) HOURS OR MORE DEPENDING ON THE CIRCUMSTANCES. FOLLOWING AN ESD EVENT WHERE THE CAUSE REMAINS UNKNOWN, CONSIDERABLY MORE TIME IS REQUIRED TO VERIFY THE ROOT CAUSE OF THE EVENT, TO CONFIRM THAT SAFETY DEVICES FUNCTIONED AS DESIGNED, AND THAT NO DAMAGE TO THE FACILITIES RESULTED BEFORE RESTARTING THE FACILITIES. ON OCTOBER 12, 2014, IT TOOK NGPL APPROXIMATELY FIVE (5) HOURS TO VERIFY THE CAUSE OF THE ESD AND DETERMINE THAT NO DAMAGE EXISTED TO ANY OF THE FACILITIES BEFORE BRINGING THE ENTIRE STATION BACK INTO SERVICE. PLEASE NOTE THAT THE PIR VALUE PROVIDED IN PART D INCLUDES A PIPE DIAMETER OF 30 INCHES, A MAOP OF 960 PSIG, AND A 40 FOOT BUFFER VALUE.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20140112 | 16565 | 2014-11-06 09:46 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2014-10-08 11:22 | 2014 |  |  | 29.0391 | 90.9034 | 1097722 | 2014-10-08 11:50 |  | NATURAL GAS |  | 75 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-10-08 13:30 | 2014-10-17 07:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-10-08 11:22 | 2014-10-08 14:45 | OFFSHORE | [28 empty] | 15 | IN STATE WATERS | LA | SHIP SHOAL | SS47 | TERREBONE |  |  |  | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 26 |  | 0.5 | 52000 | API 5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | U.S. STEEL | OTHER | ASPHALT WITH 3" CONCRETE. | [27 empty] | 1969 | 1969 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 681 |  | NO | NO | NO |  | 0 | 0 | 53000 | 58626.2402466044 | 200 | 133.450087565674 | 350000 | 387154.416722859 | 56000 | 61944.7066756575 | 0 | 0 |  |  | 459200 | 233197.692942667 | 507858.813732687 | [8 empty] | 658 |  | 1440 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 91661 | NO | [5 empty] | YES | PIG TRAPS NOT DESIGNED TO ACCOMMODATE INTERNAL INSPECTION TOOLS. | YES |  |  | YES |  | YES | PIG TRAPS NOT DESIGNED TO ACCOMMODATE | OFFSHORE GATHERING | YES | YES | YES | NO | NO | OTHER | HELICOPTER FLYING OVER OUR THE AREA NOTIFIED TRANSCO, WHEN THEY SAW BUBBLES. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE GAS RELEASE WAS SO SMALL NO PRESSURE REDUCTION ON PIPELINE WAS DETECTED. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN | [5 empty] | YES | THIS PIPELINE HAS BEEN IN UNPROCESSED, UNDEHYDRATED SERVICE SINCE 1990. |  |  | YES | UT READINGS BY DIVERS INDICATE AN INTERNAL ISOLATED PINHOLE; NO EXTERNAL CORROSION OBSERVED BY DIVERS. | YES | [5 empty] | YES | NO | YES | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | JOHNNY LOPEZ | REGULATORY COMPLIANCE SPECIALIST | johnny.lopez@williams.com | 7132152995 | 7132152222 |  |  |  | MARIE SOTAK | MANAGER SAFETY REGULATORY COMPLIANCE | 7132152111 | marie.sotak@williams.com | AT ABOUT 10:33AM ON 10-8-2014, LA. SCHRIEVER OPERATIONS RECEIVED A PHONE CALL FROM PILOTS AT HELIPORT SAYING ONE OF THEIR HELICOPTERS FLYING FOR ANOTHER COMPANY HAD REPORTED SOME BUBBLES IN THE SS 47 AREA NEAR OUR 26". THE COORDINATES GIVEN WERE PLOTTED AND WERE SHOWN TO BE 1200+ FEET WEST OF WILLIAMS 26" PIPELINE. ONE OF OUR OWN HELICOPTERS WITH WILLIAMS PERSONNEL ON BOARD DEPARTED SCHRIEVER HELIPORT A FEW MINUTES LATER FOR NORMAL OPERATIONS WERE ASKED TO FLY OVER REPORTED BUBBLES TO VERIFY COORDINATES. WILLIAMS PERSONNEL ON BOARD HELICOPTER CALLED SCHRIEVER OFFICE AT 11:22AM WITH THEIR OWN COORDINATES OF BUBBLES AND VERIFIED TO SCHRIEVER COM THAT BUBBLES AND VERY LIGHT & SMALL SHEEN APPEARED TO BE RIGHT ON TOP OF WILLIAMS 26". THE NEW COORDINATES WERE PLOTTED, PLACING THE BUBBLES RIGHT ON TOP OF WILLIAMS 26" PIPELINE, AGREEING WITH WILLIAMS PERSONNEL OPINION. AT 11:35AM, O'BRIEN'S WAS CONTACTED BY WARREN TOUPS. O'BRIEN'S CONTACTED NRC AT 11:50AM; RECEIVED NRC# 1097722. O'BRIEN'S ALSO CONTACTED LA. STATE POLICE AT 11:56AM, RECEIVED STATE NUMBER 14-04526. BSEE PIPELINE GROUP WAS CONTACTED AT 12:02PM AND TERREBONNE PARISH L. E. P. C WAS CONTACTED AT 12:08PM AT 11:37AM, SCHRIEVER OPERATIONS REPORTED LEAK AND NECESSARY PLATFORMS THAT NEEDED TO BE SHUT-IN TO MARSHALL IN WILLIAM'S GAS CONTROL. TOMMY WITH OIL MOPS(OSRO) WAS CONTACTED, REQUESTED TOMMY PLACE ABSORBENT BOOM AROUND THE BUBBLES. SCHRIEVER OPERATIONS COMPLETED CALLING ALL PRODUCERS BY 12:35 PM; THE 26" PIPELINE WAS COMPLETELY ISOLATED AT 12:25PM. BLOWDOWN OF THE 26" STARTED AT 1:30PM FROM SS 70 AT 658#. AT 2:50PM, TOMMY WITH OIL MOPS CALLED SAYING THE ABSORBENT BOOM WAS IN PLACE AROUND BUBBLES AS REQUESTED AND THAT HE COULD SEE LITTLE TO NO SHEEN ON WATER FOR ENTIRE DAY. TWO SCHRIEVER PERSONNEL WERE SENT TO AMELIA DOCK TO BOARD THE M/V MR. COLBY AT 3:45PM TO HEAD TO SS 70 PLATFORM TO BLOW DOWN 26" PIPELINE. AT 6:00PM, THE BLOW DOWN IS STOPPED AT SS 70 DUE TO DOWN TIME OF HELICOPTER. PRESSURE 533#.. BLOWDOWN RESUMES AT MIDNITE ON SS 70 BY TWO SCHRIEVER PERSONNEL ON M/V MR. COLBY. AT 7:00AM ON 10-9-2014, PRESSURE ON 26" IS 420# TWO SCHRIEVER PERSONNEL TAKE COMPNY BOAT TO DOG LAKE TO ASSIST WITH BLOWDOWN OF 26" PIPELINE. TOMMY WITH OIL MOPS REPORTS NO SHEEN ESCAPING OUTSIDE OF BOOM; LIGHT SMALL SHEEN WITHIN BOOM. BLOW DOWN IS STOPPED AT 40 PSIG AT 6:00PM ; WAIT TO SEE IF PRESSURE IS OK FOR DIVERS. LIFT BOAT DEPARTS FOURCHON DOCKS WITH DIVERS AND REPAIR CLAMP.AT 7:15AM ON 10-10-14. LIFT BOAT ARRIVES AT LEAK SITE ABOUT MIDNIGHT AND STARTS TO DO HIS PRE-LOAD. LIFTBOAT FINALLY LOCATES ALL PIPELINES IN AREA AND FEELS SAFE TO JACK DOWN IN FINAL LOCATION NEAR 26" AT 11:05PM ON 10/11/14. DIVERS BEGIN THE INVESTIGATION. SUMMARY OF RCA INVESTIGATION AND LEAK REPAIR: UT READINGS BY DIVERS INDICATE AN INTERNAL ISOLATED PINHOLE ON LOW POINT OF THE PIPE; NO EXTERNAL CORROSION OBSERVED BY DIVERS. THE DIVERS CLEANED OFF PIPELINE AT LEAK AREA AND INSTALLED REPAIR CLAMP ON 26" PIPELINE. ROUGH WEATHER PREVENTED ANY WORK BEING DONE FOR 2 DAYS. THE PIPELINE WAS PRESSURED UP, CHECKED FOR LEAKS, ABSORBENT BOOM PICKED UP AND WAS READY FOR PRODUCERS GAS FLOW THE NEXT DAY AT 3:40PM ON 10/16/14. THE HISTORY OF THIS PIPELINE GATHERING SYSTEM IS THAT IT HAS BEEN IN UNPROCESSED AND UNDEHYDRATED SERVICE SINCE 1990. THIS LINE HAS BEEN TREATED SINCE 1990 WITH CORROSION INHIBITORS & BIOCIDES. SAMPLES ARE COLLECTED & RESIDUALS ARE MONITORED MONTHLY. FIELD TECHNICIANS CHECK CHEMICAL QUANTITIES AND CHEMICAL INJECTION PUMP OPERATIONS ON A MONTHLY BASIS. TRANSCO DOES FOLLOW A STRICT INTERNAL CORROSION MONITORING AND PREVENTION POLICY. INTERNAL CORROSION LEAK DOCUMENTATION IS PROVIDED TO ASSET INTEGRITY ENGINEERS FOR RECCOMENDATIONS.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140113 | 17151 | 2014-11-06 15:30 | SUPPLEMENTAL FINAL | 11824 | LOUISVILLE GAS & ELECTRIC CO | 220 W MAIN ST, PO BOX 32010 | LOUISVILLE | KY | 40202 | 2014-10-07 07:40 | 2014 |  |  | 38.0026 | -86.0649 | 1098364 | 2014-10-15 15:37 |  | NATURAL GAS |  | 2200 | 5 | 47 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-10-07 14:07 | 2015-10-07 09:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-10-07 14:03 | 2014-10-07 14:03 | ONSHORE | IN | 47135 | LACONIA | HARRISON | MILEPOST | KEITH 10 WELL | KEITH 10 AND 11 WELL LINE | 339656 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 42 |  | NO | [22 empty] | INTRASTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | PIPE | PIPE SEAM | 4 |  | 0.188 | 35000 | UNKNOWN | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1992 | 1992 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 84 | 1 |  | CLASS 1 LOCATION | NO |  | 42 |  | NO | NO | NO |  | 5000 | 5530.77738175513 | 22 | 24.3354204797226 | 9812 | 6547.06129597198 | 7474 | 8267.40603024757 | 48280 | 53405.1863982275 | 0 | 0 |  |  | 70588 | 37646.9263539023 | 73774.7665266819 | [8 empty] | 234 |  | 305 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A LOCAL CONTROL SYSTEM AUTOMATICALLY SHUT DOWN THE UNATTENDED FIELD COMPRESSOR UPON THE PIPELINE FAILURE AS DESIGNED AND NO SCADA ALARMS WERE ACTIVATED. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | SELECTIVE SEAM CORROSION |  | YES |  |  |  |  | YES | YES |  |  | YES |  |  |  | YES | SEAM | YES | NO | NOT APPLICABLE - NOT MAINLINE PIPE | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | ERIC BENGE | CHEMICAL ENGINEER III | eric.benge@lge-ku.com | 502-364-8569 |  |  |  |  | GREG CORNETT | ASSOCIATE GENERAL COUNSEL | 502-627-2756 | greg.cornett@lge-ku.com | AT APPROXIMATELY 7:40 AM ON OCTOBER 7, 2014, A 4-INCH PIPELINE IN DOE RUN INDIANA NATURAL GAS STORAGE FIELD RUPTURED RESULTING IN THE ACCIDENTAL RELEASE OF NATURAL GAS, BRINE WATER, AND DEBRIS. THE PIPELINE WAS LOCATED IN A REMOTE AREA AND WAS NOT DETECTED UNTIL APPROXIMATELY 2:07 PM WHEN AN OPERATOR EMPLOYEE DETECTED THE SOUND OF BLOWING GAS. THE OPERATOR EMPLOYEE QUICKLY IDENTIFIED THE FAILURE LOCATION AND IMMEDIATELY ISOLATED THE PIPELINE SECTION THAT FAILED. FIELD EXAMINATION OF THE FAILURE INDICATED A PIPE SEAM FAILURE. ANALYSIS OF THE CORROSION CHARACTERISTICS AND RECOVERED SLUDGE SAMPLE, AND REVIEW OF THE GAS COMPOSITION INDICATES THAT THE MOST LIKELY CAUSE OF THE INTERNAL CORROSION WAS EXPOSURE TO LOW PH BRINE. THE LOW PH BRINE WAS MOST LIKELY CAUSED BY WELL ACIDIZING FLUID. PIPELINE CONSTRUCTION WAS COMPLETED BY JULY 27, 2015. THE NEW PIPELINE WAS PUT BACK IN SERVICE ON OCTOBER 7, 2015.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140114 | 16864 | 2014-11-10 12:23 | SUPPLEMENTAL FINAL | 12576 | ENABLE MISSISSIPPI RIVER TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2014-10-22 13:52 | 2014 |  |  | 35.613 | -91.3065 | 1099022 | 2014-10-22 14:32 |  | NATURAL GAS |  | 11127 | 19949 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-10-22 19:19 | 2014-10-23 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 5 | 2014-10-22 14:41 | 2014-10-22 14:41 | ONSHORE | AR | 72112 | NEWPORT | JACKSON | SURVEY STATION NO. | 1799+88 | MAINLINE 3 | SERIES 1550 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 26 |  | 0.25 | 52000 | X-52 | DSAW |  | US STEEL | COAL TAR | [28 empty] | 1968 | 1968 | CARBON STEEL |  | MECHANICAL PUNCTURE | 2 | 6 | [7 empty] | CLASS 1 LOCATION | NO |  | 481 |  | NO | NO | NO |  | 0 | 0 | 73612 | 81426.3169251517 | 41058 | 27395.9684763573 | 95150 | 105250.6935748 | 1000 | 1106.15547635103 | 0 | 0 |  |  | 210820 | 114600.072669472 | 215179.13445266 | [8 empty] | 575 |  | 720 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 124537 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY EXCAVATION DAMAGE CAUSED THE EVENT. | [12 empty] | YES | 1 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | YES |  |  |  |  | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ROAD WORK | YES | 1410160638 | ARKANSAS ON-CALL | CONTRACT LOCATOR | NO | NO | NO |  | LOCATING PRACTICES NOT SUFFICIENT |  | FACILITY WAS NOT LOCATED OR MARKED | [264 empty] | JIMMY CROSS | DOT COMPLIANCE MANAGER | jimmy.cross@enablemidstream.com | 3184293664 | 3184293994 |  |  |  | JOHNNY CAVITT | MANAGER OF DOT COMPLIANCE PROGRAMS | 3184293606 | johnny.cavitt@enablemidstream.com | OVERVIEW OF THE FACTS: TANNER CONSTRUCTION WAS A CONTRACTOR TO THE ARKANSAS HIGHWAY AND TRANSPORTATION DEPARTMENT. WAYNE YARBROUGH WITH TANNER CALLED THE ARKANSAS ONE CALL (AOC) SYSTEM AT 12:13 PM THURSDAY AFTERNOON OCTOBER 16, 2014 TO REPORT A PLANNED EXCAVATION FOR THE ARKANSAS HIGHWAY AND TRANSPORTATION DEPARTMENT. TANNER INITIATED EXCAVATION ON A PORTION OF GROUND NEAR THE INTERSECTION OF HIGHWAY 367 AND HIGHWAY 14 IN JACKSON COUNTY, ARKANSAS TWO MILES SOUTH OF NEWPORT, ARKANSAS. DURING THE EXCAVATION ACTIVITIES ON OCTOBER 22, 2014, A TANNER EMPLOYEE STRUCK THE EMRT MAINLINE 3 CAUSING A LEAK THAT REQUIRED A TWENTY MILE SECTION OF THE PIPELINE TO BE BLOWN DOWN FOR THE REPAIR TO BE COMPLETED. TIMELINE OF EVENTS LEADING UP TO THE EVENT: ON OCTOBER 16, 2014 AT 1213, WAYNE YARBROUGH CALLED ARKANSAS ONE CALL TO REPORT A PLANNED EXCAVATION. A WORK ORDER TO LOCATE UTILITIES, #AR141016-0638, WAS ISSUED BY ARKANSAS ONE CALL AND PROVIDED TO TANNER. THE WORK ORDER STATED THE WORK WAS TO BEGIN 10/20/2014 AT 1215. THE WORK ORDER TO LOCATE UTILITIES, #AR141016-0638, WAS ASSIGNED TO ARKANSAS UTILITY PROTECTION SERVICES BY ARKANSAS ONE CALL AT 1221 ON OCTOBER 16, 2014. AFTER 1221 ON THURSDAY OCTOBER 16, 2014 JUSTIN SIMPSON, ARKUPS EMPLOYEE, RECEIVED THE AOC TICKET #AR141016-0638 WHICH REQUIRED THE LOCATE WORK TO BEGIN BY 1215 ON OCTOBER 20, 2014. JUSTIN SIMPSON STATED THAT DUE TO A BACKLOG OF WORK, ARKUPS DID NOT BEGIN THE UTILITIES LOCATE WORK BEFORE 1215 ON OCTOBER 20, 2014 AS REQUIRED. IN A WRITTEN STATEMENT TO EMRT EMPLOYEE, BILL WARREN, WAYNE YARBROUGH STATED THAT HE STARTED EXCAVATION AT THE SITE AT 1300 ON OCTOBER 20, 2013. IN A STATEMENT TAKEN AFTER THE PIPE LINE STRIKE BY EMRT EMPLOYEES, JOE ANDERSON AND BEN VINSON, THOMAS NEWBY, A TANNER EMPLOYEE, THE BACK HOE OPERATOR THAT STRUCK THE PIPE LINE, INDICATED THAT HE HAD REFUSED TO BEGIN THE EXCAVATION ON MONDAY OCTOBER 20, 2014. HE LEFT THE WORK SITE AND RETURNED TO HIS MOTEL. APPROXIMATELY 1300 HIS BOSS CALLED HIM AND SAID THEY WERE GOOD TO GO. NEWBY STATED HE RETURNED TO WORK, STARTED THE EXCAVATION, BUT VOICED HIS CONCERN MONDAY, TUESDAY AND WEDNESDAY. ON MONDAY OCTOBER 20, 2014 SOMETIME BETWEEN 1500 AND 1600 JUSTIN SIMPSON WITH ARKUPS MADE HIS FIRST CONTACT BY PHONE WITH YARBROUGH. YARBROUGH INFORMED SIMPSON THAT EXCAVATION HAD ALREADY BEGUN. SIMPSON TOLD YARBROUGH HE WOULD NOT BE ON LOCATION UNTIL TUESDAY OCTOBER 21, 2014. ARKUPS EMPLOYEE, SIMPSON STATED HE ARRIVED AT THE EXCAVATION LOCATION AT APPROXIMATELY 1631 OCTOBER 21, 2014. EXCAVATION HAD ALREADY STARTED. BASED UPON HIS STATEMENT AND ENTRY INTO THE ONE CALL TICKET ON 10/21/14, HE WAS NOT ABLE TO LOCATE THE PIPELINE. AT APPROXIMATELY 1630 ARKUPS EMPLOYEE SIMPSON STATED HE CALLED EMRT EMPLOYEE, ANDERSON, TO INFORM ANDERSON THAT ARKUPS WAS NOT ABLE TO LOCATE THE PIPELINE. SIMPSON STATED HE INFORMED ANDERSON THAT EXCAVATION HAD STARTED. AFTER TALKING TO ANDERSON, ARKUPS EMPLOYEE SIMPSON STATED AT APPROXIMATELY 1700 HE INFORMED YARBROUGH BY PHONE THAT THE PIPELINE HAD NOT BEEN LOCATED AND THAT THE GAS COMPANY WOULD BE ON SITE THE NEXT DAY, OCTOBER 22, 2014 TO LOCATE THE PIPELINE. TANNER DID NOT WAIT FOR EMRT PERSONNEL TO LOCATE THE PIPELINE BUT CONTINUED THE EXCAVATION ON THE MORNING OF OCTOBER 22, 2014. ANDERSON MADE PLANS TO GO TO THE LOCATION ON OCTOBER 22, 2014. ANDERSON STATED THE HE WAS NOT AWARE THAT EXCAVATION WAS OCCURRING. IN ADDITION TO THE TURNED BACK ORDER FROM SIMPSON, ANDERSON HAD THREE OTHER TURNED BACK ORDERS FROM ARKUPS. THE TURNED BACK ORDER #AR14106-0638 FROM SIMPSON WAS NOT CODED CRITICAL WHICH WOULD INDICATE EXCAVATION WAS OCCURRING. TANNER CONTINUED EXCAVATION UNTIL TANNER EMPLOYEE, THOMAS NEWBY, STRUCK THE PIPELINE WITH THE TRACK HOE HE WAS OPERATING. WAYNE YARBOROUGH NOTIFIED EMRT SYSTEM CONTROL ABOUT THE LINE STRIKE AT 1352 ON OCTOBER 22, 2014. YARBOROUGH STATED HE OBTAINED THE EMRT CONTACT PHONE NUMBER FROM THE PIPELINE SIGN NEAR THE ENTRANCE TO THE EXCAVATION SITE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140115 | 16537 | 2014-11-11 13:32 | ORIGINAL FINAL | 12696 | CYPRESS GAS PIPELINE COMPANY | 1100 LOUISIANA ST. | HOUSTON | TX | 77002 | 2014-07-19 09:30 | 2014 |  |  | 30.4933 | -91.1987 | 1097962 | 2014-10-10 14:45 |  | NATURAL GAS |  | 331 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-07-19 15:30 | 2014-10-23 11:55 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-07-19 09:30 | 2014-07-19 09:30 | ONSHORE | LA | 70767 | PORT ALLEN | WEST BATON ROUGE | MILEPOST | 4371+87.24 | MISSISSIPPI RIVER CROSSING #2 (BRW#1) | 580-0100 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 144 |  | YES | [6 empty] | YES | UNCASED | MISSISSIPPI RIVER | 35 | BELOW WATER, PIPE BURIED BELOW BOTTOM (NOT IN BORED/DRILLED CROSSING) | [11 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10.75 |  | 0.5 | 30000 | ASTM A-106 | LONGITUDINAL ERW - LOW FREQUENCY |  | UNKNOWN | NONE | [28 empty] | 1946 | 1946 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 157 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 327 | 218.190893169877 | 1000000 | 1106155.47635103 | 0 | 0 | 0 | 0 |  |  | 1000327 | 507980.759990931 | 1106373.6672442 | [8 empty] | 334 |  | 450 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 5090 | NO |  |  | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER IN GAS CONTROL DID NOT SHOW A PRESSURE LOSS ON THE SCADA SYSTEM. THE RATE OF GAS LOSS FROM THE PIPELINE WAS BELOW THE THRESHOLD THAT WOULD INDICATE A PRESSURE DROP ON THE GAS CONTROL MONITORING SYSTEM. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [146 empty] | NATHAN L. GRAY JR. | SENIOR PIPELINE COMPLIANCE SPECIALIST | ngray@eprod.com | 985 493 4629 | 985 448 1857 |  |  |  | NATHAN L. GRAY JR. | SENIOR PIPELINE COMPLIANCE SPECIALIST | 985 493 4629 | ngray@eprod.com | DURING SURVEY WORK AT THE MISSISSIPPI RIVER CROSSING FOR FUTURE CONSTRUCTION, A SMALL AMOUNT OF GAS BUBBLES WERE NOTICED IN THE RIVER. OPERATIONS PERSONNEL ISOLATED THE PIPELINE AND VERIFIED THAT THE PIPELINE HAD A SMALL LEAK. ORIGINAL INVESTIGATION DID NOT MEET NRC REPORTABLE CRITERIA. PIPELINE REMAINED SHUTDOWN UNTIL A PLAN OF ACTION WAS DETERMINED. LATER, IT WAS DETERMINED THAT A TEMPORARY REPAIR USING A PIPELINE CLAMP WAS WARRANTED. THESE PIPELINE REPAIRS EXCEEDED THE MINIMUM REPORTING REQUIREMENTS AND THE NRC WAS SUBSEQUENTLY CALLED. UPON COMPLETION OF THE REPAIR, THE PIPELINE WAS LEAK TESTED AND RETURNED TO SERVICE. INCIDENT CAUSE IS UNKNOWN BECAUSE THE PIPELINE IS UNDER THE MISSISSIPPI RIVER AND DOES NOT CURRENTLY ACCOMMODATE INTERNAL INSPECTION TOOLS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140116 | 17209 | 2014-11-12 09:22 | SUPPLEMENTAL FINAL | 15105 | PANHANDLE EASTERN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2014-10-13 10:15 | 2014 |  |  | 38.7674 | -93.8759 | 1098139 | 2014-10-13 11:07 |  | NATURAL GAS |  | 28670 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-10-13 11:25 | 2014-11-07 11:09 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 1 | 2014-10-13 10:15 | 2014-10-13 11:20 | ONSHORE | MO | 64019 | CENTERVIEW | JOHNSON COUNTY | SURVEY STATION NO. | 2339+26 | PANHANDLE EASTERN PIPE LINE COMPANY | LOUISBURG 100 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 22 |  | 0.312 | 30700 | API-5L 3RD EDITION | LAP WELDED |  | NATIONAL TUBE | COAL TAR | [28 empty] | 1931 | 1931 | CARBON STEEL |  | OTHER | [8 empty] | IN SERVICE RELEASE, THAT INITIATED BY PIPE MOVEMENT OUT OF THE MECHANICAL DRESSER COUPLINGS. | CLASS 1 LOCATION | NO |  | 331 |  | NO | YES | NO |  | 42000 | 46458.5300067431 | 0 | 0 | 103976 | 69378.0315236427 | 628509 | 695228.672285907 | 2100 | 2322.92650033715 | 224964 | 248845.160581832 | UPDATES DUE TO METALLURGICAL ANALYSIS. |  | 1001549 | 527674.131646105 | 1062233.32089846 | [8 empty] | 441 |  | 475 | 192.619(A)(4) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 39444 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PRESSURE AT THE TIME OF THE INCIDENT WAS BELOW MAOP. | [12 empty] | YES | 3 | 0 | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | YES | [7 empty] | YES | SEE PART H NARRATIVE FOR DETAILS. | [10 empty] | YES | [6 empty] | YES | [58 empty] | YES | YES |  |  | YES |  |  |  | 2009 | [31 empty] | 2009 | [23 empty] | YES | 1953 | 736 | NO | [13 empty] | NO | [63 empty] | NATHAN HLAVATY | DIRECTOR REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 7138575479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR REGULATORY COMPLIANCE | 7138575479 | nathan.hlavaty@energytransfer.com | ON OCTOBER 13, 2014 AT APPROXIMATELY 10:09 AM CST, THE PANHANDLE EASTERN PIPE LINE COMPANY 22-INCH LOUISBURG 100 LINE EXPERIENCED AN IN-SERVICE RELEASE WHICH SUBSEQUENTLY IGNITED IN JOHNSON COUNTY, MO JUST WEST OF THE RURAL COMMUNITY OF CENTERVIEW. THERE WERE NO INJURIES; HOWEVER, THERE WAS ONE SELF-EVACUATION OF A RESIDENT CLOSEST TO THE SITE AS A PRECAUTIONARY MEASURE. THE RELEASE OCCURRED IN A RURAL AREA AND WITHIN A PASTURE. THE CLOSEST STRUCTURE INTENDED FOR HUMAN OCCUPANCY IS ABOUT 500 FEET NORTHWEST (LANDOWNER RESIDENCE). THIS STRUCTURE WAS UNDAMAGED; HOWEVER A BARN LOCATED APPROXIMATELY 221 FEET TO THE NORTHWEST HAD MINOR DAMAGE FROM FLYING DEBRIS. THE RELEASE APPEARED TO HAVE INITIATED BY PIPE MOVEMENT OUT OF THE MECHANICAL DRESSER COUPLINGS. THE PIPE SEGMENT INVOLVED DOES NOT CONTAIN AN HCA. THE PRESSURE AT THE TIME OF THE RELEASE WAS 441 PSIG AT THE LOUISBURG 105 GATE; THE MAOP OF THIS SEGMENT IS 475 PSIG. GAS CONTROL ALARMS ACCOMPANIED BY A COINCIDENT CALL FROM JOHNSON COUNTY 911 SET IN MOTION A RESPONSE BY LOCAL EMPLOYEES WHICH HAD THE AFFECTED SEGMENT ISOLATED ON THE UPSTREAM (105 GATE) AND DOWNSTREAM (106 GATE) SIDES BY APPROXIMATELY 11:25 AM. LOCAL LAW ENFORCEMENT AND FIRE FIGHTERS RESPONDED TO THE EVENT AND PERFORMED ADMIRABLY AS THEY SECURED THE INCIDENT SITE AND WORKED COOPERATIVELY WITH LOCAL PEPL EMPLOYEES. THIS SUPPLEMENTAL REPORT UPDATES THE PART G APPARENT CAUSE BASED ON THE ROOT CAUSE ANALYSIS. THE DIRECT CAUSE OF THIS INCIDENT SHOULD BE CATEGORIZED AS A CONSTRUCTION FAILURE. THE PIPE WAS CONSTRUCTED IN 1931 WITH AN OVER BEND AT THE COUPLING THAT EXCEEDED THE COUPLING MANUFACTURER DEFLECTION RECOMMENDATIONS. THE PIPE DISENGAGED AT THE COUPLING DUE TO THAT DEFLECTION EXCEEDANCE COMBINED WITH AN UPWARD COMPONENT FORCE DUE TO INTERNAL PRESSURE. ALSO A CONTRIBUTING FACTOR WAS INADEQUATE RESISTIVE FORCES ON THE PIPE AS A RESULT OF CHANGES IN SOIL PROPERTIES DUE TO WATER SATURATION. ADDITIONAL UPDATES WERE MADE TO PART C, 3; PART D - COSTS 7B, AND 7D; PART E 2A; AND PART G - CAUSE. THE SUPPLEMENTAL/FINAL REPORT DATED 10/20/16, UPDATES WERE MADE TO THE FOLLOWING SECTIONS: PART A - (4) AND (7); PART B (11) - DEPTH-OF-COVER; PART C - (3)H COATING TYPE. THE SUPPLEMENTAL/FINAL REPORT DATED 10/27/16, UPDATES WERE MADE TO THE FOLLOWING SECTIONS: PART A - (4) AND PART C - (3)H COATING TYPE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140117 | 16743 | 2014-11-13 11:11 | SUPPLEMENTAL FINAL | 38987 | KINETICA ENERGY EXPRESS LLC | 1001 MCKINNEY STREET, SUITE 900 | HOUSTON | TX | 77002 | 2014-10-11 14:00 | 2014 |  |  | 28.6 | -92.5669 | 1098019 | 2014-10-11 15:10 |  | NATURAL GAS |  | 110 | 100 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-10-11 14:30 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-10-11 14:02 | 2014-10-11 14:02 | OFFSHORE | [28 empty] | 150 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | VERMILLION | 241 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 20 |  | 0.5 | 60000 | API 5L | DSAW |  | BETHLEHEM | COAL TAR | [28 empty] | 1979 | 1979 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO | NO |  | 0 | 0 | 20000 | 22123.1095270205 | 8357 | 5576.2119089317 | 225000 | 248884.982178981 | 25000 | 27653.8869087757 | 0 | 0 | ISOLATION AND PREP FOR ABANDONMENT. |  | 278357 | 142874.841011912 | 304238.190523709 | [8 empty] | 660 |  | 1250 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 14000 | NO |  |  |  | YES |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | BSSE RECEIVED REPORT FROM TEXAS EASTERN ABOUT GAS BUBBLE. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OFFSHORE PIPELINE OPERATING WELL BELOW MAOP WITHOUT OPERATIONAL ISSUES. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  | YES |  |  |  |  | YES | [5 empty] | YES |  |  |  | YES | NO | NOT APPLICABLE - NOT MAINLINE PIPE | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | SUSIE RICHMOND | MANAGER OF PIPELINE COMPLIANCE AND TRAINING | susie.richmond@kineticallc.com | 985-223-6145 |  |  |  |  | SUSIE RICHMOND | MANAGER OF PIPELINE COMPLIANCE AND TRAINING | 985-223-6145 | susie.richmond@kineticallc.com | TEXAS EASTERN PIPELINE MADE A THIRD PARTY REPORT TO BSEE WHICH IDENTIFIED THIS LEAK. WE RECEIVED NOTIFICATION FROM BSEE AND FLEW TO THE LOCATION TO VERIFY COORDINATES AND ON-SCENE CONDITIONS. AFTER REMAPPING THE AREA AND IDENTIFYING THE LEAK ON THE KINETICA 509A-1100 THE PRODUCER WAS ASKED TO SHUT IN PRODUCTION. THIS PIPELINE WILL NOT BE RETURNED TO SERVICE AS AN ADDITIONAL LEAK WAS IDENTIFIED ON 10/16/14. THIS SUPPLEMENTAL REPORT WAS CREATED TO CORRECT THE SMYS, PER OUR PIPELINE ENGINEER RICHARD SACCO, PE. THIS SUPPLEMENTAL WAS CREATED IN ORDER TO MARK FINAL, AT THE REQUEST OF THE PHMSA ENGINEER.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140118 | 16744 | 2014-11-13 11:36 | SUPPLEMENTAL FINAL | 38987 | KINETICA ENERGY EXPRESS LLC | 1001 MCKINNEY STREET, SUITE 900 | HOUSTON | TX | 77002 | 2014-10-16 12:53 | 2014 |  |  | 28.5992 | -92.5794 | 1098447 | 2014-10-16 14:05 |  | NATURAL GAS |  | 9 | 1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | PIPELINE WAS ALREADY SHUT-IN PRIOR TO THE RELEASE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-10-16 12:53 | 2014-10-16 13:30 | OFFSHORE | [28 empty] | 150 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | VERMILLION | 241 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 20 |  | 0.5 | 60000 | L5 | DSAW |  | BETHLEHEM | COAL TAR | [28 empty] | 1979 | 1979 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO | NO |  | 0 | 0 | 3500 | 3871.54416722859 | 0 | 0 | 22500 | 24888.4982178981 | 2500 | 2765.38869087756 | 0 | 0 |  |  | 28500 | 14471.0047201618 | 31525.4310760042 | [8 empty] | 400 |  | 1250 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 2500 | NO |  |  |  | YES |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OFFSHORE LEAK ON OUT OF SERVICE PIPELINE. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  | YES |  |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NOT APPLICABLE - NOT MAINLINE PIPE | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | SUSIE RICHMOND | MANAGER OF PIPELINE COMPLIANCE AND TRAINING | susie.richmond@kineticallc.com | 985-223-6145 |  |  |  |  | SUSIE RICHMOND | MANAGER OF PIPELINE COMPLIANCE AND TRAINING | 985-209-4263 | susie.richmond@kineticallc.com | WHILE COMPANY PERSONNEL WERE PATROLLING THIS PIPELINE TO MONITOR A LEAK REPORTED 10/11/14, THEY IDENTIFIED A SECOND LOCATION GAS RELEASE. THE PIPELINE WAS ALREADY IN THE PROCESS OF BEING BLOWN DOWN AND REMOVED FROM SERVICE. THIS LINE WILL BE PREPARED FOR ABANDONMENT. THIS SUPPLEMENTAL REPORT WAS CREATED TO CORRECT THE SMYS PROVIDED BY OUR PIPELINE ENGINEER RICHARD SACCO, PE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140119 | 16746 | 2014-11-13 13:21 | SUPPLEMENTAL FINAL | 38987 | KINETICA ENERGY EXPRESS LLC | 1001 MCKINNEY STREET, SUITE 900 | HOUSTON | TX | 77002 | 2014-11-02 14:40 | 2014 |  |  | 29.1239 | -92.5011 | 1100003 | 2014-11-02 17:00 |  | NATURAL GAS |  | 200 | 100 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-11-09 12:00 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-11-02 14:20 | 2014-11-02 16:30 | OFFSHORE | [28 empty] | 120 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | VERMILLION | 119 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12.75 |  | 0.375 | 42000 | L5 | SEAMLESS |  | YOUNGSTOWN | COAL TAR | [28 empty] | 1981 | 1981 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO | NO |  | 0 | 0 | 806 | 891.561313938927 | 7000 | 4670.7530647986 | 500000 | 553077.738175513 | 100000 | 110615.547635103 | 0 | 0 |  |  | 607806 | 309904.362905693 | 669255.600189353 | [8 empty] | 810 |  | 1250 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 45000 | NO |  |  |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | AIR PATROL |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OFFSHORE PIPELINE OPERATING WELL BELOW MAOP | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  | YES |  |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NOT APPLICABLE - NOT MAINLINE PIPE | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | SUSIE RICHMOND | MANAGER OF PIPELINE COMPLIANCE AND TRAINING | susie.richmond@kineticallc.com | 985-223-6145 |  |  |  |  | SUSIE RICHMOND | MANAGER OF PIPELINE COMPLIANCE AND TRAINING | 985-209-4263 | susie.richmond@kineticallc.com | DURING ROUTINE PATROL A LEAK ON THE PIPELINE WAS IDENTIFIED. THE COORDINATES HAD TO BE RE-VERIFIED PRIOR THE REPORT BEING FILED DUE TO CONFLICTING INFORMATION. 5 509A-1500 PIPELINE SMYS WAS CORRECTED BY OUR PIPELINE ENGINEER, RICHARD SACCO, PE. SUPPLEMENTAL WAS CREATED IN ORDER TO PUT INTO FINAL STATUS AS REQUESTED BY PHMSA ENGINEER.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140120 | 16543 | 2014-11-14 17:06 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2014-10-15 18:10 | 2014 |  |  | 34.5579 | -118.15 | 1098406 | 2014-10-15 22:16 |  | NATURAL GAS |  | 0 | 28 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-11-08 10:00 | 2014-11-16 10:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-11-15 18:10 | 2014-11-15 18:35 | ONSHORE | CA | 93551 | PALMDALE | LOS ANGELES | MILEPOST | 217.55 | L235 | SL44-772 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 55 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2004 |  | CARBON STEEL |  | OTHER | [8 empty] | CURB VALVE INSTALLED IN CLOSED POSITION | CLASS 3 LOCATION | YES | METHOD1 | 579 |  | NO | NO | NO |  | 0 | 0 | 166 | 183.62180907427 | 0 | 0 | 50603 | 55974.785569791 | 600 | 663.693285810616 | 0 | 0 |  |  | 51369 | 26082.8435603507 | 56822.1006646759 | [8 empty] | 600 |  | 780 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 120 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [204 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | [6 empty] | YES | WRONG EQUIPMENT WAS USED RESULTING IN GAS OUTAGES TO CUSTOMERS | CONSTRUCTION | NO | [150 empty] | TROY A. BAUER | PIPELINE SAFETY AND COMPLIANCE ADVISOR | tbauer@semprautilities.com | 909-376-7208 | 909-885-6270 |  |  |  | TROY A. BAUER | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 909-376-7208 | tbauer@semprautilities.com | ON OCTOBER 15TH, 2014, SEVERAL CALLS WERE RECEIVED REPORTING NO GAS FROM THE PALMDALE AREA. NO INJURIES OR PUBLIC DAMAGE RESULTED FROM THIS INCIDENT. ALL CUSTOMERS WHOSE SERVICES WERE INTERRUPTED HAVE BEEN RESTORED. INVESTIGATION OF THE INCIDENT SHOWED THAT THE REGULATOR STATION SUPPLYING GAS TO THE AFFECTED CUSTOMERS WAS FED FROM TWO GAS TRANSMISSION LINES (LINE 235 AND LINE 335). FURTHER INVESTIGATION SHOWED A PIN OFF TEE ON THE TRANSMISSION LINE AND INSTRUMENTATION DIAGRAM OF LINE 235 FEEDING THE SUPPLY LINE TO THE REGULATOR STATION. A PIN OFF TEE IS NORMALLY BURIED IN THE OPEN (PIN RAISED POSITION) AND CANNOT BE OPERATED (PIN LOWERED) UNLESS EXCAVATED TO PROVIDE ACCESS TO THE PIN BY REMOVING A CAP ON THE PIN OFF TEE. THERE WAS NO PIN OFF TEE ON LINE 235 AND THE SUPPLY LINE TO THE REGULATOR STATION WAS ACTUALLY CONNECTED TO LINE 235 WITH A CLOSED CURB VALVE TEE INSTEAD. WHEN THE LINE 335 FEED WAS ISOLATED AND DEPRESSURIZED, THE FEED TO THE REGULATOR STATION WAS LOST RESULTING IN GAS OUTAGES. INITIALLY WHEN THE LINE 235 VALVE WAS CLOSED, THAT PIPELINE WAS NOT BLOWN DOWN AND THE VALVE BYPASSED ENOUGH THAT UPON CHECKING THE INLET FEED TO THE REGULATOR STATION IT APPEARED THE LINE 235 PIN OFF TEE WAS OPEN. THIS INCIDENT WAS REPORTED TO THE DOT AND CPUC WHEN ESTIMATED COSTS OF REPAIR AND RECOVERY WERE ANTICIPATED TO EXCEED $50,000 THRESHOLD.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140121 | 16674 | 2014-11-17 16:04 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2014-11-11 06:32 | 2014 |  |  | 41.7172 | -93.591 | 1100737 | 2014-11-11 07:58 |  | NATURAL GAS |  | 3990 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE DELIVERY POINT WAS BY-PASSED TO MAINTAIN SERVICE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-11-11 06:32 | 2014-11-11 06:55 | ONSHORE | IA | 50023 | ANKENY | POLK | SURVEY STATION NO. | 736031 | ANKENY #1 | 736031 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | FILTER/STRAINER/SEPARATOR | [38 empty] | 2014 |  | CARBON STEEL |  | OTHER | [8 empty] | THE RELIEF VALVE OPENED AFTER THE LINE PRESSURE STARTED TO EXCEED THE DELIVERY SET POINT DUE TO THE STRAINER ON THE METER BEING FULL OF DEBRIS. | CLASS 3 LOCATION | NO |  | 69 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 18135 | 12100.5866900175 | 0 | 0 | 300 | 331.846642905308 | 0 | 0 | NONE. |  | 18435 | 12697.5540362285 | 12432.4333329228 | [8 empty] | 131 |  | 275 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CAUSE OF THE INCIDENT WAS DUE TO EQUIPMENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [25 empty] | YES | DEBRIS COLLECTED IN THE STRAINER BLOCKED THE FLOW OF GAS | [161 empty] | J. DAVID CULLISON | PIPELINE SAFETY ENGINEER | j.cullison@nngco.com | 402-398-7439 | 402-548-5267 |  |  |  | THOMAS CORRELL | SR. DIRECTOR OF PIPELINE SAFETY AND RISK | 402-398-7715 | thomas.correll@nngco.com | ON NOVEMBER 11, 2014, AT APPROXIMATELY 0632 AN UNINTENTIONAL RELEASE OF GAS VENTED FROM A RELIEF VALVE AT THE GAS METERING STATION IN ANKENY, IOWA. A CALL FROM A CITIZEN WAS REPORTED TO NORTHERN JUST AS THE GAS CONTROL SYSTEM WAS ABLE TO CONFIRM A DROP IN INLET PRESSURE AT THE METERING STATION. NORTHERN DISPATCHED TECHNICIANS TO THE SITE AND VERIFIED THE 6-INCH RELIEF VALVE WAS VENTING GAS. THE STATION WAS BY-PASSED AT 0808 AND THE RELIEF VALVE STOPPED VENTING. AN INVESTIGATION CONCLUDED THAT THE METER STRAINER WAS FILLED WITH DEBRIS LIKELY FROM A CONSTRUCTION PROJECT TO REPLACE THE RELIEF VALVE AT THE STATION IN MAY OF 2014. THE REGULATOR DID NOT LOCK-UP FAST ENOUGH WHEN THE FLOW DECREASED AND THE PRESSURE WAS ABLE TO BUILD UP BETWEEN THE REGULATOR AND STRAINER TO REACH THE SET POINT OF THE RELIEF VALVE. ONCE THE RELIEF VALVE STARTED TO VENT, THERE WAS SUFFICIENT FLOW TO KEEP THE REGULATOR OPEN. THE STRAINERS WERE CLEANED, WHICH ALLOWED NORMAL FLOW, AND THE SYSTEM WAS RETURNED TO SERVICE.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20140122 | 16742 | 2014-11-19 13:26 | SUPPLEMENTAL FINAL | 18273 | SHELL PIPELINE CORP | 150 NORTH DAIRY ASHFORD ROAD WCK BLDG. A | HOUSTON | TX | 77079 | 2014-10-31 20:49 | 2014 |  |  | 28.0188 | -92.2543 | 1099934 | 2014-11-01 14:12 |  | NATURAL GAS |  | 420.4 | 11143.48 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-10-31 20:50 | 2014-11-21 07:27 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-10-31 20:50 | 2014-10-31 20:50 | OFFSHORE | [28 empty] | 600 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | VERMILLION | 397 | SPLASH ZONE OF RISER | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | FLANGE ASSEMBLY | [38 empty] | 1994 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | INSULATING GASKET MATERIAL | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 1 |  | NO | NO | NO |  | 0 | 0 | 40000 | 44246.219054041 | 1500 | 1000.87565674256 | 600000 | 663693.285810616 | 0 | 0 | 20000 | 22123.1095270205 | STANDBY VESSEL FOR ONE DAY |  | 661500 | 336155.657285783 | 731063.49004842 | [8 empty] | 1158 |  | 2160 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | REMOTELY CONTROLLED | 189758 | YES | [7 empty] | NO | [6 empty] | OFFSHORE GATHERING | YES | YES | YES | NO | NO | OTHER | PLATFORM OPERATOR TRANS CANADA |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | GASKET | [17 empty] | YES | MULTIPLE SANDBLASTING SINCE ORIGINAL CONSTRUCTION THINNED THE INSULATING GASKET | [161 empty] | RICHARD KLASEN | REGULATORY SPECIALIST | richard.klasen@shell.com | 713 241 1064 | 713 241 8498 |  |  |  | DEBORAH PRICE | INTEGRITY AND REG SRVC MANAGER | 713 241 2035 | deborah.price@shell.com | OFFSHORE NATURAL GAS GATHERING PIPELINE INSULATING GASKET FAILURE ON THE RISER AT THE TERMINUS OF THE PIPELINE SEGMENT. INSULATING GASKET WAS LOCATED IN THE SPLASH ZONE AT PLUS 12 OF THE PLATFORM. GASKET REPLACED WITH STAINLESS STEEL RTJ GASKET 11/16. DETERMINED THE INSULATING GASKET HAD WORN DOWN DUE TO MULTIPLE BLASTING AND PAINTING SINCE ORIGINAL CONSTRUCTION IN 1994. GASKET HAD ERODED REDUCING THE AREA OF THE INSULATING GASKET TO HOLD MAINLINE PRESSURE. BEGAN FILLING THE LINE SEGMENT 11/17. PERFORMED PRESSURE STAND UP ON SYSTEM 11/19. STARTED UP THE PIPELINE SYSTEM ON 11/21. NOTES 4/27/15 PIPELINE RELEASE LOCATION ON VR-397 PLATFORM WAS FLOWN OVER BY HELICOPTER ON 11/1/14 AT 10:35HRS TO VERIFY FLANGE GASKET FAILURE. NOT ALLOWED TO LAND ON PLATFORM DUE TO UNSAFE AIR MONITORING CONDITIONS. 2/21/15 - PLANNED SHUTDOWN TO RE-SURFACE FLANGE FACES AND INSTALL AN ANSI 900 VERY CRITICAL SERVICE FIRE (VCSF) PIKOTEK INSULATING GASKET KIT. LINE FILLED AND RETURNED TO OPERATION 4/9/15.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140123 | 16548 | 2014-11-20 17:11 | ORIGINAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2014-10-23 00:39 | 2014 |  |  | 41.802 | -85.5866 | 1099670 | 2014-10-29 14:37 |  | NATURAL GAS |  | 9258 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | OPERATOR ERROR DID NOT REQUIRE SHUTDOWN OF THE FACILITY. NO FIREGATE EVENT. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-10-23 00:39 | 2014-10-23 00:39 | ONSHORE | MI | 49099-9775 | WHITE PIGEON | ST. JOSEPH |  |  | WHITE PIGEON COMPRESSOR STATION | BLOWDOWN VALVES 634, 636, 638, 751, 761, 771 & 781 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 2010 |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENDED OPERATION OF BLOWDOWN VALVES. | CLASS 1 LOCATION | NO |  | 641 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 47598 | 31759.7863397548 | 0 | 0 | 60 | 66.3693285810616 | 0 | 0 |  |  | 47658 | 32957.2778825522 | 31826.1556683359 | [8 empty] | 792 |  | 960 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT OCCURRED DUE TO OPERATOR ERROR. CONTROLLER/CONTROL ROOM ISSUES DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | OPERATOR INTERRUPTED POWER TO UPS SYSTEM, RESULTING IN ACTIVATION OF BLOWDOWN VALVES AND VENTING GAS. |  | YES |  |  |  | NON-ROUTINE OPERATING CONDITIONS (ABNORMAL OPERATIONS OR EMERGENCIES) | NO | [150 empty] | ALAN M. CHICHESTER | GAS REGULATORY SERVICES ENGINEER | alan.chichester@cmsenergy.com | 989-791-5841 |  |  |  |  | TRACY A. GOBLE | REGULATORY AND COMPLIANCE MANAGER | 517-768-3187 | tracy.goble@cmsenergy.com | ON OCTOBER 23, 2014, A "PRIORITY 1, 120V" BATTERY REPLACEMENT ALARM FOR THE UNINTERRUPTED POWER SUPPLY (UPS) SYSTEM TRIGGERED AT WHITE PIGEON COMPRESSOR STATION IN ST. JOSEPH COUNTY, MICHIGAN. AT APPROXIMATELY 12:39 AM, AFTER SEVERAL UNSUCCESSFUL ATTEMPTS TO CLEAR THE ALARM, AN OPERATOR ATTEMPTED TO CLEAR THE ALARM BY CUTTING POWER TO THE UPS SYSTEM. SINCE THE UPS SYTEM CONTROLS BLOWDOWN VALVE SOLENOIDS AT WHITE PIGEON, THIS POWER INTERRUPTION CAUSED SEVEN BLOWDOWN VALVES (VALVE NUMBERS 634, 636, 638, 751, 761, 771, AND 781) TO VENT GAS TO ATMOSPHERE. ADDITIONAL ALARMS WERE TRIGGERED AS A RESULT OF THE BLOWDOWN VALVE OPERATION, PRESSURE FLUCTUATIONS, AND LOSS OF POWER TO THE UPS AND DOWNSTREAM SYSTEMS. POWER WAS RESTORED TO THE UPS SYSTEM IMMEDIATELY AFTER SHUTDOWN. UPON ALARM ACKNOWLEDGMENT, BLOWDOWN VALVES WERE CLOSED BY A COMBINATION OF AUTOMATIC AND MANUAL OPERATION. AS A RESULT, THE BLOWDOWN VALVES VENTED FOR VARIOUS DURATIONS (BETWEEN 2 AND 11 MINUTES).
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140124 | 16549 | 2014-11-21 12:01 | ORIGINAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2014-10-29 23:55 | 2014 |  |  | 29.2913 | -95.9364 | 1099795 | 2014-10-30 18:04 |  | NATURAL GAS |  | 4900 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | LOCAL OPERATIONS WERE NOT INTERUPTED. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-10-30 00:10 | 2014-10-30 00:10 | ONSHORE | TX | 77042 | BOLING | WHARTON |  |  | WILSON STORAGE FACILITY (COMPRESSOR STATION) | UNIT 897 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1980 |  | CARBON STEEL |  | OTHER |  |  |  | BLOW DOWN VALVE DID NOT SEAT |  |  |  |  | UNIT BLOWDOWN VALVE DID NOT PROPERLY SEAT DURING OPERATION. | CLASS 1 LOCATION | NO |  | 578 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 19300 | 12877.9334500876 | 0 | 0 | 0 | 0 | 0 | 0 | NO PROPERTY DAMAGE |  | 19300 | 13351.1383537653 | 12877.9334500876 | [8 empty] | 1900 |  | 2539 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM OR CONTROLLER DID NOT AFFECT OR CONTRIBUTE TO THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | OTHER | BLOWDOWN VALVE DID NOT PROPERLY SEAT DURING OPERATION. | [20 empty] | YES | ADDITIONAL FACTORS NOT IDENTIFIED SINCE INOPERATION COULD NOT BE REPLICATED. | [161 empty] | MICHAEL D. SMITH | COMPLIANCE SPECILIEST | mdsmith@eprod.com | 713-381-5650 |  |  |  |  | MICHAEL D. SMITH | COMPLIANCE SPECILIEST | 713-381-5650 | mdsmith@eprod.com | ON 10/29/2014 AT 23:55, WILSON STORAGE COMPRESSOR UNIT# 897 WAS STARTED FOR DELIVERING NATURAL GAS INTO STORAGE. AN ENTERPRISE EMPLOYEE DISCOVERED THAT NATURAL GAS WAS VENTING FROM THE UNIT BLOWDOWN VALVE. OPERATIONS SHUTDOWN THE COMPRESSOR TO INVESTIGATE AND DETERMINE THE ROOT CAUSE BUT COULD NOT REPLICATE THE ISSUE AS THE VALVE WORKED PROPERLY EACH TIME AS DESIGNED. NO OPERATIONAL OR DESIGN ISSUES WERE DISCOVERED. OPERATIONS RESTARTED THE COMPRESSOR AT 03:00 AND IT RAN FOR 6 HOURS WITH NO ADDITIONAL ISSUES. OPERATIONS WILL CONTINUE TO MONITOR THIS UNIT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140125 | 16550 | 2014-11-21 13:06 | ORIGINAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2014-11-01 10:01 | 2014 |  |  | 32.178 | -97.3345 | 1099919 | 2014-11-01 10:53 |  | NATURAL GAS |  | 12231 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | HEADER #2 WAS BYPASSED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-11-01 06:03 | 2014-11-01 06:03 | ONSHORE | TX | 76031 | CLEBURNE | JOHNSON | SURVEY STATION NO. | 0+00 | CLEBURNE COMPLRESSOR STATION | HEADER #2 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 2006 |  | CARBON STEEL |  | OTHER | [8 empty] | SOLENOID FAILED AND CONTROL VALVE FAILED OPEN | CLASS 1 LOCATION | NO |  | 201 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 48312 | 32236.2031523643 | 750 | 829.61660726327 | 0 | 0 | 0 | 0 |  |  | 49062 | 33801.5514653522 | 33065.8197596275 | [8 empty] | 921 |  | 1180 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | YES | [10 empty] | YES | FAILURE OF SOLENOID CAUSED CONTROL VALVE TO FAIL OPEN | [22 empty] | YES | SOLENOID FAILURE | [161 empty] | DANNY NICHOLS | DIRECTOR REGULATORY COMPLIANCE | danny.nichols@energytransfer.com | 713-989-7232 | 713-989-1188 |  |  |  | DANNY NICHOLS | DIRECTOR REGULATORY COMPLIANCE | 713-989-7232 | danny.nichols@energytransfer.com | ON NOVEMBER 1, 2014, AT APPROXIMATELY 5:14 AM, ENERGY TRANSFER COMPANY EXPERIENCED AN EQUIPMENT FAILURE AT THE CLEBURNE COMPRESSOR STATION ON THE HEADER #2 IN JOHNSON COUNTY NEAR CLEBURNE, TEXAS. THE COMPRESSOR STATION IS PART OF AN INTRASTATE NATURAL GAS PIPELINE LOCATED IN A RURAL AREA (CLASS 1) UNDER THE JURISDICTION OF THE TEXAS RAILROAD COMMISSION. THE INCIDENT WAS REPORTED TO THE TEXAS RAILROAD COMMISSION AND ALSO TO THE NRC UNDER ID# 1099919. THERE WERE NO FATALITIES, INJURIES, EVACUATIONS, ROAD CLOSURES, EXPLOSIONS, FIRE, MEDIA INTEREST, SPILLS OR ANY RESPONSE BY AN EMERGENCY OFFICIAL. THE NEAREST STRUCTURE INTENDED FOR HUMAN OCCUPANCY IS 150 YARDS NORTH AND THE NEAREST PUBLIC ROAD IS WEST HWY 67 LOCATED 0.5 MILES NORTH OF THE INCIDENT SITE. AT 5:14 AM ETC GAS CONTROL RECEIVED NOTIFICATION FROM AN AREA LAND OWNER THAT THE LAND OWNER COULD HEAR A "ROARING" NOISE AT THE CLEBURNE COMPRESSOR STATION. THE ON-CALL ETC TECHNICIAN WAS NOTIFIED IMMEDIATELY THAT THE DISCHARGE PRESSURE HAD FALLEN SUDDENLY AT THE STATION. UPON ARRIVAL, THE ETC TECHNICIAN FOUND A CONTROL VALVE HAD FAILED FULLY OPEN AND WAS RELEASING GAS FROM STATION HEADER #2. ETC TECHNICIAN CLOSED THE VALVE MANUALLY AT 6:03 AM. ETC TECHNICIAN FOUND THE SOLENOID FOR THE CONTROL VALVE HAD FAILED. THE SOLENOID WAS REPLACED AND IN SERVICE AT 11:30 AM. THE FAILED CONTROL VALVE RELEASED 12,231 MCF OF NATURAL GAS. THE CALCULATIONS WERE CONFIRMED AT 10:01 AM AND THE EVENT WAS DETERMINED TO BE A REPORTABLE INCIDENT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140126 | 31444 | 2014-11-21 20:56 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2014-10-24 07:28 | 2014 |  |  | 35.2449 | -119.0488 | 1099198 | 2014-10-24 |  | NATURAL GAS |  | 92000 | 10000 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-10-24 11:51 | 2014-10-26 11:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 2 | 2014-10-24 07:28 | 2014-10-24 07:57 | ONSHORE | CA | 93313 | BAKERSFIELD | KERN | MILEPOST | MP 271.55 | L-300A |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 54 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 34 |  | 0.375 | 52000 | API 5L X-52 | DSAW |  | CONSOLIDATED WESTERN STEEL | ASPHALT | [28 empty] | 1954 | 1954 | CARBON STEEL |  | MECHANICAL PUNCTURE | 8 | 18 | [7 empty] | CLASS 1 LOCATION | NO |  | 646 |  | NO | NO | NO |  | 0 | 0 | 45000 | 49776.9964357962 | 414000 | 276241.681260946 | 520000 | 575200.847702534 | 0 | 0 | 0 | 0 |  |  | 979000 | 573273.615865979 | 901219.525399275 | [8 empty] | 640 |  | 757 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 42240 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY DIG IN | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | YES |  |  | YES | PRIVATE LANDOWNER | [7 empty] | FARMER | FARM EQUIPMENT | AGRICULTURE | YES | 422144 | USAN | UTILITY OWNER | NO | NO | YES | 47 | LOCATING PRACTICES NOT SUFFICIENT |  | FACILITY WAS NOT LOCATED OR MARKED | [264 empty] | ENZA BARBATO | PROGRAM MANAGER | e1bo@pge.com | 925-357-7889 |  |  |  |  | SUSIE RICHMOND | MANAGER OF REGULATORY COMPLIANCE | 925-328-5776 | gsr8@pge.com | AT 0732 HOURS ON OCT. 24, 2014, PG&E WAS INFORMED OF A THIRD-PARTY DIG IN NEAR WIBLE ROAD AND HOUGHTON ROAD IN BAKERSFIELD. A THIRD PARTY FURROWING A FIELD STRUCK TRANSMISSION LINE L-300A CAUSING AN UNINTENTIONAL RELEASE OF NATURAL GAS. L-300A IS A 34-INCH LINE LOCATED DOWNSTREAM OF MILE POINT 270.85, DURING THE INCIDENT, VALVES AT MP 270.85 AND MP278.70 WERE CLOSED AND THE BLOWOFF VALVES (AT BOTH LOCATIONS) WERE OPENED TO EXPEDITE DEPRESSURIZING OF APPROXIMATELY 8 MILES OF THE PIPE. THE FLOW OF GAS STOPPED AT 1151 HOURS. THE FIRE DEPARTMENT ESTABLISHED AN 8 SQUARE-MILE EXCLUSION ZONE AROUND THE DIG-IN AREA AND EVACUATED TWO ELEMENTARY SCHOOLS. NO INJURIES, NO FATALITIES, AND NO IGNITION OCCURRED DURING THE INCIDENT. KERN COUNTY FIRE LIFTED THE EXCLUSION ZONE AT ABOUT 1230 HOURS. ENVIRONMENTAL HEALTH AND HAZARDOUS MATERIALS PERSONNEL MONITORED THE AIR QUALITY FOR APPROXIMATELY 30 MINUTES AFTER THE GAS WAS SHUT IN AND DEEMED IT WAS SAFE TO LIFT THE ORDER. TRAFFIC CONTROL WAS CONDUCTED BY THE CALIFORNIA HIGHWAY PATROL AND KERN COUNTY SHERIFF'S OFFICE. TRANSMISSION LINE L-312, WHICH IS TAPPED OFF OF THIS SECTION OF L-300A AND SERVES ROUGHLY 100 CUSTOMERS, WAS ALSO ISOLATED BUT DUE TO LINE PACK THE CUSTOMERS WERE NOT AFFECTED. THREE COMMERCIAL CUSTOMERS LOST SERVICE DURING THE INCIDENT: TEXACO, VULCAN MATERIALS, AND INDUSTRIAL OIL AND ASPHALT. BY 0900 HOURS ON OCT. 26, VULCAN AND RIDGELINE OIL AND ASPHALT WERE RETURNED TO SERVICE. LINE 312 AND TEXACO WERE RETURNED TO SERVICE AT APPROXIMATELY 1100 HOURS ON OCT. 26. REPAIRS WERE MADE BY REPLACING THE DAMAGED PORTION OF PIPELINE WITH PRE-TESTED PIPE, SUCCESSFUL RADIOGRAPHIC EXAMINATIONS OF THE WELDS WERE MADE, AND THE APPROXIMATE 8 MILES OF L-300A WAS PURGED AND RE-PRESSURIZED WITH NATURAL GAS PRIOR TO 0145 HOURS ON OCT. 26, 2014. THE FACILITY WAS NOT LOCATED AND MARKED UNDER USA TICKET 422144. THE INCIDENT WAS REPORTED TO THE CPUC AND DOT BECAUSE DAMAGES EXCEED $50,000. SAFETY AND ENFORCEMENT DIVISION OF THE CALIFORNIA PUBLIC UTILITIES COMMISSION (CPUC) ISSUED A CITATION TO PG&E FOR FAILING TO FOLLOW ITS PROCEDURES TO ADEQUATELY DOCUMENT THE EXCAVATION AREA IN USA TICKET 0422144 AND FOR FAILING TO SUBMIT A SUPPLEMENTARY REPORT TO PHMSA REFLECTING THIS INFORMATION. THIS INCIDENT IS CURRENTLY THE SUBJECT OF A DISPUTE IN A CIVIL LAW SUIT PENDING IN KERN COUNTY SUPERIOR COURT OF CALIFORNIA ENTITLED PG&E V. ALEXANDER ET AL. CASE NO. BCV-15-101623 AND RELATED CROSS-ACTION. PG&E WILL SUBMIT A SUPPLEMENTAL REPORT TO PHMSA WHEN THE LITIGATION IS RESOLVED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140127 | 16643 | 2014-11-24 14:53 | SUPPLEMENTAL FINAL | 31531 | ONEOK WESTEX TRANSMISSION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2014-09-23 10:44 | 2014 |  |  | 31.4078 | -103.258 | 1096235 | 2014-09-23 14:22 |  | NATURAL GAS |  | 38 | 6604 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-09-23 15:37 | 2014-12-12 14:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-09-23 10:44 | 2014-09-23 11:30 | ONSHORE | TX | 79719 | Not Within a Municipality | REEVES | MILEPOST | PECOS RIVER | 4001-000 | PECOS RIVER CROSSING | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 84 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 |  | 0.219 | 42000 | X-42 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | JONES AND LAUGHLIN STEEL | COAL TAR | [28 empty] | 1968 | 1968 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 256 |  | NO | NO | NO |  | 0 | 0 | 26259 | 29046.5366535016 | 144 | 96.0840630472855 | 121863 | 134799.424814565 | 1000 | 1106.15547635103 | 0 | 0 |  |  | 149266 | 75816.9889524359 | 165048.201007465 | [8 empty] | 840 |  | 953 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 92770 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1968 | YES | YES | YES | YES | YES |  | 2014 | 2006 | 2006 |  | YES | [190 empty] | NO | [63 empty] | NO |  |  | Yes, but the point of the Accident was not identified as a dig site |  | 2006 | [11 empty] | NO | [63 empty] | PATTI FORD | SENIOR PIPELINE SAFETY ENGINEER | patti.ford@oneok.com | 918 588 7131 | 918 732 1311 |  |  |  | WESLEY R. DUNBAR | VICE PRESIDENT | 918 588 7424 | wesley.dunbar@oneok.com | AT APPROXIMATELY 1044 HOURS ON SEPTEMBER 23, 2014, ONEOK WESTEX TRANSMISSION (OWT) WAS NOTIFIED BY THE PUBLIC OF A POSSIBLE GAS LEAK NEAR A PECOS RIVER CROSSING ON THE 12 INCH LINE 4001-000 ABOUT 14 MILES EAST OF PECOS, TX IN A CLASS I AREA. OWT PERSONNEL ARRIVED ON SITE AT APPROXIMATELY 1130 HOURS AND OBSERVED GAS BUBBLING UP IN WATER STANDING OVER THE PIPELINE. THE LOCATION IS VERY RURAL WITH AN OIL FIELD LEASE ROAD BRIDGE CROSSING THE RIVER ABOUT 150 FEET NORTH OF THE OWT PIPELINE. THERE WAS NO FIRE OR EXPLOSION ASSOCIATED WITH THE RELEASE. RECENT FLOODING AND CONTINUED RAIN IN THE AREA PREVENTED IMMEDIATE DIRECT ACCESS TO THE LEAKING SECTION OF PIPELINE. THE LINE SEGMENT WAS SHUT IN AND PRESSURE IN THE 17.5 MILE SEGMENT WAS REDUCED IMMEDIATELY UPON DISCOVERY OF THE LEAK. A POSITIVE PRESSURE IS BEING MAINTAINED ON THE ISOLATED SEGMENT TO KEEP WATER AND SILT OUT OF THE PIPELINE UNTIL PERSONNEL CAN SAFELY ASSESS THE PIPELINE. THE PIPELINE LEAK WILL BE ASSESSED AND REPAIRED ONCE THE FLOOD WATERS HAVE SUBSIDED. THIS WILL HOPEFULLY TO START SOON, PENDING SITE ACCESSIBILITY WITH EQUIPMENT. THIS INCIDENT REPORT WAS NOT FILED WITHIN THE 30 DAYS OF THE LEAK DISCOVERY AS IT WAS NOT EXPECTED TO MEET THE REPORTABLE INCIDENT CRITERIA AT THAT TIME. ONCE ACCESS TO THE SITE IMPROVED, A BETTER ESTIMATE FOR REPAIR WAS ESTABLISHED. THE NEW COST ESTIMATE IS MORE THAN $50,000 SO THIS INCIDENT REPORT IS BEING FILED. THIS INCIDENT REPORT IS MISSING INFORMATION THAT CAN ONLY BE DETERMINED ONCE THE LEAK IS ACCESSED AND REPAIRED. IT WILL BE UPDATED ONCE THE PIPE AND THE LEAK HAVE BEEN EVALUATED. UPDATE: THE LEAK WAS FINALLY ACCESSIBLE ON DECEMBER 8TH, 2014. EXCAVATION VIA HYDROVAC EXPOSED THE PIPELINE AND THE AREA OF THE LEAK. A 0.100' PIN HOLE WAS LOCATED AT THE 7 O'CLOCK POSITION OF THE PIPE. THE 17.57 MILE ISOLATED SECTION OF PIPELINE WAS BLOWN DOWN AND CONTRACTOR COMPLETED EXCAVATION ON DECEMBER 9TH, 2014. APPROXIMATELY 115' OF THE PIPELINE WAS CUT OUT ON DECEMBER 10TH, 2014 AND NEW 12.75' OD X-42 0.250' WT FBE ERW PIPE WAS INSTALLED ON DECEMBER 10TH AND 11TH. THE PIPELINE WAS PURGED, PRESSURED UP AND RETURNED TO SERVICE ON DECEMBER 12TH, 2014 AT APPROXIMATELY 2:30PM. THE CAUSE OF THE LEAK WAS LOCALIZED EXTERNAL CORROSION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140128 | 17015 | 2014-11-25 13:23 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2014-10-15 12:12 | 2014 |  |  | 39.4023 | -82.5138 | 1099737 | 2014-10-30 10:40 |  | NATURAL GAS |  | 2 | 3745 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-10-15 13:45 | 2014-10-19 05:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-10-15 10:05 | 2014-10-15 10:15 | ONSHORE | OH | 43135 | TOWN OF SOUTH BLOOMINGVILLE | HOCKING COUNTY | SURVEY STATION NO. | 918+56 | LINE R-701 | FAIRVIEW ROAD | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 93 |  | YES |  |  |  |  | YES | CASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 |  | 0.25 | 60200 | 5L | DSAW |  | US STEEL - NATIONAL TUBE | COAL TAR | [28 empty] | 1968 | 1968 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 365 |  | NO | NO | NO |  | 0 | 0 | 14718 | 16280.3963009344 | 8 | 5.33800350262697 | 315650 | 349157.976110201 | 0 | 0 | 0 | 0 |  |  | 330376 | 167751.389848523 | 365443.710414638 | [8 empty] | 454 |  | 750 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 31680 | NO |  | YES |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER WAS NOT INVOVLVED OR HAD ANY ROLE IN IDENTIFYING THIS NON-HAZARDOUS LEAK INSIDE THE CASING OF THE PIPE | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  |  | YES | [7 empty] | YES |  |  |  | YES | YES | 1978 | NO | NO | [8 empty] | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | GEORGE HAMATY | ENGINEER | ghamaty@cpg.com | (304)357-3728 |  |  |  |  | PERRY M. HOFFMAN | MANAGER | (304)357-2548 | mikehoffman@cpg.com | ON OCTOBER 15, 2014, A CONTRACTOR EMPLOYED BY COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA) WAS WORKING ON A NEAR-BY PROJECT, WHEN HE DETECTED THE ODOR OF NATURAL GAS. UPON FURTHER INVESTIGATIONS, A CASING VENT WAS TESTED FOR EVIDENCE OF A NON-HAZARDOUS NATURAL GAS LEAK INSIDE A CASING. OPERATIONS PERSONNEL WERE NOTIFIED TO ASSIST IN SECURING THE SITE PENDING FURTHER ASSESSMENT AND NECESSARY SAFETY MEASURES. THE SEGMENT WAS ISOLATED BY COLUMBIA PERSONNEL AND THE LINE WAS BLOWN DOWN. HENCE, THE SITE WAS SECURED. UPON FURTHER INVESTIGATION, A DECISION WAS MADE TO REPLACE THE CASING AND THE PIPE WITH A PIPE. UPON REMOVAL OF THE PIPE, AN EXTERNAL CORROSION PIT WITH 100 PERCENT WALL PENETRATION WAS DETERMINED TO BE THE CAUSE OF THE UNINTENDED NATURAL GAS RELEASE. THE CORROSION PIT WAS APPROXIMATELY 3.75 INCHES INSIDE OF THE NORTH END OF THE CASING AT THE 5 O'CLOCK POSITION WHEN FACING NORTH. THE PIT WAS AT A LOCATION OF DAMAGED OR MISSING COATING. THE DAMAGED COATING WAS LOCATED UNDER THE RUBBER CASING ISOLATOR. BOTH RUBBER ISOLATORS AND WOODEN CENTRALIZERS WERE OBSERVED TO BE IN USE UPON REMOVAL OF THE CASING. HOWEVER, THE CARRIER PIPE WAS NOT CENTERED THROUGH THE CASING. WATER MARKS WERE OBSERVED ON BOTH THE CARRIER PIPE AND ON THE CASING, INDICATING THAT THE CASING SEALS HAD BEEN COMPROMISED AND, AT TIMES, WATER HAD BEEN PRESENT IN THE ANNULAR SPACE. WATER FLOWED OUT OF THE SOUTH SIDE OF THE CASING WHEN THE SOUTH SIDE CASING SEAL WAS EXPOSED. NO KNOWN SOIL CONDITIONS OR MEASURED POTENTIAL READINGS COMMONLY ASSOCIATED WITH MICROBIOLOGICALLY INFLUENCED CORROSION OR CATHODIC PROTECTION INTERFERENCE WERE OBSERVED. 1. THE EXTERNAL CORROSION PIT OCCURRED AS A RESULT OF CORROSION AT THE SITE OF COATING DAMAGE UNDER THE RUBBER CASING ISOLATOR ON THE NORTH SIDE OF THE CASING. 2. THE COATING DAMAGE LIKELY OCCURRED DURING INSTALLATION OF THE CASING OR DURING A SUBSEQUENT EXCAVATION OF THE CASING ENDS. THE WOODEN CENTRALIZERS CAUSED AND/OR EXACERBATED THE COATING DAMAGE. 3. THE PLACEMENT OF THE CASING ISOLATOR OVER THE AREA OF DAMAGED COATING DID NOT ISOLATE THE EXPOSED STEEL FROM EVENTUAL ELECTROLYTE INTRUSION. WITH WATER BEING PRESENT BETWEEN THE CASING SEAL AND THE PIPE, ATMOSPHERIC AND CREVICE CORROSION PITTED THE PIPE TO CAUSE THE LEAK. 4. THE INTRODUCTION OF WATER AS AN ELECTROLYTE TO THE EXPOSED STEEL CREATED A LOCALIZED CORROSION CELL UNDER THE RUBBER CASING ISOLATOR. EXTERNAL CORROSION OCCURRED WHEN THE NON-LEVEL CASING FILLED WITH WATER COMPLETELY TO THE NORTH (HIGH) SIDE OF THE ROAD AND ATMOSPHERIC CORROSION OCCURRED WHEN THE CASING WAS NOT COMPLETELY FILLED. 5. DURING THE TIME WHEN THE CASING WAS COMPLETELY FILLED WITH WATER, THE RUBBER CASING ISOLATOR SHIELDED THE EXPOSED STEEL FROM CATHODIC PROTECTION CURRENT THAT COULD HAVE MITIGATED THE CORROSION CELL DURING THAT TIME. DURING THE TIME WHEN ATMOSPHERIC CORROSION WAS OCCURRING, ONLY RE-COATING THE EXPOSED STEEL OR MAINTAINING DRY CONDITIONS INSIDE THE CASING COULD HAVE MITIGATED THE CORROSION CELL. KEY LESSONS LEARNED/CORRECTIVE MEASURES: 1) THE NATURE AND LOCATION OF THE CORROSION PIT THAT CAUSED THE LEAK MAKES IT DIFFICULT, IF NOT IMPOSSIBLE, TO DETECT DURING TYPICAL, NON-EXCAVATION CASING POTENTIAL OR SHORT TESTS. BECAUSE THE CORROSION OCCURRED IN AN ELECTRICALLY SHIELDED AREA, THE ONLY RELIABLE METHOD FOR DETECTION IS THE USE OF IN-LINE INSPECTION TOOLS. LINE R-701-N IS IN THE PROCESS OF BEING RECONFIGURED FOR THE PURPOSE OF RUNNING IN-LINE INSPECTION TOOLS IN THE FUTURE. 2) THERE WERE NO INDICATORS FOR A LOW PIPE-TO-SOIL POTENTIAL MEASUREMENTS FOR THE PIPELINE IN THE AREA GOING BACK TO 2008. LIKEWISE, NO CASING-TO-SOIL POTENTIAL MEASUREMENTS INDICATED SHORT TESTING WAS NEEDED. 3) FILLING THE ANNULAR SPACE BETWEEN THE CARRIER PIPE AND THE CASING WITH A DIELECTRIC MATERIAL REMOVES THE CORROSIVE ENVIRONMENT AND CAN PREVENT CORROSION FROM OCCURRING. FILLING OF THIS CASING COULD HAVE PREVENTED THIS LEAK.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140129 | 16978 | 2014-11-25 21:34 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2014-10-15 13:00 | 2014 |  |  | 37.4006 | -121.9657 | 1099669 | 2014-10-29 |  | NATURAL GAS |  | 0 | 830 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-11-14 17:00 | 2014-11-21 20:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-10-15 13:00 | 2014-10-15 13:00 | ONSHORE | CA | 95050 | SANTA CLARA | SANTA CLARA | MILEPOST | 3.07 | LINE 132 | 113 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 66 |  | YES |  |  | YES | CASED | [18 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 |  | 0.281 | 40000 | GRADE B | SEAMLESS |  | NATIONAL TUBE CO. | ASPHALT | [28 empty] | 1944 | 1944 | CARBON STEEL |  | LEAK |  |  | OTHER | TO BE DETERMINED | [5 empty] | CLASS 3 LOCATION | YES | METHOD2 | 322 |  | NO | NO | NO |  | 0 | 0 | 3735 | 4131.49070417108 | 0 | 0 | 200000 | 221231.095270205 | 0 | 0 | 0 | 0 |  |  | 203735 | 103447.373567094 | 225362.585974376 | [8 empty] | 285 |  | 300 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | YES | NO | PHMSA |  |  | MANUAL | REMOTELY CONTROLLED | 15998 | YES | [7 empty] | YES |  | YES |  |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS DETECTED DURING ROUTINE LEAK SURVEY. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  |  |  |  | YES | [6 empty] | YES |  |  | YES | YES |  | YES | YES |  |  | YES |  |  |  | 2014 |  | YES | [190 empty] | NO | [63 empty] | YES | 2011 | 695 | Yes, and an investigative dig was cunducted at the point of the Accident | 2014 | [12 empty] | YES | 2014 |  |  |  | 2014 |  |  | YES |  |  |  | YES | [51 empty] | STEPHEN RAMOS | COMPLIANCE ENGINEER | s3rc@pge.com | 925-328-6107 |  |  |  |  | LARRY DENISTON | MANAGER OF GAS REGULATORY COMPLIANCE | 925-328-5756 | lcd1@pge.com | ON OCT. 15, 2014 DURING A ROUTINE LEAK SURVEY, A NON-HAZARDOUS LEAK WAS DISCOVERED AT THE CASING VENT ON PG&E'S TRANSMISSION LINE L-132 AT MILE POINT 3.07. THE 30-INCH CASING AND 24-INCH DIAMETER TRANSMISSION PIPE L-132 CROSS BENEATH THE UNION PACIFIC RAIL ROAD NEAR LAFAYETTE AND GIANERA STREETS. IN RESPONSE, PG&E IMMEDIATELY BEGAN EXCAVATIONS TO ASSESS THE PIPE CONDITION ON OCTOBER 15, 2014. AN EMERGENCY EXCAVATION NOTICE WAS SENT TO THE CPUC ON OCTOBER 16 REGARDING THIS MATTER. THE CASING ENDS WERE EXCAVATED, THE NON-HAZARDOUS LEAK HAS BEEN DETERMINED TO ORIGINATE FROM THE BOTTOM OF THE CARRIER PIPE. THE CAUSE OF THE LEAK IS DUE TO MICROBIOLOGICAL EXTERNAL CORROSION. ON OCTOBER 23, 2014, PRESSURE FOR L-132 WAS LOWERED 20% (FROM 285 PSIG TO 228 PSIG) AND A SAFETY RELATED CONDITION REPORT WAS SUBMITTED TO THE DOT AND CPUC. THIS INCIDENT WAS REPORTED TO THE DOT AND CPUC ON OCTOBER 29, 2014 UPON DETERMINATION THAT RESPONSE COSTS ARE ESTIMATED TO EXCEED $50,000. THERE ARE NO INJURIES, NO FATALITIES, AND NO IGNITION. NO MEDIA WAS OBSERVED ON SCENE. A LIQUEFIED NATURAL GAS (LNG) INSTALLATION NOTIFICATION WAS SENT TO THE CPUC ON NOVEMBER 13, 2014 IN THE EVENT THAT ADDITIONAL GAS SUPPLY WAS REQUIRED TO PREVENT THE LOSS OF CUSTOMERS DURING REPAIRS. DURING THE SHUTDOWN OF THE TRANSMISSION LINE, THE FEED TO THIS CRITICAL REGULATOR STATION WAS TEMPORARILY SUPPLIED WITH COMPRESSED NATURAL GAS (CNG), AS TEMPERATURES WERE MILD AND THE LNG SUPPORT WAS NOT REQUIRED. ON NOVEMBER 19, PG&E INSTALLED THE NEW 24-INCH PIPE INTO THE EXISTING 30-INCH CASING. BY NOVEMBER 21 AT APPROXIMATELY 2313 HOURS, PG&E COMPLETED TIE-IN AND RETURNED L-132 TO NORMAL OPERATING PRESSURE OF 285 PSIG.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140130 | 16620 | 2014-12-03 11:50 | SUPPLEMENTAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2014-11-05 05:10 | 2014 |  |  | 32.7877 | -84.2543 | 1100216 | 2014-11-05 09:35 |  | NATURAL GAS |  | 12000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | FACILITY CONTINUED TO OPERATE SAFELY | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-11-05 05:15 | 2014-11-05 06:28 | ONSHORE | GA | 30256 | THOMASTON | HUDSON | MILEPOST | 346.954 | THOMASTON COMPRESSOR | THOMASTON COMPRESSOR | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | VENT VALVE RELEASE | CLASS 1 LOCATION | NO |  | 860 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 40620 | 27103.7127845884 | 300 | 331.846642905308 | 200 | 221.231095270205 | 0 | 0 |  |  | 41120 | 28353.5270130953 | 27656.790522764 | [8 empty] | 928 |  | 1200 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS CONTROL PERSONNEL NOTICED SCADA ALARM. THE CONTROLLER DID NOT CONTRIBUTE TO THE INCDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [6 empty] | YES | AUTO-OPERATED UNIT VENT VALVE | [22 empty] | YES | LATCH RELAY" FAILED, PREVENTENG VENT VALVE FROM CLOSING PROPERLY | [161 empty] | ZACHARY RAGAIN | ENGINEER - PIPELINE | zachary_ragain@kindermorgan.com | 713-420-6633 |  |  |  |  | ZACHARY RAGAIN | ENGINEER - PIPELINE | 713-420-6633 | zachary_ragain@kindermorgan.com | ON NOVEMBER 5, 2014, AT 5:08 AM EST, GAS CONTROL SENT A START COMMAND TO INITIATE A START ON THOMASTON UNIT 3. TRENDING DATA INDICATES THAT AT 05:10 AM EST, DURING THE PURGE/PRESSURIZE SEQUENCE, THE UNIT VENT VALVE FAILED TO CLOSE AND THE START SEQUENCE FAILED. ALL AFFECTED VALVES SHOULD HAVE RETURNED TO THEIR NORMAL POSITIONS. AT 5:15 AM EST, GAS CONTROL RECEIVED A SEQUENCE ALARM INDICATING UNIT VALVES WERE OUT OF POSITION; THE PURGE VALVE REMAINED OPEN, RESULTING IN THE UNINTENDED RELEASE OF GAS THROUGH THE VENT VALVE. GAS CONTROL DISPATCHED A TECHNICIAN TO THE FACILITY. AT 06:28 AM EST, THE TECHNICIAN ARRIVED ON SITE, CHECKED THE COMPRESSOR AUTOMATION SYSTEM AND SENT A 'CLOSE' COMMAND TO THE PURGE VALVE AND IT CLOSED PROPERLY, STOPPING THE UNINTENDED GAS RELEASE. 1/21/2014 - UPDATE - FAULTY RELAY AND LOOSE WIRING CONTRIBUTED TO THE FAILURE OF THE VENT VALVE TO CLOSE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140131 | 16559 | 2014-12-03 12:07 | ORIGINAL FINAL | 22655 | WBI ENERGY TRANSMISSION, INC. | 1250 WEST CENTURY AVENUE | BISMARCK | ND | 58503 | 2014-11-03 13:43 | 2014 |  |  | 48.0685 | -103.6774 | 1100074 | 2014-11-03 14:36 |  | NATURAL GAS |  | 5904 | 0 | 2.5 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-11-03 14:46 | 2014-11-03 23:55 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-11-03 13:43 | 2014-11-03 13:43 | ONSHORE | ND | 58801 | WILLISTON | WILLIAMS COUNTY | SURVEY STATION NO. | 6644+98 | CABIN CREEK - WILLISTON LINE | N. MISSOURI RIVER VALVE TO S. MISSOURI RIVER VALVE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 |  | 0.25 | 52000 | UNKNOWN | LONGITUDINAL ERW - LOW FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1967 | 1967 | CARBON STEEL |  | MECHANICAL PUNCTURE | 24 | 4 | [7 empty] | CLASS 1 LOCATION | NO |  | 205 |  | NO | NO | NO |  | 0 | 0 | 589 | 651.525575570754 | 25182 | 16802.700525394 | 13156 | 14552.5814468741 | 1500 | 1659.23321452654 | 0 | 0 |  |  | 40427 | 25160.8407308516 | 33666.0407623654 | [8 empty] | 427 |  | 500 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 34729 | NO |  | YES | [5 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 1 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO | YES | STATE HIGHWAY | [9 empty] | CONTRACTOR | GRADER/SCRAPER | ROAD WORK | NO |  |  | UTILITY OWNER | NO | YES | YES | 9 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | KENT KAHL | DOT COMPLIANCE SUPERVISOR | kent.kahl@wbienergy.com | 406-359-7222 | 406-359-7244 |  |  |  | KENT KAHL | DOT COMPLIANCE SUPERVISOR | 406-359-7222 | kent.kahl@wbienergy.com | CENTRAL SPECIALTIES WAS OPERATING A D-8 DOZER PERFORMING LEVELING/GRADING WORK IN THE EXISTING HIGHWAY RIGHT-OF-WAY ADJACENT TO NORTH DAKOTA STATE HIGHWAY 85 APPROXIMATELY 5 MILES SOUTH OF WILLISTON, ND. THE D-8 STRUCK AND PUNCTURED WBI ENERGY'S (WBI) 12' STEEL, HIGH PRESSURE, NATURAL GAS TRANSMISSION LINE ON NOVEMBER 3, 2014 AT 1:43 PM CST. THIS WORK WAS BEING PERFORMED FOR THE HIGHWAY 85 RECONSTRUCTION PROJECT THAT HAS BEEN ONGOING. THE LAST LOCATE REQUEST BY CENTRAL SPECIALTIES FOR THIS AREA OF WORK WAS PUT IN ON 10/2/14 AND LOCATED ON 10/6/14 BY WBI, NTMS TICKET NO. 14179562. THE LOCATE TICKET 14179562 EXPIRED ON 10/27/14; THEREFORE THE EXCAVATION WORK BEING PERFORMED DID NOT HAVE A VALID ONE-CALL TICKET, SO WBI WAS UNAWARE OF THE CONTINUED EXCAVATION. WBI WAS ABLE TO ISOLATE THIS LINE SECTION WITH MINIMAL IMPACT TO CUSTOMERS. WBI PERSONNEL REPAIRED THE DAMAGED LINE BY REMOVING A CYLINDER OF PIPE AND WELDING IN A NEW CYLINDER OF PIPE. THE PIPELINE WAS PUT BACK INTO SERVICE AT 11:55 PM CST.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140132 | 16619 | 2014-12-03 14:38 | SUPPLEMENTAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2014-11-06 10:15 | 2014 |  |  | 31.035 | -83.2737 | 1100340 | 2014-11-06 11:08 |  | NATURAL GAS |  | 321 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-11-06 11:43 | 2014-11-07 06:25 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 10 | 2014-11-06 10:15 | 2014-11-06 11:10 | ONSHORE | GA | 31645 | RAY CITY | BERRIEN | MILEPOST | 1.95 | LINE 34 - NASHVILLE LINE | LINE 34 - NASHVILLE LINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | YES |  |  |  |  | YES | UNCASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 3.5 |  | 0.188 | 35000 | API 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | REPUBLIC | COAL TAR | [28 empty] | 1960 | 1960 | CARBON STEEL |  | MECHANICAL PUNCTURE | 2 | 1 | [7 empty] | CLASS 1 LOCATION | NO |  | 80 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 1203 | 802.702276707531 | 43837 | 48490.5376167999 | 3470 | 3838.35950293806 | 0 | 0 |  |  | 48510 | 24852.5424702377 | 53131.5993964455 | [8 empty] | 935 |  | 1078 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 12 | NO | [5 empty] | YES | TO SMALL TO ACCOMMODATE A SMART PIG | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLERS DID NOT CONTRIBUTE TO THE INCIDENT | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO | YES | COUNTY ROAD | [9 empty] | COUNTY | GRADER/SCRAPER | ROAD WORK | NO |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | YES | 20 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | ZACHARY RAGAIN | ENGINEER - PIPELINE | zachary_ragain@kindermorgan.com | 713-420-6633 |  |  |  |  | ZACHARY RAGAIN | ENGINEE - PIPELINE | 713-420-6633 | zachary_ragain@kindermorgan.com | ON NOVEMBER 6, 2014, SOUTHERN NATURAL GAS LINE 34 (NASHVILLE LINE) WAS STRUCK BY A ROAD GRADER WHERE IT CROSSES BRADFORD RD IN BERRIEN COUNTY, GA. THE ROAD GRADER WAS BEING RUN BY A BERRIEN COUNTY ROAD CREW WHO HAD FAILED TO MAKE A ONE-CALL NOTIFICATION. BRADFORD ROAD IS UNPAVED AT THIS LOCATION, AND THE PIPELINE IS UNCASED. THE ROAD GRADER MADE A 2 IN X 1 IN PUNCTURE IN THE 3 INCH PIPELINE. SNGS FIRST NOTIFICATION OF THE INCIDENT CAME AS A CALL FROM A NEARBY LANDOWNER TO GAS CONTROL AT 10:15 AM EST. GAS CONTROL IMMEDIATELY CALLED OPERATIONS. THE FIRST PERSON ARRIVED AT THE UPSTREAM TAP VALVE AT 11:10 AM EST AND HAD THE VALVE SHUT WITHIN 5 MINUTES. THERE WERE TWO ROAD GRADERS, ONE CUTTING THE DITCH AND A SECOND GRADER FOLLOWING BEHIND AND GRADING THE ROAD. THE FIRST GRADER THAT WAS CUTTING THE DITCH IS THE GRADER THAT STUCK THE PIPELINE. THERE WERE SNG PIPELINE MARKERS ON EITHER SIDE OF BRADFORD ROAD WHERE IT WAS CROSSED BY SNG LINE 34. REPORT FINALIZED ON 1/21/2015 WITH NOT ADDITIONAL UPDATES.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140133 | 16717 | 2014-12-05 11:21 | SUPPLEMENTAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 1111 LOUISIANA STREET | HOUSTON | TX | 77002 | 2014-11-14 17:17 | 2014 |  |  | 34.013 | -93.3697 | 1101082 | 2014-11-14 18:42 |  | NATURAL GAS |  | 2820 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | LOWERED & MONITORED PRESSURE TO ALLOW INSTALLATION OF A TEMPORARY REPAIR SLEEVE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-11-14 18:14 | 2014-11-14 18:14 | ONSHORE | AR | 71962 | OKLONA | CLARK | MILEPOST | 695+18 | AM-153 | AM-153 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 4 |  | 0.188 | 30000 | API 5L GRADE A | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1958 | 1958 | CARBON STEEL |  | MECHANICAL PUNCTURE | 2.2 | 1.2 | [7 empty] | CLASS 1 LOCATION | NO |  | 37 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 11280 | 7526.58493870403 | 48525 | 53676.1944899335 | 1000 | 1106.15547635103 | 9500 | 10508.4770253347 | RESTORE SERVICE TO LOST CUSTOMERS |  | 70305 | 37773.3647715558 | 72817.4119303233 | [8 empty] | 116 |  | 175 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 1 | NO | YES | [6 empty] | YES |  | YES |  |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY DAMAGE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  |  |  | YES | [6 empty] | CONTRACTOR | FARM EQUIPMENT | AGRICULTURE | NO |  |  | UNKNOWN/OTHER | NO | UNKNOWN/OTHER |  |  | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | JIMMY CROSS | DOT COMPLIANCE MANAGER | jimmy.cross@enablemidstream.com | 3184293664 | 3184293997 |  |  |  | JOHNNY CAVITT | MANAGER OF DOT COMPLIANCE PROGRAMS | 3184293606 | johnny.cavitt@enablemidstream.com | FRIDAY 11/14/2014 AT 17:17, SYSTEM CONTROL RECEIVED A CALL FROM MR. GARY GRADY REPORTING THAT A NATURAL GAS LINE HAD BEEN HIT BY A BULLDOZER AND WAS BLOWING GAS NEAR OKOLONA, ARKANSAS. SYSTEM CONTROL CONTACTED EMMET TEAM PERSONNEL TO INVESTIGATE THE CALL. EMMET TEAM PERSONNEL CONTACTED MR. GRADY TO DETERMINE THE LOCATION AND SITUATION. ADDITIONAL PERSONNEL WERE CALLED OUT TO ASSIST WITH RESPONDING TO THE LEAK. AT 18:14, EMMET TEAM PERSONNEL CONFIRMED THAT LINE AM-153 WAS LEAKING GAS. THE SITE OF THE LEAK WAS REPORTED TO BE AT GPS COORDINATES -93.36972716 W, 34.01297563 N. THE SITE OF THE LEAK WAS APPROXIMATELY 1.5 MILES WEST ALONG THE PIPELINE FROM THE OKOLONA CITY LIMITS IN SECTION 29 TOWNSHIP 8S AND RANGE 22W OF CLARK COUNTY. THE LEAK WAS LATER DETERMINED TO BE AT STATION 695+18 ON LINE AM-153. THE PIPELINE WAS MARKED WITH CARSONITE MARKERS AND BURIED APPROXIMATELY 30 INCHES DEEP AT THE LEAK SITE. ADDITIONAL SIGNS WERE ADDED ONCE REPAIR WAS MADE. MR. GRADY TOLD EMMET TEAM PERSONNEL THAT HE WAS OPERATING THE BULLDOZER SUB-CULTIVATING THE PROPERTY FOR THE LANDOWNER IN PREPARATION FOR REPLANTING OF TREES. HE STATED THAT HE HAD NOT NOTIFIED 811 ARKANSAS ONE CALL PRIOR TO STARTING HIS WORK. ARKANSAS ONE CALL PERSONNEL CONFIRMED THAT NO REQUEST TO LOCATE UNDERGROUND UTILITIES WAS RECEIVED WHEN THEY SEARCHED THEIR RECORDS FOR THE HARETOWN ROAD AREA IN CLARK COUNTY. BECAUSE THE LOCAL TEMPERATURE WAS IN THE HIGH 30S AND EXPECTED TO DROP DURING THE NIGHT INTO THE 20S, A PLAN WAS DEVELOPED TO TEMPORARILY STOP THE LEAK AND MAKE PERMANENT REPAIRS DURING THE NEXT DAY. ADDITIONAL PERSONNEL WERE CALLED OUT TO MONITOR LINE PRESSURES AT THE AM-153 TAKE-OFF FROM LINE S NEAR GURDON AND THE END OF AM-153 NEAR DELIGHT. EQUIPMENT AND A TEMPORARY REPAIR SLEEVE WERE BROUGHT FROM THE EMMET OFFICE. AN EMERGENCY EXCAVATION NOTICE WAS GIVEN TO ARKANSAS ONE CALL ABOUT THE IMPENDING EXCAVATION NEAR THE LINE AM-153 LEAK, TICKET # AR14114-0908. THE INSTALLATION OF THE STYLE 96 BOLT-ON REPAIR SLEEVE OVER THE LEAKING PIPE WAS STARTED. AT 00:15 ON SATURDAY 11/15/2014, EMMET TEAM PERSONNEL COMPLETED THE INSTALLATION AND NOTIFIED SYSTEM CONTROL THAT THE LEAK WAS STOPPED. THE LINE PRESSURE AT DELIGHT WAS OBSERVED TO BE APPROXIMATELY 1 PSIG. SYSTEM CONTROL PROVIDED LOCAL, STATE AND FEDERAL AGENCIES WITH UPDATED STATUS REPORTS ABOUT THE AM-153 LEAK. DURING THE INSTALLATION OF THE TEMPORARY LEAK REPAIR, LOCAL DISTRIBUTION COMPANY EXPERIENCED THE LOSS OF NATURAL GAS SERVICE TO 5 OR 6 HOMES. DISTRIBUTION PERSONNEL CLOSED OFF THE DELIGHT DISTRIBUTION SYSTEM AT THE TOWN BORDER STATION DUE TO A CONCERN ABOUT THE POSSIBILITY OF PILOT LIGHTS EXTINGUISHING AND OF ESCAPING GAS. NATURAL GAS DISTRIBUTION SERVICE WAS STOPPED TO APPROXIMATELY 200 CUSTOMERS. AFTER SUNRISE ON 11/15/2014, A CONTRACTOR WAS MOBILIZED. REPAIR MATERIALS INCLUDING PRE-TESTED PIPE, FITTINGS AND STOPPLES WERE BROUGHT TO THE LEAK SITE. SYSTEM CONTROL WAS NOTIFIED OF THE REPAIR WORK THAT WOULD OCCUR. EXCAVATION FOR THE REPAIR INSTALLATION BEGAN AT 09:49. TWO STOPPLES AND A BY-PASS PIPE WERE INSTALLED TO REPLACE THE DAMAGE SECTION OF PIPE. WELDS WERE CHECKED. THE NEW PIPING WAS SUCCESSFULLY LEAK TESTED FROM 13:30 TO 14:00. THE STOPPLES WERE TAPPED TO ALLOW GAS TO FLOW AROUND THE DAMAGED SECTION OF PIPE. THE DAMAGED SECTION OF PIPE WAS REMOVED AND REPLACED WITH WELD CAPS. AT 19:18 ON 11/15/2014, SYSTEM CONTROL WAS NOTIFIED THAT THE PERMANENT REPAIRS WERE COMPLETED. DURING THE INSTALLATION OF THE PERMANENT LEAK REPAIR, THE TOWN BORDER STATION AT DELIGHT WAS REOPENED TO PROVIDE NATURAL GAS TO THE DELIGHT DISTRIBUTION SYSTEM. SGO ASSEMBLED APPROXIMATELY 20 TECHNICIANS TO RELIGHT PILOTS AND RESTORE NATURAL GAS SERVICE TO CUSTOMERS IN DELIGHT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140134 | 16866 | 2014-12-11 08:08 | SUPPLEMENTAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 1111 LOUISIANA STREET | HOUSTON | TX | 77002 | 2014-11-24 16:35 | 2014 |  |  | 34.6958 | -93.1269 | 1101914 | 2014-11-24 20:18 |  | NATURAL GAS |  | 3043 | 15732 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-11-24 23:20 | 2014-12-07 17:05 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-11-24 19:31 | 2014-11-24 19:31 | ONSHORE | AR | 71949 | JESSIEVILLE | GARLAND | MILEPOST | 3762+30 | BT-1-AN | BT-1-AN | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 96 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 |  | 0.281 | 60000 | API 5LX | DSAW |  | US STEEL | ASPHALT | [28 empty] | 1967 | 1967 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 2 LOCATION | NO |  | 523 |  | NO | NO | NO |  | 0 | 0 | 54276 | 60037.6946344283 | 10498 | 7004.79509632224 | 205641 | 227470.918312301 | 4950 | 5475.46960793758 | 2500 | 2765.38869087756 | FREIGHT LAB COSTS FOR METALLUGIC REVIEW |  | 277865 | 143019.000335383 | 302754.266341867 | [8 empty] | 935 |  | 1000 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 68977 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LAND OWNER STATED WHEN HE REPORTED THE LEAK THAT HE SEES FOAM, SMELLS GAS AND HEARS A HISSING NOISE COMING FROM THE GROUND THAT HAS BEEN GOING ON FOR THREE OR FOUR DAYS. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED |  | YES | [15 empty] | OTHER | EXTERNAL FORCE |  |  |  |  | YES | [63 empty] | YES | YES | [6 empty] | 2013 | [55 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | JIMMY CROSS | DOT COMPLIANCE MANAGER | jimmy.cross@enablemidstream.com | 3184293664 | 3184293997 |  |  |  | JOHNNY CAVITT | MANAGER OF DOT COMPLIANCE PROGRAMS | 3184293606 | johnny.cavitt@enablemidstream.com | 1635 - THIRD PARTY CALLED AND REPORTED A GAS LEAK NEAR HIS HOUSE AT 314 HARDING LANE IN JESSIEVILLE, AR. REPORTS THAT HE CAN SEE FOAM, SMELL GAS, AND HEAR A HISSING NOISE COMING FROM AN UNDERGROUND LINE. HE STATES THAT THIS HAS BEEN GOING ON FOR 3-4 DAYS. 1643 - SYSTEM CONTROL NOTIFIED MARK ATKINSON (MALVERN TEAM) AND RELAYED ALL INFORMATION. MARK REPORTS THAT IT WILL TAKE HIM APPROXIMATELY 2 HOURS TO GET ON-SITE AND NOTIFIED HIM THAT BT-1 AND BT-1-AN ARE CLOSE TO THE REPORTED LEAK. STATES THAT THIS MAY BE LOCAL DISTRIBUTION COMPANY LEAK. 1648 - SYSTEM CONTROL NOTIFIED LOCAL DISTRIBUTION COMPANY AND RELAYED INFORMATION. 1931 - TECHNICIAN REPORTS THAT THEY HAVE FOUND A TRANSMISSION LEAK ON EITHER BT-1 OR BT-1-AN. HE STATES THAT HE IS IN TOUCH WITH THE OPERATION MANAGER AND ARE TRYING TO GET A GAME PLAN IN ACTION ON GETTING THE LEAK DUG UP AND REPAIRED. 2005 - SYSTEM CONTROL MADE REPORT TO ARKANSAS SERC (#16826). 2010 - SYSTEM CONTROL NOTIFIED THE GARLAND COUNTY DISPATCH OFFICE AND MADE A REPORT. HE REQUESTED THAT WE NOTIFY THE JESSIEVILLE FIRE DEPARTMENT DISPATCH OFFICE AS WELL. 2015 - SYSTEM CONTROL NOTIFIED THE JESSIEVILLE FIRE DEPARTMENT DISPATCH OFFICE. 2018 - SYSTEM CONTROL MADE REPORT TO THE NRC (#1101914). 2100 - SYSTEM CONTROL SPOKE WITH FIELD PERSONNEL; HE STATES THAT THEY ARE GOING TO ISOLATE BT-1-AN AND WATCH FOR PRESSURE DROPS TO SEE IF IT IS THE LEAKING LINE. THEY ARE GOING TO VALVE OFF THE MAINLINE VALVES ON GM-232 AND GM-233 ON THE 24 INCH(BT-1-AN). 2320 - OPERATION MANAGER CALLED AND REPORTED THAT THEY HAVE CONFIRMED THAT BT-1-AN IS THE LEAKING LINE. THEY HAVE WORKED THIS PLAN FOR THE BLOW-DOWN. ESTIMATES APPROXIMATELY 4-5 HOURS FOR THE BLOWDOWN TO BE COMPLETE; GOAL IS TO GET TO 0# ON THE LINE, BUT WILL ACCEPT PRESSURES UNDER 50#. APPROXIMATE GAS RELEASED DURING BLOWDOWN WILL BE 15,732.2 MCF. LINE BACK IN SERVICE DECEMBER 7TH AT 17:05. UPDATE APRIL 10, 2015 - PIPE WAS SENT TO LAB FOR METALLUGIC REVIEW, COMPLETED REPORT RECEIVED APRIL 2, 2015. STRESS ENGINEERING'S TEST RESULTS ARE AS FOLLOWS: VISUAL, METALLOGRAPHIC, AND FRACTOGRAPHIC EXAMINATION OF THE SAMPLE INDICATED THAT CRACKS INITIATED ON THE OUTSIDE SURFACE OF THE PIPE. THE MORPHOLOGY OF THE CRACKS INCLUDED CLOSELY-SPACED CRACKS IN COLONIES, TRANSGRANULAR AND BRANCHED GROWTH PATH, CRESCENT-SHAPED CRACKS PARTIALLY COVERED WITH MAGNETITE, AND ENLARGEMENT OF THE CRACKS AT THE OUTSIDE SURFACE DUE TO CORROSION. THESE FEATURES SUPPORT THE CONCLUSION THAT THIS LEAK WAS THE RESULT OF NEAR-NEUTRAL PH STRESS CORROSION CRACKING (SCC). THESE CRACKS WERE ALIGNED PERPENDICULAR TO THE LONGITUDINAL AXIS OF THE PIPE AT THE EXTRADOS OF AN OVER-BEND AND WERE CREATED BY BENDING LOADS IN THE PIPELINE. THE FACT THAT THE FINAL FAILURE WAS DUE TO DUCTILE OVERLOAD ALSO SUPPORTS THE ASSERTION THAT THE LONGITUDINAL STRESSES WERE SIGNIFICANT AT THIS LOCATION. FURTHER, THE UPWARD MOVEMENT OF THE PIPE AFTER IT WAS CUT IN THE DITCH DURING EXCAVATION IS CONFORMATION OF THIS CONCLUSION. STRESS ENGINEERING DID NOT OBSERVE ANY MATERIAL FLAWS OR DEFECTS IN THE SAMPLE MATERIAL. THE MICROSTRUCTURE OF THE SAMPLE IS TYPICAL FOR A CARBON-STEEL PIPE MATERIAL. THE PROPERTIES OF THE MATERIAL ARE CONSISTENT WITH THE REQUIREMENTS OF API 5LX (1968) FOR GRADE X60 AND ARE NOT BELIEVED TO HAVE CONTRIBUTED TO THE FAILURE. 9/23/2015 ADDITIONAL ANALYSIS WAS CONDUCTED ON THE ILI DATA TO LOOK FOR SIMILAR CONDITIONS IN THE LINE SEGMENT AND THESE AREAS WERE OVERLAID WITH CIS DATA. THREE (3) LOCATIONS WERE SELECTED TO INVESTIGATE, THEY WILL DUG PRIOR TO THE END OF OCTOBER.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140135 | 16676 | 2014-12-12 15:53 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION LP (SPECTRA ENERGY CORP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2014-11-17 07:30 | 2014 |  |  | 28.5532 | -92.7933 | 1101220 | 2014-11-17 07:45 |  | NATURAL GAS |  | 223 | 26800 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-11-17 08:47 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 35 | 2014-11-17 07:30 | 2014-11-17 09:05 | OFFSHORE | [28 empty] | 200 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EAST CAMERON | 321 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 |  | 0.375 | 52000 | API-5L X52 | SEAMLESS |  | U.S. STEEL | OTHER | CONCRETE AND SOMASTIC | [27 empty] | 1975 | 1975 | CARBON STEEL |  | OTHER | [8 empty] | LINE SEVERED BY BARGE ANCHOR | CLASS 1 LOCATION | NO |  | 419 |  | NO | NO | NO |  | 0 | 0 | 92460 | 102275.135343416 | 836 | 557.821366024518 | 2000000 | 2212310.95270205 | 0 | 0 | 0 | 0 |  |  | 2093296 | 1063034.40774782 | 2315143.90941149 | [8 empty] | 680 |  | 1440 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 306398 | NO |  |  |  | YES |  |  |  | YES |  | YES |  |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | THIRD PARTY PLATFORM OPERATOR OBSERVATION |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INFORMATION ABOUT THE EVENT WAS RECEIVED IMMEDIATELY UPON OCCURRENCE BY THE NEARBY PLATFORM OPERATOR. TEXAS EASTERN PIPELINE WAS THE ONLY PIPELINE IN THE VICINITY. CONTROLLER ACTIONS WOULD NOT HAVE IMPACTED THE COMPANY RESPONSE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ROUTINE OR NORMAL FISHING OR OTHER MARITIME ACTIVITY NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | FISHING OR MARITIME ACTIVITY | [103 empty] | ROUTINE OR NORMAL FISHING OR OTHER MARITIME ACTIVITY NOT ENGAGED IN EXCAVATION | [261 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | deteschendorf@spectraenergy.com | 713-627-5573 | 713-386-4468 |  |  |  | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 713-627-5008 | nyatanu@spectraenergy.com | ON THE MORNING OF NOVEMBER 17, 2014, A LARGE BARGE WAS BEING PUSHED BY A TUG IN 15 FOOT SEAS WHEN THE TUG LOST POWER. THE TUG COULD NOT REGAIN POWER IN A TIMELY MANNER. AN ANCHOR WAS DROPPED WHICH SNAGGED TEXAS EASTERN TRANSMISSION LP'S 16-INCH LINE 41-A-5 NATURAL GAS TRANSMISSION PIPELINE IN EAST CAMERON BLOCK 321. THE ANCHOR COMPLETELY SEVERED THE PIPELINE CAUSING A SUBSTANTIAL RELEASE OF NATURAL GAS.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20140136 | 16771 | 2014-12-15 15:26 | SUPPLEMENTAL FINAL | 30940 | WILLIAMS ENERGY, LLC | ONE WILLIAMS CENTER P.O. BOX 645 | TULSA | OK | 74172 | 2014-12-03 15:00 | 2014 |  |  | 28.3614 | -90.1975 | 1102545 | 2014-12-03 15:14 |  | NATURAL GAS |  | 11000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | ABLE TO ISOLATE THE BYPASS | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-12-03 15:00 | 2014-12-03 15:00 | OFFSHORE | [28 empty] | 220 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SOUTH TIMBALIER | 231 | BELOW WATER, PIPE ON OR ABOVE SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | DRAIN LINES | [38 empty] | 1997 |  | CARBON STEEL |  | LEAK |  |  | OTHER | BROKEN PIPING ON BYPASS VALVE | [5 empty] | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 42500 | 28358.1436077058 | 2733406 | 3023572.01599075 | 0 | 0 | 0 | 0 |  |  | 2775906 | 1417299.51296007 | 3051930.15959846 | [8 empty] | 700 |  | 1850 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL |  | YES | [7 empty] | YES |  |  |  |  | YES | SUB-SEA CONNECTION | OFFSHORE GATHERING | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTRACTOR BROKE VALVE ASSEMBLY WHILE SETTING MATS. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [103 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [261 empty] | SHANE FRASIER | PIPELINE SAFETY ENGINEER | shane.frasier@williams.com | 713-215-3051 |  |  |  |  | SHANE FRASIER | PIPELINE SAFETY ENGINEER | 713-215-3051 | shane.frasier@williams.com | A DIVE COMPANY WAS SETTING MATS TO COVER AND PROTECT A NEWLY INSTALLED VALVE ASSEMBLY ON THE DISCOVERY 18 INCH PIPELINE AT A DEPTH OF 230 FEET. AN UNEXPECTED CURRENT CAUSED THE MAT TO CATCH ON THE 2 INCH BY-PASS LINE WHICH DAMAGED THE PIPING AND CAUSED THE RELEASE. THE LINE WAS QUICKLY ISOLATED AND REPAIRED. THE DIVER WAS NOT INJURED AND THERE WAS NO OTHER DAMAGE AS A RESULT OF THIS INCIDENT. THERE WAS NO SHEEN REPORTED ON THE WATER. ADDITIONAL NRC NOTIFICATION WAS MADE BY WILLIAMS AT THE SAME TIME WITT O'BRIEN'S WAS MAKING NOTIFICATION. WILLIAMS NUMBER IS 1102550.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140137 | 17594 | 2014-12-15 18:09 | SUPPLEMENTAL FINAL | 2620 | COLUMBIA GULF TRANSMISSION, LLC | 700 LOUISIANA ST. SUITE 700 | HOUSTON | TX | 77002 | 2014-11-17 08:45 | 2014 |  |  | 29.5628 | -90.5551 | 1101230 | 2014-11-17 09:42 |  | NATURAL GAS |  | 153 | 246 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | LINE PRESSURE WAS REDUCED DOWN TO 125 PSIG TO MONITOR BUBBLES | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-11-17 07:45 | 2014-11-17 08:00 | ONSHORE | LA | 70343 | BOURG | LAFROUCHE PARRISH | SURVEY STATION NO. | EL-100-013 | PIPELINE | EL-100 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | IN A NAVIGABLE WATERWAY | 48 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 |  | 0.245 | 35000 | API-5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | NATIONAL TUBE | COAL TAR | [28 empty] | 1954 | 1954 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 275 |  | NO | NO | NO |  | 0 | 0 | 900 | 995.539928715923 | 560 | 373.660245183888 | 793505 | 877739.901261921 | 0 | 0 | 0 | 0 |  |  | 794965 | 403750.145094492 | 879109.101435821 | [8 empty] | 812 |  | 1110 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 5700 | NO |  | YES | [5 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS FROM A PINHOLE THAT WAS IDENTIFIED BY A BOAT PASSING BY THAT AREA | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY BOATS, BARGES, DRILLING RIGS, OR OTHER MARITIME EQUIPMENT OR VESSELS SET ADRIFT OR WHICH HAVE OTHERWISE LOST THEIR MOORING | OTHER OUTSIDE FORCE DAMAGE | MARITIME EQUIPMENT OR VESSEL ADRIFT | [103 empty] | DAMAGE BY BOATS, BARGES, DRILLING RIGS, OR OTHER MARITIME EQUIPMENT OR VESSELS SET ADRIFT OR WHICH HAVE OTHERWISE LOST THEIR MOORING | [5 empty] | YES | IT WAS DETERMINED THE PIPELINE HAD BEEN DAMAGED BY AN ANCHOR BEING DROPPED AND DRAGGED ACROSS THE PIPELINE. THE THIRD PARTY DAMAGE CONSISTED OF TWO DENTS AND ONE GOUGE AREA. THE GOUGE AREA HAD A PINHOLE LEAK. | [254 empty] | CODY BOWERS | COMPLIANCE SPECIALIST | cody_bowers@transcanada.com | (304)357-2814 |  |  |  |  | LEE ROMACK | MANAGER US REGULATORY COMPLIANCE | (832)320-5315 | lee_romack@transcanada.com | ON NOVEMBER 16, 2014, A TUG BOAT TRAVELING ALONG THE INTRACOASTAL CANAL IN BOURG, LA SPOTTED BUBBLES. THE CREW OF THIS BOAT CONTACTED THE COAST GUARD, WHO IN TURN CONTACTED COLUMBIA GULF TRANSMISSION, LLC (COLUMBIA) TO INVESTIGATE IF THE SUBJECT BUBBLES WERE EMANATING FROM A NEAR-BY LINE THAT RUNS IN THIS AREA. COLUMBIA OPERATIONS PERSONNEL WERE DISPATCHED TO INVESTIGATE THIS REPORTED LEAK. AFTER CLOSING THE TWO MAINLINE VALVES THAT ARE WITHIN THE UPSTREAM AND DOWNSTREAM SEGMENT OF THE LINE, BUBBLES KEPT SURFACING. SAMPLES OF THE RELEASED MATERIAL WERE COLLECTED AND SENT TO THE LABORATORY FOR ANALYSIS. THE LINE PRESSURE WAS RESTRICTED TO ABOUT 125 PSIG TO ENSURE THAT THE RELEASED BUBBLES WERE IDENTIFIABLE FOR REPAIRS, IF THE LINE TURNS OUT TO BE COLUMBIA'S. THEREAFTER, THE AREA WAS MADE SAFE WHERE PIPELINE OPERATIONS PERSONNEL MANNED THE TWO MAINLINE VALVES OVERNIGHT, MONITORING LINE PRESSURE VIA DIGITAL PRESSURE GAUGES. THE FOLLOWING DAY (NOVEMBER 17, 2014), THE LINE RELEASING BUBBLES WAS DECLARED AS COLUMBIA OWNED, OPERATED AND MAINTAINED LINE. THEN A REPORT TO THE NRC WAS MADE ON THAT MORNING DUE TO THE EXPECTED REPAIR COSTS THAT WILL EXCEED $50,000. THE UNINTENDED RELEASE OF MATERIAL DID NOT EXCEED 3,000 MCF. NO EVIDENCE OF SHEEN WAS NOTED THROUGHOUT THE ENTIRE RELEASE FOR MATERIAL ON THE SURFACE OF THE WATERWAY. AFTER THE CAUSE ANALYSIS WAS CONDUCTED, IT WAS DETERMINED THE PIPELINE HAD BEEN DAMAGED BY AN ANCHOR BEING DROPPED AND DRAGGED ACROSS THE PIPELINE. THE THIRD PARTY DAMAGE CONSISTED OF TWO DENTS AND ONE GOUGE AREA. THE GOUGE AREA HAD A PINHOLE LEAK. THE DAMAGE TO THE PIPELINE HAS BEEN REPAIRED BUT HAS NOT BEEN RETURNED TO SERVICE SINCE THE DATE OF THE INCIDENT.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20140138 | 16579 | 2014-12-17 11:49 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2014-11-24 12:45 | 2014 |  |  | 29.1857 | 91.1733 | 1101890 | 2014-11-24 14:05 |  | NATURAL GAS |  | 50 | 3598 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-11-24 15:45 | 2014-11-30 15:20 |  |  |  |  | NO |  |  |  |  | NO | [7 empty] | 2014-11-24 12:45 | 2014-11-24 12:45 | OFFSHORE | [28 empty] | 9 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SHIP SHOAL | 7 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 |  | 0.312 | 52000 | API 5L | FLASH WELDED |  | A.O SMITH | OTHER | ASPHALT WITH 3" CONCRETE OVERLAYED. | [27 empty] | 1959 | 1959 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 418 |  | NO | NO | NO |  | 0 | 0 | 13150 | 14545.944514016 | 10 | 6.67250437828371 | 275000 | 304192.755996532 | 5000 | 5530.77738175513 | 5000 | 5530.77738175513 | LABOR |  | 298160 | 151393.937243222 | 329806.927778437 | [8 empty] | 740 |  | 1440 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 58450 | NO | [5 empty] | YES | LAUNCHING AND RECEIVING PIG TRAPS ARE NOT DESIGNED TO HANDLE A SMART PIG. | YES |  |  | YES |  | YES | LOW PRESSURE UNPROCESSED GAS. | OFFSHORE GATHERING | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE SMALL SIZE OF THE LEAK WITH MINIMAL PRESSURE LOSS GENERATED FROM THE LEAK WAS UNDETECTABLE BY THIS METHOD. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN | [5 empty] | YES | THIS PIPELINE HAS BEEN IN UNPROCESSED AND UNDEHYDRATED SERVICE SINCE 1990. THIS LINE HAS BEEN TREATED SINCE 1990 WITH CORROSION INHIBITORS & BIOCIDES. SAMPLES ARE COLLECTED & RESIDUALS ARE MONITORED MONTHLY, INCLUDING FIELD TECHS MONITORING OF CHEMICAL QUANTITIES AND CHEMICAL INJECTION PUMP OPERATIONS ON A MONTHLY BASIS. |  |  | YES | UT READINGS TAKEN BY DIVERS INDICATED NO EXTERNAL CORROSION AND/OR DAMAGE. THESE RESULTS CONCLUDED THE LEAK CAUSE TO BE AN INTERNAL ISOLATED PINHOLE. | YES |  |  |  | YES | THE LOCATION OF THE PINHOLE LEAK WAS ON THE 7 O'CLOCK POSTION. | YES | NO | YES | YES | [168 empty] | NO | [63 empty] | NO | [16 empty] | NO | [63 empty] | JOHNNY LOPEZ | REGULATORY COMPLIANCE SPECIALIST | johnny.lopez@williams.com | 7132152995 | 7132152222 |  |  |  | MARIE SOTAK | MANAGER SAFETY REGULATORY COMPLIANCE | 7132152111 | marie.sotak@williams.com | 11-24-2014 TRANSCONTINENTAL'S (TRANSCO) SCHRIEVER OPERATIONS DISTRICT WAS CONTACTED BY COAST GUARD REGARDING BUBBLES THAT HAD BEEN SITED IN THE VICINTY OF TRANSCO'S FACILITIES (AREA/BLOCK SS 7). THE COORDINATES THAT WERE RECIEVED FROM THE COAST GUARD WERE PLOTTED BY THE SCHRIEVER OPERATIONS TEAM. TRANSCO'S 16" & 20" GAS GATHERING PIPELINES NEAR THE SUSPECT LEAK LOCATION WERE ISOLATED AND BLOWN DOWN. TRANSCO'S SUPPORT ENGINEER BEGINS THE PROCESS OF CONTACTING CONTRACTOR DIVE TEAMS AND EQUIPMENT TO INVESTIGATE AND REPAIR THE LEAK. ONCE THE BLOW DOWN OF THE LINES WAS COMPLETE THE 16" LINE WAS IDENTIFIED AS THE LEAKING LINE. 11-28-2014 THE DIVE TEAM BEGINS CLEANING THE LINE AND INITIATES THE INVESTIGATION. A UT READING OF THE LEAKING LINE IS PERFORMED BY THE DIVE TEAM. A REPAIR CLAMP HAS BEEN INSTALLED ON THE LEAK 11-30-2014. THE LINE IS REPRESSURED AND BACK IN FULL SERVICE 12-1-2014. THE RESULTS OF THE INVESTIGATION "SHOWN BELOW" DETERMINED THE MOST PROBABLE CAUSE OF THE LEAK ON THE 16" GAS GATHERING PIPELINE WAS DUE TO INTERNAL CORROSION. THE LOCATION OF THE LEAK ON THE PIPE WAS AT THE 7 O'CLOCK POSITION. THE UT INSPECTION RESULTS SHOWED NO EXTERNAL CORROSION OR DAMAGE ON THE PIPELINE. A LOW FLOW UNPROCESSED & UNDEHYDRATED GAS IS TRANSPORTED THROUGH THE PIPELINE SINCE 1990. TRANSCO DOES REVIEW EVERY INTERNAL CORROSION LEAK AND FOLLOWS IT'S POCEDURES TO PREVENT AND MITIGATE THESE TYPES OF ENVIROMENT. - THIS LINE HAS BEEN TRANSPORTING UNPROCESSED AND UNDEHYDRATED GAS SINCE 1990 AND HAS BEEN TREATED SINCE 1990 WITH CORROSION INHIBITORS & BIOCIDES. - SAMPLES ARE COLLECTED & RESIDUALS ARE MONITORED MONTHLY. - FIELD TECHS MONITOR THE CHEMICAL QUANTITIES AND CHEMICAL INJECTION PUMP OPERATIONS ON A MONTHLY BASIS. - TRANSCO'S CORROSION ENGINEERS AND SMES REVIEW EVERY INTERNAL CORROSION LEAK THAT OCCUR ON THIER SYSTEMS AND MAKE RECCOMENDATIONS AS NEEDED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140139 | 17375 | 2014-12-17 14:29 | SUPPLEMENTAL FINAL | 2620 | COLUMBIA GULF TRANSMISSION, LLC | 700 LOUISIANA ST. SUITE 700 | HOUSTON | TX | 77002 | 2014-11-19 01:05 | 2014 |  |  | 37.31 | -85.0611 | 1101420 | 2014-11-19 04:11 |  | NATURAL GAS |  | 19637 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | BECAUSE THE STATION EMERGENCY SHUTDOWN SYSTEM WAS ACTIVATED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-11-19 01:05 | 2014-11-19 01:46 | ONSHORE | KY | 42539 | LIBERTY | CASEY | MILEPOST | SHAFER ACT | CLEMENTSVILLE COMPRESSOR STATION | 2SH-1DBD | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2013 |  | CARBON STEEL |  | OTHER | [8 empty] | BLOW-OFF VALVE RELEASE | CLASS 1 LOCATION | NO |  | 169 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 71871 | 47955.9562171629 | 500 | 553.077738175513 | 0 | 0 | 0 | 0 |  |  | 72371 | 49971.9946137958 | 48509.0339553384 | [8 empty] | 660 |  | 935 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE REASON BEHIND THE FAILED BLOW-OFF VALVE AND THE CONTROLLER WAS ABLE TO IDENTIFY THE EVENT THROUGH SCADA | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | OTHER | SOLENOID VALVE HAD A SPRING THAT WAS NOT SEATED | [20 empty] | YES | IMPROPERLY SEATED SPRING | [161 empty] | CODY BOWERS | SPECIALIST | cody_bowers@transcanada.com | (304) 357-2814 |  |  |  |  | LEE ROMACK | MANAGER | (832) 320-5315 | lee_romack@transcanada.com | ON NOVEMBER 19TH, 2014, A COLUMBIA GULF TRANSMISSION, LLC (COLUMBIA) COMPRESSOR STATION (CS) WAS SUBJECT TO AN UNINTENDED LOSS OF NATURAL GAS (MATERIAL) THROUGH AN 8-IN BLOW-OFF VALVE. THIS EVENT OCCURRED AT THE COLUMBIA CLEMENTSVILLE CS LOCATED IN CASEY COUNTY, NEAR THE TOWN OF LIBERTY, KY. THE EVENT THAT LED TO AN UNINTENDED RELEASE OF MATERIAL EXCEEDING 3,000 MCF WAS REPORTED TO THE NATIONAL RESPONSE CENTER ACCORDINGLY. ONCE THE ROOT CAUSE ANALYSIS INVESTIGATION HAD BEEN PERFORMED, IT WAS DETERMINED THAT THE BLOW-OFF VALVE FAILED TO CLOSE WHEN COMMANDED DUE TO AN UNDETECTED OPEN CIRCUIT IN THE SOLENOID COIL. ELEVATED RESISTIVITY WAS MEASURED ON THE SOLENOID COIL WIRING AND MOISTURE WAS DETECTED IN ITS ENCLOSURE. MOISTURE WAS REMOVED, RETESTED WHERE IT DISPLAYED NORMAL RESISTIVITY LEVELS. COVER PLATE WAS INSTALLED WITH PROPER SEALANT TO AVOID MOISTURE FROM ACCUMULATING INSIDE THE SOLENOID COIL WIRING ENCLOSURE. THEREAFTER, A FULL SYSTEM CHECK WAS PERFORMED BEFORE RETURNING THE CS BACK INTO SERVICE.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20140140 | 16580 | 2014-12-17 14:42 | ORIGINAL FINAL | 31836 | LEGACY RESOURCES CO LP | 1423 W. CAUSEWAY APPROACH | MANDEVILLE | LA | 70471 | 2014-12-09 01:00 | 2014 |  |  | 30.2869 | 88.0682 | 1102980 | 2014-12-09 09:12 |  | NATURAL GAS |  | 73.5 |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-12-09 17:53 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-12-09 08:47 | 2014-12-09 16:30 | OFFSHORE | [28 empty] | 13 | IN STATE WATERS | AL | MOBILE BAY | BLOCK 76 | MOBILE |  |  |  | PLATFORM | INTRASTATE | OFFSHORE PLATFORM, INCLUDING PLATFORM-MOUNTED EQUIPMENT AND PIPING | OTHER | [37 empty] | WELLHEAD | 2003 |  | CARBON STEEL |  | OTHER | [8 empty] | ACTUATOR & STEM SHEARED OFF | CLASS 1 LOCATION | NO |  | 96 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 296 | 197.506129597198 | 400000 | 442462.19054041 | 200000 | 221231.095270205 | 0 | 0 |  |  | 600296 | 304857.494523455 | 663890.791940213 | [8 empty] | 580 |  | 5000 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | OFFSHORE GATHERING | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | INVESTIGATION IS COMPLETE, IT IS BELIEVED THAT A UNKNOWN VESSEL RAN OVER WELL & PLATFORM | [147 empty] | JEREMY DUGAS | PLANS AND WATER QUALITY MANAGER | jdugas@hlpengineering.com | 337-839-1075 |  |  |  |  | TOM FARMER | PRODUCTION MANAGER | 337-237-4761 | tomfarmer@legacyresourcesco.com | AN UNKNOWN VESSEL RAN OVER THE STRUCTURAL PLATFORM AND WELL. THE ACTUATOR AND STEM ON THE UPPERMASTER TREE VALVE WAS SHEARED OFF AND COULD NOT CLOSE. GAS WAS BUBBLING OUT OF THE UPPERMASTER. DIVERS WERE DISPATCHED AND FOUND THAT THE STEM OF THE MANUAL LOWER MASTER VALVE WAS ALSO BENT BY THE UNKNOWN VESSEL. DIVERS WERE ABLE TO RELIEVE CONTROL PRESSURE TO THE SCSSV AND IT CLOSED, STOPPING THE LEAK. DIVERS REMOVED ALL VALVES ABOVE LOWER MASTER VALVEAND INSTALLED A NEW VALVE AND CLOSED IT. THE WELL HAS BEEN PLUGGED AND ABANDONED, THE STUCTURE IS BEING CLEARED AND FLOWLINES ABANDONED. NO SUPPLEMENTAL REPORT WILL BE FILED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140141 | 17247 | 2014-12-17 15:23 | SUPPLEMENTAL FINAL | 2620 | COLUMBIA GULF TRANSMISSION, LLC | 700 LOUISIANA ST. SUITE 700 | HOUSTON | TX | 77002 | 2014-11-28 03:22 | 2014 |  |  | 37.31 | -85.0611 | 1102136 | 2014-11-28 05:39 |  | NATURAL GAS |  | 16431 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE FACILITY WAS RESTARTED AFTER IDENITIFYING AND CORRECTING THE PLC ERROR. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-11-28 03:22 | 2014-11-28 03:49 | ONSHORE | KY | 42539 | LIBERTY | CASEY COUNTY | MILEPOST | SHAFER ACT | CLEMENTSVILLE COMPRESSOR STATION | 2SH-1DBD | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2013 |  | CARBON STEEL |  | OTHER | [8 empty] | PROGRAMMABLE LOGIC CONTROLLER SETTING | CLASS 1 LOCATION | NO |  | 238 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 60138 | 40127.1068301226 | 0 | 0 | 0 | 0 | 0 | 0 | NO OTHER COSTS WERE NOTED |  | 60138 | 41601.5936952715 | 40127.1068301226 | [8 empty] | 660 |  | 935 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER DID PERFORM AS HE WAS TRAINED AND QUALIFIED TO DO SO AND RESPONDED ACCORDINGLY. HE HAD NO INTERACTION WITH ANY VALVE COMMANDS BEFORE THE ALARMS WERE NOTED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | OTHER | 8-IN BLOW-OFF VALVE | [20 empty] | YES | INTERNAL SPRING WAS OUT OF POSITION | [161 empty] | GEORGE HAMATY | ENGINEER | george_hamaty@transcanada.com | (304) 357-3728 |  |  |  |  | LEE ROMACK | MANGER US REGULATORY COMPLIANCE | (832)320-5315 | lee_romack@transcanada.com | AN 8-IN BLOW-OFF VALVE FAILED TO CLOSE AFTER INADVERTENTLY RELEASING FOR THE SECOND TIME MATERIAL INTO ATMOSPHERE. THE EMERGENCY SHUTDOWN WAS NOT ACTIVATED. IT WAS IDENTIFIED THAT THIS VALVE FAILED TO CLOSE DUE TO A SOLENOID VALVE HAD A SPRING THAT WAS IMPROPERLY SEATED. A ROOT CAUSE ANALYSIS INVESTIGATION IDENTIFIED THAT THE VALVE FAILED TO CLOSE THUS ALLOWING THE MATERIAL TO FLOW THROUGH THE VALVE UNTIL IT WAS CONTROLLED BY COMPRESSOR STATION PERSONNEL. A CHANGE TO THE PROGRAMMABLE LOGIC CONTROL SETTINGS WAS COMPLETED, TESTED THE SYSTEM AND THEN RETURNED INTO SERVICE. THE FACILITY WAS MONITORED TO ENSURE THAT THE SAME ERROR WILL NOT BE REGENERATED. NO FURTHER ISSUES WERE NOTED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140142 | 16583 | 2014-12-17 18:45 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2014-11-19 21:02 | 2014 |  |  | 35.1694 | -119.1797 | 1101516 | 2014-11-19 23:50 |  | NATURAL GAS |  | 36589 | 140 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-11-19 22:41 | 2014-11-21 00:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-11-19 21:02 | 2014-11-19 21:29 | ONSHORE | CA | 93311 | BAKERSFIELD | KERN | MILEPOST | 0.78 | 203 | NA | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10.75 |  | 0.25 | 35000 | GRADE B | SEAMLESS |  | YOUNGSTOWN STEEL PRODUCTS CO. | COAL TAR | [28 empty] | 1955 | 1955 | CARBON STEEL |  | MECHANICAL PUNCTURE | 10 | 10 | [7 empty] | CLASS 1 LOCATION | NO |  | 242 |  | NO | NO | NO |  | 0 | 0 | 564 | 623.871688661979 | 147512 | 98427.4465849387 | 63821 | 70595.9486561988 | 31000 | 34290.8197668818 | 0 | 0 |  |  | 242897 | 150476.371055264 | 203938.086696681 | [8 empty] | 640 |  | 771 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 47853 | NO |  | YES |  |  |  | YES | NON-HCA PIPELINE | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PRESSURE DROP WAS IDENTIFIED BY THE CONTROLLER AND WAS CONFIRMED BY THE FIELD CREW AS THIRD PARTY DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | NO |  |  | YES | PRIVATE LANDOWNER | YES | [6 empty] | FARMER | FARM EQUIPMENT | AGRICULTURE | YES | 478602 | THERE ARE TWO TICKETS ASSOCIATED WITH THIS INCIDENT. 478040 | UTILITY OWNER | YES | YES | YES | 25 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO MAINTAIN CLEARANCE | [263 empty] | TROY BAUER | PIPELINE SAFETY AND COMPLIANCE ADVISOR | tbauer@semprautilities.com | 909-376-7208 | 909-885-6270 |  |  |  | TROY BAUER | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 909-376-7208 | tbauer@semprautilities.com | ON NOVEMBER 19, 2014, A THIRD PARTY CONTRACTOR WAS OPERATING A RIPPER AT NIGHT AND STRUCK A 10 INCH STEEL TRANSMISSION LINE, RESULTING IN A GAS LEAK. NO INJURIES OR FURTHER DAMAGE RESULTED FROM THIS INCIDENT. THE INCIDENT LOCATION IS 3,000 FEET SOUTH OF MILLUX RD, BAKERSFIELD. THE INITIAL INCIDENT LOCATION REPORTED TO DOT WAS LAKE ROAD, TAFT. ALL REPAIRS TO THE DAMAGED LINE WERE COMPLETED AND THE PIPELINE WAS RETURNED TO SERVICE IN APPROXIMATELY 26 HOURS. SERVICE TO AFFECTED CUSTOMERS WAS RESTORED OVER A PERIOD OF 2 DAYS. INVESTIGATION OF THE INCIDENT SHOWED THAT THE CONTRACTOR HAD NOTIFIED THE ONE-CALL CENTER AND THE LINE HAD BEEN MARKED CORRECTLY, BUT THE CONTRACTOR FAILED TO MAINTAIN PROPER CLEARANCE BY NOT DIGGING WITHIN 25 FEET OF EITHER SIDE OF THE LINE MARKINGS AS REQUIRED BY AGREEMENT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140143 | 16924 | 2014-12-18 07:31 | SUPPLEMENTAL FINAL | 2620 | COLUMBIA GULF TRANSMISSION, LLC | 700 LOUISIANA ST. SUITE 700 | HOUSTON | TX | 77002 | 2013-10-13 13:30 | 2013 |  |  | 30.6203 | -92.2541 | 1101367 | 2014-11-18 13:17 |  | NATURAL GAS |  | 3 | 15560 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2013-10-13 13:30 | 2013-10-14 08:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2013-10-13 12:45 | 2013-10-13 12:45 | ONSHORE | LA | 70586 | VILLE PLATTE | EVANGELINE | MILEPOST | 22.5 | PIPELINE | 100 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 50 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION | [19 empty] | OTHER BUTT WELD | [18 empty] | 2013 |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 338 |  | NO | NO | NO |  | 0 | 0 | 53533 | 60361.2960526316 | 11 | 8.58811475409836 | 0 | 0 | 0 | 0 | 105000 | 118393.067556952 | COST OF REPAIRS TO REPLACE THE SECOND VALVE |  | 158544 | 82061.8733468121 | 178762.951724338 | [8 empty] | 791 |  | 935 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 56138 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | AFTER PRESSURING THE LINE PIPE, THE LEAK WAS IDENTIFIED DURING LEAKAGE SURVEY |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER HAD NO ROLE IN THE INITATION OF THE INCIDENT | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES |  | YES | CRACK IN A WELD | [5 empty] | YES | CRACK IN A WELD | [12 empty] | YES | [63 empty] | NO | [63 empty] | YES |  |  | NO | [13 empty] | NO | [63 empty] | GEORGE HAMATY | ENGINEER | ghamaty@nisource.com | (304) 357-3728 |  |  |  |  | PERRY MICHAEL HOFFMAN | MANAGER SYSTEM INTEGRITY | (304) 357-2548 | mikehoffman@nisource.com | LINE 100 WAS SUBJECT TO AN INSTALLATION OF A SECOND VALVE AFTER THE FIRST VALVE WAS DAMAGED DUE TO A FAILED STOPPLE INSTALLATION. THE FAILED STOPPLE INSTALLATION WAS REFERENCED IN THE NRC REPORT NO.: 1062828 REPORTED ON OCTOBER 12, 2013 14:55, WITH AN ODES REPORT NUMBER OF 20130100 - 16173. COLUMBIA GULF TRANSMISSION, LLC, (COLUMBIA) WAS ADVISED BY PHMSA SOUTHWESTERN REGION TO FILE A SECOND INCIDENT REPORT, SEPARATE FROM THE OCTOBER 12, 2013 REPORT TO ADDRESS SEPARATE INSTANCE. ON OCTOBER 13, 2013 FOLLOWING THE OCTOBER 12, 2013 EVENT, A NEW VALVE WAS INSTALLED DUE TO A CRACKED WELD. THE CRACKED WELD RESULTED IN ONLY A SMALL AMOUNT OF GAS RELEASED TO THE ATMOSPHERE (LESS THAN THE INCIDENT REPORTING THRESHOLD OF 3,000 MCF). HOWEVER; THE COST OF REPAIRS EXCEEDED $50,000. THE CRACK WAS FOUND IN A CIRCUMFERENTIAL WELD BETWEEN THE NEW 16" HOT TAP VALVE AND 16" BRANCH PIPING. THE FIRST VALVE, WAS REMOVED AND A NEW VALVE WAS INSTALLED. THE NEW WELD FOR THIS VALVE WAS INSPECTED BY NON-DESTRUCTIVE TESTING TECHNICIANS PASSED THE INSPECTION CODE REQUIREMENT. ON OCTOBER 14, 2013 THE PIPELINE WAS RETURNED TO SERVICE. COLUMBIA'S ENGINEERING DEPARTMENT WORKED WITH THE CONTRACTED WELDING VENDOR TO ENSURE THAT THE PROPER WELDING PROCEDURES WERE FOLLOWED. IN ADDITION, COLUMBIA REVISED THE WELDING PROCEDURE USED IN THIS PROJECT TO AVOID ANY FUTURE RE-OCCURRENCE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140144 | 16587 | 2014-12-18 15:02 | ORIGINAL FINAL | 31604 | EQT MIDSTREAM | 2200 ENERGY DRIVE | CANONSBURG | PA | 15317 | 2014-11-19 01:30 | 2014 |  |  | 39.3171 | -80.1581 | 1101425 | 2014-11-19 08:03 |  | NATURAL GAS |  | 5000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-11-19 01:40 | 2014-11-19 02:50 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-11-19 01:30 | 2014-11-19 02:10 | ONSHORE | WV | 26330 | BRIDGEPORT | TAYLOR | SURVEY STATION NO. | 0+00 GSF608 | COMET COMPRESSOR STATION | COMET COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | ESD SYSTEM | 1970 |  | CARBON STEEL |  | OTHER | [8 empty] | EXTENDED VENTING OF ESD SYSTEM | CLASS 1 LOCATION | NO |  | 218 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 22050 | 14712.8721541156 | 0 | 0 | 200 | 221.231095270205 | 0 | 0 | 200 |  | 22250 | 15355.0535372872 | 14934.1032493858 | [8 empty] | 896 |  | 1000 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE GAS RELEASE WAS FROM AN ESD CAUSED BY AN INVALID GAS DETECTOR READING NOT MONITORED BY GAS CONTROL. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | ESD VALVE DID NOT CLOSE DUE TO MOISTURE IN SUPPLY GAS WHICH CAUSED FREEZE OFF | [161 empty] | JOE LOMBARDO | MANAGER COMPLIANCE | jlombardo@eqt.com | 412-395-3135 |  |  |  |  | JOE LOMBARDO | MANAGER COMPLIANCE | 412-395-3135 | jlombardo@eqt.com | AT APPROXIMATELY 1:30 AM NOVEMBER 19, 2014 THE EQT CALL CENTER RECEIVED A CALL FROM A MEMBER OF THE PUBLIC ABOUT NOISE AT COMET COMPRESSOR STATION. THE CALL CENTER CONTACTED OPERATIONS PERSONNEL TO RESPOND AND OPERATIONS PERSONNEL ARRIVED AT APPROXIMATELY 2:10 AM TO FIND THE ESD HAD ACTIVATED, AN ESD VALVE HAD NOT CLOSED AND GAS WAS VENTING AT THE STATION SITE. GAS CONTROL ALSO CONTACTED OPERATIONS AND WERE NOTIFIED PERSONNEL WERE IN ROUTE. THE APPLICABLE VALVES WERE SHUT WHICH STOPPED THE VENTING. ONCE CALCULATIONS WERE COMPLETED IT WAS DETERMINED THE GAS LOSS WAS GREATER THAN THE 3 MMCF FOR REPORTING. THE INITIAL ESD WAS DETERMINED TO BE CAUSED BY A BAD GAS DETECTOR SENSOR WHICH WAS REPLACED. IT APPEARS THE VALVE DID NOT CLOSE DUE TO MOISTURE IN THE SUPPLY GAS LINE CAUSING FREEZE OFF.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140145 | 16590 | 2014-12-19 10:53 | ORIGINAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2014-11-27 03:17 | 2014 |  |  | 36.8665 | -97.9308 | 1102104 | 2014-11-27 05:55 |  | NATURAL GAS |  | 3910 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE RELIEF VALVE FAILED AT THE WRONG SET POINT. THE RELIEF VALVE WAS SHUT IN. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-11-27 03:20 | 2014-11-27 04:16 | ONSHORE | OK | 73771 | WAKITA | GRANT | SURVEY STATION NO. | 150/10321+78 | WAKITA STATION-LINE N | OKLAHOMA HUGOTON 26" | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1965 |  | CARBON STEEL |  | OTHER | [8 empty] | THE RELIEF VALVE MALFUNCTIONED AND STARTED TO RELIEVE GAS BELOW THE SET POINT. | CLASS 1 LOCATION | NO |  | 236 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 16031 | 10696.6917688266 | 2100 | 2322.92650033715 | 1300 | 1438.00211925633 | 0 | 0 |  |  | 19431 | 12816.1115349324 | 14457.6203884201 | [8 empty] | 542 |  | 720 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) | [6 empty] | YES | [6 empty] | YES | 1 | 0 | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [24 empty] | YES |  |  |  | YES | VALVE BEGAN BLOWING BELOW SET POINT. | [161 empty] | DAVID COOMES | COMPLIANCE ENGINEER | david.coomes@sscgp.com | 2708524391 |  |  |  |  | DAVID SINCLAIR | PIPELINE COMPLIANCE MANAGER | 2708524424 | david.l.sinclair@sscgp.com | ON 11/27/2014 AT 03:20 SSC GAS CONTROL BEGAN RECEIVING ALARMS THAT LASTED APPROXIMATELY 15 MINUTES. DURING THIS TIME THE PRESSURES ON THE "GUYMON 26IN." WERE OBSERVED AS DECREASING AND CONTINUED FOR APPROXIMATELY 40 MINUTES. GAS CONTROL ATTEMPTED TO INVESTIGATE THE POTENTIAL CAUSE AND AFTER NO REASONING COULD BE DETERMINED, SSC OPERATIONS WERE CALLED AT 03:50. SSC OPERATIONS ARRIVED AT THE WAKITA COMPRESSOR STATION AND CONFIRMED WITH GAS CONTROL, AT 04:16, THE CAP ON THE RELIEF VALVE WAS OFF AND IT WAS THE EXPECTED CAUSE OF THE DROP IN PRESSURE. BY 11:29 ALL RELIEF VALVES BETWEEN WAKITA STATION AND THE UPSTREAM ALVA STATION HAD BEEN CONFIRMED AS NOT BLOWING. THE SET-POINTS WERE TESTED ON THE RELIEF AND FOUND TO WORK CORRECTLY. THE STATION PIPING WAS ISOLATED UNTIL 12/2 WHEN THE RELIEF WAS REBUILT AND TESTED AGAIN.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20140146 | 16903 | 2014-12-19 12:58 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2014-11-23 06:16 | 2014 |  |  | 40.7065 | -82.3607 | 1101766 | 2014-11-23 09:30 |  | NATURAL GAS |  | 4424 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-11-23 07:20 | 2014-11-25 15:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-11-23 06:16 | 2014-11-23 07:00 | ONSHORE | OH | 44864 | PERRYSVILLE | RICHLAND | MILEPOST | C105-169 | LUCAS COMPRESSOR STATION | 5C-1120-06 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 2 |  | 0.218 | 35000 | API 5L | SEAMLESS |  | UNKNOWN | PAINT | [28 empty] | 1981 | 1981 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 2 | 2 |  | CLASS 1 LOCATION | NO |  | 44 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 16059 | 10715.3747810858 | 12000 | 13273.8657162123 | 0 | 0 | 0 | 0 |  |  | 28059 | 17202.1702057055 | 23989.2404972981 | [8 empty] | 714 |  | 720 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRELIMIANRY INDICATIONS ARE POINTING TO A PRE-EXISTING CONDITION ON THE FAILED 2-IN TAP THAT BROKE-OFF LEADING TO AN UNINTENDED RELEASE OF MATERIAL INTO ATMOSPHERE. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES |  |  |  | YES | MECHANICAL VIBRATION | [16 empty] | YES | [6 empty] | YES | FAILURE OF THE 2-IN DIAMETER PIPE WAS FATIGUE AS A RESULT OF CYCLIC BENDING DUE TO INADEQUATE PIPE SUPPORT. | [55 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | GEORGE HAMATY | ENGINEER | ghamaty@cpg.com | (304) 357-3728 | (304) 357-3522 |  |  |  | PERRY MICHAEL HOFFMAN | MANAGER - SYSTEM INTEGRITY | (304) 357-2548 | mikehoffman@cpg.com | A RELIEF VALVE (RV) WAS ACTIVATED AND RELEASED AN UNINTENDED AMOUNT OF MATERIAL INTO ATMOSPHERE AT A COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA) COMPRESSOR STATION (CS) FACILITY IN PERRYSVILLE, OH. THIS CS IS OWNED, OPERATED AND MAINTAINED BY COLUMBIA. WHILE THE RV WAS STILL RELIEVING MATERIAL, THE 2-IN PIPELINE THAT THIS RV WAS INSTALLED ON WAS BROKEN. THIS STAND-OFF STEEL PIPE IS OF 2-IN DIAMETER WITH A WALL THICKNESS OF .218-IN. WAS FOUND BROKEN-OFF AT ITS LOWER SECTION (CLOSE TO THE PIPELINE THIS RV IS PROTECTING) AND SEPARATING THE RV FROM ITS PIPE. THE BROKEN 2-IN PIPE WAS REMOVED AND SENT TO A METALLURGICAL INVESTIGATION FAILURE CONSULTANT FOR FURTHER ANALYSIS AND INVESTIGATION. PRIOR TO THE MATERIAL RELEASE, THE CS UNITS WERE SHUT DOWN AS FLOW FROM THE STORAGE FIELD WAS NOT REQUIRED TO MAINTAIN CUSTOMER DEMAND. WHEN THIS OCCURS, DEPENDING ON STORAGE VOLUME, THE PIPELINE PRESSURE GRADUALLY INCREASED UP TO THE PREVAILING STORAGE FIELD WELL PRESSURE. AT THE TIME, THE COMPRESSOR STATION PIPING AND VALVING WAS CONFIGURED TO ALLOW THIS PRESSURE RISE INTO THE CS SUCTION PIPING WHICH HAS TWO RELIEF VALVES SET AT 720 PSIG. ONE RV ACTUATED AND VENTED AS INTENDED; AND KEPT THE SUCTION PIPING PRESSURE FROM INCREASING FURTHER. RESULTS OF METALLURGICAL FAILURE ANALYSIS INDICATE THAT THE CAUSE OF THE 2-IN DIAMETER PIPE FAILURE WAS FATIGUE AS A RESULT OF CYCLIC BENDING. AS A PREVENTIVE MEASURE TO PREVENT THE CHAIN OF EVENTS FROM RE-OCCURING IN THE FUTURE, A SUPPORT WAS INTRODUCED TO THE RV-PIPE ASSEMBLY WHERE IT WILL DIS-ALLOW THE RV VENT STACK FROM SWAYING, HENCE, DAMPENING THE CYCLIC EFFECT THAT LED TO THIS INCIDENT. SIMILAR INSTALLATION WAS APPLIED ON A SIMILAR APPLICATION WITHIN THE SAME FACILITY.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140147 | 16659 | 2014-12-22 16:21 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2014-11-26 12:00 | 2014 |  |  | 29.2421 | -91.5051 | 1102064 | 2014-11-26 13:14 |  | NATURAL GAS |  | 2500 | 12000 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-12-13 00:05 | 2014-12-18 05:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-11-26 12:00 | 2014-12-03 13:00 | OFFSHORE | [28 empty] | 15 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EUGENE ISLAND | 55 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE SEAM | 20 |  | 0.406 | 52000 | API 5L | DSAW |  | UNITED STATES STEEL | COAL TAR | [28 empty] | 1965 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 506 |  | NO | NO | NO |  | 0 | 0 | 49440 | 54688.3267507947 | 10425 | 6956.08581436077 | 500000 | 553077.738175513 | 0 | 0 | 0 | 0 |  |  | 559865 | 286192.35084017 | 614722.150740669 | [8 empty] | 905 |  | 1050 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 184800 | NO |  |  | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | AIR PATROL |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE SMALL SIZE OF THE DEFECT(PINHOLE LEAK) AND THE SMALL AMOUNT OF GAS LEAKING WOULD NOT BE DETECTABLE BY THE CONTROLLERS OR CONTROL ROOM. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | YES | YES | [13 empty] | YES | WELD ANOMOLY | [13 empty] | YES | PINHOLE IN WELD | [55 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | YES |  |  | 2014 |  |  | TIME OF FLIGHT DIFFRACTION (TOFD) | 2014 |  |  | YES |  |  | YES | [50 empty] | ROGER R. STREET | FIELD COMPLIANCE SPECIALIST | roger_street@transcanada.com | 6154655123 |  |  |  |  | ROBERT LATIMER | MANAGER U.S. REGULATORY COMPLIANCE | (402)492-7454 | rob_latimer@transcanada.com | ON 26 NOVEMBER 2014 DURING A FLIGHT OVER THE GULF OF MEXICO, AN TRANSCANADA/ ANR PIPELINE COMPANY (ANR) TECHNICIAN OBSERVED A POTENTIAL LEAK NEAR TC OFFSHORE (TCO) ASSETS IN THE OUTER CONTINENTAL SHELF (OCS) EUGENE ISLAND BLOCK 55 (EI-55). THE LEAK WAS REPORTED TO ANR, OPERATOR FOR TC OFFSHORE, AS A BUBBLING PATTERN APPROXIMATELY TWO FEET IN DIAMETER OVER TC OFFSHORE'S 733 TRANSMISSION PIPELINE AT APPROXIMATE MILEPOST 40.8 (29.24206280, -91.50513440). FOLLOWING THE REPORT OF THE INCIDENT TO THE NATIONAL RESPONSE CENTER, TRANSCANADA/ANR MAINTAINED CONTACT AND UPDATED REGULARLY U.S. COAST GUARD, BSEE, AND PHMSA. WHILE PREPARING TO DISPATCH AN INVESTIGATION AND REPAIR VESSEL TO THE SITE, ANR SCHEDULED AERIAL PATROLS TWICE DAILY TO MONITOR THE LEAK. NO SHEEN OR PRODUCT WAS DOCUMENTED AT THE SITE FOR THE DURATION OF THE LEAK AND REPAIR. THE REPAIR VESSEL AND CONTRACT EMPLOYEES ARRIVED AT THE INCIDENT LOCATION ON 3 DECEMBER TO BEGIN EXPOSING THE PIPE FOR THE LEAK INVESTIGATION. COVER MATERIAL JETTING AND CONCRETE REMOVAL AT THE LEAK SITE WAS COMPLETED ON 8 DECEMBER. OBSERVATION AND INVESTIGATION BY THE DIVERS DETERMINED THAT THE LEAK WAS LOCATED AT THE TWELVE O'CLOCK POSITION IN THE LONGITUDINAL SEAM 45 INCHES DOWNSTREAM OF A GIRTH WELD. DURING THE COVER MATERIAL REMOVAL, ULTRASONIC TESTS TO DETERMINE THE POSSIBILITY OF METAL LOSS WERE CONDUCTED ON THE PIPELINE AT TWO LOCATIONS UPSTREAM AND DOWNSTREAM OF LEAK AREA. THESE TESTS INDICATED NO METAL LOSS TO THE PIPELINE. UPON DISCOVERY OF THE LEAK LOCATION, ANR DECIDED TO ISOLATE THE PIPELINE SEGMENT, REDUCE THE PRESSURE ON THE LINE, AND PERFORM ADDITIONAL TESTING AND ANALYSIS TO DETERMINE THE MOST EFFECTIVE REPAIR. ON 13 DECEMBER, SUBSEA VALVE 733-1A-2 LOCATED AT EUGENE ISLAND BLOCK 63 (EI-63) WAS CLOSED, ISOLATING THE 733 PIPELINE BETWEEN EI-63 AND ANR'S PATTERSON COMPRESSOR STATION LOCATED IN ST. MARY PARISH, LOUISIANA. ADDITIONALLY, THE PRODUCER, CASTEX, WAS SHUT-IN AND THE VALVE WAS CLOSED AT EUGENE ISLAND BLOCK 18. PRESSURE ON THE 733 LINE WAS REDUCED FROM APPROXIMATELY 800 PSIG TO 400 PSIG AND FLARED AT THE PATTERSON COMPRESSOR STATION. FOLLOWING THE REDUCTION IN PRESSURE, TIME OF FLIGHT DIFFRACTION NON-DESTRUCTIVE TESTING (NDT) WAS CONDUCTED ON 15 DECEMBER 2014 TO DETERMINE THE CHARACTERISTICS AND LOCATION OF LEAK. THE AREA INSPECTED INCLUDED ONE FOOT UPSTREAM AND ONE FOOT DOWNSTREAM OF THE ANOMALY AREA. TESTING INDICATED A SMALL DEFECT LOCATED WITHIN THE LONGITUDINAL SEAM WITH NO INDICATION OF CRACKS OR LACK OF FUSION. ON 18 DECEMBER AT 05:00 CST, A PLIDCO BOLT-ON CLAMP WAS SUCCESSFULLY INSTALLED OVER THE LEAK LOCATION BY QUALIFIED CONTRACT EMPLOYEES. THE CLAMP IS CONSIDERED A PERMANENT REPAIR. FOLLOWING THE INSTALLATION OF THE CLAMP, PIPELINE PRESSURE WAS INCREASED, THE PRODUCER VALVE AT EI-18 WAS ALLOWED TO RESUME FLOWING, AND THE SUBSEA VALVE AT EI-63 WILL BE REOPENED WHEN IT CAN BE SAFELY ACCESSED. THERE WERE NO INDICATIONS OF FURTHER LEAKAGE AT THE REPAIR LOCATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140148 | 16896 | 2014-12-22 21:24 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2014-11-22 16:52 | 2014 |  |  | 35.1603 | -118.8042 | 1103815 | 2014-12-18 14:17 |  | NATURAL GAS |  | 119000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE RELIEF VALVE WAS ISOLATED BUT THIS DID NOT SHUT DOWN THE PIPELINE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 100 | 2014-11-22 16:52 | 2014-11-22 17:41 | ONSHORE | CA | 93203 | ARVIN | KERN COUNTY | MILEPOST | 4-PLS | L-300B | MP 256.64 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2014 |  | CARBON STEEL |  | OTHER | [8 empty] | PRESSURE RELIEF VALVE UNINTENTIONALLY VENTED NATURAL GAS | CLASS 1 LOCATION | NO |  | 650 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 564525 | 376679.553415061 | 5000 | 5530.77738175513 | 0 | 0 | 0 | 0 |  |  | 569525 | 393059.569605559 | 382210.330796816 | [8 empty] | 764 |  | 803 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 26 | NO |  | YES |  |  |  | YES | A PIG LAUNCHER IS INSTALLED AT PLS-4, WHICH ALLOWS INSPECTION ON L-300B BETWEEN MP 256.65-298.96 (PLS-4 TO PLS-5). HOWEVER, THE SECTION OF L-300B SOUTH OF PLS-4 IS NOT CURRENTLY PIGGABLE DUE TO LACK OF A LAUNCHER/RECEIVER AND PLUG VALVES REQUIRING REPLACEMENT. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELEASE OF GAS WAS DUE TO A MALFUNCTIONED PRESSURE RELIEF VALVE AND NOT DUE TO THE CONTROLLER OR CONTROL ROOM ISSUES | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | STILL UNDER INVESTIGATION | [161 empty] | CHERYL DIZON | COMPLIANCE ENGINEER | c1dz@pge.com | 925-328-5721 |  |  |  |  | LARRY DENISTON | MANAGER OF GAS OPERATIONS REGULATORY COMPLIANCE | 925-328-5756 | lcd1@pge.com | ON NOVEMBER 22, 2014 AT 1652 HOURS AN 8-INCH PRESSURE RELIEF VALVE ON PG&E'S 34-INCH TRANSMISSION LINE L-300B AT PRESSURE LIMITING STATION 4-PLS MALFUNCTIONED RESULTING IN AN UNINTENTIONAL RELEASE OF NATURAL GAS TO THE ATMOSPHERE. PG&E PERSONNEL ARRIVED ON SCENE AT 1741 HOURS AND THE RELEASE OF GAS WAS STOPPED AT 1948 HOURS BY CLOSING TWO BRIDAL VALVES, WHICH ISOLATED THE RELIEF VALVE, ALLOWING GAS TO BYPASS THE RELIEF VALVE THROUGH A MAINLINE VALVE ON THE TRANSMISSION LINE. NO CUSTOMERS EXPERIENCED GAS SERVICE INTERRUPTION. THERE WERE NO INJURIES, NO FATALITIES AND NO IGNITION AS A RESULT OF THIS INCIDENT. A LOCAL RESIDENTIAL CLUBHOUSE WAS EVACUATED BY THE FIRE DEPARTMENT OUT OF AN ABUNDANCE OF CAUTION. LOCAL MEDIA WAS ON SCENE DURING THE INCIDENT. THE PRESSURE RELIEF VALVE (PRV) INSTRUMENTATION TUBING WAS REPLACED, ITS SET POINTS WERE RE-TESTED, AND A FUNCTIONAL CHECK OUT WAS COMPLETED BY DECEMBER 10, 2014. PRIOR TO REPAIRING THE MALFUNCTIONING PRV, OVERPRESSURE PROTECTION WAS PROVIDED BY CONTROLLING AND RESTRICTING THE NATURAL GAS PRESSURE THROUGH 3-PLS (THE PRESSURE LIMITING STATION UPSTREAM OF 4-PLS.) FOLLOWING THE INCIDENT, PG&E CONTRACTED A THIRD PARTY ENGINEERING FIRM TO PERFORM A ROOT CAUSE ANALYSIS AND PROVIDE RECOMMENDATIONS TO THE STATION. PG&E IMPLEMENTED SEVERAL MODIFICATIONS AND IS CURRENTLY IN THE DESIGN PHASE TO REBUILD PLS-4. PG&E INSPECTS AND CALIBRATES PRESSURE RELIEF VALVES (PRV) AS PART OF PG&E'S ROUTINE MAINTENANCE PROGRAM, WHICH IS DESIGNED TO ENSURE THE RELIABLE OPERATION OF THIS EQUIPMENT AT PG&E'S PRESSURE LIMITING STATIONS. THE UNINTENTIONAL RELEASE OF NATURAL GAS IS ESTIMATED TO BE APPROXIMATELY 119 MILLION CUBIC FEET (MMCF), THEREFORE THE INCIDENT WAS REPORTED TO THE DOT AND CPUC.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20140149 | 16605 | 2014-12-31 11:07 | ORIGINAL FINAL | 18152 | SEA ROBIN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2014-12-03 16:30 | 2014 |  |  | 28.8789 | -92.1403 | 1102618 | 2014-12-04 11:30 |  | NATURAL GAS |  | 4469 | 29455 | 0.7 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-12-05 15:30 | 2014-12-12 21:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-12-03 16:30 | 2014-12-05 06:30 | OFFSHORE | [28 empty] | 90 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SOUTH MARSH ISLAND | 27 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 26 |  | 0.5 | 60000 | API 5LX | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | SAW CRISPIN (S.V.) DUNKERQUE, FRANCE | OTHER | CONCRETE WITH SOMASTIC | [27 empty] | 1970 | 1970 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 634 |  | NO | NO | NO |  | 0 | 0 | 101031 | 111755.993931221 | 15329 | 10228.2819614711 | 300000 | 331846.642905308 | 0 | 0 | 0 | 0 |  |  | 416360 | 214229.439919792 | 453830.918797999 | [8 empty] | 852 |  | 1250 | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 122364 | NO |  |  | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | OTHER | NOTIFICATION FROM THIRD PARTY PERSONNEL ON A NEARBY PLATFORM |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT DUE TO A SMALL PINHOLE LEAK. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | PINHOLE LEAK. |  |  |  |  | YES | LOW FLOW. |  |  | YES | HISTORICAL DATA. |  |  |  |  | YES | LEAK LOCATED AT THE 6 O'CLOCK POSITION. | YES | NO | YES | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | NATHAN HLAVATY | DIRECTOR - REGULATORY COMPLIANCE |  | 7138575479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - REGULATORY COMPLIANCE | 7138575479 | nathan.hlavaty@energytransfer.com | AT APPROXIMATELY 16:30 PM ON 12/03/2014, GAS CONTROL RECEIVED A CALL FROM PRODUCER PLATFORM PERSONNEL AT ANKOR'S SMI 27JA PLATFORM REPORTING SEEING BUBBLES SOUTH OF THEIR FACILITY IN THE SMI 27 BLOCK. WEATHER PREVENTED PERSONNEL TO INVESTIGATE OVERNIGHT. THE NRC WAS NOTIFIED (NRC # 1102618), AT 11:30 AM ON 12/04 OF A POSSIBLE LEAK. WE WERE ABLE TO MAKE A FLIGHT ON 12/05 AND BASED ON THE COORDINATES FOR THE LEAK, WE SHUT DOWN THE PIPELINE AT 15:30 PM ON 12/05/14. THE PIPELINE WAS REPAIRED AND RESTARTED AT 21:30 PM ON 12/12/14.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20150001 | 16691 | 2015-01-07 14:53 | SUPPLEMENTAL FINAL | 32296 | TARGA RESOURCES OPERATING LLC | 811 LOUISIANA ST SUITE 2100 | HOUSTON | TX | 77002 | 2014-12-07 10:00 | 2014 |  |  | 29.5322 | -93.2233 | 1102856 | 2014-12-07 12:40 |  | NATURAL GAS |  | 750 | 2233 | 1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-12-07 11:00 | 2014-12-11 17:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-12-07 12:08 | 2014-12-08 19:00 | OFFSHORE | [28 empty] | 45 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST CAMERON | 109 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12.75 |  | 0.375 | 52000 | API5L | SEAMLESS |  | UNKNOWN | OTHER | CONCRETE | [27 empty] | UNKNOWN | 1969 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 200 |  | NO | NO | NO |  | 0 | 0 | 11000 | 12167.7102398613 | 3000 | 2001.75131348511 | 190000 | 210169.540506695 | 10000 | 11061.5547635103 | 0 | 0 |  |  | 214000 | 109211.516864216 | 235400.556823552 | [8 empty] | 480 |  | 1240 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 110544 | NO |  |  | YES |  |  |  |  | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  |  | YES | [5 empty] | YES | FIELD EXPERIENCE. | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | TIM HUFFER | MANAGER REGULATORY COMPLIANCE | thuffer@targaresources.com | 337-583-4642 | 337-583-4630 |  |  |  | TIM HUFFER | MANAGER REGULATORY COMPLIANCE | 337-583-4642 | thuffer@targaresources.com | TARGA RECEIVED NOTIFICATION OF INDICATIONS OF A LEAK IN THE VICINITY OF ITS PIPELINE FROM A THIRD PARTY. TARGA DISPATCHED A HELICOPTER AND BEGAN SHUTDOWN OF THE PIPELINE TO REDUCE FLOW. REPAIR COMPLETED BY INSTALLATION OF A BOLTED SPLIT SLEEVE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150002 | 16611 | 2015-01-09 21:27 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2014-12-10 09:00 | 2014 |  |  | 34.8857 | -117.1707 | 1103102 | 2014-12-10 |  |  |  | 0 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | NATURAL GAS WAS NOT RELEASED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-12-10 09:00 | 2014-12-10 09:00 | ONSHORE | CA | 92347 | HINKLEY | SAN BERNARDINO COUNTY | MILEPOST | MP 1.2 | L-314 | MP 1.2 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | OTHER | SUSPICIOUS DEVICE ON PIPE RIGHT-OF-WAY |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | SUSPICIOUS DEVICE FOUND ON GROUND | 1957 |  | CARBON STEEL |  | OTHER | [8 empty] | A SUSPICIOUS DEVICE ON THE PIPELINE RIGHT OF WAY WAS IDENTIFIED. | CLASS 1 LOCATION | NO |  | 259 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | [8 empty] | 481 |  | 861 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL |  | NO | YES | YES | YES | YES |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A PG&E EMPLOYEE WAS PERFORMING A ROUTINE PATROL OF TRANSMISSION PIPELINE L-314 WHEN THE EMPLOYEE IDENTIFIED A SUSPICIOUS DEVICE ON THE GROUND | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | THE CAUSE FOR REPORTING THIS INCIDENT WAS THE DISCOVERY OF AN EXPLOSIVE DEVICE IN OUR PIPELINE RIGHT-OF-WAY WHICH WE CONSIDERED A SIGNIFICANT EVENT. THERE WAS NO EXPLOSION, NO RELEASE OF GAS, AND NO DAMAGES TO OUR FACILITIES. | [147 empty] | WINI CHEN | PROGRAM MANAGER | wcce@pge.com | 925-328-5798 |  |  |  |  | LARRY DENISTON | MANAGER OF GAS OPERATIONS REGULATORY COMPLIANCE | 925-328-5756 | lcd1@pge.com | AT APPROXIMATELY 0900 HOURS, A PG&E EMPLOYEE WAS PERFORMING A ROUTINE PATROL OF TRANSMISSION PIPELINE L-314 (ABOUT A MILE FROM THE HINKLEY COMPRESSOR STATION, NEAR MILE POINT 1.2) WHEN THE EMPLOYEE IDENTIFIED A SUSPICIOUS DEVICE ON THE GROUND. THE DEVICE WAS DISCOVERED ABOVE TWO BURIED PIPELINES (A PG&E NATURAL GAS TRANSMISSION PIPELINE AND A MOJAVE WATER DISTRICT PIPELINE) AND THE PIPELINE ROUTE WAS CLEARLY MARKED AS SHARED BY PG&E AND THE MOJAVE WATER DISTRICT. THE PG&E EMPLOYEE MOVED THE DEVICE ABOUT 2,000 FEET ALONG THE ROAD, TO A LOCATION ABOVE THE RIGHT-OF-WAY SHARED BY PG&E AND THE KINDER MORGAN COMPANY, PRIOR TO REPORTING THE DEVICE TO HIS SUPERVISOR. THE SUPERVISOR THEN REPORTED THE MATTER TO PG&E'S CORPORATE SECURITY DEPARTMENT AND THE SAN BERNARDINO COUNTY SHERIFF'S DEPARTMENT. THE SHERIFF'S DEPARTMENT PATROL DEPUTY ARRIVED ON SCENE AT APPROXIMATELY 0930 HOURS. UPON SEEING THE DEVICE, THE DEPUTY ESTABLISHED A ONE MILE PERIMETER AROUND THE DEVICE'S LOCATION, INSTRUCTED HINKLEY COMPRESSOR STATION EMPLOYEES TO SHELTER IN PLACE, AND CALLED THE SHERIFF'S DEPARTMENT BOMB SQUAD. PG&E'S CORPORATE SECURITY DEPARTMENT DISPATCHED AN INVESTIGATOR TO THE SCENE WHO ESTABLISHED CONTACT WITH HINKLEY COMPRESSOR STATION AND SAN BERNARDINO SHERIFF'S DEPARTMENT. BOMB SQUAD PERSONNEL ARRIVED AT APPROXIMATELY 1300 HOURS. THE BOMB SQUAD EXAMINED THE DEVICE, THEN REMOVED IT TO A SAFE AREA NEARBY AND RENDERED IT SAFE AT APPROXIMATELY 1345 HOURS. PG&E'S CORPORATE SECURITY DEPARTMENT WAS ADVISED SHORTLY THEREAFTER THAT THE SHERIFF'S BOMB TECHNICIANS DECLARED IT WAS A FUNCTIONAL DEVICE, WHICH COULD HAVE EXPLODED IF IT HAD AN OUTSIDE POWER SOURCE, WHICH IT LACKED. THE DEVICE WAS DESCRIBED AS A PVC PIPE, ABOUT TWO INCHES IN DIAMETER, SEVERAL INCHES LONG, WITH END CAPS ATTACHED. THE SAN BERNARDINO SHERIFF'S DEPARTMENT ADVISED THE DEVICE WOULD NOT HAVE BEEN POWERFUL ENOUGH TO AFFECT THE PIPES HAD IT EXPLODED ABOVE THEM. CORPORATE SECURITY COMMUNICATED THE DETAILS OF THE INCIDENT TO THE TRANSPORTATION SECURITY ADMINISTRATION AND THE RIVERSIDE RESIDENT AGENCY OFFICE OF THE FEDERAL BUREAU OF INVESTIGATION. FROM DECEMBER 10 TO 11, PG&E RE-INSPECTED THE PIPELINE L-314 ROUTE, ALONG WITH OTHER PG&E PIPELINE ROUTES IN THE AREA, TO LOOK FOR OTHER DEVICES. NO OTHER DEVICES WERE DISCOVERED. THERE WAS NO RELEASE OF GAS, NO INJURIES OR FATALITIES, NO MAJOR MEDIA ON SCENE AND DAMAGES ARE LESS THAN $50,000. NO CUSTOMERS EXPERIENCED GAS SERVICE INTERRUPTION AND NO GAS FACILITIES WERE SHUT DOWN. THIS INCIDENT WAS REPORT TO CPUC AND DOT BECAUSE OF THE SIGNIFICANCE OF THE EVENT. (PLEASE NOTE THAT THE RESPONSES TO PART E, QUESTIONS 5A, 5B, AND 5C OF THIS PHMSA 7100 REPORT ARE MERELY PLACEHOLDERS AND DO NOT APPLY SINCE THERE WAS NO RELEASE OF NATURAL GAS. THE PHMSA 7100 REPORT FORM DOES NOT ALLOW THESE FIELDS TO BE LEFT BLANK.)
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150003 | 16614 | 2015-01-14 08:22 | ORIGINAL FINAL | 18152 | SEA ROBIN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2014-12-12 16:00 | 2014 |  |  | 28.8997 | -92.1122 | 1103392 | 2014-12-14 09:15 |  | NATURAL GAS |  | 33.1 | 29455 | 0.12 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-12-14 14:00 | 2014-12-21 14:26 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-12-12 16:00 | 2014-12-17 05:30 | OFFSHORE | [28 empty] | 87 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SOUTH MARSH ISLAND | 27 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 26 |  | 0.5 | 60000 | API 5LX | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | SAW CRISPIN (S.V.) DUNKERQUE, FRANCE | OTHER | CONCRETE WITH SOMASTIC | [27 empty] | 1970 | 1970 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 634 |  | NO | NO | NO |  | 0 | 0 | 190573 | 210803.367594644 | 123 | 82.0718038528897 | 265000 | 293131.201233022 | 0 | 0 | 0 | 0 |  |  | 455696 | 231404.351894737 | 504016.640631519 | [8 empty] | 852 |  | 1250 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 122364 | NO |  |  | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS TOO SMALL FOR SCADA TO DETECT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | PINHOLE LEAK |  |  |  |  | YES | LOW FLOW |  |  | YES | HISTORICAL DATA |  |  |  |  | YES | LEAK LOCATED AT THE 4 O'CLOCK POSITION | YES | NO | YES | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | NATHAN HLAVATY | DIRECTOR - REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713.857.5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - REGULATORY COMPLIANCE | 713.857.5479 | nathan.hlavaty@energytransfer.com | THIS INCIDENT REPORT IS BEING SUBMITTED ON 01/14/15, DUE TO DATA INPUT ISSUES WITH THE PORTAL NOT ALLOWING COST INFORMATION TO BE ENTERED IN THE PART D 7. (A -F) SECTIONS OF THE REPORT FROM 01/10/15 - 01/14/15. LISTED BELOW IS THE SUMMARY OF EVENTS: 12.14.14, OUR EMPLOYEES NOTED A SMALL SHEEN AND BUBBLES. GIVEN ITS PROXIMITY TO A PRODUCER SATELLITE FACILITY WE BELIEVED IT TO BE THEIR ISSUE, HOWEVER UPON HAVING THE COORDINATES PLOTTED OUT IT LOOKED TO BE ON OUR 26" LINE. WE STARTED THE PROCESS OF ISOLATING THE SEGMENT BETWEEN SMI 33 AND VR 149 WHILE WE SOURCED A DSV TO INVESTIGATE FOR US. WE SPOKE TO THE USCG THE PREVIOUS EVENING ABOUT THIS AND JUST UPDATED THEM, AS WELL AS NOTIFYING THE NRC. 12.15.14, OUR FLIGHT REPORTED THAT THE LEAK AND ASSOCIATED SHEEN WERE AS PREVIOUSLY REPORTED WITH NO APPRECIABLE CHANGE. WE CONTINUED TO DISCUSS OPTIONS WITH DSV PROVIDERS. PRESSURE MONITORING WAS ONGOING WITH LITTLE DEVIATION NOTED. THE USCG WAS UPDATED AS TO STATUS. 12.16.14, WE LOCATED A DSV. THE SHEEN WAS STILL PRESENT BUT ONLY 1/4 MILE LONG AND WAS ENCOUNTERING A CHANGING CURRENT AND CHOPPY SEAS. WE GAVE THE USCG THEIR DAILY UPDATE. 12.17.14, THE DSV MADE IT TO THE SITE. INITIAL REPORT WAS THAT THEY LOCATED THE LEAK SOURCE VIA PROBE WITH APPROXIMATELY 5 FEET OF COVER. THEY CONFIRMED THE PIPE SIZE AS OUR 26'. THERE WAS NO REPORTED CHANGE TO THE LEAK ITSELF AT THE TIME. 12.18.14, OVERNIGHT WE WERE ABLE TO LOWER THE LINE PRESSURE AND BEGAN REMOVING CONCRETE AND MASTIC IN THE EARLY HOURS. IT APPEARED AT THE TIME TO BE A PIN HOLE LEAK. DIVERS CONTINUED TO CLEAN UP THE AREA TO OBTAIN THE VARIOUS UT AND CP READINGS NEEDED. 12.19.14, WE COMPLETED ALL PREP WORK ON THE PIPELINE AND CONFIRMED THAT A LEAK CLAMP WOULD BE OUR REPAIR METHOD. DUE TO THE INCREASING SEAS AND THE RISK OF A VESSEL TO VESSEL TRANSFER OF THE CLAMP, THE DSV WENT TO DOCK TO PICK UP THE CLAMP AND EQUIPMENT. 12.21.14, THE CLAMP WAS INSTALLED AND ALL LEAK CHECKS WENT WELL. WE WERE UNABLE TO FLY TO ALLOW PRODUCERS BACK ON AND RETURN THE LINE TO NORMAL SERVICE DUE TO WEATHER. 12.22.14, WEATHER FINALLY CLEARED UP. WE MADE AN OVER FLIGHT TO THE SMI 33 FACILITY, SEEING NO SIGNS OF LEAKAGE WHILE IN ROUTE. THE SMI 33 FACILITY WAS THEN PLACED INTO NORMAL SERVICE. THE HELICOPTER MADE STOPS AT THE LOCKED PRODUCER FACILITIES AND PLACED THEM IN NORMAL OPERATIONS.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150004 | 16836 | 2015-01-14 16:09 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2014-12-16 10:00 | 2014 |  |  | 36.8665 | -97.9308 | 1103567 | 2014-12-16 11:27 |  | NATURAL GAS |  | 12500 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-12-16 10:50 | 2014-12-16 15:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-12-16 10:00 | 2014-12-16 10:43 | ONSHORE | OK | 73771 | WAKITA | GRANT | SURVEY STATION NO. | 150/10321+78 | WAKITA STATION - LINE N | OKLAHOMA HUGOTON 26" | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1965 |  | CARBON STEEL |  | OTHER | [8 empty] | STATION ESD WAS ACTIVATED CAUSING THE STATION TO BLOW DOWN AND A MAINLINE VALVE DID NOT FULLY CLOSE, CAUSING EXCESSIVE GAS LOSS. | CLASS 1 LOCATION | NO |  | 236 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 44563 | 29734.6812609457 | 0 | 0 | 900 | 995.539928715923 | 0 | 0 |  |  | 45463 | 31284.2733170917 | 30730.2211896616 | [8 empty] | 625 |  | 765 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | NO | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) | [5 empty] | YES | [5 empty] | YES | INVESTIGATION WAS DONE AND IT WAS DISCOVERED THAT GAS CONTROL -SCADA SYSTEM COULD NOT CONFIRM OR SEE THE GAS PRESSURE CHANGES DUE TO A COMMUNICATION LOSS WITH WAKITA STATION AT THE TIME OF THE ESD. ONCE NOTIFIED OF THE INCIDENT ALL PROCEDURES WERE FOLLOWED. | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | YES |  |  | YES | [30 empty] | YES | ORIFIACE TIMER WAS NOT ALLOWING ENOUGH TIME FOR THE VALVE TO FULLY CLOSE | [161 empty] | DAVID COOMES | PIPELINE COMPLIANCE ENGINEER | david.coomes@sscgp.com | 2708524391 |  |  |  |  | DAVID SINCLAIR | PIPELINE COMPLIANCE MANAGER | 2708524424 | david.l.sinclair@sscgp.com | AT 10:00 ON 12/16/2014 SSC GAS CONTROL RECEIVED A CALL FROM SSC FIELD OPERATIONS STATING THERE MAY BE AN ISSUE AT THE WAKITA STATION, POSSIBLE ESD. THE FIELD OPERATOR WAS NEAR BY AND GOING TO INVESTIGATE. AT 10:00 SSC GAS CONTROL LOST COMMUNICATIONS WITH WAKITA STATION AND BEGAN CONTACTING THE COMMUNICATIONS DEPARTMENT TO CORRECT THE ISSUE. AT 10:06 SSC GAS CONTROL BEGAN RECEIVING LOW ALARMS FOR THE BLACKWELL/GUYMON, LINE N. AT 10:08 THE LOCAL PSAP AND THE LOCAL OPERATOR WAS NOTIFIED OF THE ALARMS/ISSUE. AT 10:43 OPERATIONS WAS ON SITE AND WORKING ON A MAINLINE VALVE THAT WAS STUCK OPEN LEAVING THE ESD VALVE TO CONTINUE BLOWING MAINLINE GAS PRESSURE. AT 10:56 THE MAINLINE VALVE WAS CLOSED AND THE GAS HAD STOPPED BLOWING.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150005 | 16734 | 2015-01-20 10:06 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2014-12-29 22:45 | 2014 |  |  | 43.6734 | -94.5909 | 1104518 | 2014-12-30 01:43 |  | NATURAL GAS |  | 13900 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | NORTHERN BORDER REGULATORS WERE MANUALLY SET TO A LOWER SET POINT. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-12-29 22:48 | 2014-12-29 23:20 | ONSHORE | MN | 56181 | WELCOME | MARTIN | MILEPOST | STA 0+00 | NORTHERN BORDER INTERCONNECT; WELCOME INTERCONNECT | MNB91501 NBPL WELCOME INTERCONNECT | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2007 |  | CARBON STEEL |  | OTHER | [8 empty] | THE 8-INCH ANDERSON GREENWOOD RELIEF OPENED WHEN THE NORTHERN BORDER DELIVERY PRESSURE REACHED 894 PSIG. | CLASS 1 LOCATION | NO |  | 248 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 52862 | 35272.1926444834 | 1500 | 1659.23321452654 | 3000 | 3318.46642905308 | 0 | 0 |  |  | 57362 | 38853.1791949154 | 40249.892288063 | [8 empty] | 894 |  | 800 | 192.619(A)(2) |  |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PROBABLY CAUSE IS A FAILURE OF NORTHERN BORDER PIPELINE REGULATORS WHICH ARE NOT MONITORED BY NORTHERN NATURAL GAS SCADA. NORTHERN NATURAL SCADA POINTS ARE DOWNSTREAM OF THE REGULATORS ON NORTHERN NATURAL EQUIPMENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [10 empty] | YES | YES | [176 empty] | JOHN A. GORMLEY | SR. CORROSION SPECIALIST | john.gormley@nngco.com | 402-398-7494 |  |  |  |  | THOMAS CORRELL | DIRECTOR OF PIPELINE SAFETY AND RISK | 402-398-7715 | thomas.correll@nngco.com | AT APPROXIMATELY 22:45 ON 29 DECEMBER 2014, AN 8-INCH ANDERSON-GREENWOOD RELIEF VALVE OWNED BY NORTHERN NATURAL GAS COMPANY OPENED ON NORTHERN'S 12-INCH-DIAMETER NBPL/WELCOME INTERCONNECT PIPING. APPARENTLY, NBPL EXPERIENCED SOME REGULATOR ISSUES THAT CAUSED FLOWS TO INCREASE AND THE PRESSURE TO EXCEED THE 830 PSIG SET POINT. NORTHERN BELIEVES NBPL EXPERIENCED TWO REGULATOR FAILURES AS THE RELIEF HAS SUFFICIENT CAPACITY TO PROTECT THE 800 PSIG MAOP IN A SINGLE REGULATOR FAILURE MODE; THE PRESSURE IN THE 800 PSIG MAOP MNB91501 LINE REACHED 894 PSIG FOR A BRIEF PERIOD EXCEEDING THE MAOP PLUS ALLOWABLE BUILDUP BY 14 PSIG. CALCULATIONS INDICATE IT WOULD TAKE TWO REGULATORS TO FAIL TO REACH THIS PRESSURE WITH THE RELIEF WIDE OPEN. MOREOVER, THE PIPELINE PRODUCES A HOOP STRESS OF 39% SMYS AT ITS 800 MAOP. THE HOOP STRESS WAS CALCULATED AS 42% AT THE OVERPRESSURE CONDITION, WHICH IS WELL BELOW THE ALLOWABLE STRESS FOR PIPE IN THIS LOCATION. THIS EVENT RESULTED IN A REPORTABLE INCIDENT BECAUSE 13.9 MMCF OF NATURAL GAS WAS LOST. ACCORDING TO 191.23(B)(2), A SRC SHOULD NOT BE REQUIRED SINCE THE EVENT RESULTS IN AN INCIDENT BEFORE THE DEADLINE FOR FILING A SAFETY RELATED CONDITION REPORT. NORTHERN BORDER PIPELINE CURRENTLY IS OPERATING ITS REGULATORS AT A REDUCED PRESSURE AND VOLUME UNTIL THE PROBABLE CAUSE CAN BE DETERMINED. THE PROBABLE CAUSE WAS A FAILURE OF CONTROL VALVES OWNED AND OPERATED BY NOTHERN BORDER PIPELINE COMPANY (NBPL). IT IS DIFFICULT TO ESTABLISH THE EXACT SEQUENCE OF EVENTS DUE TO THE LACK OF VALVE POSITION FEEDBACK ON NBPL'S SYSTEM, AND SINCE NO DETERMINATION HAS BEEN MADE WHY THEIR PNEUMATIC BACK-UP CONTROLLERS DID NOT OVERRIDE THEIR DIGITAL CONTROL LOOP TO TAKE OVER CONTROL OF THE PRESSURE. IT IS CLEAR, HOWEVER, THAT NBPL FAILED TO CONTROL PRESSURE TO THE POINT WHERE PRESSURE INCREASED TO CAUSE NORTHERN'S RELIEF VALVE TO VENT. NBPL DID INDICATE BOTH OF THEIR CONTROL VALVES WERE AT 96% OPEN.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150006 | 16618 | 2015-01-20 10:16 | ORIGINAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2015-01-03 02:51 | 2015 |  |  | 32.0823 | -94.2014 | 1104781 | 2015-01-03 03:40 |  | NATURAL GAS |  | 3406 | 789 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-01-03 02:37 | 2015-01-03 03:59 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-01-03 02:37 | 2015-01-03 03:59 | ONSHORE | TX | 75633 | CARTHAGE | PANOLA | MILEPOST | 0 | CARTHAGE JUNCTION | INDEX 816 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | OTHER | COMPRESSOR STATION YARD |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 1981 |  | CARBON STEEL |  | OTHER | [8 empty] | EMERGENCY SHUTDOWN OF COMPRESSOR STATION | CLASS 1 LOCATION | NO |  | 907 |  | NO | NO | NO |  | 0 | 0 | 2517 | 2750.80527267536 | 10865 | 9717.28873239437 | 0 | 0 | 360 | 393.440563433901 | 0 | 0 |  |  | 13742 | 11517.6462655569 | 12861.5345685036 | [8 empty] | 1079 |  | 1333 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | STATION ESD ACTIVATED DUE TO AN EXTERNAL INFLUENCE (LIGHTNING). | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [52 empty] | LIGHTNING |  |  | SECONDARY IMPACT SUCH AS RESULTING NEARBY FIRES |  |  | NO | [306 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 270-688-6357 | 270-688-6948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 270-688-6361 | jeff.mcmaine@bwpmlp.com | EMERGENCY SHUT-DOWN ACTIVATED AS A RESULT OF A LIGHTNING STRIKE ACTIVATING THE RECIP FIRE EYES.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150007 | 16622 | 2015-01-22 09:34 | ORIGINAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2015-01-07 09:08 | 2015 |  |  | 37.2965 | -87.3143 | 1105051 | 2015-01-07 09:45 |  | NATURAL GAS |  | 9798 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | VALVE VENTING GAS DID NOT CAUSE FACILITY SHUT DOWN. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-01-07 09:08 | 2015-01-07 09:08 | ONSHORE | KY | 42325 | BREMEN | MUHLENBERG | MILEPOST | 18.6313 | MIDLAND 3 | SLAUGHTERS- MIDLAND 30" | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ABOVEGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2005 |  | CARBON STEEL |  | OTHER | [8 empty] | VALVE VENTING TO ATMOSPHERE | CLASS 1 LOCATION | NO |  | 218 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 31488 | 28161.8028169014 | 500 | 546.445226991529 | 0 | 0 | 0 | 0 |  |  | 31988 | 29447.4524964578 | 28708.2480438929 | [8 empty] | 800 |  | 1000 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LOCAL OPERATING PERSONNEL DETERMINED THE CAUSE WAS WEATHER-RELATED. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | NO | [306 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 270-688-6357 | 270-688-6948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 270-688-6361 | jeff.mcmaine@bwpmlp.com | AN OPERATOR EMPLOYEE HEARD GAS VENTING IN COMPRESSOR STATION YARD. THE SOURCE WAS AN ESD BLOW DOWN VALVE. A DOWNSTREAM VALVE WAS CLOSED TO STOP THE RELEASE. THE ESD PNEUMATIC CONTROL VALVE THAT INITIATES THE VALVE THAT WAS VENTING WAS REMOVED AND INSPECTED, THEN REBUILT WITH THE MANUFACTURER'S REPAIR KIT. THE VALVE WAS PLACED BACK INTO SERVICE AND MONITORED FOR PROPER OPERATION.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150008 | 16667 | 2015-01-22 18:18 | SUPPLEMENTAL FINAL | 31705 | KATY STORAGE & TRANSPORTATION LP | 20329 STATE HIGHWAY 249 SUITE 500 | HOUSTON | TX | 77070 | 2014-12-23 10:46 | 2014 |  |  | 29.7516 | -95.8038 | NRC NOTIFICATION NOT REQUIRED |  |  | NATURAL GAS |  | 0.19 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-12-23 10:46 | 2014-12-23 13:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-12-23 10:46 | 2014-12-23 10:46 | ONSHORE | TX | 77494 | Not Within a Municipality | FORT BEND COUNTY | MILEPOST | KATY FACILITY | KATY STORAGE AND TRANSPORTATION FACILITY | KATY GAS STORAGE FACILITY | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | INSTRUMENTATION | [38 empty] | 2014 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | PLC | OTHER | [8 empty] | DURING MAINTENANCE ON THE PLC, THE PLC WENT INTO FAULT MODE WHICH CAUSED IT TO ESD THE FACILITY. | CLASS 3 LOCATION | YES | METHOD2 | 304 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 581 | 387.672504378284 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 581 | 401.9176882662 | 387.672504378284 | [8 empty] | 1050 |  | 1250 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [5 empty] | YES | AS STATED PREVIOUSLY, MAINTENANCE ACTIVITIES ON THE PLC, RESULTED IN A FACILITY ESD WHICH INDIRECTLY AFFECTED CONTROL ROOM OPERATIONS, PROCEDURES AND CONTROLLER RESPONSES. | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | MAINTENANCE ACTIVITIES ON THE PLC CAUSED A FAULT WHICH RESULTED IN A FACILITY ESD. | [147 empty] | SHERRI PEEBLES | DIRECTOR EHS | sherri.peebles@enstorinc.com | 281-374-3081 | 281-374-3051 |  |  |  | ZARIN IMAM | CHIEF REGULATORY OFFICER | 281-379-7420 | zarin.imam@iberdrolaren.com | ON DECEMBER 23, 2014, AT 10:46 AM, THE ENSTOR KATY GAS STORAGE FACILITY WAS ON INJECTION MODE USING TWO COMPRESSORS TO INJECT NATURAL GAS INTO THE RESERVOIR VIA 3 STORAGE WELLS AND 2 COMPRESSORS. ENSTOR PERSONNEL WERE PERFORMING MAINTENANCE ON THE PLC WHEN A LINE OF LOGIC (WHICH CONTAINED A TYPO) WAS SAVED TO THE NEW MASTER CONTROL CENTER (MCC) PLC. THIS CAUSED A PLC FAULT WHICH IN TURN CAUSED THE FACILITY TO ESD, AS DESIGNED. THIS ESD CORRECTLY ACTED TO FULLY BLOCK AND BLEED AND FLARE-TO-VENT, HOWEVER A CONTROL VALVE ON THE VENT SIDE FAILED TO OPEN CAUSING AN OVERPRESSURE EVENT WHICH RELIEVED VIA A PRESSURE RELIEF VALVE, AS DESIGNED. ENSTOR RESPONDED TO PUBLIC INQUIRIES REGARDING THE GAS RELEASE AND RESULTING NOISE. THESE CALLS WERE FROM THE PUBLIC, REGULATORS AND FIRST RESPONDERS. CALLS REPORTING SMOKE AND FIRE WERE EXPLAINED TO BE ONLY LOUD NOISE, DUST AND DEBRIS FROM THE PSV LINE. A PLANT INVESTIGATION PROCESS WAS INITIATED AND COMPLETED. THE ORIGINAL CAUSE WAS DETERMINED TO BE A FAULT IN THE PLC. UPON INVESTIGATING WHY THE FLARE/VENT LINE HAD NOT RELEASED, IT WAS DISCOVERED THAT THE VENT BLOCK VALVE HAD FAILED TO OPEN CAUSED BY A FAULTY VERSA VALVE (NV-105B). THE FAULT WAS IMMEDIATELY CLEARED AND CORRECTED IN THE PLC WITH CORRECT LOGIC, AND THE VERSA VALVE WAS REPLACED. THIS EVENT DOES NOT MEET THE INCIDENT REPORTING REQUIREMENTS AS DEFINED IN 49 CFR 191.3.1(I), 191.3.1(II), 191.3.1(III), OR 191.3. THIS INCIDENT REPORT HAS BEEN COMPLETED AND SUBMITTED AT THE REQUEST OF PHMSA SOUTHWEST REGION DUE TO A CALL FROM A LOCAL RESIDENT WHO LIVES CLOSE TO THE KATY GAS STORAGE FACILITY. THE TOTAL RELEASE TIME WAS APPROXIMATELY 40 SECONDS WITH AN ESTIMATED RELEASE VOLUME OF 197,000 SCF OF NATURAL GAS.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150009 | 16730 | 2015-01-23 08:45 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2014-12-24 21:12 | 2014 |  |  | 36.8665 | -97.9308 | 1104546 | 2014-12-30 11:28 |  | NATURAL GAS |  | 1890 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-12-24 21:38 | 2015-01-30 20:53 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-12-24 21:12 | 2014-12-24 21:38 | ONSHORE | OK | 73771 | WAKITA | GRANT | SURVEY STATION NO. | 150/10321+78 | WAKITA STATION - LINE N | OKLAHOMA HUGOTON 26" | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 26 |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | PULSATION BOTTLE OR DRIP/DRIP COLLECTION DEVICE | [38 empty] | 1965 |  | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 73 | 23 |  | CLASS 1 LOCATION | NO |  | 236 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 5178 | 3455.02276707531 | 58700 | 64931.3264618052 | 300 | 331.846642905308 | 0 | 0 |  |  | 64178 | 33539.4975277311 | 68718.1958717858 | [8 empty] | 630 |  | 765 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | GENERAL CORROSION |  | YES | YES |  |  | YES | AMORPHOUS TAR COMPOUNDS | YES |  | YES | THE ANALYSIS SHOWS THE PRESENCE OF ELEMENTAL SULFUR (37.083MIN), POSSIBLY INDICATIVE OF SPENT SULFUR SCAVENGER AND THE PRESENCE OF TRIETHYLENE GLYCOL (22.991M, 13.253M, 26.361M) AND ALKANES. | YES |  | YES |  | YES | THIS WAS THE DRIP UNDER THE SCRUBBER | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [313 empty] | DAVID COOMES | PIPELINE COMPLIANCE ENGINEER | david.coomes@sscgp.com | 2708524391 |  |  |  |  | DAVID SINCLAIR | PIPELINE COMPLIANCE MANAGER | 2708524424 | david.l.sinclair@sscgp.com | AT 21:12 ON DECEMBER 24, 2014, SSC OPERATOR CALLED GAS CONTROL AND REPORTED A POSSIBLE RELIEF VALVE BLOWING AT OR NEAR THE WAKITA STATION. SSC GAS CONTROL RECEIVED TWO LOW RATE OF CHANGE ALARMS AT WAKITA STATION AT THE SAME TIME. PSAP WAS NOTIFIED AND PRESSURE CONTINUED TO FALL IN THE AREA. AT 21:38 SSC GAS CONTROL WAS NOTIFIED THAT LOCAL OPERATIONS DISCOVERED A LINE UNDER THE SEPARATOR TANK LEAKING. OPERATIONS HAD CLOSED THE SUCTION AND DISCHARGE VALVES TO THE STATION AND ISOLATED BOTH UNITS. NO HORSEPOWER WAS RUNNING AT THE TIME. THIS WAS NOT A RELIEF VALVE BLOWING. BECAUSE THE STATION WAS NOT NEEDED AND THE AFFECTED PIPELINE WAS ISOLATED THE ISSUE WAS CONTAINED AND THERE WAS NOT ANY IMMEDIATE THREAT. IT WAS DETERMINED THAT THE LEAK WOULD BE INVESTIGATED AT A LATER DATE TO DETERMINE THE CAUSE. WHEN SSC OPERATIONS BEGAN INVESTIGATING IT WAS DETERMINE THAT THE REPAIR OF THE LEAK COULD BE EXTENSIVE AND THE NRC WAS NOTIFIED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150010 | 16909 | 2015-01-23 17:56 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2014-12-23 04:00 | 2014 |  |  | 39.5658 | -121.6889 | 1104165 | 2014-12-23 15:00 |  | NATURAL GAS |  | 0.01 | 0.24 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-12-24 13:00 | 2014-12-28 01:40 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-12-23 04:00 | 2014-12-23 04:00 | ONSHORE | CA | 95965 | OROVILLE | BUTTE | MILEPOST | MP 31.64 | L-50A | MP 31.64 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 84 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6.625 |  | 0.188 | 28000 | UNKNOWN | LAP WELDED |  | US STEEL | ASPHALT | [28 empty] | 1928 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 92 |  | NO | NO | NO |  | 0 | 0 | 2 | 2.21231095270205 | 0 | 0 | 100000 | 110615.547635103 | 0 | 0 | 0 | 0 |  |  | 100002 | 50776.4706675658 | 110617.759946055 | [8 empty] | 380 |  | 400 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 740 | NO | [5 empty] | YES | PRESSURE CONTROL FITTINGS, PERMANENT LAUNCHER AND RECEIVER AND ASSOCIATED VALVES | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PG&E PERSONNEL IDENTIFIED THE MINOR LEAK | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING | [6 empty] | YES | STILL UNDER INVESTIGATION |  |  | YES |  |  |  | YES | YES | 1966 |  | YES |  |  | YES |  |  |  | 2015 |  | YES | [190 empty] | YES |  |  | YES | [24 empty] | 2014 | [35 empty] | YES | 2014 | 600 | NO | [13 empty] | NO | [63 empty] | STEPHEN RAMOS | COMPLIANCE ENGINEER | s3rc@pge.com | 925-328-6107 |  |  |  |  | LARRY DENISTON | MANAGER OF GAS OPERATIONS REGULATORY COMPLIANCE | 925-328-5756 | lcd1@pge.com | ON DECEMBER 23, 2014 AT APPROXIMATELY 0400 HOURS, PG&E CREWS WERE PERFORMING A ROUTINE LEAK INSPECTION AND REPAIR ON A NON-HAZARDOUS LEAK ON PG&E'S 6-INCH TRANSMISSION LINE (L-50A NEAR MP 31.64) ON THE SOUTHBOUND SHOULDER OF HIGHWAY 99, SOUTH OF SKILLIN LANE IN OROVILLE. DURING THE COURSE OF THE LEAK INVESTIGATION, THE LEAK CONTINUED TO MIGRATE THROUGH THE EXCAVATION AND WAS UPGRADED TO A HAZARDOUS LEAK, WHICH REQUIRED IMMEDIATE REPAIR. BY 2145 HOURS ON DECEMBER 23, A 10% PRESSURE REDUCTION WAS TAKEN ON L-50A WHILE PG&E CREW INVESTIGATED THE LEAK. ADDITIONAL PRESSURE REDUCTION WAS TAKEN ON L-50A TO LOWER LINE PRESSURE BELOW THE MAXIMUM WELDING PRESSURE OF 254 PSIG AT APPROXIMATELY 0400 HOURS ON DECEMBER 24. BY 1030 HOURS ON DECEMBER 24, PRESSURE CONTROL FITTINGS WERE INSTALLED AT MP 31.65 AND MP 31.79. PG&E ISOLATED APPROXIMATELY 740 FEET OF PIPE. PG&E IDENTIFIED EXTERNAL CORROSION WITH A PIN-HOLE LEAK. FURTHER ANALYSIS IS CURRENTLY BEING CONDUCTED ON THE PIPE. PG&E WILL SUPPLEMENT THIS REPORT AS INFORMATION BECOMES AVAILABLE. BY DECEMBER 27 1530 HOURS, PG&E REMOVED A 66 FOOT SECTION OF PIPE. BY 0140 HOURS ON DECEMBER 28, REPAIRS WERE COMPLETED (A NEW SECTION OF HYDRO-TESTED PIPE WAS INSTALLED) AND PG&E BEGAN RESTORING L-50A TO NORMAL OPERATING PRESSURE. IT IS ESTIMATED THAT LESS THAN 3MMCF OF NATURAL GAS WAS RELEASED. THERE WERE NO INJURIES, NO FATALITIES, NO IGNITION AND NO MEDIA ASSOCIATED WITH THIS INCIDENT. CALTRANS AND CALIFORNIA HIGHWAY PATROL WERE OBSERVED ON SCENE THROUGH THE COURSE OF THE WORK. NO EVACUATIONS WERE PERFORMED AND TRAFFIC ON HIGHWAY 99 WAS REDUCED TO ONE LANE IN BOTH DIRECTIONS NEAR THE LEAK. THIS IS A CLASS 1 LOCATION. NO CUSTOMERS EXPERIENCED GAS SERVICE INTERRUPTION. AT 1400 HOURS ON DECEMBER 23, IT WAS DETERMINED THAT DAMAGES WOULD LIKELY EXCEED $50,000, THEREFORE THE INCIDENT WAS REPORTED TO THE DOT AND CPUC.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150011 | 16630 | 2015-01-29 11:21 | ORIGINAL FINAL | 22655 | WBI ENERGY TRANSMISSION, INC. | 1250 WEST CENTURY AVENUE | BISMARCK | ND | 58503 | 2014-12-30 06:21 | 2014 |  |  | 46.704 | -103.9661 | 1104536 | 2014-12-30 07:19 |  |  |  | 0 | 111 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-12-30 09:10 | 2014-12-30 16:40 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-12-30 03:45 | 2014-12-30 04:52 | ONSHORE | ND | 58632 | Not Within a Municipality | GOLDEN VALLEY | SURVEY STATION NO. | 0+00 | GOLVA - BEACH TAKE-OFF | GOLVA - BEACH LATERAL | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 2013 |  | CARBON STEEL |  | OTHER | [8 empty] | THE REGULATOR SUPPLYING GAS TO THE LATERAL FROZE OFF. | CLASS 1 LOCATION | NO |  | 65 |  | NO | NO | NO |  | 0 | 0 | 475 | 525.423851266737 | 0 | 0 | 300 | 331.846642905308 | 4925 | 5447.8157210288 | 180000 | 199107.985743185 | THE LDC HAD TO RELIGHT 900 HOMES. |  | 185700 | 94290.020229265 | 205413.071958386 | [8 empty] | 20 |  | 400 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | OTHER | LDC PERSONNEL |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO SCADA POINTS EXISTED ON THE LATERAL INVOLVED IN THE INCIDENT AT THE TIME OF THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS | ,, | NO | [306 empty] | KENT KAHL | DOT COMPLIANCE SUPERVISOR | kent.kahl@wbienergy.com | 406-359-7222 | 406-359-7244 |  |  |  | KENT KAHL | DOT COMPLIANCE SUPERVISOR | 406-359-7222 | kent.kahl@wbienergy.com | ON 12/30/14 THE REGULATORS SUPPLYING GAS TO THE GOLVA-BEACH LATERAL FROZE OFF CAUSING SERVICE TO BE LOST TO THE TOWNS OF SENTINEL BUTTE, ND, BEACH, ND, AND WIBAUX, MT. WBI'S GAS CONTROL RECEIVED A CALL FROM LDC PERSONNEL NOTIFYING WBI THAT THE LDC HAD RECEIVED A LOW OUTLET PRESSURE ALARM AT THE BEACH TBS. AT THE TIME OF THE INCIDENT, WBI DID NOT HAVE ANY SCADA POINTS ON THE GOLVA-BEACH LATERAL. WBI RELIES ON LDC ALARMING FOR THIS LATERAL SYSTEM. WBI PERSONNEL WERE DISPATCHED TO THE REGULATOR STATION WHICH IS APPROXIMATELY 2 MILES SOUTH OF GOLVA, ND. WHEN WBI PERSONNEL ARRIVED AT THE REGULATOR STATION, THE OUTLET OF THE REGULATOR STATION SUPPLYING GAS TO THE GOLVA-BEACH LATERAL WAS APPROXIMATELY 20 PSI. WBI PERSONNEL BYPASSED THE REGULATOR STATION AND WERE ABLE TO MAINTAIN SERVICE TO GOLVA, ND BUT LOST SERVICE TO SENTINEL BUTTE, ND, BEACH , ND, AND WIBAUX, MT. THE REGULATOR STATION WAS PUT INTO SERVICE IN 2013. NO PROBLEMS WERE ENCOUNTERED DURING THE WINTER OF 2013, BUT THE BUILDING HEATER WAS MOVED TO A NEW LOCATION WITHIN THE BUILDING IN 2014. MOVING THE HEATER MAY HAVE CREATED CONDITIONS THAT MADE THE REGULATORS MORE SUSCEPTIBLE TO FREEZING OFF, EVEN THOUGH PIPELINE QUALITY GAS WAS FLOWING THROUGH THE STATION. SINCE THE INCIDENT, WBI HAS INSTALLED A PRESSURE TRANSDUCER AT THE REGULATOR STATION WHICH GIVES THE ABILITY TO MONITOR PRESSURE ON THE GOLVA-BEACH LATERAL. IN ADDITION, WBI ALSO INSTALLED REGULATOR PILOT HEATERS AND A SECONDARY HEATER WITHIN THE REGULATOR STATION BUILDING.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20150012 | 16632 | 2015-01-29 15:27 | ORIGINAL FINAL | 31485 | ENBRIDGE OFFSHORE (GAS GATHERING) L.L.C. | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2015-01-04 17:00 | 2015 |  |  | 28.3157 | -91.9094 | 1104865 | 2015-01-04 18:13 |  | NATURAL GAS |  | 5150 | 1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-01-07 07:00 | 2015-01-14 14:34 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-01-04 17:06 | 2015-01-05 08:00 | OFFSHORE | [28 empty] | 220 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SMI | 128 | PLATFORM | INTERSTATE | OFFSHORE PLATFORM, INCLUDING PLATFORM-MOUNTED EQUIPMENT AND PIPING | OTHER | [37 empty] | 2" BYPASS PIPING AROUND VALVE | 1997 |  | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 490 |  | NO | NO | NO |  | 0 | 0 | 1475 | 1612.01341962501 | 19146 | 17123.5352112676 | 60000 | 65573.4272389835 | 405000 | 442620.633863139 | 10000 | 10928.9045398306 | HELICOPTER AND LABOR |  | 495621 | 256783.842414916 | 537858.514272846 | [8 empty] | 1300 |  | 1975 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | OFFSHORE GATHERING | YES | NO | NO | NO | NO | OTHER | GAS CONTROL FROM ANOTHER OPERATOR NOTIFIED OUR GAS CONTROL |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA WAS NOT IN OPEARION BECAUSE THE PLATFORM'S GENERATOR HAD GONE DOWN. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  |  | YES | [7 empty] | YES |  |  |  | NO | [11 empty] | YES | YES | [335 empty] | GREGG JOHNSON | MANAGER COMPLIANCE | gregg.johnson@enbridge.com | 713-353-6369 |  |  |  |  | GREGG JOHNSON | MANAGER COMPLIANCE | 713-353-6369 | gregg.johnson@enbridge.com | ON 1-4-15 1706 HRS. ' ENBRIDGE GAS CONTROL RECEIVED A PHONE CALL FROM TRUNKLINE GAS / SEA ROBIN CONTROL CENTER REGARDING A 2' BYPASS VALVE THAT HAS A LEAK UNDERNEATH THE PLATFORM AND IS VENTING GAS TO THE ATMOSPHERE. ENB. GAS CONTROL NOTIFIED ENB. OPERATIONS OF THE SITUATION ON SMI-128. OPERATION CONFIRMED WITH THE SMI 128 PLATFORM OPERATORS THAT THERE WAS A LEAK ON THE 2' BYPASS LINE AROUND THE16' ESD VALVE ON INCOMING RISER OWNED BY ENBRIDGE. 1-5-2015 ' ENBRIDGE REPRESENTATIVE DEPARTED FOR SMI-128 FROM HOUMA VIA HELICOPTER. ARRIVED AND CONFIRMED THE LEAK AND LOCATION. REVIEWED WITH PLATFORM OPERATOR THE PLAN FOR ISOLATION AND REPAIR 1-6-2015 ' 0345 HRS. DIVE VESSEL DEPARTED PORT WITH DIVE CREW FOR SSV SHUT IN ' 2300 HRS. DIVE VESSEL ARRIVED ON LOCATION AND DROPPED ANCHORS AND PROCEEDED WITH VALVE CLOSURE 1-7-2015 ' ~0700 HRS. 16' SSV WAS CLOSED AND PRESSURE WAS REDUCED ON THE 16' PIPELINE. ONCE PRESSURE WAS REDUCED THE PIPELINE WAS SECURED AND PURGED WITH NITROGEN. 1-8-2015 ' CONSTRUCTION CREW REMOVED 2' PIPING AND REPLACED WITH NEW PIPING. REPAIRS WERE COMPLETED, X-RAY WAS COMPLETED ON FIELD WELD AND PIPELINE WAS TURNED OVER TO OPERATION FOR RE-PRESSURIZATION. 1-9-2015 ' CONTINUE TO REPRESSURE 16' PIPELINE TO LINE PRESSURE. 1-12-2015 ' LINE REPRESSURED WAITING ON DIVE VESSEL 1-14-2015 ' 1415 DIVERS ON LOCATION AND OPENING VALVE ONCE VALVE WAS FULLY OPENED PIPELINE WAS BACK IN SERVICE
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150013 | 16699 | 2015-02-04 16:03 | SUPPLEMENTAL FINAL | 38987 | KINETICA ENERGY EXPRESS LLC | 1001 MCKINNEY STREET, SUITE 900 | HOUSTON | TX | 77002 | 2015-01-10 11:30 | 2015 |  |  | 29.3714 | -93.1557 | 1105323 | 2015-01-10 13:10 |  | NATURAL GAS |  | 120 | 388 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-01-10 11:30 | 2015-01-13 08:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-01-10 11:30 | 2015-01-10 11:30 | OFFSHORE | [28 empty] | 51 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST CAMERON | 180 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 20 |  | 0.469 | 52000 | L5 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | U.S. STEEL | COAL TAR | [28 empty] | 1974 | 1972 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO | NO |  | 0 | 0 | 1144 | 1250.26667935662 | 354 | 316.605633802817 | 235000 | 256829.256686019 | 15000 | 16393.3568097459 | 0 | 0 |  |  | 251498 | 126318.533906973 | 274789.485808924 | [8 empty] | 675 |  | 1273 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 46910 | NO | YES | [6 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | BSEE INSPECTOR WORKING IN THE AREA NOTICED BUBBLE ON THE WATERS SURFACE. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE WAS OPERATING AT APPROXIMATELY 50% OF MAOP WITH NO SUSPECTED CONTROLLER INVOLVEMENT. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  |  | YES | ENGINEERING REVIEW | [5 empty] | YES | MANUFACTURING DEFECT | [12 empty] | YES | [63 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | SUSIE RICHMOND | MANAGER OF PIPELINE COMPLIANCE AND TRAINING | susie.richmond@kineticallc.com | 985-290-4263 |  |  |  |  | SUSIE RICHMOND | MANAGER OF PIPELINE COMPLIANCE AND TRAINING | 985-209-4263 | susie.richmond@kineticallc.com | A BSEE INSPECTOR PERFORMING INSPECTIONS IN THE AREA IDENTIFIED BUBBLES ON THE WATER'S SURFACE. WE WERE CONTACTED BY THE AGENCY AND KINETICA DISPATCHED PERSONNEL TO THE LOCATION TO VERIFY COORDINATES. UPON VERIFICATION BY PERSONNEL AND TELEPHONE COORDINATION WITH THE OPERATIONS DIRECTOR, THE PIPELINE WAS IDENTIFIED AS BELONGING TO KINETICA ENERGY EXPRESS. AT THAT TIME THE VALVES WERE CLOSED AND LOCKED. A REPAIR CLAMP WAS PROCURED AND INSTALLED WITH OVERSIGHT BY A COMPANY INSPECTOR. THE PIPELINE REPAIR WAS TESTED AND RETURNED TO SERVICE IN ACCORDANCE WITH KINETICA PROCEDURES. SUPPLEMENTAL CREATED TO FINALIZE REPORT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150015 | 16902 | 2015-02-06 19:12 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2015-01-07 17:04 | 2015 |  |  | 35.1603 | -118.8042 | 1105278 | 2015-01-09 |  | NATURAL GAS |  | 4250 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | CLOSED VALVE BY REMOTELY LOWERING PRESSURE OF UPSTREAM REGULATOR SETPOINT | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-01-07 17:04 | 2015-01-07 17:45 | ONSHORE | CA | 93203 | ARVIN | KERN COUNTY | MILEPOST | 4-PLS | L-300B | MP 256.64 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2014 |  | CARBON STEEL |  | OTHER | [8 empty] | PRESSURE RELIEF VALVE UNINTENTIONALLY VENTED NATURAL GAS | CLASS 1 LOCATION | NO |  | 650 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 14000 | 12521.1267605634 | 5000 | 5464.45226991529 | 0 | 0 | 0 | 0 |  |  | 19000 | 15489.548438756 | 17985.5790304787 | [8 empty] | 720 |  | 757 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | REMOTELY CONTROLLED |  | NO |  | YES |  |  |  | YES | A PIG LAUNCHER IS INSTALLED AT PLS-4, WHICH ALLOWS INSPECTION ON L-300B BETWEEN MP 256.65-298.96 (PLS-4 TO PLS-5). HOWEVER, THE SECTION OF L-300B SOUTH OF PLS-4 IS NOT CURRENTLY PIGGABLE DUE TO LACK OF A LAUNCHER/RECEIVER AND PLUG VALVES REQUIRING REPLACEMENT. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA-RELATED EQUIPMENT OPERATED AS INTENDED | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [13 empty] | YES | [177 empty] | CHERYL DIZON | COMPLIANCE ENGINEER | c1dz@pge.com | 925-328-5721 |  |  |  |  | LARRY DENISTON | MANAGER OF GAS OPERATIONS REGULATORY COMPLIANCE | 925-328-5756 | lcd1@pge.com | ON JANUARY 7, 2015 AT 1704 HOURS IN ARVIN, AN 8-INCH PRESSURE RELIEF VALVE (AT PRESSURE LIMITING STATION,4-PLS OFF OF TRANSMISSION LINE L-300B) OPENED PRIOR TO REACHING ITS SET POINT OF 749 PSIG RESULTING IN AN UNINTENTIONAL RELEASE OF NATURAL GAS TO THE ATMOSPHERE. THE PRESSURE IN L-300B AT THE TIME THE RELIEF VALVE OPERATED WAS 720 PSIG. THE INCIDENT WAS IDENTIFIED ON PG&E'S SCADA SYSTEM. IN RESPONSE, PG&E GAS CONTROL REMOTELY LOWERED THE PRESSURE IN L-300B BY LOWERING THE SETPOINT OF THE UPSTREAM REGULATOR TO 675 PSIG, WHICH ALLOWED THE PRESSURE RELIEF VALVE TO CLOSE AT 1710 HOURS. PG&E PERSONNEL ARRIVED ON SCENE AT 1745 HOURS AND THE VALVE'S SET POINT OF 749 PSIG WAS TESTED AND VERIFIED. PG&E CONTRACTED A THIRD PARTY ENGINEERING FIRM TO PERFORM A ROOT CAUSE ANALYSIS AND PROVIDE RECOMMENDATIONS TO THE STATION. PG&E IMPLEMENTED SEVERAL MODIFICATIONS AND IS CURRENTLY IN THE DESIGN PHASE TO REBUILD PLS-4. PG&E INSPECTS AND CALIBRATES PRESSURE RELIEF VALVES (PRV) AS PART OF PG&E'S ROUTINE MAINTENANCE PROGRAM, WHICH IS DESIGNED TO ENSURE THE RELIABLE OPERATION OF THIS EQUIPMENT AT PG&E'S PRESSURE LIMITING STATIONS. NO CUSTOMERS LOST GAS SERVICE DURING THE INCIDENT. PRESSURE IN L-300B DID NOT EXCEED THE MAOP OF 757 PSIG. THERE WERE NO INJURIES, NO FATALITIES AND NO MEDIA OBSERVED ON SCENE DURING THE INCIDENT. ON JANUARY 9, 2015, IT WAS ESTIMATED THAT THE VOLUME OF GAS RELEASED EXCEEDED 3 MILLION CUBIC FEET (MMCF), THEREFORE THE INCIDENT WAS REPORTED TO THE NATIONAL RESPONSE CENTER AND THE CPUC. (PLEASE NOTE THAT THE RESPONSES TO PART E, QUESTIONS 5A, 5B, AND 5C OF THIS PHMSA 7100 REPORT ARE MERELY PLACEHOLDERS AND DO NOT APPLY. PG&E GAS CONTROL REMOTELY LOWERED THE PRESSURE IN L-300B BY LOWERING THE SETPOINT OF THE UPSTREAM REGULATOR, WHICH ALLOWED THE PRESSURE RELIEF VALVE TO CLOSE. THE PHMSA 7100 REPORT FORM DOES NOT ALLOW THESE FIELDS TO BE LEFT BLANK.)
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150016 | 16964 | 2015-02-09 18:20 | SUPPLEMENTAL FINAL | 2620 | COLUMBIA GULF TRANSMISSION, LLC | 700 LOUISIANA ST. SUITE 700 | HOUSTON | TX | 77002 | 2015-01-11 02:00 | 2015 |  |  | 37.8888 | -83.8627 | 1105361 | 2015-01-11 02:32 |  | NATURAL GAS |  | 12144 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE OPERATOR DID NOT FIND THAT THERE WAS A NEED TO SHUT IT DOWN | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-01-11 12:50 | 2015-01-11 12:50 | ONSHORE | KY | 40380 | STANTON | POWELL COUNTY | MILEPOST | LINE 100 DISC | STANTON COMPRESSOR STATION | 1SG-21 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1970 |  | CARBON STEEL |  | OTHER | [8 empty] | INADVERTENT ACTIVATION OF A RELIEF VALVE | CLASS 2 LOCATION | NO |  | 169 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 37889 | 33886.6408450704 | 0 | 0 | 315 | 344.260493004664 | 0 | 0 | NO OTHER ASSOCIATED COSTS DUE TO PROPERTY DAMAGE |  | 38204 | 35289.8438990595 | 34230.9013380751 | [8 empty] | 801 |  | 935 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | AN INADVERTENT ACTIVATION OF A RELIEF VALVE WAS IDENTIFIED TO BE THE PROBABLE CAUSE TO INITIATE THIS INCIDENT. THERE WERE NO INDICATIONS TO INITIATE A CONTROLLER'S INVESTIGATION. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | SUSPECT FOREIGN OBJECT (FROST) CONTRIBUTING TO THE RELEASE | [161 empty] | GEORGE HAMATY | ENGINEER | ghamaty@cpg.com | (304) 357-3728 | (304) 357-2252 |  |  |  | PERRY MICHAEL HOFFMAN | MANAGER | (304) 357-2548 | mikehoffman@cpg.com | ON JANUARY 11, 2015, STANTON COMPRESSOR STATION (CS) NIGHT SHIFT OPERATOR HEARD WHAT WAS NOTED TO BE A RELIEF VALVE (RV) VENTING MATERIAL INTO ATMOSPHERE. STANTON CS IS A TRANSMISSION FACILITY THAT IS OWNED, OPERATED AND MAINTAINED BY COLUMBIA GULF TRANSMISSION, LLC (COLUMBIA). THE FACILITY IS LOCATED IN THE TOWN OF STANTON IN POWELL COUNTY, KENTUCKY. THE STATION OPERATOR IDENTIFIED THE RV TO BE ON LINE 100 DISCHARGE PIPE. AFTER 25 MINUTES, THE OPERATOR WAS ABLE TO MANUALLY SECURE THE RV AND NO MATERIAL WAS NOTED TO BE VENTING INTO ATMOSPHERE THEREAFTER. INVESTIGATION INTO THIS INCIDENT WAS INITIATED THE FOLLOWING DAY WHERE IT INVOLVED A TEAM FROM COLUMBIA COMPRESSOR ENGINEERING SUPPORT AND COMPRESSOR OPERATIONS PERSONNEL. A CONTACT WITH THE RV ENGINEERING TECHNICAL SUPPORT WAS ESTABLISHED TO DETERMINE IF ANY HELP MAY BE PROVIDED TO DETERMINE THE PROBABLE CAUSE THAT LED TO THE INADVERTENT ACTIVATION OF THIS RV. THE RV ENGINEERING TECHNICAL SUPPORT INDICATED THAT BASED ON THE PROVIDED INFORMATION WHERE THE RV ACTIVATED BEFORE ACHIEVING THE SET POINT VALUE, IT WAS NOTED THAT IT MAY BE DUE TO THE PRESENCE OF FROST IN THE BODY OF THE RV THAT MAY HAVE INITIATED THIS UNINTENDED RELEASE. FURTHER INVESTIGATIONS ARE STILL ONGOING INTO THIS INCIDENT. THE FACILITY WAS RETURNED BACK TO SERVICE AFTER THE RV WAS BENCH TESTED AND EVALUATED WHERE ALL PERFORMED CHECKS DID NOT INDICATE OF ANY MALFUNCTIONS. HENCE, THE RV WAS RETURNED BACK INTO SERVICE. THE ROOT CAUSE ANALYSIS (RCA) REPORT FOR THIS INCIDENT IDENTIFIED THAT COLLECTED MOISTURE HAD SEEPED THROUGH A FAILED O-RING IN THE RV PISTON CAVITY. DUE TO THE REDUCED TEMPERATURE THAT WAS WIDESPREAD THROUGHOUT THE REGION (18 DEGREES F), THE COLLECTED MOISTURE FROZE, THENCE, FORCING THE RV TO UNSEAT AND RELEASING UNINTENTIONALLY MATERIAL INTO ATMOSPHERE. FOLLOW-UP ACTION ITEMS TO THE RCA REPORT WERE TO ENSURE THAT THE DRILLED VENT PASSAGE FOR THE SPRING CHAMBER OF THE RELIEF CONTROL CARTRIDGE SHOULD BE SEALED USING A SMALL AMOUNT OF GREASE SO THAT MOISTURE WILL NOT COLLECT IN THE CAVITY. VINTAGE RV ON THE DISCHARGE LINE OF CENTRIFUGAL COMPRESSORS WITH OBSOLETE SPARE PARTS, WILL BE REPLACED AND/OR PHASED-OUT FROM THE PIPELINE SYSTEM SUBJECT TO OPERATIONAL REQUIREMENTS. THIS WILL APPLY IF OVER PRESSURE PROTECTION AND OVER PRESSURE CONTROL STRATEGIES ARE IN PLACE WITH COMPREHENSIVE ENGINEERING ASSESSMENTS TO BE PERFORMED BEFORE ANY OF THESE STEPS ARE IMPLEMENTED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150017 | 33284 | 2015-02-11 14:57 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2015-01-14 06:22 | 2015 |  |  | 32.4692 | -89.9494 | 1105600 | 2015-01-14 07:03 |  | NATURAL GAS |  | 51085 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-01-14 07:35 | 2015-02-16 16:50 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 0 | 2015-01-14 06:29 | 2015-01-14 06:40 | ONSHORE | MS | 39042 | BRANDON | RANKIN | MILEPOST | 253.3 | INDEX 130 | KOSCUISKO 30" | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 41 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 |  | 0.375 | 52000 | 5LX-52 | FLASH WELDED |  | AO SMITH | COAL TAR | [28 empty] | 1952 | 1952 | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | THREE PIPE FRAGMENTS WERE CREATED DURING RUPTURE. | 1200 | 1 |  | CLASS 1 LOCATION | NO |  | 628 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 162961 | 145746.809859155 | 600720 | 656521.153516703 | 0 | 0 | 0 | 0 |  |  | 763681 | 452462.868658766 | 802267.963375858 | [8 empty] | 767 |  | 920 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 36115 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO ACTIONS WERE TAKEN BY CONTROLLER(S) TO INITIATE THIS INCIDENT. | [12 empty] | YES | 6 | 0 | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | YES | YES | [13 empty] | YES | HARD SPOT | [13 empty] | YES | HARD SPOT AND TYPE A SLEEVE FAILURE | [55 empty] | YES | YES |  |  | YES |  |  |  | 2011 |  | HARD SPOTS | [29 empty] | 2004 | [23 empty] | YES | 1974 | 1237 | NO | [13 empty] | NO | [63 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 270-688-6357 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 270-688-6497 | tina.baker@bwpipelines.com | THE FAILURE OF THE PIPELINE WAS THE RESULT OF HYDROGEN CRACKING IN A HARD SPOT THAT IS UNDERSTOOD TO HAVE BEEN PRODUCED IN THE PLATE USED TO MANUFACTURE THE PIPE BY A. O. SMITH. 2-19-16 UPDATED WITH RESTART DATE/TIME AND COST OF UNINTENTIONAL GAS LOSS AS REQUESTED BY PHMSA. FINAL REPORT TO FOLLOW WHEN WORK IS COMPLETE. 3-2-16 REVISED COST TO REFLECT ONLY THOSE COSTS DIRECTLY ASSOCIATED WITH THE INCIDENT AND NOT ADDITIONAL WORK THAT FOLLOWED. 2-5-2020: REVISED PER PHMSA REQUEST. CAUSE WAS CONFIRMED AS A HARD SPOT WITH A BRINELL HARDNESS GREATER THAN 300, THAT WAS GREATER THAN TWO (2) INCHES IN LENGTH, AND WAS PREVIOUSLY REINFORCED WITH A TYPE A SLEEVE. FOLLOWING PHMSA INVESTIGATION, GULF SOUTH ENTERED INTO A CONSENT AGREEMENT (CPF NO. 2-2015-1001S) WITH PHMSA SOUTHERN REGION. ALL REMEDIATION REQUIREMENTS HAVE BEEN SUBMITTED TO PHMSA SOUTHERN REGION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150018 | 16792 | 2015-02-11 15:31 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2015-01-27 14:00 | 2015 |  |  | 29.7697 | -92.9991 | 1106719 | 2015-01-27 14:40 |  | NATURAL GAS |  | 500 | 37148 | 0.1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-01-13 14:50 | 2015-02-01 13:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-01-09 17:30 | 2015-01-09 18:00 | ONSHORE | LA | 70643 | GRAND CHENIER | CAMERON | MILEPOST | A767-MLV3 | A767-3-10 (MAINLINE VALVE 3) | 560161 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 100 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | MAINLINE | GATE |  | ROCKWELL INTERNATIONAL |  |  |  | UNKNOWN | UNKNOWN | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | VITON | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 806 |  | NO | NO | NO |  | 5000 | 5464.45226991529 | 107729 | 117735.995717141 | 1450 | 1296.83098591549 | 15000 | 16393.3568097459 | 10000 | 10928.9045398306 | 1200000 | 1311468.54477967 | ENVIRONMENTAL ANALYTICAL; TRANSPORTATION AND DISPOSAL - IMPACTED SOIL AND WATER |  | 1339179 | 672437.046526103 | 1463288.08510222 | [8 empty] | 740 |  | 1300 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | AUTOMATIC | 159421 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SMALL SIZE OF THE LEAK AND MINIMAL AMOUNT OF GAS LEAKING AROUND THE VALVE | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | SEAL (NOT COMPRESSOR SEAL) OR PACKING | [5 empty] | YES | [8 empty] | YES | [165 empty] | ROGER R. STREET | FIELD COMPLIANCE SPECIALIST | No Email Address | 6154655123 |  |  |  |  | ROGER STREET | FIELD COMPLIANCE SPECIALIST | 6154655123 | roger_street@transcanada.com | ON 9 JANUARY 2015 AT APPROXIMATELY 17:30 CST, A PIPELINE TECHNICIAN NOTIFIED TC OFFSHORE (TCO) AREA MANAGER OF A GAS AND CONDENSATE LEAK AT MAINLINE VALVE 3 (767-3-10) ON THE TC OFFSHORE 767 LATERAL NEAR THE GRAND CHENIER LIQUID HANDLING FACILITY. GAS WAS OBSERVED BUBBLING UP AROUND THE NECK OF THE BELOW GRADE 30-INCH BLOCK VALVE AND CONDENSATE WAS OBSERVED AT THE GROUND SURFACE OF THE VALVE WITHIN THE VALVE YARD. INITIAL CLEANUP ACTIONS TO CONTAIN CONDENSATE INCLUDED DISPATCHING A VACUUM TRUCK AND THE DEPLOYMENT ABSORBENT PADS AND BOOM. THE SITE WAS MONITORED DAILY WITH ADDITIONAL ABSORBENT MATERIALS DEPLOYED AS NECESSARY. ON 12 JANUARY, A FIELD TECHNICIAN REPORTED THAT SHEEN HAD MIGRATED FROM THE VALVE YARD TO ADJACENT PROPERTY OUTSIDE OF THE YARD VALVE FENCING CREATING SHEEN ON THE GROUND AND IN STANDING WATER. A TRANSCANADA ENVIRONMENTAL SPECIALIST REPORTED THE RELEASE TO LOUISIANA STATE POLICE (LSP), INCIDENT #15-00155, AS A RELEASE OF CONDENSATE FROM THE VALVE SITE. AFTER INVESTIGATING AND EVALUATING OPTIONS TO REPAIR THE VALVE, IT WAS DECIDED TO ISOLATE THE 767 LATERAL FROM WEST CAMERON 171 TO THE GRAND CHENIER LIQUID HANDLING FACILITY AND REDUCE THE PRESSURE TO ALLOW FURTHER INVESTIGATION. ON 13 JANUARY, THE PIPELINE SECTION WAS ISOLATED AND THE LINE PRESSURE WAS REDUCED BY FLARED BLOW DOWN AT GRAND CHENIER LIQUID HANDLING FACILITY. PRESSURE REDUCTION AND FLARING CONTINUED UNTIL 19 JANUARY WHEN LINE PRESSURE WAS REDUCED TO ALLOW FOR ADDITIONAL INVESTIGATION OF THE LEAK. TO GAIN ACCESS TO THE VALVE AND FURTHER INVESTIGATE, SOIL WAS EXCAVATED AND CONTAINERIZED ONSITE AND APPROVAL IS PENDING FOR TRANSPORTATION AND DISPOSAL. ADDITIONALLY, IMPACTED WATER RECOVERED FROM THE EXCAVATION HAS BEEN CONTAINERIZED FOR DISPOSAL. FOLLOWING THE EXCAVATION AND INVESTIGATION, IT WAS DETERMINED THAT THE LEAK WAS THE RESULT OF A PRIMARY STEM SEAL FAILURE. THE PRIMARY STEM SEAL WAS REPLACED ON VALVE 767-3-10 WITH THE REPAIRS COMPLETED ON 28 JANUARY. FOLLOWING THE REPAIR, A PURGE AND LOAD PLAN WAS ESTABLISHED AND THE 767 LATERAL WAS RETURNED TO SERVICE ON 2 FEBRUARY 2015. IMPACTED SOIL AND WATER WILL REMAIN CONTAINERIZED AT THE SITE UNTIL APPROVED FOR TRANSPORTATION AND DISPOSAL. A DETERMINATION ON WHY THE STEM SEAL FAILED IS MOST LIKELY CONTRIBUTED TO A MISALIGNMENT OR MANUFACTURER DEFECT. THE FAILED O-RING SEAL WAS REMOVED FROM THE VALVE AND REPLACED WITH A NEW O-RING SEAL, WHICH REPAIRED THE LEAK AND ALLOWED THE LINE TO BE PLACED BACK INTO SERVICE. INITIAL ESTIMATES FOR THE REPAIR AND REMEDIATION OF THE VALVE AND VALVE SITE DID NOT EXCEED THE AMOUNT NECESSARY TO REPORT THE INCIDENT TO THE NATIONAL RESPONSE CENTER (NRC). FOLLOWING THE INITIAL INVESTIGATION AND DETERMINING ESTIMATES FOR THE VALVE REPAIR, THE TRANSPORTATION AND DISPOSAL OF IMPACTED SOIL AND WATER, AND REMEDIATION OF THE SITE, IT WAS DETERMINED THAT ESTIMATED REPAIR AND REMEDIATION FOR THE VALVE AND VALVE SITE BEGAN TO APPROACH AND COULD EXCEED $50,000 IN TOTAL COSTS. UPON MAKING THIS DETERMINATION ON 27 JANUARY, TRANSCANADA REPORTED THE INCIDENT TO THE NRC (REPORT # 1106719) AND CONTACTED PHMSA SOUTHWEST REGIONAL. FOLLOWING THE REPLACEMENT OF THE O-RING AND REPAIR OF THE VALVE, THE SITE WAS RESTORED AND REMEDIATED IN ACCORDANCE REGULATIONS UNDER THE JURISDICTION OF LOUISIANA DEPARTMENT OF ENVIRONMENTAL QUALITY (LDEQ) AND THE UNITED STATES ENVIRONMENTAL PROTECTION AGENCY (USEPA). LIQUID PRODUCT ALONG WITH IMPACTED WATER AND SOIL WAS RECOVERED AND TRANSPORTED FOR PROPER DISPOSAL AND THE SITE HAS BEEN RESTORED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150019 | 16719 | 2015-02-12 15:59 | SUPPLEMENTAL FINAL | 31202 | ENABLE MIDSTREAM PARTNERS, LP | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2015-01-21 07:18 | 2015 |  |  | 34.8923 | -95.4136 | 1106316 | 2015-01-22 10:31 |  | NATURAL GAS |  | 4580 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-01-21 07:20 | 2015-01-26 10:29 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-01-21 07:18 | 2015-01-21 07:18 | ONSHORE | OK | 74578 | Not Within a Municipality | LATIMER | MILEPOST | WILBURTON STA | FH-120 | PSV FH-120-1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2012 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE VENTING, WATER IN PILOT | CLASS 1 LOCATION | NO |  | 131 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 14638 | 13091.7323943662 | 100 | 109.289045398306 | 0 | 0 | 1000 | 1092.89045398306 | TBD - UNDER INVESTIGATION |  | 15738 | 14124.6255391554 | 14293.9118937476 | [8 empty] | 678 |  | 1050 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 5988 | NO | YES | [6 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NOT CONTROLLED BY CONTROLLER | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [16 empty] | YES | [174 empty] | JIMMY CROSS | DOT COMPLIANCE MANAGER | jimmy.cross@enablemidstream.com | 3184293664 | 3184293997 |  |  |  | DONNIE BROWN | INTRASTATE PIPELINES COMPLIANCE MANAGER | 9184039123 | donnie.brown@enablemidstream.com | AN ENABLE EMPLOYEE RECEIVED A CALL FROM THE ENABLE WILBURTON PLANT OPERATOR ON 1-21-15 AT 7:18AM. THE PLANT OPERATOR REPORTED THAT THE RELIEF WAS BLOWING ON F AND H YARD AND HAD HIM SHUT DOWN THE WILBURTON BOOSTER UNIT AT THE WILBURTON OFFICE. THE BOOSTER WAS SHUT DOWN ON 1-21-15 AT 7:20AM. DISCHARGE PRESSURE WAS 651PSI ON THE ENGINE PANEL. EMPLOYEES CLOSED THE INLET ISOLATION TO THE RELIEF VALVE AFTER THE BOOSTER UNIT WAS SHUT DOWN AND GAS WAS NO LONGER FLOWING INTO LINE FH-120. IT WAS DETERMINED THAT NGPL SHUT IN AT THEIR FACILITY CAUSING AN INCREASE IN PRESSURE. THE WILBURTON BOOSTER WAS STILL RUNNING. EMPLOYEES CHECKED THE SET POINT AND FOUND THE VALVE WAS VENTING AT APPROXIMATELY 750 TO 770 PSI AND THAT THE SET POINT WAS AT 1050 PSI. IT WAS DETERMINED THAT THE RELIEF VALVE WAS VENTING PREMATURELY. THE PILOT WAS REMOVED AND FOUND TO BE FULL OF WATER. THE PIPELINE WAS LOCKED AND TAGGED OUT AS WELL AS THE STATION SUCTION AND BYPASS. THE PILOT WAS OVERNIGHTED TO AEON WITH INSTRUCTIONS TO REPAIR THE PILOT, PERFORM A FAILURE ANALYSIS AND RECOMMEND A PROCEDURE TO KEEP THE WATER OUT OF THE PILOT. THE REPAIRED PILOT CAME BACK 1-26-2015. ENABLE EMPLOYEES INSTALLED THE PILOT AND TESTED THE VALVE. EMPLOYEES RETURNED THE BOOSTER TO SERVICE AND REESTABLISHED NORMAL OPERATIONS ON 1/26/2015. ENABLE IS AWAITING THE RESULTS OF THE FAILURE ANALYSIS TO DETERMINE THE CAUSE OF WATER ACCUMULATING IN THE PILOT. SUPPLEMENTAL INFORMATION: AEON DETERMINED THE CAUSE OF THE WATER IN THE VALVE WAS FROM: A BAD ADJUSTMENT SCREW. IT HAS BEEN DETERMINED THAT THE ADJUSTMENT SCREW WAS FAULTY.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150020 | 16677 | 2015-02-12 16:59 | SUPPLEMENTAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2015-01-16 19:05 | 2015 |  |  | 31.3266 | -90.0447 | 1105861 | 2015-01-16 20:22 |  | NATURAL GAS |  | 8151 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-01-16 19:05 | 2015-01-17 14:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-01-16 17:50 | 2015-01-16 19:05 | ONSHORE | MS | 39478 | Not Within a Municipality | WALTHALL COUNTY | MILEPOST | MP: 36.355 | PEARL RIVER METER STATION | PEARL RIVER COMPRESSOR STATION 5130 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 2014 |  | CARBON STEEL |  | OTHER | [8 empty] | MASTER FUEL REGULATOR BEGAN TO LEAK CAUSING THE RELIEF VALVE TO ACTIVATE AND RESET. | CLASS 1 LOCATION | NO |  | 614 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 25350 | 22672.1830985915 | 1500 | 1639.33568097459 | 0 | 0 | 0 | 0 |  |  | 26850 | 24257.7800245846 | 24311.5187795661 | [8 empty] | 540 |  | 600 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [25 empty] | YES | ICE BUILD-UP ON REGULATOR PILOT SENSING LINE. | [161 empty] | STEPHEN R. DINES | ENGINEER | stephen_dines@kindermorgan.com | (719) 329-5633 |  |  |  |  | REJI GEORGE | DIRECTOR OF ENGINEERING CODES AND STANDARDS | (713) 420-5433 | reji_george@kindermorgan.com | THE MASTER FUEL GAS LINE AT THE PEARL RIVER COMPRESSOR STATION SUPPLIES FUEL GAS TO TWO (2) GENERAL ELECTRIC TURBINES, AN EMERGENCY ELECTRIC POWER GENERATOR, AND DOMESTIC HEAT FOR TWO (2) STATION BUILDINGS. ON JANUARY 16, 2015, A LOCAL RESIDENT REPORTED THE SOUND OF GAS AT THE STATION TO SOUTHERN NATURAL GAS PIPELINE COMPANY, LLC (SNG). SNG GAS CONTROL RESPONDED BY DISPATCHING A LOCAL SNG FIELD TECHNICIAN AND HE IMMEDIATELY ISOLATED THE FUEL GAS METER RUN TO STOP THE FLOW OF GAS SINCE HE OBSERVED THE RELIEF VALVE ON THE FIRST CUT OF THE MASTER FUEL RUN REPEATEDLY ACTIVATING AND RESETTING AT THE DESIGNATED SET-POINTS. IT SHOULD BE NOTED THAT THE STATION COMPRESSION WAS OFF-LINE DURING THE EVENT. THE RESPONDING FIELD TECHNICIAN OBSERVED ICE BUILD-UP ON THE FIRST-CUT, REGULATOR SENSING LINE WHICH CAUSED THE REGULATOR TO MALFUNCTION AND THE RELIEF VALVE TO ACTUATE. THE ESTIMATED GAS VOLUME RELEASED, USING METER STATION FLOW DATA, WAS 8,151 MSCF OVER A 23 HOUR PERIOD FROM 20:15 HOURS LOCAL TIME ON JANUARY 15, 2015 TO 19:05 HOURS LOCAL TIME ON JANUARY 16, 2015 WHEN SNG PERSONNEL ISOLATED THE FUEL METER STATION. THE RESULTS OF THE INVESTIGATION BY SNG, COMPLETED ON JANUARY 30, 2015, SHOWED THAT ALTHOUGH A FUEL GAS HEATER WAS INSTALLED TO HEAT FUEL GAS FOR THE COMPRESSOR STATION, WHEN THE STATION TURBINES ARE OFFLINE, THE RESULTING LOW FUEL GAS FLOW (FOR DOMESTIC PURPOSES ONLY) CAN ENABLE THE FUEL TEMPERATURE TO DROP, ESPECIALLY ON COLD DAYS, BEFORE THE GAS REACHES THE MASTER FUEL METER. SNG CONCLUDED THAT DURING EXTENDED PERIODS OF BELOW-FREEZING TEMPERATURES, WITH LOW FLOW, THE FUEL TEMPERATURE CAN DROP AND CAUSES ICE BUILD-UP ON THE REGULATOR PILOT SENSING LINE. SNG WILL COMPLETE THE FOLLOWING CORRECTIVE ACTIONS TO MINIMIZE THE EFFECTS OF FREEZING ON THE REGULATOR SENSING LINES AND INCREASE SITUATIONAL AWARENESS OF GAS RELEASE FROM OPP ON THE FUEL GAS SYSTEM: 1) INSTALLATION OF CATALYTIC HEATERS ON PILOT REGULATOR SENSING LINES TO PREVENT ICE BUILD-UP DURING CONDITIONS OF LOW GAS FLOW AND LOW AMBIENT TEMPERATURES. 2) INSTALLATION OF ADDITIONAL PRESSURE TRANSMITTER TO DETECT FLOW THROUGH THE MASTER FUEL METER RELIEVE VALVE AND GENERATE A SYSTEM ALARM WHEN THE PRESSURE APPROACHES THE RELIEF VALVE SET POINT. THIS WILL PROMPT A CALL-OUT TO STATION PERSONNEL.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150021 | 16911 | 2015-02-15 21:10 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2015-01-17 10:50 | 2015 |  |  | 33.5473 | -84.4109 | 1105945 | 2015-01-17 20:03 |  | NATURAL GAS |  | 245 | 1550 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-01-19 11:40 | 2015-01-22 15:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 55 | 2015-01-17 10:50 | 2015-01-17 11:13 | ONSHORE | GA | 30274 | RIVERDALE | CLAYTON | MILEPOST | 640 GA HWY 13 | RIVERDALE TO FOREST PKWY 30-IN LINE | GIS OBJECT ID #204779 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | REPAIR SLEEVE OR CLAMP | [38 empty] | 2012 |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | YES | METHOD1 | 358 |  | NO | NO | NO |  | 0 | 0 | 4735 | 5174.83629960978 | 749 | 669.880281690141 | 312794 | 341849.576663177 | 3799 | 4151.89083468164 | 0 | 0 |  |  | 322077 | 161893.685178582 | 351846.184079159 | [8 empty] | 263 |  | 300 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 1500 | NO | [5 empty] | YES | STILL UNDER ANALYSIS | YES |  | YES |  |  |  |  | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS SMALL ENOUGH WHERE IT WOULD NOT HAVE BEEN PICKED UP BY THE CONTROLLER OR CONTROL ROOM. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | OTHER | BASED ON AN ANALYSIS PERFORMED, THE END PLATE ASSOCIATED WITH THE WELD-OVER SLEEVE WAS NOT ADEQUATE TO RESIST THE BENDING FORCES EXPERIENCED ON THE PIPELINE. | [16 empty] | YES | END PLATE ON WELD-OVER SLEEVE NOT ADEQUATE TO RESIST BENDING FORCES | [161 empty] | RALPH MCCOLLUM | SR. COMPLIANCE ENGINEER | rmccollu@aglresources.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICHARD R. LONN | MANAGING DIRECTOR COMPLIANCE AND PRM | (404) 584-3552 | rlonn@aglresources.com | A LEAK CALL WAS RECEIVED AT THE COMPANY'S CALL CENTER WHERE UPON INVESTIGATION A CRACK WAS DISCOVERED IN A 30-INCH WELD-OVER FITTING NEAR THE INTERSECTION OF WHERE THE FITTING IS WELDED TO THE PIPE. APPARENT CAUSE IS IDENTIFIED IN SECTION G6.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150023 | 16657 | 2015-02-16 15:17 | ORIGINAL FINAL | 4350 | ELIZABETHTOWN GAS CO | 520 GREEN LANE | UNION | NJ | 07083 | 2015-01-15 14:00 | 2015 |  |  | 40.6106 | -75.1534 | 1105757 | 2015-01-15 15:59 |  | NATURAL GAS |  | 4669.8 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-01-15 15:14 | 2015-01-16 13:20 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 6 | 2015-01-15 14:08 | 2015-01-15 14:31 | ONSHORE | NJ | 08848 | HOLLAND TOWNSHIP | HUNTERDON | MILEPOST | 2021-09-15 | GILBERT 12" | NONE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 44 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | DRAIN LINES | [38 empty] | 1980 |  | CARBON STEEL |  | OTHER | [8 empty] | SEE PART H FOR DETAIL. | CLASS 2 LOCATION | NO |  | 42 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 28000 | 25042.2535211268 | 60000 | 65573.4272389835 | 10000 | 10928.9045398306 | 0 | 0 |  |  | 98000 | 61079.0302552602 | 101544.585299941 | [8 empty] | 574 |  | 950 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 32990 | NO | YES | YES |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS AN EXCAVATION DAMAGE BY A GAS COMPANY CONTRACTOR WITH CONTRACTED OVERSIGHT. COMPANY OPERATIONS SUPERVISION WAS NOTIFIED DIRECTLY AND IMMEDIATELY BY THE CREW. | [12 empty] | NO |  |  | YES | 5 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [10 empty] | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 143012494 |  | UTILITY OWNER | YES | YES | YES | 18 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO USE HAND TOOLS WHERE REQUIRED | [263 empty] | PHIL SALVATORE | COMPLIANCE ENGINEER | psalvato@aglresources.com | 9086628306 | 9084138409 |  |  |  | RICK LONN | MANAGING DIRECTOR OF COMPLIANCE | 4045873552 | rlonn@aglresourcers.com | THE COMPANY CONTRACTOR SHEARED OFF A 2 INCH BLOW-OFF VALVE CAUSING A GAS RELEASE DURING EXCAVATION ACTIVITIES WITH MECHANIZED EQUIPMENT ALONG THE 12 INCH GILBERT II STEEL GAS TRANSMISSION PIPELINE JUST NORTH OF THE EXISTING 10 INCH GII-18 VALVE. NOTE FOR PART G: THE CONTRACTOR ORIGINALLY NOTIFIED THE NJ ONE CALL CENTER ON 10/28/14 OF THE INTENT TO EXCAVATE AND TICKET 143012494 WAS ISSUED AS INDICATED. HOWEVER, UNDER NEW JERSEY REGULATIONS THAT TICKET EXPIRED ON 1/6/15. THE CONTRACTOR MADE A SECOND NOTIFICATION TO EXCAVATE ON 1/12/2015 AND WAS GIVEN TICKET # 150121636 WHICH HAD A DIG START DATE OF 1/16/2015. SO THE ONE CALL CENTER WAS NOTIFIED BUT NEITHER TICKET WAS LEGALLY IN FORCE AT THE TIME OF THE EXCAVATION UNDER NEW JERSEY REGULATIONS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150024 | 16662 | 2015-02-20 12:17 | ORIGINAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2015-01-24 04:19 | 2015 |  |  | 32.0288 | -90.1432 | 1106478 | 2015-01-24 04:25 |  | NATURAL GAS |  | 23377 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | VALVE WAS ISOLATED; STATION REMAINED ONLINE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-01-24 04:19 | 2015-01-24 03:30 | ONSHORE | MS | 39073 | FLORENCE | RANKIN | MILEPOST | 0.01 | HARRISVILLE COMPRESSOR STATION | INDEX 818 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2009 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 27 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 75737 | 67736.6126760563 | 500 | 546.445226991529 | 1500 | 1639.33568097459 | 0 | 0 |  |  | 77737 | 71228.9531783193 | 69922.3935840225 | [8 empty] | 1458 |  | 1480 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A 1-INCH VALVE WAS VENTING WHICH PRODUCED A LOUD NOISE. BOARDWALK RECEIVED NOTIFICATION FROM THE PUBLIC. THE GAS THAT VENTED WAS NOT OF ENOUGH VOLUME OR PRESSURE LOSS TO BE DETECTED BY SCADA. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | THERMAL RELIEF VALVES VENTED PREMATURELY | [161 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 2706886361 | jeff.mcmaine@bwpmlp.com | THE RELIEF VALVES ON THE COOLING FANS ARE SET AT 1,500 PSI AND SIX OF THEM VENTED AT 1,471 PSI. WHEN THREE OF THE RELIEF VALVES RELIEVED, THE VENT STACKS SLID DOWN IN THE BRACKET THAT WAS SECURING THEM ON THE TOP FRAME OF THE COOLING FANS. THE DOWNWARD FORCE BROKE THE NIPPLE UNDERNEATH THE RELIEF VALVE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150025 | 16908 | 2015-02-27 20:17 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2015-01-28 03:48 | 2015 |  |  | 35.1603 | -118.8042 | 1106769 | 2015-01-28 05:00 |  | NATURAL GAS |  | 15175 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | CLOSED VALVE BY REMOTELY LOWERING PRESSURE OF MAINLINE REGULATOR SETPOINT | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-01-28 03:48 | 2015-01-28 06:45 | ONSHORE | CA | 93203 | ARVIN | KERN COUNTY | MILEPOST | 4-PLS | L-300B | MP 256.64 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2014 |  | CARBON STEEL |  | OTHER | [8 empty] | PRESSURE RELIEF VALVE UNINTENTIONALLY VENTED NATURAL GAS | CLASS 1 LOCATION | NO |  | 650 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 49396 | 44178.1126760563 | 5000 | 5464.45226991529 | 0 | 0 | 0 | 0 |  |  | 54396 | 48309.7831805401 | 49642.5649459716 | [8 empty] | 734 |  | 757 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | REMOTELY CONTROLLED |  | NO |  | YES |  |  | YES | YES | A PIG LAUNCHER IS INSTALLED AT PLS-4, WHICH ALLOWS INSPECTION ON L-300B BETWEEN MP 256.65-298.96 (PLS-4 TO PLS-5). HOWEVER, THE SECTION OF L-300B SOUTH OF PLS-4 IS NOT CURRENTLY PIGGABLE DUE TO LACK OF A LAUNCHER/RECEIVER AND PLUG VALVES REQUIRING REPLACEMENT. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA-RELATED EQUIPMENT OPERATED AS INTENDED | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [13 empty] | YES | [177 empty] | CHERYL DIZON | COMPLIANCE ENGINEER | c1dz@pge.com | 925-328-5721 |  |  |  |  | LARRY DENISTON | MANAGER OF GAS OPERATIONS REGULATORY COMPLIANCE | 925-328-5756 | lcd1@pge.com | AT APPROXIMATELY 0348 HOURS ON JANUARY 28, 2015 AN 8-INCH PRESSURE RELIEF VALVE (AT PRESSURE LIMITING STATION,4-PLS OFF OF TRANSMISSION LINE L-300B) IN ARVIN OPENED PRIOR TO REACHING ITS SET POINT RESULTING IN AN UNINTENTIONAL RELEASE OF NATURAL GAS TO THE ATMOSPHERE. PRESSURE IN L-300B DID NOT EXCEED THE MAOP OF 757 PSIG. OPERATION OF THE PRESSURE RELIEF VALVE WAS OBSERVED ON SCADA BY GAS CONTROL ROOM PERSONNEL AT THE TIME OF THE RELEASE, SO THE MAIN LINE REGULATOR SET POINT WAS REMOTELY LOWERED WHICH ALLOWED THE PRESSURE RELIEF VALVE TO RE-SEAT ITSELF AND NATURAL GAS RELIEVING TO ATMOSPHERE WAS STOPPED AT 0408 HOURS. PG&E PERSONNEL ARRIVED ON SITE AT 0645 HOURS. THERE WERE NO INJURIES, NO FATALITIES AND NO MEDIA OBSERVED ON SCENE DURING THE INCIDENT. PG&E CONTRACTED A THIRD PARTY ENGINEERING FIRM TO PERFORM A ROOT CAUSE ANALYSIS AND PROVIDE RECOMMENDATIONS TO THE STATION. PG&E IMPLEMENTED SEVERAL MODIFICATIONS AND IS CURRENTLY IN THE DESIGN PHASE TO REBUILD PLS-4. PG&E INSPECTS AND CALIBRATES PRESSURE RELIEF VALVES (PRV) AS PART OF PG&E'S ROUTINE MAINTENANCE PROGRAM, WHICH IS DESIGNED TO ENSURE THE RELIABLE OPERATION OF THIS EQUIPMENT AT PG&E'S PRESSURE LIMITING STATIONS. THIS INCIDENT WAS REPORTED TO DOT & CPUC BECAUSE THE ESTIMATED VOLUME OF NATURAL GAS RELEASED WAS ESTIMATED ABOVE 3 MILLION CUBIC FEET (MMCF). PG&E LATER CONFIRMED THAT APPROXIMATELY 15.2 MMCF WAS UNINTENTIONALLY RELEASED. (PLEASE NOTE THAT THE RESPONSES TO PART E, QUESTIONS 5A, 5B, AND 5C OF THIS PHMSA 7100 REPORT ARE MERELY PLACEHOLDERS AND DO NOT APPLY. PG&E GAS CONTROL REMOTELY LOWERED THE PRESSURE IN L-300B BY LOWERING THE SETPOINT OF THE MAIN LINE REGULATOR, WHICH ALLOWED THE PRESSURE RELIEF VALVE TO CLOSE. THE PHMSA 7100 REPORT FORM DOES NOT ALLOW THESE FIELDS TO BE LEFT BLANK.)
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150026 | 17056 | 2015-03-01 10:44 | SUPPLEMENTAL | 32163 | ROCKIES EXPRESS PIPELINE LLC | 370 VAN GORDON ST | LAKEWOOD | CO | 80228 | 2015-01-29 17:56 | 2015 |  |  | 39.3968 | -91.2623 | 1106914 | 2015-01-29 19:18 |  | NATURAL GAS |  | 181000 | 56302 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-01-29 17:56 | 2015-02-08 07:02 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 100 | 2015-01-29 17:56 | 2015-01-29 19:40 | ONSHORE | MO | 63334 | BOWLING GREEN | PIKE COUNTY | SURVEY STATION NO. | 56639+02 | ROCKIES EXPRESS PIPELINE | REX 014-001-00-00 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 120 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 42 |  | 0.486 | 70000 | API 5L | SPIRAL WELDED |  | WELSPUN | EPOXY | [9 empty] | PIPE GIRTH WELD | [18 empty] | 2008 | 2008 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 121.8 | 1.5 |  | CLASS 1 LOCATION | NO |  | 1155 |  | NO | NO | NO |  | 100000 | 109289.045398306 | 159898 | 174750.997810983 | 1457447 | 1303491.33098592 | 900000 | 983601.408584753 | 35000 | 38251.1658894071 | 20000 | 21857.8090796612 | EN ENGINEERING METALLURGICAL ANALYSIS |  | 2672345 | 1960861.1312474 | 2631241.75774903 | [8 empty] | 1296 |  | 1480 | OTHER | 0.8 DESIGN FACTOR |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | AUTOMATIC | 95621 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER ACKNOWLEDGED THE ALARM BEFORE FIELD OPERATIONS RESPONDED. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | YES | YES | ROOT CAUSE INVESTIGATION | [5 empty] | YES | OVERBURDEN | [17 empty] | YES |  | YES | OVERBURDEN DUE TO CONSTRUCTION ACTIVITIES. | [55 empty] | YES | YES |  |  | YES |  |  | YES | 2012 | [31 empty] | 2012 | [17 empty] | COMBINATION TOOL | 2012 |  |  |  |  | NO |  |  | NO | [13 empty] | YES | 2008 | [6 empty] | YES | [55 empty] | TIM ARNOLD | COMPLIANCE ENGINEER | tim.arnold@tallgrassenergylp.com | 3037633315 |  |  |  |  | JENNIFER ECKELS | COMPLIANCE MANAGER | 3037633486 | jennifer.eckels@tallgrassenergylp.com | AT APPROXIMATELY 17:56 CST ON JANUARY 29, 2015, A RUPTURE RESULTING IN A NATURAL GAS RELEASE OCCURRED ON THE ROCKIES EXPRESS PIPELINE (REX) NEAR STATE ROAD U AND PIKE COUNTY ROAD 43 (CLASS 1 AREA) IN PIKE COUNTY, MISSOURI. THE 42" PIPELINE WAS OPERATING AT 1296 PSIG AT THE TIME OF THE INCIDENT, WITH AN ESTABLISHED MAXIMUM ALLOWABLE OPERATING PRESSURE (MAOP) OF 1480 PSIG. THERE WAS NO FIRE, EXPLOSION, INJURY/DEATH, OR MAJOR PRIVATE PROPERTY DAMAGE ASSOCIATED WITH THE RUPTURE. FIFTY FAMILIES WERE EVACUATED BY LOCAL LAW ENFORCEMENT. THE FIRST SCADA SAFETY RELATED LINE BREAK ALARM FOR THE MEXICO COMPRESSOR STATION WAS RECEIVED IN THE OPERATIONAL CONTROL CENTER (OCC) AT 17:56 CST. THE CONTROLLER IMMEDIATELY CONTACTED THE ON-CALL STATION OPERATOR AT MEXICO COMPRESSOR STATION TO DETERMINE IF THERE WAS AN ISSUE AT THE STATION. THE VALVE DOWNSTREAM OF THE RUPTURE SITE (MLV 65) CLOSED IMMEDIATELY UPON SENSING THE PRESSURE DROP. A REPRESENTATIVE OF THE BOWLING GREEN FIRE DEPARTMENT CONTACTED OCC AT 18:15 CST, WHICH WAS FOLLOWED BY A CALL FROM THE PIKE COUNTY SHERIFF AT 18:20 CST TO COMMUNICATE THEIR ARRIVAL ON SITE. AT 18:30 CST THE CONTROLLER SPOKE WITH LOCAL FIELD OPERATIONS PERSONNEL WHO WERE IN ROUTE TO THE SITE. TALLGRASS FIELD OPERATIONS PERSONNEL ARRIVED ON SITE AT 19:40 CST, MET WITH THE LOCAL INCIDENT COMMANDER, AND AT THAT TIME CONFIRMED THE RUPTURE. FIELD OPERATIONS SUPERVISED THE BLOWDOWN OF GAS UNTIL IT WAS SAFE TO APPROACH THE RUPTURE SITE IN PREPARATION FOR THE INCIDENT INVESTIGATION. AT 0:52 CST EMERGENCY RESPONSE ACTIVITIES CONCLUDED AND THE SITE WAS DEEMED SECURE. INCIDENT INVESTIGATION AND CLEAN-UP BEGAN THE MORNING OF JANUARY 30, 2015. THE FIELD INVESTIGATION REVEALED THAT THE FAILURE OCCURRED AT A WELD. INCLUDED ARE BOTH THE UPSTREAM AND DOWNSTREAM PIPE CHARACTERISTICS: - UPSTREAM: X70, WT. 0.74, ARO - DOWNSTREAM: X80, WT. 0.486, FBE - 0.740" BEVEL WAS PREPARED IN ACCORDANCE WITH ASME B31.8 ANNEX I AND SHOWED EVIDENCE OF GOOD WORKMANSHIP SUBSEQUENT TO THE ROOT CAUSE ANALYSIS DISCUSSION, AND WITH AGREEMENT FROM ALL PARTIES INVOLVED, IT WAS DEEMED THAT THE GIRTH WELD RUPTURE WAS AN OVERLOAD FAILURE CAUSED BY AXIAL STRESS THAT EXCEEDED THE CROSS SECTION TENSILE STRENGTH OF THE CRACK INITIATION LOCATION. THIS DETERMINATION IS SUPPORTED BY CRACK CHARACTERISTICS, METALLURGICAL ANALYSIS, POTENTIAL FAILURE MODES AND OBSERVATION OF THE PIPE GEOMETRY RESULTING FROM THE RUPTURE. THE RCA IDENTIFIED FIVE AXIAL LOAD INDUCING VARIABLES THAT LIKELY LEAD TO THE EXCEEDANCE OF THE CROSS SECTION TENSILE STRENGTH, HOWEVER, NO SINGLE VARIABLE CAN BE BLAMED FOR THE OVERALL CAUSE OF THE RUPTURE. THE FIVE PREDOMINATE AXIAL LOAD INDUCING VARIABLES ARE AS FOLLOWS: PIPELINE SETTLEMENT, PIPELINE MISALIGNMENT, TEMPERATURE STRESSES, INTERNAL PRESSURE, AND CONSTRUCTION FORCES.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150027 | 16672 | 2015-03-03 17:18 | ORIGINAL FINAL | 31594 | SOUTHCROSS CCNG TRANSMISSION LTD | 2103 CITYWEST BLVD. SUITE 900 | HOUSTON | TX | 77042 | 2014-03-25 11:30 | 2014 |  |  | 28.123 | -97.0294 | 1077691 | 2014-03-25 12:00 |  | NATURAL GAS |  | 327400 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-03-25 12:00 | 2014-04-21 15:00 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 0 | 2014-03-25 11:30 | 2014-03-25 12:00 | OFFSHORE | [28 empty] | 12 | IN STATE WATERS | TX | COPANO BAY | COPANO BAY - GPS COR. LAT 28.123034 LON -97.029354 | ARANSAS |  |  |  | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTRASTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE SEAM | 12.75 |  | 0.375 | 42000 | X42 ERW | LONGITUDINAL ERW - LOW FREQUENCY |  | N/A | COAL TAR | [28 empty] | 1951 | 1951 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 3 | 1 |  | CLASS 1 LOCATION | NO |  | 190 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 16457 | 10980.9404553415 | 275000 | 304192.755996532 | 0 | 0 | 275000 | 304192.755996532 | NO PROPERTY DAMAGE, JUST REPAIRS/TESTING |  | 566457 | 290649.442951229 | 619366.452448406 | [8 empty] | 447 |  | 525 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 11612 | NO | [5 empty] | YES | NO PIG TRAPS WERE INSTALLED BEFORE, BUT WERE INSTALLED DURING REPAIRS. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | FREE FLOWING PIPELINE | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | YES | [14 empty] | YES | PIPE SEAM FAILURE | [7 empty] | YES | [62 empty] | NO | [63 empty] | YES | 2012 | 1038 | Yes, but the point of the Accident was not identified as a dig site |  | 2013 | [11 empty] | YES | [5 empty] | DIRECT ASSESSMENT | 2012 | [5 empty] | YES | [50 empty] | KEVIN BEVILLE | SENIOR ENGINEER | kevin.beville@southcrossenergy.com | 2149793748 | 2149793848 |  |  |  | KEVIN BEVILLE | SENIOR ENGINEER | 2149793748 | kevin.beville@southcrossenergy.com | ON MARCH 25, 2014 A LEASE OPERATOR NOTIFIED SOUTHCROSS OF A PIPELINE RUPTURE IN THE MIDDLE OF COPANO BAY AND GAS CONTROL CALLED STATING A PRESSURE DROP ON THAT SYSTEM. 11:30 AM - LARRY WASHINGTON NOTIFIED RAZ PEREZ OF A GAS LEAK IN THE MIDDLE OF COPANO BAY CROSSING. 11:37 AM - RAZ PEREZ NOTIFIED LAMAR HELLUMS TO HEAD TO THE SOUTH BLOCK VALVE AND DENNIS HENNEKE TO PROCEED TO THE NORTH BLOCK VALVE ON THE 12" ST. CHARLES LINE. 11:50 AM - LEONARD STROMAN NOTIFIED THE RRC AND NRC. 12:15 PM - LAMAR HELLUMS CLOSED SOUTHSIDE BLOCK VALVE. LAMAR CITY GATE WAS CONNECTED BETWEEN BLOCK VALVES, SO WE HAD TO ROUND UP 1" HIGH PRESSURE HOSES TO CONNECTED FROM THE UPSTREAM SIDE OF BLOCK VALVE BEFORE NORTH BLOCK VALVE WAS CLOSED. 2:45 PM - HOSES HOOKED UP TO LAMAR CITY GATE. 3:00 PM - LAMAR HELLUMS CLOSED NORTHSIDE BLOCK VALVE AND BLOWOUT SECTION BLED DOWN TO 0#. PRODUCERS WERE NOTIFIED TO SHUT IN.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150028 | 16673 | 2015-03-08 18:17 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2015-02-10 22:27 | 2015 |  |  | 42.2444 | -71.5156 | 1107843 | 2015-02-11 00:17 |  | NATURAL GAS |  | 11809 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | ISOLATION VALVE BENEATH RELIEF VALVE WAS CLOSED TO STOP EVENT | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-02-10 22:37 | 2015-03-10 23:10 | ONSHORE | MA | 01748 | HOPKINTON | MIDDLESEX | SURVEY STATION NO. | 448+40 | TGP 200-2 LINE / COMPRESSOR STATION 267 | 266 - 267 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2000 |  | CARBON STEEL |  | OTHER | [8 empty] | RAIN WATER OR SNOW ENTERED VENT OF PILOT; RAIN WATER OR SNOW FROZE; THE RESULTING ICE DEFORMED THE END OF THE PILOT CONTROLLER; DAMAGED CONTROLLER CAUSED RELIEF VALVE TO ACTIVATE BELOW 700 PSIG MAOP; | CLASS 3 LOCATION | YES | METHOD2 | 488 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 51820 | 46346.0563380282 | 2980 | 3256.81355286952 | 350 | 382.511658894071 | 0 | 0 |  |  | 55150 | 49719.6073353289 | 49985.3815497918 | [8 empty] | 532 |  | 700 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | NEXT DOOR LNG PLANT EMPLOYEE FAMILIAR WITH TGP STATION 267; |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CHANGE IN PRESSURE WAS VERY SMALL; | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | OTHER | RAIN OR SNOW ENTERED VENT OF PILOT; RAIN OR SNOW FROZE; THE RESULTING ICE DEFORMED THE END OF THE PILOT CONTROLLER; DAMAGED CONTROLLER CAUSED RELIEF VALVE TO ACTIVATE BELOW 700 PSIG MAOP; | YES |  |  |  | YES | EXTREME COLD AND BLIZZARD CONDITIONS OCCURRING IN THE NORTHEASTERN REGION OF THE UNITED STATES; | [301 empty] | WILLIAM MARTIN MULLER | SPECIALIST - PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205-325-3863 | 205-325-3508 |  |  |  | WILLIAM MARTIN MULLER | SPECIALIST - PIPELINE TECHNICAL | 205 325 3863 | martin_muller@kindermorgan.com | RAIN OR SNOW ENTERED VENT OF PILOT; RAIN OR SNOW FROZE; THE RESULTING ICE DEFORMED THE END OF THE PILOT CONTROLLER; DAMAGED CONTROLLER CAUSED RELIEF VALVE TO ACTIVATE BELOW 700 PSIG MAOP; EVENT WAS REPORTABLE AS NATURAL GAS RELEASED WAS >3,000 MCF;
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150029 | 17012 | 2015-03-10 17:14 | SUPPLEMENTAL FINAL | 13769 | NORTHERN BORDER PIPELINE COMPANY | 700 LOUISIANA STREET | HOUSTON | TX | 77002 | 2015-02-09 10:18 | 2015 |  |  | 47.2546 | -102.7171 | 1107691 | 2015-02-09 11:55 |  | NATURAL GAS |  | 4000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-02-09 10:18 | 2015-02-10 17:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-02-09 10:18 | 2015-02-09 10:18 | ONSHORE | ND | 58642 | Not Within a Municipality | DUNN | MILEPOST | ND 272 | NORTHERN BORDER PIPELINE | CS 05 MANNING COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1998 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | RUBBER | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 1158 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 9960 | 8907.88732394366 | 40572 | 44340.7514990007 | 4788 | 5232.75949367089 | 0 | 0 |  |  | 55320 | 31990.7609011833 | 58481.3983166152 | [8 empty] | 1017 |  | 1440 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM ACTIONS COULD NOT HAVE AFFECTED THE EVENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [18 empty] | YES | [174 empty] | KURT SMITH | COMPLIANCE SPECIALIST | kurt_smith@transcanada.com | 509 533-2848 | 509 533-2993 |  |  |  | KURT SMITH | COMPLIANCE SPECIALIST | 509 533-2848 | kurt_smith@transcanada.com | A COMPRESSOR STATION EMERGENCY SHUTDOWN (ESD) WAS INITIATED BY THE FAILURE OF A BATTERY CHARGER IN THE STATION CONTROL SYSTEM. THE STATION BLOCK VALVES (SUCTION AND DISCHARGE) WERE COMMANDED CLOSED, AND THE STATION VENT VALVE WAS COMMANDED OPEN. THE DISCHARGE AND VENT VALVES OPERATED AS DESIGNED, BUT THE STATION SUCTION VALVE REMAINED OPEN. GAS VENTED THROUGH THE STATION VENT VALVE AND VENT STACK FOR 3 MINUTES BEFORE OPERATOR PERSONNEL CLOSED THE STATION VENT VALVE TO CONTROL THE GAS RELEASE. THIS VENTED AN AMOUNT OF GAS THAT EXCEEDED THE LEVEL REQUIRED FOR REPORTING AS AN INCIDENT. THE STATION SUCTION VALVE FAILED TO OPERATE DUE TO THE FAILURE OF A RUBBER DIAPHRAGM IN THE CONTROL SYSTEM FOR THE VALVE OPERATOR.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150030 | 16761 | 2015-03-12 17:52 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2015-02-13 15:00 | 2015 |  |  | 31.2703 | -103.0846 | 1108250 | 2015-02-16 12:05 |  | NATURAL GAS |  | 22 | 825 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-02-13 16:00 | 2015-02-24 06:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-02-13 15:00 | 2015-02-13 15:00 | ONSHORE | TX | 79730 | COYANOSA | PECOS | MILEPOST | WAHA STATION | WAHA COMPRESSOR STATION | 225-NORTH TEXAS GAS SYSTEM | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 72 |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 20 |  | 0.375 |  | UNKNOWN | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | EPOXY | [28 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 1600 |  | NO | NO | NO |  | 0 | 0 | 2226 | 2432.77415056629 | 59 | 52.7676056338028 | 294000 | 321309.793471019 | 0 | 0 | 0 | 0 |  |  | 296285 | 148661.08765205 | 323795.335227219 | [8 empty] | 885 |  | 1051 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS NOT DETECTABLE BY CONTROLLER IN CONTROL ROOM; THEREFORE, CONTROLLER WAS NOT THE CAUSE NOR A CONTRIBUTING FACTOR TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [64 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | [10 empty] | NO |  |  |  |  | YES | [6 empty] | UNKNOWN/OTHER | UNKNOWN/OTHER | NATURAL GAS | YES |  | BECAUSE WHEN THE INCIDENT OCCURRED IS UNKNOWN, ONE CALL INFORMATION CANNOT BE VALIDATED. | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO |  | PREVIOUS DAMAGE | [121 empty] | NO | [62 empty] | NO | NO |  |  | NO | [13 empty] | NO | [63 empty] | MICHAEL D. SMITH | COMPLIANCE SPECIALIST | mdsmith@eprod.com | 713-381-5650 |  |  |  |  | MICHAEL D. SMITH | COMPLIANCE SPECIALIST | 731-381-5650 | mdsmith@eprod.com | ON 2/13/2015 OPERATIONS TECHNICIAN IDENTIFIED A LEAK WHILE PERFORMING A LEAK SURVEY WITH DETECTION EQUIPMENT. THE FACILITY WAS IMMEDIATELY SHUTDOWN, ISOLATED AND BLOWN DOWN. THIS AREA WAS EXCAVATED USING A HYDRO-VAC TO DETERMINE THE CAUSE OF THE LEAK. THE LEAK SOURCE WAS DETERMINED TO BE ON THE 20 INCH STATION DISCHARGE PIPING AS A RESULT OF MECHANICAL DAMAGE. THE DAMAGED PIPE WAS REMOVED FROM SERVICE AND REPLACED. ENTERPRISE CANNOT VERIFY WHEN THIS DAMAGE OCCURRED. 5/15/2015, UP DATED PART D (7B) "COST OF REPAIR"
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150031 | 16680 | 2015-03-13 09:31 | ORIGINAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2015-02-16 20:32 | 2015 |  |  | 33.3949 | -91.0185 | 1108291 | 2015-02-16 21:07 |  | NATURAL GAS |  | 7082 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | BLOWDOWN VALVE OPENED DUE TO WEATHER EVENT. ONSITE EMPLOYEE CLOSED VALVE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-02-16 20:32 | 2015-02-16 20:32 | ONSHORE | MS | 38703 | GREENVILLE | WASHINGTON | MILEPOST | 114 | GREENVILLE COMPRESSOR STATION | MAIN LINE SYSTEM | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1957 |  | CARBON STEEL |  | OTHER | [8 empty] | PREMATURE OPENING OF ESD VALVE DUE TO WEATHER. | CLASS 1 LOCATION | NO |  | 200 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 20696 | 18509.8028169014 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 20696 | 19189.9530516432 | 18509.8028169014 | [8 empty] | 580 |  | 840 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS WEATHER-RELATED. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | YES |  |  |  | YES | ICE STORM | [301 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 2706886361 | jeff.mcmaine@bwpmlp.com | FREEZING RAIN ACCUMULATED ON THE ESD PILOT CAUSING VALVE TO ACTUATE. ONSITE EMPLOYEE CLOSED VALVE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150032 | 16681 | 2015-03-13 09:34 | ORIGINAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2015-02-16 22:00 | 2015 |  |  | 33.3949 | -91.0185 | 1108294 | 2015-02-16 22:20 |  | NATURAL GAS |  | 8619 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | BLOWDOWN VALVE OPENED DUE TO WEATHER EVENT. ONSITE EMPLOYEE CLOSED VALVE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-02-16 22:00 | 2015-02-16 22:00 | ONSHORE | MS | 38703 | GREENVILLE | WASHINGTON | MILEPOST | 114 | GREENVILLE COMPRESSOR STATION | MAIN LINE SYSTEM | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1966 |  | CARBON STEEL |  | OTHER | [8 empty] | PREMATURE OPENING OF ESD VALVE FROM WEATHER | CLASS 1 LOCATION | NO |  | 200 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 25187 | 22526.4014084507 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 25187 | 23354.1431924883 | 22526.4014084507 | [8 empty] | 585 |  | 840 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | WEATHER RELATED FAILURE | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | YES |  |  |  | YES | ICE STORM | [301 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 2706886361 | jeff.mcmaine@bwpmlp.com | FREEZING RAIN ACCUMULATED ON ESD PILOT CAUSING THE VALVE TO ACTUATE. AN ONSITE EMPLOYEE CLOSED THE VALVE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150033 | 17043 | 2015-03-16 16:10 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2015-02-26 13:00 | 2015 |  |  | 37.1901 | -96.7215 | 1109160 | 2015-02-26 13:21 |  | NATURAL GAS |  | 1623 | 10 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE LEAK IS MINIMUL AND AT LOW PRESSURE. THE LEAK BEING MONITORED REGULARLY | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-02-18 15:23 | 2015-02-18 15:23 | ONSHORE | KS | 67038 | Not Within a Municipality | COWLEY | SURVEY STATION NO. | 110/69+80 | LINE S-16 | DEXTER TAP | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | YES | [6 empty] | YES | UNCASED | GROUSE CREEK | UNKNOWN | BELOW WATER, PIPE IN BORED/DRILLED CROSSING | [11 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | UNKNOWN AS THE PIPE HAS NOT BEEN EXPOSED | 2000 |  | CARBON STEEL |  | LEAK |  |  | OTHER | UNKNOWN | [5 empty] | CLASS 1 LOCATION | NO |  | 20 |  | NO | NO | NO |  | 0 | 0 | 28 | 30.6009327115257 | 4035 | 3608.7676056338 | 375000 | 409833.920243647 | 7500 | 8196.67840487294 | 0 | 0 | N/A |  | 386563 | 195642.495158158 | 421669.967186865 | [8 empty] | 55 |  | 60 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 44526 | NO | [5 empty] | YES | ACETYLENE WELDED PIPE. PIPE IS SMALLER THAN SMALLEST KNOWN PIGGING TOOLS. | YES |  | YES |  |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [146 empty] | DAVID COOMES | PIPELINE COMPLINACE ENGINEER | david.coomes@sscgp.com | 2708524391 |  |  |  |  | DAVID SINCLAIR | PIPELINE COMPLIANCE MANAGER | 2708524424 | david.l.sinclair@sscgp.com | UPON INVESTIGATING AN EXPOSED PIPELINE ALONG GROUSE CREEK BANK NORTH OF DEXTER KS, A LEAK WAS DETECTED ON THE WEST BANK. A PIPE TO SOIL TEST INDICATED THAT THE EXPOSED PIPELINE IS ABANDONED AND NO LONGER ACTIVE. WHILE CONDUCTING THIS PIPE TO SOIL IN THE CREEK THE SSC TECHNICIAN NOTICED BUBBLES IN THE WATER. GAS WAS EASILY DETECTED WITH CGI BEFORE AND AFTER PROBING THE GROUND ON THE WEST BANK. AFTER CLEARING ON BOTH THE EAST AND WEST BANKS AND DIGGING AS CLOSE AS POSSIBLE TO THE CREAK BANKS IT WAS DETERMINED THAT THE LEAK WAS LOCATED UNDER THE CREEK AND WOULD REQUIRE A NEW BORE TO REPLACE THE PIPE. WHEN DETERMINATION WAS MADE THAT A BORE WOULD BE REQUIRED THE NRC WAS NOTIFIED. THE PIPE COULD NOT BE REMOVED TO INSPECT FOR A CAUSE OF THE LEAK.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150034 | 16687 | 2015-03-18 16:58 | ORIGINAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2015-02-16 07:05 | 2015 |  |  | 42.2079 | -83.9686 | 1108236 | 2015-02-16 11:23 |  | NATURAL GAS |  | 5800 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE VALVE ISOLATED AND HYDRAULICALLY PUMPED CLOSED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-02-16 07:06 | 2015-02-16 07:06 | ONSHORE | MI | 48158 | MANCHESTER | WASHTENAW | MILEPOST | FREEDOM CS | FREEDOM COMPRESSOR STATION | BLOWDOWN VALVE 612 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 2011 |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENDED OPERATION OF BLOWDOWN VALVE | CLASS 2 LOCATION | NO |  | 108 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 43268 | 38697.4366197183 | 0 | 0 | 522 | 570.488816979157 | 0 | 0 |  |  | 43790 | 40381.2590917479 | 39267.9254366975 | [8 empty] | 680 |  | 800 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE FAILURE WAS IDENTIFIED BY CONTROL ROOM PERSONNEL AND CONTACT WITH THE STATION WAS MADE WITHIN MINUTES OF THE EVENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | AMBIENT TEMPERATURES WERE BELOW -20 DEGREES | [161 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST I | carmella.king@cmsenergy.com | 517-788-0509 |  |  |  |  | ALAN CHICHESTER | GAS REGULATORY SERVICES ENGINEER | 989-791-5841 | alan.chichester@cmsenergy.com | ON THE MORNING OF MONDAY, FEBRUARY 16, 2015 AT APPROXIMATELY 7:05 A.M. A 6" BLOWDOWN VALVE IN PLANT # 2 AT THE FREEDOM COMPRESSOR STATION UNEXPECTEDLY OPENED. BLOWDOWN VALVE # 612 WAS IN THE NORMAL OPERATING BLOCKED POSITION PRIOR TO THE EVENT WITH 680PSIG UPSTREAM AT THE TIME OF THE EVENT AND THE OUTLET OF THE VALVE AT ATMOSPHERIC PRESSURE. WITH THE ACTIVATION OF THE VALVE, GAS WAS VENTED OUT THE EAST VENT STACK (AT THE FENCE LINE). CMS EMPLOYEES AT THE STATION WERE ABLE TO VERIFY AND ISOLATE PLANT #2 BY UTILIZING VALVE #607 TO LIMIT SUCTION UP-STREAM OF THE SINGLE BLOWDOWN VALVE WHICH HAD OPENED. VALVE #612 WAS HYDRAULICALLY PUMPED CLOSED AT APPROXIMATELY 7:19 A.M. THE ESTIMATED GAS LOSS DURING THIS 14 MINUTE PERIOD IS APPROXIMATELY 5.8 MMCF. GAS CONTROL EMPLOYEES IDENTIFIED A CHANGE OF THE DESIRED RATE AND A PRESSURE CHANGE AND CONTACTED THE STATION CONTROL ROOM OPERATORS WITHIN MINUTES OF THE EVENT. VALVE # 612 CYCLED NORMALLY AND SIMILAR VALVES #611, # 613 AND # 614 HAD NO SIGNS OF ISSUES. PILOT PRESSURE WAS NOTICED NEAR 130PSIG AND STEADY AT 150PSIG AT THE TIME OF RESET WHICH WAS APPROXIMATELY 9:30 A.M. PRESSURE WAS BACK TO 180-190PSIG WITH SYSTEMS BACK IN SERVICE BY 10:00 A.M. NO ABNORMAL CONDITIONS WERE FOUND OTHER THAN LOW PILOT PRESSURE. THE PILOT AND POWER GAS REGULATOR PRESSURE SETTINGS WERE INCREASED BY A ONE-QUARTER TURN EACH RESULTING IN 190-195PSIG PILOT GAS PRESSURE AND 490-495PSIG POWER GAS PRESSURE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150035 | 16995 | 2015-03-19 13:57 | SUPPLEMENTAL FINAL | 12350 | CENTERPOINT ENERGY RESOURCES CORP., DBA CENTERPOINT ENERGY MINNESOTA GAS | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2015-02-19 09:37 | 2015 |  |  | 44.8122 | -93.2841 | 1108576 | 2015-02-20 07:10 |  | NATURAL GAS |  | 10 | 352 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-02-20 11:00 | 2015-02-20 20:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-02-19 11:00 | 2015-02-19 10:30 | ONSHORE | MN | 55420 | BLOOMINGTON | HENNEPIN | MILEPOST | 131+71 | LYNDALE | LYNDALE 1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 48 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | MECHANICAL COUPLING | 1959 |  | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 3 LOCATION | NO |  | 243 |  | NO | NO | NO |  | 1500 | 1639.33568097459 | 1355 | 1480.86656514704 | 39 | 34.8802816901408 | 37859 | 41375.7396973446 | 7462 | 8155.14856762159 | 6351 | 6940.94727324641 | BRAUN X-RAYS AND LAKE SUPERIOR CONSULTING SERVICES |  | 54566 | 27390.4797599722 | 59626.9180660244 | [8 empty] | 168 |  | 215 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 15000 | NO | [5 empty] | YES | THERE IS NO LAUNCHER OR RECEIVER. THE UPSTREAM AND DOWNSTREAM VALVES ARE 20" PLUG VALVES. | YES |  | YES | YES |  | YES | REPLACE VALVES | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS NOT SUFFICIENT ENOUGH NOR CLOSE ENOUGH TO PRESSURE SENSING EQUIPMENT TO BE DISCOVERABLE IN THE SCADA SYSTEM. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | GASKET | [15 empty] | YES | [164 empty] | STEVE OLINGER | OPERATIONS SPECIALIST I | steve.olinger@centerpointenergy.com | 6123215453 |  |  |  |  | DEAN HEADLEE | PIPELINE SAFETY AND COMPLIANCE MANAGER | 6123215366 | dean.headlee@centerpointenergy.com | APPARENT CAUSE OF LEAK WAS A COUPLING GASKET DUE TO FROST LEVELS/ MOVEMENT. A GAS ODOR WAS REPORTED BY A RESIDENT IN THE AREA. CENTERPOINT ENERGY PERSONNEL RESPONDED AND FOUND A LEAK ON THE GASKET OF A STYLE 38 DRESSER COUPLING. THE SITE WAS EXCAVATED AND A WELDED COVER SLEEVE WAS INSTALLED OVER THE GASKET. THE INSTALLATION WAS COMPLETED AT 21:59 ON 2/30/15.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150036 | 16689 | 2015-03-23 12:27 | ORIGINAL FINAL | 19610 | TRANSWESTERN PIPELINE COMPANY LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2015-02-22 17:50 | 2015 |  |  | 33.9191 | -105.3264 | 1108801 | 2015-02-22 19:36 |  | NATURAL GAS |  | 130000 | 495 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE STATION WAS NOT RUNNING AT THE TIME OF THE ESD. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-02-22 17:50 | 2015-02-22 19:02 | ONSHORE | NM | 88316 | CORONA | LINCOLN | MILEPOST | 289950.2 | CORONA STATION 8 | 060MM198 STA9 TO STA8 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2007 |  | CARBON STEEL |  | OTHER | [8 empty] | 6" BALL VALVE OPENING UNINTENTIONAL | CLASS 1 LOCATION | NO |  | 657 |  | NO | NO | NO |  | 0 | 0 | 1386 | 1514.74616922052 | 364000 | 325549.295774648 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 365386 | 338207.045550228 | 327064.041943868 | [8 empty] | 715 |  | 1008 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EQUIPMENT FAILURE IN THE FIELD. | [12 empty] | YES | 6 | 0 | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | EMERGENCY SHUTDOWN SYSTEM PILOT GAS SUPPLY LINE FROZE. | [22 empty] | YES | SUB ZERO TEMPERATURES | [161 empty] | NATHAN HLAVATY | DIRECTOR - REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 7138575479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - REGULATORY COMPLIANCE | 7138575479 | nathan.hlavaty@energytransfer.com | THE TW CORONA COMPRESSOR STATION 8 - SIX INCH DISCHARGE BLOWDOWN VALVE OPENED UNINTENTIONALLY AND BLEW GAS TO THE ATMOSPHERE. THE BLOW DOWN VALVE, SHAFER OPERATOR PILOT GAS LINE FROZE OFF, DUE TO SUB ZERO TEMPERATURES CAUSING A LOSS OF PILOT PRESSURE, WHICH HOLDS THE VALVE IN THE CLOSED POSITION.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150037 | 16690 | 2015-03-23 15:25 | ORIGINAL FINAL | 13063 | NATIONAL FUEL GAS SUPPLY CORP | 6363 MAIN STREET | WILLIAMSVILLE | NY | 14221-5887 | 2015-03-05 17:54 | 2015 |  |  | 42.05 | -77.8411 | 1109781 | 2015-03-06 09:10 |  | NATURAL GAS |  | 12400 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-03-06 05:20 | 2015-03-06 15:50 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2015-03-06 05:19 | 2015-03-06 05:19 | ONSHORE | NY | 14895 | Not Within a Municipality | ALLEGANY | MILEPOST | STATION WGA3 | BEECH HILL COMPRESSOR STATION | STARTING GAS SYSTEM | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1980 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL RELIEF RUPTURE DISC | OTHER | [8 empty] | REGULATOR MALFUNCTION RAISING DOWNSTREAM PRESSURE ABOVE SET POINT CAUSING A RELIEF RUPTURE DISC TO BURST THEREBY ALLOWING NATURAL GAS TO VENT. | CLASS 1 LOCATION | NO |  | 24 |  | NO | NO | NO |  | 0 | 0 | 600 | 655.734272389835 | 33100 | 29603.5211267606 | 8500 | 9289.568858856 | 0 | 0 | 0 | 0 |  |  | 42200 | 35256.4711162824 | 39548.8242580064 | [8 empty] | 341 |  | 300 | 192.619(A)(1) |  |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 | NO | [22 empty] | TRANSMISSION IN STORAGE FIELD | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE FOR THE STARTING GAS SYSTEM IS NOT MONITORED BY GAS CONTROL. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [25 empty] | YES | REGULATOR MALFUNCTIONED RAISING DOWNSTREAM PRESSURE ABOVE THE SET POINT. | [161 empty] | JOHN SEAGER | INTEGRITY ENGINEER | seagerj@natfuel.com | 716-868-7902 | 716 -857-7469 |  |  |  | BRIAN KEMPSKI | OPERATION SUPERINTENDENT | 716- 827-2131 | kempskib@natfuel.com | BEECH HILL COMPRESSOR STATION STARTING GAS REGULATOR MALFUNCTIONED RAISING THE DOWNSTREAM PRESSURE ABOVE THE 175 PSIG SET POINT TO 341 PSIG. THE OVER PRESSURIZATION CAUSED THE RUPTURE DISC RATED AT 311 PSIG TO BURST AT 17:54 ON MARCH 5. THE DOWNSTREAM PIPING HAS AN MAOP OF 300 PSIG AND WAS NOT IN USE AT THE TIME OF THE INCIDENT. THE PRESSURE DROPPED IMMEDIATELY TO APPROXIMATELY 140 PSIG AS THE RUPTURE DISC RELIEVED THE PIPELINE PRESSURE. THE COMPANY WAS NOTIFIED OF A FIRE AT THE FACILITY AT 05:04 ON MARCH 6. AT 05:20, COMPANY PERSONNEL ACTIVATED THE EMERGENCY SHUTDOWN SYSTEM. SITE SECURITY CAMERAS SHOW THAT THE GAS DISCHARGE DID NOT IGNITE UNTIL 04:43 ON MARCH 6. THE REGULATOR WAS REPLACED AND THE STATION WAS BACK IN SERVICE AT 15:50 ON MARCH 6.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150038 | 16700 | 2015-03-27 10:44 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2015-03-07 09:30 | 2015 |  |  | 32.0319 | -90.1414 | 1109875 | 2015-03-07 10:20 |  | NATURAL GAS |  | 12546 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | UNIT TAKEN OFF-LINE BUT STATION REMAINED ONLINE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-03-07 09:30 | 2015-03-07 09:30 | ONSHORE | MS | 39073 | HARRISVILLE | SIMPSON | MILEPOST | 0 | HARRISVILLE COMPRESSOR STATION | INDEX 818 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | OTHER | VALVE YARD |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2008 |  | CARBON STEEL |  | OTHER | [8 empty] | BLOW-DOWN STACK FROM HORSEPOWER UNIT VENTED. | CLASS 1 LOCATION | NO |  | 53 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 36839 | 32947.5563380282 | 2000 | 2185.78090796612 | 0 | 0 | 0 | 0 |  |  | 38839 | 35161.5588121221 | 35133.3372459943 | [8 empty] | 1334 |  | 1480 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE VALVE THAT VENTED IS NOT REMOTE CONTROLLED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | YES | [18 empty] | YES | [177 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 2706886361 | jeff.mcmaine@bwpmlp.com | LIMIT SWITCH ON VALVE OPERATOR MALFUNCTIONED. 3-30-15 REVISED TO CORRECT LAT/LONG.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150039 | 16851 | 2015-03-27 13:40 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2015-02-27 16:00 | 2015 |  |  | 29.7746 | -92.9997 | 1109267 | 2015-02-27 17:53 |  |  |  | 1 | 51 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE VALVE AND PRESSURE VESSEL WERE ISLOATED NOT AFFECTING OPERATION | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-02-27 16:00 | 2015-02-27 16:00 | ONSHORE | LA | 70643 | GRAND CHENIER | CAMERON | SURVEY STATION NO. | 8003767 | GRAND CHENIER LIQUID HANDLING | VALVE HV302 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1977 |  | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 277 |  | NO | NO | NO |  | 0 | 0 | 150 | 163.933568097459 | 4 | 3.57746478873239 | 75000 | 81966.7840487294 | 0 | 0 | 0 | 0 |  |  | 75154 | 37703.8754758174 | 82134.2950816156 | [8 empty] | 760 |  | 1100 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE SMALL SIZE OF THE LEAK | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  |  | YES | [7 empty] | YES |  |  |  | NO | [11 empty] | YES | YES | [335 empty] | ROGER R. STREET | FIELD COMPLIANCE SPECIALIST | roger_street@transcanada.com | 615-465-5123 |  |  |  |  | ROGER STREET | FIELD COMPLIANCE SPECIALIST | 6154655123 | roger_street@transcanada.com | ON FRIDAY 27 FEBRUARY 2015 AT 16:00 , A PINHOLE LEAK WAS IDENTIFIED AT A THREAD-O-LET CONNECTION ON BLOCK VALVE (HV302) TO A SEPARATOR PRESSURE VESSEL AT GRAND CHENIER LIQUID HANDLING FACILITY BY TRANSCANADA OPERATIONS STAFF DURING DAILY ACTIVITIES. UPON THE IDENTIFICATION OF THE LEAK, THE VALVE WAS ISOLATED AND BLOWN DOWN AT 16:30 ON 27 FEBRUARY. THE VALVE IS LOCKED OUT OF SERVICE UNTIL REPAIRED. OPERATIONS AT THE FACILITY ARE UNAFFECTED BY THE OUT OF SERVICE VALVE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150040 | 17403 | 2015-03-30 12:38 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2015-03-02 06:48 | 2015 |  |  | 34.565 | -89.653 | 1109404 | 2015-03-02 09:07 |  | NATURAL GAS |  | 3664.1 | 7587.9 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-03-02 09:04 | 2015-03-18 13:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-03-02 06:48 | 2015-03-02 08:00 | ONSHORE | MS | 38619 | Not Within a Municipality | MARSHALL | MILEPOST | 66-1+2.73 | TGP LINE 100-1 | LINE 100-1, 66-1+2.73 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 54 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 |  | 0.281 | 45000 | API 5L | SEAMLESS |  | NATIONAL TUBE | OTHER | CTE | [27 empty] | 1944 | 1944 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 454 |  | NO | NO | NO |  | 1000 | 1092.89045398306 | 27305 | 29841.3738460074 | 12825 | 11470.2464788732 | 238760 | 260938.524792995 | 2000 | 2185.78090796612 | 0 | 0 |  |  | 281890 | 146872.368256843 | 305528.816479825 | [8 empty] | 705 |  | 750 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 45776 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO OPERATOR OR CONTROL ROOM ACTIONS COULD HAVE CONTRIBUTED TO THIS UNFORTUANTE EVENT. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES | [7 empty] | YES | RESULTS OF THE ROOT CAUSE ANALYSIS ARE PRESENTED IN PART H OF THIS REPORT. | [16 empty] | YES | [59 empty] | YES | YES |  |  | YES |  |  |  | 2011 | [31 empty] | 2011 | [23 empty] | YES | 1977 | 982 | NO | [13 empty] | NO | [63 empty] | STEPHEN R. DINES | ENGINEER | stephen_dines@kindermorgan.com | 719 329-5633 |  |  |  |  | REJI GEORGE | DIRECTOR ENGINEERING CODES AND STANDARDS | (713) 420-5433 | reji_george@kindermorgan.com | A PIPELINE LEAK OF NATURAL GAS RESULTING IN NO INJURIES, FIRES, OR CUSTOMER IMPACTS WAS DISCOVERED ON MARCH 2, 2015 ON SECTION OF THE 100-1 MAINLINE OF TGP IN MARSHALL COUNTY, MISSISSIPPI. THE SEGMENT FROM VALVE SECTION 66-1 TO 67-1 WAS SECURED AND PROMPTLY BLOWN DOWN TO ISOLATE THE LEAK AND INITIATE REPAIRS. THE IMPACTED SEGMENT OF PIPE WAS SENT OFF FOR METALLURGICAL ANALYSIS ON MARCH 6, 2015 AND THE RESULTS SHOW THAT THE FRACTURE INITIATED FROM MULTIPLE ORIGINS ON THE INSIDE SURFACE OF THE PIPE AT THE PEAK OF THE WRINKLE. THE FRACTURE MODE WAS BRITTLE (QUASI-CLEAVAGE). THE FRACTURE SHOWED NO EVIDENCE OF FATIGUE AND THE FRACTURE LOCATION WAS ON THE TOP OF A RIDGE CONTAINING TWO 1° SAG WRINKLE BENDS. CONSTRUCTION RECORDS INDICATE THE WRINKLE BENDS WERE COLD-FORMED AND COLD WORK COULD REDUCE DUCTILITY. THE COLD-FORMED REGION IS ALSO POTENTIALLY SUSCEPTIBLE TO STRAIN-AGING, WHICH COULD ALSO CONTRIBUTE TO LOWER DUCTILITY. THESE FACTORS COULD INCREASE THE DUCTILE TO BRITTLE TRANSITION TEMPERATURE OF THE WRINKLE BEND COMPARED TO THE PIPE BODY. RESULTS OF THE ROOT-CAUSE ANALYSIS SHOW THAT THE PRIMARY METALLURGICAL FAILURE MECHANISM WAS BRITTLE FRACTURE AND THAT THE CRACK APPEARS TO HAVE FAILED BY TENSILE OVERLOAD. TGP WAS UNABLE TO DETERMINE THE SOURCE OF EACH OF THE TENSILE FORCES, BUT THE TENSILE OVERLOAD DOES NOT APPEAR TO BE A RESULT OF THIRD PARTY DAMAGE OR OBSERVABLE LAND MOVEMENT. IN ADDITION THE FOLLOWING CONCLUSIONS ARE PRESENTED: 1. THERE WAS NO EVIDENCE THE FAILURE RESULTED FROM INSERVICE FATIGUE CRACK GROWTH OR STRESS CORROSION CRACKING. 2. THE MAOP WAS NOT EXCEEDED AND OVERPRESSURE WAS NOT A CONTRIBUTING FACTOR TO THE FAILURE. 3. INTERNAL OR EXTERNAL CORROSION WAS NOT A CONTRIBUTING FACTOR.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150041 | 16841 | 2015-03-30 20:36 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2015-02-28 | 2015 |  |  | 36.5762 | -121.9087 | 1109328 | 2015-02-28 |  | NATURAL GAS |  | 3784 | 204 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-02-28 15:10 | 2015-03-01 10:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 6 | 2015-02-28 11:45 | 2015-02-28 12:01 | ONSHORE | CA | 93923 | CARMEL | MONTEREY | MILEPOST | DFM 1815-15 | DFM 1815-15 | DFM 1815-15 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 30 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10 |  | 0.219 | 35000 | GRADE B | SEAMLESS |  | UNKNOWN | ASPHALT | [28 empty] | 1959 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 3 | 4 | [7 empty] | CLASS 3 LOCATION | NO |  | 132 |  | NO | NO | NO |  | 0 | 0 | 875 | 956.279147235177 | 16225 | 14511.0915492958 | 450000 | 491800.704292377 | 0 | 0 | 0 | 0 |  |  | 467100 | 241232.765206607 | 507268.074988908 | [8 empty] | 264 |  | 313 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 13400 | NO |  |  |  | YES |  |  |  | YES |  | YES | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA-RELATED EQUIPMENT OPERATED AS INTENDED | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  | YES | PRIVATE EASEMENT | YES | [6 empty] | CONTRACTOR | GRADER/SCRAPER | GRADING | NO | [5 empty] | YES | 19 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | CHERYL DIZON | COMPLIANCE ENGINEER | c1dz@pge.com | 925-328-5721 |  |  |  |  | LAURENCE DENISTON | MANAGER | 925-3285756 | lcd1@pge.com | ON FEBRUARY 28, 2015 AT 1133 HOURS PACIFIC GAS AND ELECTRIC'S (PG&E) GAS CONTROL ROOM RECEIVED A LOW PRESSURE ALARM ON DISTRIBUTION FEEDER MAIN (DFM) 1815-15 (A TRANSMISSION PIPELINE) AND IMMEDIATELY CONTACTED THE LOCAL SUPERVISOR TO VERIFY THE LOW PRESSURE READINGS IN THE FIELD. WHILE LOCAL FIELD PERSONNEL WAS EN ROUTE, AT 1145 HOURS, PG&E DISPATCH RECEIVED A REPORT OF THIRD PARTY DAMAGE TO PG&E'S PIPELINE NEAR 610 VIEJO RD IN CARMEL THAT RESULTED IN AN UNINTENTIONAL RELEASE OF GAS. A HOMEOWNER HIRED A DAY LABORER TO GRADE HIS PROPERTY FOR A NEW ROADWAY, AND THE DAY LABORER STRUCK THE 10-INCH STEEL TRANSMISSION LINE WITH A RIPPER TOOTH PULLED BY A BULLDOZER. THE HOMEOWNER AND THE LABORER DID NOT CALL USA. PG&E'S GAS SERVICE REPRESENTATIVE WAS ON SITE AT 1201 HOURS. CREWS WERE ON SITE AT APPROXIMATELY 1215 HOURS. FIRE DEPARTMENT, POLICE, AND LOCAL MEDIA WERE OBSERVED ON SCENE. HIGHWAY 1 WAS TEMPORARILY CLOSED IN BOTH DIRECTIONS, AND THE FIRE DEPARTMENT EVACUATED 6 HOMES OUT OF PRECAUTION. PG&E STOPPED THE FLOW OF GAS AT 1510 HOURS BY CLOSING FOUR MAINLINE VALVES TO ISOLATE THE IMPACTED PIPELINE SECTION. A DISTRIBUTION BACK-TIE AROUND THE DAMAGED DFM SECTION WAS ABLE TO SUPPLY GAS TO THE AFFECTED AREA. COMPRESSED NATURAL GAS WAS USED TO SUPPLEMENT GAS SUPPLY; HOWEVER PG&E HAD TO CURTAIL FOUR NON-CORE CUSTOMERS.. THE FOUR IMPACTED CUSTOMERS WERE ABLE TO HAVE GAS SERVICE RESTORED BY 1000 HOURS ON MARCH 1, 2015. ON MARCH 5, 2015, A VISUAL INTEGRITY ASSESSMENT WAS COMPLETED ON DFM 1815-15 AND NO ADDITIONAL DAMAGE WAS OBSERVED ON THE PIPE, SO DFM 1815-15 WAS RESTORED TO NORMAL OPERATING PRESSURE. THIS INCIDENT WAS REPORTED TO THE DOT AND THE CPUC DUE TO DAMAGES EXCEEDING $50,000.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150042 | 30088 | 2015-04-01 13:52 | SUPPLEMENTAL | 207 | ALASKA PIPELINE CO | 3000 SPENARD ROAD P.O. BOX 190288 | ANCHORAGE | AK | 99519 | 2015-02-03 16:09 | 2015 |  |  | 60.7131 | -150.1486 | 1110991 | 2015-03-17 14:30 |  | NATURAL GAS |  | 1300 | 3000 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-03-16 10:10 | 2015-03-20 15:50 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-02-03 16:09 | 2015-02-03 16:09 | ONSHORE | AK | 99572 | Not Within a Municipality | KENAI PENINSULA BOROUGH | MILEPOST | MP46 | B"-LINE | K10 | YES | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 16 |  | 0.312 | 46000 | API 5L X-46 | LONGITUDINAL ERW - HIGH FREQUENCY |  | KAISER | EXTRUDED POLYEHYLENE | [9 empty] | PIPE GIRTH WELD | [18 empty] | 1974 | 1974 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 358 |  | NO | NO | NO |  | 0 | 0 | 2300 | 2513.64804416104 | 1000 | 894.366197183099 | 60000 | 65573.4272389835 | 5000 | 5464.45226991529 | 0 | 0 |  |  | 68300 | 34689.3219856559 | 74445.893750243 | [8 empty] | 780 |  | 1050 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 103488 | NO | YES | [6 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [8 empty] | YES | INCOMPLETE ROOT | [12 empty] | YES | [63 empty] | NO | [63 empty] | NO |  |  | Yes, but the point of the Accident was not identified as a dig site |  | 2015 | [11 empty] | NO | [63 empty] | NATHAN BURKE | ENGINEER | nathan.burke@enstarnaturalgas.com | 907-334-7739 |  |  |  |  | NATHAN BURKE | ENGINEER | 9073347739 | nathan.burke@enstarnaturalgas.com | A PINHOLE LEAK WAS FOUND IN A GIRTH WELD DURING A ROUTING ANNUAL LEAK SURVEY. THE GAS LEAKAGE WAS MINIMAL. THE PIPELINE REMAINED IN SERVICE DURING A COLD SPELL, AND THEN IMMEDIATELY TAKEN OUT OF SERVICE. AFTER THE SECTION WAS REPLACED, IT WAS FOUND THAT THE WELD HAD AN INCOMPLETE ROOT PASS AND HAD A LESS THAN 3", HAIRLINE FRACTURE UNDERNEATH THE PINHOLE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150043 | 16704 | 2015-04-02 10:00 | ORIGINAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2015-03-13 11:15 | 2015 |  |  | 32.0308 | -90.3242 | 1110537 | 2015-03-13 11:30 |  | NATURAL GAS |  | 0 | 173 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-03-14 10:55 | 2015-03-14 15:33 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-03-13 06:35 | 2015-03-13 07:00 | ONSHORE | MS | 39059 | CRYSTAL SPRINGS | COPIAH | MILEPOST | 21 | MAGNOLIA 6" | INDEX 302 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 24 |  | YES |  |  |  |  | YES | UNCASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | REPAIR SLEEVE OR CLAMP | [38 empty] | UNKNOWN |  | CARBON STEEL |  | LEAK |  |  | OTHER | LEAKING SPLIT SLEEVE CLAMP | [5 empty] | CLASS 1 LOCATION | NO |  | 88 |  | NO | NO | NO |  | 12000 | 13114.6854477967 | 509 | 556.281241077377 | 0 | 0 | 40000 | 43715.6181593224 | 1000 | 1092.89045398306 | 0 | 0 |  |  | 53509 | 26843.6222518321 | 58479.4753021795 | [8 empty] | 420 |  | 447 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 28512 | NO | YES | YES |  | YES | YES |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS NOT LARGE ENOUGH TO BE DETECTED BY SCADA. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | RUBBER SEAL ON SPLIT SLEAVE CLAMP | [9 empty] | YES | [168 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 2706886361 | jeff.mcmaine@bwpmlp.com | THE RUBBER SEAL ON AN UNDERGROUND SPLIT SLEEVE CLAMP FAILED RESULTING IN LEAK.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150044 | 16705 | 2015-04-02 13:42 | ORIGINAL FINAL | 19730 | TRUNKLINE GAS CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2015-03-05 12:39 | 2015 |  |  | 35.9404 | -89.308 | 1109725 | 2015-03-05 12:55 |  | NATURAL GAS |  | 21900 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE COMPRESSOR UNIT AFFECTED WAS NOT REQUIRED TO MAINTAIN THROUGHPUT VOLUMES. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-03-05 05:55 | 2015-03-05 06:20 | ONSHORE | TN | 38024 | DYERSBURG | DYER | MILEPOST | 0.9 | DYERSBURG COMPRESSOR STATION | UNIT 5701 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1985 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 124 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 71613 | 64048.2464788732 | 13 | 14.2075759017798 | 0 | 0 | 0 | 0 |  |  | 71626 | 66408.2470043445 | 64062.454054775 | [8 empty] | 822 |  | 900 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EQUIPMENT FAILURE IN THE FIELD. | [12 empty] | YES | 1 | 0 | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | PIPE NIPPLE | [19 empty] | YES | CARBON STEEL NIPPLE | [161 empty] | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | THERE WERE TWO SEPARATE RELEASES FROM THE SAME DEVICE RELATED TO THIS INCIDENT REPORT. LISTED BELOW ARE THE SPECIFICS FOR EACH RELEASE: PART A.10 - THE ESTIMATED VOLUME RELEASED UNINTENTIONALLY FOR THE FIRST RELEASE WAS 4.3 MMCF. THE ESTIMATED VOLUME RELEASED UNINTENTIONALLY FOR THE SECOND RELEASE WAS 17.6 MMCF. PART A.19.A - THE TIME THE OPERATOR IDENTIFIED THE FIRST RELEASE WAS 03:06. THE TIME THE OPERATOR IDENTIFIED THE SECOND RELEASE WAS 05:55. PART A.19.B - THE TIME THE OPERATOR RESOURCES ARRIVED ON SITE FOR THE FIRST RELEASE WAS 03:40. THE TIME THE OPERATOR RESOURCES ARRIVED ON SITE FOR THE SECOND RELEASE WAS 06:20. PART D.7.F - THE ESTIMATED COST OF THE GAS RELEASED FOR THE FIRST RELEASE WAS $14,061. THE ESTIMATED COST OF THE GAS RELEASED FOR THE SECOND RELEASE WAS $57,552. PART E.1 - THE ESTIMATED PRESSURE AT THE POINT AND TIME OF THE INCIDENT FOR THE FIRST RELEASE WAS 858 PSIG. THE ESTIMATED PRESSURE AT THE POINT AND TIME OF THE INCIDENT FOR THE SECOND RELEASE WAS 822 PSIG. PART G: APPARENT CAUSE: FOR THE FIRST RELEASE - PART G.6 EQUIPMENT FAILURE SUB-CAUSE - WAS THE RELIEF VALVE SOLENOID FROZE. FOR THE SECOND RELEASE - PART G.6.3 EQUIPMENT FAILURE SUB-CAUSE - WAS A PIPE NIPPLE FAILED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150045 | 17470 | 2015-04-02 13:53 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2015-03-15 16:10 | 2015 |  |  | 30.3964 | -93.2926 | 1110747 | 2015-03-15 16:48 |  | NATURAL GAS |  | 10 | 235 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-05-16 10:15 | 2017-05-18 13:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-03-15 16:10 | 2015-03-15 16:10 | ONSHORE | LA | 70633 | DEQUINCY | CALCASIEU | MILEPOST | 40.3 | CALL JUNCTION TO IOWA COMPRESSOR STATION | INDEX 201 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 84 |  | YES | [6 empty] | YES | UNCASED | HICKORY FLAT CREEK | 11 | BELOW WATER, PIPE ON OR ABOVE BOTTOM | [11 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 14 |  | 0.281 | 33000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | AO SMITH | ASPHALT | [28 empty] | 1931 | 1931 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 198 |  | NO | NO | NO |  | 0 | 0 | 900 | 983.601408584753 | 25 | 22.3591549295775 | 197208 | 215526.740649091 | 400 | 437.156181593224 | 0 | 0 |  |  | 198533 | 99607.807000341 | 216969.857394199 | [8 empty] | 375 |  | 419 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 47520 | NO |  | YES | YES | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS TOO SMALL FOR SCADA TO DETECT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | OTHER | BECAUSE THIS LOCATION WAS UNDERWATER, NO VISUAL OBSERVATION COULD BE MADE; DIVERS WERE ABLE TO FEEL "SCALES" OR AN UNEVEN SURFACE ON THE PIPE. IN THE VALLEYS OF THE SCALE, DIVERS COULD FEEL GAS LEAKING. | YES | [10 empty] | YES | DIVERS MADE THE DETERMINATION | NO | [11 empty] | YES | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | SHANNON MATTINGLY | PA OQ AND EVENT SUPPORT PROGRAM LEADER | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 2706886361 | jeff.mcmaine@bwpmlp.com | LEAK DISCOVERED ON PIPELINE THAT IS 7 FEET UNDER WATER IN A CREEK WITH A MUD LINE AT 11 FEET. PRESSURE WAS LOWERED FROM 375 PSIG TO 300 PSIG. INITIAL INDICATIONS ARE THAT THIS IS A FITTING LEAK. WHEN WATER RECEDES, REMEDIATION WILL OCCUR. UNTIL THAT TIME, THIS SECTION OF LINE REMAINS ISOLATED AND PRESSURE LOWERED. 2-12-16 LEAK IS LOCATED IN A DEEP CREEK IN A NARROW RIGHT OF WAY. FOR THIS REASON, REPAIR IS SCHEDULED FOR JULY/AUGUST 2016 TIME FRAME WHEN WATER LEVELS WILL BE LOWER AND PERMITTING CAN BE OBTAINED. 3-30-17 GULF SOUTH EXPECTS TO REPAIR IN LATE APRIL 2017. 5-18-17 GULF SOUTH CUT AND CAPPED THE LINE. THE FINAL REPORT IS BEING SUBMITTED NOW (9-26-17) BECAUSE OF THE AMOUNT OF TIME REQUIRED TO BE ABLE TO CORRECTLY DOCUMENT THE REPAIR COSTS. 10-16-17 REVISED APPARENT CAUSE TO EXTERNAL CORROSION BASED ON ADDITIONAL INFORMATION RECEIVED AND ANSWERED ADDITIONAL QUESTIONS THAT RESULTED FROM THAT CHANGE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150046 | 16759 | 2015-04-02 18:10 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2015-03-04 23:00 | 2015 |  |  | 30.0088 | -97.4188 | 1109679 | 2015-03-05 01:35 |  | NATURAL GAS |  | 6190 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELIEF VALVE RESET ITSELF | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-03-04 23:08 | 2015-03-05 00:05 | ONSHORE | TX | 78602 | BASTROP | BASTROP | MILEPOST | VALVE STATION | HILBIG REGULATOR STATION | BASTROP LATERAL-LINE 36 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2012 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE VENTED PREMATURELY. | CLASS 1 LOCATION | NO |  | 373 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 18260 | 16331.1267605634 | 0 | 0 | 200 | 218.578090796612 | 100 | 109.289045398306 | COST FOR TECHNICIANS LABOR AND TIME FOR TESTING/INSPECTION OF RELIEF VALVE. |  | 18560 | 17081.7203241657 | 16658.9938967583 | [8 empty] | 697 |  | 730 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY. LEAK WAS NOT DETECTABLE BY CONTROLLER IN THE CONTROL ROOM; THEREFORE, CONTROLLER WAS NOT THE CAUSE NOR A CONTRIBUTING FACTOR TO THE INCIDENT. NO OTHER FACTORS WERE DETERMINED REQUIRING AN INVESTIGATION. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | ACCUMULATION OF HYDRATES IN PILOT/SENSING LINE AND FREEZING TEMPERATURES | [161 empty] | MICHAEL D. SMITH | COMPLIANCE SPECIALIST | mdsmith@eprod.com | 713-381-5650 |  |  |  |  | MICHAEL D. SMITH | COMPLIANCE SPECIALIST | 713-381-5650 | mdsmith@eprod.com | ON 3/4/2015 AT 23:00 THE 8 INCH RELIEF VALVE AT THE HILBIG REGULATOR STATION FOR LINE 36 PREMATURELY ACTUATED VENTING NATURAL GAS TO THE ATMOSPHERE. A NEARBY RESIDENT REPORTED THE EVENT TO ENTERPRISE PIPELINE CONTROL AT 23:08 AND AN ENTERPRISE TECHNICIAN WAS DISPATCHED TO THE HILBIG REGULATOR STATION. UPON TECHNICIAN'S ARRIVAL AT 00:05 ON 3/5/2015, THE TECHNICIAN FOUND THE RELIEF VALVE HAD RESET ITSELF. UPON FURTHER INVESTIGATION, IT WAS DISCOVERED THAT THE RELIEF VALVE OPERATED PREMATURELY BELOW ITS SET POINT. THE CAUSE FOR THE PREMATURE ACTUATION WAS DUE TO HYDRATES FREEZING IN THE PILOT REGULATOR/SENSING LINE. LATER ON 3/5/2015, THE RELIEF VALVE WAS TESTED SEVERAL TIMES AND FUNCTIONED PROPERLY EACH TIME AT THE DESIRED SET POINT. THE CORRECTIVE ACTION TO PREVENT FUTURE RECURRENCE INCLUDES REPLACING PILOT WITH ONE MORE SUITABLE FOR COLDER TEMPERATURES AND INSTALLING A KNOCK-OUT CYLINDER IN SENSING LINE. CORRECTIVE ACTION TAKEN: INSTALLED NEW REGULATOR WITH FILTER.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150047 | 16710 | 2015-04-02 18:30 | ORIGINAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2015-03-09 05:00 | 2015 |  |  | 30.0148 | -99.5007 | 1109995 | 2015-03-09 07:40 |  | NATURAL GAS |  | 6600 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | COMPRESSOR UNIT WAS NOT SHUT DOWN DUE TO HAVING REDUNDANT RELIEF VALVES | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-03-09 06:00 | 2015-03-09 06:00 | ONSHORE | TX | 78873 | LEAKY | REAL | MILEPOST | REAL STATION | GREY RANCH-NEW BRAUNFELS @ REAL COMPRESSOR STATION | LINE 146-GREY RANCH-NEW BRAUNFELS | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2006 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE RELIEVED PREMATURELY DUE TO LEAK IN SENSING LINE CAUSED BY EXCESSIVE VIBRATION | CLASS 1 LOCATION | NO |  | 644 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 16480 | 14739.1549295775 | 225 | 245.900352146188 | 0 | 0 | 0 | 0 |  |  | 16705 | 15393.6259238755 | 14985.0552817237 | [8 empty] | 765 |  | 858 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY. SINCE THE CONTROLLER OR CONTROL ROOM DID NOT CAUSE NOR CONTRIBUTE TO THE INCIDENT. NO PRESSURE ALARM THRESHOLDS WERE MET; NO ALARMS WERE ACTIVATED. NO OTHER FACTORS WERE DETERMINED REQUIRING AN INVESTIGATION. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | RELIEF VALVE RELIEVED PREMATURELY DUE TO LEAK IN SENSING LINE. | [161 empty] | MICHAEL D. SMITH | COMPLIANCE SPECIALIST | mdsmith@eprod.com | 713-381-5650 |  |  |  |  | MICHAEL D. SMITH | COMPLIANCE SPECIALIST | 713-381-5650 | mdsmith@eprod.com | AT 06:00 OPERATIONS TECHNICIAN ARRIVED AT THE REAL COMPRESSOR STATION AND DISCOVERED A RELIEF VALVE VENTING NATURAL GAS TO ATMOSPHERE ON THE C-200 COMPRESSOR UNIT. TECHNICIAN RESPONDED IMMEDIATELY AND CLOSED THE ISOLATION VALVE TO THE 3X4" RELIEF VALVE THUS, ENDING THE EVENT. THIS UNIT HAS TWO RELIEF VALVES ON THE UNIT OPERATING IN PARALLEL AS A REDUNDANT SYSTEM. UPON FURTHER INVESTIGATION, IT WAS DETERMINED THAT THE RELIEF VALVE LIFTED PREMATURELY DUE TO A LEAK ON THE SENSING LINE FOR THE RELIEF VALVE DUE TO EXCESSIVE VIBRATION. THE SENSING LINE TUBING WAS REPLACED WITH ADDITIONAL SUPPORTS TO PREVENT FUTURE RECURRENCE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150048 | 16718 | 2015-04-10 15:46 | ORIGINAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2015-03-13 11:22 | 2015 |  |  | 28.6974 | -91.8412 | 1110549 | 2015-03-13 12:22 |  | NATURAL GAS |  | 250 | 8700 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-03-13 17:27 | 2015-03-16 17:59 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-03-13 11:22 | 2015-03-15 13:27 | OFFSHORE | [28 empty] | 112 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EUGENE ISLAND | 200 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | OTHER | [37 empty] | THREADED PLUG | 1968 |  | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 359 |  | NO | NO | NO |  | 0 | 0 | 23500 | 25682.9256686019 | 1350 | 1207.39436619718 | 300000 | 327867.136194918 | 0 | 0 | 0 | 0 |  |  | 324850 | 163540.568025073 | 354757.456229717 | [8 empty] | 830 |  | 1380 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | AUTOMATIC | 97152 | NO | YES | [6 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | AIR PATROL |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SMALL SIZE OF THE LEAK | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | THREADED FITTING | [7 empty] | YES | [174 empty] | ROGER R. STREET | FIELD COMPLIANCE SPECIALIST | roger_street@transcanada.com | 8325702966 |  |  |  |  | ROBERT LATIMER | MANAGER U.S. REGULATORY COMPLIANCE | 402-332-8122 | rob_latimer@transcanada.com | ON 13 MARCH 2015 AT 11:22 CDT DURING A TRANSCANADA AVIATION FLIGHT OVER THE GULF OF MEXICO, A POTENTIAL LEAK WAS IDENTIFIED NEAR TC OFFSHORE (TCO) ASSETS IN THE OUTER CONTINENTAL SHELF (OCS) EUGENE ISLAND BLOCK 200 (EI-200). THE LEAK WAS REPORTED TO TRANSCANADA/ ANR PIPELINE, OPERATOR FOR TC OFFSHORE, AS A BUBBLING PATTERN OVER TCO'S 737 (20') TRANSMISSION PIPELINE NEAR MILE POST 15.6 (28.69737930, -91.84116430). NO SHEEN OR PRODUCT WAS OBSERVED AT THE LEAK LOCATION. THE NRC WAS NOTIFIED OF AN INCIDENT ON 13 MARCH 2015 AT 12:22 CDT (NRC REPORT #1110549). FOLLOWING THE REPORT OF THE INCIDENT TO THE NATIONAL RESPONSE CENTER, TRANSCANADA/ANR CONTACTED U.S. COAST GUARD, BSEE, AND PHMSA TO INFORM AND UPDATE THE AGENCIES ON THE INCIDENT. WHILE PREPARING TO DISPATCH AN INVESTIGATION AND REPAIR VESSEL TO THE SITE, A PIPELINE SEGMENT OF 18.4 MILES WAS ISOLATED AND BLOWN DOWN FROM 830 PSIG TO 200 PSIG FROM THE VALVES AT SOUTH MARSH ISLAND 76 TO EUGENE ISLAND 199. ADDITIONALLY, ANR SCHEDULED AERIAL PATROLS TO MONITOR THE LEAK. NO SHEEN OR PRODUCT WAS DOCUMENTED AT THE SITE FOR THE DURATION OF THE LEAK AND REPAIR. THE REPAIR VESSEL AND CONTRACT EMPLOYEES ARRIVED AT THE INCIDENT LOCATION ON 15 MARCH AT 13:27 CDT AND BEGIN EXPOSING THE PIPE FOR THE LEAK INVESTIGATION. FOLLOWING THE REMOVAL OF THE COVER MATERIAL, THE INVESTIGATION BY THE DIVERS DETERMINED THAT THE LEAK WAS CAUSED BY A DEFECT IN A BODY BLEED THREADED PLUG VALVE ON A 12-INCH SIDE VALVE. THE THREADED PLUG VALVE ON THE BODY BLEED WAS REPLACED ON 16 MARCH AT 17:59 CDT. FOLLOWING THE REPLACEMENT OF THE THREADED PLUG VALVE, THE LINE WAS INSPECTED TO CONFIRM THE REPAIR AND THE LINE AND VALVE WERE RE-COVERED. NO ADDITIONAL LEAKING WAS OBSERVED AND THE LINE WAS RETURNED TO SERVICE ON 17 MARCH 2015.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150049 | 16720 | 2015-04-13 16:43 | ORIGINAL FINAL | 31286 | ONEOK GAS TRANSPORTATION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2015-03-16 16:58 | 2015 |  |  | 35.5184 | -96.7694 | 1110885 | 2015-03-16 18:14 |  | NATURAL GAS |  | 201 | 13178 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-03-16 18:45 | 2015-03-17 20:09 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-03-16 16:18 | 2015-03-16 16:58 | ONSHORE | OK | 74864 | Not Within a Municipality | LINCOLN | MILEPOST | 35.5184 -096. | A-1300 24" | COUNTYLINE-HWY99 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 |  | 0.281 | 60000 | API-5LX60 | DSAW |  | KAISER STEEL | COAL TAR | [28 empty] | 1976 | 1976 | CARBON STEEL |  | MECHANICAL PUNCTURE | 0.3 | 0.3 | [7 empty] | CLASS 1 LOCATION | NO |  | 581 |  | NO | NO | NO |  | 500 | 546.445226991529 | 36791 | 40208.5326924907 | 561 | 501.739436619718 | 45000 | 49180.0704292377 | 6000 | 6557.34272389835 | 2800 | 3060.09327115257 | X-RAY |  | 91652 | 46217.393244879 | 100054.223780391 | [8 empty] | 570 |  | 800 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 77616 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | AUGER | UNKNOWN/OTHER | NO | [5 empty] | YES | 25 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | KAREN A PEREZ | REGULATORY COMPLIANCE COORDINATOR DOT | karen.perez@oneok.com | 918-595-1703 |  |  |  |  | WESLEY DUNBAR | VICE PRESIDENT NATURAL GAS PIPELINE OPERATIONS | 918-588-7424 | wesley.dunbar@oneok.com | ON 03-16-2015 AT 1618 GAS CONTROL RECEIVED A CALL ON EMERGENCY LINE FROM THIRD PARTY STATING THAT A CONTRACTOR HAD STRUCK A GAS LINE THAT COULD BELONG TO OGT NEAR HWY 62 AND CR3500 INTERSECTION, LINCOLN COUNTY, OK. CONTROLLER DETERMINED ONEOK GAS TRANSPORTATION (OGT) A1300 24" PIPELINE WAS WITHIN 1/2 MILE OF THE REPORTED LOCATION; THE CONTROLLER COULD NOT SEE AN INCREASE IN FLOW RATE AT PURCELL JUNCTION (DOWNSTREAM OF LINE STRIKE). CONTROLLER DISPATCHED OGT OPERATIONS PERSONNEL TO LOCATION; PIPELINE OPERATOR ARRIVED ON SITE AT 1658 AND CONFIRMED THAT OGT A1300 24" NATURAL GAS PIPELINE HAD BEEN STRUCK BY A THIRD PARTY POLE TRUCK; THERE WERE NO FATALITIES OR INJURIES, THERE WAS GAS ESCAPING BUT HAD NOT IGNITED. PIPELINE OPERATOR CONTACTED 911 AT 1710 TO MAKE THEM AWARE OF THE SITUATION. GAS FLOW INTO A1300 24" WAS CURTAILED WHICH AFFECTED (6) GAS PROCESSING PLANTS. THE PIPELINE WAS ISOLATED AT 1845 ON 03-16-2015. A NEW SECTION OF PIPELINE WAS INSTALLED TO REPAIR DAMAGED SEGMENT AND PIPELINE WAS RESTARTED AT 2009 ON 03-17-2015.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150050 | 16968 | 2015-04-15 08:22 | SUPPLEMENTAL FINAL | 6660 | GREAT LAKES GAS TRANSMISSION CO | 700 LOUISIANA STREET | HOUSTON | TX | 77002 | 2015-03-16 13:20 | 2015 |  |  | 48.602 | -96.6527 | 1110848 | 2015-03-16 14:19 |  | NATURAL GAS |  | 500 | 64020 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-03-16 14:30 | 2015-05-14 12:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-03-16 13:20 | 2015-03-16 13:20 | ONSHORE | MN | 56729 | Not Within a Municipality | KITTSON | MILEPOST | MLV 1-2 | MLV 1-2 | MP 33.40 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION | [19 empty] | FILLET WELD | [18 empty] | 1980 |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 835 |  | NO | NO | NO |  | 0 | 0 | 171570 | 187507.215189873 | 1340 | 1198.45070422535 | 546500 | 597264.633101742 | 40000 | 43715.6181593224 | 0 | 0 |  |  | 759410 | 381540.09652407 | 829685.917155163 | [8 empty] | 828 |  | 974 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | AUTOMATIC | 90077 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK, WHICH EMANATED FROM A SMALL CRACK IN A WELD, WAS OF SUCH A SMALL RATE THAT IT COULD NOT BE DETECTED BY THE CONTROL ROOM. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROST HEAVE |  | NO | [306 empty] | ROBERT CADORIN | REGULATORY COMPLIANCE SPECIALIST | robert_cadorin@transcanada.com | 248-205-7669 |  |  |  |  | ROBERT CADORIN | REGULATORY COMPLIANCE SPECIALIST | 248-205-7669 | robert_cadorin@transcanada.com | ON MARCH 16, 2015, LOCAL TRANSCANADA EMPLOYEES WERE NOTIFIED BY A LOCAL UTILITY EMPLOYEE OF A POSSIBLE GAS LEAK AT GREAT LAKES GAS TRANSMISSION COMPANY'S (GLGT) MAIN LINE VALVE 1-2 LOCATED AT APPROXIMATE MILEPOST 33.40 IN KITTSON COUNTY, MINNESOTA. TRANSCANADA EMPLOYEES FROM THE GLGT ST. VINCENT COMPRESSOR STATION NEAR ST. VINCENT, MINNESOTA, RESPONDED TO THE REPORT AND ARRIVED AT THE MLV SITE AT 1:20 PM CDT. WHEN EMPLOYEES ARRIVED AT THE MLV SITE, THEY OBSERVED THE VALVE SITE TO BE PARTIALLY FLOODED AND GAS BUBBLES TO BE EMANATING FROM NEAR THE BASE OF THE UPSTREAM 20-INCH BLOWDOWN VALVE (1-2-2Y) ON THE 200 LINE PIPELINE. USE OF A GAS DETECTOR REVEALED LOW LEVELS (APPROXIMATELY 10% LEL) OF GAS NEAR THE LEAK SITE. THE UPSTREAM PIPELINE SECTION BETWEEN MLV 1-1-2 TO MLV 1-2-2 WAS THEN SHUT IN AND ISOLATED FROM THE PIPELINE SYSTEM. AFTER PUMPING THE FLOODWATER FROM THE VALVE SITE, IT WAS DETERMINED THAT THE LEAK WAS ORIGINATING FROM A FILLET WELD ON A 2-INCH WELD-O-LET THAT CONNECTED A 2-INCH POWER GAS LINE TO THE 20-INCH BLOWDOWN RISER. THE UPSTREAM PIPELINE SECTION WAS THEN BLOWN DOWN TO ATMOSPHERIC PRESSURE. THIS POWER GAS LINE WAS CONNECTED TO THE RISER AT GROUND LEVEL. BECAUSE THIS CONNECTION WAS SITUATED AT GROUND LEVEL, IT WAS DETERMINED THAT OVER TIME FROST HEAVE PLACED STRESSES ON THE POWER GAS LINE, EVENTUALLY RESULTING IN THE FORMATION OF A CRACK ON THE LOWER SIDE OF THE SUBJECT FILLET WELD AND THE EVENTUAL LEAK. BASED ON THIS INFORMATION, THE POWER GAS CONNECTION TO THE DOWNSTREAM BLOWDOWN RISER WAS ALSO INSPECTED, WHICH REVEALED THE COATING TO BE CRACKED ON THE SIMILAR FILLET WELD AS THE UPSTREAM LOCATION. NONDESTRUCTIVE TESTING OF THIS WELD REVEALED THAT THE WELD WAS NOT CRACKED. NONE-THE-LESS, BASED ON THESE FINDINGS, IT WAS DETERMINED THAT BOTH THE UPSTREAM AND DOWNSTREAM POWER GAS CONNECTIONS WOULD BE REPLACED. AT THIS POINT, THE DOWNSTREAM PIPELINE SECTION BETWEEN MLV 1-2-2 AND MLV 1-3-2 WAS SHUT IN, ISOLATED FROM THE PIPELINE SYSTEM, AND BLOWN DOWN TO ATMOSPHERIC PRESSURE. IN ADDITION TO THE REPLACEMENT OF THE POWER GAS PIPING, SECTIONS OF BOTH THE UPSTREAM AND DOWNSTREAM 20-INCH RISERS WERE REPLACED BECAUSE THE POWER GAS CONNECTIONS WERE RELOCATED TO MORE SUITABLE LOCATIONS ON THE FACILITY PIPING, MITIGATING THE EFFECTS OF ANY FUTURE FROST HEAVE ACTIVITY. REPAIR ACTIVITIES WERE COMPLETED AND THE FACILITIES PLACED BACK INTO SERVICE ON MAY 14, 2015.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150051 | 17013 | 2015-04-16 10:43 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2015-04-04 19:27 | 2015 |  |  | 42.4385 | -91.2876 | 1112585 | 2015-04-05 00:10 |  | NATURAL GAS |  | 3448 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-04-04 21:40 | 2015-04-05 00:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-04-04 15:52 | 2015-04-04 21:00 | ONSHORE | IA | 52041 | Not Within a Municipality | DELEWARE | MILEPOST | 54.51 | EARLVILLE COMPRESSOR STATION | IA-074 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | UNKNOWN |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | RUBBER | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 556 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 8500 | 7602.11267605634 | 1200 | 1311.46854477967 | 240 | 262.293708955934 | 0 | 0 |  |  | 9940 | 8603.85380012699 | 9175.87492979194 | [8 empty] | 425 |  | 960 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | YES | [6 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | THE O-RING ON THE PILOT ON THE RELIEF VALVE WAS FOUND TO BE DETERIATED. | [15 empty] | YES | NO OTHER FACTORS | [161 empty] | J. DAVID CULLISON | PIPELINE SAFETY ENGINEER | j.cullison@nngco.com | 402-398-7439 | 402-548-5267 |  |  |  | THOMAS CORRELL | SR. DIRECTOR OF PIPELINE SAFETY AND RISK | 402-398-7715 | thomas.correll@nngco.com | A NEAR-BY RESIDENT REPORTED A NOISE AT THE EARLVILLE, IOWA, COMPRESSOR STATION AT 19:30 HOURS ON 4/4/15. OPERATIONS RESPONDED AND AND FOUND THE FISHER 399 FUEL RUN RELIEF VALVE VENTING. OPERATIONS ISOLATED THE FUEL RUN TO STOP THE VENTING GAS. INVESTIGATION FOUND THE FISHER 6356EBH RELIEF VALVE PILOT WAS NOT HOLDING THE SET POINT AND OPERATING PREMATURELY. OPERATIONS REPLACED THE FISHER 6358EBH-5 PILOT WITH A NEW ASSEMBLY. THE NEW ASSEMBLY WAS TESTED AND VERIFIED AT THE SET POINT OF 450 PSIG. DISASSEMBLY OF THE FISHER 6358EBH PILOT DISCOVERED A FAILED O-RING UNDER THE DIAPHRAGM. THE FAILED O-RING IS ATTRIBUTED TO THE PREMATURE OPERATION OF THE RELIEF VALVE. A TREND OF THE FUEL RUN PRESSURE WAS REVIEWED AND A PRESSURE DROP WAS OBSERVED AT 15:52 HOURS ON 4/4/15. WE DETERMINED THIS WAS THE TIME THAT THE RELIEF VALVE STARTED VENTING. THE SCADA SYSTEM HAD A HIGH ALARM SET AT 490 PSIG AND THE PRESSURE NEVER EXCEEDED 435 PSIG, SO NO ALARM NOTIFICATION WAS RECEIVED. THE ALARM HAS BEEN ADJUSTED TO 425 PSIG TO PREVENT FUTURE OCCURANCES WITH NO ALARM NOTIFICATIONS.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150052 | 16723 | 2015-04-16 14:26 | ORIGINAL FINAL | 31978 | ATMOS PIPELINE - TEXAS | 5420 LBJ FREEWAY, SUITE 1800 | DALLAS | TX | 75240 | 2015-03-19 15:47 | 2015 |  |  | 33.1229 | -97.0262 | 1111214 | 2015-03-19 18:09 |  | NATURAL GAS |  | 5793 | 1268 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-03-19 16:40 | 2015-03-20 11:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 8 | 2015-03-19 15:47 | 2015-03-19 16:20 | ONSHORE | TX | 75065 | LAKE DALLAS | DENTON | SURVEY STATION NO. | 1781+30 | F | F | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 120 |  | YES |  |  |  |  | YES | UNCASED | [16 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12.75 |  | 0.25 | 42000 | X42 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1982 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 4 | 5 | [7 empty] | CLASS 3 LOCATION | YES | METHOD1 | 197 |  | NO | NO | NO |  | 20000 | 21857.8090796612 | 3800 | 4152.98372513562 | 17400 | 15561.9718309859 | 25000 | 27322.2613495765 | 10000 | 10928.9045398306 | 0 | 0 |  |  | 76200 | 45631.7375270946 | 79823.9305251898 | [8 empty] | 332 |  | 500 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 18988 | NO | YES | YES | YES | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE WAS DUE TO 3RD PARTY, NO CONTROLLER ISSUES WERE PRESENT | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | YES | [7 empty] | NO | YES | INTERSTATE HIGHWAY | [9 empty] | UTILITY | BORING | TELECOMMUNICATIONS | YES | 1557503534 | TEXAS811 | CONTRACT LOCATOR | YES | YES | YES | 19 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO VERIFY LOCATION BY TEST-HOLD (POT-HOLING) | [263 empty] | JAMES M. DOYLE | COMPLIANCE SUPERVISOR | james.doyle@atmosenergy.com | 254-722-7844 | 940-380-7466 |  |  |  | L. A. TREADWAY | COMPLIANCE DIRECTOR | 214-206-2044 | andy.treadway@atmosenergy.com | THIRD PARTY EXCAVATOR HAD CALLED IN, AND ACCURATE LOCATES WERE PERFORMED. THE THIRD PARTY EXCAVATOR DID NOT CONTACT THE OPERATOR PRIOR TO EXPOSING THE ACTIVE PIPELINE. THE EXCAVATOR EXPOSED AN ABANDONED SECTION OF 16" PIPE, THEY ASSUMED IT TO BE ACTIVE. THE EXCAVATOR DID NOT CONTACT THE OPERATOR TO CONFIRM IF THE LINE WAS ACTIVE OR NOT. DURING THE BORING PROCESS, THE ACTIVE 12" LINE WAS STRUCK. THE 12" LINE WAS 8.5 FEET BELOW THE ABANDONED 16" LINE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150053 | 16740 | 2015-04-17 08:08 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2015-03-28 11:20 | 2015 |  |  | 32.1956 | -97.444 | 1111962 | 2015-03-28 11:30 |  | NATURAL GAS |  | 7450 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-03-28 08:10 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-03-28 07:20 | 2015-03-28 08:10 | ONSHORE | TX | 76048 | GRANDBURY | HOOD | MILEPOST | DECORDOVA | NORTH TEXAS GAS SYSTEM | LINE 225 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | UNKNOWN |  | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 805 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 18625 | 16657.5704225352 | 45000 | 49180.0704292377 | 500 | 546.445226991529 | 0 | 0 |  |  | 64125 | 40095.4424358722 | 66384.0860787644 | [8 empty] | 925 |  | 1041 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY. LEAK WAS DETECTABLE BUT DID NOT MEET ALARM THRESHOLDS OR REPORTING CRITERIA BY THE CONTROLLER IN THE CONTROL ROOM; THEREFOR, CONTROLLER WAS NOT THE CAUSE NOR A CONTRIBUTING FACTOR TO THE INCIDENT. NO OTHER FACTORS WERE DETERMINED REQUIRING AN INVESTIGATION. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | COMPRESSOR UNIT 812 SUCTION VALVE | [22 empty] | YES | VALVE SEATS AND ACTUATOR FAILURE | [161 empty] | MICHAEL D. SMITH | COMPLIANCE SPECILIEST | mdsmith@eprod.com | 713-381-5650 |  |  |  |  | MICHAEL D. SMITH | COMPLIANCE SPECILIEST | 713-381-5650 | mdsmith@eprod.com | ON 3/28/2015 AT 07:20 AM, GAS CONTROL RECEIVED A CALL FROM A THIRD PARTY REPORTING A POSSIBLE LEAK AT THE DECORDOVA COMPRESSOR STATION AND AN ENTERPRISE TECHNICIAN WAS DISPATCHED TO THE DECORDOVA COMPRESSOR STATION. UPON THE TECHNICIANS ARRIVAL AT APPROXIMATELY 08:10 AM, THE TECHNICIAN DISCOVERED THAT THE UNIT SUCTION VALVE ON UNIT 810 DID NOT COMPLETELY CLOSE (90% CLOSURE) AT TIME GAS CONTROL REMOTELY SHUT DOWN COMPRESSOR (SCHEDULED SHUTDOWN). THE TECHNICIAN MANUALLY SHUT THE VALVE, THUS ENDING THE UNINTENTIONAL GAS THROUGH THE BLOW DOWN STACK. THE VALVE WAS TESTED SEVERAL TIMES AND FOUND TO BE FAULTY WITH WORN VALVE SEATS AND A BAD ACTUATOR. UNIT 810 HAS BEEN TAKEN OUT OF SERVICE UNTIL FURTHER NOTICE (LOCKED OUT-TAGGED OUT). A NEW VALVE AND ACTUATOR HAVE BEEN ORDERED FOR REPLACEMENT/REPAIR. ON 4/23/2015, NEW VALVE AND ACTUATOR INSTALLATION HAS BEEN COMPLETED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150054 | 16881 | 2015-04-19 22:44 | SUPPLEMENTAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2015-03-23 10:35 | 2015 |  |  | 33.444 | -81.9374 | 1111552 | 2015-03-23 15:39 |  | NATURAL GAS |  | 2450 | 2136 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-03-23 20:08 | 2015-03-26 13:55 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-03-23 10:35 | 2015-03-23 10:35 | ONSHORE | GA | 30901 | AUGUSTA | RICHMOND | MILEPOST | M.P. 491.127 | DSM CHEMICAL METER STATION | SOUTH MAINLINE LOOP | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | HOT TAP EQUIPMENT | [38 empty] | 2003 |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 2 LOCATION | NO |  | 422 |  | NO | NO | NO |  | 0 | 0 | 5489 | 5998.87570191301 | 6296 | 5630.92957746479 | 220000 | 240435.899876273 | 80000 | 87431.2363186447 | 0 | 0 |  |  | 311785 | 159091.149502835 | 339496.941474295 | [8 empty] | 1099 |  | 1200 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 21009 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS NOT CAUSED BY ANY OF THE OPERATOR OR CONTROLLERS ACTIONS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | HOT TAP ASSEMBY | [22 empty] | YES | TBD BY INVESTIGATION. INVESTIGATION IS PENDING. | [161 empty] | STEPHEN R. DINES | ENGINEER | stephen_dines@kindermorgan.com | 719 329-5633 |  |  |  |  | REJI GEORGE | DIRECTOR OF ENGINEERING CODES AND STANDARDS | 713 420-5433 | reji_george@kindermorgan.com | ON MARCH 23, 2015, A NATURAL GAS LEAK WAS DISCOVERED ON THE SOUTHERN NATURAL GAS SOUTH MAIN LINE LOOP AT THE INTERCONNECT WITH DSM CHEMICAL TAP. THE SOUTH MAIN LINE LOOP WAS DEPRESSURIZED AND REMOVED FROM SERVICE AND REPAIRS WERE INITIATED. A CRACKED WELD WAS DISCOVERED ON THE HOT TAP FITTING. THE SECTION OF PIPE CONTAINING THE HOT TAP ASSEMBLY WAS REPLACED WITH NEW PRETESTED SEGMENT OF PIPE. SNG WILL COMPLETE INSTALLATION OF A NEW HOT TAP ASSEMBLY. NO CUSTOMER SERVICE WAS IMPACTED BY THE INCIDENT. AN INVESTIGATION INTO THE ROOT CAUSE OF THE INCIDENT IS CURRENTLY UNDERWAY. THE METALLURGICAL REPORT REGARDING THE NPS 16 X NPS 6 HOT TAP FITTING AT THE DSM CHEMICAL METER STATION AT MP 491.127 IN RICHMOND COUNTY, GA ON THE SOUTHERN NATURAL GAS (SNG) SOUTH MAIN LOOP LINE WAS COMPLETED JUNE 2015. THE SIGNIFICANT CONCLUSIONS PRESENTED IN THE REPORT INCLUDED THE FOLLOWING: - THE HOT TAP FITTING LEAKED AT THE TOE OF THE CIRCUMFERENTIAL FILLET WELD JOINING THE FITTING TO THE IN-SERVICE PIPE. - THE LEAK WAS DUE TO A HYDROGEN CRACK AT THE TOE OF THE WELD. - THE UNUSUALLY HIGH CARBON EQUIVALENT OF THE IN-SERVICE PIPE WAS A SIGNIFICANT FACTOR CONTRIBUTING TO THE CRACKING. THE ROOT CAUSE INVESTIGATION IDENTIFIED THE UNUSUALLY HIGH CARBON EQUIVALENT OF THE IN-SERVICE PIPE AS A SIGNIFICANT FACTOR CONTRIBUTING TO THE CRACKING. A REVIEW OF AVAILABLE RECORDS WAS COMPLETED FOLLOWING THE ROOT CAUSE INVESTIGATION TO IDENTIFY ANY OTHER SEGMENTS ON THE SOUTH MAIN LOOP LINE, WITH SAME VINTAGE OF PIPE AND TAPS, THAT MAY EXIST AND REQUIRE FURTHER INVESTIGATION OR MONITORING. FROM A REVIEW OF THE AVAILABLE RECORDS, NO OTHER HOT-TAPS ON PIPE CONTAINING A HIGH CARBON EQUIVALENT WERE IDENTIFIED. FROM THIS REVIEW, SNG DETERMINED THAT OTHER TAPS OR CONNECTIONS WERE EITHER WELD-IN FITTINGS, WHICH ARE NOT AS PRONE TO HYDROGEN CRACKING, OR WERE INSTALLED ON A DIFFERENT VINTAGE OF PIPE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150055 | 16947 | 2015-04-20 18:02 | SUPPLEMENTAL FINAL | 38987 | KINETICA ENERGY EXPRESS LLC | 1001 MCKINNEY STREET, SUITE 900 | HOUSTON | TX | 77002 | 2015-03-26 14:05 | 2015 |  |  | 29.7306 | -92.9659 | 1111811 | 2015-03-26 15:48 |  | NATURAL GAS |  | 180 | 180 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-03-26 14:30 | 2015-04-01 16:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-03-26 14:30 | 2015-03-26 14:30 | ONSHORE | LA | 70643 | Not Within a Municipality | CAMERON | MILEPOST | VALVE STATION | 507F-100 | 507F-100 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | BURIED UNDERWATER IN A PIPELINE CANAL | 86 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 26 |  | 0.5 | 52000 | L5 | DSAW |  | A.O. SMITH | COAL TAR | [28 empty] | 1970 | 1968 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO | NO |  | 0 | 0 | 400 | 437.156181593224 | 500 | 447.183098591549 | 225000 | 245900.352146188 | 3000 | 3278.67136194918 | 0 | 0 |  |  | 228900 | 115044.028081436 | 250063.362788322 | [8 empty] | 744 |  | 1247 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 41600 | NO |  |  | YES |  |  |  |  | YES |  |  |  |  | YES | TOOL WILL NOT FIT IN THE LAUNCHER | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE WAS OPERATING WELL BELOW MOP / MAOP. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES | [5 empty] | YES | PIPE IS SUBMERGED. WE CAN ONLY MAKE A DETERMINATION BASED ON DISCUSSIONS WITH OUR CORROSION CONTROL CONSULTANTS. IN ACCORDANCE WITH CORROSION CONTROL MANUAL, PIPE IS ROUTINELY PIGGED, INHIBITOR IS INJECTED, PIGGING MATERIAL ANALYZED FOR CORROSIVENESS, AND CORROSION COUPONS INSTALLED/MONITORED. |  |  |  |  | YES | WELD AT 5:00 POSITION | YES | NO | YES | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KURT CHERAMIE | SR. DIRECTOR | kurt.cheramie@kineticallc.com | 985-209-2283 |  |  |  |  | KURT CHERAMIE | SR. DIRECTOR | 985-209-2283 | kurt.cheramie@kineticallc.com | DURING A LOCATION VISIT WITH THE LAND OWNER, OUR RIGHT OF WAY DIRECTOR SAW UNUSUAL INFREQUENT DISTURBANCE ON THE TOP OF THE WATER IN THE PIPELINE CANAL FOR THE 507F-100 PIPELINE. THE DISTURBANCE OF THE WATER SURFACE WAS NOT CONSISTENT WITH A PIPELINE LEAK AND APPEARED TO BE RELATED TO SWAMP GAS. OUR OPERATIONS DIRECTOR MADE A DECISION TO DISPATCH A SHALLOW WATER DIVE PACKAGE TO THE LOCATION TO INVESTIGATE THE POTENTIAL FOR A MAINTENANCE LEAK. UPON EXCAVATION, IT WAS DETERMINED THAT THERE WAS VERY SMALL, INTERMITTENT BUBBLES BEING RELEASED. THE PIPE WAS CLEANED AND PREPPED AND A REPAIR CLAMP WAS INSTALLED. UPDATED: DISTANCE BETWEEN VALVES. EXPLANATION FOR SUSPECTED MIC
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150056 | 32420 | 2015-04-21 16:23 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2015-03-25 06:00 | 2015 |  |  | 38.8758 | -78.8606 | 1111665 | 2015-03-25 06:59 |  | NATURAL GAS |  | 5446 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE FAULTY BLOW-OFF VALVE WAS ON THE COMPRESSOR STATION HEADER | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-03-25 05:45 | 2015-03-25 05:50 | ONSHORE | WV | 26812 | MATHIAS | HARDY | MILEPOST | 8-IN BO VALVE | LOST RIVER COMPRESSOR STATION | C10-94 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1997 |  | CARBON STEEL |  | OTHER | [8 empty] | BLOW-OFF VALVE INADVERTENTLY RELIEVED NATURAL GAS INTO ATMOSPHERE | CLASS 2 LOCATION | NO |  | 752 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 15359 | 13736.5704225352 | 0 | 0 | 0 | 0 | 0 | 0 | NO ADDITIONAL COSTS DID INCUR IN LIEU OF THIS INCIDENT |  | 15359 | 14241.3262910798 | 13736.5704225352 | [8 empty] | 700 |  | 1000 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE FAULTY BLOW-OFF VALVE WAS OUTSIDE THE MONITORED SEGMENT OF THE COMPRESSOR STATION WITHIN THE SCADA SYSTEM. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [18 empty] | YES | [172 empty] | CHRIS LEGG | US REGULATORY COMPLIANCE SPECIALIST | chris_legg@transcanada.com | 304-545-4350 |  |  |  |  | GEORGE HAMATY | MANAGER US REGULATORY COMPLIANCE | 304-357-3728 | george_hamaty@transcanada.com | ON MARCH 25TH, 2015, AN 8-IN BLOW-OFF VALVE RELEASED INADVERTENTLY MATERIAL INTO ATMOSPHERE AT LOST RIVER COMPRESSOR STATION LOCATED IN THE TOWN OF MATHIAS, HARDY COUNTY, WV. THE COMPRESSOR STATION HEADER WAS ISOLATED AND THE SECTION WAS BLOWN DOWN TO STOP THE UNINTENDED RELEASE. PRELIMINARY INVESTIGATIONS INDICATED THAT THE SUPPLY TUBING HAD A LOW POINT THAT ALLOWED FOR THE COLLECTION OF MOISTURE WHICH, APPARENTLY, FROZE AND ISOLATED THE ACTUATOR FROM THE EMERGENCY SHUTDOWN (ESD) TRIGGER AIR SUPPLY. THEN, A NUISANCE LEAK WAS FOUND IN THE LAST TUBING CONNECTION TO THE ACTUATOR. THE COMBINATION OF THESE TWO FINDINGS, ALLOWED THE ESD TRIGGER PRESSURE ON THIS VALVE ACTUATOR TO LEAK DOWN TO THE POINT THE VALVE ACTUATED INADVERTENTLY, RELEASING MATERIAL INTO ATMOSPHERE. AS A RECOMMENDATION, (I) AN INSPECTION TO ESD VALVES WITH SIMILAR INSTALLATIONS WAS TO BE PERFORMED, (II) RE-ROUTING TO THE TUBING WAS INTRODUCED TO PREVENT THE COLLECTION OF THIS MOISTURE COLLECTION AND (III) RESEARCH THE INTRODUCTION OF AN ALARM WHENEVER ANY UPSET CONDITIONS DO EXIST TO SIMILAR VALVE INSTALLATIONS. THESE STEPS WILL NOT ALLOW THE CHAIN OF EVENTS LEADING TO THE ACTIVATION OF THE BLOW-OFF VALVE FROM FUTURE RE-OCCURRENCE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150057 | 16874 | 2015-04-24 14:33 | SUPPLEMENTAL FINAL | 4060 | DOMINION EAST OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2015-03-25 09:30 | 2015 |  |  | 40.4121 | -81.5483 | 1111688 | 2015-03-25 12:02 |  |  |  | 774 | 4514 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-03-24 11:53 | 2015-03-28 13:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-03-09 12:00 | 2015-03-24 07:00 | ONSHORE | OH | 44663 | NEW PHILADELPHIA | TUSCARAWAS | SURVEY STATION NO. | 2110+40 | L#259 | 470420089 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 84 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 |  | 0.312 | 52000 | API 5LX | SEAMLESS |  | U.S. STEEL | COAL TAR | [28 empty] | 1966 | 1966 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 470 |  | NO | NO | NO |  | 0 | 0 | 22524 | 24616.2645855144 | 3870 | 3461.19718309859 | 51800 | 56611.7255163225 | 5000 | 5464.45226991529 | 0 | 0 |  |  | 83194 | 43382.4988692984 | 90153.6395548508 | [8 empty] | 545 |  | 675 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 58132 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DEO DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER'S ACTIONS OR CONTROL ROOM WAS NECESSARY | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | YES | [6 empty] | YES | [21 empty] | YES | SETTLEMENT OF THE BRANCH CONNECTION DUE TO IMPROPER SUPPORT | [55 empty] | YES | YES | [6 empty] | 2010 | [55 empty] | NO |  |  | NO | [13 empty] | YES |  |  |  |  | 2015 | [6 empty] | YES | [51 empty] | AARON MCCOY | TECHNICAL SPECIALIST | aaron.m.mccoy@dom.com | 3304589186 | 3304783760 |  |  |  | AARON MCCOY | TECHNICAL SPECIALIST | 3304589186 | aaron.m.mccoy@dom.com | ON MARCH 25, 2015 AT APPROXIMATELY 9:30 A.M., WHILE WORKING TO REPAIR A GRADE 2 LEAK A CRACK ON A DOMINION FACILITY NEAR THE PAD SADDLE AROUND THE TAP WAS DISCOVERED. ON MARCH 26, 2015, THE SECTION OF PIPE WAS CUT OUT AND REPLACED. PRESSURE WAS RESTORED AND THE LINE WAS PUT BACK INTO SERVICE ON MARCH 28, 2015 AT APPROXIMATELY 1:00 P.M. THE SECTION OF PIPE THAT LEAKED WAS SENT TO A 3RD PARTY LABORATORY FOR FAILURE ANALYSIS. THE RESULT OF THE 3RD PARTY ANALYSIS DETERMINED THAT THE FAILURE WAS CAUSED BY DUCTILE OVERLOAD OF THE PIPE WALL AT THE WELD TOE. THE PRIMARY FACTOR TO THE FAILURE WAS SETTLEMENT OF THE BRANCH CONNECTION DUE TO IMPROPER SUPPORT. THE SETTLEMENT CAUSED BENDING STRESSES IN THE CARRIER PIPE AT THE SADDLE REINFORCEMENT FILLET WELD WHICH RESULTED IN THE FORMATION OF A CRACK. THE GEOMETRY OF THE FILLET WELD THAT ATTACHED THE SADDLE REINFORCEMENT PAD TO THE CARRIER PIPE WAS ALSO A CONTRIBUTING FACTOR TO THE FAILURE. THE SADDLE THICKNESS WAS 2.5 TIMES THE THICKNESS OF THE CARRIER PIPE WHICH CONTRIBUTED TO A STRESS CONCENTRATION IN THE THINNER PIPE AT THE FILLET WELD TOE. UNDERCUT AT THE TOE OF THE FILLET WELD FURTHER CONCENTRATED THE STRESS AND CONTRIBUTED TO THE FORMATION OF A CRACK.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150058 | 16778 | 2015-04-29 08:56 | SUPPLEMENTAL FINAL | 31451 | KINDER MORGAN TEXAS PIPELINE CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2015-03-30 11:03 | 2015 |  |  | 26.593 | -99.0868 | 1112292 | 2015-04-01 12:36 |  | NATURAL GAS |  | 10600 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-03-30 11:03 | 2015-03-30 11:33 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-03-30 11:03 | 2015-03-30 11:03 | ONSHORE | TX | 78545 | Not Within a Municipality | STARR | SURVEY STATION NO. | 123+33 | BOB WEST COMPRESSOR STATION / STA #582 | NA | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2014 |  | CARBON STEEL |  | OTHER | [8 empty] | AN ELECTRICAL UPS CIRCUIT WAS SHORTED CAUSING THE COMPRESSOR STATION TO RELEASE A REPORTABLE AMOUNT OF NATURAL GAS TO ATMOSPHERE. | CLASS 1 LOCATION | NO |  | 687 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 42400 | 37921.1267605634 | 2000 | 2185.78090796612 | 0 | 0 | 0 | 0 |  |  | 44400 | 40317.8851032019 | 40106.9076685295 | [8 empty] | 800 |  | 1100 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EVENT CAUSED BY ELECTRICAL SHORT; NOT A CONTROLLER ACTION ISSUE NOR A CONTROL ROOM ISSUE; | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | AN ELECTRICAL UPS CIRCUIT WAS SHORTED CAUSING THE COMPRESSOR STATION TO RELEASE A REPORTABLE AMOUNT OF NATURAL GAS TO ATMOSPHERE. NATURAL GAS WAS RELEASED THROUGH COMPRESSOR BLOW DOWN VALVES. | [11 empty] | YES | [173 empty] | WILLIAM MARTIN MULLER | SPECIALIST PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205 325 3863 | 205 325 3508 |  |  |  | WILLIAM MARTIN MULLER | SPECIALIST PIPELINE TECHNICAL | 205 325 3863 | martin_muller@kindermorgan.com | MARCH 30, 2015, 11:03 AM, BOB WEST COMPRESSOR STATION (COMMISSIONED 12/2014); ALL COMPRESSOR ENGINES SHUT DOWN BECAUSE OF AN ELECTRICAL POWER FAILURE RESULTING FROM A CIRCUIT SHORT TO A GROUND WIRE TIED INTO THE UPS PANEL; SAID UPS PANEL PROVIDES POWER TO ALL UNIT CONTROL PANELS AND COMPRESSOR STATION CONTROL PANEL; COMPRESSOR BLOW DOWN VALVES FOR UNITS 1 THROUGH UNIT 8 FAILED OPEN; SUCTION AND DISCHARGE SIDE VALVES FOR UNITS 1 THROUGH UNIT 8 REMAINED IN LAST POSITION WHICH WAS OPEN; SUCTION SIDE VALVE GOV-1001 AND DISCHARGE SIDE VALVE GOV-1002 REMAINED IN LAST POSITION WHICH WAS OPEN; COMPRESSOR BLOW DOWN VALVES OPERATED IN FAIL ESD STATE WHICH IS OPEN; AN ON-SITE STATION OPERATING TECHNICIAN CLOSED THE STATION SIDE VALVES; AN ON-SITE CONTROLS TECHNICIAN CLOSED THE SUCTION AND DISCHARGE VALVES ON UNITS 1 THROUGH UNIT 8; RELEASE OF NATURAL GAS ENDED 11:18 AM; THE COMPRESSOR BLOW DOWN VALVES RESET AUTOMATICALLY WHEN ELECTRIC POWER WAS RESTORED AT 11:33 AM; APRIL 01, 2015, 11:50 AM, NATURAL GAS LOST WAS RECALCULATED AND DETERMINED TO BE AN AMOUNT MEETING REPORTING CRITERIA; THE EVENT WAS REPORTED TO THE NRC AND TO THE TEXAS RAILROAD COMMISSION;
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150059 | 16921 | 2015-04-29 14:04 | SUPPLEMENTAL FINAL | 15105 | PANHANDLE EASTERN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2015-03-31 03:52 | 2015 |  |  | 38.8466 | -93.3655 | 1112157 | 2015-03-31 07:46 |  | NATURAL GAS |  | 12100 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE COMPRESSOR UNIT AFFECTED WAS NOT REQUIRED TO MAINTAIN THROUGHPUT VOLUMES. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-03-31 03:52 | 2015-03-31 04:35 | ONSHORE | MO | 65337 | LAMONTE | PETTIS | MILEPOST | HOUSTONIA | PANHANDLE EASTERN PIPELINE COMPANY | HOUSTONIA COMPRESSOR STATION MER#1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2014 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE WAS RELIEVING BELOW SETPOINT. | CLASS 1 LOCATION | NO |  | 93 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 46116 | 41244.5915492958 | 0 | 0 | 216 | 236.064338060341 | 0 | 0 |  |  | 46332 | 42868.5006052303 | 41480.6558873561 | [8 empty] | 890 |  | 900 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EQUIPMENT FAILURE IN THE FIELD. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | RELIEF VALVE PILOT MALFUNCTION. | [161 empty] | NATHAN HLAVATY | DIRECTOR-INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 7138575479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR-INTERSTATE REGULATORY COMPLIANCE | 7138575479 | nathan.hlavaty@energytransfer.com | GAS CONTROL RECEIVED A CALL AT 3:52 (CST) FROM PETTIS COUNTY OF A NOISE AT THE HOUSTONIA STATION. ON-CALL WAS NOTIFIED AND WENT TO THE STATION. WHEN THEY ARRIVED, THEY FOUND THE UNIT RELIEF VALVE ON E0812 WAS BLOWING AND THE UNIT RELIEF ON E0811 WAS OPENING INTERMITTENTLY. PRESSURE WAS CHECKED AT THE SITE AND DETERMINED TO BE 870 PSIG, 30 PSIG BELOW MAOP. THE OPERATOR ADJUSTED THE RELIEF ON E0812 UNTIL IT STOPPED BLOWING. HE ATTEMPTED TO ADJUST THE RELIEF ON E0811, BUT HE HAD TO SHUTDOWN THE UNIT TO WORK ON THE DEVICE. BASED ON THE SCADA TRACKED PRESSURE, NEITHER MAOP NOR OPP WERE EXCEEDED. THIS SUPPLEMENTAL REPORT IS TO ACKNOWLEDGE THERE ARE NO FURTHER UPDATES AND IS BEING SUBMITTED AS A FINAL.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150060 | 16749 | 2015-04-30 13:39 | ORIGINAL FINAL | 15931 | PUBLIC SERVICE CO OF COLORADO | 1800 LARIMER STREET | DENVER | CO | 80202 | 2015-04-13 12:50 | 2015 |  |  | 38.0188 | -106.1973 | 113508 | 2015-04-13 18:30 |  | NATURAL GAS |  | 4430 | 220 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-04-13 14:20 | 2015-04-14 00:07 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-04-13 12:59 | 2015-04-13 13:20 | ONSHORE | CO | 81149 | Not Within a Municipality | SAGUACHE | SURVEY STATION NO. | 1494+13 | 8" NORTHERN SAN LUIS VALLEY | 71006 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 12 |  | YES |  |  |  |  | YES | UNCASED | [16 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8.625 |  | 0.188 | 42000 | API-5L | LONGITUDINAL ERW - LOW FREQUENCY |  | UNKNOWN | POLYOLEFIN | [28 empty] | 1962 | 1962 | CARBON STEEL |  | MECHANICAL PUNCTURE | 6 | 6 | [7 empty] | CLASS 1 LOCATION | NO |  | 167 |  | NO | NO | NO |  | 0 | 0 | 782 | 854.640335014752 | 15745 | 14081.7957746479 | 8000 | 8743.12363186447 | 1000 | 1092.89045398306 | 0 | 0 |  |  | 25527 | 19506.5295608874 | 24772.4501955102 | [8 empty] | 620 |  | 790 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 84353 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  | YES | NO CONTROL ROOM ISSUES | YES | YES | [7 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO | YES | COUNTY ROAD | [9 empty] | COUNTY | GRADER/SCRAPER | DRAINAGE | NO | [5 empty] | YES | 10 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | SARAH ROBINSON | PRINCIPAL ENGINEER | sarah.robinson@xcelenergy.com | 303-571-3926 |  |  |  |  | MIKE O'SHEA | MANAGER HP GAS TRANSMISSION | 303-571-3916 | michael.oshea@xcelenergy.com | ON APRIL 13 A THIRD PARTY EXCAVATOR DAMAGED A 8' TRANSMISSION LINE NEAR THE TOWN OF SAGUACHE, CO. THE EXCAVATOR WAS PERFORMING DRAINAGE WORK FOR THE COUNTY ROAD, AND NO LOCATE TICKET WAS REQUESTED. THE INCIDENT WAS IDENTIFIED BY SCADA CONTROLLERS, AND THE LINE WAS ISOLATED BY MANUALLY-OPERATED MAINLINE VALVES. THERE WERE NO INJURIES AND THE GAS DID NOT IGNITE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150061 | 16801 | 2015-05-01 15:36 | SUPPLEMENTAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2015-04-09 14:10 | 2015 |  |  | 29.9662 | -91.3076 | 1113119 | 2015-04-09 14:55 |  | NATURAL GAS |  | 41 | 100 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-04-09 14:10 | 2015-05-08 14:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-04-09 14:10 | 2015-04-09 14:10 | ONSHORE | LA | 99999 | Not Within a Municipality | ST MARTIN PARISH | MILEPOST | MP 0.4 | BAYOU POSTILLION PIPELINE | BAYOU POSTILLION PIPELINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | PIPELINE CANAL: 11FT H2O+2FT MUD COVER | 156 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10.75 |  | 0.279 | 42000 | API 5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | REPUBLIC STEEL | OTHER | CONCRETE | [27 empty] | 1975 | 1975 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 244 |  | NO | NO | NO |  | 0 | 0 | 390 | 426.227277053393 | 160 | 143.098591549296 | 71462 | 78100.1376225374 | 840 | 918.02798134577 | 0 | 0 |  |  | 72852 | 36615.4294257662 | 79587.4914724858 | [8 empty] | 845 |  | 1085 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 3918 | NO | [5 empty] | YES | NO PIG TRAPS | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS A SMALL LEAK IDENTIFIED BY LOCAL OPERATIONS PERSONNEL. BUBBLES WERE OBSERVED, THE LINE WAS SHUT-IN AND DEPRESSURIZATION OF THE LINE RESULTED IN THE SUBSIDENCE OF THE BUBBLES. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [146 empty] | KRISTIN VAN DER LAAN | COMPLIANCE ENGINEER III | kristin_vanderlaan@kindermorgan.com | 303-914-7753 |  |  |  |  | REJI GEORGE | DIRECTOR - COMPLIANCE-CODES AND STANDARDS | 713-806-6751 | reji_george@kindermorgan.com | AT 2:10 PM ON APRIL 9, 2015, A NATURAL GAS LEAK WAS IDENTIFIED BY COMPANY EMPLOYEES IN THE PIPELINE CANAL OF THE SNG 10-INCH BAYOU POSTILLION LINE, LOCATED IN ST. MARY PARISH, LOUISIANA. THE LEAK WAS CONFIRMED AT 10:40 AM ON 4/10/15, BY DEPRESSURIZING LINE AND THE SUBSIDENCE OF BUBBLES. MAY 8, 2015: AN ULTRASONIC TEST WAS PERFORMED BY THE DIVE CREW TO DETERMINE IF THERE WAS SIGNIFICANT WALL LOSS ON THE PIPE. THE UT READINGS DID NOT INDICATE SIGNIFICANT WALL LOSS. THE DIVERS WERE ABLE TO DETERMINE THE LEAK LOCATION AT THE 7 O'CLOCK POSITION. THE LEAK WAS A PINHOLE LEAK MEASURING NO MORE THAN 1/32-INCHES. REPAIRS WERE MADE AND COMPLETED BY INSTALLING A CLAMP OVER THE AREA OF THE LEAK. THE LINE HAS BEEN RETURNED TO SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150062 | 16879 | 2015-05-04 15:36 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2015-04-04 07:19 | 2015 |  |  | 39.5439 | -94.8667 | 1112603 | 2015-04-05 10:53 |  | NATURAL GAS |  | 147 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | PRESSURE WAS REDUCED AND THE LINE WAS BYPASSED AND REPLACED. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-04-04 07:19 | 2015-04-04 10:00 | ONSHORE | MO | 64440 | Not Within a Municipality | BUCHANAN | SURVEY STATION NO. | 170/736+08 | XS | ST. JOE 16" LOOP LINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 84 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION | [19 empty] | FILLET WELD | [18 empty] | UNKNOWN |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 246 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 340 | 304.084507042254 | 137944 | 150757.680784239 | 2500 | 2732.22613495765 | 0 | 0 |  |  | 140784 | 70771.1756043702 | 153793.991426239 | [8 empty] | 475 |  | 500 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 61101 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [103 empty] | OTHER OUTSIDE FORCE DAMAGE | [9 empty] | IT IS EXPECTED THAT THE CRACK IN THE WELD IS ATTRIBUTED TO EITHER GROUND MOVEMENT OR CATTLE PUSHING THE PIG PEN AGAINST THE PIPE SEGMENT AND CAUSING EXCESSIVE STRESS TO THE WELD. | [251 empty] | DAVID COOMES | PIPELINE COMPLIANCE ENGINEER | david.coomes@sscgp.com | 270.852.4391 |  |  |  |  | DAVID SINCLAIR | PIPELINE COMPLIANCE MANAGER | 270.852.4424 | david.l.sinclair@sscgp.com | ON APRIL 4TH AT 7:19 AM A LOCAL LAND OWNER CALLED SSC GAS CONTROL NOTIFYING OF A POSSIBLE LEAK. THE GAS CONTROLLER NOTIFIED LOCAL OPERATIONS IMMEDIATELY AFTER, AND OPERATIONS ARRIVED ON SITE AT APPROXIMATELY 10:00 AM. ONCE ONSITE AND INSPECTED IT WAS DETERMINED AN EXCAVATION WOULD BE NECESSARY BASED ON SIZE OF THE LEAK. AT THIS TIME AN EMERGENCY ONE-CALL TICKET WAS CALLED. AN OPERATOR REMAINED ONSITE TO SECURE THE SITE. AFTER THE RISER WAS DUG UP AND INVESTIGATED ON APRIL 5TH, AT APPROXIMATELY 9:29 AM, IT WAS DETERMINED THAT THE LEAK WAS UPSTREAM OF THE DOMESTIC LINE TAP VALVE. AT THIS POINT SSC IMPLEMENTED A 20% PRESSURE REDUCTION. BECAUSE THE LINE COULD NOT BE TAKEN OUT OF SERVICE SSC NOTIFIED NRC BECAUSE OF THE REPAIR COST EXCEEDING $50,000.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150063 | 16856 | 2015-05-05 10:35 | SUPPLEMENTAL FINAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2015-04-13 10:58 | 2015 |  |  | 35.8788 | -101.5631 | 1113463 | 2015-04-13 12:17 |  | NATURAL GAS |  | 108000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-04-13 12:54 | 2015-09-02 13:00 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 1 | 2015-04-13 10:58 | 2015-04-13 12:00 | ONSHORE | TX | 79083 | Not Within a Municipality | HUTCHINSON | SURVEY STATION NO. | 519+89 | AMARILLO #4 PIPELINE | AMARILLO #4 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 |  | 0.289 | 52000 | API 5L | DSAW |  | REPUBLIC | ASPHALT | [28 empty] | 1968 | 1967 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 131 | 48 |  | CLASS 1 LOCATION | NO |  | 552 |  | NO | NO | NO |  | 6000 | 6557.34272389835 | 0 | 0 | 275000 | 245950.704225352 | 162000 | 177048.253545256 | 1000 | 1092.89045398306 | 11000 | 12021.7949938136 | LABORATORY ANALYSIS |  | 455000 | 345288.063044043 | 442670.985942303 | [8 empty] | 708 |  | 712 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | AUTOMATIC | 60457 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | STEADY STATE CONDITION OF FACILITIES, PRESSURE LESS THAN MAOP. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED | YES | YES | [15 empty] | STRESS CORROSION CRACKING | [12 empty] | YES | NO ADDITIONAL FACTORS. | [55 empty] | YES | YES |  |  | YES |  |  |  | 2011 | [31 empty] | 2011 | [23 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KENNETH C. PETERS | SENIOR PIPELINE ENGINEER | ken_peters@kindermorgan.com | 2053257554 | 2053253508 |  |  |  | REJI GEORGE | DIRECTOR CODES AND STANDARDS | 7134205433 | reji_george@kindermorgan.com | ON APRIL 13, 2015, NATURAL GAS PIPELINE (NGPL) COMPANY OF AMERICA INCURRED A FAILURE OF ITS 30" AMARILLO #4 PIPELINE ABOUT 7 MILES WEST OF STINNETTE, TX. THE FAILURE RESULTED IN A RELEASE OF NATURAL GAS THAT IGNITED AND BURNED ABOUT A 200' RADIUS OF A CULTIVATED WHEAT FIELD. THERE WERE NO INJURIES NOR FATALITIES BUT ONE PERSON IN A HOME ABOUT 3/4 MILE AWAY SELF-EVACUATED. UPSTREAM AND DOWNSTREAM VALVES WERE CLOSED TO ISOLATE THE INCIDENT AND LET THE FIRE BURN OUT. METALLURGICAL ANALYSIS WAS COMPLETED WITH A FINAL REPORT SUBMITTED TO THE PHMSA SOUTHWEST REGION OFFICE ON JUNE 1, 2015. THE ANALYSIS REVEALED THE CAUSE OF THE INCIDENT TO BE STRESS CORROSION CRACKING. THE PIPELINE WAS SPIKE STRENGTH TESTED, NECESSARY REPAIRS MADE, AND PLACED BACK INTO NATURAL GAS SERVICE, ALL PURSUANT TO THE PHMSA CORRECTIVE ACTION ORDER CPF NO. 4-2015-1006H.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150064 | 16756 | 2015-05-12 11:56 | ORIGINAL FINAL | 26330 | ENABLE OKLAHOMA INTRASTATE TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2015-04-20 07:00 | 2015 |  |  | 36.2826 | -95.6616 | 1114121 | 2015-04-20 09:39 |  | NATURAL GAS |  | 23147 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE VALVE WAS BYPASSED AND THE COMPRESSOR UNIT WAS SHUTDOWN FOR REPAIRS. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-04-20 07:28 | 2015-04-20 07:00 | ONSHORE | OK | 74019 | CLAREMORE | ROGERS | MILEPOST | CLAREMORE CS | CLAREMORE COMPRESSOR STATION | CLAREMORE COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | 1/4" NPT FITTING | UNKNOWN |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 55010 | 49199.0845070423 | 10 | 10.9289045398306 | 400 | 437.156181593224 | 0 | 0 |  |  | 55420 | 51212.6077607104 | 49647.1695931753 | [8 empty] | 871 |  | 1014 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS NOT RELATED TO THE CONTROL ROOM AND THE PRESSURE DROP WAS SLOW AND GRADUAL, NOT ENOUGH TO BE SEEN AS AN INCIDENT BY THE CONTROL ROOM. THERE IS CURRENTLY NO ALARM ON THIS VENT PIPING TO ALARM THE CONTROL ROOM WHEN A PRV HAS OPENED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | THREADED FITTING |  |  |  |  | YES | [14 empty] | YES | THE VALVE WAS REMOVED FOR TESTING IN MARCH, THE FITTING MAY HAVE BEEN DAMAGED | [161 empty] | PATRICK KELLEY | SR. DOT COMPLIANCE COORDINATOR | kenneth.kelley@enablemidstream.com | 918-688-3330 |  |  |  |  | PAUL M BREWER | SVP OPERATIONS AND EHS | 405 525 7788 | paul.brewer@enablemidstream.com | 4/20/2015 AT 06:39: COMPRESSION TECHNICIAN WAS CONTACTED BY GAS CONTROL IN REGARDS TO AN ODOR OF GAS IN THE AREA CLOSE TO THE CLAREMORE COMPRESSOR STATION. - 07:00: HE ARRIVED ON LOCATION AND PARKED TRUCK OUTSIDE OF GATE AND WALKED INTO THE FACILITY AND NOTICED GAS VENTING OUT OF THE SILENCER. HE THEN WENT INTO THE CONTROL ROOM TO CHECK FOR ANY VALVES OUT OF POSITION THAT WOULD BE VENTING AND FOUND NONE. HE WALKED THROUGH THE YARD TO VERIFY THE GAS WAS NOT VENTING FROM THE ESD VENT VALVES AND VERIFIED IT WAS NOT. HE WENT INTO THE COMPRESSOR BUILDING AND FOUND THAT A 1/4 INCH NPT FITTING HAD BROKEN OFF THAT WAS CONNECTED TO THE TOP OF THE RELIEF VALVE ON THE INTERSTAGE DISCHARGE PIPING ON UNIT 427 CAUSING THE VALVE TO RELIEVE GAS. A SECOND COMPANY EMPLOYEE HAD ARRIVED ON THE SCENE AND ASSISTED THE COMPRESSION TECHNICIAN. - 07:28: THE BLOCK VALVE LOCATED ON THE VENT PIPING WAS CLOSED TO STOP THE GAS FROM VENTING AND THEY WERE ABLE TO MONITOR THE INTERSTAGE PRESSURE. AFTER CLOSING THE BLOCK VALVE ON THE RELIEF VALVE VENT PIPING, THE GAS BEING VENTED OUT OF THE SILENCER WAS ISOLATED. - 08:34: SHUT DOWN UNIT 427, DEPRESSURIZED, LOCKED AND TAGGED THE UNIT OUT AND REPLACED THE 1/4 INCH NPT FITTING. - APPROXIMATELY 09:08: PUT UNIT 427 BACK INTO SERVICE AND VERIFIED THE RELIEF VALVE WAS BACK TO ITS NORMAL OPERATING STATUS AND THE THERE WAS NO LONGER GAS VENTING OUT OF THE RELIEF VALVE VENT PIPING. - AFTER REVIEWING THE HISTORICAL DATA, IT WAS FOUND THAT THE INTERSTAGE DISCHARGE PRESSURE HAD DECREASED AT APPROXIMATELY 01:40 ON 4/20/15 INDICATING THE TIME THE 1/4 INCH NPT FITTING HAD FAILED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150065 | 16967 | 2015-05-13 17:50 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2015-04-14 17:25 | 2015 |  |  | 28.5065 | -91.1015 | 1113615 | 2015-04-14 19:15 |  | NATURAL GAS |  | 1 | 540 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-04-14 16:50 | 2015-05-11 12:40 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-04-14 17:25 | 2015-04-15 12:00 | OFFSHORE | [28 empty] | 112 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SHIP SHOAL | 219 | PORTION OF RISER OUTSIDE OF SPLASH ZONE, INCLUDING RISER BEND | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12 |  | 0.375 | 46000 | API 5L | SEAMLESS |  | ACIPCO | FIELD APPLIED EPOXY | [28 empty] | 1970 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 359 |  | NO | NO | NO |  | 0 | 0 | 1400 | 1530.04663557628 | 5 | 4.47183098591549 | 310000 | 338796.040734748 | 0 | 0 | 0 | 0 |  |  | 311405 | 156223.290380748 | 340330.559201311 | [8 empty] | 1176 |  | 1300 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | AUTOMATIC | 8666 | NO | [5 empty] | YES | NO PIG LAUNCH OR RECEIVING TRAPS ON THE LINE. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | NOTIFICATION FROM PRODUCER THAT OWNS THE PLATFORM |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SMALL SIZE OF THE LEAK AND SMALL AMOUNT OF GAS THAT WAS UNINTENTIONALLY RELEASED | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  |  | YES | [7 empty] | YES | YES |  |  | NO | [11 empty] | YES | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | ROGER R. STREET | FIELD COMPLIANCE SPECIALIST | roger_street@transcanada.com | 8325702966 |  |  |  |  | ROGER STREET | FIELD COMPLIANCE SPECIALIST | 6154655123 | roger_street@transcanada.com | ON 14 APRIL 2015 AT 17:15 CDT, A LEAK ON A TC OFFSHORE (TCO) PIPELINE RISER WAS DISCOVERED BY THE OWNER / THIRD PARTY PRODUCER, OF THE PLATFORM (THIRD PARTY) LOCATED IN OUTER CONTINENTAL SHELF SHIP SHOAL BLOCK 219 (SS219). THE LEAK DISCOVERY WAS IDENTIFIED BY AN AUDIBLE RELEASE OF GAS EMANATING FROM BENEATH A RISER CLAMP AND REPORTED TO TRANSCANADA/ANR PIPELINE COMPANY (ANR), OPERATOR FOR TCO. THE LEAK WAS LOCATED ABOVE THE WATER LINE ON THE PIPELINE RISER AT MILEPOST 0 ON THE 763 TRANSMISSION LINE TO A PLATFORM OWNED BY THE THIRD PARTY, RENAISSANCE ENERGY. THIS PLATFORM IS LOCATED AT COORDINATES; 28.506467, -91.101507. FOLLOWING THE DISCOVERY LEAK, THE PIPELINE SECTION WAS ISOLATED AT 16:50 CDT FROM THE THIRD PARTY PRODUCER AT SS219 ISOLATING THE SEGMENT FROM SS219 TO SHIP SHOAL BLOCK 204. THE LEAK WAS REPORT TO TRANSCANADA BY THE PRODUCER AT 17:25 CDT ON 14 APRIL. THE INCIDENT WAS REPORTED TO THE NATIONAL RESPONSE CENTER ON 14 APRIL 2015 AT 19:15 CDT. FOLLOWING THE REPORT OF THE INCIDENT TO THE NATIONAL RESPONSE CENTER, ANR MAINTAINED CONTACT AND UPDATED U.S. COAST GUARD, BSEE, AND PHMSA. THE PIPELINE WAS BLOWN DOWN AND FLARING PROCEDURES WERE INITIATED ON 16 APRIL 2015. NO SHEEN OR PRODUCT WAS OBSERVED DUE TO THE LEAK. ON 1 MAY 2015, PERSONNEL WERE DISPATCHED TO THE INCIDENT LOCATION TO REMOVE THE PIPELINE RISER CLAMP AND EVALUATE REPAIR OPTIONS FOR THE LEAK LOCATION. FOLLOWING THE REMOVAL OF THE CLAMP, THE LEAK AREA WAS SANDBLASTED, INSPECTED, AND EVALUATION THROUGH NON-DESTRUCTIVE EXAMINATION (NDE). ANALYSIS DETERMINED THAT THE LEAK WAS CAUSED BY CORROSION PITTING DUE TO EXTERNAL CORROSION UNDER THE RISER CLAMP. TO REPAIR THE LEAK, FULL ENCIRCLEMENT SLEEVE AND WELD WERE INSTALLED ON THE PIPELINE ACCORDING TO TRANSCANADA'S PROCEDURE. FOLLOWING THE INSTALLATION ADDITIONAL NDE WAS PERFORMED TO ENSURE THE ACCEPTABLE REPAIR WAS CONDUCTED. ON 11 MAY 2015 AT 12:40 CDT, THE PIPELINE WAS PURGED, RELOADED, AND PUT BACK INTO SERVICE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150066 | 16758 | 2015-05-13 21:00 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2015-04-13 11:13 | 2015 |  |  | 38.3368 | -121.79 | 1113520 | 2015-04-13 23:45 |  | NATURAL GAS |  | 1 | 749 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-04-13 16:22 | 2015-04-14 05:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-04-13 11:13 | 2015-04-13 11:50 | ONSHORE | CA | 95620 | DIXON | SOLANO COUNTY | MILEPOST | MP 6.71 | L-220 | MP 6.71 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 4 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10.75 |  | 0.259 |  | UNKNOWN | SEAMLESS |  | UNKNOWN | ASPHALT | [28 empty] | 1937 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 0.1 | 0.1 | [7 empty] | CLASS 1 LOCATION | NO |  | 209 |  | NO | NO | NO |  | 0 | 0 | 2148 | 2347.52869515561 | 2 | 1.7887323943662 | 85000 | 92895.68858856 | 0 | 0 | 0 | 0 |  |  | 87150 | 43721.0043601605 | 95245.00601611 | [8 empty] | 670 |  | 796 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 24816 | NO | YES |  | YES |  |  | YES | WRINKLE BENDS, BELL AND SPIGOT JOINTS, PLUG VALVES | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY DIG-IN INCIDENT | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  | YES | PRIVATE LANDOWNER | [7 empty] | FARMER | GRADER/SCRAPER | AGRICULTURE | NO | [5 empty] | NO |  | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | WINI CHEN | PROGRAM MANAGER | wcce@pge.com | [5 empty] | LAURENCE DENISTON | MANAGER OF GAS OPERATIONS REGULATORY COMPLIANCE | 925-328-5756 | lcd1@pge.com | AT 1113 HOURS ON APRIL 13, 2015, PG&E WAS NOTIFIED OF A LEAK NEAR MAINE PRAIRIE ROAD AND ROBBEN ROAD IN DIXON. A PG&E GAS SERVICE REPRESENTATIVE (GSR) ARRIVED ON SCENE AT 1150 HOURS. A THIRD-PARTY DIG-IN OCCURRED ON PG&E'S TRANSMISSION LINE L-220 AT MILEPOINT (MP) 6.71 THAT RESULTED IN AN UNINTENTIONAL RELEASE OF GAS. THE THIRD-PARTY, GLI-CO FARMS, OPERATED A GRADER AND STRUCK PG&E'S TRANSMISSION LINE. THE THIRD PARTY DID NOT CALL USA. AT 1622 HOURS, GAS WAS SHUT IN BY ISOLATING A PORTION OF THE LINE. NO CUSTOMERS LOST GAS SERVICE AS A RESULT OF THIS INCIDENT. FIRE DEPARTMENT WAS ON SCENE. THERE WERE NO INJURIES OR FATALITIES AND NO IGNITION AS A RESULT OF THIS INCIDENT. AT 2245 HOURS ON APRIL 13, 2015, THE PIPELINE ENGINEER REPORTED THAT THIS INCIDENT WILL LIKELY EXCEED $50,000 IN DAMAGES AND THEREFORE IT WAS REPORTED TO THE CPUC AND DOT. LESS THAN 3 MMCF OF GAS WAS UNINTENTIONALLY RELEASED DURING THE INCIDENT. (PLEASE NOTE THE RESPONSE TO PART C, QUESTION 6 SHOULD BE "1MM BY 1MM" INSTEAD.)
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150067 | 17202 | 2015-05-15 11:17 | SUPPLEMENTAL FINAL | 18536 | SOUTHWEST GAS CORP | 5241 SPRING MOUNTAIN ROAD | LAS VEGAS | NV | 89103 | 2014-11-13 11:09 | 2014 |  |  | 35.0969 | -114.6836 | 1101004 | 2014-11-13 17:31 |  | NATURAL GAS |  | 21963 | 138 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-11-13 12:08 | 2014-11-14 02:08 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-11-13 11:09 | 2014-11-13 11:09 | ONSHORE | NV | 89029 | LAUGHLIN | CLARK COUNTY | MILEPOST | 2.86 | 500 SOUTHERN NV TRANSMISSION | 16-INCH L LINE 500 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.25 | 42000 | API 5LX | LONGITUDINAL ERW - LOW FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1956 | 1956 | CARBON STEEL |  | MECHANICAL PUNCTURE | 18 | 1 | [7 empty] | CLASS 1 LOCATION | NO |  | 251 |  | NO | NO | NO |  | 0 | 0 | 662 | 732.274925344379 | 105202 | 70196.0805604203 | 755 | 835.147384645025 | 19499 | 21568.9256333687 | 0 | 0 |  |  | 126118 | 83395.6582990176 | 93332.4285037784 | [8 empty] | 492 |  | 515 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 12000 | NO | YES | YES |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CAUSE OF INCIDENT WAS DAMAGE BY FRONT-END LOADER. | [12 empty] | NO |  |  | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | [10 empty] | NO | YES | OTHER | [8 empty] | YES | UTILITY | UNKNOWN/OTHER | UNKNOWN/OTHER | NO |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO |  | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | EXCAVATION PRACTICES NOT SUFFICIENT (OTHER) | [263 empty] | RENEE CRONISTER | COMPLIANCE SPECIALIST | renee.cronister@swgas.com | (702) 365-2080 | (702) 369-0542 |  |  |  | THOMAS CARDIN | DIRECTOR OF GAS OPERATIONS | (702) 365-2028 | thomas.cardin@swgas.com | AN EMPLOYEE OF A PIPELINE CONTRACTOR (NPL CONSTRUCTION CO.) PERFORMING WORK ON BEHALF OF SOUTHWEST GAS UTILIZING A SOUTHWEST GAS PROVIDED FRONT-END LOADER, WAS PERFORMING MAINTENANCE TO REPAIR BERMS AND WATER BARS ALONG THE SOUTHWEST GAS TRANSMISSION LINE RIGHT-OF-WAY LOCATED IN LAUGHLIN, NEVADA AT MILE POST 2.86. THE SOUTHWEST GAS EMPLOYEE ONSITE AT THE TIME OF THE INCIDENT EXPLAINED THE SCOPE OF WORK TO THE EQUIPMENT OPERATOR (INCLUDING SPECIFYING THE CONSTRUCTION MEANS, METHODS, SEQUENCES, TECHNIQUES, AND PROCEDURES, AND COORDINATING ALL PORTIONS OF THE WORK). THE ROLE OF THE SOUTHWEST GAS EMPLOYEE WAS ALSO TO INSPECT THE WORK PERFORMED BY THE EQUIPMENT OPERATOR. THE BERM PROTECTING THE PIPELINE IS LOCATED BESIDE THE ROADWAY AND DIRECTLY ABOVE THE PIPELINE. PORTIONS OF THE BERM, WATER BARS AND ROADWAY HAD BEEN WASHED OUT BY PREVIOUS RAIN. THE INCIDENT HAPPENED WHILE THE EQUIPMENT OPERATOR WAS OPERATING THE FRONT-END LOADER AND RESULTED IN THE BUCKET DAMAGING THE PIPELINE. PART B, 11: THE FACILITY WAS UNDER SOIL, BUT THE DEPTH OF COVER IS UNKNOWN AS THE SOIL WAS DISPLACED BY THE ESCAPING GAS. PART C, 3.G: SOUTHWEST GAS DOES NOT TRACK THE PIPE MANUFACTURE DATE; THEREFORE, THE PIPE INSTALLATION DATE HAS BEEN LISTED. PART G3, EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY): SOUTHWEST GAS HAS CLASSIFIED THE SUB-CAUSE AS FIRST PARTY EXCAVATION DAMAGE BECAUSE THE EMPLOYEE OF A PIPELINE CONTRACTOR THAT DAMAGED THE PIPELINE DID SO WHILE OPERATING A SOUTHWEST GAS PROVIDED FRONT-END LOADER AND WHILE WORKING UNDER THE DIRECTION OF A SOUTHWEST GAS EMPLOYEE WHO HAD SPECIFIED THE CONSTRUCTION MEANS, METHODS, SEQUENCES, TECHNIQUES, AND PROCEDURES. PART G3, 8: THE LAND USE RIGHTS IN THE SUBJECT AREA WERE OBTAINED FROM THE US BUREAU OF LAND MANAGEMENT BY RIGHT-OF-WAY GRANT. THE BLM TRANSFERRED ITS PROPERTY RIGHTS, SUBJECT TO SOUTHWEST GAS' RIGHT-OF-WAY GRANT, AND THE LAND IS NOW OWNED BY CLARK COUNTY, NEVADA. PART G3, 10: SOUTHWEST GAS CLASSIFIES THE TYPE OF EXCAVATION EQUIPMENT AS UNKNOWN/OTHER BECAUSE A FRONT-END LOADER WAS USED. PART G3 11: PLEASE SEE THE ABOVE NARRATIVE. PART G3 13-15: NEVADA LAW DOES NOT REQUIRE A ONE CALL TICKET UNDER THESE CIRCUMSTANCES. PART G3 17: SOUTHWEST GAS DESCRIBES THIS INCIDENT AS "EXCAVATION PRACTICES NOT SUFFICIENT (OTHER)" BECAUSE NONE OF THE OTHER SECOND LEVEL CAUSES USED IN THE DIRT REPORTING MATRIX APPLIES. SUPPLEMENTAL: PART C, 3.E: SUBSEQUENT LABORATORY INVESTIGATION DETERMINED THAT THE PIPE SEAM TYPE IS LONGITUDINAL ERW - LOW FREQUENCY.
2021-02-26 10:37 | YES | YES | GT (Gas Transmission) | 20150068 | 17537 | 2015-05-15 20:59 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2015-04-17 14:29 | 2015 |  |  | 36.8421 | -119.9294 | 1113940 | 2015-04-17 15:27 |  | NATURAL GAS |  | 7200 | 200 | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES | 0 | 0 | 0 | 13 | 0 | 13 |  | YES |  | 2015-04-17 15:20 | 2015-09-03 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 0 | 2015-04-17 14:33 | 2015-04-17 14:42 | ONSHORE | CA | 93722 | FRESNO | FRESNO COUNTY | MILEPOST | MP 0.26 | L-118B | 101.5 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 45 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 |  | 0.25 | 42000 | API 5LX-X42 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COLD APPLIED TAPE | [28 empty] | 1962 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 12 | 19 |  | CLASS 3 LOCATION | YES | METHOD2 | 176 |  | NO | NO | NO |  | 0 | 0 | 850 | 928.9568858856 | 30700 | 27457.0422535211 | 1230600 | 1344910.99267155 | 743100 | 812126.896354811 | 3973000 | 4342053.77367469 | INVESTIGATION AND COST INCURRED DUE TO DELAYS CAUSED BY THE INCIDENT |  | 5978250 | 3012146.94178842 | 6527477.66184046 | [8 empty] | 369 |  | 400 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 3200 | NO | YES |  |  | YES |  | YES | UNKNOWN FIELD BENDS, PLUG VALVES | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY DIG-IN | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES | YES | OTHER | [9 empty] | COUNTY | UNKNOWN/OTHER | ROAD WORK | NO | [5 empty] | NO |  | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | STEPHEN RAMOS | GAS ENGINEER | s3rc@pge.com | 925-413-7311 |  |  |  |  | SUSIE RICHMOND | MANAGER OF GAS OPERATIONS REGULATORY COMPLIANCE | 925-328-5776 | gsr8@pge.com | ON APRIL 17, 2015 AT 1433 HOURS, PG&E WAS NOTIFIED ABOUT A GAS INCIDENT LOCATED AT 7633 NORTH WEBER AVENUE IN FRESNO. A THIRD PARTY, FRESNO COUNTY DEPARTMENT OF PUBLIC WORKS, STRUCK PG&E'S TRANSMISSION LINE, L-118B, CAUSING AN UNINTENTIONAL RELEASE OF NATURAL GAS WHICH IGNITED DURING THE INCIDENT. PG&E'S GAS SERVICE REPRESENTATIVE ARRIVED ON SCENE AT 1442 HOURS. THE FLOW OF GAS WAS SHUT IN AT 1520 HOURS BY CLOSING VALVES UPSTREAM AND DOWNSTREAM OF THE INCIDENT SITE. THE FLAMES EXTINGUISHED AT 1556 HOURS FOLLOWING THE RELEASE OF THE REMAINING GAS IN THE LINE. THE THIRD PARTY DID NOT NOTIFY USA. WITH THE CPUC'S APPROVAL, THE IMPACTED SECTION OF THE PIPELINE WAS REMOVED AND TRANSPORTED TO AN INDEPENDENT THIRD-PARTY ENGINEERING FIRM FOR ANALYSIS. THE THIRD PARTY'S REPORT "INDICATES THAT PG&E LINE 118B RUPTURED WHEN IT WAS STRUCK BY A FRONT LOADER THAT WAS OPERATING IN THE AREA AT THE TIME OF THE INCIDENT." THE REPORT GOES ON TO SAY "THE SIGNIFICANT GOUGING, SCRAPING AND DEFORMATION PRESENT AT THE LINE 118B RUPTURE LOCATION COULD HAVE ONLY BEEN CAUSED BY CONTACT WITH THE FRONT-LOADER BUCKET." NO CUSTOMERS LOST GAS SERVICE DURING THE INCIDENT. HIGHWAY 99 WAS SHUT DOWN IN BOTH DIRECTIONS DURING THE INCIDENT. MAJOR MEDIA WAS REPORTED ON SCENE. MORE THAN 3MMCF OF GAS WAS UNINTENTIONALLY RELEASED DURING THE INCIDENT. THIRTEEN INDIVIDUALS WERE INJURED AND THERE WAS ONE FATALITY.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150069 | 16962 | 2015-05-19 20:58 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2015-04-23 10:43 | 2015 |  |  | 39.9035 | -80.2244 | 1114481 | 2015-04-23 12:28 |  | NATURAL GAS |  | 4830 | 463 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-04-23 10:50 | 2015-05-14 17:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-04-23 10:45 | 2015-04-23 10:45 | ONSHORE | PA | 15370 | WAYNESBURG | GREENE COUNTY | SURVEY STATION NO. | 4488 | LINE 1547 | VS-9353 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 38 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 14 |  | 0.312 | 45000 | UNKNOWN | SEAMLESS |  | US STEEL CORP.-NATIONAL TUBE CORP. | NONE | [28 empty] | 1948 | 1947 | CARBON STEEL |  | OTHER | [8 empty] | FAILURE OCCURRED AT THE GIRTH WELD OF THE PIPE. NO FRAGMENTATION WAS NOTED CIRCUMFERENTIALLY ON BOTH SEPARATED ENDS OF THE PIPE. PIPE WAS DISPLACED VERTICALLY AND SHIFTED LATERALLY AT THE NORTH-ENDED JOINT. | CLASS 2 LOCATION | NO |  | 296 |  | NO | NO | NO |  | 0 | 0 | 1148 | 1254.63824117255 | 11978 | 10712.7183098592 | 0 | 0 | 0 | 0 | 0 | 0 | THE TOTAL COSTS CANNOT BE DETERMINED AT THIS TIME DUE TO ONGOING INVESTIGATIONS. |  | 13126 | 11682.273560975 | 11967.3565510317 | [8 empty] | 795 |  | 936 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 7920 | NO |  | YES | [5 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PIPELINE POTENTIALLY HAD FAILED DUE TO REASONS NOT RELATED TO HUMAN INTERVENTION OR MANIPULATION OF VALVES POSITION. | [12 empty] | YES | 2 | 0 | YES | 3 | 0 | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [7 empty] | YES | [14 empty] | YES | [63 empty] | NO | [63 empty] | YES | 1967 | 1447 | NO | [13 empty] | NO | [63 empty] | GEORGE HAMATY | ENGINEER | ghamaty@cpg.com | (304)357-3728 |  |  |  |  | PERRY MICHAEL HOFFMAN | MANAGER SYSTEM INTEGRITY | (304)357-2548 | mikehoffman@cpg.com | LINE 1547 IS A 14-IN STEEL, BARE CATHODICALLY PROTECTED TRANSMISSION PIPE THAT IS OWNED, OPERATED AND MAINTAINED BY COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA). ON APRIL 23, 2015, AT 10:43 AM, A COLUMBIA COMPRESSOR STATION (CS) OPERATOR HEARD A NOISE TO THE NORTHWEST OF HIS LOCATION. UPON VISUALLY CHECKING THE SOURCE OF THE NOISE, THE CS OPERATOR OBSERVED A CLOUD OF DUST BLOWING INTO ATMOSPHERE. HE THEN IMMEDIATELY OBSERVED A DROP IN PRESSURE IN LINE 1547 WHICH IS ON THE DISCHARGE SIDE OF THE CS. THE CS OPERATOR CLOSED THE VALVES TO ISOLATE AND STOP THE FLOW OF MATERIAL THROUGH LINE 1547, THEN CONTACTED THE PROPER COLUMBIA PERSONNEL REQUESTING LOGISTICAL AND LOCATION ASSESSMENT AND CONFIRMATION SUPPORT. COLUMBIA PERSONNEL CONFIRMED THE INCIDENT INVOLVED LINE 1547 WHICH WAS NOTED BY FIRST RESPONDERS TO HAVE SEPARATED AT THE GIRTH WELD. AT THE TIME OF THE FAILURE, LINE 1547 WAS IMMEDIATELY ADJACENT TO A 16-IN DIAMETER LINE THAT WAS UNDER CONSTRUCTION AND INTENDED TO REPLACE THE EXISTING 14-IN LINE AS PART OF COLUMBIA S PLANNED CONSTRUCTION PROGRAM. SINCE CONSTRUCTION OF LINE 1547 WAS ALREADY WELL UNDERWAY, COLUMBIA DECIDED TO ABANDON THE FAILED 14-IN PIPE AND FINISH THE CONSTRUCTION OF THE REPLACEMENT LINE RATHER THAN BRING OLD LINE 1547 BACK INTO SERVICE. SEGMENTS OF THE FAILED PIPE WERE SENT TO A CONTRACTED METALLURGICAL FAILURE ANALYSIS CONSULTANT FOR A ROOT CAUSE ANALYSIS FAILURE DETERMINATION. FURTHERMORE, A GEOTECHNICAL ASSESSMENT OF THE IMMEDIATE AREA AFFECTING BOTH LINES (THE 14-IN PIPE AND THE NEW 16-IN PIPE) WAS PERFORMED AND STRAIN GAUGES WERE INSTALLED ONTO THE NEW 16-IN PIPELINE FOR MONITORING ANY POTENTIAL FUTURE STRESSES. FINALLY, AN INTEGRITY ASSESSMENT WAS PERFORMED TO THE NEW 16-IN PIPE 1547 LINE. CONSTRUCTION WAS COMPLETED ON THE NEW 16-IN REPLACEMENT PIPELINE AND LINE 1547 WAS PLACED INTO SERVICE ON MAY 14, 2015.THE NEWLY CONSTRUCTED 16-IN LINE PIPE WAS CONSTRUCTED AND WAS PUT IN SERVICE AS OF MAY 14, 2015. THE METALLURGICAL FAILURE ANALYSIS REPORT OF THE 14-IN PIPE IDENTIFIED THE FOLLOWING: THE PIPELINE FAILURE WAS INITIATED AT THE GIRTH WELD, WHERE INCOMPLETE PENETRATION (IP) WELD DEFECTS WERE PRESENT. THERE WAS NO EVIDENCE OF IN-SERVICE GROWTH OF THE IP DEFECTS. HIGH AXIAL TENSILE STRESSES ACTING ON THE GIRTH WELD WERE LIKELY TO BE CONSIDERED AS CONTRIBUTING FACTORS IN THE PIPELINE FAILURE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150070 | 16936 | 2015-05-22 15:12 | SUPPLEMENTAL FINAL | 38987 | KINETICA ENERGY EXPRESS LLC | 1001 MCKINNEY STREET, SUITE 900 | HOUSTON | TX | 77002 | 2015-04-23 16:30 | 2015 |  |  | 28.4867 | -92.08 | 1114530 | 2015-04-23 18:06 |  | NATURAL GAS |  | 500 | 1516 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-04-23 16:30 | 2015-05-04 10:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-04-23 16:30 | 2015-04-23 16:30 | OFFSHORE | [28 empty] | 90 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SOUTH MARSH ISLAND | 27A | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12.75 |  | 0.375 | 42000 | 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | US STEEL | COAL TAR | [28 empty] | 1970 | 1970 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO | NO |  | 0 | 0 | 14179 | 15496.0937470258 | 1375 | 1229.75352112676 | 170000 | 185791.37717712 | 5000 | 5464.45226991529 | 0 | 0 |  |  | 190554 | 96179.5295890377 | 207981.676715188 | [8 empty] | 1010 |  | 1250 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 5712 | NO | YES | YES |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | BSEE HELICOPTER FLIGHT |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE WAS BELOW MAOP WITH NO UNUSUAL OPERATING CIRCUMSTANCE AND WAS LOCATED SUBSEA. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES | [7 empty] | YES | 6:00 POSITION | YES | NO | YES | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KURT CHERAMIE | SR. DIRECTOR | kurt.cheramie@kineticallc.com | 985-209-2283 |  |  |  |  | KURT CHERAMIE | SR. DIRECTOR | 985-209-2283 | kurt.cheramie@kineticallc.com | OVER FLIGHT OF THE AREA RESULTED IN A LEAK BEING IDENTIFIED ON THE KINETICA 523M-1300 PIPELINE. THE LINE WAS IMMEDIATELY ISOLATED AT THE PLATFORM AND A DIVE VESSEL WAS DISPATCHED TO CLOSE OFF THE SUBSEA VALVE FROM THE BLUEWATER HEADER. THE LOCATION WAS EXCAVATED AFTER PRESSURE REDUCTION AND A PINHOLE LEAK WAS IDENTIFIED AT THE 6:00 POSITION. A REPAIR CLAMP WAS INSTALLED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150071 | 17221 | 2015-05-22 18:39 | SUPPLEMENTAL FINAL | 9171 | MARKWEST JAVELINA PIPELINE COMPANY, LLC | 1515 ARAPAHOE STREET TOWER 1, SUITE 1600 | DENVER | CO | 80202 | 2015-04-28 13:41 | 2015 |  |  | 27.8091 | -97.4956 | 1114936 | 2015-04-28 14:40 |  | HYDROGEN GAS |  | 833 | 16 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-04-28 13:55 | 2015-05-29 16:42 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 0 | 2015-04-28 13:41 | 2015-04-28 13:41 | ONSHORE | TX | 78410 | CORPUS CHRISTI | NUECES | MILEPOST | CITGO WEST | CITGO WEST VALVE-METERING STATION | HY-850 10" HYDROGEN PIPELINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | FILTER/STRAINER/SEPARATOR | [38 empty] | 2015 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | BLIND FLANGE CONNECTION | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | YES | METHOD1 | 214 |  | NO | NO | NO |  | 0 | 0 | 19 | 20.7649186256781 | 1008 | 901.521126760563 | 1450000 | 1584691.15827544 | 0 | 0 | 0 | 0 |  |  | 1451027 | 728359.236161808 | 1585613.44432082 | [8 empty] | 1280 |  | 1480 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | REMOTELY CONTROLLED | 14032 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WAS NO INDICATION THAT THE ACTIONS OF THE CONTROLLER(S) OR CONTROL ROOM WERE THE CAUSE OF, OR A CONTRIBUTING FACTOR TO, THE INCIDENT. | [12 empty] | NO |  |  | YES | 4 | 0 | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | OTHER | TEMPORARY SEPARATOR FILTER BLIND FLANGE CONNECTION | [16 empty] | YES | TEMPORARY SEPARATOR FILTER BLIND FLANGE CONNECTION | [161 empty] | MATT CARNES | SR. PIPELINE INTEGRITY ENGINEER | mcarnes@markwest.com | 303-925-9219 | 303-573-4954 |  |  |  | MATT CARNES | SR. PIPELINE INTEGRITY ENGINEER | 303-925-9219 | mcarnes@markwest.com | AN IN-LINE INSPECTION OF THE HYDROGEN PIPELINE WAS BEING CONDUCTED AND PRIOR TO THE LAST RUN OF THE IN-LINE INSPECTION TOOL (MFL), HYDROGEN GAS WAS RELEASED AND IGNITED FROM A BLIND FLANGE CONNECTION FAILURE ON A TEMPORARY SEPARATOR FILTER INSTALLED AT THE RECEIVER SITE. THE FIRE WAS IMMEDIATELY IDENTIFIED BY ON-SITE PERSONNEL. THERE WERE NO INJURIES SUSTAINED AS A RESULT OF THE INCIDENT. THE PIPELINE SECTION WAS ISOLATED AND DE-PRESSURED TO THE FACILITY FLARE. LOCAL EMERGENCY RESPONDERS WERE DISPATCHED AND CONTAINED/EXTINGUISHED THE FIRE. THE FIRE AFFECTED THE STATION PIPING AND EQUIPMENT IN THE SURROUNDING AREA. REPAIRS AND/OR REPLACEMENT OF AFFECTED PIPING AND EQUIPMENT WERE COMPLETED AND RE-COMMISSIONED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150072 | 16772 | 2015-05-29 09:04 | ORIGINAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2015-05-02 15:00 | 2015 |  |  | 38.1726 | -95.299 | 1115331 | 2015-05-02 18:35 |  | NATURAL GAS |  | 15650 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-05-02 16:43 | 2015-05-06 14:18 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-05-02 15:15 | 2015-05-02 16:13 | ONSHORE | KS | 66091 | WELDA | ANDERSON | SURVEY STATION NO. | 100/0+00 | WELDA STATION/WELDA - OTTAWA 30" | DT | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1954 |  | CARBON STEEL |  | OTHER | [8 empty] | STATION ESD, CAUSED BY LOSS OF POWER AND POWER SURGE KNOCKING OUT BATTERY CHARGER. EXCESSIVE GAS LOSS WAS CAUSED BY A MAINLINE VALVE THAT DIDN'T CLOSE. | CLASS 1 LOCATION | NO |  | 401 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 37685 | 33704.1901408451 | 77500 | 84699.0101836871 | 1500 | 1639.33568097459 | 0 | 0 |  |  | 116685 | 74574.2432666173 | 120042.536005507 | [8 empty] | 435 |  | 500 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | NO | NO | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES |  | YES | [6 empty] | YES | 1 | 0 | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [13 empty] | YES | [173 empty] | DAVID COOMES | PIPELINE COMPLIANCE ENGINEER | david.coomes@sscgp.com | 2708524391 |  |  |  |  | DAVID SINCLAIR | PIPELINE COMPLIANCE MANAGER | 2708524424 | david.l.sinclair@sscgp.com | SSC GAS CONTROL LOST COMMUNICATIONS WITH WELDA COMPRESSOR STATION AT 10:10 AM ON 5/2/2015. AT 10:25 AM SSC SUPPORT WAS NOTIFIED OF THE ISSUE AND BEGAN TROUBLESHOOTING. AFTER SUPPORT COULD NOT FIX THE ISSUE A FIELD COMMUNICATION TECHNICIAN WAS NOTIFIED AND THEY HEADED TOWARD THE STATION AT 12:30 PM. AFTER REACHING ELK STATION AT 14:00 PM AND DISCOVERING NO ISSUES WITH COMMUNICATION THE ERROR WITH THE LOCATION WAS DISCOVERED AND THE COMMUNICATION TECHNICIAN LEFT FOR WELDA STATION. SSC GAS CONTROL RECEIVED A CALL A 15:15 PM, FROM A FORMER EMPLOYEE, THAT THE WELDA STATION HAD ESD AND GAS HAD BEEN CONTINUOUSLY BLOWING SINCE 15:00 PM. SSC GAS CONTROL RECEIVED A SECOND CALL AT 15:20 FROM LOCAL EMERGENCY RESPONDERS NOTIFYING THEM OF THE BLOWING GAS. SSC OPERATIONS WERE DISPATCHED AT 15:23 PM. THE SSC COMMUNICATIONS TECHNICIAN ARRIVED, AT WELDA STATION, AT 15:51 PM AND WAS NOTIFIED TO REMAIN OUTSIDE THE FACILITY SINCE THEY WERE NOT QUALIFIED TO SHUT-IN THE BLOWING GAS. SSC OPERATIONS ARRIVED ONSITE AT 16:13 PM AND HAD THE STATION SHUT IN AT 16:43 PM. IT WAS DETERMINED THAT THE STATION HAD LOST COMMUNICATIONS DUE TO A POWER SURGE WHICH TRIP BREAKERS AT THE STATION INCLUDING THE BATTERY CHARGER. ONCE BATTERY BACK-UP DEPLETED ITS POWER THE STATION ESD. DURING THE ESD TWO GATES REMAINED OPEN BECAUSE OF DEBRIS IN THE ESD SIGNAL LINE THAT MADE ITS WAY TO THE POPPET BOCK, CAUSING EXCESSIVE BLOWING GAS FROM THE MAINLINE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150073 | 17149 | 2015-06-03 11:42 | SUPPLEMENTAL FINAL | 18536 | SOUTHWEST GAS CORP | 5241 SPRING MOUNTAIN ROAD | LAS VEGAS | NV | 89150 | 2015-05-07 02:35 | 2015 |  |  | 35.0939 | -114.646 | 1115757 | 2015-05-07 06:37 |  | NATURAL GAS |  | 0 | 674 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | LEAK SECURED WITHOUT SHUT DOWN. SEE PART H FOR ADDITIONAL INFORMATION. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-05-07 02:35 | 2015-05-07 02:35 | ONSHORE | NV | 89029 | LAUGHLIN | CLARK | MILEPOST | 4 | FORT_MOHAVE_720_SYS | INTERSECTION POINT / 21TVE0018413 | NO | OPERATOR-CONTROLLED PROPERTY | TRANSITION AREA | OTHER | VALVE OPERATOR AND STEM ASSEMBLY |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | MAINLINE | BALL |  | CAMERON |  |  |  | 2006 | 1996 | CARBON STEEL |  | LEAK |  |  | OTHER | SEE PART H FOR DESCRIPTION. | [5 empty] | CLASS 1 LOCATION | NO |  | 296 |  | NO | NO | NO |  | 0 | 0 | 1648 | 1801.08346816408 | 0 | 0 | 98737 | 107908.724754925 | 9409 | 10283.0062815266 | 0 | 0 |  |  | 109794 | 55079.8680879414 | 119992.814504616 | [8 empty] | 544 |  | 720 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS CAUSED BY THIRD PARTY VEHICULAR DAMAGE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [260 empty] | ALYSE BAKER | ENGINEERING TECHNICIAN | alyse.baker@swgas.com | 702-365-2077 | 702-221-4116 |  |  |  | THOMAS CARDIN | DIRECTOR - GAS OPERATIONS | 702-365-2028 | thomas.cardin@swgas.com | A VEHICLE OPERATED BY A THIRD PARTY STRUCK SECURITY FENCING AND HIT A SOUTHWEST GAS ABOVE GROUND REGULATOR/METERING STATION LOCATED ADJACENT TO NEEDLES HIGHWAY, JUST NORTH OF MILE POST 4 IN LAUGHLIN, NEVADA, THE FACILITY SUFFERED IRREPARABLE DAMAGE TO A 16-INCH VALVE OPERATOR AND STEM ASSEMBLY. THE ESTIMATED COSTS OF SOUTHWEST GAS' EMERGENCY RESPONSE AND FACILITY REPAIR RESULTED IN THE INCIDENT MEETING PHMSA/DOT NOTIFICATION CRITERIA. PART A, 15: GAS FACILITIES HAVE BEEN SECURED, BUT MAY REQUIRE SHUT DOWN FOR REPLACEMENT ONCE NEW MATERIALS HAVE BEEN RECEIVED FROM SUPPLIER. PART C, 6 TYPE OF INCIDENT: LEAK/OTHER - THE SOURCE OF THE LEAK WAS A BROKEN GREASE FITTING THAT RESULTED FROM THE DAMAGE TO THE STEM ASSEMBLY. SUPPLEMENTAL: SUPPLEMENTAL REPORT FILED TO UPDATE FINAL REPAIR COST INFORMATION INITIALLY ESTIMATED IN PART D, 7 - ESTIMATED PROPERTY DAMAGE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150074 | 16774 | 2015-06-03 12:07 | ORIGINAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2015-05-04 09:42 | 2015 |  |  | 37.0349 | -85.9654 | 1115436 | 2015-05-04 10:39 |  | NATURAL GAS |  | 1651 | 219 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-05-04 12:06 | 2015-05-06 10:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 4 | 2015-05-04 09:42 | 2015-05-04 10:15 | ONSHORE | KY | 42141 | GLASGOW | BARREN | MILEPOST | 4+5116 | PARK CITY GLASGOW 8" | PCG 8" | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 38 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8.625 |  | 0.188 | 42000 | API 5LX | LONGITUDINAL ERW - LOW FREQUENCY |  | REPUBLIC STEEL | COAL TAR | [28 empty] | 1967 | 1967 | CARBON STEEL |  | MECHANICAL PUNCTURE | 2 | 5.5 | [7 empty] | CLASS 1 LOCATION | NO |  | 129 |  | NO | NO | NO |  | 9000 | 9836.01408584753 | 575 | 628.412011040259 | 4329 | 3871.71126760563 | 129000 | 140982.868563815 | 100 | 109.289045398306 | 0 | 0 |  |  | 143004 | 73582.4498925599 | 155428.294973706 | [8 empty] | 477 |  | 543 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 40700 | NO | [5 empty] | YES | NO PIG TRAPS | YES |  |  |  |  | YES | SINGLE LINE SOURCE FOR CUSTOMERS | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY DAMAGE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [7 empty] | CONTRACTOR | TRENCHER | TELECOMMUNICATIONS | NO | [5 empty] | YES | 46 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 2706886361 | jeff.mcmaine@bwpmlp.com | THIRD PARTY CONTRACTOR HIT PARK CITY-GLASGOW 8" LINE IN BARREN COUNTY, KY WHILE INSTALLING FIBER OPTIC CABLE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150075 | 17042 | 2015-06-03 17:49 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2015-05-04 22:35 | 2015 |  |  | 42.3892 | -84.0781 | 1115506 | 2015-05-05 00:46 |  | NATURAL GAS |  | 48000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-05-05 00:33 | 2016-01-16 16:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-05-04 22:35 | 2015-05-05 00:26 | ONSHORE | MI | 48169 | CHELSEA | WASHTENAW | SURVEY STATION NO. | 738+90 | LINE 100A | CHELSEA TO STOCKBRIDGE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.25 | 52000 | PA40200 250-6R | FLASH WELDED |  | A.O. SMITH | OTHER | TRAVEL LINE WRAPPED WITH 6X WAX AND NO. 7 WRAPPER | [27 empty] | 1949 | 1949 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 134 | 20 |  | CLASS 1 LOCATION | NO |  | 385 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 358080 | 320254.647887324 | 5000000 | 5464452.26991529 | 27773 | 30352.8465784715 | 53295 | 58245.5967450271 | INVESTIGATION (LAB SERVICES) |  | 5439148 | 2881019.34000807 | 5873305.36112612 | [8 empty] | 747 |  | 780 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 62499 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE OPERATOR RECOGNIZED THE DROP IN PRESSURE ON LINE 100A AND NOTIFIED APPROPRIATE PERSONNEL. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED | YES | YES | [15 empty] | STRESS CORROSION CRACKING | [12 empty] | YES | STRESS CORROSION CRACKING | [55 empty] | YES |  | YES |  | YES | [15 empty] | 2013 | [19 empty] | 2013 | [23 empty] | YES | 1968 | 1170 | NO | [13 empty] | NO | [63 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST I | carmella.king@cmsenergy.com | 517-788-0509 |  |  |  |  | ALAN CHICHESTER | GAS REGULATORY SERVICES ENGINEER | 989-791-5841 | alan.chichester@cmsenergy.com | AT APPROXIMATELY 22:35 HOURS ON MONDAY, MAY 4, 2015, CONSUMERS ENERGY'S GAS CONTROL PERSONNEL RECEIVED AN ALARM FROM A SCADA POINT AT STOCKBRIDGE CITY GATE IDENTIFYING A PRESSURE DROP OF APPROXIMATELY 200 PSIG AS A RESULT OF A RUPTURE OF LINE 100A. LINE 100A IS A 20" INTRASTATE TRANSMISSION PIPELINE STRETCHING APPROXIMATELY 60 MILES FROM FREEDOM COMPRESSOR STATION IN MANCHESTER, MICHIGAN (WASHTENAW COUNTY) TO OVID SUBSTATION IN OVID, MICHIGAN (CLINTON COUNTY). CONSUMERS ENERGY EMPLOYEES ARRIVED ON SITE AT APPROXIMATELY 00:26 HOURS ON MAY 5, 2015 AND ISOLATED A 12 MILE SEGMENT OF LINE 100A UTILIZING EMERGENCY VALVES LOCATED AT THE CHELSEA INTERCHANGE NEAR CHELSEA, MICHIGAN (WASHTENAW COUNTY) AS WELL AS STOCKBRIDGE CITY GATE IN STOCKBRIDGE, MICHIGAN (INGHAM COUNTY). GAS WAS SHUT OFF TO THE RUPTURED SEGMENT OF PIPELINE AT APPROXIMATELY 00:33. EMPLOYEES ARRIVING ON SITE TO ISOLATE THE AFFECTED SEGMENT CONFIRMED THE LOCATION OF THE PIPELINE RUPTURE NEAR SOUTH LAKE DRIVE AND ROEPKE ROAD IN CHELSEA AT APPROXIMATELY 01:09. LOCAL POLICE AND FIRE PERSONNEL WERE ALSO ON SITE RESPONDING. NO INJURIES, FATALITIES, OR IGNITION OCCURRED AS A RESULT OF THE RELEASE. THE DAMAGED PIPELINE AND ASSOCIATED FRAGMENTS WERE SECURED AND TRANSPORTED TO CONSUMERS ENERGY'S TRAIL STREET LABORATORY FOR METALLURGICAL TESTING AND DETERMINATION OF A FAILURE MODE. PRELIMINARY RESULTS INDICATE THE PRESENCE OF STRESS CORROSION CRACKING (SCC). THE POTENTIAL FOR ADDITIONAL SCC CONDITIONS ON LINE 100A HAS RESULTED IN CONSUMERS ENERGY TAKING A REDUCTION IN PRESSURE FOR LINE 100A OF MORE THAN 20% OF THE OPERATING PRESSURE AT THE TIME OF CONDITION DETERMINATION. THIS REDUCTION WAS MADE FOR THE ENTIRETY OF LINE 100A BETWEEN FREEDOM AND OVID, AND WAS COMPLETED ON JUNE 2, 2015 PENDING ADDITIONAL INTEGRITY MANAGEMENT TESTING AND REMEDIATION. REMEDIATION ACTIVITIES AND HYDROSTATIC TESTING WERE PERFORMED IN ACCORDANCE WITH APPLICABLE REGULATIONS AND LIVE GAS WAS RETURNED TO THE RELEVANT PORTIONS OF LINE 100A, FREEDOM COMPRESSOR STATION TO OVID VALVE SITE ON JANUARY 16, 2016.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150076 | 16922 | 2015-06-05 21:49 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2015-05-06 23:59 | 2015 |  |  | 39.1129 | -121.6177 | 1115710 | 2015-05-07 01:21 |  | NATURAL GAS |  | 0.01 | 20 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-05-07 00:45 | 2015-05-07 05:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-05-06 23:59 | 2015-05-06 12:45 | ONSHORE | CA | 95991 | YUBA CITY | SUTTER COUNTY | MILEPOST | MP 0.71 | DFM 1501-01 | MP 0.71 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 52 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 3 |  | 0.148 | 28000 | UNKNOWN | OTHER | ERW | UNKNOWN | ASPHALT | [28 empty] | 1943 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | LEAK FOUND ON GIRTH WELD | [5 empty] | CLASS 3 LOCATION | YES | METHOD2 | 38 |  | NO | NO | NO |  | 0 | 0 | 57 | 62.2947558770344 | 1 | 0.894366197183099 | 160000 | 174862.472637289 | 0 | 0 | 0 | 0 |  |  | 160058 | 80296.0111740843 | 174925.661759364 | [8 empty] | 236 |  | 245 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 18585 | NO | YES |  |  |  |  | YES | SMALL DIAMETER PIPE | YES |  |  |  |  | YES | (SEE PART E, QUESTION 5D ABOVE) | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PG&E PERSONNEL DETECTED THE LEAK WHILE CONDUCTING WORK | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [7 empty] | YES | [14 empty] | YES | [63 empty] | NO | [63 empty] | NO |  |  | Yes, and an investigative dig was cunducted at the point of the Accident | 2015 | [12 empty] | YES | 2015 | [6 empty] | YES | [55 empty] | STEPHEN RAMOS | COMPLIANCE ENGINEER | s3rc@pge.com | [5 empty] | LARRY DENISTON | MANAGER GAS REGULATORY COMPLIANCE | 925-328-5756 | lcd1@pge.com | AT APPROXIMATELY 1245 HOURS ON MAY 6, 2015 WHILE CONDUCTING GAS TRANSMISSION ASSESSMENT WORK, A PG&E CREW SMELLED GAS NEAR THE INTERSECTION OF GARDEN HIGHWAY AND LINCOLN ROAD IN YUBA CITY. A PG&E GAS CONSTRUCTION CREW EXCAVATED THE GAS FACILITY TO DETERMINE THE LEAK SOURCE. A LEAK ON DFM 1501-01 WAS DISCOVERED ON THE GIRTH WELD AT 2359 HOURS ON MAY 6, 2015. PG&E ISOLATED AND DE-PRESSURIZED A SECTION OF THE DFM BY APPROXIMATELY 0045 HOURS ON MAY 7, 2015. A 5-FOOT SECTION OF PIPE (WITH THE LEAK) WAS CUT OUT AND REPLACED WITH PRE-TESTED PIPE. THE LINE WAS PUT BACK IN SERVICE BY 0530 HOURS, ON MAY 7, 2015. DURING THE INCIDENT, THERE WERE NO INJURIES OR FATALITIES, AND THERE WAS NO IGNITION OF THE GAS. NO MEDIA WAS PRESENT. PG&E PROVIDED CNG TO THE CUSTOMERS SERVED OFF THIS SECTION OF THE DFM, THUS NO CUSTOMERS LOST GAS SERVICE DURING THE INCIDENT. THE INCIDENT WAS REPORTED TO THE NATIONAL RESPONSE CENTER AND THE CPUC WHEN ESTIMATED DAMAGES WERE DETERMINED TO LIKELY TO EXCEED $50,000. THE CAUSE OF THE LEAK ORIGINATED FROM THE GIRTH WELD CRACK, WHICH WAS FOUND TO BE CAUSED BY DUCTILE OVERLOAD AT A LOCATION WHERE INCOMPLETE FUSION, AND INCOMPLETE PENETRATION WERE PRESENT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150077 | 17077 | 2015-06-09 16:59 | SUPPLEMENTAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2015-03-20 15:30 | 2015 |  |  | 32.6997 | -90.931 | 1111322 | 2015-03-20 19:23 |  | NATURAL GAS |  | 5 | 4499 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-03-20 17:30 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-03-20 16:00 | 2015-03-20 16:00 | ONSHORE | MS | 39159 | ROLLING FORK | SHARKEY | MILEPOST | 1 | ONWARD/VICKSBURG LATERAL | ONWARD/VICKSBURG LATERAL | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | WATER | 11 |  | YES | [6 empty] | YES | UNCASED | DEER CREEK | 6 | BELOW WATER, PIPE BURIED BELOW BOTTOM (NOT IN BORED/DRILLED CROSSING) | [11 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 6.625 |  | 0.188 | 25000 | API 5L | SEAMLESS |  | NATIONAL TUBE | COAL TAR | [9 empty] | PIPE GIRTH WELD | [18 empty] | 1930 | 1930 | CARBON STEEL |  | LEAK |  |  | OTHER | UNDER INVESTIGATION | [5 empty] | CLASS 1 LOCATION | NO |  | 102 |  | NO | NO | NO |  | 0 | 0 | 22495 | 24584.5707623489 | 25 | 22.3591549295775 | 60000 | 65573.4272389835 | 850 | 928.9568858856 | 0 | 0 |  |  | 83370 | 41834.4965406474 | 91109.3140421476 | [8 empty] | 500 |  | 500 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 14784 | NO | [5 empty] | YES | LOW FLOW. | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  |  | YES | ACETYLENE WELDED PIPE | [5 empty] | YES | ACETYLENE WELDED PIPE | [19 empty] | YES | ACETYLENE WELDED PIPE. | [55 empty] | NO | [63 empty] | YES | 1963 | 550 | NO | [13 empty] | NO | [63 empty] | VALERIE BERGMAN | KMI PIPELINE ENGINEER | valerie_bergman@kindermorgan.com | 713-420-4810 |  |  |  |  | VALERIE BERGMAN | KMI PIPELINE ENGINEER | 713-420-4810 | valerie_bergman@kindermorgan.com | A TRUCK DRIVER STOPPED OFF OF HIGHWAY 61 AND NOTICED BUBBLING WATER IN DEER CREEK. THE TRUCK DRIVER CALLED MS811, WHO THEN NOTIFIED SOUTHERN NATURAL GAS CONTROL AT APPROXIMATELY 15:30. KMI OPERATIONS ARRIVED ON SITE AND CONFIRMED THAT THERE WERE BUBBLES IN DEER CREEK, THIS CREEK LIES SOUTH OF THE ONWARD COMPRESSOR STATION NEAR MILE POST 1. AT 16:00, A KMI LINE PATROLLER USED A LASER METHANE LEAK DETECTOR AND CONFIRMED THE PRESENCE OF METHANE GAS. AT 17:30, KMI OPERATIONS BEGAN TO BLOW DOWN THE FIRST 2.3 MILES OF THE ONWARD VICKSBURG LINE TO BELOW 100 PSI; BUBBLES WERE NO LONGER VISIBLE IN THE CREEK AND METHANE WAS NOT DETECTED THEREAFTER. THROUGH ITS INVESTIGATION, SNG HAS CONCLUDED THAT THIS 2.3 MILE SEGMENT OF PIPE WILL BE ABANDONED WITHOUT AFFECTING THE CAPACITY OR OPERATION OF THE REST OF THE SNG SYSTEM. THIS 2.3 MILE SEGMENT OF PIPE IS ONE OF THREE PARALLEL PIPES ACROSS THIS 2.3 MILE AREA, AND THE REMAINING TWO PIPES HAVE SUFFICIENT CAPACITY TO MAKE-UP FOR THE LOSS OF THIS ONE 2.3 MILE SEGMENT OF PIPE. THEREFORE, SNG DOES NOT PLAN TO EXCAVATE THE LEAKING PIPE TO FURTHER ASSESS IT OR REPAIR IT. SNG WILL CONTINUE TO MAINTAIN THIS SEGMENT OF PIPE TO BELOW 100 PSI UNTIL CONDITIONS ALLOW FOR IT TO BE ABANDONED WITH MINIMAL IMPACTS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150078 | 16893 | 2015-06-12 12:19 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2015-05-15 16:25 | 2015 |  |  | 28.4537 | -91.4564 | 1116658 | 2015-05-15 18:08 |  | NATURAL GAS |  | 1 | 2700 | 0.1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-05-16 09:30 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-05-15 16:25 | 2015-05-16 13:15 | OFFSHORE | [28 empty] | 174 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EUGENE ISLAND | 259 | PORTION OF RISER OUTSIDE OF SPLASH ZONE, INCLUDING RISER BEND | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12 |  | 0.375 | 46000 | API 5L | SEAMLESS |  | UNKNOWN | FIELD APPLIED EPOXY | [28 empty] | 1967 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 371 |  | NO | NO | NO |  | 0 | 0 | 8100 | 8852.41267726278 | 4 | 3.57746478873239 | 375000 | 409833.920243647 | 0 | 0 | 0 | 0 |  |  | 383104 | 192191.78353711 | 418689.910385699 | [8 empty] | 866 |  | 1250 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | CHECK VALVE | 57182 | NO | YES | [6 empty] | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | NO |  |  |  |  | OTHER | NOTIFICATION FROM THE PLATFORM OWNER |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SMALL SIZE AND VOLUME OF THE LEAK | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  |  | YES | [7 empty] | YES |  |  |  | NO | [11 empty] | YES | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | YES |  |  |  |  | 2015 | [6 empty] | YES | [51 empty] | ROGER R. STREET | FIELD COMPLIANCE SPECIALIST | roger_street@transcanada.com | 615-465-5123 |  |  |  |  | ROGER STREET | FIELD COMPLIANCE SPECIALIST | 615-465-5123 | roger_street@transcanada.com | ON 15 MAY 2015 AT 16:25 CDT, A LEAK ON TC OFFSHORE (TCO) PIPELINE RISER WAS REPORTED BY THE OWNER OF THE PLATFORM LOCATED IN OUTER CONTINENTAL SHELF SHIP EUGENE ISLAND BLOCK 259 (EI259). AN AUDIBLE RELEASE OF GAS WAS DISCOVERED BY THE THIRD PARTY PRODUCER EMANATING FROM BENEATH A RISER CLAMP AND REPORTED TO TRANSCANADA/ANR PIPELINE COMPANY (ANR), OPERATOR FOR TCO. THE LEAK WAS LOCATED ABOVE THE WATER LINE ON THE PIPELINE RISER NEAR MILEPOST 0 ON THE 757 12' TRANSMISSION LINE ON A PLATFORM OWNED BY ENERGY XXI (28.45374, -91.456405). THE INCIDENT WAS REPORTED TO THE NATIONAL RESPONSE CENTER ON 15 MAY 2015 AT 18:08 CDT (REPORT #116658). FOLLOWING THE REPORT OF THE INCIDENT TO THE NATIONAL RESPONSE CENTER, ANR MAINTAINED CONTACT AND UPDATED U.S. COAST GUARD, BSEE, AND PHMSA. FOLLOWING THE DISCOVERY LEAK, THE 10.83 MILE PIPELINE SECTION WAS ISOLATED AT 09:30 CDT ON 16 MAY 2015 FROM EI259 TO EUGENE ISLAND 231. THE PIPELINE WAS ATTEMPTED TO BE BLOWN DOWN BEGINNING ON 16 MAY, WHEN PROCESS WATER WAS DISCOVERED IN THE PIPELINE. DURING THE BLOW DOWN, THE WATER FROM THE PIPELINE WAS PROCESSED BY A VENT SCRUBBER AND STORED IN TANKS AT THE PLATFORM ON EI259. ADDITIONALLY, A GAS BUSTER WAS USED TO FURTHER REDUCE THE PRESSURE ON THE PIPELINE AND REMOVE PROCESS WATER. ON 18 MAY 2015 AT 06:45, A PIPELINE TECHNICIAN OBSERVED THE PRESENCE OF SHEEN ON THE SURFACE OF THE WATER FROM LEAK LOCATION. AN ADDITIONAL NRC REPORT WAS FILED ON 18 MAY 2015 AT (NRC REPORT #1116799). LOCATION AND AREA OF THE SHEEN WAS MONITORED UNTIL THE LEAKING CEASED ON 21 MAY 2015. ON 24 MAY 2015, VENTING WAS COMPLETED, THE LINE WAS PURGED WITH NITROGEN, AND PREPARATIONS WERE MADE TO REPAIR THE LINE. FOLLOWING VENTING OF THE LINE, THE CLAMP ON THE PIPELINE RISER WAS REMOVED AND NON-DESTRUCTIVE EXAMINATION (MAG PARTICLE) WAS PERFORMED ON THE LEAK AREA. ANALYSIS DETERMINED THAT THE LEAK WAS CAUSED BY PITTING ATTRIBUTED TO EXTERNAL CORROSION. ON 25 MAY 2015, AN EXTERNAL WELD-ON SPLIT SLEEVE REPAIR CLAMP WAS SUCCESSFULLY INSTALLED ONTO THE PIPELINE TO REPAIR THE LEAK LOCATION. THE PIPELINE WAS RE-COATED WITH CARBO-MASTIC EPOXY PAINT AND THE RISER CLAMP WAS REINSTALLED. IN SEPTEMBER 2015, THE PIPELINE WAS PLACE RETURNED TO SERVICE
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150079 | 16781 | 2015-06-12 13:06 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2015-05-15 13:00 | 2015 |  |  | 37.9171 | -83.9856 | 1116644 | 2015-05-15 14:29 |  | NATURAL GAS |  | 5321 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELIEF VALVE WAS ISOLATED AND RESET. A STATION SHUT-IN WAS NOT REQUIRED. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-05-15 13:00 | 2015-05-15 13:00 | ONSHORE | KY | 40312 | Not Within a Municipality | POWELL COUNTY | MILEPOST | MP876-1+00 | STATION 106 | TGP LINE NO. 5. | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | RELIEF VALVE | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | PREMATURE ACTIVATION OF RELIEF VALVE BELOW ESTABLISHED SETPOINT PRESSURE. THIS WAS DETERMINED TO HAVE RESULTED FROM DEBRIS IN RELIEF VALVE PILOT CONTROL. | CLASS 2 LOCATION | YES | METHOD2 | 567 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 23000 | 20570.4225352113 | 0 | 0 | 400 | 437.156181593224 | 0 | 0 |  |  | 23400 | 21526.9573023305 | 21007.5787168045 | [8 empty] | 743 |  | 750 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO THE RELEASE NOT CAUSED BY ANY OF THE CONTROLLERS ACTIONS. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | THE RELIEF VALVE OPENED PREMATURELY DUE TO DEBRIS FOUND IN THE RELIEF VALVE PILOT CONTROLS. | [147 empty] | STEPHEN R. DINES | ENGINEER CODES AND STANDARDS | stephen_dines@kindermorgan.com | (719) 351-4199 |  |  |  |  | REJI GEORGE | DIRECTOR OF ENGINEERING CODES AND STANDARDS | (713) 420-5433 | reji_george@kindermorgan.com | INCIDENT DESCRIPTION: RELIEF VALVE ('RV') 800 BD5 LIFTED PREMATURELY AT STATION 106 COMPRESSOR STATION ON MAY 15, 2015. RV LIFTED AT 748 PSIG AND DID NOT RE-SEAT. EVENT DURATION WAS 7 MINUTES UNTIL KMI ON-SITE OPERATIONS CLOSED THE VALVE UNDER THE RV TO STOP THE VENTING. THE INCIDENT RESULTED IN A TOTAL OF 5,321 MCF OF GAS LOSS. MAOP OF THE STATION FACILITIES WAS NOT EXCEEDED DURING THE INCIDENT. IMMEDIATE ACTION TAKEN: THREE COMPRESSOR UNITS WERE TAKEN OFF LINE, THE RV WAS ISOLATED, TO STOP THE VENTING OF GAS AND UNIT WAS PROMPTLY REPAIRED. TGP FOUND DEBRIS FOULING THE RELIEF VALVE EXTERNAL CONTROL BOX WHICH ALLOWED THE RELIEF VALVE TO OPEN PRIOR TO THE ESTABLISHED SET POINT. TGP WILL INCREASE THE FREQUENCY OF MAINTENANCE ON THE PILOT CONTROL TO EVALUATE THE LEVEL OF DEBRIS ACCUMULATION ON THE STATION YARD RVS INITIALLY. TWO OUT-OF-CYCLE INSPECTIONS ON EACH STATION YARD RV PILOT CONTROLS WILL BE COMPLETED TO EVALUATE THE LEVEL OF DEBRIS ACCUMULATION BEING EXPERIENCED AND TO DETERMINE WHETHER INCREASED INSPECTIONS ARE WARRANTED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150080 | 17171 | 2015-06-15 16:08 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2015-05-15 13:10 | 2015 |  |  | 44.1606 | -85.0044 | 1116955 | 2015-05-19 16:11 |  | NATURAL GAS |  | 3600 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-05-15 14:30 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-05-15 13:10 | 2015-05-15 13:10 | ONSHORE | MI | 49665 | MARION | CLARE | SURVEY STATION NO. | LATERAL 60W | MARION STORAGE FIELDS | CRANBERRY LAKE FIELD | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 24 |  | NO | [22 empty] | INTRASTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | PIPE | PIPE BODY | 6 |  | 0.25 | 35000 | API5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | YOUNGSTOWN SHEET & TUBE | OTHER | BLACK WRAP WITH LIGHT BROWN OUTER-LAYER NO ASBESTOS FIBERS | [27 empty] | 1957 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 117 |  | NO | NO | NO |  | 0 | 0 | 382 | 417.484153421529 | 26865 | 24027.1478873239 | 21101 | 23061.0814694965 | 500 | 546.445226991529 | 9798 | 10708.140668126 | LABORATORY ANALYSIS |  | 58646 | 40853.4682559045 | 58760.2994053595 | [8 empty] | 455 |  | 800 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE FACILITY WAS NOT MONITORED BY A CONTROLLER AT THE TIME OF THE INCIDENT | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  | YES | WATER DROP-OUT |  | YES |  |  | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | YES | YES | [6 empty] | 2005 | [55 empty] | YES | 1999 | 1241 | NO | [13 empty] | NO | [63 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 734-513-6256 |  |  |  |  | AMANDA L. WARD | GAS REGULATORY SERVICES ENGINEER | 517-545-8746 | amanda.ward@cmsenergy.com | AT APPROXIMATELY 13:10 ON FRIDAY, MAY 15, 2015 A CONSUMERS ENERGY (CE) EMPLOYEE INSTALLING PIPELINE MARKERS AT THE CRANBERRY STORAGE FIELD OBSERVED BUBBLING FROM A STANDING WATER PUDDLE AND A FROST BALL IN AN AREA ABOVE LATERAL 60 WEST BETWEEN WELLS C270 AND C367. LATERAL 60 WEST IS A 6" PIPELINE (APPROXIMATELY 1 1/2 MILES LONG) LOCATED IN CONSUMERS ENERGY'S CRANBERRY STORAGE FIELD, MARION, MICHIGAN (MISSAUKEE COUNTY). ADDITIONAL CE EMPLOYEES ARRIVED ON-SITE AT APPROXIMATELY 14:00 ON MAY 15, 2015 TO BEGIN IMPLEMENTING THE STANDARD PRECAUTIONARY LOCK OUT TAG OUT PROCESS, ISOLATING AND SHUTTING DOWN LATERAL 60 WEST AND BARRICADING THE LOCATION UNTIL FURTHER INVESTIGATION COULD BE PERFORMED. THE BLOW-DOWN PROCESS WAS COMPLETE AND THE LINE SHUT-DOWN AT APPROXIMATELY 14:30. ON MONDAY, MAY 18, 2015 A 11/2 FOOT SECTION OF THE PIPELINE WAS CUT OUT AND A PINHOLE LEAK DISCOVERED. THE LEAK WAS VISUALLY EXAMINED AND PRELIMINARY ANALYSIS IDENTIFIED CORROSION AS A POSSIBLE LEAK SOURCE. THE APPROXIMATE GAS LOSS OF 3.6 MMCF WAS ESTIMATED BASED ON INFORMATION OBTAINED FROM THE LEAK PATROL CONDUCTED ON MARCH 18, 2015. THERE WAS NO INDICATION OF ABNORMAL CONDITIONS AT THIS LOCATION AT THAT TIME. THE DAMAGED SECTION OF THE PIPELINE WAS TRANSPORTED TO THE CONSUMERS ENERGY TRAIL STREET LABORATORY FOR FURTHER EXAMINATION. THE LABORATORY ANALYSIS CONFIRMED THE LEAK WAS A RESULT OF A LOCALIZED CORROSION PIT ON THE PIPE ID WHICH DEVELOPED AN OVAL THROUGH WALL HOLE AT THE OD MEASURING APPROXIMATELY .375"X 0.25". THE PRESENCE OF SIGNIFICANT CONCENTRATION OF SULFUR WITHIN THE PIT INDICATES MICROBIOLOGICAL INFLUENCE CORROSION (MIC) CAUSED BY SULFATE-REDUCING BACTERIA (SRB) MAY HAVE CAUSED OR CONTRIBUTED TO THE FAILURE. HOWEVER, IT COULD NOT BE DEMONSTRATED THAT THE DAMAGE MEETS THE THREE CRITERIA REQUIRED TO VALIDATE MIC. IN ADDITION TO COMPREHENSIVE METALLURGICAL TESTING, CONSUMERS ENERGY CONDUCTED A REVIEW OF THE 2005 TOOL DATA AND IDENTIFIED TWO DIG LOCATIONS AS VERIFICATION. THE LOCATIONS, DIG #1 JT 60 AND DIG #2 JT 117, WERE EXPOSED, EXAMINED AND ONE SECTION (DIG #2 JT 117) WAS REPLACED DUE TO THE PRESENCE OF MINOR CORROSION. ULTRASONIC THICKNESS (UT) SENSORS WERE ALSO INSTALLED AT THESE TWO LOCATION TO MONITOR INTERNAL CORROSION. REMEDIATION WORK WAS COMPLETED AND LATERAL 60 WEST WAS PLACED BACK INTO SERVICE ON OCTOBER 7, 2016. ON OCTOBER 24, 2015 AN ADDITIONAL LEAK WAS DISCOVERED ON LATERAL 60 WEST APPROXIMATELY 677 FEET NORTH OF THE LEAK IDENTIFIED IN MAY. AN INCIDENT REPORT-GAS TRANSMISSION AND GATHERING PIPELINE SYSTEMS (2015140-16931) WAS SUBMITTED TO PHMSA ON NOVEMBER 24, 2015. LABORATORY ANALYSIS CONFIRMED THE LEAK DISCOVERED IN OCTOBER WAS A RESULT OF A LOCALIZED CORROSION PIT ON THE PIPE ID. THE MIC TESTING PERFORMED ON SLUDGE EXTRACTED FROM THE PIPE INDICATES MICROBIOLOGICAL INFLUENCE CORROSION (MIC) MAY HAVE CAUSED OR CONTRIBUTED TO THE FAILURE.
2021-02-26 10:37 | NO | NO | GG (Gas Gathering) | 20150081 | 30505 | 2015-06-17 16:38 | SUPPLEMENTAL | 11272 | LAVACA PIPELINE CO | 103 FANNIN ROAD, PO BOX 769 | POINT COMFORT | TX | 77978 | 2015-05-22 17:45 | 2015 |  |  | 28.3519 | -96.6043 | 1117310 | 2015-05-22 18:00 |  | NATURAL GAS |  | 350 | 100 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-05-22 20:15 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-05-22 18:30 | 2015-05-22 20:15 | OFFSHORE | [28 empty] | 15 | IN STATE WATERS | TX | SEADRIFT | MM 487 | CALHOUN |  |  |  | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTRASTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 8 |  | 0.322 | 35000 | GRADE B | SEAMLESS |  | UNKNOWN | COAL TAR | [28 empty] | 1980 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 156 | 4 |  | CLASS 1 LOCATION | NO |  | 146 |  | NO | NO | NO |  | 0 | 0 | 275 | 300.544874845341 | 688 | 615.323943661972 | 55000 | 60108.9749690682 | 850 | 928.9568858856 | 0 | 0 |  |  | 56813 | 28793.9136194024 | 61953.8006734612 | [8 empty] | 510 |  | 600 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 41593 | NO | [5 empty] | YES | WHEN THESE LINES WERE LAYED, THEY WERE NOT DESIGNED TO BE PIGGABLE. | YES |  |  |  |  | YES | WHEN THESE LINES WERE LAYED, THEY WERE N | OFFSHORE GATHERING | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | FURTHER EXAMINATION IS NEEDED DUE TO THE DEPTH OF THE PIPE UNDER THE MUD BED. DIVER CONFIRMED PIPE WAS SMOOTH ON OUTSIDE DIAMETER OF PIPE. |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NOT APPLICABLE - NOT MAINLINE PIPE | YES | [168 empty] | NO | [63 empty] | YES | 2012 | 835 | NO | [13 empty] | NO | [63 empty] | DAVID GASKAMP | SAFETY AND ENVIRONMENTAL COORDINATOR | davidgaskamp@ftpc.fpcusa.com | 361-987-8903 | 361-987-8933 |  |  |  | WESLEY LIN | MANAGER | 361-987-8904 | wesleylin@ftpc.fpcusa.com | SUPPLEMENTAL UPDATE: THE STEAMBOAT PASS SOUTH 8" LINE IS STILL SHUT DOWN. THE PIPELINE WILL REMAIN INACTIVE AND IS IN THE PROCESS OF BEING ABANDONED (WELLS PLUGGED, PIPE BLIND FLANGE AND CAPPED). THE ABANDONMENT IS PENDING DUE TO MULTIPLE AGENCY PERMITTING DELAYS. LAVACA PIPE LINE COMPANY LPL EXPERIENCED A LEAK IN THE STEAMBOAT PASS SOUTH 8" LINE LOCATED IN INTERCOASTAL WATERWAY AT MM 487 ON MAY 22, 2015. THE INCIDENT WAS CALLED IN TO THE CALHOUN COUNTY SHERIFF'S OFFICE AND IN RETURN THE COAST GUARD WAS CALLED. THE COAST GUARD NOTIFIED THE TEXAS GENERAL LAND OFFICE. TEXAS GENERAL LAND OFFICE NOTIFIED RICHARD GARCIA, POINT OF CONTACT FOR LPL, AT 18:30. PIPELINE PERSONNEL WERE DISPATCHED TO THE ISOLATION VALVES AT SOUTHPASS AND THE ISOLATION VALVE AT LPL'S LANE ROAD FACILITY. THE ISOLATION VALVE AT SOUTHPASS WAS CLOSED AT 19:30. THE ISOLATION VALVE AT LANE ROAD CLOSED AS SOON AS IT WAS RELAYED THAT THE SOUTHPASS VALVE WAS CLOSED. THE BLOW-DOWN VALVE WAS OPENED INTO BLOW-DOWN TANK TO RELEASE ANY PRESSURE, BUT PRESSURE WAS ALREADY DOWN TO 40 PSI. THE 40 PSI LEFT ON THE LINE WAS DEPLETED IN A MATTER OF MINUTES. AT THAT TIME, GLO WAS AT THE SCENE, AND IT WAS DETERMINED THAT THE COAST GUARD, TEXAS GENERAL LAND OFFICE, AND DAVID GASKAMP (SENIOR SUPERVISOR LPL) WOULD INVESTIGATE THE AREA OF THE LEAK ON SATURDAY MAY 23, 2015. ON MAY 23, 2015, THE INVESTIGATION CONCLUDED THAT THERE WAS NO DAMAGE TO THE ENVIRONMENT AND THAT NO GAS OR CONDENSATE WAS PRESENT. TEXAS GENERAL LAND OFFICE DETERMINED THAT IT WAS A NON-RECORDABLE INCIDENT, AND COAST GUARD CONCURRED. LPL IS REPORTING THE INCIDENT DUE TO THE FACTOR OF THE ESTIMATED PROPERTY DAMAGE OF $50,000 OR MORE IS CONSIDERED DUE TO THE PRICE OF THE REPAIRS THAT WILL BE NEEDED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150082 | 17008 | 2015-06-18 14:18 | SUPPLEMENTAL FINAL | 2620 | COLUMBIA GULF TRANSMISSION, LLC | 700 LOUISIANA ST. SUITE 700 | HOUSTON | TX | 77002 | 2015-05-21 21:47 | 2015 |  |  | 30.3197 | -92.2636 | 1117424 | 2015-05-21 23:46 |  | NATURAL GAS |  | 34860 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE COMPRESSOR STATION WAS SET IN BY-PASS MODE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-05-21 21:47 | 2015-05-21 22:33 | ONSHORE | LA | 70578 | RAYNE | ACADIA PARRISH | MILEPOST | RAYNE | COMPRESSOR STATION | ESD VALVE 10SH-1D | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1970 |  | CARBON STEEL |  | OTHER | [8 empty] | ESD 8-IN VALVE FAILED TO CLOSE | CLASS 1 LOCATION | NO |  | 179 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 85407 | 76385.1338028169 | 20000 | 21857.8090796612 | 0 | 0 | 0 | 0 | NO OTHER ASSOCIATED COSTS |  | 105407 | 89225.2477456344 | 98242.9428824781 | [8 empty] | 697 |  | 1008 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE FAILURE EOF THE VALVE TO CLOSE WAS IDENTIFIED TO BE DUE TO A SOFTWARE GLITCH AND WAS NOT DUE TO HUMAN INTERVENTION OR ACTIONS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | CENTRAL PROCESSING UNIT (CPU) INITIATED A FAULTY SIGNAL TO THE ESD VALVE TO STAY OPEN. | [15 empty] | YES | CPU SOFTWARE ERROR | [161 empty] | GEORGE HAMATY | ENGINEER | ghamaty@cpg.com | (304) 357-3728 | (304) 357-3522 |  |  |  | PERRY MICHAEL HOFFMAN | MANAGER | (304) 357-2548 | mikehoffman@cpg.com | ON MAY 21, 2015, COLUMBIA GULF TRANSMISSION, LLC (COLUMBIA) RECEIVED AN ALARM FROM RAYNE COMPRESSOR STATION (CS) FACILITY REGARDING AN EMERGENCY SHUTDOWN (ESD). COLUMBIA PERSONNEL WERE DISPATCHED TO INVESTIGATE THIS ALARM. UPON ARRIVING AT THE SITE, COLUMBIA PERSONNEL NOTED THAT THE FACILITY WAS IN AN ESD MODE AND MATERIAL WAS STILL VENTING INADVERTENTLY INTO ATMOSPHERE. THE FACILITY WAS INSPECTED TO IDENTIFY THE LOCATION OF THE OPEN VALVE IN ORDER TO ACT ACCORDINGLY. THE COLUMBIA PERSONNEL DISCOVERED AN 8-IN ESD VALVE IN THE OPEN POSITION. COLUMBIA PERSONNEL ASKED FOR ASSISTANCE TO MANUALLY OVER-RIDE THIS VALVE. AFTER 21 MINUTES, THE VALVE STOPPED FLOWING MATERIAL AND THE FACILITY WAS PUT INTO SAFE OPERATION. FOLLOWING THE INCIDENT, COLUMBIA ASSEMBLED AN INVESTIGATIVE TEAM FROM COMPRESSION, AUTOMATION AND ELECTRICAL GROUPS IN ADDITION TO THE VALVE MANUFACTURER, IN ORDER TO INVESTIGATE AND HELP ASSEMBLE THE CHAIN OF EVENTS THAT LED THIS 8-IN ESD VALVE FROM FAILING TO CLOSE. PRELIMINARY INDICATIONS FOCUSED ON A SOFTWARE GLITCH WHICH LED TO INITIATE THIS ESD EVENT AND FALSE SIGNAL BY THE CONTROL PROCESSING UNIT TO INITIATE PROPER SIGNALS TO STOP THE MATERIAL FROM FLOWING INADVERTENTLY INTO ATMOSPHERE. THE FAULTY VALVE WAS ISOLATED AND WAS NOT RETURNED BACK INTO SERVICE UNTIL AN INVESTIGATION WAS COMPLETED TO ENSURE THAT THAT THE SAME HARDWARE ERROR WILL NOT TRIGGER ANOTHER EVENT. THE ESD SYSTEM WAS RETURNED BACK INTO SERVICE ON JUNE 12, 2015. DURING THIS TIME, THE CS WAS MANNED. THE KEY LESSONS IDENTIFIED FROM THIS INCIDENT WAS THAT COLUMBIA PERSONNEL TO ASSURE QUARTER TURN VALVES ARE IN THE OPEN POSITION AFTER ANY VALVE MAINTENANCE IS PERFORMED AND TO PERIODICALLY CHECK THE CENTRAL PROCESSING UNIT AREA FOR ANY FUTURE SIGNS OF TAMPERING OR EVIDENCE OF RODENTS. INITIAL INCIDENT REPORT WAS SUBMITTED ON JUNE 18, 2015
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150083 | 16970 | 2015-06-19 15:24 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2015-05-29 14:39 | 2015 |  |  | 37.375 | -100.2272 | 1118007 | 2015-05-29 18:57 |  | NATURAL GAS |  | 461 | 14 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-05-29 22:30 | 2015-05-31 14:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-05-29 14:39 | 2015-05-29 15:30 | ONSHORE | KS | 67844 | Not Within a Municipality | MEADE | MILEPOST | MP 7.84 | FOWLER BRANCHLINE | 179KSB22101 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 54 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 3.5 |  | 0.216 |  | UNKNOWN | LAP WELDED |  | YOUNGSTOWN | NONE | [28 empty] | 1930 | 1930 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 9.5 | 0.5 |  | CLASS 1 LOCATION | NO |  | 38 |  | NO | NO | NO |  | 500 | 546.445226991529 | 42 | 45.9013990672885 | 1383 | 1236.90845070423 | 60309 | 65911.1303892643 | 3000 | 3278.67136194918 | 0 | 0 |  |  | 65234 | 33314.2065899729 | 71019.0568279765 | [8 empty] | 214 |  | 250 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 49145 | NO | [5 empty] | YES | PIPE IS TOO SMALL FOR TOOL INSPECTION. | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATOR IDENTIFIED THE LEAK FIRST. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [8 empty] | YES | YES |  |  | YES | NO |  | NO | NO | [8 empty] | NO | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | J. DAVID CULLISON | PIPELINE SAFETY ENGINEER | j.cullison@nngco.com | 402-398-7439 | 402-548-5267 |  |  |  | THOMAS CORRELL |  | 402-398-7715 | thomas.correll@nngco.com | A LOW LOW PRESSURE ALARM WAS DETECTED AT 14:39 ON MAY 29, 2015, AT THE FOWLER METERING STATION. FIELD PERSONNEL WERE DISPATCHED TO INVESTIGATE IF THE ALARM WAS ACCURATE OR A DATA ERROR. FIELD PERSONNEL ARRIVED AT APPROXIMATELY 15:00 AND MEASURED THE PRESSURE AT THE INLET VALVE AND CONFIRMED THE LOW PRESSURE THAT SCADA HAD INDICATED. PERSONNEL BEGAN SEARCHING ALONG THE RIGHT-OF-WAY FOR AN INDICATION OF BLOWING GAS. A LEAK WAS DISCOVERED AT 16:45 APPROXIMATELY 830 FEET FROM THE NEAREST ROAD IN A FIELD WITH NO FIRE DETECTED. COORDINATION WITH THE LOCAL UTILITY ALLOWED THE LINE TO REMAIN IN SERVICE UNTIL 22:30 WHEN THE LINE WAS SHUT IN AND THE TOWN WAS SUPPLIED WITH A BOTTLE TRUCK. THE SITE WAS EXCAVATED ON MAY 30, 2015, AND THE DAMAGED PIPE, DUE TO THE LEAK, WAS REPLACED ON THE SAME DAY. THE PIPELINE WAS RETURNED TO SERVICE ON MAY 31, 2015, AND RESTRICTED TO 170 PSIG OR 80% OF THE ACTUAL OPERATING PRESSURE AT THE TIME OF THE INCIDENT. THIS REDUCTION WAS HELD UNTIL THE ENTIRE LINE COULD BE LEAK SURVEYED TO ENSURE NO FURTHER LEAKS WERE PRESENT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150085 | 16869 | 2015-06-25 08:22 | SUPPLEMENTAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2015-05-27 12:30 | 2015 |  |  | 30.4564 | -92.5288 | 1117735 | 2015-05-27 13:30 |  |  |  | 46 | 0 | 2 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | AREA ISOLATED WITHIN COMPRESSOR STATION YARD | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-05-27 12:30 | 2015-05-27 12:30 | ONSHORE | LA | 70535 | EUNICE | ACADIA | MILEPOST | 0 | EUNICE COMPRESSOR STATION | EUT 1 | NO | OPERATOR-CONTROLLED PROPERTY | TRANSITION AREA | OTHER | LIQUID HOLDING BOTTLE |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | PULSATION BOTTLE OR DRIP/DRIP COLLECTION DEVICE | [38 empty] | 1978 |  | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 96 | 120 |  | CLASS 1 LOCATION | NO |  | 519 |  | NO | NO | NO |  | 21000 | 22950.6995336442 | 0 | 0 | 138 | 123.422535211268 | 23000 | 25136.4804416104 | 30000 | 32786.7136194918 | 0 | 0 |  |  | 74138 | 37251.2089123683 | 80997.3161299576 | [8 empty] | 812 |  | 838 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  | YES |  |  |  | YES | RUPTURE OF THE DRIP BOTTLE CAN BE ATTRIBUTED TO INTERNAL CORROSION. A SUBSEQUENT CAUSE OF THE RUPTURE CAN BE ATTRIBUTED TO THE STATION'S TYPICAL FLOW PATTERNS. THE INJUNCTION OF FLUID INTO THE DRIP BOTTLE AT HIGH VOLUMES AND/OR PRESSURES GENERATED PREFERENTIAL SITES FOR INTERNAL CORROSION AT THE BOTTOM OF THE DRIP BOTTLE UNDER THE 4" INLET. THE WALL BECAME THIN AND NO LONGER HAD THE STRENGTH TO CONTAIN THE PRESSURE IN THE BOTTLE. |  | YES |  |  |  |  | YES |  |  |  | NO | NO | YES | YES | [313 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 2706886361 | jeff.mcmaine@bwpmlp.com | A 30"/26" DRIP BOTTLE FAILED DURING OPERATIONS TO ABANDON THE BOTTLE. DRIP BOTTLE RUPTURED. COMPLETE ROOT CAUSE DETERMINATION WILL BE SUBMITTED IN A FUTURE REPORT. 9-29-15 RUPTURE OF THE DRIP BOTTLE CAN BE ATTRIBUTED TO INTERNAL CORROSION. A SUBSEQUENT CAUSE OF THE RUPTURE CAN BE ATTRIBUTED TO THE STATION'S TYPICAL FLOW PATTERNS. THE INJUNCTION OF FLUID INTO THE DRIP BOTTLE AT HIGH VOLUMES AND/OR PRESSURES GENERATED PREFERENTIAL SITES FOR INTERNAL CORROSION AT THE BOTTOM OF THE DRIP BOTTLE UNDER THE 4" INLET. THE WALL BECAME THIN AND NO LONGER HAD THE STRENGTH TO CONTAIN THE PRESSURE IN THE BOTTLE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150086 | 17264 | 2015-06-25 13:26 | SUPPLEMENTAL FINAL | 26330 | ENABLE OKLAHOMA INTRASTATE TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2015-05-31 02:30 | 2015 |  |  | 34.9369 | -96.4006 | 1118132 | 2015-05-31 05:17 |  | NATURAL GAS |  | 3441.2 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-05-31 03:30 | 2017-01-10 07:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-05-31 02:30 | 2015-05-31 03:20 | ONSHORE | OK | 74827 | Not Within a Municipality | HUGHES | MILEPOST | L-111A | L-111A | L-111A | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | EXPOSED DUE TO FLOODING OF RIVER |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.25 | 52000 | X52 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | STUPP CORPORATION | COAL TAR | [28 empty] | 1970 | 1970 | CARBON STEEL |  | LEAK |  |  | OTHER | CANNOT BE DETERMINED | [5 empty] | CLASS 1 LOCATION | NO |  | 342 |  | NO | NO | NO |  | 28707 | 31373.6062624917 | 0 | 0 | 9033 | 8078.80985915493 | 2753908 | 3009719.76434758 | 0 | 0 | 0 | 0 |  |  | 2791648 | 1404317.77094613 | 3049172.18046922 | [8 empty] | 450 |  | 960 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 89000 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL ROOM DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [52 empty] | HEAVY RAINS/FLOODS |  | WASHOUTS/SCOURING |  |  |  | YES |  |  |  | YES | PROLONGED PERIODS OF HEAVY RAIN CAUSED EXTREME RIVER FLOODING. THIS PIPELINE CROSSED THE RIVER AT THIS LOCATION. THE ACTUAL LOCATION OF THE DAMAGE WAS PREVIOUSLY COVERED BY SOIL BUT THE FLOODING WASHED THE SOIL AWAY. | [301 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | PROLONGED PERIODS OF RAIN CAUSED EXTREME FLOODING IN THE SOUTH CANADIAN RIVER WHERE THIS PIPELINE CROSSES THE RIVER. THE PIPELINE WAS UNDERGROUND. APPROXIMATELY 100 YARDS HORIZONTAL DISTANCE OF SOIL FROM THE ORIGINAL RIVER BED HAS BEEN WASHED AWAY EXPOSING THE PIPELINE. DUE TO CONSIDERABLE RAINFALL SINCE THE INCIDENT, THE PIPELINE IS STILL UNDER WATER SO NO ASSESSMENT OF DAMAGE HAS BEEN MADE. PLANS ARE TO ASSESS THE PIPELINE ONCE IT IS POSSIBLE AND PLAN THE REPAIRS ACCORDINGLY. A SUPPLEMENTAL REPORT WILL BE COMPLETED ONCE ALL INFORMATION IS KNOWN. SUPPLEMENTAL INFORMATION: WITH WATER LEVELS BACK TO THE NORMAL IN THE RIVER, THE PIPELINE STILL CANNOT BE SEEN VISUALLY. THE COMPANY HAS MADE A DECISION TO ABANDON THE PIPE LOCATED IN THE RIVER. THE PERMANENT SOLUTION WILL BE TO BORE THE RIVER AND LAY NEW PIPE. EXPECTED COMPLETION OF THIS PROJECT IS SCHEDULED FOR OCTOBER 2015. UPON COMPLETION, A FINAL REPORT WILL BE SENT IN WITH DAMAGE AND REPAIR COSTS. SUPPLEMENTAL INFORMATION: BORE CONSTRUCTION IS COMPLETE. THE NEW LINE WAS TIED ON 1/5/17 AND BACKFILLED ON 1/9/17. PIPELINE WAS PUT BACK IN SERVICE ON 1/10/17. THE SECTION OF PIPE WITH THE DEFECT WAS ABANDONED IN PLACE. WATER LEVELS IN THE SOUTH CANADIAN RIVER NEVER RECEDED ENOUGH FOR AN EXTERNAL EXAMINATION OF THE LEAK SITE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150087 | 32776 | 2015-06-25 19:12 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION LP (SPECTRA ENERGY CORP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2015-05-31 12:00 | 2015 |  |  | 34.7484 | -92.2427 | 1118293 | 2015-06-01 13:48 |  | NATURAL GAS |  | 3858 | 4383 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-06-01 12:25 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-06-01 12:25 | 2015-06-01 12:25 | ONSHORE | AR | 72117 | NORTH LITTLE ROCK | PULASKI | MILEPOST | 216.6 | TEXAS EASTERN TRANSMISSION, LP | 24-INCH AUXILIARY LINE 1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 |  | YES | [6 empty] | YES | UNCASED | ARKANSAS RIVER | 35 | BELOW WATER, PIPE BURIED BELOW BOTTOM (NOT IN BORED/DRILLED CROSSING) | [11 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 |  | 0.5 | 40000 | API -5LX | FLASH WELDED |  | AO SMITH | OTHER | COAL TAR WITH CONCRETE COVER | [27 empty] | 1952 | 1952 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 324 | 24 |  | CLASS 1 LOCATION | NO |  | 472 |  | NO | NO | NO |  | 10000 | 10928.9045398306 | 11834 | 12933.2656324355 | 10416 | 9315.71830985915 | 1000000 | 1092890.45398306 | 0 | 0 | 0 | 0 |  |  | 1032250 | 522276.95022098 | 1126068.34246518 | [8 empty] | 700 |  | 811 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 24288 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [52 empty] | HEAVY RAINS/FLOODS |  | WASHOUTS/SCOURING |  |  |  | YES |  |  |  | YES | VORTEX INDUCED VIBRATION | [301 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | deteschendorf@spectraenergy.com | 713-627-5573 |  |  |  |  | NATHAN ATANU | SUPERVISOR OPERATIONAL COMPLIANCE | 713-627-5008 | nyatanu@spectraenergy.com | AT APPROXIMATELY 12:25 PM CDT ON JUNE 1, 2015, SPECTRA ENERGY WAS NOTIFIED BY JEFFREY SAND COMPANY, WHICH IS LOCATED ON THE NORTH BANK OF THE ARKANSAS RIVER AT THE TEXAS EASTERN TRANSMISSION, LP NATURAL GAS PIPELINE CROSSING, THAT IT APPEARED CONCRETE ANCHORING MATERIAL FROM THE PIPELINE HAD DAMAGED ONE OF THEIR TUG BOATS. SPECTRA ENERGY PERSONNEL WERE IMMEDIATELY DISPATCHED TO THE ISOLATION VALVES ON BOTH SIDES OF THE RIVER TO TAKE PRESSURE MEASUREMENTS ON THE AUXILIARY LINE. THE AUXILIARY CROSSING WAS FOUND TO BE AT ATMOSPHERIC PRESSURE. THE AUXILIARY LINE HAD BEEN ISOLATED FROM THE MAINLINE FOR SOME TIME AND SHOULD HAVE HAD NATURAL GAS PRESSURE IN EXCESS OF 700 PSIG. SPECTRA ENERGY PERSONNEL OPENED THE ISOLATION VALVES ON THE AUXILIARY LINE AND IMMEDIATELY OBSERVED BUBBLING ABOUT 100 FEET FROM THE NORTH BANK OF THE RIVER, THUS CONFIRMING A PIPELINE FAILURE. UPON CONFIRMING THE FAILURE, TEXAS EASTERN NOTIFIED THE NATIONAL RESPONSE CENTER, PHMSA, AND THE ARKANSAS PUBLIC SERVICE COMMISSION. ANALYSIS CONCLUDED HIGH WATER FLOW RATES IN THE ARKANSAS RIVER ERODED THE COVER OVER THE PIPELINE AND LED TO SCOUR OF THE SOIL SUPPORT UNDER THE PIPELINE. ONCE THE PIPELINE WAS EXPOSED AS A FREE SPAN, VORTEX-INDUCED VIBRATION (VIV) CAUSED VERTICAL OSCILLATION OF THE PIPELINE, CREATING CYCLIC BENDING STRESSES. THIS RESULTED IN A CIRCUMFERENTIALLY ORIENTED FATIGUE CRACK THAT INITIATED ADJACENT TO THE TOE OF A GIRTH WELD, WHICH CAUSED THE FAILURE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150088 | 16797 | 2015-06-29 11:22 | ORIGINAL FINAL | 31470 | VECTREN ENERGY DELIVERY OF OHIO | 211 NW RIVERSIDE DRIVE | EVANSVILLE | IN | 47708 | 2015-05-13 01:14 | 2015 |  |  | 40.2205 | -84.2711 | 1118381 | 2015-06-02 10:42 |  | NATURAL GAS |  | 9229 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-05-13 05:02 | 2015-05-14 00:21 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-05-13 01:57 | 2015-05-13 02:58 | ONSHORE | OH | 45356 | Not Within a Municipality | SHELBY COUNTY | MILEPOST | Z-167-155 | Z-167 | TWIN WOODS | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | 4 INCH STEEL BLOW-DOWN VALVE STACK | 1953 |  | CARBON STEEL |  | OTHER | [8 empty] | VEHICLE SHEARED OFF STEEL BLOW DOWN VALVE STACK FROM ABOVE GROUND VALVE SETTING. | CLASS 1 LOCATION | NO |  | 176 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 28341 | 25347.2323943662 | 69630 | 76097.9623108404 | 12808 | 13997.740934615 | 0 | 0 |  |  | 110779 | 67634.9318904768 | 115442.935639822 | [8 empty] | 303 |  | 400 | 192.619(A)(4) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 23898 | NO |  | YES | YES | YES |  | YES | LACKING LAUNCHER/RECEIVER FACILITIES. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY DAMAGE WAS CAUSE OF INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [260 empty] | JOHN SPINKS | MANAGER GAS COMPLIANCE | jaspinks@vectren.com | 937-440-1844 | 937-440-1818 |  |  |  | JAMES FRANCIS | VICE PRESIDENT SAFETY AND SYSTEM INTEGRITY | 812-491-4369 | jmfrancis@vectren.com | A PASSENGER VEHICLE TRAVELING SOUTH ON PATTERSON HALPIN ROAD FAILED TO NEGOTIATE A CURVE AND LEFT THE ROADWAY TRAVELING APPROXIMATELY 200 FEET BEFORE DRIVING THROUGH A CHAIN-LINK FENCE ENCLOSURE AND STRIKING VECTREN'S ABOVE GROUND TRANSMISSION VALVE SETTING. THE VEHICLE DENTED THE 12 INCH PIPELINE AND SHEARED OFF THE 4 INCH VALVE BLOW DOWN STACK ATTACHED TO THE TOP OF IT RESULTING IN A RELEASE OF NATURAL GAS. VECTREN PERSONNEL ISOLATED THE DAMAGED SECTION OF PIPING, CLOSING THE VALVES UPSTREAM AND DOWNSTREAM OF THE SITE, ALLOWING THE RESIDUAL LINE PACK GAS TO VENT TO ATMOSPHERE. REMEDIATION INCLUDED REPLACING THE DENTED SECTION OF 12 INCH PIPELINE, REPLACING THE VALVE BLOW DOWN STACK, REPLACING THE DAMAGED SECTION OF CHAIN-LINK FENCE ENCLOSURE AND RESTORING THE SITE. AS CONTRACTOR REPAIR AND LABOR COSTS WERE ACCUMULATED, THE TOTAL AMOUNT EXCEEDING THE $50,000 IN DAMAGES REPORTING THRESHOLD WAS REALIZED 18 DAYS AFTER THE INCIDENT OCCURRED. THE VOLUME OF UNINTENTIONALLY RELEASED GAS WAS INVESTIGATED AND CALCULATED SOON AFTER THIS TIME FRAME AND VERIFIED IT MET THE REPORTING CRITERIA ALSO. THE INCIDENT WAS REPORTED TO THE APPROPRIATE REGULATORY CONTACTS ONCE THE REPAIR COSTS WERE SUBSTANTIATED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150089 | 16816 | 2015-06-29 11:25 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2015-06-10 12:15 | 2015 |  |  | 35.4602 | -100.9793 | 1119343 | 2015-06-10 14:14 |  | NATURAL GAS |  | 3648 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-06-10 12:38 | 2015-06-10 18:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-06-10 12:15 | 2015-06-10 12:20 | ONSHORE | TX | 79065 | Not Within a Municipality | GRAY | MILEPOST | MILEPOST 68 | LINE 3044 | MILEPOST 68 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1993 |  | CARBON STEEL |  | OTHER | [8 empty] | PIPELINE RELIEF VALVE PREMATURELY OPERATED BELOW MAOP; | CLASS 1 LOCATION | NO |  | 366 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 14595 | 13053.2746478873 | 800 | 874.312363186447 | 150 | 163.933568097459 | 0 | 0 |  |  | 15545 | 14009.5048136923 | 14091.5205791712 | [8 empty] | 845 |  | 867 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 1 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELIEF VALVE OPERATED PREMATURELY; NEARBY RESIDENT IMMEDIATELY CALLED EPNG STAFF; | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | DEBRIS MAY HAVE CAUSED PREMATURE OPERATION OF RELIEF VALVE | [161 empty] | WILLIAM MARTIN MULLER | SPECIALIST - PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205 325 3863 | 205 325 3508 |  |  |  | WILLIAM MARTIN MULLER | SPECIALIST - PIPELINE TECHNICAL | 205 325 3863 | martin_muller@kindermorgan.com | EPNG; LINE 3044; MILEPOST 68; PIPELINE 4X6 RELIEF VALVE PREMATURELY OPERATED; 12:15 (MOUNTAIN) TO 12:38 (MOUNTAIN); NEARBY RESIDENT CONTACTED EPNG STAFF; EPNG TECHNICIANS WERE IN THE AREA AND WERE DISPATCHED TO THE RELIEF VALVE SITE; EPNG TECHNICIANS CLOSED THE BLOCK VALVE BENEATH THE RELIEF VALVE HALTING THE RELEASE OF NATURAL GAS AT 12:38 (MOUNTAIN); SCADA DATA SHOWED 845 PSIG OPERATING PRESSURE WITH PRESSURE DECREASE TO 833 PSIG DURING THE RELEASE EVENT; MAOP IS 867 PSIG; EPNG TECHNICIANS INVESTIGATED RELIEF (BELIEVE DEBRIS OR TRASH MAY HAVE BEEN THE CAUSE OF PREMATURE RELIEF); RELIEF VALVE WAS RESET AND RETURNED TO SERVICE; PIPELINE SEGMENT WAS MANNED AND PRESSURE MANUALLY MONITORED WHILE RELIEF VALVE WAS NOT IN SERVICE; RELIEF VALVE RETURNED TO SERVICE 18:00 (MOUNTAIN);
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150090 | 16992 | 2015-06-29 17:46 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2015-06-09 12:23 | 2015 |  |  | 32.7357 | -91.8966 | 1119200 | 2015-06-09 14:23 |  | NATURAL GAS |  | 115 | 883 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-06-13 09:22 | 2015-06-17 13:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-06-09 12:23 | 2015-06-09 12:23 | ONSHORE | LA | 71220 | Not Within a Municipality | MOOREHOUSE PARISH | SURVEY STATION NO. | 48-2 | LINE 100-2 | MLV 48-2 TO MLV 49-2 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 35 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 26 |  | 0.281 | 52000 | API | FLASH WELDED |  | A O SMITH | COAL TAR | [9 empty] | PIPE GIRTH WELD | [18 empty] | 1948 | 1948 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 492 |  | NO | NO | NO |  | 0 | 0 | 2650 | 2896.15970305511 | 345 | 308.556338028169 | 65000 | 71037.8795088988 | 5400 | 5901.60845150852 | 0 | 0 |  |  | 73395 | 36966.5632536056 | 80144.2040014906 | [8 empty] | 674 |  | 750 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 48961 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CORROSION STAFF WERE ON PIPELINE ROW FOR OTHER WORK AND NOTICED SOME "BUBBLING" IN RAIN WATER; NOT ENOUGH GAS LEAK FOR SCADA NOR GAS CONTROL TO OBSERVE; | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [8 empty] | YES | PINHOLE IN FIELD GIRTH WELD, WELD PENETRATION | [19 empty] | YES | PINHOLE IN GIRTH WELD, WELD PENETRATION | [55 empty] | YES | [6 empty] | YES | [50 empty] | COMBINATION TOOL | 2015 |  |  |  |  | YES | 1966 | 1112 | NO | [13 empty] | NO | [63 empty] | WILLIAM MARTIN MULLER | SPECIALIST - PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205 325 3863 | 205 325 3508 |  |  |  | REJI GEORGE | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713 420 5433 | reji_george@kindermorgan.com | CORROSION EMPLOYEES WERE ON THE PIPELINE RIGHTS-OF-WAY FOR OTHER WORK; SAID EMPLOYEES NOTICED "BUBBLING" IN STANDING RAIN WATER OVER THE PIPELINE; AFTER PUMPING DOWN THE PIPELINE THEN BLOWING DOWN THE REMAINING 56 PSIG, THE PIPELINE WAS EXPOSED; A PINHOLE LEAK IN THE GIRTH WELD AT THE 6:00 POSITION WAS FOUND; DOUBLE PLATE WELD SLEEVE WAS INSTALLED TO REPAIR LEAK; EXPOSED PIPELINE WAS RECOATED AND COVERED; VALVE SECTION WAS RETURNED TO SERVICE ON 06/17/2015; REPORTABLE EVENT BY REPAIR COST;
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150091 | 16997 | 2015-07-09 15:21 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2015-06-09 21:30 | 2015 |  |  | 41.2638 | -76.4946 | 1119244 | 2015-06-09 22:41 |  | NATURAL GAS |  | 96379 | 16812 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-06-09 22:07 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 150 | 2015-06-09 21:30 | 2015-06-09 23:03 | ONSHORE | PA | 17814-7935 | BENTON | LYCOMING COUNTY | MILEPOST | MP 118.6 | LEIDY LINE B | 517LB10 TO 517LB0 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 43 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 |  | 0.344 | 1720 | 60000 | FLASH WELDED |  | AO SMITH | COAL TAR | [28 empty] | 1963 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 24 | 408 |  | CLASS 1 LOCATION | NO |  | 574 |  | NO | NO | NO |  | 0 | 0 | 47700 | 52130.8746549919 | 273454 | 244568.014084507 | 420000 | 459013.990672885 | 10000 | 10928.9045398306 | 0 | 0 |  |  | 751154 | 493200.401500721 | 766641.783952214 | [8 empty] | 1141 |  | 1200 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | REMOTELY CONTROLLED | 75504 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER ACTIONS DID NOT APPEAR TO CAUSE THE INCIDENT | [12 empty] | YES | 3 | 0 | YES | 3 | 0 | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED | YES | YES | [15 empty] | STRESS CORROSION CRACKING | [5 empty] | YES | [63 empty] | YES | YES |  |  | YES |  |  |  | 2010 | [31 empty] | 2010 | [23 empty] | YES | 1987 | 1555 | NO | [13 empty] | NO | [63 empty] | TROY STAHLE | PIPELINE SAFETY ENGINEER | troy.stahle@williams.com | 9183446359 |  |  |  |  | MARIE SOTAK | MANAGER PIPELINE SAFETY | 17132152111 | marie.sotak@williams.com | ON JUNE 9,2015 LEIDY B LINE RUPTURED BETWEEN MLV517LB0 AND MLV517LB10. AT APPROXIMATELY 9:30 GAS CONTROL RECIEVED A LOW LOW PRESSURE ALARM AND NOTIFIED LOCAL PERSONNEL. THE MAINLINE BLOCK VALVES WERE CLOSED TO ISOLATE THE SEGMENT. EMERGENCY RESPONDERS AND WILLIAMS PERSONNELL ISOLATED THE INCIDENT SITE AND NOTIFIED THE NRC.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150092 | 16889 | 2015-07-09 16:21 | SUPPLEMENTAL FINAL | 32335 | REGENCY INTRASTATE GAS LP | 800 E. SONTERRA BLVD | SAN ANTONIO | TX | 78258 | 2015-06-09 20:05 | 2015 |  |  | 32.5793 | -93.7357 | 1119243 | 2015-06-09 22:19 |  | NATURAL GAS |  | 4000 | 111.6 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-06-09 21:19 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-06-09 19:32 | 2015-06-09 20:05 | ONSHORE | LA | 71111 | SHREVEPORT | BOSSIER | MILEPOST | SEC 2/MLV 2 | RT05 NORTH ELM GROVE 12" | SWEPCO 12" | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | DREDGED RIVER CROSSING |  |  | YES | [6 empty] | YES | UNCASED | RED RIVER CROSSING | 40 | BELOW WATER, PIPE BURIED BELOW BOTTOM (NOT IN BORED/DRILLED CROSSING) | [11 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 |  | 0.219 | 52000 | X52 API 5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | OTHER | TGF 2- CONCRETED | [27 empty] | 1972 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 38 | 1 |  | CLASS 1 LOCATION | NO |  | 278 |  | NO | NO | NO |  | 0 | 0 | 300 | 327.867136194918 | 10000 | 8943.66197183099 | 700000 | 765023.317788141 | 0 | 0 | 0 | 0 |  |  | 710300 | 360588.689543434 | 774294.846896167 | [8 empty] | 619 |  | 893 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 4072 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE CAUSED BY NATURAL FORCE/FLOODING. SYSTEM WAS OPERATING WELL WITHIN ITS ESTABLISHED PRESSURE LIMITS AND THE CONTROLLER WAS ONLY MONITORING, NOT CHANGING, SET POINTS. | [12 empty] | YES | 1 | 0 | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [52 empty] | HEAVY RAINS/FLOODS |  | WASHOUTS/SCOURING |  |  |  | YES |  |  |  | YES | EXTENSIVE HEAVY RAINS | [301 empty] | BILL MEYER | MANAGER- INTRASTATE COMPLIANCE | bill.meyer@energytransfer.com | 7139896460 | 7139891188 |  |  |  | DANNY NICHOLS | DIRECTOR- REGULATORY COMPLIANCE | 7139897232 | danny.nichols@energytransfer.com | ON 6/9/15 AT APPROXIMATELY 7:30PM, ENERGY TRANSFER'S GAS CONTROL RECEIVED A CALL FROM THE STALL POWER PLANT OPERATOR SAYING THAT THEIR PRESSURE WAS DROPPING. GAS CONTROL BEGAN POLLING LINE PRESSURES AND CALLED THE ENERGY TRANSFER FIELD OPERATOR. THE ENERGY TRANSFER FIELD OPERATOR FOUND THE LEAK AT APPROXIMATELY 8:05PM. THE LEAK WAS IN THE RED RIVER AND SEVERE FLOODING HAD BEEN OCCURRING. SEVERAL OF THE ROADS WERE CLOSED DUE TO THE FLOODING. THE LINE WAS ISOLATED AT APPROXIMATELY 9:10PM. FINAL UPDATE: OCT. 16, 2015 PLANS ARE TO LEAVE DAMAGED SECTION OF PIPE IN PLACE TO MITIGATE ANY POSSIBLE EROSION TO RIVER BANK AND SUBSEQUENT LEVEE. ALSO TO BORE A NEW RIVER CROSSING AND TIE-IN EXISTING PIPELINE ON EITHER SIDE OF RIVER. ALL PLANS ARE BEING COORDINATED WITH LDNR, ARMY CORPS OF ENGINEER AND PARISH LEVEE BOARDS.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150093 | 16808 | 2015-07-10 14:17 | ORIGINAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2015-06-16 11:35 | 2015 |  |  | 34.9768 | -90.0331 | 1119966 | 2015-06-16 12:34 |  | NATURAL GAS |  | 3140 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELIEF VALVE WAS STUCK OPEN; LINE REMAINED IN SERVICE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-06-16 11:35 | 2015-06-16 12:15 | ONSHORE | MS | 38671 | SOUTHAVEN | DESOTO | MILEPOST | 239+4009 | MAIN LINE SYSTEM | MLS 26-1 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1994 |  | CARBON STEEL |  | OTHER | [8 empty] | FAILED PILOT ON RELIEF VALVE | CLASS 3 LOCATION | YES | METHOD2 | 462 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 8855 | 7919.61267605634 | 300 | 327.867136194918 | 500 | 546.445226991529 | 0 | 0 |  |  | 9655 | 8611.95451076434 | 8793.92503924279 | [8 empty] | 668 |  | 663 | 192.619(A)(1) |  |  |  | PRESSURE EXCEEDED MAOP, BUT DID NOT EXCEED THE APPLICABLE ALLOWANCE IN 192.201 | NO |  |  |  |  | AUTOMATIC | REMOTELY CONTROLLED | 1 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELEASE WAS INITIATED BY AREA PERSONNEL | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | PILOT FAILED TO RESET | [161 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 2706886357 |  |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 2706886361 | jeff.mcmaine@bwpmlp.com | PIPELINE WAS TEMPORARILY OVERPRESSURED (EXCEEDED MAOP BY .7%) WHILE ATTEMPTING TO MOVE A CLEANING PIG THAT WAS SLOWED OR STOPPED USING HIGH PRESSURE DISCHARGE GAS. THE RELIEF VALVE OPENED APPROPRIATELY; HOWEVER, THE PILOT ON THE RELIEF VALVE FAILED TO RESET CAUSING GAS TO VENT TO ATMOSPHERE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150094 | 16809 | 2015-07-13 13:15 | ORIGINAL FINAL | 38987 | KINETICA ENERGY EXPRESS LLC | 1001 MCKINNEY STREET, SUITE 900 | HOUSTON | TX | 77002 | 2015-06-15 18:00 | 2015 |  |  | 29.6599 | -92.7108 | 1119882 | 2015-06-15 18:45 |  | NATURAL GAS |  | 2 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-06-15 15:30 | 2015-07-12 16:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-06-15 13:30 | 2015-06-15 15:30 | ONSHORE | LA | 70643 | Not Within a Municipality | CAMERON | MILEPOST | 507A-1001 | 507A-1000 | ROLLOVER - EAST CAMERON LINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | IN SMALL POND WITH 2' OF WATER, IN MARSH | 96 |  | NO | [22 empty] | INTERSTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | PIPE | PIPE BODY | 12 |  | 0.312 | 42000 | API L5 | SEAMLESS |  | NATIONAL TUBE | COAL TAR | [28 empty] | 1960 | 1960 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 10 | 8.94366197183099 | 125000 | 136611.306747882 | 3000 | 3278.67136194918 | 0 | 0 |  |  | 128010 | 64222.4635063323 | 139898.921771803 | [8 empty] | 750 |  | 1160 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | RANGER AT ROCKEFELLER WILDLIFE REFUGE NOTICED VERY SMALL GAS BUBBLE |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE WAS OPERATING WELL BELOW MAOP / MOP AT THE TIME OF THE INCIDENT. VERY TINY GAS BUBBLES WERE IDENTIFIED IN A REMOTE POND IN THE MARSH. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  |  | YES | [5 empty] | YES | IN CONSULTATION WITH CORROSION CONSULTANT WHO HAS STUDIED OUR PIPELINE CONDITIONS AND IS ASSISTING WITH DEVELOPING OUR NEW CORROSION CONTROL PROGRAM. | YES | [5 empty] | YES | NO | YES | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | SUSIE RICHMOND | MANGER PIPELINE COMPLIANCE | susie.richmond@kineticallc.com | 985-223-6145 |  |  |  |  | SUSIE RICHMOND | MANGER PIPELINE COMPLIANCE | 985-223-6145 | susie.richmond@kineticallc.com | A FISH AND WILDLIFE RANGER AT THE ROCKEFELLER WILDLIFE REFUGE IDENTIFIED TINY GAS BUBBLES IN A POND LOCATED ON THE REFUGE IN CLOSE PROXIMITY TO MULTIPLE PIPELINES. AFTER BEING CONTACTED WE TRAVELED TO THE LOCATION TO VERIFY COORDINATES AND ON SCENE CONDITIONS. A SHUT IN OF PRODUCTION AT EAST CAMERON 33 CF WAS REQUESTED SO THAT PIPELINE CONDITIONS COULD BE MONITORED TO VERIFY SOURCE OF LEAK AT THE 507A-1000. AFTER PRODUCTION WAS SHUT IN AND THE LINE TOTALLY ISOLATED, WE WERE ABLE TO DETERMINE IT WAS THE KINETICA LINE. MOBILE COMPRESSION WAS BROUGHT TO THE LOCATION FOR THE PUMP DOWN OF THE PIPELINE. A REPAIR CLAMP WAS INSTALLED AND THE PIPELINE WAS REPRESSURIZED.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20150095 | 16857 | 2015-07-14 14:24 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2015-06-15 15:00 | 2015 |  |  | 28.9933 | -91.8724 | 1119867 | 2015-06-15 15:59 |  | NATURAL GAS |  | 4680 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-06-18 18:30 | 2015-08-01 05:50 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 2 | 2015-06-15 07:19 | 2015-06-18 09:30 | OFFSHORE | [28 empty] | 50 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SOUTH MARSH ISLAND | 288 | SPLASH ZONE OF RISER | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 8.625 |  | 0.5 | 35000 | 5L GRADE B | SEAMLESS |  | U.S. STEEL | COMPOSITE | [28 empty] | 1980 | 1978 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 199 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 13000 | 11626.7605633803 | 563000 | 615297.325592462 | 0 | 0 | 0 | 0 |  |  | 576000 | 294491.698804866 | 626924.086155843 | [8 empty] | 870 |  | 1300 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | MANUAL | 5492 | NO | YES |  |  | YES |  | YES | PIPELINE CONNECTS TO A SUBSEA 12" PIPELINE. | YES |  |  |  |  | YES | SUBSEA ASSEMBLY NOT SMART PIGABLE | OFFSHORE GATHERING | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CHEVRON PLATFORM OPERATORS IDENTIFIED THE LEAK AND SHUT IN FACILITIES. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  |  | YES | [7 empty] | YES |  |  |  | NO | [11 empty] | YES | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | NATHAN L. GRAY JR. | SENIOR PIPELINE COMPLIANCE SPECIALIST | ngray@eprod.com | 985 804 1376 |  |  |  |  | NATHAN L. GRAY JR. | SENIOR PIPELINE COMPLIANCE SPECIALIST | 985 804 1376 | ngray@eprod.com | CHEVRON PLATFORM OPERATORS DISCOVERED A PIN HOLE LEAK ON THE ENTERPRISE EXPORT PIPELINE RISER AT THE +6 FOOT ELEVATION LEVEL FROM THE GULF OF MEXICO WATER LINE JUST ABOVE A CLAMP SUPPORT. TOPSIDE VALVES AT SM 288 PLATFORM WERE CLOSED AND SUBSEA VALVES IN BLOCK SM 287 WERE CLOSED TO BLEED DOWN PIPELINE AND PIPELINE RISE TO ZERO PRESSURE. ENTERPRISE WAS NOT ABLE TO CLOSE SUBSEA VALVES IMMEDIATELY DUE TO TROPICAL STORM BILL AND WEATHER RELATED ISSUES. THE PLATFORM OPERATORS WERE EVACUATED UNTIL PIPELINE WAS ISOLATED. PIPELINE RISER REPAIR IS ON GOING WITH THE INSTALLATION A PRE-FABRICATED SECTION OF PIPELINE TESTED IN ACCORDANCE WITH 49 CFR 192 REGULATIONS. ONCE ALL WORK HAS BEEN COMPLETED, A 2 HOUR PRESSURE LEAK TEST OF THE PIPELINE AND PIPELINE RISER WILL BE PERFORMED. PIPELINE RISER REPAIRS WERE COMPLETED ON AUGUST 1, 2015.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150096 | 16858 | 2015-07-15 15:00 | SUPPLEMENTAL FINAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2015-06-15 16:41 | 2015 |  |  | 32.4343 | -94.4284 | 1120204 | 2015-06-18 13:56 |  | NATURAL GAS |  | 4390 | 18438 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-06-18 19:22 | 2015-07-02 11:06 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-06-18 19:22 | 2015-06-17 11:40 | ONSHORE | TX | 75672 | MARSHALL | HARRISON | SURVEY STATION NO. | 23209+22.8 | GULF COAST #3 MAINLINE | GULF COAST #3 MAINLINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 36 |  | 0.33 | 65000 | API 5L GRADE X65 | FLASH WELDED |  | AO SMITH CORPORATION | ASPHALT | [28 empty] | 1967 | 1967 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 768 |  | NO | NO | NO |  | 0 | 0 | 51753 | 56560.3596649853 | 12322 | 11020.3802816901 | 193863 | 211871.022080518 | 2617 | 2860.09431807367 | 0 | 0 |  |  | 260555 | 135955.274674474 | 282311.856345267 | [8 empty] | 659.1 |  | 858 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 77088 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | NOTIFICATION FROM OTHER PIPELINE OPERATOR (BP AMOCO) |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM PERSONNEL WERE NOT INVOLVED IN THE INITIAL IDENTIFICATION OF THE LEAK NOR WOULD THEY HAVE SEEN ANY CHANGES IN PRESSURES OR OTHER INDICATORS BASED ON THE ESTIMATED SIZE OF THE LEAK. THE EVENT QUALIFIED AS A REPORTABLE INCIDENT BASED ON REPAIR COSTS. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [146 empty] | KRISTIN VAN DER LAAN | COMPLIANCE ENGINEER III | kristin_vanderlaan@kindermorgan.com | 303-914-7753 |  |  |  |  | REJI GEORGE | DIRECTOR - COMPLIANCE-CODES AND STANDARDS | 713-420-5433 | reji_george@kindermorgan.com | JUNE 17, 2015: BP AMOCO CALLED NATURAL GAS PIPELINE COMPANY OF AMERICA (NGPL) TO REPORT A HISSING SOUND IN THE VICINITY OF NGPL ROW. LOCAL NGPL OPERATIONS PERSONNEL SECURED THE AREA AND NOTIFIED NGPL GAS CONTROL AND OPERATIONS MANAGEMENT OF A POSSIBLE LEAK. THE AREA WAS UNDER 2 TO 3-FEET OF WATER THEREFORE THE SYSTEM WAS SHUT-IN TO ATTEMPT TO VERIFY WHETHER OR NOT IT WAS AN NGPL LEAK. TO FURTHER IDENTIFY THE PIPELINE ASSOCIATED WITH THE LEAK, LOCAL NGPL OPERATIONS PERSONNEL ALSO ISSUED AN EMERGENCY ONE CALL TO PROMPT IMMEDIATE RESPONSE FROM OTHER PIPELINE OPERATORS IN THE AREA. JUNE 18, 2015: THE PRESSURES HAD NOT DROPPED AND THE LEAK WAS STILL UNCONFIRMED AT 12:48. A DETERMINATION WAS MADE TO REPORT TO THE NRC IN THE EVENT THAT IT WAS VERIFIED AS AN NGPL NATURAL GAS LEAK. OPERATIONS MANAGEMENT INSTRUCTED THE LOCAL OPERATIONS TO BLOWDOWN THE PIPELINE SECTION. BUBBLES STOPPED AFTER BLOWDOWN WAS COMPLETE. THE LEAK WAS CONFIRMED AS NGPL'S AT 19:22. AUGUST 12, 2015: METALLURGICAL REPORT COMPLETED. THE LEAK WAS LOCATED AT THE 10:56 CIRCUMFERENTIAL POSITION ADJACENT TO THE ELECTRIC FLASH WELD SEAM. CORROSION, LIGHTNING STRIKE, AND THIRD-PARTY DAMAGE DETERMINED UNLIKELY BASED ON FINDINGS. NO EVIDENCE OF STRESS CORROSION CRACKING. THE LEAK AREA WAS ERODED SUCH THAT THERE WAS NO CONCLUSIVE EVIDENCE OF A ROOT CAUSE. NOTE THAT THE INCIDENT TIME (PART A. 4) HAS BEEN ESTIMATED BASED ON THE CONDITION OF THE LEAK AREA.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150097 | 16870 | 2015-07-15 15:08 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2015-06-18 14:15 | 2015 |  |  | 28.6663 | -96.9922 | 1120230 | 2015-06-18 16:06 |  | NATURAL GAS |  | 1 | 8830 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-06-18 20:42 | 2015-08-14 23:40 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-06-18 14:15 | 2015-06-18 14:15 | ONSHORE | TX | 77905 | VICTORIA | VICTORIA | SURVEY STATION NO. | 49978.2 | LINE 100-1 PIPELINE | 8-1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 50 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 |  | 0.25 | 50000 | API 5L X50 | FLASH WELDED |  | AO SMITH CORPORATION | COAL TAR | [28 empty] | 1944 | 1944 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 454 |  | NO | NO | NO |  | 0 | 0 | 24724 | 27020.6235842771 | 3 | 2.6830985915493 | 133620 | 146032.022461216 | 999 | 1091.79756352908 | 0 | 0 |  |  | 159346 | 79939.676426983 | 174147.126707614 | [8 empty] | 665 |  | 750 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 69168 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | BUBBLING DISCOVERED DURING AERIAL PATROL. CONTROL ROOM PERSONNEL WERE NOT INVOLVED IN THE INITIAL IDENTIFICATION OF THE LEAK NOR WOULD THEY HAVE SEEN ANY CHANGES IN PRESSURES BASED ON THE SIZE OF THE LEAK. THE EVENT QUALIFIED AS A REPORTABLE INCIDENT BASED ON REPAIR COSTS. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [9 empty] | YES |  |  | YES | YES | 1944 | YES | YES | YES | YES |  |  | 2014 | 2013 |  |  | NO | [190 empty] | YES | YES |  |  | YES |  |  |  | 2004 | [31 empty] | 2015 | [23 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KRISTIN VAN DER LAAN | COMPLIANCE ENGINEER III | kristin_vanderlaan@kindermorgan.com | 303-914-7753 |  |  |  |  | REJI GEORGE | DIRECTOR - COMPLIANCE-CODES AND STANDARDS | 713-420-5433 | reji_george@kindermorgan.com | ON JUNE 18, 2015, THE TENNESSEE GAS PIPELINE DAMAGE PREVENTION SUPERVISOR RECEIVED A CALL FROM THE AERIAL PATROLLER REPORTING BUBBLING IN THE TGP RIGHT-OF-WAY. THE AREA, AT THE TIME OF DISCOVERY WAS INACCESSIBLE DUE TO FLOODING FROM THE GUADALUPE RIVER. THE LEAK WAS CONFIRMED BY ISOLATION AND MONITORING. THE INCIDENT WAS DETERMINED TO BE A PHMSA REPORTABLE INCIDENT BASED ON ESTIMATED COST OF REPAIRS. THE METALLURGICAL REPORT CONCLUDED THAT THE TGP LINE 100-1 LEAKED DUE TO EXTERNAL PITTING CORROSION IN THE BOTTOM QUARTER OF THE PIPE AT STATION 49978.2 BETWEEN MLV 8-1 AND MLV 9-1 IN VICTORIA COUNTY, TEXAS. THE BOTTOM QUARTER OF THE PIPE JOINT THAT LEAKED EXHIBITED DISBONDED COAL TAR ENAMEL COATING WITH EXPOSED STEEL IN SOME AREAS.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20150098 | 16813 | 2015-07-16 13:17 | ORIGINAL | 9171 | MARKWEST JAVELINA PIPELINE COMPANY, LLC | 1515 ARAPAHOE STREET, TOWER 1, SUITE 1600 | DENVER | CO | 80202 | 2015-03-16 10:45 | 2015 |  |  | 27.806 | -97.4838 | 1110874 | 2015-03-16 16:08 |  | OTHER GAS | PLANT INLET GAS | 5 | 20 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-03-16 13:00 | 2015-04-24 14:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 10 | 2015-03-16 10:45 | 2015-03-16 11:00 | ONSHORE | TX | 78410 | CORPUS CHRISTI | NUECES | MILEPOST | 0.75 MILE | PLANT INLET GAS PIPELINE SYSTEM | RG-210 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | BORE | 600 |  | YES |  |  |  |  | YES | BORED/DRILLED | [16 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.25 | 35000 | API 5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | AMERICAN STEEL PIPE | EPOXY | [28 empty] | 1990 | 1990 | CARBON STEEL |  | LEAK |  |  | OTHER | UNKNOWN | [5 empty] | CLASS 3 LOCATION | NO |  | 137 |  | NO | NO | NO |  | 0 | 0 | 75 | 81.9667840487294 | 19 | 16.9929577464789 | 1500000 | 1639335.68097459 | 0 | 0 | 0 | 0 |  |  | 1500094 | 752553.576731319 | 1639434.64071638 | [8 empty] | 50 |  | 99 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | MANUAL | 5650 | YES | [7 empty] | NO | [6 empty] | TYPE B GATHERING | YES | YES | YES | NO | NO | OTHER | NOTIFICATON PROVIDED BY EMERGENCY RESPONDERS |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WAS NO INDICATION THAT ACTIONS OF THE CONTROLLER(S) OR THE CONTROL ROOM WERE THE CAUSE OF, OR A CONTRIBUTING FACTOR TO, THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [146 empty] | MATT CARNES | SR. PIPELINE INTEGRITY ENGINEER | mcarnes@markwest.com | 303-925-9219 | 303-573-4954 |  |  |  | MATT CARNES | SR. PIPELINE INTEGRITY ENGINEER | 303-925-9219 | mcarnes@markwest.com | THE RG-210 20" PLANT INLET GAS PIPELINE EXPERIENCED A LEAK IN A BORED ROAD CROSSING. LOCAL EMERGENCY RESPONDERS NOTIFIED MARKWEST JAVELINA PERSONNEL AND APPROXIMATELY 10 PEOPLE WERE EVACUATED FROM A LOCAL BUSINESS. THERE WERE NO INJURIES SUSTAINED. THE PIPE SECTION WAS ISOLATED AND DE-PRESSURED TO A FLARE. THE BORED CROSSING WAS REPLACED AND THE LINE WAS RE-COMMISSIONED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150099 | 16861 | 2015-07-20 13:08 | SUPPLEMENTAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2015-06-24 00:15 | 2015 |  |  | 32.2107 | -85.0011 | 1120755 | 2015-06-24 03:25 |  | NATURAL GAS |  | 6805 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | VENT VALVE RELEASE DID NOT SHUT DOWN UNIT. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-06-24 00:15 | 2015-06-24 01:25 | ONSHORE | AL | 36859 | HOLY TRINITY | RUSSELL | MILEPOST | LINE-01 MP 27 | HOLY TRINITY COMPRESSOR STATION | HOLY TRINITY COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | VENT VALVE | 1977 |  | CARBON STEEL |  | OTHER | [8 empty] | VENT VALVE RELEASE | CLASS 1 LOCATION | NO |  | 368 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 8782 | 7854.32394366197 | 0 | 0 | 0 | 0 | 55 | 60.1089749690682 | BRACKET FOR VENT VALVE OPERATOR |  | 8837 | 8170.52587789674 | 7914.43291863104 | [8 empty] | 731 |  | 1110 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLERS DID NOT CONTRIBUTE TO THE INCIDENT | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | VENT VALVE RELEASE | YES |  | YES | [175 empty] | ZACHARY RAGAIN | ENGINEER-PIPELINE | zachary_ragain@kindermorgan.com | 713-420-6633 |  |  |  |  | ZACHARY RAGAIN | ENGINEER-PIPELINE | 713-420-6633 | zachary_ragain@kindermorgan.com | THE VENT VALVE ON HOLY TRINITY COMPRESSOR STATION UNIT #2 IS CONTROLLED BY A BETTIS PNEUMATIC OPERATOR WITH AIR SUPPLY TO OPERATE. BROKEN BOLTS ON THE BRACKET HOLDING THE CONTACT HOUSING TO THE OPERATOR CAUSED THE CONTACT HOUSING TO FALL TO THE GROUND AND DAMAGE THE AIR SUPPLY LINE FOR THE PNEUMATIC OPERATOR. THE VENT VALVE IS SPRING-LOADED TO DEFAULT TO THE OPEN POSITION, AND IT'S HELD CLOSED BY THE PNEUMATIC OPERATOR. WHEN THE PNEUMATIC OPERATOR LOST AIR SUPPLY PRESSURE, DUE TO THE CONTACT HOUSING FALLING AND DAMAGING THE AIR LINE, THE VENT VALVE "FAILED OPEN". THE BOLTS HAVE BEEN REPLACED AND THE BRACKET HAS BEEN REPAIRED. OPERATIONS IS WORKING WITH A MACHINE SHOP TO BUILD A STRONGER BRACKET AND A PIPE SUPPORT TO STABILIZE THE OPERATOR. THESE PIECES WILL BE INSTALLED ON BOTH UNITS AT HOLY TRINITY COMPRESSOR STATION IN AN EFFORT TO PREVENT THIS INCIDENT FROM REOCCURRING.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150100 | 17112 | 2015-07-29 12:50 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2015-06-29 02:50 | 2015 |  |  | 43.8639 | -85.5269 | 1121281 | 2015-06-29 03:56 |  | NATURAL GAS |  | 16012 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-06-29 02:50 | 2016-04-15 14:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-06-29 02:50 | 2015-06-29 03:30 | ONSHORE | MI | 49677 | Not Within a Municipality | OSCEOLA | MILEPOST | MP 3.8 | 8250 LINE | SEGMENT 2 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 |  | 0.25 | 52000 | API-5LX-X52 | FLASH WELDED |  | A. O. SMITH | OTHER | WAX | [27 empty] | 1950 | 1950 | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | ORIENTATION WAS BOTH LONGITUDINAL (APPROXIMATELY 310 INCHES) AND CIRCUMFERENTIAL (APPROXIMATELY 75.4 INCHES) | 310 | 75.4 |  | CLASS 1 LOCATION | NO |  | 482 |  | NO | NO | NO |  | 50000 | 54644.5226991529 | 0 | 0 | 44600 | 39888.7323943662 | 3684600 | 4026864.16674598 | 128200 | 140108.556200628 | 0 | 0 |  |  | 3907400 | 1979188.17095332 | 4261505.97804013 | [8 empty] | 634 |  | 650 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | MANUAL | 53380 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 3 | 0 | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED |  | YES | [15 empty] | STRESS CORROSION CRACKING | [5 empty] | YES | [63 empty] | YES | YES |  |  | YES |  |  |  | 2012 | [31 empty] | 2012 | [23 empty] | YES | 1969 | 1079 | NO | [13 empty] | NO | [63 empty] | ROBERT CADORIN | REGULATORY COMPLIANCE SPECIALIST | robert_cadorin@transcanada.com | 248-205-7669 | 248-205-5369 |  |  |  | ROBERT CADORIN | REGULATORY COMPLIANCE SPECIALIST | 248-205-7669 | robert_cadorin@transcanada.com | ON JUNE 29TH, 2015, AT 2:50 AM EDT FAILURE OCCURRED AT APPROXIMATE MP 3.8 ON ANR PIPELINE COMPANY'S 8250 LINE PIPELINE NEAR REED CITY, MICHIGAN. THE PIPELINE, WHICH HAS AN MAOP OF 650 PSIG, IS 24-INCHES OD, X52 GRADE, WITH A NOMINAL WALL THICKNESS OF 0.250 INCHES. THE ELECTRONIC FLASH WELDED PIPE WAS MANUFACTURED BY AO SMITH AND INSTALLED IN 1950. FLOW IN THE PIPELINE IS SEASONALLY BI-DIRECTIONAL AND WAS STATIC AT A PRESSURE OF 634 PSI (58% SMYS BASED ON NOMINAL PROPERTIES) AT THE TIME OF THE FAILURE. GAS RELEASED FROM THE FAILURE LOCATION DID NOT IGNITE. THERE WERE NO INJURIES, FATALITIES OR DAMAGE TO SURROUNDING STRUCTURES OR THE ENVIRONMENT. INVESTIGATIONS SUBSEQUENT TO THE INCIDENT REVEALED THAT A FAILURE OF THE WAX-TYPE COATING APPLIED DURING ORIGINAL CONSTRUCTION CONTRIBUTED TO THE EVENTUAL FORMATION OF TRANSGRANULAR STRESS CORROSION CRACKING (SCC), ALSO KNOW AS NEAR NEUTRAL PH SCC, IN THE PIPE, WHICH ULTIMATELY RESULTED IN THE PIPELINE FAILURE. THUS, THE DIRECT CAUSE OF THE FAILURE WAS THE NEAR NEUTRAL PH SCC, AS DOCUMENTED BY A THIRD-PARTY METALLURGICAL ANALYSIS. AND THE ROOT CAUSE OF THE SCC ON THE RUPTURED PIPE WAS ATTRIBUTED TO THE COATING THAT FAILED TO PERFORM ITS INTENDED PURPOSE OF ELIMINATING THE ENVIRONMENTAL COMPONENT REQUIRED FOR TRANSGRANULAR SCC TO INITIATE AND PROPAGATE. CONCURRENT TO THE ROOT CAUSE FAILURE INVESTIGATION, WHICH INCLUDED A REVIEW OF THE RESPONSE OF OPERATIONS AND GAS CONTROL PERSONNEL DURING THE EVENT, REPAIRS WERE MADE TO THE 8250 LINE, INCLUDING SUBSEQUENT MULTIPLE PRESSURE TESTS TO ASSURE PIPELINE FACILITY INTEGRITY AND SAFETY.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150101 | 16829 | 2015-07-31 12:41 | SUPPLEMENTAL FINAL | 31978 | ATMOS PIPELINE - TEXAS | 5420 LBJ FREEWAY, SUITE 1800 | DALLAS | TX | 75240 | 2015-07-02 21:45 | 2015 |  |  | 30.628 | -96.5435 | 1121735 | 2015-07-03 04:48 |  | NATURAL GAS |  | 3700 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-07-03 03:10 | 2015-07-17 11:38 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-07-02 21:45 | 2015-07-02 23:00 | ONSHORE | TX | 77807 | BRYAN | BRAZOS | MILEPOST | 61336 | L8-9 | L8-9 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | UNDER WATER | 276 |  | YES | [6 empty] | YES | UNCASED | BRAZOS RIVER | 23 | BELOW WATER, PIPE ON OR ABOVE BOTTOM | [11 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6.625 |  | 0.28 | 35000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1984 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | RUPTURE SIZE IS UNKNOWN; PIPE WAS LEFT IN PLACE ON RIVER BOTTOM AND WILL NOT BE EXAMINED. | 6 | 6 |  | CLASS 1 LOCATION | NO |  | 92 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 150000 | 134154.929577465 | 950000 | 1038245.93128391 | 0 | 0 | 0 | 0 |  |  | 1100000 | 615666.785523266 | 1172400.86086137 | [8 empty] | 315 |  | 400 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | YES | NO | NOT MANDATED |  |  | MANUAL | MANUAL | 21120 | NO | YES | [6 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLERS RECEIVED ALARMS AND RESPONDED TO OPERATIONS FIELD PERSONNEL. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [146 empty] | DARYL TALLEY | OPERATIONS SUPERVISOR | daryl.talley@atmosenergy.com | 979-774-2502 | 979-774-2521 |  |  |  | L. A. TREADWAY | COMPLIANCE DIRECTOR | 214-206-2044 | andy.treadway@atmosenergy.com | MIC TECH RECEIVED A CALL FROM THE COMPANY GAS CONTROL NOTIFYING US OF PRESSURE PROBLEMS ON JULY 2, 2015. AFTER FURTHER INVESTIGATION IT WAS DETERMINED THAT DURING NORMAL OPERATIONS THE PIPELINE L8-9 AS IT CROSSES THE BRAZOS RIVER ON HWY 21 HAD DEVELOPED A LEAK. THE LINE WAS SHUT IN TO ELIMINATE THE LEAK AND ACTIONS TO CORRECT THE PROBLEM WERE STARTED IMMEDIATELY. A NEW LINE WAS BORED UNDERNEATH THE RIVER AND WAS PLACED IN SERVICE ON JULY 17, 2015. THE EXISTING LINE WAS ABANDONED AND LEFT IN PLACE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150102 | 16834 | 2015-08-12 16:42 | ORIGINAL FINAL | 2564 | COLORADO INTERSTATE GAS CO | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2015-07-18 17:22 | 2015 |  |  | 39.6085 | -104.3501 | 1123182 | 2015-07-18 19:07 |  | NATURAL GAS |  | 3600 | 500 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-07-18 17:46 | 2015-07-22 14:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-07-18 17:24 | 2015-07-18 17:46 | ONSHORE | CO | 80103 | BYERS | ARAPAHOE | MILEPOST | 1 | LATIGO STORAGE | YARD PIPING | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | OTHER | [37 empty] | ESD VENT VALVE | 1978 |  | CARBON STEEL |  | OTHER | [8 empty] | RELEASE THROUGH 6" VENT VALVE OUTLET PIPE. | CLASS 1 LOCATION | NO |  | 207 |  | NO | NO | NO |  | 0 | 0 | 1375 | 1502.72437422671 | 9900 | 8854.22535211268 | 2500 | 2732.22613495765 | 1500 | 1639.33568097459 | 0 | 0 |  |  | 15275 | 11876.0298298787 | 14728.5115422716 | [8 empty] | 1520 |  | 2130 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL ROOM WAS NOT INVOLVED IN ANY WAY. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | INSTRUMENT AIR DRYER FAILED ALLOWING WATER TO GET INTO THE ESD SYSTEM | [15 empty] | YES | SOLENOID VALVE ON TOWER SWITCH VALVE FAILED. | [161 empty] | KENNETH C PETERS | SR. ENGINEER | ken_peters@kindermorgan.com | 2053257554 | 2053253508 |  |  |  | REJI GEORGE | DIRECTOR CODES STANDARDS | 7134205433 | reji_george@kindermorgan.com | A SOLENOID VALVE ON THE TOWER SWITCH VALVE FAILED, RENDERING THE AIR DRYER INOPERABLE. THIS ALLOWED WATER TO ENTER THE ESD SYSTEM CAUSING THE ESD VENT VALVE TO ACTIVATE (THE WATER INTERFERED WITH THE ESD'S PNEUMATIC OPERATION). GAS WAS RELEASED THROUGH A 6" VENT STACK INTO THE ATMOSPHERE. A VOLUME GREATER THAN THE REPORTING THRESHOLD OF 3,000 MCF WAS RELEASED RESULTING IN THE INCIDENT REPORT TO THE NRC. THE INSTRUMENT AIR DRYER HAS BEEN REPAIRED AND THE FACILITY WAS SUCCESSFULLY PLACED BACK INTO SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150103 | 17027 | 2015-08-16 15:08 | SUPPLEMENTAL FINAL | 32513 | AMEREN ILLINOIS COMPANY | 10 EXECUTIVE DR. | COLLINSVILLE | IL | 62234 | 2015-07-17 14:40 | 2015 |  |  | 38.8114 | -89.942 | 1123102 | 2015-07-17 16:47 |  | NATURAL GAS |  | 9180 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-07-17 20:24 | 2015-07-18 09:20 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-07-17 14:49 | 2015-07-17 15:30 | ONSHORE | IL | 62025 | EDWARDSVILLE | MADISON | MILEPOST | SEE PART A, 5 | EDWARDSVILLE 8 IN TRANSMISSION MAIN | FID 6149084 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 |  | 0.25 | 42000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | NEWPORT / L.B. FOSTER | EPOXY | [28 empty] | 1996 | 1996 | CARBON STEEL |  | MECHANICAL PUNCTURE | 6 | 2 | [7 empty] | CLASS 3 LOCATION | NO |  | 176 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 40254 | 36001.8169014084 | 55198 | 60325.3672789569 | 8640 | 9442.57352241363 | 0 | 0 |  |  | 104092 | 69350.0440926706 | 105769.757702779 | [8 empty] | 377.7 |  | 720 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 37342 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE WAS CAUSED BY THIRD PARTY EXCAVATOR. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  | YES | PRIVATE EASEMENT | [7 empty] | CONTRACTOR | GRADER/SCRAPER | GRADING | NO | [5 empty] | YES | 18 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | JOHN BOZARTH | MANAGER GAS COMPLIANCE AND TRAINING | jbozarth@ameren.com | 217-625-6854 | 314-613-2640 |  |  |  | JOHN BOZARTH | MANAGER GAS COMPLIANCE AND TRAINING | 217-625-6854 | jbozarth@ameren.com | AN 8" GAS TRANSMISSION MAIN SERVING DISTRIBUTION CUSTOMERS IN AND AROUND THE VICINITY OF EDWARDSVILLE, IL WAS DAMAGED BY A THIRD PARTY EXCAVATOR. THE EXCAVATOR MIKE MAEDGE TRUCKING, AN EARTHMOVING CONTRACTOR, WAS USING A JOHN DEERE 750J CRAWLER DOZER TO IMPROVE A HAUL ROAD FOR THE RICHARDS BRICK COMPANY. THE EXCAVATOR DID NOT REQUEST A DIG TICKET FROM JULIE, THE ONE CALL AGENCY IN ILLINOIS. THE EXCAVATOR REMOVED APPROXIMATELY 2 TO 3 FEET OF COVER, CREATING A GOUGE IN THE PIPELINE APPROXIMATELY 6" LONG BY 2" CIRCUMFERENTIALLY. THE LOCATION OF THE DAMAGE WAS IN A WOODED AREA ON AND ADJACENT TO THE RICHARDS BRICK COMPANY PROPERTY. GAS ESCAPED TO ATMOSPHERE AND DID NOT IGNITE. AMEREN ILLINOIS GAS CONTROL RECEIVED LOW PRESSURE ALARMS TO NEARBY REGULATOR STATIONS BEING FED FROM THIS 8" MAIN AND DISPATCHED GAS REGULATOR TECHNICIANS TO THESE LOCATIONS. ADDITIONAL GAS FIELD PERSONNEL WERE DISPATCHED AND CONFIRMED THE PIPELINE HIT HAD OCCURRED. AMEREN ILLINOIS SAFELY ISOLATED AND REPAIRED THE DAMAGED PIPELINE SEGMENT, MINIMIZING THE SCOPE OF THE OUTAGE WHICH ULTIMATELY IMPACTED AROUND 30 CUSTOMERS. UPDATE 01/29/2016 FOR FINAL SUBMISSION: GPS DATA WAS VERIFIED COST INFORMATION WAS UPDATED BASED ON FINAL COST ESTIMATE WHICH IS SPLIT INTO EMERGENCY RESPONSE AND DAMAGE REPAIR. ADDITIONAL DETAIL ON OUTAGE - TOTAL NUMBER OF CUSTOMERS IMPACTED WERE 32. SERVICE RESTORATION BEGAN ON SATURDAY JULY 18 AT 7:00 AM AND WAS COMPLETED BY 12:00 NOON ON SATURDAY JULY 18, FOR ALL CUSTOMERS EXCEPT 4 WHO WERE NOT HOME TO ALLOW ACCESS FOR RELIGHTS AT THIS TIME. THE EXCAVATOR STATED THAT SINCE THEY WERE GRADING DIRT, THAT THIS WAS NOT EXCAVATING AND THEREFORE DID NOT BELIEVED THEY NEEDED TO CONTACT THE ONE CALL CENTER FOR LOCATES. UPDATE 02/29/2016 FOR FINAL SUBMISSION: INITIAL TIME THAT THE INCIDENT ACTUALLY OCCURRED WAS UPDATED TO 14:40 PM, IN PART A, #4.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150104 | 17120 | 2015-08-22 15:55 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION LP (SPECTRA ENERGY CORP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2015-07-28 14:53 | 2015 |  |  | 28.5317 | -93.1728 | 1124120 | 2015-07-28 16:25 |  | NATURAL GAS |  | 2111 | 5505 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-07-29 09:00 | 2015-08-04 19:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-07-28 14:53 | 2015-08-28 14:53 | OFFSHORE | [28 empty] | 100 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST CAMERON | 480 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 |  | 0.438 | 42000 | API 5LX | SEAMLESS |  | US STEEL | OTHER | CONCRETE AND SOMASTIC | [27 empty] | 1976 | 1976 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 419 |  | NO | NO | NO |  | 0 | 0 | 16515 | 18049.0858475302 | 6333 | 5664.02112676056 | 111400 | 121747.996573713 | 0 | 0 | 0 | 0 |  |  | 134248 | 70042.6975209016 | 145461.103548004 | [8 empty] | 898 |  | 1440 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 62917 | YES | [7 empty] | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS TOO SMALL TO BE IDENTIFIED BY THE CONTROLL ROOM PERSONNEL. A REVIEW OF OPERATING RECORDS FOUND ABNORMAL OPERATING CONDITIONS DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | deteschendorf@spectraenergy.com | 713-627-5573 |  |  |  |  | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 713-627-5008 | nyatanu@spectraenergy.com | BUBBLES ON THE SURFACE OF THE WATER IN THE GULF OF MEXICO AT WEST CAMERON BLOCK 480 WERE OBSERVED BY A SPECTRA ENERGY (TEXAS EASTERN) EMPLOYEE ON JULY 28, 2015 WHILE FLYING IN A HELICOPTER. THE PIPELINE SEGMENT SHUT IN WAS COMPLETED JULY 29, 2015. A DIVE BOAT WAS DISPATCHED TO THE LOCATION WHERE THE BUBBLES WERE OBSERVED. DIVERS CONFIRMED THE LEAK WAS COMING FROM A PIN HOLE LEAK DUE TO INTERNAL CORROSION IN TEXAS EASTERN 16-INCH LINE 41-A-8. A LEAK CLAMP WAS INSTALLED AND THE PIPELINE WAS RETURNED TO SERVICE AUGUST 4, 2015.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150105 | 17595 | 2015-08-23 11:15 | SUPPLEMENTAL FINAL | 2620 | COLUMBIA GULF TRANSMISSION, LLC | 700 LOUISIANA ST. SUITE 700 | HOUSTON | TX | 77002 | 2015-07-26 17:15 | 2015 |  |  | 30.053 | -92.6901 | 1123892 | 2015-07-26 18:59 |  | NATURAL GAS |  | 1613 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-07-26 19:10 |  | YES |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2015-07-26 17:15 | 2015-07-26 17:41 | ONSHORE | LA | 70549 | LAKE ARTHUR | JEFFERSON DAVIS PARRISH | SURVEY STATION NO. | MS-704 | ADOBE LINE MEASURING STATION 704 | MS-704 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | METER | [38 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | FIRE CAUSED BY A LIGHTNING STRIKE ON THE LOCAL PRODUCER'S TANK BATTERY, LOCATED ADJACENT TO COLUMBIA'S MEASUREMENT FACILITY. | CLASS 1 LOCATION | NO |  | 42 |  | NO | NO | NO |  | 73000 | 79781.0031407633 | 0 | 0 | 4420 | 3953.0985915493 | 1100000 | 1202179.49938136 | 0 | 0 | 0 | 0 | NO OTHER ASSOCIATED COSTS |  | 1177420 | 592552.054342489 | 1285913.60111368 | [8 empty] | 819 |  | 1050 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS INITIATED BY AN OUTSIDE FACTOR NOT RELATED TO ANY SCADA-RELATED COMPONENTS OR ANY COMPANY PERSONNEL | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [103 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [261 empty] | CODY BOWERS | SPECIALIST | cody_bowers@transcanada.com | (304)357-2814 |  |  |  |  | LEE ROMACK | MANAGER - US REGULATORY COMPLIANCE | (832)320-5315 | lee_romack@transcanada.com | ON SUNDAY, JULY 26, 2015, COLUMBIA GULF TRANSMISSION, LLC (COLUMBIA) MEASUREMENT FACILITY AT MS-704 JOB LAKE ARTHUR WAS SUBJECT TO A FIRE FROM AN ADJACENT LIQUID HYDROCARBON STORAGE TANK BATTERY OWNED BY A LOCAL PRODUCER. THE FIRE WAS CAUSED BY A LIGHTNING STRIKE ON THE PRODUCER'S TANK BATTERY, LOCATED ADJACENT TO COLUMBIA'S MEASUREMENT FACILITY. DURING THE INCIDENT, A COLUMBIA RELIEF VALVE (RV) MALFUNCTIONED DUE TO EXPOSURE TO EXTREME HEAT AND INADVERTENTLY RELEASED NATURAL GAS AND THE GAS EXHAUST SUBSEQUENTLY CAUGHT FIRE. THE COLUMBIA MEASUREMENT FACILITY WAS ISOLATED AND BLOWN DOWN TO ATMOSPHERE. COLUMBIA'S ABOVE GROUND FACILITY AT THE METER SITE WAS EXPOSED TO EXTREME HEAT AND IS NO LONGER SERVICEABLE. THE METER STATION AND ASSOCIATED PIPELINE REMAIN BLOWN DOWN AND NOT IN SERVICE AND HAS ADDITIONALLY BEEN DISCONNECTED FROM THE PRODUCERS FLOW LINE SINCE THE DAY OF THE EVENT. A RETURN TO SERVICE PLAN WILL BE IMPLEMENTED IF COLUMBIA ELECTS TO RETURN THE ASSET BACK INTO SERVICE IN THE FUTURE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150106 | 16844 | 2015-08-25 15:04 | ORIGINAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2015-08-11 09:25 | 2015 |  |  | 31.6069 | -83.6695 | 1125313 | 2015-08-11 10:40 |  | NATURAL GAS |  | 915 | 15 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-08-11 10:57 | 2015-08-12 19:20 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 3 | 2015-08-11 09:25 | 2015-08-11 10:25 | ONSHORE | GA | 31714 | Not Within a Municipality | TURNER | MILEPOST | 7.378 | ASHBURN LINE | LINE 28 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 20 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 3.5 |  | 0.188 | 35000 | API 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | REPUBLIC | COAL TAR | [28 empty] | 1960 | 1960 | CARBON STEEL |  | MECHANICAL PUNCTURE | 3.5 | 5 | [7 empty] | CLASS 1 LOCATION | NO |  | 80 |  | NO | NO | NO |  | 2000 | 2185.78090796612 | 40 | 43.7156181593224 | 2200 | 1967.60563380282 | 35000 | 38251.1658894071 | 5000 | 5464.45226991529 | 0 | 0 |  |  | 44240 | 23129.9260899619 | 47912.7203192506 | [8 empty] | 1028 |  | 1082 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 70509 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NOT NECESSARY - THIRD PARTY DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES | YES | COUNTY ROAD |  |  | YES | [6 empty] | COUNTY | GRADER/SCRAPER | DRAINAGE | NO | [5 empty] | YES | 32 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | KENNETH PETERS | SR. PIPELINE ENGINEER | ken_peters@kindermorgan.com | 2053257554 | 2053253508 |  |  |  | REJI GEORGE | DIRECTOR COMPLIANCE | 7134205433 | reji_george@kindermorgan.com | A TURNER COUNTY (GA) ROAD GRADER WAS CLEANING DITCHES FOR NEISMITH ROAD ON AUGUST 11, 2015, AND STRUCK SOUTHERN NATURAL GAS COMPANY'S 3.5" ASHBURN PIPELINE (LINE 28), CAUSING A PUNCTURE AND RELEASE OF NATURAL GAS. THE COUNTY DID NOT MAKE ANY ONE-CALL NOTIFICATIONS PRIOR TO THE WORK. THE PIPELINE WAS ISOLATED AND ALLOWED TO BLOW DOWN IN ORDER TO MAKE REPAIRS. THE DAMAGED PIPE WAS CUT OUT WITH A NEW PIPE CYLINDER BEING INSTALLED. THE PIPELINE WAS PLACED BACK INTO SERVICE AUGUST 12, 2015.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150107 | 17058 | 2015-08-26 16:56 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2015-07-27 14:00 | 2015 |  |  | 31.5275 | -92.2124 | 1123985 | 2015-07-27 15:20 |  | NATURAL GAS |  | 8600 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | OPERATIONS RESUMED WHEN VALVES WERE CLOSED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-07-27 10:16 | 2015-07-27 10:16 | ONSHORE | LA | 71342 | JENA | LA SALLE | MILEPOST | MP 76.8 | JENA COMPRESSOR STATION | FACILITY ID: 2473 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2015 |  | CARBON STEEL |  | OTHER | [8 empty] | ACTIVATION OF EMERGENCY SHUTDOWN DEVICE | CLASS 1 LOCATION | NO |  | 181 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 24000 | 21464.7887323944 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 24000 | 22253.5211267606 | 21464.7887323944 | [8 empty] | 791 |  | 858 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA BASED SYSTEMS OPERATED AS DESIGNED WHEN THE EMERGENCY RELIEF VALVES WERE ACTIVATED. ALTHOUGH SCADA BASED ALARMS COULD IDENTIFY THE LOSS OF GAS, THE INCIDENT OCCURRED WITHIN A COMPRESSOR STATION CONTROLLED BY LOCAL OPERATING PERSONNEL. THE STATION TECHNICIAN IDENTIFIED THE GAS RELEASE, CLOSED THE VALVES, AND CONTACTED THE CONTROL ROOM INFORMING THEM OF THE INCIDENT AND ACTIONS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [14 empty] | YES |  |  |  |  | YES | [167 empty] | ROGER R. STREET | FIELD COMPLIANCE SPECIALIST | roger_street@transcanada.com | 615-465-5123 |  |  |  |  | ROGER STREET | FIELD COMPLIANCE SPECIALIST | 6154655123 | roger_street@transcanada.com | ON 27 JULY 2015 AT 10:16 CT, TWO EMERGENCY SHUTDOWN DEVICE (ESD) VENT VALVES AT JENA COMPRESSOR STATION OPENED AND RELEASED NATURAL GAS TO THE ATMOSPHERE. APPROXIMATELY 8.6 MMCF OF NATURAL GAS WAS RELEASED PRIOR TO THE VALVES BEING SHUT AT 10:25 CT. THE INCIDENT WAS REPORTED TO THE NRC AT 14:20 CT ON 27 JULY 2015. NO PROPERTY DAMAGE OR INJURIES WERE IDENTIFIED DUE TO THE INCIDENT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150108 | 16865 | 2015-08-31 19:44 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2015-08-08 20:30 | 2015 |  |  | 32.606 | -103.3087 | 1125137 | 2015-08-09 04:54 |  | NATURAL GAS |  | 5521 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELIEF VALVE RELEASE MET REPORTABLE QUANTITIES - NO FACILITY SHUTDOWN REQUIRED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-08-09 02:30 | 2015-08-09 02:40 | ONSHORE | NM | 88240 | HOBBS | LEA | MILEPOST | MP 0 ON L3070 | MONUMENT COMPRESSOR STATION | UNIT #4A DISCHARGE RELIEF VALVE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1953 |  | CARBON STEEL |  | OTHER | [8 empty] | RELEASE OF GAS DUE TO RELIEF VALVE ACTIVATION. | CLASS 1 LOCATION | NO |  | 328 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 13803 | 12344.9366197183 | 1194 | 1304.91120205577 | 200 | 218.578090796612 | 0 | 0 |  |  | 15197 | 13497.8781235045 | 13868.4259125707 | [8 empty] | 560 |  | 564 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | NOTIFICATION FROM UPSTREAM PRODUCER |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  |  |  | YES | [6 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | THE REASON FOR THE EQUIPMENT FAILURE COULD NOT BE DETERMINED | [161 empty] | KRISTIN VAN DER LAAN | COMPLIANCE ENGINEER III | kristin_vanderlaan@kindermorgan.com | 303-914-7753 |  |  |  |  | REJI GEORGE | COMPLIANCE - CODES AND STANDARDS DIRECTOR | 713-420-5433 | reji_george@kindermorgan.com | AN UPSTREAM PRODUCER CALLED EPNG GAS CONTROL AT 8:30PM MTN ON AUGUST 8, 2015 REPORTING HIGHER THAN NORMAL PRESSURES (RESULTING FROM PURCHASE POWER LOSSES IN THE AREA IMPACTING EPNG COMPRESSION FACILITIES). DURING THAT CALL THE PRODUCER MENTIONED THAT A RELIEF VALVE WAS RELIEVING. THE PRODUCER DID NOT SAY THAT IT WAS EPNG'S RELIEF VALVE AND THE EPNG CONTROLLER BELIEVED THE REFERENCE WAS TO A PRODUCER RELIEF VALVE. FURTHER, MAOP WAS NOT EXCEEDED AND THERE WERE NO ALARMS ASSOCIATED WITH THE MONUMENT STATION SO THE GAS CONTROLLER DID NOT TAKE ANY ACTION RELATED TO THE RELIEF VALVE. THE PRODUCER CALLED AGAIN AT 2:13AM MTN ON AUGUST 9, 2015 TO REPORT THAT THEY HEARD AN EPNG RELIEF VALVE RELIEVING IN THE MONUMENT STATION. THE EPNG GAS CONTROLLER CALLED OUT THE LOCAL OPERATIONS SPECIALIST WHO ARRIVED AT THE STATION AT 2:40AM. BY 3:00AM MTN THE UNIT SUCTION AND DISCHARGE HAD BEEN CLOSED AND THE VENTING HAD BEEN STOPPED. THE GAS LOSS ORIGINALLY REPORTED TO THE NRC WAS REVISED TO 5521MCF BASED ON ENGINEERING CALCULATIONS (ORIGINALLY CALCULATED AS A 4" ORIFICE BUT THE RELIEF VALVE IS A 1.28" ORIFICE). AN INVESTIGATION INTO THIS INCIDENT DETERMINED THAT THE RELIEF VALVE ACTUATED AT A PRESSURE BELOW THE MAOP OF THE FACILITY AND VENTED GAS TO ATMOSPHERE FOR SEVERAL HOURS. THE RELIEF VALVE WAS INSPECTED ON AUGUST 12, 2015 AND THE CAUSE OF THE EQUIPMENT FAILURE COULD NOT BE DETERMINED. THE RELIEF VALVE SEAT WAS LAPPED, THE SET POINT RESET AND TESTED, AND PLACED BACK INTO SERVICE. CONTRIBUTING TO THE INCIDENT WERE THE CONTROLLERS ACTIONS. IT WAS FOUND THAT THE CONTROLLER LACKED AN UNDERSTANDING OF WHAT CONSTITUTES A POTENTIAL ABNORMAL OPERATION AND FAILED TO THOROUGHLY QUESTION WHICH RELIEF VALVE WAS VENTING TO ASCERTAIN WHETHER OR NOT THE DEVICE IN QUESTION WAS AN EPNG DEVICE. THE CONTROLLER'S OQ WAS REVOKED AND THE CONTROLLER WAS GIVEN EXTENSIVE RE-TRAINING WITH A FOCUS ON THE IDENTIFICATION OF ABNORMAL OPERATIONS AND THE APPROPRIATE TIMELY RESPONSE REQUIRED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150109 | 16849 | 2015-09-01 11:54 | ORIGINAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2015-08-13 16:19 | 2015 |  |  | 29.9756 | -95.6021 | 1125583 | 2015-08-13 17:15 |  | NATURAL GAS |  | 1069 | 12888 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-08-13 21:15 | 2015-08-16 17:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 19 | 2015-08-13 16:19 | 2015-08-13 16:19 | ONSHORE | TX | 77429 | HOUSTON | HARRIS | MILEPOST | 159.18 | INDEX 129 | WEST 30" | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | EXPOSED DURING INCIDENT | 6 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 0.5 |  | 0.125 |  | API 5L | OTHER | FORGED 2" BY 1/2" SWAGE FITTING REDUCER FROM SEAMLESS MATERIAL | UNKNOWN FOR REDUCER; COUPLING IS LADISH | ASPHALT | [28 empty] | 1952 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | INCIDENT OCCURRED DURING BACKFILLING OPERATION | CLASS 3 LOCATION | YES | METHOD2 | 10 |  | NO | NO | NO |  | 0 | 0 | 38327 | 41887.2124298087 | 3179 | 2843.19014084507 | 8500 | 9289.568858856 | 6500 | 7103.78795088988 | 0 | 0 |  |  | 56506 | 29699.9834398351 | 61123.7593803997 | [8 empty] | 622 |  | 780 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | MANUAL | 55874 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS A RESULT OF WORK PERFORMED AT SITE | [12 empty] | NO |  |  | YES | 7 | 1 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [10 empty] | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 157176171 | TEXAS 811 | UTILITY OWNER | NO | YES | NO |  | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO USE HAND TOOLS WHERE REQUIRED | [263 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 2706886361 | jeff.mcmaine@bwpmlp.com | UNINTENTIONAL RELEASE FROM 1/2-INCH POWER GAS LINE CAUSED DURING BACKFILLING OPERATIONS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150110 | 16929 | 2015-09-02 18:12 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2015-08-03 20:36 | 2015 |  |  | 27.2222 | -98.1103 | 1124690 | 2015-08-03 21:49 |  | NATURAL GAS |  | 50740 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-08-03 22:06 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 100 | 2015-08-03 20:36 | 2015-08-03 21:30 | ONSHORE | TX | 78355 | FALFURRIAS | BROOKS | MILEPOST | 403-1+51168 | SAN SALVADOR (400-1) | LINE 400-1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 33 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.25 | 42000 | API 5L X42 | LONGITUDINAL ERW - LOW FREQUENCY |  | YOUNGSTOWN SHEET & TUBE | COAL TAR | [28 empty] | 1947 | 1947 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 675 | 16 |  | CLASS 2 LOCATION | NO |  | 332 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 147585 | 131995.035211268 | 40601 | 44372.4453221662 | 3312 | 3619.65318359189 | 0 | 0 |  |  | 191498 | 158874.886052491 | 179987.133717026 | [8 empty] | 827 |  | 903 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 58925 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE RUPTURE WAS NOT RELATED TO CONTROLLER ACTIONS AND THE CONTROLLER NOTIFIED TGP OPERATIONS AS SOON AS THE INCIDENT WAS IDENTIFIED. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED |  | YES | [15 empty] | STRESS CORROSION CRACKING | [12 empty] | YES | PREEXISTING OXIDE INCLUSIONS AND SEAMS/LAPS IN THE STEEL | [55 empty] | YES | [6 empty] | YES | [50 empty] | COMBINATION TOOL | 2009 |  |  |  |  | YES | 1997 | 1225 | NO | [13 empty] | NO | [63 empty] | KRISTIN VAN DER LAAN | COMPLIANCE ENGINEER III | kristin_vanderlaan@kindermorgan.com | 303-914-7753 |  |  |  |  | REJI GEORGE | DIRECTOR - COMPLIANCE CODES AND STANDARDS | 713-420-5433 | reji_george@kindermorgan.com | ON 08/03/2015 AT APPROXIMATELY 8:36PM TENNESSEE GAS PIPELINE (TGP) GAS CONTROL RECEIVED A PRESSURE RATE OF CHANGE CRITICAL ALARM ON LINE 400-1. THE GAS CONTROLLER CONTACTED TGP OPERATIONS TO DISPATCH PERSONNEL TO THE POSSIBLE LEAK SITE AND TAKE TGP STATION 1 OFFLINE. THE CONTROLLER ALSO CONFIRMED THAT LOCAL EMERGENCY RESPONDERS, INCLUDING THE BROOKS COUNTY SHERIFFS DEPARTMENT, WERE ON-SITE. OPERATIONS INITIATED EMERGENCY RESPONSE. THE 400-1 LINE FROM MAINLINE VALVE (MLV) 403-1 TO MLV 404-1 WAS ISOLATED AT 10:06PM AND THE ISOLATED SECTION WAS BLOWN DOWN TO A ZERO PRESSURE BY 10:15PM. THE FIRE MARSHAL EVACUATED HOMES AND TX DOT TEMPORARILY CLOSED HWY 285 FOR A 5 MILE DISTANCE EAST AND WEST UNTIL THE ISOLATED SEGMENT WAS BLOWN DOWN. THE METALLURGICAL REPORT CONCLUDED THAT THE CAUSE WAS HIGH PH STRESS CORROSION CRACKING.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150111 | 17019 | 2015-09-04 14:56 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2015-08-09 22:20 | 2015 |  |  | 40.0975 | -75.6812 | 1125195 | 2015-08-10 00:16 |  | NATURAL GAS |  | 6659 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-08-09 23:14 | 2015-08-10 03:14 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-08-09 22:19 | 2015-08-09 22:36 | ONSHORE | PA | 19425 | CHESTER SPRING | CHESTER COUNTY | MILEPOST | L-7210 | EAGLE COMPRESSOR STATION | EMERGENCY VALVE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | FAILED SUCTION HEADER EMERGENCY VALVE. | CLASS 3 LOCATION | NO |  | 422 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 18579 | 16616.4295774648 | 456236 | 498615.969163415 | 0 | 0 | 0 | 0 |  |  | 474815 | 246104.893784426 | 515232.39874088 | [8 empty] | 775 |  | 936 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ROOT CAUSE INVESTIGATIONS IDENTIFIED THAT DUE TO A BREACHED ETHANOL LINE INITIATING THE FIRE IN THE COMPRESSOR UNIT BUILDING. SCADA SYSTEM FUNCTIONED AS IT WAS DESIGNED TO AND ALERTED THE GAS CONTROLLER TO PERFORM NECESSARY CALL-OUTS TO ADDRESS THE ALARMS. | [12 empty] | YES | 1 | 0 | NO |  |  | EQUIPMENT FAILURE | FAILURE OF EQUIPMENT BODY (EXCEPT COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL | MATERIAL/WELD/EQUIP FAILURE | FAILURE OF EQUIPMENT BODY | [166 empty] | FAILURE OF EQUIPMENT BODY (EXCEPT COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL | [19 empty] | EMERGENCY SHUT VALVE LOCATED ON LINE 1804 SUCTION HEADER FAILED TO CLOSE AFTER THE EMERGENCY SHUTDOWN SYSTEM WAS ACTIVATED | [15 empty] | YES | IMPURITIES IN THE ACTUATOR TUBING | [161 empty] | GEORGE HAMATY | ENGINEER | ghamaty@cpg.com | (304) 357-3728 |  |  |  |  | PERRY MIKE HOFFMAN | MANAGER SYSTEM INTEGRITY | (304)357-2548 | mikehoffman@cpg.com | ON AUGUST 9, 2015 AT 22:19 EST, THE COMPRESSION UNITS AT EAGLE COMPRESSOR STATION (CS) LOCATED IN CHESTER SPRINGS, PA DID SHUT DOWN DUE TO AN EMERGENCY SHUTDOWN (ESD) SIGNAL THAT WAS TRIGGERED BY THE FIRE DETECTION/MELT-OUT SENSORS OVER UNIT 3. AT THE TIME OF THE ESD, ALL 4 UNITS AT THE STATION WERE RUNNING. WHEN THE STATION OPERATOR ARRIVED AT THE STATION IN RESPONSE TO A CALLOUT, HE NOTED PRESENCE OF FIRE IN THE COMPRESSOR BUILDING, LINE 1804 BLOWDOWN STACK WAS FOUND TO BE RELEASING NATURAL GAS (MATERIAL) INTO ATMOSPHERE AND LINE 1804 SUCTION HEADER EMERGENCY VALVE (L-7210) NOT FULLY CLOSED ALLOWING MATERIAL TO CONTINUE TO FLOW TO THE STATION AND OUT THE BLOWDOWN STACK. MATERIAL FLOWING INTO THE STATION THROUGH LINE 1804 WAS SHUT-OFF USING UPSTREAM BLOCK VALVES WHICH WERE MANUALLY CLOSED. THE SOURCE OF THE FIRE WAS DETERMINED TO BE A COOLANT LEAK ON A SHORT FLEXIBLE HOSE CONNECTION BETWEEN THE COOLANT HEADER AND HEAD CONNECTION AT CYLINDER NO. 5 ON AN ENGINE/COMPRESSOR PACKAGE. THE OTHER UNITS WERE INSPECTED FOR SIMILAR INDICATIONS ON THE ETHANOL HOSES BEFORE THE OTHER UNITS WERE RETURNED BACK INTO SERVICE. AFTER THE FULL INSPECTION AND SAFETY CHECKS ON THE OTHER UNITS WAS COMPLETED, THEY WERE RETURNED BACK INTO SERVICE IN SEQUENCE. UNIT NO. 3 WAS REPAIRED AND RETURNED BACK TO SERVICE AFTER NECESSARY REPAIRS/REPLACEMENTS WERE PERFORMED. KEY ACTION ITEMS WERE THE REPLACEMENT OF EMERGENCY VALVE(S) AND BLOWDOWN ACTUATORS (THIS PROJECT WAS UNDERWAY AT TIME OF THIS INCIDENT AND NEW VALVE ACTUATORS WERE ONSITE AWAITING INSTALLATION). REPLACEMENT OF THE PNEUMATIC COMPRESSORS WAS COMPLETED BACK IN 2015. ALSO, MODIFICATION TO VALVE INSPECTION PROCEDURE TO INCLUDE METHOD OF TESTING AND MAINTAINING AUXILIARY VALVES AND ACTUATOR HYDRAULICS. ENSURE NO EVIDENCE TO CONTAMINATION IN THE PNEUMATIC SYSTEM TO PREVENT MOISTURE ACCUMULATION IS HAMPERING THE EMERGENCY VALVE ACTUATOR FROM FUNCTIONING. INITIAL INCIDENT REPORT WAS SUBMITTED ON SEPTEMBER 04, 2015.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150112 | 16935 | 2015-09-14 15:39 | SUPPLEMENTAL FINAL | 38987 | KINETICA ENERGY EXPRESS LLC | 1001 MCKINNEY STREET, SUITE 900 | HOUSTON | TX | 77002 | 2015-08-12 14:42 | 2015 |  |  | 28.58 | -91.8707 | 1125462 | 2015-08-12 15:50 |  | NATURAL GAS |  | 30 | 623 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-08-12 14:00 | 2015-08-20 16:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-08-12 14:42 | 2015-08-12 14:00 | OFFSHORE | [28 empty] | 145 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SOUTH MARSH ISLAND | 78 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 |  | 0.375 | 52000 | 5L | SEAMLESS |  | NIPPON | EPOXY | [28 empty] | 1991 | 1988 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO | NO |  | 0 | 0 | 1713 | 1872.12134767298 | 83 | 74.2323943661972 | 0 | 0 | 1600 | 1748.62472637289 | 265000 | 289615.970305511 | COST OF REPAIR CLAMP, DIVE VESSEL, DIVERS AND COMPANY PERSONNEL |  | 268396 | 134680.350500292 | 293310.948773923 | [8 empty] | 880 |  | 1250 | OTHER | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 8622 | NO | [5 empty] | YES | SUBSEA TIE-IN CONFIGURATION WILL NOT ALLOW FOR THE PASSAGE OF INSPECTION TOOLS | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | PLATFORM OPERATOR IDENTIFIED BUBBLES ON SEA SURFACE |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | REMOTE LOCATION OFFSHORE WITH PRESSURES WELL BELOW ESTABLISHED MAOP | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | PINHOLE IDENTIFIED |  |  | YES |  |  |  | YES | [7 empty] | YES | 6:00 POSITION | YES | NO | NOT APPLICABLE - NOT MAINLINE PIPE | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KURT J. CHERAMIE | SENIOR DIRECTOR | kurt.cheramie@kineticallc.com | 9852092283 | 9852236197 |  |  |  | KURT J. CHERAMIE | SENIOR DIRECTOR | 9852092283 | kurt.cheramie@kineticallc.com | PLATFORM OPERATOR FOR ENERGY XXI CONTACTED KINETICA ENERGY EXPRESS PIPELINE OPERATIONS SUPERVISOR ON 8/12/2015 STATING THAT BUBBLES HAD BEEN SPOTTED ON THE WATER'S SURFACE ABOUT 1/2 MILE FROM THEIR PLATFORM. KINETICA PERSONNEL WERE DISPATCHED VIA HELICOPTER TO THE PLATFORM IN ORDER TO ISOLATE PIPELINE. AT 14:00, PLATFORM VALVES WERE CLOSED TO ISOLATE PRODUCTION FROM THE PIPELINE. PRESSURE WAS MONITORED TO DETERMINE IF LEAK WAS IN FACT ON KINETICA'S PIPELINE. AT 14:42, IT WAS DETERMINED THAT LEAK WAS ON KINETICA'S LINE. ARRANGEMENTS WERE MADE WITH PRODUCER TO RELIEVE PRESSURE FROM THE PIPELINE TO 70 PSIG SO DIVERS COULD WORK ON PIPELINE AT LEAK LOCATION. DIVE VESSEL WAS PROCURED AND DISPATCHED TO THE AREA. UPON ARRIVAL IN THE AREA, FIRST CLOSED SUB-SEA TIE-IN VALVE IN PREPARATION OF PIPELINE REPAIR. DIVER EXCAVATED LEAK AREA AND REMOVED CONCRETE COATING FROM PIPE. DIVER IDENTIFIED A SMALL PINHOLE LEAK. THE GENERAL AREA HAD UT INSPECTION PERFORMED, AND NO INDICATIONS OF GENERALIZED CORROSION WERE IDENTIFIED. A REPAIR CLAMP WAS INSTALLED. THE PLATFORM VALVES WERE RE-OPENED. PLATFORM OPERATOR WAS ASKED TO BEGIN PRODUCTION INTO THE LINE TO INCREASE PRESSURE WHILE DIVE VESSEL MONITORED FOR LEAKS. AFTER THE INITIAL PRESSURIZATION, THE PIPELINE WAS RETURNED TO SERVICE IN INCREMENTAL STEPS WHILE DIVE VESSEL CONTINUALLY MONITORED LOCATION FOR SIGNS OF LEAK. AFTER DETERMINING THAT THE REPAIR WAS SUCCESSFUL, THE DIVE VESSEL DEPARTED LOCATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150113 | 16860 | 2015-09-17 09:24 | ORIGINAL FINAL | 18152 | SEA ROBIN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2015-08-18 09:30 | 2015 |  |  | 28.5607 | -90.8064 | 1125967 | 2015-08-18 09:30 |  | NATURAL GAS |  | 6881 | 1940 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-08-21 10:30 | 2015-09-01 02:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-08-20 12:00 | 2015-08-20 08:00 | OFFSHORE | [28 empty] | 80 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SHIP SHOAL | 189 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 10 |  | 0.365 | 52000 | API 5LX | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | JONES & LAUGHLIN | COAL TAR | [28 empty] | 1972 | 1972 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 239 |  | NO | NO | NO |  | 0 | 0 | 5374 | 5873.19329970496 | 19060 | 17046.6197183099 | 200000 | 218578.090796612 | 0 | 0 | 0 | 0 |  |  | 224434 | 120702.06665353 | 241497.903814627 | [8 empty] | 958 |  | 1200 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 56911 | NO | YES | [6 empty] | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | UNITED STATES COAST GUARD |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS TOO SMALL FOR SCADA TO DETECT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | PINHOLE LEAK |  |  |  |  | YES | LOW FLOW |  |  | YES | HISTORICAL DATA |  |  |  |  | YES | 6 O'CLOCK POSITION | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | YES |  |  | 2015 | [6 empty] | YES | [53 empty] | NATHAN HLAVATY | DIRECTOR - REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 7138575479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - REGULATORY COMPLIANCE | 7138575479 | nathan.hlavaty@energytransfer.com | AT APPROXIMATELY 9:30 AM ON 8/18/2015, GAS CONTROL RECEIVED A CALL FROM THE UNITED STATES COAST GUARD REPORTING SEEING BUBBLES IN THE AREA NEAR A SEA ROBIN PIPELINE IN THE SOUTH TIMBALIER 189 AREA. THE NRC WAS NOTIFIED (NRC # 1125967), AT 9:30 AM ON 8/18/15 OF A POSSIBLE LEAK. WE WERE ABLE TO MAKE A FLIGHT ON 8/18/15 AND BASED ON THE COORDINATES FOR THE LEAK, WE SHUT DOWN THE PIPELINE AT 10:30 AM ON 8/21/15. IT TOOK 2 DAYS TO GET THE DSV ON SITE DUE TO WEATHER. THE PIPELINE WAS REPAIRED AND RESTARTED AT 2:30 AM ON 9/1/2015.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150114 | 17139 | 2015-09-18 16:17 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2015-08-26 20:45 | 2015 |  |  | 29.0431 | -91.6994 | 1126790 | 2015-08-26 21:40 |  | NATURAL GAS |  | 2631 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-08-26 20:45 | 2015-09-06 16:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2015-08-26 20:45 | 2015-08-26 23:50 | OFFSHORE | [28 empty] | 25 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EUGENE ISLAND | 95 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | FLANGE ASSEMBLY | [38 empty] | 2006 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 382 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 8098 | 7242.57746478873 | 625000 | 683056.533739412 | 10000 | 10928.9045398306 | 200000 | 218578.090796612 | INVESTIGATION |  | 843098 | 426399.448427183 | 919806.106540643 | [8 empty] | 925 |  | 1200 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | AUTOMATIC | 174240 | NO |  |  |  | YES |  | YES | SUB-SEA TIE-IN | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT OCCURRED WHILE CONTRACTOR WAS ONSITE FOR SCHEDULED OUTAGE PERFORMED BY AREA. | [12 empty] | YES | 2 | 0 | YES | 24 | 0 | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | DIVE COMPANY WAS JETTING TO EXPOSE SUB-SEA TIE-IN VALVE ASSEMBLY FOR PIPELINE ABANDONMENT. SUB-SEA CONNECTOR APPEARED TO BE DAMAGED DURING WORK ACTIVITIES, THEREBY, CAUSING A GAS RELEASE. | [147 empty] | SHANNON MATTINGLY | PA OQ AND EVENT SUPPORT PROGRAM LEADER | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 2706886361 | jeff.mcmaine@bwpmlp.com | DIVE COMPANY WAS JETTING TO EXPOSE SUB-SEA TIE-IN VALVE ASSEMBLY FOR PIPELINE ABANDONMENT. LINE DISCONNECTED, GAS RELEASED AND IGNITED AT THE SURFACE. CAUSE IS STILL UNDER INVESTIGATION. 7-7-16 DIVE COMPANY WAS JETTING TO EXPOSE SUB-SEA TIE-IN VALVE ASSEMBLY FOR PIPELINE ABANDONMENT. SUB-SEA CONNECTOR APPEARED TO BE DAMAGED DURING WORK ACTIVITIES, THEREBY, CAUSING A GAS RELEASE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150115 | 17026 | 2015-09-20 15:26 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2015-08-22 06:30 | 2015 |  |  | 40.6524 | -82.1316 | 1126372 | 2015-08-22 08:40 |  | NATURAL GAS |  | 15006 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-08-22 07:40 | 2015-08-25 08:25 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 15 | 2015-08-22 06:19 | 2015-08-22 06:21 | ONSHORE | OH | 44638 | LAKEVILLE | HOLMES | SURVEY STATION NO. | 214650 | SL-2481 IN HOLMES STORAGE FIELD | DRIP | NO | OPERATOR-CONTROLLED PROPERTY | BELOWGROUND STORAGE OR ABOVEGROUND STORAGE VESSEL, INCLUDING ATTACHED APPURTENANCE |  |  |  |  | NO | [22 empty] | INTERSTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | PULSATION BOTTLE OR DRIP/DRIP COLLECTION DEVICE | [38 empty] | 1954 |  | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 180 | 60 |  | CLASS 1 LOCATION | NO |  | 478 |  | NO | NO | NO |  | 675 | 737.701056438565 | 0 | 0 | 41867 | 37444.4295774648 | 581996 | 636057.872656324 | 0 | 0 | 59363 | 64877.2560197963 | CONSULTANT'S FEE TO PERFORM METALLURGICAL FAILURE ANALYSIS INVESTIGATION. |  | 683901 | 360906.684146406 | 739117.259310024 | [8 empty] | 1087 |  | 1200 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | NO | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE DRIP FAILURE WAS NOT RELATED TO ANY HUMAN INTERACTION. | [12 empty] | YES | 1 | 0 | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING | [5 empty] | YES | METALLURGICAL FAILURE ANALYSIS INVESTIGATION REPORT REFERENCED INTERNAL CORROSION PITTING DUE TO A GAS-PHASE RELATED CORROSION MECHANISM. | YES | YES |  |  | YES | [5 empty] | YES | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [313 empty] | GEORGE HAMATY | ENGINEER | ghamaty@cpg.com | (304)357-3728 |  |  |  |  | PERRY MICHAEL HOFFMAN | MANAGE | (304)357-2548 | mikehoffman@cpg.com | ON THE MORNING OF AUGUST 22, 2015, A DRIP INSTALLED ALONG LINE SL-2481 FAILED LEADING TO AN UNINTENDED AMOUNT OF NATURAL GAS (MATERIAL) TO VENT INTO ATMOSPHERE EXCEEDING THE INCIDENT REPORTING THRESHOLD. THIS PIPELINE IS LOCATED IN LAKEFIELD, HOLMES COUNTY, OHIO AND OWNED, OPERATED AND MAINTAINED BY COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA), WITHIN THE HOLMES STORAGE FIELD (SF). THE FAILURE WAS IDENTIFIED BY A NEARBY COLUMBIA EMPLOYEE WHO WAS THE FIRST RESPONDER TO THE FAILURE SITE. NECESSARY SAFETY MEASURES WERE TAKEN TO ISOLATE ALL WELLS, SF LINES FOR HOLMES AND WAYNE SF. THE AFFECTED STORAGE LINE (SL) WAS ISOLATED AND MATERIAL STOPPED FLOWING INTO ATMOSPHERE IN LESS THAN AN HOUR FROM THE TIME THE FIRST RESPONDER ARRIVED ON SITE. THE DRIP WAS REMOVED WITH THE SECTION OF THE SL THAT IT WAS TAPPED INTO AND A NEW PRE-TESTED PIPE WAS INSTALLED, WHICH DID NOT INCLUDE A DRIP. THE REPAIRED SL WAS RETURNED BACK INTO SERVICE ON AUGUST 25, 2015. THE RESULTS OF THE METALLURGICAL FAILURE ANALYSIS INDICATE THAT THE METALLURGICAL CAUSE OF THE FAILURE WAS DUE TO INTERNAL PITTING CORROSION. THE LOCATION OF THE FAILURE POINT WAS AT THE 08:00 O'CLOCK POSITION AND THE PRESENCE OF SEVERE CORROSION AT THE 04:00 O'CLOCK POSITION, SUGGESTS THAT THE FAILED DRIP WAS PARTIALLY FILLED WITH SLUDGE/DEPOSITS AND THAT AN AQUEOUS PHASE WAS PRESENT ON TOP OF THE SLUDGE/DEPOSITS. THIS GEOMETRY IS CONSISTENT WITH A GAS-PHASE RELATED CORROSION MECHANISM. THE INITIAL INCIDENT REPORT WAS SUBMITTED ON SEPTEMBER 20, 2015.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150116 | 17343 | 2015-09-28 15:31 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2015-09-23 05:17 | 2015 |  |  | 40.8222 | -73.959 | 1129387 | 2015-09-25 15:36 |  |  |  | 0 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | PERIODIC TESTING OF A REMOTE OPERATED VALVE (ROV) | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-09-23 05:17 | 2015-09-23 05:17 | ONSHORE | NY | 10031 | NEW YORK | NEW YORK | MILEPOST | ROV-62190 | CON EDISON | M1 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | IN UNDERGROUND ENCLOSED SPACE (E.G. VAULT) |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | MAINLINE | BALL |  | CAMERON |  |  |  | 2013 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | EXCEEDED MAXIMUM ALLOWABLE OPERATING PRESSURE (MAOP) UPSTREAM OF VALVE. VALVE WAS CLOSED AS PART OF PERIODIC REMOTE TESTING PROCEDURE | CLASS 4 LOCATION | YES | METHOD1 | 387 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | [8 empty] | 396 |  | 350 | 192.619(A)(1) |  |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 | NO |  |  |  |  | AUTOMATIC | REMOTELY CONTROLLED | 87 | NO | YES | YES | YES |  |  |  |  | YES |  |  |  |  | YES | NO LAUNCHERS | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT IS A NORMALLY PERFORMED TEST THAT WILL BE RE-EVALUATED. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | PIPELINE OR EQUIPMENT OVERPRESSURED | INCORRECT OPERATION | PIPELINE/EQUIPMENT OVERPRESSURED | [204 empty] | PIPELINE OR EQUIPMENT OVERPRESSURED |  |  |  | YES |  |  |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | GIUSEPPE MIRASOLA | DEPARTMENT MANAGER | mirasolag@coned.com | 718 794 2873 |  |  |  |  | ANTHONY LETO | CHIEF ENGINEER | 7188391759 | letoa@coned.com | ON SEPTEMBER 23, 2015 A BIENNIAL REMOTE CLOSURE TEST OF REMOTELY OPERATED VALVE (ROV) 62190 WAS PERFORMED; AS PART OF THIS PROCEDURE, TWO CLOSURES ARE COMPLETED TO FIRST TEST A FRAME RELAY COMMUNICATION PATH, FOLLOWED BY A WIRELESS COMMUNICATION PATH. INITIAL CONDITIONS WERE ROV 62190 IN THE 100% OPEN CONDITION ON FRAME RELAY COMMUNICATIONS. FLOW THROUGH THE TRANSCO 134TH STREET GATE STATION UPSTREAM OF THE ROV WAS 1700 DTH/H. THE SEQUENCE OF EVENTS IS AS FOLLOWS: 5:07:55 - SET POINT FOR ROV 62190 SET TO 0% OPEN 5:08:02 - ROV 62190 IN TRAVEL 5:09:10 - ROV 62190 43% OPEN - ALARM FOR POSITION 5:10:11 - ROV 62190 0% OPEN - ALARM FOR FULL CLOSURE 5:10:15 - SET POINT FOR ROV 62190 SET TO 100% OPEN 5:10:24 - ROV 62190 IN TRAVEL 5:12:14 - ROV 62190 100% OPEN 5:13:48 - ROV 62190 WIRELESS COMMUNICATION PATH SELECTED 5:14:07 - SET POINT FOR ROV 62190 SET TO 0% OPEN 5:15:04 - ROV 62190 VALVE IN TRAVEL 5:15:04 - ROV 62190 59% OPEN - ALARM GENERATED FOR POSITION 5:16:32 - TRANSCO 134TH STREET FLOW IS 2517 DTH/H 5:16:54 - TRANSCO 134TH STREET PRESSURE IS 346 PSIG - ALARM FOR HI PRESSURE 5:17:17 - ROV 62190 0% OPEN - ALARM FOR FULL CLOSURE 5:17:17 - ROV 62190 NORTH (UPSTREAM) PRESSURE IS 375.7 PSIG - ALARM FOR HI HI PRESSURE. TRENDING SHOWS AN INSTANTANEOUS PRESSURE PEAK AT 396 PSIG; MAOP + 10% EXCEEDED FOR 20 SECONDS (>385 PSIG) 5:17:22 - SET POINT FOR ROV 62190 SET TO 100% OPEN 5:17:32 - ROV 62190 IN TRAVEL 5:18:05 - TRANSCO 134TH STREET PRESSURE IS 288 PSIG - PRESSURE IN NORMAL RANGE 5:18:44 - ROV 62190 NORTH (UPSTREAM) PRESSURE IS 288 PSIG - PRESSURE IN NORMAL RANGE 5:19:58 - ROV 62190 100% OPEN DUE TO CONFLICTING PRESSURE READINGS ON THE SAME LINE THE CONTROLLER NOTIFIED GAS ENGINEERING DURING NORMAL BUSINESS HOURS ON 9/23/15. PRESSURE CONTROL (PC) INSTRUMENTS AND CONTROLS (I/C) VERIFIED TRANSDUCER CALIBRATION FOR BOTH TRANSDUCERS ON 9/24/15. TRANSCO WILLIAMS WAS CONTACTED TO EXTRACT STATION DATA ON 9/24/15; TRANSCO STATED THAT PHYSICAL DATA WOULD BE AVAILABLE WITHIN 24 HOURS. ON 9/25/15 INFORMATION FROM TRANSCO INDICATED A DISCRETE HIGH PRESSURE ALARM IN EXCESS OF 360 PSIG AND TRAVEL OF THE FIRST OF TWO OVER PRESSURE PROTECTION (OPP) DEVICES SET AT 365 PSIG AND 370 PSIG RESPECTIVELY. DUE TO THE HIGH PROBABILITY OF AN EVENT, CENTRAL INFORMATION GROUP (CIG), PUBLIC SERVICE COMMISSION (PSC), AND NATIONAL REPORTING CENTER (NRC) WERE NOTIFIED ON 9/25. POST-ANALYSIS FOUND THAT INTERNAL SPECIFICATION G-11810-29 "PROCEDURE FOR INSPECTION AND MAINTENANCE OF GAS TRANSMISSION PIPELINES" MADE NO PROVISION FOR TIME PERIODS BETWEEN VALVE MOVEMENTS TO ALLOW FOR SYSTEM STABILIZATION. REVISION G-11810-30A INCORPORATED A 15 MINUTE STABILIZATION TIME FOR ALL VALVE MOVEMENTS FOR ROV FULL-CLOSURE INSPECTIONS. PROCEDURAL PRACTICE ALSO INCORPORATED REDUCING FLOW TO 0 DTH/H PRIOR TO ANY FULL-CLOSURE TEST OF A ROV.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150117 | 17249 | 2015-10-05 14:45 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2015-09-08 12:53 | 2015 |  |  | 37.5611 | -82.2261 | 1127891 | 2015-09-08 13:53 |  | NATURAL GAS |  | 9072 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-09-08 17:58 | 2015-09-13 09:08 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-09-08 12:40 | 2015-09-08 14:45 | ONSHORE | KY | 41501 | PIKEVILLE | PIKE | MILEPOST | VS-7070 | LINE KA-WEST | VS-7070 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 35 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.25 | 42000 | API-5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | U.S. STEEL | EPOXY | [28 empty] | 1999 | 1999 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 341 |  | NO | NO | NO |  | 0 | 0 | 1567 | 1712.55934139145 | 23224 | 20770.7605633803 | 300000 | 327867.136194918 | 0 | 0 | 30300 | 33114.5807556867 | COST OF FAILURE ANALYSIS INVESTIGATION |  | 355091 | 188020.233781548 | 383465.036855376 | [8 empty] | 172 |  | 374 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 44530 | NO |  | YES | [5 empty] | YES |  | YES |  |  |  |  | TRANSMISSION SYSTEM | YES | NO | NO | NO | NO | AIR PATROL |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS FOUND TO BE DUE TO A CRACK IN THE BODY OF THE PIPELINE | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [52 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | LANDSLIDE |  |  |  |  | NO | [306 empty] | GEORGE HAMATY | ENGINEER | george_hamaty@transcanada.com | (304)357-3728 |  |  |  |  | LEE ROMACK | MANAGER US REGULATORY COMPLIANCE | (832)320-5315 | lee_romack@transcanada.com | ON SEPTEMBER 8, 2015, A COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA) PIPELINE WAS INSPECTED BY COLUMBIA OPERATIONS PERSONNEL AND WAS FOUND TO HAVE A GRADE 1 LEAK IN A RURAL AREA NEAR THE CITY OF PIKEVILLE, PIKE COUNTY, KENTUCKY. LINE KA-WEST IS A 20 INCH IN DIAMETER TRANSMISSION PIPELINE THAT IS OPERATED AND MAINTAINED BY COLUMBIA. THE AREA WAS MADE SAFE BY ISOLATING THE AFFECTED SEGMENT UPON CLOSING THE UPSTREAM AND DOWNSTREAM CRITICAL VALVES. A NEAR-BY COMPRESSOR STATION WAS UTILIZED TO HELP CONTROL THE FLOW OF NATURAL GAS THROUGH THE LEAK AREA. COLUMBIA OPERATIONS PERSONNEL RESPONDED TO THE SITE, MOBILIZED EQUIPMENT AND PREPARED THE AREA TO INITIATE A PIPELINE REPLACEMENT WITH PRE-TESTED JOINTS OF PIPE. THE LINE WAS REPAIRED AND RETURNED TO SERVICE ON SEPTEMBER 13TH, 2015. THE RESULTS OF THE METALLURGICAL FAILURE ANALYSIS REPORT AS PRESENTED BY THE METALLURGICAL ANALYSIS CONSULTANT INDICATED THE FOLLOWING: THE FAILURE OF THE PIPELINE SECTION WAS INITIATED AT AN OVERBEND CONTAINING A BUCKLE THAT WAS LIKELY THE RESULT OF DUCTILE OVERLOAD FROM BENDING STRESSES SUCH AS THOSE CAUSED BY LAND/SOIL MOVEMENT. THERE WAS NO EVIDENCE OF PRE-EXISTING DEFECTS OR IN-SERVICE GROWTH ON THE FRACTURE SURFACE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150118 | 17097 | 2015-10-05 17:11 | SUPPLEMENTAL FINAL | 6660 | GREAT LAKES GAS TRANSMISSION CO | 700 LOUISIANA STREET | HOUSTON | TX | 77002 | 2015-09-05 20:50 | 2015 |  |  | 48.9903 | -97.0592 | 1127708 | 2015-09-05 22:07 |  | NATURAL GAS |  | 7260 | 26610 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-09-05 21:19 | 2015-09-22 16:20 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 2 | 2015-09-05 20:50 | 2015-09-05 21:15 | ONSHORE | MN | 56755 | Not Within a Municipality | KITTSON | MILEPOST | MP 0.7 | 200 LINE | VALVE SECTION 1-0-2 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 40 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | PIG SIGNAL | 1972 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 835 |  | NO | NO | NO |  | 0 | 0 | 71050 | 77649.8667554963 | 19380 | 17332.8169014085 | 520000 | 568303.036071191 | 80000 | 87431.2363186447 | 0 | 0 |  |  | 690430 | 354612.389862158 | 750716.95604674 | [8 empty] | 794 |  | 974 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | AUTOMATIC | 86275 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 1 | 0 | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | MECHANICAL COUPLING | [19 empty] | YES | CONNECTION SOCKET HEAD CAP SCREWS FAILED DUE TO STRESS CORROSION CRACKING | [161 empty] | ROBERT CADORIN | COMPLIANCE SPECIALIST | robert_cadorin@transcanada.com | 248-205-7669 |  |  |  |  | ROBERT CADORIN | COMPLIANCE SPECIALIST | 248-205-7669 | robert_cadorin@transcanada.com | ON SEPTEMBER 5, 2015, GREAT LAKES GAS TRANSMISSION COMPANY (GLGT) EXPERIENCED AN INCIDENT ON ITS 200 LINE PIPELINE IMMEDIATELY DOWNSTREAM OF A PIG LAUNCHER ON PROPERTY CONTROLLED BY GLGT AT ITS ST. VINCENT COMPRESSOR STATION IN KITTSON COUNTY, MINNESOTA. THE INCIDENT, WHICH RESULTED IN A SHUTDOWN OF THE PIPELINE VALVE SECTION BETWEEN THE COMPRESSOR STATION AND MLV 1-1-2, WAS THE RESULT OF A CONNECTION FAILURE OF A TWO-INCH DIAMETER PIG SIGNAL COMPONENT AT THE ABOVEMENTIONED LOCATION. GAS WAS RELEASED AND SUBSEQUENTLY IGNITED. FOLLOWING CONTROL OF THE RELEASE AND CONTROLLED BLOWDOWN OF THE PIPELINE SECTION, THE AREA WAS EXCAVATED AND THE SOURCE OF THE GAS LEAK CONFIRMED AS A FAILED CONNECTION BETWEEN THE BASE OF A PIG SIGNAL OFFTAKE TUBE AND A BOLTED MOUNTING PLATE ATTACHED TO THE GLGT 200 LINE. THE DAMAGED PIG SIGNAL COMPONENTS, INCLUDING THE PIG SIGNAL OFFTAKE TUBE WITH ASSOCIATED BASE (WHICH WAS ALREADY DISCONNECTED FROM THE PIPELINE) AND THE LOWER MOUNTING PLATE, WERE REMOVED FROM THE PIPELINE AND SENT TO A THIRD-PARTY LABORATORY FOR FAILURE ANALYSIS. THE PIG SIGNAL WAS NOT REPLACED. THE PIPELINE WAS REPAIRED BY REMOVAL OF THE WELD-O-LET THAT CONNECTED THE BASE MOUNTING PLATE TO THE PIPELINE AND THEN INSTALLING A CONTOURED INSERT FITTING (VESSELET) AND CAP. FOLLOWING COMPLETION OF THE REPAIR, THE PIPELINE WAS PLACED BACK INTO SERVICE THE AFTERNOON OF SEPTEMBER 22, 2015. FAILURE ANALYSIS OF THE PIG SIGNAL COMPONENTS INDICATED THAT THREE (3) OF THE FOUR (4) FASTENERS, SOCKET HEAD CAP SCREWS (SHCS), OF THE BOLTED MOUNTING PLATE CONNECTION FAILED BY A TIME-DEPENDENT, STRESS CORROSION CRACKING (SCC) MECHANISM. THE WEST SHCS FAILURE MAY HAVE BEEN EXACERBATED BY ADDITIONAL FACTORS DUE TO ITS VERY HIGH HARDNESS AND POSSIBLE UN-TEMPERED MARTENSITIC CONDITION. THE SOUTH SHCS FAILED LAST AND EXHIBITED WITH MIXED SCC AND DUCTILE RUPTURE MODES. ITS REMAINING LIGAMENT FAILED SUDDENLY WHEN ITS LOAD BEARING CAPACITY WAS EXCEEDED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150119 | 17527 | 2015-10-07 17:27 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2015-09-09 14:30 | 2015 |  |  | 34.363 | -102.9703 | 1128021 | 2015-09-09 17:09 |  | NATURAL GAS |  | 3550 | 630 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-09-09 16:30 | 2015-09-10 20:50 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-09-09 14:30 | 2015-09-09 16:30 | ONSHORE | TX | 79325 | FARWELL | PARMER | MILEPOST | MP 37+4500 | EPNG | LINE 2125 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 42 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 |  | 0.188 | 30000 | API 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | LONE STAR STEEL | COAL TAR | [28 empty] | 1959 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 2.4 | 2.4 | [7 empty] | CLASS 1 LOCATION | NO |  | 155 |  | NO | NO | NO |  | 0 | 0 | 1726 | 1886.32892357476 | 9727 | 8699.5 | 28407 | 31045.7391262968 | 2780 | 3038.2354620729 | 0 | 0 |  |  | 42640 | 25530.4851210304 | 44669.8035119444 | [8 empty] | 539 |  | 793 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 62574 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS CONTROL DID NOT CONTRIBUTE TO INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  | YES | PRIVATE LANDOWNER | [7 empty] | COUNTY | GRADER/SCRAPER | GRADING | NO | [5 empty] | YES | 28 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | KRITI BHAYANI | PIPELINE ENGINEER I-COMPLIANCE | kriti_bhayani@kindermorgan.com | 7134206633 |  |  |  |  | REJI GEORGE | DIRECTOR - COMPLIANCE - CODES AND STANDARDS | 713-420-5433 | reji_george@kindermorgan.com | ON SEPTEMBER 9, 2015 KINDER MORGAN (KM) OPERATIONS PERSONNEL RECEIVED A CALL OF A POSSIBLE LINE STRIKE ON EPNG 2125 LINE FROM ATMOS. THE LINE 2125 IS LOCATED NEAR FARWELL, TEXAS IN PARMER COUNTY, TEXAS. KM OPERATIONS SPECIALIST AT STATION 169 (HEREFORD) RECEIVED A CALL (2:30 PM-LOCAL TIME) FROM AN ATMOS EMPLOYEE STATING THAT HE THOUGHT OUR EPNG LINE HAD BEEN STRUCK. KM OPS DISPATCHED THREE (3) OPERATION SPECIALISTS TO THE ALLEGED LINE STRIKE SITE TO VERIFY THE LINE STRIKE. THERE WERE VISIBLE SIGNS AROUND THE VICINITY. THE KM SPECIALIST, WHO ARRIVED ON SITE, CONFIRMED THAT THE 8" EPNG 2125 LINE HAD BEEN STRUCK AND WAS VENTING GAS. HIS TIME OF ARRIVAL AT THE SCENE WAS 3:30 PM LOCAL TIME. KM DISCOVERED THAT THE PIPELINE HAD GOUGE IN IT AND LEARNED THAT A COUNTY ROAD MAINTAINER WAS DIGGING A BAR DITCH FOR THE LOCAL FARMER AND ACCIDENTALLY STRUCK THE LINE. MAINLINE VALVES 6 AND 7 WERE CLOSED TO ISOLATE THE LINE AND IMMEDIATELY STARTED REPAIRS AND ALL REPAIR WORK CONCLUDED ON 9/10/15 AT 8:50 PM. THE CONTROL ROOM FOR EPNG RECEIVED AN ALARM ON THE EPNG SCADA SYSTEM AND IMMEDIATELY STARTED WORKING WITH OUR FIELD MEASUREMENT TECHNICIAN TO TROUBLESHOOT THE ROOT CAUSE OF THE ALARM. GIVEN THE REMOTE LOCATION OF THE SITE, IT TOOK OUR FIELD KM PERSONNEL SOME TIME TO ARRIVE ON SITE AND CONFIRM THAT OUR EPNG LINE WAS STRUCK AND RELEASING GAS. UPON CONFIRMATION OF THE LINE STRIKE AND RELEASE OF GAS, KM PERSONNEL IMMEDIATELY STARTED ISOLATING THE LINE SEGMENT AFFECTED BY A 3RD PARTY LINE STRIKE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150120 | 17094 | 2015-10-08 14:25 | SUPPLEMENTAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2015-09-09 16:30 | 2015 |  |  | 32.8486 | -92.2857 | 1128025 | 2015-09-09 17:23 |  | NATURAL GAS |  | 42100 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | REROUTED GAS FLOW | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 16 | 2015-09-09 16:33 | 2015-09-09 17:30 | ONSHORE | LA | 71241 | FARMERVILLE | UNION | MILEPOST | 28+4276 | MAIN LINE SYSTEM | MLS | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 26 |  | 0.281 | 52000 | API 5L | FLASH WELDED |  | A. O. SMITH | COAL TAR | [28 empty] | 1949 | 1949 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 552 | 26 |  | CLASS 1 LOCATION | NO |  | 511 |  | NO | NO | NO |  | 5000 | 5464.45226991529 | 114655 | 125305.355001428 | 133367 | 119278.936619718 | 207439 | 226708.102883792 | 7500 | 8196.67840487294 | 0 | 0 |  |  | 467961 | 291516.174814599 | 484953.525179726 | [8 empty] | 766 |  | 810 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 52800 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT OCCURRED AT A PRESSURE BELOW MAOP | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED | YES | YES | [15 empty] | STRESS CORROSION CRACKING |  | YES | [67 empty] | NO | [63 empty] | YES | 1976 | 1012 | NO | [13 empty] | NO | [63 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 2706886361 | jeff.mcmaine@bwpmlp.com | TEXAS GAS EXPERIENCED A PIPELINE FAILURE OF ITS MAIN LINE SYSTEM 26" NO. 1 LINE IN UNION PARISH, LOUISIANA. THERE WERE NO INJURIES. THE CAUSE REMAINS UNDER INVESTIGATION. 3-15-16 UPDATE TO FINALIZE REPORT INCLUDING COST AND CAUSE. BASED ON STRESS ENGINEERING'S VISUAL EXAMINATION AND METALLURGICAL ANALYSES OF THE SAMPLES PROVIDED, ALONG WITH OBSERVATIONS FROM A VISIT TO THE SITE, SES CONCLUDED THAT THE MONROE FAILURE WAS CAUSED BY A COMBINATION OF CORROSION AND NEAR-NEUTRAL PH STRESS CORROSION CRACKING. THE INFORMATION AVAILABLE TO SES DID NOT ALLOW A DETERMINATION OF THE PRECISE TIMING OR EXACT CONDITIONS THAT LED TO THE FAILURE. HOWEVER, IT WAS APPARENT THAT CORROSION ENLARGED CRACKS IN THE PIPE, THEREBY SIGNIFICANTLY CONTRIBUTING TO THE FAILURE. THE MECHANICAL PROPERTIES OF THE PIPE MATERIAL WERE TESTED AND FOUND TO MEET THE REQUIREMENTS OF API 5LX IN EFFECT IN 1948 (AS WELL AS CURRENT REQUIREMENTS). WHILE THE MATERIAL TOUGHNESS WAS LOW, THIS PROPERTY ALONE DID NOT PLAY A SIGNIFICANT ROLE IN THE FAILURE. 4-29-16 REVISED CAUSE ON PART G TO REFLECT LABORATORY ANALYSIS FINDINGS. 5-23-16 REVISED PER PHMSA REQUEST TO REPORT CAUSE UNDER SECTION G5 INSTEAD G1.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150121 | 16878 | 2015-10-12 12:23 | ORIGINAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2015-09-18 09:45 | 2015 |  |  | 30.8914 | -92.4071 | 1128800 | 2015-09-18 10:30 |  | NATURAL GAS |  | 7820 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-09-18 11:00 | 2015-09-18 23:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-09-18 09:45 | 2015-09-18 09:20 | ONSHORE | LA | 70585 | TURKEY CREEK | EVANGELINE | MILEPOST | 60 | INDEX 202 | IOWA MARKSVILLE 6" | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 8 |  | YES |  |  |  |  | YES | UNCASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 |  | 0.188 | 35000 | API 5L | SEAMLESS |  | UNKNOWN | COAL TAR | [28 empty] | 1931 | 1931 | CARBON STEEL |  | MECHANICAL PUNCTURE | 22 | 10 | [7 empty] | CLASS 1 LOCATION | NO |  | 828 |  | NO | NO | NO |  | 1500 | 1639.33568097459 | 0 | 0 | 20097 | 17974.0774647887 | 40000 | 43715.6181593224 | 4320 | 4721.28676120681 | 0 | 0 |  |  | 65917 | 41620.8580429948 | 68050.3180662925 | [8 empty] | 370 |  | 490 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 19008 | NO |  | YES |  | YES |  | YES | DRESSER COUPLINGS | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY DAMAGE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO | YES | COUNTY ROAD |  |  | YES | [6 empty] | CONTRACTOR | GRADER/SCRAPER | GRADING | NO | [5 empty] | YES | 12 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 2706886361 | jeff.mcmaine@bwpmlp.com | GULF SOUTH PIPELINE, LP EXPERIENCED A PIPELINE FAILURE ON ITS INDEX 202 IN EVANGELINE PARISH, LA NEAR TURKEY CREEK AS THE RESULT OF THIRD-PARTY DAMAGE. PIPELINE WAS STRUCK BY A PARISH ROAD CONTRACTOR CLEANING THE ROADWAY DITCH. NO ONE-CALL WAS MADE BY THE ROAD CONTRACTOR. NO INJURIES WERE INCURRED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150122 | 16883 | 2015-10-13 15:02 | ORIGINAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION LP (SPECTRA ENERGY CORP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2015-09-21 18:15 | 2015 |  |  | 28.5475 | -92.9047 | 1129074 | 2015-09-21 19:15 |  | NATURAL GAS |  | 65 | 18802 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-09-22 18:00 | 2015-09-25 07:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-09-21 18:15 | 2015-09-22 12:00 | OFFSHORE | [28 empty] | 150 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EAST CAMERON | 246 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 20 |  | 0.406 | 52000 | API-5L X-52 | SEAMLESS |  | US STEEL | OTHER | CONCRETE AND SOMASTIC | [27 empty] | 1971 | 1971 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 524 |  | NO | NO | NO |  | 0 | 0 | 47005 | 51371.3157894737 | 162 | 144.887323943662 | 325000 | 355189.397544494 | 0 | 0 | 0 | 0 |  |  | 372167 | 186772.306537426 | 406705.600657911 | [8 empty] | 900 |  | 1440 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 100425 | YES | [7 empty] | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | COAST GUARD HELCOPTER DISCOVERED THE LEAK |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS TOO SMALL TO BE IDENTIFIED BY CONTROL ROOM PERSONNEL. A REVIEW OF OPERATING RECORDS FOUND ABNORMAL OPERATING CONDITIONS DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | YES | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | deteschendorf@spectraenergy.com | 713-627-5573 | 713-386-4468 |  |  |  | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 713-627-5008 | nyatanu@spectraenergy.com | INDICATIONS OF BUBBLES ON THE WATER SURFACE IN EAST CAMERON 246 WERE REPORTED BY A COAST GUARD HELICOPTER ON SEPTEMBER 21, 2015. UPON INVESTIGATION, IT WAS DETERMINED THE LEAK WAS CAUSED BY A PINHOLE LEAK RESULTING FROM INTERNAL CORROSION ON TEXAS EASTERN TRANSMISSION, L.P. 20-INCH LINE 41-A-2 NATURAL GAS PIPELINE. REPAIR BY INSTALLATION OF A CLAMP WAS COMPLETED SEPTEMBER 25, 2015.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150123 | 17599 | 2015-10-15 12:41 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2015-09-16 11:00 | 2015 |  |  | 38.8933 | -79.8432 | 1128651 | 2015-09-16 14:06 |  | NATURAL GAS |  | 107 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-09-16 12:25 | 2015-09-16 14:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-09-16 11:00 | 2015-09-16 11:00 | ONSHORE | WV | 26241 | ELKINS | RANDOLPH | MILEPOST | 18862 | LINE 8223 | 8223-010 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [22 empty] | INTERSTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | PIPE | PIPE BODY | 8 |  | 0.25 |  | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | NONE | [28 empty] | 1974 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | 2-IN TAP | [5 empty] | CLASS 3 LOCATION | NO |  | 67 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 273 | 244.161971830986 | 3000 | 3278.67136194918 | 0 | 0 | 0 | 0 |  |  | 3273 | 1758.13047170431 | 3522.83333378016 | [8 empty] | 147 |  | 150 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 3 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | [10 empty] | NO |  |  |  |  | YES | [6 empty] | UTILITY | BACKHOE/TRACKHOE | NATURAL GAS | YES | 1525273220 |  | UTILITY OWNER | YES | YES | YES | 4 | LOCATING PRACTICES NOT SUFFICIENT |  | INCORRECT FACILITY RECORDS/MAPS | [264 empty] | CHRIS LEGG | US REGULATORY COMPLIANCE SPECIALIST | chris_legg@transcanada.com | (304) 722-8530 |  |  |  |  | LEE ROMACK | MANAGER | (832) 320-5315 | lee_romack@transcanada.com | ON SEPTEMBER 16, 2015, A COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA) TRANSMISSION PIPELINE WAS SUBJECT TO UNINTENDED RELEASE OF NATURAL GAS (MATERIAL) INTO ATMOSPHERE DUE TO A DAMAGE TO AN OLD TAP BY COLUMBIA PERSONNEL. THE SITE WAS UNDERWORK IN PREPARATIONS FOR A NEW TAP. THE MATERIAL DID NOT IGNITE AND THE COLUMBIA PERSONNEL NOTIFIED THE LOCAL EMERGENCY RESPONDERS (TO SECURE THE AREA) AND THE MONITORING CENTER. EMERGENCY VALVES WERE OPERATED TO ISOLATE THE AFFECTED SEGMENT. AFTER ISOLATING THE AFFECTED SEGMENT, NECESSARY REPAIR STEPS WERE IMPLEMENTED WHERE A PRE-TESTED PIPE WAS INSTALLED. THE PIPELINE WAS REPAIRED, PURGED AND RETURNED TO SERVICE AFTER APPROXIMATELY FOUR HOURS OF DISRUPTED SERVICE AND THE LOCAL DISTRIBUTION COMPANY (LDC) RE-ESTABLISHED SERVICE TO THEIR CUSTOMERS. AN INVESTIGATION WAS INITIATED TO IDENTIFY THE CAUSAL FACTORS LEADING TO THE DAMAGE OF THE OLD TAP AND HOW IT CAN BE PREVENTED FROM RE-OCCURRING IN SIMILAR FUTURE APPLICATIONS. EVEN THOUGH THE TOTAL AMOUNT OF MATERIAL UNINTENTIONALLY RELEASED INTO ATMOSPHERE AND COST OF DAMAGES DID NOT EXCEED THE REPORTING THRESHOLD, COLUMBIA REPORTED THIS EVENT AS AN INCIDENT DUE TO THE NUMBER OF LDC CUSTOMERS AFFECTED BY THIS DISRUPTION OF SERVICE. SUPPLEMENTAL INFORMATION: ON 10/19/2015 AS A FOLLOW-UP TO THE INCIDENT, AN INTERNAL COLUMBIA PIPELINE GROUP "SAFETY ALERT" WAS RELEASE TO CPG EMPLOYEES DESCRIBING THE EVENT AND WARNING EMPLOYEES TO USE CAUTION WHEN MECHANICALLY EXCAVATING, PARTICULARLY AROUND STOPPLE FITTINGS AND TO SUSPECT, AND WATCH FOR SIDE CONNECT BYPASSES.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150124 | 16923 | 2015-10-15 15:52 | SUPPLEMENTAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2015-09-17 15:22 | 2015 |  |  | 33.1577 | -92.7288 | 1128754 | 2015-09-17 16:10 |  | NATURAL GAS |  | 0.5 | 50 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | NO, INSTALLED STOPPALS | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-09-17 11:15 | 2015-09-16 17:13 | ONSHORE | AR | 71731 | Not Within a Municipality | UNION | SURVEY STATION NO. | 389+10 | LINE KT-1 | ROUTE 7 SERIES 1330 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 12 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1953 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | BRASS | LEAK |  |  | OTHER | THREADS AND STEM LEAKING | [5 empty] | CLASS 3 LOCATION | NO |  | 141 |  | NO | NO | NO |  | 0 | 0 | 150 | 163.933568097459 | 2 | 1.7887323943662 | 350000 | 382511.658894071 | 1000 | 1092.89045398306 | 0 | 0 |  |  | 351152 | 176161.714553365 | 383770.271648546 | [8 empty] | 315 |  | 420 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 81 | NO |  | YES |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | LOCAL DISTRIBUTION COMPANY |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SMALL LEAK THAT WOULD NOT HAVE REGISTERED ON SCADA SYSTEM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [64 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | [10 empty] | YES | YES | COUNTY ROAD | [9 empty] | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO | [7 empty] | PREVIOUS DAMAGE | [266 empty] | JIMMY CROSS | DOT COMPLIANCE MANAGER | jimmy.cross@enablemidstream.com | 3184293664 |  |  |  |  | JOHNNY CAVITT | SENIOR MANAGER DOT COMPLIANCE | 3184293606 | johnny.cavitt@enablemidstream.com | ON 9/16/15 AT 17:33 AN ENABLE EMPLOYEE WITH THE EL DORADO DISTRICT REPORTS A POSSIBLE LEAK WAS FOUND DURING A LOCAL DISTRIBUTION COMPANY LEAK SURVEY OF THEIR PIPELINE. THE ENABLE EMPLOYEE REPORTED THE POSSIBLE LEAK TO SYSTEM CONTROL. ENABLE'S KT-1, THE DISTRIBUTION COMPANY AND 2 FOREIGN PIPELINES ARE NEAR THE POSSIBLE LEAK. THE ENABLE EMPLOYEE COULD NOT CONFIRM WHICH OF THE 4 PIPELINES IN THE AREA IS LEAKING. LEAK INDICATIONS WERE SMALL. ON 9/17/15 11:15 ENABLE EMPLOYEES CONFIRMED KT-1 IS LEAKING TO SYSTEM CONTROL. AT 15:22 LOCAL EMPLOYEES CALCULATED AND PROVIDED SYSTEM CONTROL A COST ESTIMATE FOR REPAIRS OF $300,000. ON 9/17/15 16:10 SYSTEM CONTROL NOTIFIED THE NRC (REPORT # 1128754) AFTER DECIDING AND DETERMINING THEY WOULD REPLACE THE CROSSING. ON 9/19/2015 PERFORMED A LINE STOP TO ELIMINATE THE LEAKING VALVE AND PIPE CROSSING. THE CROSSING PIPE WAS LEFT IN PLACE AND A NEW SECTION OF PIPE WAS INSTALLED ADJACENT TO THE EXISTING PIPELINE CROSSING.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150125 | 16937 | 2015-10-16 16:31 | SUPPLEMENTAL FINAL | 38987 | KINETICA ENERGY EXPRESS LLC | 1001 MCKINNEY STREET, SUITE 900 | HOUSTON | TX | 77002 | 2015-09-17 17:45 | 2015 |  |  | 29.6324 | -93.0383 | 1128765 | 2015-09-17 18:30 |  | NATURAL GAS |  | 260 | 6900 | 0.1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-09-17 18:53 | 2015-11-04 16:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-09-17 17:45 | 2015-09-17 18:15 | OFFSHORE | [28 empty] | 33 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST CAMERON | 68 | SPLASH ZONE OF RISER | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 20 |  | 0.5 | 42000 | X-42 | DSAW |  | NATIONAL TUBE | OTHER | CONCRETE COATING ON SUB-SEA RISER THROUGH SPLASH ZONE | [27 empty] | 1970 | 1962 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO | NO |  | 0 | 0 | 17250 | 18852.3603312078 | 650 | 581.338028169014 | 250000 | 273222.613495765 | 3000 | 3278.67136194918 | 50000 | 54644.5226991529 | BLOWDOWN/FLARE EQUIPMENT |  | 320900 | 161261.093934247 | 350579.505916244 | [8 empty] | 726 |  | 999 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 69484 | NO |  |  | YES |  |  |  |  | YES |  |  |  |  | YES | TOOL WILL NOT FIT IN LAUNCHER | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE WAS OPERATING WELL BELOW MOP/MAOP. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  |  | YES | [7 empty] | YES | YES |  |  | NO | [11 empty] | YES | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KURT CHERAMIE | SR. DIRECTOR | kurt.cheramie@kineticallc.com | 985-209-2283 |  |  |  |  | KURT CHERAMIE | SR. DIRECTOR | 985-209-2283 | kurt.cheramie@kineticallc.com | ON 9/17, FIELDWOOD FIELD SUPPLY BOAT OBSERVED A LEAK ON KINETICA'S WC 68CG PLATFORM. KINETICA PERSONNEL DISPATCHED AND CONFIRMED LEAK ON THE 20" RISER AT THE +3' ELEVATION. KINETICA PERSONNEL CLOSED BLOCK VALVE ON THE PLATFORM TO ISOLATE LEAK FROM ALL PRODUCTION. KINETICA LAND PERSONNEL DISPATCHED TO CLOSE BLOCK VALVE LOCATED ONSHORE TO COMPLETELY ISOLATE PIPELINE. KINETICA BEGAN OBTAINING NECESSARY BLOWDOWN/FLARE EQUIPMENT IN ORDER TO EVACUATE PRESSURE FROM LINE. ON 9/23, WHILE EQUIPMENT WAS BEING SET UP TO PREPARE FOR EVACUATION OF LINE, CONDENSATE BEGAN TO MIST FROM THE LEAK LOCATION CAUSING A SLIGHT SILVERY SHEEN. BLOWDOWN/FLARING OF GAS FROM THE LINE BEGAN AT NOON ON 9/23 (675PSIG). MISTING AND SHEEN CONTINUED UNTIL PRESSURE WAS REDUCED TO 78PSIG ON THE MORNING OF 9/24. JACK-UP BOAT AND DIVERS WERE LOCATED AND DISPATCHED TO WC 68CG PLATFORM TO EVALUATE LEAK. DUE TO LOCATION OF LEAK AT THE +3' ELEVATION ON RISER, WORK HAD TO BE PERFORMED DURING PERIODS OF CALM SEAS. ON 10/10, KINETICA CONTRACTOR COMPLETED THE REPAIR. ON 10/11, PIPELINE WAS PRESSURED-UP TO 300PSIG. KINETICA PERSONNEL DISCOVERED REPAIR LOCATION WAS LEAKING. BLOCK VALVE ON PLATFORM WAS CLOSED TO ONCE AGAIN ISOLATE PRODUCTION. PIPELINE EVACUATED OF PRESSURE. VESSEL AND CONTRACTOR LOCATED AND DISPATCHED TO LOCATION TO INITIATE REPAIRS. SUPPLEMENTAL REPORT WILL BE PREPARED AND SUBMITTED UPON COMPLETION OF REPAIR AND PLACEMENT OF PIPELINE BACK INTO SERVICE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150126 | 16941 | 2015-10-26 12:35 | SUPPLEMENTAL FINAL | 31451 | KINDER MORGAN TEXAS PIPELINE CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2015-10-03 01:00 | 2015 |  |  | 26.593 | -99.0868 | 1130001 | 2015-10-03 12:27 |  | NATURAL GAS |  | 17714 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | OPERATOR ISOLATED THE COMPRESSOR AND UNIT RELIEF VALVE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-10-03 02:00 | 2015-10-03 02:50 | ONSHORE | TX | 78545 | Not Within a Municipality | STARR | SURVEY STATION NO. | 123+33 | BOB WEST COMPRESSOR STATION / STA #582 | NA | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2014 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE PILOT BROKE (VIBRATION); RELIEF VALVE VENTED; | CLASS 1 LOCATION | NO |  | 687 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 42444 | 37960.4788732394 | 2000 | 2185.78090796612 | 100 | 109.289045398306 | 0 | 0 |  |  | 44544 | 40408.8497808972 | 40255.5488266039 | [8 empty] | 1000 |  | 1100 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DISCHARGE RELIEF VALVE PILOT BROKE (VIBRATION WAS CAUSE); DISCHARGE RELIEF VALVE VENTED; CONTROL ROOM ACTIONS WERE NOT PART OF THE CAUSE; | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [13 empty] | YES | [177 empty] | WILLIAM MARTIN MULLER | SPECIALIST-PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205 325 3863 |  |  |  |  | REJI GEORGE | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713 420 5433 | reji_george@kindermorgan.com | KMTP BOB WEST COMPRESSOR STATION, 10/03/2015 (SATURDAY), APPROXIMATELY 1:00 AM, PILOT TUBING ON THE DISCHARGE RELIEF VALVE FOR COMPRESSOR UNIT #3 BROKE ALLOWING THE DISCHARGE RELIEF VALVE TO VENT NATURAL GAS TO ATMOSPHERE. LOCAL POLICE HEARD THE DISCHARGE RELIEF VALVE VENTING AND CONTACTED KMTP GAS CONTROL. NOTIFICATIONS WERE MADE BY KMTP GAS CONTROL. LOCAL POLICE ARRIVED AT BOB WEST COMPRESSOR STATION APPROXIMATELY 2:00 AM AND LOCAL FIRE DEPARTMENT ARRIVED AT BOB WEST COMPRESSOR STATION APPROXIMATELY 2:15 AM; HOWEVER THERE WAS NO FIRE AND NO EVACUATION NECESSARY. KMTP STATION OPERATOR ARRIVED AT BOB WEST COMPRESSOR STATION AT 2:50 AM AND VERIFIED THE RELIEF VALVE WAS VENTING. AT 3:00 AM, KMTP STATION OPERATOR HAD COMPRESSOR #3 ISOLATED; VENTING CEASED. PILOT OF DISCHARGE RELIEF VALVE HAS BEEN REPAIRED. DISCHARGE RELIEF VALVE HAS BEEN INSPECTED AND TESTED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150127 | 16914 | 2015-10-28 07:50 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2015-10-10 08:15 | 2015 |  |  | 40.3641 | -74.6827 | 1130535 | 2015-10-10 09:15 |  | NATURAL GAS |  | 6271 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-10-10 11:20 | 2015-10-10 17:14 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-10-10 08:47 | 2015-10-10 09:40 | ONSHORE | NJ | 08540 | PRINCETON | MECER | MILEPOST | 1776.75 | MAINLINE B COVENTRY FARMS | MLV J951 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | TUBING | [38 empty] | 2015 |  | CARBON STEEL |  | OTHER | [8 empty] | OPERATOR TECHNICIANS INTENTIONALLY CUT A VALVE GREASE LINE DURING A MODIFICATION PROCESS. AN INTERNAL VALVE COMPONENT (CHECK VALVE) FAILED ALLOWING GAS TO ESCAPE. | CLASS 2 LOCATION | NO |  | 660 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 15700 | 14041.5492957746 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 15700 | 14557.5117370892 | 14041.5492957746 | [8 empty] | 721 |  | 800 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | AUTOMATIC | 17688 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | A MODIFICATION TO A VALVE INVOLVED CUTTING A VALVE GREASE LINE. THE VALVE BODY WAS BLOWN DOWN OF ALL GAS BUT AN INTERNAL CHECK VALVE FAILED AND ALLOWED GAS TO ESCAPE FROM THE GREASE LINE. THE AFFECTED GAS LINE SEGMENT WAS ISOLATED UNTIL THE LINE WAS COMPLETELY BLOWN DOWN, THE GREASE LINE WAS REPAIRED AND THE AFFECTED GAS LINE SEGMENT WAS PRESSURED UP AND PUT BACK INTO SERVICE. | [147 empty] | JOHNNY LOPEZ | REGULATORY COMPLIANCE SPECIALIST | johnny.lopez@williams.com | 7132152995 | 7132152000 |  |  |  | MARIE SOTAK | MANAGER PIPELINE SAFETY | 7132152111 | marie.sotak@williams.com | DUE TO THE LOCATION OF A VALVE ON A MAINLINE TRANSMISSION SYSTEM AN ATTACHED VALVE GREASE LINE HAD TO BE EXTENDED. A FUNCTION OF THE MODIFICATION PROCESS INCLUDED CUTTING THE GREASE LINE. WHEN THE GREASE LINE WAS CUT AN INTERNAL VALVE COMPONENT FAILED ALLOWING GAS TO ESCAPE, THE TRANSMISSION LINE SEGMENT WAS ISOLATED AND THE GREASE LINE WAS REPAIRED WITH A COUPLING. AFTER THE VALVE GREASE LINE WAS REPAIRED THE TRANSMISSION LINE SEGMENT WAS PRESSURED UP AND PUT BACK IN SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150128 | 17305 | 2015-10-29 14:58 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2015-10-11 12:30 | 2015 |  |  | 32.376 | -93.3548 | 1130610 | 2015-10-11 14:22 |  | NATURAL GAS |  | 21822 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | FLOW REROUTED AND PRESSURE REDUCED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-10-11 12:30 | 2015-10-11 13:00 | ONSHORE | LA | 71008 | RINGGOLD | BIENVILLE | MILEPOST | 20+93 | BISTINEAU STORAGE FIELD INDEX 901-6 | B-LATERAL, B8 WELL LINE | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10.75 |  | 0.344 | 60000 | API 5L | SEAMLESS |  | US STEEL | COAL TAR | [28 empty] | 1966 | 1966 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 96 | 12 |  | CLASS 1 LOCATION | NO |  | 322 |  | NO | NO | NO |  | 5000 | 5464.45226991529 | 0 | 0 | 56312 | 50363.5492957746 | 120000 | 131146.854477967 | 2500 | 2732.22613495765 | 0 | 0 |  |  | 183812 | 116176.536831471 | 189707.082178615 | [8 empty] | 2100 |  | 2160 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 2513 | NO | [5 empty] | YES | WELL LINE AND NOT SET UP FOR INTERNAL INSPECTION TOOLS. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  | YES |  |  |  |  | YES | [7 empty] | YES | BOTTOM OF PIPE BUT NOT NECESSARILY THE LOW POINT | YES | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | SHANNON MATTINGLY | PA OQ AND EVENT SUPPORT PROGRAM LEADER | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 2706886361 | jeff.mcmaine@bwpmlp.com | GULF SOUTH EXPERIENCED A FAILURE ON ITS INDEX 901-6 LATERAL LINE IN BIENVILLE PARISH, LA NEAR RINGGOLD. THE ROOT CAUSE OF THE EVENT APPEARS TO BE INTERNAL CORROSION. 3-23-17 THIS UPDATE IS PROVIDED AT PHMSA'S REQUEST. REPAIR WAS MADE IN THE FORM OF PIPE REPLACEMENT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150129 | 17233 | 2015-10-30 10:10 | SUPPLEMENTAL FINAL | 31531 | ONEOK WESTEX TRANSMISSION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2015-10-01 15:05 | 2015 |  |  | 32.305 | -101.7102 | 1129881 | 2015-10-01 15:56 |  | NATURAL GAS |  | 3624 | 452 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-10-01 16:08 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-10-01 15:05 | 2015-10-01 15:26 | ONSHORE | TX | 79782 | Not Within a Municipality | MARTIN | MILEPOST | 54 | 800-000 | 800-000 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 35 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 |  | 0.22 | 24000 | UNKNOWN | LAP WELDED |  | REPUBLIC STEEL | COAL TAR | [28 empty] | 1930 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | 4 INCH DIA CORRODED AREA | [5 empty] | CLASS 1 LOCATION | NO |  | 115 |  | NO | NO | NO |  | 0 | 0 | 1284 | 1403.27134291425 | 10292 | 9204.81690140845 | 200000 | 218578.090796612 | 1000 | 1092.89045398306 | 0 | 0 |  |  | 212576 | 111021.967032933 | 230279.069494918 | [8 empty] | 350 |  | 428 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 51744 | NO | YES | YES | [5 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CORRECT RESPONSE BY CONTROL ROOM OPERATORS TO THE SITUATION. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | YES |  |  | YES | YES |  |  |  | 2015 |  |  |  | NO | [190 empty] | NO | [63 empty] | YES | 1956 | 420 | NO | [13 empty] | NO | [63 empty] | PATRICK VAUGHAN | MANAGER REGULATORY COMPLIANCE | pat.vaughan@oneok.com | 918-588-7734 | 918-5915032 |  |  |  | WES DUNBAR | VP NATURAL GAS PIPELINE OPERATIONS | 918-588-7424 | wesley.dunbar@oneok.com | ON OCTOBER 1, 2015, THE OPERATING PRESSURE ON PARALLEL LINES 800-000 AND 801-000 APPEARED TO THE CONTROL ROOM OPERATORS TO BE LOWER THAN EXPECTED. FIELD OPERATIONS PERSONNEL CONFIRMED GAS VENTING TO ATMOSPHERE ON LINE 800-000. THE PIPELINE IS IN A LOW WET AREA THAT HAS PREVENTED CLOSE EXAMINATION OF THE FAILURE BEYOND A SINGLE PHOTOGRAPH OF THE PIPE BEFORE BEING COVERED BY GROUND WATER. LINE 800-000 WILL REMAIN OUT OF SERVICE UNTIL A REPAIR METHOD HAS BEEN DETERMINED. LINE 801-000 WILL REMAIN IN SERVICE. SUPPLEMENTAL - THE FAILURE SITE BECAME ACCESSIBLE AND THE PIPELINE WAS REPAIRED BY INSTALLING A CYLINDER OF TESTED PIPE. EXTERNAL CORROSION WAS CONFIRMED TO BE THE CAUSE OF THE FAILURE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150130 | 17576 | 2015-11-04 08:21 | SUPPLEMENTAL | 32037 | PITT LANDFILL GAS, LLC | 10600 NATIONS FORD RD SUITE 150 | CHARLOTTE | NC | 28273 | 2015-08-14 08:00 | 2015 |  |  | 35.6053 | -77.4117 | NRC NOTIFICATION NOT REQUIRED |  |  | LANDFILL GAS |  | 390 | 9 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-08-21 | 2015-08-21 08:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-08-14 08:00 | 2015-08-21 | ONSHORE | NC | 27834 | GREENVILLE | PITT | MILEPOST | 1.56 MILE MAR | PITT LANDFILL GAS | PITT LANDFILL GAS | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 72 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | REPAIR SLEEVE OR CLAMP | [38 empty] | 1998 |  | PLASTIC |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | NO |  | 65 |  | NO | NO | NO |  | 0 | 0 | 5 | 5.4644522699153 | 1100 | 983.802816901409 | 25000 | 27322.2613495765 | 0 | 0 | 0 | 0 |  |  | 26105 | 13564.1002868197 | 28311.5286187478 | [8 empty] | 6 |  | 60 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 10900 | YES | [7 empty] | YES |  | YES |  |  | YES | PLASTIC PIPE, NO ACCESS EXCEPT AT ENDS | TRANSMISSION SYSTEM | NO |  |  |  |  | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | OTHER | FAILURE OF ELECTROFUSION JOINT WHERE PIPE WAS CONNECTED. | [6 empty] | YES | [172 empty] | TIMOTHY L KEESLING | EHS AND ENGINEERING DIRECTOR | timothy.keesling@landfillgroup.com | 7048448990 | 7048448994 |  |  |  | WILLIAM P. BRINKER | MANAGER OF THE LLC | 7048448990 | william.brinker@landfillgroup.com | LINE IS A LOW PRESSURE (6 PSIG) LINE THAT TRANSMITS LANDFILL GAS (LFG) APPROXIAMTELYK 11,000 FEET FROM THE LANDFILL TO A HOSPITAL BOILER ROOM. EVIDENCE OF LEAK WAS FOUND DURING A LINE WALK IN Q4 2014. SEVERAL ATTEMPTS WERE MADE IN Q1 OF 2015 TO FIND AND REPAIR THE LEAK. LEAK WAS FOUND IN Q3 2015 UNDER SIDEWALK IMMEDIATELY ADJACENT TO BUSY ROADWAY. LEAK WAS REPAIRED WHEN FOUND. LEAK APPEARS TO HAVE BEEN FROM A PREVIOUS REPAIR (HDPE ELECTROFUSION FITTING WAS FOUND TO BE LEAKING).
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20150131 | 16917 | 2015-11-04 18:58 | SUPPLEMENTAL FINAL | 32296 | TARGA RESOURCES OPERATING LLC | 811 LOUISIANA ST SUITE 2100 | HOUSTON | TX | 77002 | 2015-10-09 09:30 | 2015 |  |  | 28.673 | -90.1568 | 1130473 | 2015-10-09 10:30 |  | NATURAL GAS |  | 400 | 10 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-10-05 13:00 | 2015-11-10 09:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-10-05 16:12 | 2015-10-05 16:12 | OFFSHORE | [28 empty] | 140 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SOUTH TIMBALIER | 131 | SPLASH ZONE OF RISER | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 8.625 |  | 0.5 | 35000 | API 5L | SEAMLESS |  | UNKNOWN | COMPOSITE | [28 empty] | 1977 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 170 |  | NO | NO | NO |  | 0 | 0 | 30 | 32.7867136194918 | 1200 | 1073.23943661972 | 492000 | 537702.103359665 | 0 | 0 | 0 | 0 |  |  | 493230 | 247947.179720562 | 538808.129509904 | [8 empty] | 820 |  | 1440 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 4500 | NO | YES |  | YES |  |  |  |  | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | NO |  |  |  |  | OTHER | PLATFORM OPERATOR PERSONNEL NOTIFIED COMPANY |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  |  | YES | [7 empty] | YES |  |  |  | NO | [11 empty] | YES | NO | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | TIM HUFFER | MANAGER REGULATORY COMPLIANCE | thuffer@targaresouces.com | (337) 583-4642 | 3375834630 |  |  |  | TIM HUFFER | MANAGER REGULATORY COMPLIANCE | (337) 583-4642 | thuffer@targaresources.com | TARGA RECEIVED NOTIFICATION OF A POTENTIAL LEAK ON A RISER TO THE PLATFORM AT ST 131 ON 10/5/2015. TARGA RESPONDED AND IDENTIFIED THE LEAK AS ORIGINATING FROM TARGA'S 8 INCH PIPELINE RISER. TARGA CLASSIFIED THE LEAK AS A NON-REPORTABLE INCIDENT BECAUSE THE VOLUME OF GAS LOST AND COST OF PROPERTY DAMAGE AND REPAIR WOULD NOT MEET THE LEVEL REQUIRED TO CLASSIFY AS AN INCIDENT. UPON ADDITIONAL EVALUATION OF THE COST TO REPAIR, TARGA DETERMINED ON OCTOBER 9, 2015 THAT THE COST TO REPAIR THE PIPELINE WOULD EXCEED $50,000 AND REPORTED THE LEAK AS AN INCIDENT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150132 | 17336 | 2015-11-05 20:11 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2015-10-07 19:30 | 2015 |  |  | 41.2684 | -83.4531 | 1130361 | 2015-10-07 21:44 |  | NATURAL GAS |  | 883 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-10-07 20:32 | 2015-10-08 06:52 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-10-07 20:10 | 2015-10-07 20:10 | ONSHORE | OH | 43457 | RISING SUN | WOOD | MILEPOST | D533-102 | LINE D-533 | D533-102 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 8 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 2 |  | 0.125 | 24000 | UNKNOWN | OTHER | UNKNOWN | UNKNOWN | NONE | [28 empty] | 1950 | 1950 | CARBON STEEL |  | LEAK |  |  | OTHER | DAAMGE DUE TO FARM ACTIVITIES | [5 empty] | CLASS 1 LOCATION | NO |  | 25 |  | NO | NO | NO |  | 0 | 0 | 500 | 546.445226991529 | 2110 | 1887.11267605634 | 7000 | 7650.23317788141 | 0 | 0 | 0 | 0 | NO OTHER ASSOCIATED COSTS |  | 9610 | 5718.94707127956 | 10083.7910809293 | [8 empty] | 119 |  | 140 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL |  | NO | YES | [6 empty] | YES |  | YES |  |  |  |  | TRANSMISSION SYSTEM | NO |  |  |  |  | OTHER | LOCAL DISTRIBUTION COMPANY NOTIFICAITON TO COMPANY'S MONITORING CENTER |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [260 empty] | GEORGE HAMATY | ENGINEER | george_hamaty@transcanada.com | (304) 357-3728 |  |  |  |  | LEE ROMACK | MANAGER | (832) 320-5315 | lee_romack@transcanada.com | ON OCTOBER 7TH, 2015, THE MONITORING CENTER CALLED TO DISPATCH A COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA) PIPELINE MECHANIC TO INVESTIGATE A REPORTED NATURAL GAS (MATERIAL) LEAK ON A COLUMBIA PIPELINE. THE PIPELINE IDENTIFIED AS LINE D-533, IS A TRANSMISSION LINE, 3-IN IN DIAMETER LOCATED IN WOOD COUNTY, OHIO, NEAR THE VILLAGE OF RISING SUN. AFTER FURTHER INVESTIGATION, THE REPORTED RELEASE WAS FOUND TO BE FROM A DAMAGED 2-IN PIPELINE APPARENTLY BY A THIRD PARTY (LANDOWNER) WHILE FARMING HIS LAND. THIS DAMAGE TO LINE D-533 CAUSED THE LOSS OF 270 CUSTOMERS THAT ARE SERVICED BY THE LOCAL DISTRIBUTION COMPANY (LDC) DOWNSTREAM OF THE FAILURE POINT. ALL EFFORTS WERE MADE BY COLUMBIA AND THE LDC PERSONNEL TO MAINTAIN MATERIAL FLOW TO THE LINE IN A SHORT TIMEFRAME. AFTER PERFORMING THE NECESSARY ENGINEERING ASSESSMENT TO THE DAMAGED LINE, A PRE-TESTED PIPE WAS INSTALLED AND THE SERVICE TO LINE D-533 WAS RE-ESTABLISHED IN A SHORT TIMEFRAME. EVEN THOUGH THE TOTAL AMOUNT OF MATERIAL VENTED INTO ATMOSPHERE WAS LESS THAN 3,000 MCF (883.0 MCF) WITH THE TOTAL COST OF LABOR PLUS MATERIAL REACHING A TOTAL VALUE LESS THAN $50,000, COLUMBIA ELECTED TO REPORT THIS EVENT AS AN INCIDENT DUE TO THE LARGE NUMBER OF LDC CUSTOMERS THAT LOST THEIR SERVICE FOR A BRIEF AMOUNT OF TIME. THE LINE WAS REPAIRED AND SERVICE WAS RESUMED TO THE AFFECTED LDC CUSTOMERS. COLUMBIA REACHED OUT TO THE FARMER (BEING PART OF THE PUBLIC AWARENESS PROGRAM) ABOUT THE SIGNIFICANCE OF FARMING ON OR NEAR AN ACTIVE TRANSMISSION LINE AND TO EXERCISE CAUTION WHILE FARMING/HARVESTING CROP WITHIN THE RIGHT-OF-WAY IDENTIFYING THE INSTALLED LINE MARKERS. THIS STEP WILL HELP AVOID SIMILAR DAMAGE FROM RE-OCCURRING IN THE FUTURE TO THE SAME PIPELINE AND OTHER PIPELINES.
2021-02-26 10:37 | YES | YES | GT (Gas Transmission) | 20150133 | 17104 | 2015-11-06 14:55 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2015-10-08 11:00 | 2015 |  |  | 29.6031 | -90.8748 | 1130404 | 2015-10-08 12:06 |  |  |  | 0 | 0 | 0 | YES | 0 | 4 | 0 | 0 | 0 | 4 | YES | 0 | 1 | 0 | 0 | 0 | 1 |  | NO | FACILITY WAS OUT OF SERVICE FOR MAINTENANCE AT THE TIME OF THE INCIDENT | [6 empty] | YES |  |  |  |  | YES | [6 empty] | 0 | 2015-10-08 11:00 | 2015-10-08 11:11 | ONSHORE | LA | 70356 | GIBSON | TERREBONNE PARISH | MILEPOST | COMPRESSOR | TRANSCO COMPRESSOR STATION 62 | SLUG CATCHER | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | FILTER/STRAINER/SEPARATOR | [38 empty] | 1989 |  | CARBON STEEL |  | OTHER | [8 empty] | IGNITION OF VAPOR DURING SLUG CATCHER MAINTENANCE | CLASS 2 LOCATION | NO |  | 434 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 3320860 | 3629336.19301418 | 451662 | 493617.088226896 | 3772522 | 4122953.28124108 | LOST REVENUE |  | 7545044 | 3785088.69553631 | 8245906.56248216 | [8 empty] | 0 |  | 990 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE CONTROL WAS NOT INVOLVED WITH THE INCIDENT AS THE FACILITY WAS SHUT DOWN FOR MAINTENANCE. | [12 empty] | YES | 11 | 0 | YES | 6 | 1 | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | [204 empty] | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | [5 empty] | YES |  |  | OTHER MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | SHANE FRASIER | PIPELINE SAFETY ENGINEER | shane.frasier@williams.com | (713) 215-3051 |  |  |  |  | JOHN SUCHAR | DIRECTOR EMPLOYEE SAFETY | (918) 573-2649 | john.suchar@williams.com | WILLIAMS PERSONNEL AND CONTRACTORS WERE PERFORMING MAINTENANCE ACTIVITIES ALONG THE LIQUID DISTRIBUTION HEADER OF THE SLUG CATCHER LOCATED AT THE TRANSCO COMPRESSOR STATION 62, LOCATED IN THE TERREBONNE PARRISH, LA. DURING THE MAINTENANCE THERE WAS AN UNINTENTIONAL IGNITION THAT OCCURRED WHILE PERFORMING HOT WORK ACTIVITIES ON A 3" WATER DRAW LINE ON THE EASTERN END OF THE LIQUID DISTRIBUTION HEADER. THE WELDING ACTIVITY AT THIS LOCATION IS BELIEVED TO BE THE SOURCE OF THE IGNITION, ACCORDINGLY A 3" FOREMAN'S PLUG THAT WAS USED DURING THE WELDING ACTIVITY AT THIS LOCATION DID NOT FUNCTION AS INTENDED. THE EXACT SOURCE OF THE VAPOR THAT IGNITED CANNOT BE DETERMINED AS THERE ARE MULTIPLE POSSIBLE SUPPLY POINTS. THERE WERE THREE CONFIRMED FATALITIES AT THE SCENE, AND TWO INDIVIDUALS HOSPITALIZED WITH SERIOUS BURNS. ONE OF THE HOSPITALIZED INDIVIDUALS LATER PASSED AWAY AT THE HOSPITAL.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150134 | 17030 | 2015-11-09 18:05 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2015-10-10 05:37 | 2015 |  |  | 41.8023 | -85.5867 | 1130580 | 2015-10-10 21:24 |  | NATURAL GAS |  | 13500 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE STATION MECHANIC CLOSED A REDUNDANT VALVE STOPPING THE GAS FLOW | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-10-10 05:37 | 2015-10-10 06:02 | ONSHORE | MI | 49099 | WHITE PIGEON | SAINT JOSEPH | MILEPOST | 638 | WHITE PIGEON COMPRESSOR STATION | PLANT #3 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | OTHER | FIREGATE BLOWDOWN VALVE |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2010 |  | CARBON STEEL |  | OTHER | [8 empty] | FIREGATE VALVE FAILED SAFE IN THE OPEN POSITION RESULTING IN A RELEASE OF GAS | CLASS 1 LOCATION | NO |  | 172 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 100710 | 90071.6197183098 | 0 | 0 | 1778 | 1943.15922718188 | 0 | 0 |  |  | 102488 | 94273.299387263 | 92014.7789454917 | [8 empty] | 708 |  | 960 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS IDENTIFIED BY THE CONTROL ROOM REPRESENTATIVE AND THE APPROPRIATE NOTIFIFCATIONS WERE MADE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | A FAILED OPERATOR RESULTING FROM A BLOWN FUSE IN THE ACTUATOR CAUSED THE VALVE TO PERFORMED AN UNINTENDED VALVE TRAVEL SEQUENCE CAUSING THE VALVE TO FAIL SAFE IN THE OPEN POSITION AND RELEASE GAS. | [22 empty] | YES | INCORRECT FUSE INSTALLED DURING MANUFACTURING | [161 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST I | carmella.king@cmsenergy.com | 571-788-0509 |  |  |  |  | AMANDA L. WARD | GAS REGULATORY SERVICES LEAD | 517-545-8746 | amanda.ward@cmsenergy | ON SATURDAY, OCTOBER 10, 2015 AT APPROXIMATELY 05:37 CONSUMERS ENERGY GAS CONTROL REPRESENTATIVE RECEIVED AN ALARM AT THE WHITE PIGEON COMPRESSOR STATION IDENTIFYING A POTENTIAL PROBLEM WITH THE EMERGENCY SHUT-DOWN SYSTEM (ESD) IN PLANT #3. THE WHITE PIGEON COMPRESSOR STATION IS LOCATED IN WHITE PIGEON, MICHIGAN (ST. JOSEPH COUNTY) A STATION MECHANIC ARRIVED AT THE LOCATION AT APPROXIMATELY 06:02 AND OBSERVED GAS BLOWING FROM FIREGATE VALVE #638. THE MECHANIC MANUALLY CLOSED THE REDUNDANT VALVE, VALVE #639 SHUTTING DOWN THE BLOWING GAS AT APPROXIMATELY 06:09. THERE WERE NO INJURIES OR SIGNIFICANT PROPERTY DAMAGE ASSOCIATED WITH THE GAS RELEASE. SUBSEQUENT INVESTIGATION OF THE INCIDENT DETERMINED A FAILED OPERATOR RESULTING FROM A BLOWN FUSE IN THE ACTUATOR CAUSED THE VALVE TO PERFORMED AN UNINTENDED VALVE TRAVEL SEQUENCE CAUSING THE VALVE TO FAIL SAFE IN THE OPEN POSITION AND RELEASE GAS. CONSUMERS ENERGY IS CONTINUING TO COLLABORATE WITH THE ROTORK REPRESENTATIVE TO EXPLORE EQUIPMENT DESIGN OPTIONS TO PROVIDE AN ADVANCE TROUBLE INDICATION WITHOUT INADVERTENTLY PERFORMING AN IMMEDIATE ESD ON FAILURE OF THE FUSE. ADDITIONAL INTERNAL MEASURES HAVE ALSO BEEN PUT IN PLACE TO MINIMIZE THE POTENTIAL FOR RE-OCCURRENCE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150135 | 17021 | 2015-11-13 12:16 | SUPPLEMENTAL FINAL | 22476 | ATMOS ENERGY CORPORATION - KY/MID-STATES (KENTUCKY) | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2015-10-16 11:30 | 2015 |  |  | 38.1911 | -85.3011 | 1131004 | 2015-10-16 12:53 |  | NATURAL GAS |  | 16500 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | BYPASS WAS BUILT AROUND DAMAGED LINE TO MAINTAIN SERVICE TO 12,500 CUSTOMERS | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 15 | 2015-10-16 11:00 | 2015-10-16 11:22 | ONSHORE | KY | 40065 | SHELBYVILLE | SHELBY | SURVEY STATION NO. | LKSURV968 | PIM9013308 | N/A | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 50 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 |  | 0.188 | 42000 | N/A | SEAMLESS |  | N/A | EPOXY | [28 empty] | 1974 | 1973 | CARBON STEEL |  | MECHANICAL PUNCTURE | 2 | 4 | [7 empty] | CLASS 1 LOCATION | NO |  | 110 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 54058 | 48347.6478873239 | 93766 | 102475.966308176 | 40185 | 43917.8028933092 | 0 | 0 |  |  | 188009 | 117322.804809313 | 194741.417088809 | [8 empty] | 380 |  | 394 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 350 | NO |  |  |  | YES |  |  |  | YES |  |  |  |  | YES | PIPELINE NOT SET UP FOR INTERNAL INSP. | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE OCCURRED DUE TO EXCAVATION DAMAGE TO PIPELINE (NO LOCATE WAS REQUESTED PRIOR TO EXCAVATION) | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  | YES | PRIVATE EASEMENT | YES | [6 empty] | FARMER | BACKHOE/TRACKHOE | DRAINAGE | NO | [7 empty] | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | GEORGE TUCKER | COMPLIANCE MANAGER | george.tucker@atmosenergy.com | 270-685-8137 | 270-685-8025 |  |  |  | GEORGE TUCKER | COMPLIANCE MANAGER | 270-685-8137 | george.tucker@atmosenergy.com | FARMER DAMAGED 8" LINE WILE CLEANING AND EXTENDING POND NEAR HIS PROPERTY. THE FARMER (PROPERTY OWNER) DID NOT CALL 811 TO HAVE FACILITIES LOCATED PRIOR TO EXCAVATION. MUELLER STOP FITTINGS WERE INSTALLED AND TEMPORARY BYPASS INSTALLED TO MAINTAIN GAS SERVICE. FIRST RESPONDERS AND ATMOS ENERGY EMERGENCY RESPONDERS WORKED CLOSELY TOGETHER TO PROTECT LIFE AND PROPERTY DURING THE ENTIRE REPAIR PROCESS. ATMOS ENERGY WAS ALSO ASSISTED BY 25-30 LARGE INDUSTRIAL CUSTOMERS TO HELP MAINTAIN GAS SERVICE TO 12,500 RESIDENTIAL AND SMALL COMMERCIAL CUSTOMERS.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150136 | 17239 | 2015-11-18 17:16 | SUPPLEMENTAL FINAL | 11824 | LOUISVILLE GAS & ELECTRIC CO | 220 W MAIN ST, PO BOX 32010 | LOUISVILLE | KY | 40202 | 2015-10-22 12:50 | 2015 |  |  | 37.9937 | -86.0663 | 1131519 | 2015-10-23 14:29 |  | NATURAL GAS |  | 8690 | 0 | 2 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-10-22 15:00 | 2015-12-09 12:40 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-10-22 14:45 | 2015-10-22 14:45 | ONSHORE | IN | 47135 | LACONIA | HARRISON | SURVEY STATION NO. | SEG ID 305885 | DOE RUN INDIANA 8" SOUTH | 305885 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [22 empty] | INTRASTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | PIPE | PIPE BODY | 8 |  | 0.188 | 35000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1984 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 24 | 6 |  | CLASS 1 LOCATION | NO |  | 96 |  | NO | NO | NO |  | 50 | 54.644522699153 | 0 | 0 | 26070 | 23316.1267605634 | 32160 | 35147.3570000952 | 630 | 688.520986009327 | 12000 | 13114.6854477967 | LIQUID AND SOIL CLEAN UP |  | 70910 | 46667.5708682475 | 72321.3347171637 | [8 empty] | 235 |  | 305 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PRESSURE ON THE PIPELINE IN QUESTION CANNOT BE CONTROLLED FROM THE CONTROL ROOM. FURTHERMORE, THERE WAS NO SPIKE IN PRESSURE ON THE PIPELINE LEADING UP TO THE FAILURE. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  | YES | YES | [5 empty] | YES |  |  |  |  | YES |  |  |  | NO | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | PETER CLYDE | MANAGER GAS REGULATORY COMPLIANCE | peter.clyde@lge-ku.com | 502-364-8715 |  |  |  |  | GREG CORNETT | ASSOCIATE GENERAL COUNSEL | 502-627-2756 | greg.cornett@lge-ku.com | A FAILURE ON A PIPE SEGMENT IN DOE RUN STORAGE FIELD, LOCATED DOWNSTREAM OF AN UNATTENDED FIELD COMPRESSOR, OCCURRED ON OCTOBER 22, 2015. REVIEW OF PRESSURE DATA RECORDED FOUND THE FIELD COMPRESSOR DISCHARGE PRESSURE DROPPED SUDDENLY AT APPROXIMATELY 12:50 PM RESULTING IN THE AUTOMATIC SHUTDOWN OF THE FIELD COMPRESSOR. AT APPROXIMATELY 2:15 PM A STORAGE FIELD MECHANIC WAS NOTIFIED BY A LOCAL RESIDENT OF A POTENTIAL ISSUE IN THE STORAGE FIELD. UPON INVESTIGATION THE FIELD MECHANIC FOUND GAS ESCAPING FROM A PIPE SEGMENT LOCATED DOWNSTREAM OF THE FIELD COMPRESSOR. THE FIELD MECHANIC ISOLATED THE PIPELINE SEGMENT AT APPROXIMATELY 3:23 PM STOPPING THE GAS RELEASE. NOTIFICATION WAS MADE TO THE INDIANA UTILITY REGULATORY COMMISSION AND PHMSA AFTER ENVIRONMENTAL CLEANUP OF THE SITE WAS COMPLETED AND EXCAVATION OF THE PIPE ENABLED DEFECT MEASUREMENTS PROVIDING THE BASIS FOR AN ENGINEERING ESTIMATE OF NATURAL GAS VOLUME RELEASED. THE FAILED PIPE SEGMENT WAS SENT TO A METALLURGICAL LAB FOR FAILURE ANALYSIS. THE RESULTS OF THE METALLURGICAL ANALYSIS INDICATE THAT THE FAILURE OCCURRED AT AN AREA OF WALL THINNING DUE TO INTERNAL CORROSION THAT FAILED BY DUCTILE OVERLOAD UNDER THE IMPOSED OPERATING PRESSURE. SIGNIFICANT WALL THINNING AT THE LOCATION OF THE RUPTURE LIKELY CORRESPONDED TO HISTORIC FLUID LINES. ADDITIONAL ANALYSIS PERFORMED ON LIQUID SAMPLES AND DEPOSITS FROM INSIDE OF THE PIPELINE, ALONG WITH A REVIEW OF THE GAS COMPOSITION DATA, POINT TOWARD THE INTERNAL CORROSION BEING CAUSED BY THE PRESENCE OF WATER, OXYGEN, CARBON DIOXIDE, AND HYDROGEN SULFIDE. THE OXYGEN IS SUSPECTED TO HAVE BEEN THE KEY DRIVER OF THE CORROSION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150137 | 17000 | 2015-11-18 17:19 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2015-10-30 09:50 | 2015 |  |  | 27.4805 | -97.2711 | 1132105 | 2015-10-30 10:20 |  | NATURAL GAS |  | 0.1 | 1930 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-10-30 11:07 | 2015-12-21 15:59 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-10-30 08:05 | 2015-10-30 08:05 | ONSHORE | TX | 78408 | CORPUS CHRISTI | NUECES | SURVEY STATION NO. | 361+24 | CLARKWOOD LATERAL #1 | 9A | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 60 |  | YES |  |  |  |  | YES | CASED | [16 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.219 | 52000 | API-5L X52 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1973 | 1973 | CARBON STEEL |  | LEAK |  |  | OTHER | UNKNOWN | [5 empty] | CLASS 4 LOCATION | YES | METHOD2 | 289 |  | NO | NO | NO |  | 0 | 0 | 4900 | 5355.16322451699 | 1 | 0.894366197183099 | 616000 | 673220.519653564 | 0 | 0 | 0 | 0 |  |  | 620901 | 311485.071134111 | 678576.577244279 | [8 empty] | 590 |  | 685 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 40187 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WERE NO SCADA ALARMS TO INDICATE TO THE CONTROLLER THAT A LEAK HAD OCCURRED. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [146 empty] | MICHAEL D. SMITH | COMPLIANCE SPECIALIST | mdsmith@eprod.com | 713-381-5650 |  |  |  |  | MICHAEL D. SMITH | COMPLIANCE SPECIALIST | 713-381-5650 | mdsmith@eprod.com | AT 08:05 AM ON 10/30/2015, OPERATIONS DISCOVERED A MINOR NATURAL GAS LEAK ON LINE 9A AT THE NAVIGATION STREET CROSSING IN CORPUS CHRISTI. THE LEAK WAS DISCOVERED WHILE CONDUCTING AN ANNUAL GAS LEAKAGE SURVEY; PRODUCT WAS DETECTED VENTING FROM THE CASING VENT PIPE. ENTERPRISE DETERMINED AT 09:50 AM ON 10/30/2015 THAT THE LEAK WAS REPORTABLE BASED ON THE EXPECTED COST TO REPAIR OR REPLACE THE SEGMENT OF PIPELINE. OPERATIONS ISOLATED THE PIPELINE SEGMENT AND PURGED THE PIPELINE AT 11:07 AM ON 10/30/2015. SUPPLEMENTAL: THE LEAKING SEGMENT WAS PURGED, CUT AND CAPPED ON BOTH SIDES OF THE CROSSING. A NEW HDD WAS INSTALLED AND THE PIPELINE WAS RETURNED TO SERVICE ON 12/21/2015. THE OLD SEGMENT COULD NOT BE EXPOSED TO CONFIRM THE CAUSE OF THE RELEASE DUE TO LOCATION OF THE CROSSING AT NAVIGATION STREET.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150138 | 17230 | 2015-11-20 10:48 | SUPPLEMENTAL FINAL | 31531 | ONEOK WESTEX TRANSMISSION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2015-10-21 08:55 | 2015 |  |  | 31.3559 | -103.8795 | 1131315 | 2015-10-21 09:05 |  | NATURAL GAS |  | 48641 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-10-21 07:28 | 2015-10-23 11:32 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-10-21 02:34 | 2015-10-21 04:04 | ONSHORE | TX | 79785 | Not Within a Municipality | REEVES | MILEPOST | MP 53.52 | OWT LINE 4001-000 | OWT LINE 4001-000 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12.75 |  | 0.219 | 42000 | API 5LX | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | JONES&LAUGHLIN | COAL TAR | [28 empty] | 1968 | 1967 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 1200 | 12 |  | CLASS 1 LOCATION | NO |  | 370 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 118737 | 106194.35915493 | 142500 | 155736.889692586 | 1000 | 1092.89045398306 | 0 | 0 |  |  | 262237 | 182085.521412955 | 263024.139301499 | [8 empty] | 877 |  | 953 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 96730 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WAS NO INVESTIGATION OF THE CONTROLLER DUE TO THE RESPONSE TIME WAS ADEQUATE AND AVAILABLE CONTROLS WERE ADDRESS/UTILIZED. THERE WERE NO INDICATIONS OF FATIGUE OR STRESS BASED ON HIS WORK SCHEDULE AND AGAIN DUE TO THE RESPONSE TIME FATIGUE DID NOT PLAY APART IN THIS RUPTURE. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1968 |  | YES | YES |  |  |  | 2015 |  |  |  | NO | [190 empty] | YES | YES |  |  | YES |  |  |  | 2015 | [31 empty] | 2015 | [23 empty] | NO |  |  | Yes, but the point of the Accident was not identified as a dig site |  | 2006 | [11 empty] | NO | [63 empty] | PATRICK VAUGHAN | MANAGER REGULATORY COMPLIANCE | pat.vaughan@oneok.com | 918-588-7734 | 918-591-5032 |  |  |  | WES DUNBAR | VP NATURAL GAS PIPELINE OPERATIONS | 918-588-7424 | wesley.dunbar@oneok.com | AT 2:32 AM ON OCT 21, PIPELINE CONTROL OPERATORS NOTICED A PRESSURE DROP ON LINE 4001-000. THE CONTROL OPERATOR NOTIFIED FIELD OPERATIONS PERSONNEL. SEVERAL MAINLINE VALVES WERE CLOSED TO DETERMINE WHICH SECTION OF THE LINE MIGHT BE LEAKING. WHEN THE LEAKING SEGMENT WAS IDENTIFIED, FIELD OPERATIONS PERSONNEL BEGAN FOLLOWING THE PIPELINE TO DETERMINE THE LOCATION OF THE LEAK. AT 8:55 AM THE LOCATION OF THE LEAK WAS IDENTIFIED. APPROXIMATELY 100 FEET OF LINE HAD RUPTURED AND WAS PARTIALLY EJECTED FROM THE DITCH. AT THIS TIME EXTERNAL CORROSION IS THE SUSPECTED CAUSE BASED ON FIELD EXAMINATION ON OCT 21. THE FAILURE PIECES HAVE BEEN SENT TO A THIRD PARTY LAB FOR EXAMINATION. A SUPPLEMENTAL REPORT WILL BE FILED IF THE ROOT CAUSE IS DETERMINED TO BE SOMETHING OTHER THAN EXTERNAL CORROSION. SUPPLEMENTAL - THE LAB REPORT CONFIRMED EXTERNAL CORROSION AS THE CAUSE OF THE FAILURE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150139 | 16930 | 2015-11-24 00:24 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2015-10-23 11:23 | 2015 |  |  | 38.5141 | -121.8909 | 1131545 | 2015-10-23 14:22 |  | NATURAL GAS |  | 2655 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-10-23 18:49 | 2015-10-25 01:40 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-10-23 11:23 | 2015-10-23 12:06 | ONSHORE | CA | 95620 | DIXON | SOLANO | MILEPOST | MILE POINT | L-150 | MP 7.23 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 39 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 |  | 0.28 | 35000 | GRADE B | SEAMLESS |  | UNKNOWN | EPOXY | [28 empty] | 1949 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 6.6 | 20.8 | [7 empty] | CLASS 1 LOCATION | NO |  | 52 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 327867.136194918 | 0 | 0 | 0 | 0 |  |  | 300000 | 150499.666888741 | 327867.136194918 | [8 empty] | 118 |  | 125 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 19483 | NO |  |  |  | YES |  |  |  | YES |  | YES | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA-RELATED EQUIPMENT OPERATED AS INTENDED | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | YES |  |  | YES | PRIVATE LANDOWNER | [7 empty] | CONTRACTOR | FARM EQUIPMENT | AGRICULTURE | YES | 490858 | USA NORTH 811 | UTILITY OWNER | YES | YES | YES | 1470 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO MAINTAIN CLEARANCE | [263 empty] | STEPHEN RAMOS | COMPLIANCE ENGINEER | s3rc@pge.com | 925-328-6107 |  |  |  |  | LARRY DENISTON | MANAGER OF REGULATORY COMPLIANCE | 925-328-5756 | lcd1@pge.com | ON OCTOBER 23, 2015 AT 1123 HOURS, PG&E WAS NOTIFIED OF BLOWING GAS IN A FIELD NEAR 5430 PUTAH CREEK RD. DIXON, SOLANO COUNTY. PG&E GAS SERVICE REPRESENTATIVE ARRIVED ON SITE AT 1206 HOURS AND A GAS PIPELINE OPERATIONS AND MAINTENANCE (GPOM) CREW AT 1245 HOURS. IT WAS DETERMINED THAT TRANSMISSION LINE L-150 AT MILEPOINT (MP) 7.23 HAD BEEN STRUCK BY A RIPPER BEING PULLED IN AN AGRICULTURAL FIELD BY A BULLDOZER BEING OPERATED BY NICHELINI CONSTRUCTION. THE EXCAVATOR HELD A USA TICKET #490858 AND THE PIPELINE HAD BEEN PROPERLY MARKED PRIOR TO THE INCIDENT. THE OPERATOR HAD MADE NUMEROUS PASSES OVER THE PIPELINE BUT FAILED TO RAISE THE RIPPER DURING THE PASS WHICH STRUCK THE PIPE. THE DEPTH, AT WHICH THE LINE WAS DAMAGED, WAS APPROXIMATELY 39 INCHES BELOW THE SURFACE OF THE SOIL. NO INJURIES, FATALITIES, OR IGNITION. DAMAGE TO THE TRANSMISSION PIPELINE, INCLUDING REPAIRS IS APPROXIMATELY $300,000. PG&E SECURED THE AREA AND CLOSED MAINLINE VALVE V-9.7 AT 1504 HOURS AND 90% CLOSED V-5.96 AT 1617 HOURS IN ORDER TO KEEP A POSITIVE PRESSURE IN THE SHUT-IN SECTION OF PIPELINE. THE FLOW OF GAS WAS COMPLETELY STOPPED AT 1849 HOURS. REPAIRS ON THE PIPELINE WERE COMPLETED ON 10/23/15 AT 2238 HOURS AND THE PIPELINE WAS RESTORED TO NORMAL OPERATION ON 10/25/15 AT 0140 HOURS. GAS SERVICE TO THE CUSTOMERS WAS RESTORED BY 10/26/15 AT 1330 HOURS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150140 | 17172 | 2015-11-24 07:13 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2015-10-24 11:55 | 2015 |  |  | 44.162 | -85.0062 | 1133332 | 2015-11-13 10:29 |  | NATURAL GAS |  | 37025 | 91.5 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-10-24 12:31 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-10-24 11:55 | 2015-10-24 12:23 | ONSHORE | MI | 49665 | MARION | MISSAUKEE | SURVEY STATION NO. | STATION 60 W | CRANBERRY LAKE STORAGE FIELD | LATERAL 60 WEST | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTRASTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | PIPE | PIPE BODY | 6 |  | 0.188 | 35000 | API5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | YOUNGTOWN SHEET & TUBE | OTHER | BLACK WRAP WITH LIGHT BROWN OUTER LAYER, NO ABESTOS FIBERS | [27 empty] | 1957 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | OVAL HOLE APPR .25 X .50 | [5 empty] | CLASS 1 LOCATION | NO |  | 117 |  | NO | NO | NO |  | 0 | 0 | 682 | 745.351289616446 | 277728 | 248390.535211268 | 10921 | 11935.456647949 | 494 | 539.887884267631 | 3127 | 3417.46844960503 | LAB ANALYSIS |  | 292952 | 265155.102907921 | 265028.699482706 | [8 empty] | 709 |  | 800 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE FACILITY WAS NOT MONITORED BY A CONTROLLER AT THE TIME OF THE INCIDENT | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  |  | YES | YES | MIC TESTING | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | YES | YES | [6 empty] | 2005 | [49 empty] | MICRO VERTILINE TOOL | [5 empty] | YES | 1999 | 1241 | NO | [13 empty] | NO | [63 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 734-513-6256 |  |  |  |  | AMANDA L. WARD | GAS REGULATORY SERVICES LEAD | 517-545-8746 | amanda.ward@cmsenergy | AT APPROXIMATELY 11:55 ON SATURDAY, OCTOBER 24, 2015 CONSUMERS ENERGY GAS CONTROL WAS NOTIFIED BY A LANDOWNER OF A POSSIBLE GAS LEAK AT THE CRANBERRY STORAGE FIELD. A GAS SYSTEM MECHANIC (GSM) WAS DISPATCH AND ARRIVED ON-SITE AT 12:23 AND IDENTIFIED BLOWING GAS ON LATERAL 60 WEST. THE LEAK LOCATION WAS APPROXIMATELY 1750 FEET NORTH OF WELL 367. LATERAL 60 WEST IS A 6 INCH PIPELINE (APPROXIMATELY 11/2 MILES LONG) LOCATED IN CONSUMERS ENERGY'S CRANBERRY STORAGE FIELD, MARION, MICHIGAN (MISSAUKEE COUNTY) THE GSM IMPLEMENTED THE STANDARD PRECAUTIONARY LOCK OUT TAG OUT PROCESS, ISOLATING AND SHUTTING DOWN LATERAL 60 WEST AND BARRICADED THE LOCATION UNTIL FURTHER INVESTIGATION COULD BE PERFORMED. THE PIPELINE WAS SHUT DOWN AT APPROXIMATELY 12:31. ON TUEDAY, NOVEMBER 3, 2015 A 4 FOOT SECTION OF PIPELINE WAS CUT OUT AND A OVAL HOLE APPROXIMATELY .25 X .50 WAS DISCOVERED. THE LEAK WAS VISUALLY EXAMINED AND PRELIMINARY ANALYSIS IDENTIFIED CORROSION AS A POSSIBLE LEAK SOURCE. THE GAS LOSS CALCULATION WAS DETERMINED BASED ON THE FOLLOWING INFORMATION: LATERAL 60 WEST WAS PLACED BACK INTO SERVICE ON OCTOBER 7, 2015. THE LEAK WAS IDENTIFIED AND THE PIPELINE WAS ISOLATED AND SHUT DOWN ON OCTOBER 24, 2015 APPROXIMATELY 36 MINUTES FOLLOWING NOTIFICATION. A VISUAL INSPECTION WAS PERFORMED BY OPERATIONS PERSONNEL WHEN THE PIPELINE WAS PLACED BACK INTO SERVICE, HOWEVER NO ADDITIONAL INSPECTIONS/PATROLS WERE CONDUCTED. BECAUSE NO ADDITIONAL LEAK INSPECTION WAS PERFORMED DURING THIS PERIOD, CONSUMERS ENERGY OPTED TO CALCULATE THE HOURS FROM THE DATE THE LINE WAS PLACED BACK IN SERVICE ON OCTOBER 7TH UNTIL THE LEAK WAS DISCOVERED AND THE LATERAL SHUT-DOWN RESULTING IN A GAS LOSS OF APPROXIMATELY 37MMCF. THE GAS LOSS CALCULATION BASED ON NOTIFICATION AND ISOLATION AND SHUT DOWN WOULD HAVE RESULTED IN A GAS LOSS CALCULATION OF LESS THAN 1MMCF. THE DAMAGED SECTION OF THE PIPELINE WAS TRANSPORTED TO THE CONSUMERS ENERGY TRAIL STREET LABORATORY FOR FURTHER EXAMINATION. LABORATORY ANALYSIS CONFIRMED THE LEAK WAS A RESULT OF A LOCALIZED CORROSION PIT ON THE PIPE ID. THE MIC TESTING PERFORMED ON SLUDGE EXTRACTED FROM THE PIPELINE INDICATES MICROBIOLOGICAL INFLUENCE CORROSION (MIC) MAY HAVE CAUSED OR CONTRIBUTED TO THE FAILURE. LATERAL 60 WEST REMAINS SHUT-IN AND SCHEDULED FOR REPLACEMENT BOTH LATERAL 60 EAST AND WEST WILL BE ELIMINATED AND REPLACED WITH ONE LATERAL IN SUMMER 2016.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150141 | 17037 | 2015-12-01 18:07 | SUPPLEMENTAL FINAL | 38987 | KINETICA ENERGY EXPRESS LLC | 1001 MCKINNEY STREET, SUITE 900 | HOUSTON | TX | 77002 | 2015-11-09 16:58 | 2015 |  |  | 28.6519 | -90.9917 | 1132999 | 2015-11-09 17:20 |  | NATURAL GAS |  | 450 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-11-10 11:00 | 2015-11-30 10:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-11-09 16:58 | 2015-11-10 11:00 | OFFSHORE | [28 empty] | 60 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SHIP SHOAL | 168 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 10.75 |  | 0.5 | 42000 | 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | US STEEL | EPOXY | [28 empty] | 1973 | 1973 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 900 | 804.929577464789 | 125000 | 136611.306747882 | 5000 | 5464.45226991529 | 0 | 0 |  |  | 130900 | 66051.0293607079 | 142880.688595262 | [8 empty] | 975 |  | 1200 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 6298 | NO | YES | YES |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | REPORTED BY BSEE INSPECTOR |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE WAS BELOW MAOP WITH NO UNUSUAL OPERATING CIRCUMSTANCES AND WAS LOCATED SUBSEA. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES | [7 empty] | YES | 6:00 POSITION | YES | NO | NOT APPLICABLE - NOT MAINLINE PIPE | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KURT J. CHERAMIE | SR. DIRECTOR | kurt.cheramie@kineticallc.com | 9852092283 |  |  |  |  | KURT J. CHERAMIE | SR. DIRECTOR | 9852092283 | kurt.cheramie@kineticallc.com | OVERFLIGHT OF THE AREA BY BSEE INSPECTOR IDENTIFIED A LEAK IN THE VICINITY OF KINETICA'S 523M-2900 PIPELINE. IT WAS TOO LATE TO FLY TO THE LOCATION, SO KINETICA PERSONNEL WERE DISPATCHED THE NEXT AM TO ISOLATE THE PIPELINE. AT 11:00 AM, PRODUCTION WAS SHUT-IN AND PLATFORM VALVE CLOSED TO ISOLATE THE PIPELINE. DIVE VESSEL WAS PROCURED AND ARRIVED ON SITE ON 11/12 TO CLOSE SUB-SEA VALVE. WEATHER (ROUGH SEAS) PROHIBITED THE REPAIR UNTIL 11/30. UPON HAVING CALMER WEATHER, DIVE VESSEL WAS DISPATCHED TO LOCATION. DIVER EXCAVATED LEAK AREA AND PREPARED PIPELINE FOR INSTALLATION OF REPAIR CLAMP. DIVER IDENTIFIED A SMALL PINHOLE LEAK AT THE 6:00 POSITION. REPAIR CLAMP WAS INSTALLED. DIVER OPENED SUB-SEA VALVE. KINETICA PERSONNEL OPENED PLATFORM VALVE TO ALLOW PRODUCTION TO COMMENCE. AREA WAS MONITORED BY DIVE VESSEL AS PRESSURE INCREASED TO NORMAL OPERATING PRESSURE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150142 | 33580 | 2015-12-02 07:44 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION LP (SPECTRA ENERGY CORP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2015-11-03 09:30 | 2015 | CENTRAL | NO | 30.8682 | -95.0996 | 1132445 | 2015-11-03 10:15 |  | NATURAL GAS |  | 1 | 12491 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2015-11-03 20:14 | 2015-11-05 17:30 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2015-11-03 20:14 | VALVE CLOSURE |  | 2015-11-03 20:14 | 0 | 2015-11-03 09:30 | 2015-11-03 09:30 | ONSHORE | TX | 77360 | Not Within a Municipality | POLK | MILEPOST | 144 | LINE 11 | HUNT-LUFK | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 24 |  | 0.312 | 52000 | API-5LX | FLASH WELDED |  | AO SMITH | COAL TAR |  | UNKNOWN | [7 empty] | PIPE GIRTH WELD |  | NO | [16 empty] | 1954 | 1954 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 517 |  | NO | NO |  |  | 0 | 0 | 31229 | 34129.8759874369 | 3 | 2.6830985915493 | 122000 | 133332.635385933 | 0 | 0 | 0 | 0 |  | 2.5001 | 153232 | 76872.4932157904 | 167465.194471962 | 0 | 0 | 0 | 0 | NO |  |  |  | 691 | 80000 | 973 | 192.619(C) |  | 2015-05-01 | YES | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 85843 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE RELEASE OF GAS WAS TOO SMALL TO BE DETECTED BY SCADA. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | YES | [7 empty] | YES | HYDROGEN INDUCED CRACKING | [12 empty] | YES | [8 empty] | 1308 | [54 empty] | YES | YES |  |  | YES |  |  |  | 2012 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2005 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [21 empty] | 2012 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | [19 empty] | NO |  |  | Yes, but the point of the Accident was not identified as a dig site |  | 2010 | 2010 | 2010 |  |  |  |  | YES | YES |  |  |  | NO | [63 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | deteschendorf@spectraenergy.com | 713-627-5573 |  | NATHAN ATANU | nathan.atanu@enbridge.com | 713-627-5008 | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 713-627-5008 | nathan.atanu@enbridge.com | COMPANY EMPLOYEES DISCOVERED A LEAK DUE TO A CRACK IN A GIRTH WELD NEAR THE 6 O'CLOCK POSITION ON TEXAS EASTERN TRANSMISSION, LP 24-INCH LINE 11 NEAR ONALASKA, TEXAS AT 9:30 AM NOVEMBER 3, 2015. THE LEAK WAS THE RESULT OF A 4" CRACK AT THE EDGE OF THE GIRTH WELD. THE CRACK WAS IN THE HEAT AFFECTED ZONE (HAZ) AT THE 6 O'CLOCK PIPE POSITION. PIPE CONTAINING LEAK WAS REPLACED AND LINE IS BACK IN SERVICE. METALLURGICAL TESTING INDICATED THAT THE CRACK WAS DUE TO HYDROGEN INDUCED CRACKING (HIC). SUPPLEMENTAL 3/17/2020 UPDATED PART G5-METALLURGICAL INVESTIGATION COMPLETE
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150143 | 17060 | 2015-12-04 16:20 | SUPPLEMENTAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2015-11-05 15:00 | 2015 |  |  | 30.8917 | -102.7246 | 1132681 | 2015-11-05 16:32 |  | NATURAL GAS |  | 63000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | CLOSING BLOWDOWN VALVE DOES NOT REQUIRE PIPELINE SHUTDOWN. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-11-05 10:00 | 2015-11-05 11:30 | ONSHORE | TX | 79735 | Not Within a Municipality | PECOS | MILEPOST | 478 | OASIS PIPELINE | SYSTEM 3951 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | DRAIN LINES | [38 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | OPERATOR ERROR | CLASS 1 LOCATION | NO |  | 500 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 50000 | 44718.3098591549 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 50000 | 46361.5023474178 | 44718.3098591549 | [8 empty] | 900 |  | 1050 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL |  | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ONLY FIELD EMPLOYEE INVOLVED | [12 empty] | YES | 1 | 0 | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | EMPLOYEE THAT WORKS ON THE GATHERING SYSTEM INCORRECTLY IDENTIFIED VALVE SITE. | [147 empty] | BILL MEYER | MANAGER INTRASTATE COMPLIANCE | bill.meyer@energytransfer.com | 713-989-6460 |  |  |  |  | DANNY NICHOLS | DIRECTOR REGULATORY COMPLIANCE | 713-989-7232 | danny.nichols@energytransfer.com | ETC/REGENCY FIELD SERVICE EMPLOYEE THOUGHT HE WAS BLOCKING THEIR GATHERING 12 IN. LINE AND BLOWING IT DOWN FOR REPAIRS BUT INSTEAD HE BLOCKED IN THE ETC/OASIS 36 IN. MAINLINE AT MLV-19 AND OPENED THE 10 IN. BLOWDOWN BY MISTAKE. THIS OCCURRED IN AN INTRASTATE PIPELINE AND WAS REPORTED TO THE RAILROAD COMMISSION OF TEXAS, REPORT NUMBER 1275
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150144 | 17039 | 2015-12-07 17:13 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2015-11-16 01:50 | 2015 |  |  | 38.1716 | -95.2998 | 1133574 | 2015-11-16 15:36 |  | NATURAL GAS |  | 1790 | 4100 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-11-16 12:20 | 2015-11-16 16:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-11-16 01:51 | 2015-11-16 02:36 | ONSHORE | KS | 66091 | WELDA | ANDERSON | SURVEY STATION NO. | 110/0+75 | LINE DP TIE-OVER | WELDA-OTTAWA 30" LOOP TIE-OVER | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | INSTRUMENTATION | [38 empty] | UNKNOWN |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 365 |  | NO | NO | NO |  | 0 | 0 | 7667 | 8379.19111068811 | 3347 | 2993.44366197183 | 369000 | 403276.577519749 | 5000 | 5464.45226991529 | 0 | 0 |  |  | 385014 | 194572.626841886 | 420113.664562324 | [8 empty] | 620 |  | 701 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [103 empty] | OTHER OUTSIDE FORCE DAMAGE | [9 empty] | COMMUNICATION TOWER ON COMPRESSOR STATION SITE FELL. WHILE FAILING IT STRUCK A 1" WELD-O-LET FOR A METER BUILDING TRANSMITTER LINE CAUSING A GAS LOSS AT THE WELD-O-LET THREADS. | [251 empty] | DAVID COOMES | PIPELINE COMPLIANCE ENGINEER | david.coomes@sscgp.com | 270-852-4391 |  |  |  |  | DAVID SINCLAIR | PIPELINE COMPLIANCE MANAGER | 270-852-4424 | david.l.sinclair@sscgp.com | ON 11/16/2015 AT 01:50 AM THE COMMUNICATIONS TOWER AT THE SSC COMPRESSOR STATION IN WELDA, KS FELL AND STRUCK A 1" WELD-O-LET THAT WAS FEEDING A MEASUREMENT TRANSMITTER LINE. THE STRIKE CAUSED A RELEASE OF NATURAL GAS AND A LOSS OF COMMUNICATIONS TO SSC GAS CONTROL AT APPROXIMATELY 01:52 AM. SSC GAS CONTROL NOTIFIED ON-CALL OPERATIONS AT 1:53 AM AND ON-CALL COMMUNICATIONS PERSONNEL AT 1:58 AM. AT 02:25 ON-CALL COMMUNICATIONS CONFIRMED GAS CONTROL OF A LOSS OF POWER AT THE WELDA STATION COMMUNICATIONS TOWER. ON-CALL OPERATIONS ARRIVED ONSITE AT 02:36 AM. OPERATIONS CONFIRMED THERE WAS A 1" LINE THAT HAD BEEN DAMAGED FROM THE FALL OF THE COMMUNICATION TOWER CAUSING A RELEASE OF GAS. THE LINE WAS BLOWN DOWN AT ON 11/16/2015 AT 12:20 PM TO MAKE REPAIRS TO THE 1" WELD-O-LET THAT HAD BEEN DAMAGED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150145 | 17064 | 2015-12-09 10:35 | SUPPLEMENTAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2015-11-10 08:30 | 2015 |  |  | 40.4535 | -97.3162 | 1133046 | 2015-11-10 09:45 |  | NATURAL GAS |  | 4000 | 1300 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-11-10 13:41 | 2015-11-11 08:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-11-10 09:12 | 2015-11-10 10:12 | ONSHORE | NE | 38453 | Not Within a Municipality | SALINE | MILEPOST | MP 35.53 | KANSAS-NEBRASKA 10-INCH | NEB49401 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 42 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10 |  | 0.188 | 42000 | API 5LX | LONGITUDINAL ERW - LOW FREQUENCY |  | YOUNGSTOWN | COAL TAR | [28 empty] | 1962 | 1962 | CARBON STEEL |  | MECHANICAL PUNCTURE | 1 | 2 | [7 empty] | CLASS 1 LOCATION | NO |  | 195 |  | NO | NO | NO |  | 0 | 0 | 3900 | 4262.27277053393 | 12000 | 10732.3943661972 | 5000 | 5464.45226991529 | 97947 | 107045.341296279 | 0 | 0 |  |  | 118847 | 64728.2202569179 | 127504.460702925 | [8 empty] | 502 |  | 800 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 105600 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE THIRD PARTY THAT CAUSED THE INCIDENT IMMEDIATELY DIALED 911. OUR FIRST NOTIFICATION CAME FROM THEM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [7 empty] | CONTRACTOR | TRENCHER | DRAINAGE | NO | [5 empty] | NO |  | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | JOHN A GORMLEY | SR. CORROSION SPECIALIST | john.gormley@nngco.com | 402-398-7494 |  |  |  |  | THOMAS CORRELL | SR. DIRECTOR OF PIPELINE SAFETY AND RISK | 402-398-7715 | thomas.correll@nngco.com | ON NOVEMBER 10, 2015 AT APPROXIMATELY 08:30 THE PIPELINE WAS STRUCK AND DAMAGED BY A DITCH WITCH RT95 CHAIN TYPE TRENCHER. THE OPERATOR OF THE EQUIPMENT IMMEDIATELY SHUT OFF THE TRENCHER, LEFT IT IN PLACE AGAINST THE PIPELINE, AND RETREATED TO SAFETY. THERE WAS NO FIRE, NO INJURIES AND NO CASUALTIES. NO ONE WAS EVACUATED FROM THEIR HOME. THE OPERATOR OF THE TRENCHER, JAQS IRRIGATION AND TRENCHING, WAS DOING SUBCONTRACT WORK FOR MUSSMAN EXCAVATING. NEITHER CONTRACTOR MADE THE REQUIRED ONE-CALL. THE PIPELINE IS A 10-INCH OPERATING AT ABOUT 500 PSI AT THE TIME OF THE INCIDENT. THE LINE HIT WAS THE ONLY DAMAGE. THE PIPELINE WAS 42-INCHES DEEP. THE TRENCHER TOOTH CAUSED A 1-INCH BY 2-INCH PUNCTURE. THE DAMAGED SECTION WAS REPLACED WITH A 10-FOOT LENGTH OF NEW PIPE. ABOUT 5,000 MCF OF NATURAL GAS WAS RELEASED DUE TO THE DAMAGE AND DURING REPAIRS. THERE WERE NO SERVICE INTERRUPTIONS BECAUSE THE COMPANY USED VOLUME BOTTLE TRAILERS TO PROVIDE TEMPORARY SERVICE TO THE TOWN OF WESTERN, NE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150146 | 17161 | 2015-12-09 17:27 | SUPPLEMENTAL FINAL | 1217 | BEAR CREEK STORAGE CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2015-11-09 03:30 | 2015 |  |  | 32.3988 | -92.9195 | 1133104 | 2015-11-10 04:20 |  | NATURAL GAS |  | 107 | 972 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-11-09 17:30 | 2015-11-20 14:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-11-09 03:30 | 2015-11-09 04:30 | ONSHORE | LA | 71008 | BIENVILLE | BIENVILLE | MILEPOST | MP 2+1703 | BEAR CREEK STORAGE | BCS LINE 5 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10.75 |  | 0.5 | 52000 | API 5L X52 | SEAMLESS |  | ARMCO STEEL | COAL TAR | [28 empty] | 1981 | 1981 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 384 |  | NO | NO | NO |  | 0 | 0 | 2751 | 3006.5416389074 | 303 | 270.992957746479 | 50000 | 54644.5226991529 | 0 | 0 | 0 | 0 |  |  | 53054 | 26744.3104643853 | 57922.0572958068 | [8 empty] | 2689 |  | 3100 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 12927 | NO | YES | [6 empty] | NO | [6 empty] | TRANSMISSION IN STORAGE FIELD | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS TOO SMALL TO BE VISIBLE IN SCADA TO A CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING | [5 empty] | YES | METALLURGICAL ANALYSIS INDICATES POSSIBLE CAUSES OF LIQUID AND/OR MICROBIOLOGICAL, BUT IS INCONCLUSIVE. |  | YES |  |  | YES | [5 empty] | NO | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | ZACHARY RAGAIN | ENGINEER-PIPELINE | zachary_ragain@kindermorgan.com | 8329190774 |  |  |  |  | ZACHARY RAGAIN | ENGINEER-PIPELINE | 8329190774 | zachary_ragain@kindermorgan.com | CONTRACTOR WAS WORKING ON ROW AND DISCOVERED BUBBLES COMING UP IN MUD AND HIGH PRESSURE 'AIR' COMING FROM GROUND. CONTRACTOR CONTACTED BEAR CREEK STORAGE EMPLOYEE. EMPLOYEE ARRIVED WITH GAS DETECTOR AND DETERMINED THAT A GAS RELEASE WAS EVIDENT IN A CREEK COMING THROUGH MATTING. THE LEAK WAS INITIALLY DISCOVERED ON 11/9/2015 AND DURING AN INITIAL CONFERENCE CALL THAT DAY WAS DETERMINED TO NET BE REPORTABLE. ON 11/10/2015, IT WAS DETERMINED THAT THE REPAIR COSTS FOR THE EVENT WOULD EXCEED $50,000, THUS MAKING THE EVENT REPORTABLE. THE NRC WAS CONTACTED ON 11/10/2015. REPAIR PERFORMED BY REPLACING A SEGMENT OF PIPE. PIPELINE RETURNED TO SERVICE ON 11/20/2015. UPDATED 6/23/2016 TO REVISE CAUSE OF CORROSION IN SECTIONS G7 AND G8 BASED OFF METALLURGICAL ANALYSIS. SUBMITTED REPORT AS FINAL ON 8/16/2016 WITH NO CHANGES.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150147 | 17022 | 2015-12-14 14:49 | SUPPLEMENTAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2015-11-29 10:58 | 2015 |  |  | 35.2329 | -98.2833 | 1134486 | 2015-11-29 11:54 |  | NATURAL GAS |  | 32036 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | STATION WAS NOT OPERATING | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-11-29 10:58 | 2015-11-29 11:53 | ONSHORE | OK | 73053 | Not Within a Municipality | CADDO | SURVEY STATION NO. | S33-11N-12W | HINTON COMPRESSOR STATION | HINTON COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | ESD SYSTEM | 2006 |  | CARBON STEEL |  | OTHER | [8 empty] | ESD ACTIVATED, VALVES FROZEN AND DID NOT CLOSE | CLASS 1 LOCATION | NO |  | 386 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 64072 | 57303.8309859155 | 0 | 0 | 0 | 0 | 0 | 0 | N/A |  | 64072 | 59409.4835680751 | 57303.8309859155 | [8 empty] | 925 |  | 1000 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DUE TO ICE STORM IN OKLAHOMA, HINTON STATION COMMUNICATIONS WENT OUT AT 10:30 ON 11/2/15. THE STATION PERFORMED AN ESD DUE TO POWER LOSS AND ICE PREVENTED THE VALVES FROM CLOSING. THE COMPRESSION HAD BEEN OFFLINE SINCE 07:00 11/27/15. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [7 empty] | YES |  |  |  | YES | GENERATOR DID NOT COME ON AND THE BATTERIES WENT DEAD, CAUSING THE ESD VALVES TO ACTIVATE. HEAVY ICING THE MAINLINE VALVES, THEY WOULD NOT CLOSE. | [11 empty] | YES | [10 empty] | YES | ICE STORM AND FREEZING OF VALVES | [161 empty] | JIMMY CROSS | DOT COMPLIANCE MANAGER | jimmy.cross@enablemidstream.com | 3184293664 |  |  |  |  | JOHNNY CAVITT | SR. MANAGER OF DOT COMPLIANCE PROGRAMS | 3184293606 | johnny.cavitt@enablemidstream.com | THE GENERATOR DID NOT COME ON AND THE BATTERIES WENT DEAD, CAUSING THE ESD VALVES TO ACTIVATE. VALVES WERE INCASED IN ICE AND WOULD NOT CLOSE. ONCE THE ICE WAS REMOVED FROM THE VALVES THE SYSTEM WORKED AS DESIGNED. UPDATE 2/25/2016: EXTREME FREEZING AND ICY CONDITIONS PREVENTED THE GENERATOR FROM STARTING. ROAD CONDITIONS SLOWED RESPONSE. THE BATTERIES LASTED FOR THE DURATION THEY WERE INTENDED FOR. FOLLOW UP TO EVALUATE THE SYSTEM RESULTED IN NO CHANGES TO THE SYSTEM OR ITS COMPONENTS. THE GENERATOR PERFORMED AND STARTED AS IT WAS DESIGNED TO DO. BATTERIES CHECKED OUT AND PERFORMED AS THEY WERE INTENDED AND DESIGNED TO DO.
2021-02-26 10:37 | YES | YES | GT (Gas Transmission) | 20150148 | 16974 | 2015-12-14 23:28 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2015-11-13 15:32 | 2015 |  |  | 35.2394 | -119.0399 | 1133387 | 2015-11-13 16:42 |  | NATURAL GAS |  | 67000 | 0 | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES | 0 | 0 | 0 | 0 | 2 | 2 |  | YES |  | 2015-11-13 15:44 | 2015-11-20 16:45 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 3 | 2015-11-13 15:33 | 2015-11-13 16:04 | ONSHORE | CA | 93313 | BAKERSFIELD | KERN | MILEPOST | NEAR V-270.85 | L-300A | L-300A | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 34 |  | 0.375 | 52000 | API 5L X-52 | DSAW |  | CONSOLIDATED WESTERN STEEL | ASPHALT | [28 empty] | 1954 | 1954 | CARBON STEEL |  | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 1 LOCATION | NO |  | 646 |  | YES | YES | NO |  | 1000000 | 1092890.45398306 | 0 | 0 | 176000 | 157408.450704225 | 642000 | 701635.671457124 | 717000 | 783602.455505853 | 0 | 0 |  |  | 2535000 | 1346621.53556471 | 2735537.03165026 | [8 empty] | 660 |  | 757 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | AUTOMATIC | 42240 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM IS NOT A CAUSE OR CONTRIBUTING FACTOR TO THE INCIDENT. THE CONTROL ROOM FUNCTIONED ACCORDINGLY. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  | YES | PRIVATE LANDOWNER | [7 empty] | FARMER | FARM EQUIPMENT | AGRICULTURE | NO | [5 empty] | YES | 25 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | STEPHEN RAMOS | COMPLIANCE ENGINEER | s3rc@pge.com | 925-328-6107 |  |  |  |  | LARRY DENISTON | MANAGER OF REGULATORY COMPLIANCE | 925-328-5756 | lcd1@pge.com | ON NOVEMBER 13, 2015, PG&E'S GAS CONTROL CENTER DETECTED A BACKFLOW ALARM VIA SCADA AT 1533 HOURS ON L-300A NEAR WIBLE RD & HOUGHTON RD. IN BAKERSFIELD. A THIRD-PARTY EXCAVATOR, JEFF ALEXANDER/BIG N DEEP AGRICULTURAL DEVELOPMENT, WAS PERFORMING AGRICULTURAL WORK WITH HEAVY EQUIPMENT, STRUCK NATURAL GAS TRANSMISSION LINE 300-A, CAUSING AN UNINTENTIONAL RELEASE OF GAS. THE GAS IGNITED RESULTING IN ONE FATALITY AND TWO INJURIES. WITHIN 4 MINUTES OF IDENTIFYING THE LOSS IN PRESSURE ON L-300A, GAS CONTROL INITIATED REMOTE SHUT OFF OF TWO MAINLINE VALVES AND ISOLATED THE PIPELINE BY 1547 HOURS. PG&E'S FIRST RESPONDERS ARRIVED ON-SITE AT 1604 HOURS AND MANUALLY SHUT OFF VALVES V-267.26A AND V-278.70A TO ISOLATE A SMALLER SECTION OF PIPELINE. THE REMAINING GAS WITHIN THE PIPELINE BURNED UNTIL APPROXIMATELY 1630 HOURS. THE VALVE CLOSEST TO THE INCIDENT, VALVE-270.85, WAS CLOSED AT 1700 HOURS ONCE THE FIRE WAS OUT AND THE EQUIPMENT WAS COOL ENOUGH TO OPERATE. THE EXCAVATOR DID NOT HOLD A VALID USA TICKET. FIRE AND POLICE DEPARTMENT WERE ON-SITE, AND BLOCKED OFF THE AREA. APPROXIMATELY NINETY GAS CUSTOMERS LOST SERVICE AS A RESULT OF THE INCIDENT. MAJORITY OF THE GAS SERVICES WERE RESTORED BY 11/14/15 AT 1500 HOURS. THERE WERE SIX TO SEVEN REMAINING CUSTOMERS THAT WERE EITHER VACANT OR OUT-OF-TOWN. SERVICE WAS RESTORED TO THE OUT-OF-TOWN CUSTOMERS WITHIN A WEEK FOLLOWING THE INCIDENT. A NEARBY HOME AND BARN ALSO SUSTAINED DAMAGES FROM THE FIRE. REPAIRS TO THE PIPE WERE COMPLETED ON 11/20/15 AT NOON, X-RAYS WERE COMPLETED BY 1330 HOURS, AND THE LINE WAS PUT BACK TO NORMAL OPERATION AT 1645 HOURS. DAMAGES RESULTING FROM THE INCIDENT ARE APPROXIMATELY $2.5 MILLION AND VOLUME OF GAS UNINTENTIONALLY RELEASED IS 67 MMCF. MEDIA WAS REPORTED ON-SITE. SAMPLES OF THE DAMAGED PIPE WERE RETAINED AND TRANSPORTED TO A THIRD PARTY CONSULTING FIRM FOR EVALUATION. THE INCIDENT WAS REPORTED TO BOTH THE DOT AND CPUC DUE TO A FATALITY, INJURIES, AND COSTS EXCEEDING $50,000, VOLUME OF GAS RELEASE EXCEEDING 3 MMCF, SUBSEQUENT IGNITION, MEDIA COVERAGE, AND TRANSMISSION EVENT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150149 | 17069 | 2015-12-16 11:02 | SUPPLEMENTAL FINAL | 15329 | PEOPLES GAS LIGHT & COKE CO | 200 E RANDOLPH STREET | CHICAGO | IL | 60601 | 2015-11-21 21:40 | 2015 |  |  | 40.2833 | -88.4167 | 1134129 | 2015-11-23 12:17 |  | NATURAL GAS |  | 11756 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | COMPRESSOR OPERATION WAS NOT AFFECTED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-11-21 21:40 | 2015-11-21 21:40 | ONSHORE | IL | 61843 | Not Within a Municipality | CHAMPAIGN | MILEPOST | MANLOVE FIELD | MANLOVE STORAGE FIELD | VALVE #V28 ON STATION PIPING | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | INSTRUMENTATION | [38 empty] | UNKNOWN |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | SEALS/GASKETS IN VERSA VALVE | OTHER | [8 empty] | INSTRUMENTATION THAT USUAULLY KEEPS VALVE #V28 CLOSED FAILED AND CAUSED THE AUTOMATIC VENT VALVE TO INADVERTENTLY OPEN | CLASS 1 LOCATION | NO |  | 205 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 42260 | 37795.9154929577 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 42260 | 39184.7417840376 | 37795.9154929577 | [8 empty] | 1751 |  | 2000 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER ACTIONS OR CONTROL ROOM ISSUES COULD NOT HAVE HAD ANY IMPACT ON THE INCIDENT | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | YES | [8 empty] | YES | [22 empty] | YES | [164 empty] | SHAWN BARTELS | COMPLIANCE SPECIALIST | srbartels@peoplesgasdelivery.com | 312-240-5421 |  |  |  |  | THOMAS WEBB | COMPLIANCE MANAGER | 312-240-4650 | tjwebb@peoplesgasdelivery.com | AT APPROXIMATELY 9:40 PM ON SATURDAY NOVEMBER 21, 2015 AN EMERGENCY VENT VALVE ON THE EMERGENCY SHUTDOWN SYSTEM FOR THE STORAGE FACILITY AT THE MANLOVE STORAGE FIELD SPURIOUSLY OPENED AND EMITTED GAS FOR 10 MINUTES UNTIL OPERATING PERSONNEL CLOSED BLOCK VALVES TERMINATING THE RELEASE. THIS VALVE IS DESIGNED TO OPEN WHEN THE EMERGENCY SHUTDOWN SYSTEM ACTIVATES. IN THIS CASE THE VALVE SHOULD NOT HAVE OPENED. CALCULATIONS ON THE SIZE OF THE RELEASE WERE COMPLETED AND THE ESTIMATED RELEASE WAS 11.756 MILLION FT3. SINCE THIS EXCEEDS THE REPORTING CRITERIA OF 3 MILLION FT3 LISTED IN 49 CFR191.3 A ONE HOUR CALL WAS MADE TO THE NRC AND A FOLLOW UP CALL WAS MADE TO THE ICC. THE CALL TO THE NRC WAS DELAYED BECAUSE THE INITIAL ASSESSMENT MADE BY MANLOVE PERSONNEL WAS THAT THIS EVENT DID NOT MEET THE DEFINITION CONTAINED IN 49CFR191.3. PERSONNEL AT MANLOVE ORIGINALLY BELIEVED THAT THE DEFINITION LIMITED REPORTABLE RELEASES TO LEAKS IN THE SYSTEM. SINCE THIS VALVE IS AN IDENTIFIED RELEASE PATH, THEY INITIALLY DETERMINED IT WAS NOT REPORTABLE. HOWEVER FURTHER REVIEW OF THE EVENT AND THE REGULATIONS DETERMINED THAT THIS EVENT DID MEET THE DEFINITION CONTAINED IN 49 CFR 191 OF A RELEASE. THE ICC WAS ON SITE ON 11/24/15 AND 11/25/15 FOR THE INVESTIGATION INTO THE INCIDENT. THE INVESTIGATION CONCLUDED THAT THE SEALS/GASKETS HAD BROKEN DOWN IN THE VERSA VALVE. THE SUSPECTED CAUSE OF THIS BREAKDOWN WAS DUE TO NUMEROUS FREEZE AND THAW CYCLES. SUPPLEMENTAL: CHANGED THE TIME THAT THE NRC RECIEVED THE REPORT TO REFLECT THE CENTRAL TIME ZONE. CHANGED THE CLASS LOCATION OF THE INCIDENT TO CLASS 1 SINCE THERE IS LESS THAN 10 OR FEWER BUILDINGS INTENDED FOR HUMAN OCCUPANCY WITHIN THE CLASS LOCATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150150 | 17146 | 2015-12-18 20:29 | SUPPLEMENTAL FINAL | 15033 | PAIUTE PIPELINE CO | 5241 SPRING MOUNTAIN ROAD | LAS VEGAS | NV | 89150 | 2015-11-21 15:50 | 2015 |  |  | 39.0911 | -119.7747 | 1134017 | 2015-11-21 16:36 |  | NATURAL GAS |  | 625 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-11-21 15:55 | 2015-11-25 10:27 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-11-21 15:53 | 2015-11-21 15:53 | ONSHORE | NV | 89705 | CARSON CITY | DOUGLAS | MILEPOST | CA-57.30 | CARSON LATERAL | MICA DRIVE RELOCATION | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 156 |  | YES |  |  |  |  | YES | UNCASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 8 |  | 0.188 | 42000 | API 5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | EXTRUDED POLYEHYLENE | [28 empty] | 1987 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 1.4 | 0.6 | [7 empty] | CLASS 3 LOCATION | NO |  | 126 |  | NO | NO | NO |  | 400000 | 437156.181593224 | 0 | 0 | 1479 | 1322.7676056338 | 27452 | 30002.0287427429 | 962 | 1051.3606167317 | 0 | 0 |  |  | 429893 | 216291.920874347 | 469532.338558332 | [8 empty] | 502 |  | 520 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 33370 | YES | [7 empty] | YES |  | YES | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A MECHANICAL PUNCTURE OCCURRED DURING AN IN-LINE INSPECTION (ILI) OF THE CARSON LATERAL. THE PUNCTURED LINE WAS ISOLATED FROM THE PARALLEL CARSON LOOP LINE. THE SCADA INFORMATION WAS LIMITED TO THE CARSON LOOP DUE TO THE PIPELINE CONFIGURATION AS PART OF THE ILI PROCEDURE. | [12 empty] | YES | 5 | 0 | YES | 2 | 0 | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [103 empty] | OTHER OUTSIDE FORCE DAMAGE | [9 empty] | PAIUTE PIPELINE WAS RUNNING AN INLINE INSPECTION TOOL THROUGH THE CARSON LATERAL. THE LEADING EYE OF THE MFL TOOL STRUCK THE INSIDE OF A LONG RADIUS 45 DEGREE ELBOW, PUNCTURING THE PIPE AND RESULTING IN A RUPTURE. | [251 empty] | KURTIS CARLSON | MANAGER OF ENGINEERING PAIUTE | kurtis.carlson@swgas.com | 775-887-2814 | 775-882-4346 |  |  |  | JEFF MAPLES | DIRECTOR OF GAS OPERATIONS PAIUTE | 775-887-2805 | jeff.maples@swgas.com | ON NOVEMBER 21, 2015, THE 8-INCH CARSON LATERAL WAS PUNCTURED ON THE SOUTH SIDE OF MICA DRIVE AT US-395 DURING AN IN-LINE INSPECTION (ILI) TOOL RUN. THE PUNCTURE OCCURRED AT A DROP SECTION CONTAINING 45-DEGREE ELBOWS INSTALLED IN 1987 AS PART OF A RELOCATION FOR THE CONSTRUCTION OF MICA DRIVE. AN INVESTIGATION ON THE CAUSE OF THE INCIDENT HAS BEEN COMPLETED AND IT WAS DETERMINED THAT DURING THE ILI OF THE CARSON LATERAL, THE LEADING EYE OF THE MFL TOOL STRUCK THE INSIDE OF THE 45 DEGREE ELBOW AND CAUSED A PUNCTURE IN THE PIPELINE. COMPANY EMPLOYEES AND CONTRACTORS WERE STATIONED AT THE SEGMENT ISOLATION VALVES AS PART OF THE ILI PROCEDURE ALLOWING FOR A RAPID RESPONSE AND SHUTDOWN OF THE PIPELINE AS PART OF THE ISOLATION PLAN. PUBLIC AND PRIVATE PROPERTY DAMAGE INCLUDES SIX VEHICLES AND A LANDSCAPE RETAINING WALL AS A RESULT OF THE BLOWING DIRT AND ROCKS. THE MAGNETIC FLUX LEAKAGE ILI TOOL WAS ALSO DAMAGED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150151 | 17189 | 2015-12-20 10:09 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2015-11-23 06:34 | 2015 |  |  | 38.8782 | -81.6905 | 1134088 | 2015-11-23 07:47 |  | NATURAL GAS |  | 10474 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | AFFECTED LINE SEMENT WAS ISOLATED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-11-23 06:34 | 2015-11-23 06:55 | ONSHORE | WV | 25275 | SANDYVILLE | JACKSON COUNTY | MILEPOST | C36-30 | RIPLEY COMPRESSOR STATION | BLOW-OFF VALVE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1999 |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENDED RELEASE OF NATURAL GAS DUE TO ACCUMULATED MOISTURE IN ESD PNEUMATIC SYSTEM | CLASS 2 LOCATION | NO |  | 244 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 19691 | 17610.9647887324 | 0 | 0 | 0 | 0 | 0 | 0 | THERE WERE NO OTHER ASSOCIATED COSTS |  | 19691 | 18258.0868544601 | 17610.9647887324 | [8 empty] | 875 |  | 1000 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ROOT CAUSE ANALYSIS INVESTIGATION INDICATED THAT GAS CONTROL PERSONNEL DID NOT PERFORM ANY ACTIVITIES OR HAD ANY OTHER INVOLVEMENTS CONTRIBUTING TO INITIATE THIS INCIDENT, | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | APPURTENANCE FAILURE | [16 empty] | YES |  |  |  |  | YES | BO VALVE ACTIVATION DUE TO ACCUMULATED MOISTURE | [161 empty] | GEORGE HAMATY | ENGINEER | ghamaty@cpg.com | (304) 357-3728 |  |  |  |  | JAMES M. PARKS | DIRECTOR | (713)386-3404 | jparks@cpg.com | ON NOVEMBER 23, 2015, A COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA) FACILITY WAS SUBJECT TO AN EVENT THAT INVOLVED AN UNINTENDED ACTIVATION OF AN 8-IN BLOW-OFF (BO) VALVE. THIS BO VALVE IS LOCATED IN RIPLEY COMPRESSOR STATION (CS) YARD. RIPLEY CS IS A TRANSMISSION FACILITY LOCATED NEAR THE TOWN OF SANDYVILLE, JACKSON COUNTY, WEST VIRGINIA IS OWNED, OPERATED AND MAINTAINED BY COLUMBIA. COLUMBIA OPERATIONS PERSONNEL RESPONDED TO THIS EVENT AND ISOLATED THE BO VALVE WITH ITS RESPECTIVE PIPELINE PREVENTING ADDITIONAL UNINTENDED RELEASE OF NATURAL GAS (MATERIAL) INTO ATMOSPHERE. THERE WAS NO PRESENCE OF FIRE, EXPLOSION OR EVACUATIONS IN LIEU OF THE MATERIAL RELEASE. THE INITIAL ASSESSMENT INDICATED THAT PRESENCE OF ACCUMULATED MOISTURE PLAYED A CONTRIBUTING FACTOR IN THE CHAIN OF EVENTS THAT LED TO THIS INCIDENT. THE EMERGENCY SHUTDOWN (ESD) SYSTEM TRIGGER PNEUMATIC PRESSURE ON THAT ACTUATOR BLED DOWN BELOW THE REQUIRED PRESSURE TO HOLD THE VALVE CLOSED. THE ESD PNEUMATIC PRESSURE TO ALL OTHER ESD VALVES REMAINED AT ITS FULL SYSTEM PRESSURE. AN ACCUMULATION OF APPROXIMATELY 2 GALLONS OF ACCUMULATED MOISTURE WAS DRAINED FROM THE ESD TRIGGER PNEUMATIC SUPPLY TANK, THAT IS LOCATED DIRECTLY DOWNSTREAM OF THE FACILITY'S AIR DRYER SYSTEM. A VENDOR TECHNICIAN WAS ON SITE THE FOLLOWING DAY OF THE INCIDENT WHERE A FULL ASSESSMENT TO THE AIR DRYER FOLLOWED. THE VENDOR'S TECHNICIAN IDENTIFIED THAT THE AIR DRYER SYSTEM'S AUTOMATIC CONTROL SYSTEM WAS LOCKED-UP. A MANUAL SWITCHING OPERATION WAS PERFORMED TO ENABLE THE FULL OPERATION OF THE TWO AIR DRYER SYSTEM TOWERS. THE ROOT CAUSE ANALYSIS (RCA) REPORT CONCLUDED THAT MOISTURE COLLECTED IN THE ESD TRIGGER PNEUMATIC TUBING FROZE WHICH ALLOWED THE PRESSURE ON THE ESD POPPET VALVE TO DECREASE TO THE POINT THAT THE VALVE TRIPPED AND THE BO VALVE OPENED. THE SOURCE OF MOISTURE WAS MOST LIKELY FROM THE ESD TRIGGER PNEUMATIC SUPPLY UNIT. ACCUMULATED MOISTURE WAS DISCOVERED IN THE ESD AIR STORAGE TANK. EVENTUALLY, THE CS AIR DRYER ALLOWED THE DEW POINT OF THE COMPRESSED AIR TO INCREASE. WHEN THE AMBIENT AIR TEMPERATURE DROPPED BELOW THE DEW POINT OF THE COMPRESSED AIR, THE WATER VAPOR CONDENSED IN THE ESD STORAGE TANK AND THE TRIGGER AIR PIPING. RECOMMENDATIONS: 1) COMPRESSOR STATIONS THAT USE A PNEUMATIC SYSTEM IN THEIR ESD SYSTEMS ARE RECOMMENDED TO CONSIDER INSTALLING A DEW POINT ANALYZER AT THE OUTLET OF THE AIR DRYER TO MONITOR PERFORMANCE AND PROVIDE AN ALARM OUTPUT TO THE CS CONTROLLER SO APPROPRIATE ACTIONS CAN BE TAKEN. 2) CONSIDER ADDING IN COLUMBIA'S WORK MANAGEMENT SYSTEM (WMS) A PREVENTIVE MAINTENANCE (PM) TASK TO THE ESD SYSTEM TO PERFORM AN ANNUAL PURGE TO THE PNEUMATIC SYSTEM AND VERIFY IF PRESENCE OF MOISTURE WAS IDENTIFIED. ALSO, CONSIDER THE ADDITION OF ANOTHER PM TO THE CRITICAL SHAFER ACTUATOR INSTALLATIONS TO INSPECT ROUTINELY THE SEALS FOR EVIDENCE OF DETERIORATION. SITE SPECIFIC: PER THE PROVIDED RECOMMENDATIONS IN THE RCA REPORT, A DEW POINT ANALYZER WITH CONTINUOUS FEEDBACK AND ALARM OUTPUT WAS INSTALLED WITH THE ADDITION OF THE APPROPRIATE PMS IN THE WMS.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20150152 | 17270 | 2015-12-22 12:00 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2015-11-26 12:37 | 2015 |  |  | 39.7257 | -78.4217 | 1134349 | 2015-11-26 15:16 |  | NATURAL GAS |  | 2618 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | UNIT NO. 2 FAULTED AND WAS ISOLATED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-11-26 12:37 | 2015-11-26 13:10 | ONSHORE | PA | 17211 | ARTEMAS | BEDFORD COUNTY | MILEPOST | RELIEF VALVE | ARTEMAS COMPRESSOR STATION | C58-84 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1970 |  | CARBON STEEL |  | LEAK |  |  | OTHER | FAILED UPSTREAM CHECK VALVE | [5 empty] | CLASS 1 LOCATION | NO |  | 113 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 4922 | 4402.07042253521 | 0 | 0 | 0 | 0 | 0 | 0 | NO ADDITIONAL COSTS |  | 4922 | 4563.82629107981 | 4402.07042253521 | [8 empty] | 1280 |  | 1650 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WAS NO INVESTIGATION INTO THE ACTIONS OF THE CONTROLLER SINCE THE FAILURE WAS IDENTIFIED DUE TO A FAILURE IN THE EQUIPMENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [5 empty] | YES | [29 empty] | YES | FAILED CHECK VALVE | [161 empty] | GEORGE HAMATY | ENGINEER | george_hamaty@transcanada.com | (304) 357-3728 |  |  |  |  | LEE ROMACK | MANAGER US REGULATORY COMPLIANCE | (832) 320-5315 | lee_romack@transcanada.com | ON NOVEMBER 26, 2015, A COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA) FACILITY WAS SUBJECT TO AN EVENT DUE TO AN UNINTENDED ACTIVATION OF AN INTERMEDIATE 4-IN RELIEF VALVE (RV) THAT EXCEEDED 3,000 MCF OF NATURAL GAS (MATERIAL). THIS RV IS LOCATED ON THE DISCHARGE LINE OF UNIT NO. 2 IN ARTEMAS COMPRESSOR STATION (CS). THIS FACILITY IS LOCATED NEAR THE TOWN OF ARTEMAS IN BEDFORD COUNTY, PENNSYLVANIA. COLUMBIA OWNS, OPERATES AND MAINTAINS THIS TRANSMISSION FACILITY. AFTER RECEIVING A CALL FROM COLUMBIA S MONITORING CENTER ABOUT A FAULT AT UNIT NO. 2, COLUMBIA OPERATIONS PERSONNEL RESPONDED TO THIS EVENT TO ADDRESS THE FAULTED UNIT. UPON REACHING THE SITE AND IDENTIFYING THE SOURCE OF THE BLOWING NOISE, COLUMBIA PERSONNEL ISOLATED THE PIPELINE TO PREVENT ADDITIONAL FLOW OF MATERIAL THROUGH THIS RV WHERE THE AREA WAS MADE SAFE AND SECURED. THERE WAS NO PRESENCE OF FIRE OR EXPLOSION IN LIEU OF THE MATERIAL RELEASE. THE INITIAL ASSESSMENT OF THIS INCIDENT INDICATED THAT A CONTRIBUTING FACTOR WAS A CHECK VALVE LOCATED UPSTREAM OF THE RV HAD FAILED TO OPERATE. HENCE, PROVIDING CONTINUOUS FLOW TO THE RV, WHICH IN TURN CONTINUED TO RELIEVE THE ADDITIONAL FLOW (AS IT WAS DESIGNED TO). UNIT NO. 2 AND THE ASSOCIATED PIPING WERE KEPT ISOLATED PENDING FURTHER INVESTIGATIONS, WHEREAS THE REST OF THE FACILITY WAS KEPT RUNNING IN ITS NORMAL OPERATIONAL MODE. THE FAILURE ANALYSIS INVESTIGATION REPORT IDENTIFIED AN ELEVATED LEVEL OF VIBRATION MAY HAVE BEEN A CONTRIBUTING FACTOR THAT TRIGGERED THE FAILURE OF THE HEADER CHECK VALVE (CV), HENCE INITIATING THE CHAIN OF EVENTS. THE CV FUNCITONS AS ASEPARATOR BETWEEN THE INTERMEDIATE DISCHARGE HEADER FROM THE HIGH PRESSURE DISCHARGE HEADER. AS A CORRECTIVE ACTION, ADDITIONAL BRACING WAS INTRODUCED TO THE SUSPECT SUBJECT PIPING TO ATTENUATE THE VIBRATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20150153 | 17068 | 2015-12-26 20:19 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2015-11-28 11:00 | 2015 |  |  | 36.7505 | -95.634 | 1134450 | 2015-11-28 16:04 |  | NATURAL GAS |  | 739 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-11-28 15:15 | 2015-12-23 17:16 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-11-28 12:36 | 2015-11-28 14:14 | ONSHORE | OK | 74027 | DELAWARE | NOWATA | SURVEY STATION NO. | 100/121+42 | LINE BE-008 | DELAWARE TB | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | OTHER | EXPOSUR IN A CREEK BED |  |  | YES | [6 empty] | YES | UNCASED | CALIFORNIA CREEK | UNKNOWN | BELOW WATER, PIPE ON OR ABOVE BOTTOM | [11 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 4 |  | 0.142 | 35000 | API | LONGITUDINAL ERW - LOW FREQUENCY |  | NEWPORT STEEL | FIELD APPLIED EPOXY | [28 empty] | 1958 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 1 | 11 | [7 empty] | CLASS 1 LOCATION | NO |  | 30 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 1430 | 1278.94366197183 | 276000 | 301637.765299324 | 2500 | 2732.22613495765 | 0 | 0 |  |  | 279930 | 141039.796395517 | 305648.935096254 | [8 empty] | 70 |  | 90 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 20646 | NO | [5 empty] | YES | NO PIGGING FACILITIES. LINE WOULD HAVE TO BE CUT TO RUN TETHERED TOOLS | YES |  | YES | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | NO | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [52 empty] | HEAVY RAINS/FLOODS |  | OTHER |  |  | HEAVY RAIN AND FLOODING CAUSE LARGE DEBRIS/TREE TO STRIKE THE 4" SSC PIPELINE THAT WAS EXPOSED IN THE CREAK DITCH. | NO | [306 empty] | DAVID COOMES | PIPELINE COMPLIANCE ENGINEER | david.coomes@sscgp.com | 2708524391 |  |  |  |  | DAVID SINCLAIR | PIPELINE COMPLIANCE MANAGER | 2708524424 | david.l.sinclair@sscgp.com | AT 12:36 ON 11/28/2015 SSC MEASUREMENT PERSONNEL RECEIVED A CALL FROM AN EMPLOYEE WITH OKLAHOMA NATURAL GAS NOTIFYING OF A LOW PRESSURE AT THE DELAWARE TB. WHILE IN ROUTE SSC MEASUREMENT NOTIFIED GAS CONTROL OF THE LOW PRESSURE NOTIFICATION. SSC GAS CONTROL REVIEWED SCADA AND COULD NOT SEE THE TB MEASUREMENT BECAUSE OF A COMMUNICATION OUTAGE DUE TO ICE ON THE EQUIPMENT. AT 14:05 ON 11/28/15 SSC GAS CONTROL RECEIVED A CALL FROM AN EMPLOYEE WITH UNION PACIFIC RAILROAD NOTIFYING OF A LEAKING PIPELINE IN CALIFORNIA CREEK NEAR THEIR RAILROAD. AT 14:08 SSC GAS CONTROL NOTIFIED SSC MEASUREMENT WHO WAS CURRENTLY IN ROUTE. SSC OPERATIONS ARRIVED ONSITE AT APPROXIMATELY 14:14. IT WAS DETERMINED THE UPSTREAM REGULATION VALVE WOULD BE CLOSED TO ELIMINATE THE BLOWING GAS. THE LINE WAS BLOWN DOWN AT 15:15 CAUSING THE GAS LOSS OF APPROXIMATELY 100 CUSTOMERS IN THE TOWN OF DELAWARE. CNG TANK TRUCKS WERE BROUGHT IN AND THE TOWN WAS RETURNED TO PRESSURE AND ALL CUSTOMERS WERE RELIT BY 8:21 ON 11/29/2015.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160001 | 17518 | 2016-01-06 16:53 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION LP (SPECTRA ENERGY CORP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2015-12-08 13:45 | 2015 |  |  | 36.386 | -86.1838 | 1135289 | 2015-12-08 14:42 |  | NATURAL GAS |  | 10 | 22775 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-12-08 15:10 | 2015-12-14 14:46 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-12-08 13:45 | 2015-12-08 13:45 | ONSHORE | TN | 37074 | Not Within a Municipality | TROUSDALE | MILEPOST | 307.7 | TEXAS EASTERN TRANSMISSION, LP 30-INCH LINE 10 | GLADEVILLE TO TOMPKINSVILLE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 30 |  | 0.375 | 52000 | API-5LX | DSAW |  | NATIONAL TUBE | COAL TAR | [9 empty] | PIPE GIRTH WELD | [18 empty] | 1952 | 1952 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 634 |  | NO | NO | NO |  | 0 | 0 | 52382 | 57247.7877605406 | 23 | 20.5704225352113 | 62000 | 67759.2081469497 | 0 | 0 | 0 | 0 |  |  | 114405 | 57402.8359513063 | 125027.566330025 | [8 empty] | 763 |  | 936 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 83538 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE RELEASE OF GAS WAS TOO SMALL TO BE DETECTED BY SCADA | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | YES | [7 empty] | YES | WELD DEFECT (LACK OF PENETRATION) | [12 empty] | YES | [63 empty] | YES | YES |  |  | YES |  |  |  | 2014 | [31 empty] | 2014 | [23 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | deteschendorf@spectraenergy.com | 713-627-5573 | 713-386-4468 |  |  |  | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 713-627-5008 | nyatanu@spectraenergy.com | ON DECEMBER 8, 2015 A LANDOWNER IN TROUSDALE COUNTY, TENNESSEE REPORTED SIGNS OF A NATURAL GAS LEAK TO SPECTRA ENERGY. COMPANY PERSONNEL CONFIRMED NATURAL GAS WAS BEING RELEASED AT A SLOW RATE FROM THE TEXAS EASTERN TRANSMISSION, LP 30-INCH LINE 10 AT MILEPOST 307.70. SPECTRA ENERGY EXCAVATED THE PIPELINE AND DETERMINED THE LEAKS WAS THE RESULT OF A CRACK IN THE GIRTH WELD. METALLURGICAL TESTING DETERMINED THE CRACK WAS CAUSED BY A WELD DEFECT (LACK OF PENETRATION) THAT WAS SUBJECTED TO SECONDARY LOADING. THE AFFECTED JOINT OF PIPE WAS REPLACED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160002 | 17167 | 2016-01-08 09:50 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2015-12-10 14:50 | 2015 |  |  | 35.7407 | -97.6512 | 1135561 | 2015-12-11 14:10 |  | NATURAL GAS |  | 5510 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-12-11 09:57 | 2015-12-11 13:09 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-12-11 09:56 | 2015-12-11 12:14 | ONSHORE | OK | 73016 | Not Within a Municipality | LOGAN COUNTY | MILEPOST | 100/2+30 | LINE VH-013 | CASHION PLD | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2014 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE ACTIVATION CAUSED A RELEASE OF MORE THAN 3 MMCF | CLASS 1 LOCATION | NO |  | 63 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 10138 | 9067.08450704225 | 1000 | 1092.89045398306 | 2000 | 2185.78090796612 | 0 | 0 |  |  | 13138 | 10905.2548848498 | 12345.7558689914 | [8 empty] | 585 |  | 720 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | THE RELIEF VALVE ACTIVATED CORRECTLY. THIS INCIDENT WAS BASED ON THE GAS LOSS EXCEEDING THE 3 MILLION LIMIT. THE CUSTOMER DELIVERED A HIGH PRESSURE GAS TO THE SSC LINE AND THE RELIEF VALE ACTIVATED TO PROTECT THE MAOP OF THE DOWNSTREAM PIPING. | [147 empty] | DAVID COOMES | PIPELINE COMPLIANCE ENGINEER | david.coomes@sscgp.com | 2708524391 |  |  |  |  | DAVID SINCLAIR | PIPELINE COMPLIANCE MANAGER | 2708524424 | david.l.sinclair@sscgp.com | ON 12/11/2015 AT 09:56 AM SSC GAS CONTROL RECEIVED PHONE CALL FROM A SUPERIOR CASHION EMPLOYEE STATING THAT THE RELIEF VALVE ON THE SSC CASHION SETTING WAS RELEASING GAS. WHILE ON THE PHONE SSC GAS CONTROL ISSUED A ZERO SET POINT AT THE FLOW CONTROL FOR THE SSC CASHION SETTING AND THE RELEASE OF GAS WAS CONFIRMED TO BE STOPPED AT 09:57. AT 09:58 SSC GAS CONTROL NOTIFIED PSAP THAT A RELIEF VALVE HAD BEEN GOING OFF IN THE AREA BUT HAD BEEN CONFIRMED TO HAVE STOPPED. SSC GAS CONTROL NOTIFIED SSC OPERATIONS AT 09:58 TO TRAVEL TO THE SITE TO INVESTIGATE THE ISSUE. SSC OPERATIONS ARRIVED ON SITE AT 12:12, AFTER INITIAL TESTING THE RELIEF VALVE ACTIVATED DURING TEST AT SET PRESSURE AND RESEATED PROPERLY. NO ISSUES WERE FOUND WITH THE RELIEF VALVE. SSC GAS CONTROL REVIEWED FLOWS OF THE SETTING AND IT WAS DISCOVERED THAT THE METER BEGAN SHOWING NO FLOW AT APPROXIMATELY 15:00 ON 12/10/15. BEFORE THAT POINT THE METER WAS RECEIVING BETWEEN 5-6 MMCF/DAY RATE. AFTER DISCUSSING THIS WITH SUPERIOR CASHION, THEY STATED THEY HAD NOT SHUT DOWN THEIR FLOWS. AT THE TIME WHEN THE FLOW WENT TO 0 THE PRESSURE ON THE SEGMENT WAS AT 360 PSIG, 53 POUNDS UNDER MAOP, AND THEN DROPPED AND SETTLED AT 343 PSIG. IT IS BELIEVED THAT THE RELIEF VALVE BEGAN RELIEVING AT 14:50 ON 12/10/2015 AND CONTINUED TO BLOW UNTIL THE NEXT MORNING WHEN SSC RECEIVED A CALL. THE PRESSURE SHOWED A STABILIZATION BECAUSE THERE IS A CHECK VALVE BETWEEN THE RELIEF AND THE METER SETTING AND THE CLOSURE OF THIS VALVE TO PREVENT BLOWING DOWN THE SSC MAINLINE WOULD CAUSE THE METER SETTING TO MEASURE THE SAME PRESSURE AS THE MAINLINE WITH 0 FLOW. SSC CONTACTED THE CUSTOMER AND DETERMINED THERE WAS A PERIOD WHEN THEY HAD DELIVERED HIGHER PRESSURE GAS. ONCE THE HIGH PRESSURE GAS SLUG REACHED THE RELIEF VALVE IT ACTIVATED. THE RELIEF VALVE ACTIVATED AS INTENDED, BUT SSC WAS NOT ABLE TO SEE THE GAS RELEASE DUE TO THE CLOSURE OF THE CHECK VALVE. BECAUSE THE CUSTOMER HAD REACHED NOMINATION FOR THE DAY GAS CONTROL DID NOT SEE ANY ISSUE WITH THE METER READING 0 FLOW (NO FLOW). SSC HAS INSTALLED A NEW TRANSMITTER FOR THE METER SETTING UPSTREAM OF THE RELIEF VALVE TO DETERMINE A DIFFERENCE IN PRESSURE ON EITHER SIDE OF THE CHECK VALVE IF CLOSED AND AID IN THE NOTIFICATION OF RELIEVING GAS IN THE FUTURE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160003 | 16979 | 2016-01-14 13:32 | ORIGINAL | 31604 | EQT MIDSTREAM | 2200 ENERGY DRIVE | CANONSBURG | PA | 15317 | 2015-12-23 10:15 | 2015 |  |  | 39.913 | -80.1278 | 1136506 | 2015-12-23 13:08 |  | NATURAL GAS |  | 6075.43 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-12-23 10:15 | 2015-12-23 13:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-12-23 10:15 | 2015-12-23 10:15 | ONSHORE | PA | 15370 | WAYNESBURG | GREENE | MILEPOST | ESD VLV 8109 | PRATT COMPRESSOR STATION | H137 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | ESD SYSTEM | 1950 |  | CARBON STEEL |  | OTHER | [8 empty] | EXTENDED VENTING OF ESD SYSTEM | CLASS 1 LOCATION | NO |  | 283 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 14067 | 12581.0492957746 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 14067 | 13043.3450704225 | 12581.0492957746 | [8 empty] | 329 |  | 605 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATOR WAS ON SITE WHEN STATION WENT IN TO ESD. HE WAS HANDLING THE PROBLEM BEFORE THE CONTROL WAS EVEN NEEDED TO DETERMINE IT WAS A PROBLEM. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | ESD BLOCK VALVE | [161 empty] | JACOB LYONS | MANAGER OF PIPELINE SAFETY AND COMPLIANCE | jlyons@eqt.com | 412-553-7870 |  |  |  |  | JACOB LYONS | MANAGER OF PIPELINE SAFETY AND COMPLIANCE | 412-553-7870 | jlyons@eqt.com | AT APPROXIMATELY 10:15 AM ON DECEMBER 23RD, 2015 PRATT GASKET LEAK AT PRATT COMPRESSOR STATION TRIGGERED THE GAS DETECTORS CAUSING AN ESD. THE COMPRESSOR TECHNICIAN ON SITE DETERMINED ALL OF THE ESD VALVES CYCLED CORRECTLY EXCEPT ONE MAINLINE VALVE WHICH ALLOWED CONTINUED GAS VENTING TO ATMOSPHERE. THE VALVE THAT WAS PARTIALLY OPEN WAS MANUALLY CLOSED BY THE COMPRESSOR TECHNICIAN BY 10:40 AM. THE VALVE WAS GREASED AND CYCLED MULTIPLE TIMES TO ENSURE NORMAL OPERATION BEFORE BEING PUT BACK IN SERVICE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160004 | 17082 | 2016-01-15 23:16 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2015-12-21 08:25 | 2015 |  |  | 42.8745 | -75.1673 | 1136314 | 2015-12-21 10:18 |  | NATURAL GAS |  | 5780 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-12-21 08:25 | 2015-12-21 11:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-12-21 08:25 | 2015-12-21 08:25 | ONSHORE | NY | 13491 | WEST WINFIELD | HERKIMER | SURVEY STATION NO. | STATION 245 | TENNESSEE GAS PIPELINE COMPRESSOR STATION 245 | TENNESSEE GAS PIPELINE COMPRESSOR STATION 245 | YES | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2015 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL | OTHER | [8 empty] | THE CHECK VALVE ON THE FUEL GAS SYSTEM FAILED CAUSING THE ESD BLOW OFF VALVE TO OPEN. | CLASS 1 LOCATION | NO |  | 152 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 10982 | 9821.92957746479 | 1500 | 1639.33568097459 | 0 | 0 | 0 | 0 |  |  | 12482 | 10935.3387100306 | 11461.2652584394 | [8 empty] | 545 |  | 760 | OTHER | PRESSURE TEST |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | OTHER | ESD ALARM |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | WAS NOT A CONTROLLLER ACTION BASED ISSUE. | [12 empty] | YES | 1 | 0 | NO |  |  | EQUIPMENT FAILURE | FAILURE OF EQUIPMENT BODY (EXCEPT COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL | MATERIAL/WELD/EQUIP FAILURE | FAILURE OF EQUIPMENT BODY | [166 empty] | FAILURE OF EQUIPMENT BODY (EXCEPT COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL | [35 empty] | YES | CHECK VALVE WAS NOT CORRECTLY SELECTED FOR SYSTEM | [161 empty] | VALERIE BERGMAN | PIPELINE ENGINEER I | valerie_bergman@kindermorgan.com | 713-420-4810 |  |  |  |  | VALERIE BERGMAN | PIPELINE ENGINEER I | 713-420-4810 | valerie_weaver@kindermorgan.com | ON 12/21/2015 AT 8:25 AM (LOCAL TIME)TENNESSE GAS PIPELINE EXPERIENCED AN ESD AT COMPRESSOR STATION 245 IN WEST WINFIELD, NY. IT WAS DETERMINED THAT STATION 245 C-BUILDING INITIATED A FUEL GAS SHUTDOWN WHEN A RUPTURE DISC ACTIVATED DURING MAINTENANCE ACTIVITIES ON THE BOILER WATER HEATING SYSTEM. SLIGHT GAS PRESSURE INADVERTENTLY CHARGED THE RED ESD PIPING DUE TO AN IMPROPERLY RATED 1/2 INCH CHECK VALVE. THIS CAUSED THE 8 INCH SUCTION ESD BLOW OFF VALVE TO OPEN, BUT DID NOT SUPPLY ENOUGH PRESSURE TO CLOSE THE SIDE VALVES. A&B BUILDINGS ALSO SHUT DOWN DUE TO FUEL LOSS WHEN THE FUEL VALVE BLOCKED AND BLED. THERE WAS AN UNINTENTIONAL RELEASE OF 5,780 MCF OF NATURAL GAS.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160005 | 17145 | 2016-01-20 15:43 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2015-12-27 14:00 | 2015 |  |  | 30.3433 | -101.5936 | 1137484 | 2016-01-07 12:08 |  | NATURAL GAS |  | 135 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE COMPRESSOR WAS NOT OPERATING AT THE TIME OF THE INCIDENT. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-12-27 14:00 | 2015-12-27 14:00 | ONSHORE | TX | 76950 | Not Within a Municipality | CROCKETT | MILEPOST | COMPRESSOR | PECOS RIVER COMPRESSOR STATION | LINE 146 / GREY RANCH - NEW BRAUNFELS | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | UNKNOWN |  | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 620 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 300 | 268.30985915493 | 70000 | 76502.3317788141 | 0 | 0 | 0 | 0 |  |  | 70300 | 35394.7579547907 | 76770.6416379691 | [8 empty] | 650 |  | 899 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 20 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE COMPRESSOR ON THE PIPELINE INVOLVED WAS NOT IN OPERATION AT THE TIME OF THE DISCOVERY OF THE LEAK. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [30 empty] | YES | WORN PACKING | [161 empty] | RICHARD S. ROMERO | SR. PIPELINE COMPLIANCE ENGINEER | rsromero@eprod.com | 713-381-6841 |  |  |  |  | RICHARD S. ROMERO | SR. PIPELINE COMPLIANCE ENGINEER | 713-381-6841 | rsromero@eprod.com | ON 12/27/2015 AT 2:00 PM, AN OPERATOR NOTICED A SMALL LEAK FROM THE VALVE STEM OF A VALVE AT THE INLET OF A COMPRESSOR AT THE PECOS RIVER COMPRESSOR STATION. AT THE TIME THE LEAK WAS IDENTIFIED, THE COMPRESSOR WAS NOT OPERATING. THE PIPING WAS BLOWN DOWN AND THE VALVE WAS ISOLATED BY INSTALLING BLINDS ON EITHER SIDE. ON 1/7/16 AT 11:20 AM, IT WAS DETERMINED THAT THE VALVE NEEDED TO BE REPLACED AND THE COST WOULD EXCEED $50,000 AT WHICH TIME THE NRC WAS IMMEDIATELY NOTIFIED. ESTIMATED COSTS ARE $27,000 FOR THE VALVE AND $43,000 FOR INSTALLATION FOR AN APPROXIMATE TOTAL OF $70,000. THE REPLACEMENT VALVE IS ON ORDER. ON 2/29/16, OPERATIONS VERIFIED THAT THE VALVE WAS REPLACED AND THE PIPELINE IS READY FOR SERVICE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160006 | 17089 | 2016-01-20 18:05 | SUPPLEMENTAL FINAL | 840 | MOJAVE PIPELINE OPERATING COMPANY | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2015-12-24 20:08 | 2015 |  |  | 34.8514 | -116.8504 | 1136620 | 2015-12-25 22:12 |  | NATURAL GAS |  | 14707 | 20 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | STATION WAS OFFLINE SINCE JAN 2015. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-12-24 20:08 | 2015-12-24 20:08 | ONSHORE | CA | 92327 | DAGGETT | SAN BERNADINO | SURVEY STATION NO. | DAGGETT STN. | MOJAVE DAGGETT COMPRESSOR STATION | MOJAVE DAGGETT COMPRESSOR STATION | YES | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | INSTRUMENTATION | [38 empty] | 1992 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | FAULTY LIMIT SWITCH | OTHER | [8 empty] | FAULTY LIMIT SWITCH FOR THE SUCTION VALVE WAS OUT OF ADJUSTMENT, INDICATED TO CONTROL ROOM THAT SUCTION VALVE WAS FULLY CLOSED. VALVE DID NOT CLOSE PROPERLY, ALLOWING GAS TO VENT OUT TO ATMOSPHERE. | CLASS 1 LOCATION | NO |  | 127 |  | NO | NO | NO |  | 0 | 0 | 40 | 43.7156181593224 | 29414 | 26306.8873239437 | 3129 | 3419.65423051299 | 0 | 0 | 0 | 0 |  |  | 32583 | 28863.3227488404 | 29770.257172616 | [8 empty] | 57 |  | 941 | OTHER | PRESSURE TEST |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | OTHER | FAULTY LIMIT SWITCH | [20 empty] | YES | FAULTY LIMIT SWITCH | [161 empty] | VALERIE BERGMAN | PIPELINE ENGINEER I-COMPLIANCE | valerie_bergman@kindermorgan.com | 7134204810 |  |  |  |  | VALERIE BERGMAN | PIPELINE ENGINEER I-COMPLIANCE | 7134204810 | valerie_bergman@kindermorgan.com | ON 12/24/15 AT 6:30 PM PST, THE DAGGETT FIRE DEPARTMENT NOTIFIED MOJAVE KM PERSONNEL OF AN ODOR COMPLAINT COMING FROM THE DAGGETT COMPRESSOR STATION. AT 6:39 PM: A TECHNICIAN WAS DISPATCHED TO INVESTIGATE THE COMPLAINT. AT 8:08 PM: THE TECHNICIAN ARRIVED ON SITE AND AFTER INSPECTING THE SITE HE DISCOVERED THAT THE UNIT VENT VALVE WAS OPEN AND VENTING GAS. AT 8:42 PM: THE TECH MANUALLY ISOLATED THE LEAK BY CLOSING THE LOADING VALVE. AT 10:12 PM: THE NRC WAS NOTIFIED OF THE RELEASE BY KM CODES AND STANDARDS PERSONNEL. AN INTERNAL INVESTIGATION WAS PERFORMED AND IT WAS DETERMINED THAT THE ROOT CAUSE FOR THIS INCIDENT INVOLVED A FAULTY LIMIT SWITCH THAT RESULTED IN A SUCTION VALVE NOT CLOSING PROPERLY. MOJAVE PERSONNEL WERE ATTEMPTING TO START THIS UNIT AT DAGGETT STATION AS A PART OF THEIR ANNUAL MAINTENANCE ON DECEMBER 22, 2015. DAGGETT STATION WAS OFFLINE AT THE TIME OF THE INCIDENT. THE LIMIT SWITCH WAS REPLACED AND FREQUENCY OF INSPECTIONS/MAINTENANCE ON LIMIT SWITCHES AND VALVES HAVE BEEN INCREASED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160007 | 17157 | 2016-01-22 12:06 | SUPPLEMENTAL FINAL | 15105 | PANHANDLE EASTERN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2015-12-28 22:20 | 2015 |  |  | 41.2832 | -84.4624 | 1136836 | 2015-12-28 23:41 |  | NATURAL GAS |  | 21402.5 | 9177.7 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-12-28 22:52 | 2016-01-01 16:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 50 | 2015-12-28 22:20 | 2015-12-28 21:48 | ONSHORE | OH | 43512 | DEFIANCE | DEFIANCE | MILEPOST | 24.67 | EDGERTON 100 LINE | 41-07-001-3000 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 37 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | 22IN DRESSER STYLE 38 COUPLING | 1936 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | RUBBER COMPOUND GASKET | LEAK |  |  | OTHER | LARGE VOLUME COUPLING LEAK | [5 empty] | CLASS 1 LOCATION | NO |  | 419 |  | NO | NO | NO |  | 15000 | 16393.3568097459 | 21751 | 23771.4602645855 | 50724 | 45365.8309859155 | 85500 | 93442.1338155515 | 1000 | 1092.89045398306 | 62000 | 67759.2081469497 | GOOD WILL AND METALLURGICAL ANALYSIS |  | 235975 | 139966.862870762 | 247824.880476731 | [8 empty] | 714 |  | 760 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 103244 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 4 | 0 | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | OTHER | COUPLING SLIP. | [5 empty] | YES | [175 empty] | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | ON DECEMBER 28, 2015, THE PANHANDLE EASTERN PIPE LINE COMPANY 22-INCH EDGERTON 100 LINE EXPERIENCED AN UNINTENTIONAL IN-SERVICE RELEASE. THE APPROXIMATE LOCATION WAS 18736 SWITZER ROAD, IN DEFIANCE COUNTY, NEAR DEFIANCE OHIO. THERE WERE NO INJURIES, LOCAL OPERATIONS CONFIRMED THAT 25 HOMES WERE EVACUATED WITH A TOTAL OF APPROXIMATELY 50 PEOPLE. A ROOT CAUSE FAILURE ANALYSIS WAS PERFORMED TO DETERMINE THE CAUSE. THIS SUPPLEMENTAL/FINAL REPORT UPDATES PART D - 7.D - ESTIMATED OTHER COSTS AND PART G - G6 - EQUIPMENT FAILURE, BASED ON THE ROOT CAUSE FAILURE ANALYSIS.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160008 | 17406 | 2016-01-22 13:44 | SUPPLEMENTAL FINAL | 31846 | DOMINION CAROLINA GAS TRANSMISSION, LLC | 121 MOORE HOPKINS LANE | COLUMBIA | SC | 29210 | 2016-01-12 14:11 | 2016 |  |  | 34.4244 | -80.3325 | 1137896 | 2016-01-12 15:26 |  | NATURAL GAS |  | 5270 | 66 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-01-12 15:53 | 2016-01-13 17:40 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-01-12 14:11 | 2016-01-12 14:53 | ONSHORE | SC | 29009 | Not Within a Municipality | KERSHAW | MILEPOST | 84.8 | LINE A | 11-410 MLV RD #341 TO 18-000 BETHUNE CS | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | EXPOSED DUE TO WASHOUT |  |  | YES | [6 empty] | YES | UNCASED | DRAINAGE DITCH | 1 | BELOW WATER, PIPE ON OR ABOVE BOTTOM | [11 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 10 |  | 0.219 | 42000 | X42 | LONGITUDINAL ERW - LOW FREQUENCY |  | JONES & LAUGHLIN | COLD APPLIED TAPE | [28 empty] | 1958 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 480 | 31.4 |  | CLASS 1 LOCATION | NO |  | 68 |  | NO | NO | NO |  | 0 | 0 | 142 | 153.770841192003 | 11383 | 11689.8194070081 | 31764 | 34397.0211241041 | 10996 | 11907.4941531498 | 0 | 0 |  |  | 54285 | 33444.9457922098 | 58148.105525454 | [8 empty] | 474 |  | 500 | 192.619(A)(4) |  |  |  | PRESSURE DID NOT EXCEED MAOP | YES | NO | NOT MANDATED |  |  | MANUAL | MANUAL | 43296 | NO |  |  |  | YES |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS DUE TO MECHANICAL DAMAGE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OPERATOR | [260 empty] | LAURA COMSTOCK | MANAGER REGULATORY AND OPERATIONS SUPPORT | laura.a.comstock@dominionenergy.com | 803-888-3450 |  |  |  |  | LAURA COMSTOCK | MANAGER REGULATORY AND OPERATIONS SUPPORT | 803-888-3450 | laura.a.comstock@dominionenergy.com | AN OPERATOR RIGHT-OF-WAY MOWING CREW WAS OPERATING A FRONT-MOUNTED TREE CUTTER NEAR A DRAINAGE DITCH. WET CONDITIONS DUE TO RECENT RAINS AND FLOODING CAUSED THE TRACTOR'S FRONT TIRE TO SINK INTO THE BANK OF THE DITCH CAUSING THE TREE CUTTER BLADES TO CONTACT THE EXPOSED PIPE UNDER THE WATER SEVERING THE PIPE AND CAUSING THE PIPE TO RUPTURE AT THE LONGITUDINAL SEAM. THE TRACTOR AUTOMATICALLY SHUT DOWN ON POWER TAKE OFF (PTO) STRESS SO THERE WAS NO IGNITION OF THE LEAKING GAS. THE TRACTOR OPERATOR RECEIVED A HEAD LACERATION AND WAS TREATED AND RELEASED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160009 | 16989 | 2016-01-25 11:02 | ORIGINAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2016-01-10 07:45 | 2016 |  |  | 35.2348 | -93.7658 | 1137711 | 2016-01-10 09:27 |  | NATURAL GAS |  | 12819 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELIEF AT COMPRESSOR STATION | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-01-10 07:45 | 2016-01-10 07:45 | ONSHORE | AR | 72943 | Not Within a Municipality | LOGAN | MILEPOST | DUNN STATION | DUNN COMPRESSOR STATION | DUNN STATION SUCTION HEADER | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | REGULATOR MALFUNCTION DUE TO ICE AND DEBRIS | CLASS 2 LOCATION | NO |  | 621 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 28202 | 28962.1617250674 | 0 | 0 | 0 | 0 | 0 | 0 | N/A |  | 28202 | 30026.3881401617 | 28962.1617250674 | [8 empty] | 600 |  | 900 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER DI NOT CONTRIBUTE TO THE CAUSE, ICE AND TRASH IN REGULATOR. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [25 empty] | YES | ICE AND DEBRIS IN REGULATOR | [161 empty] | JIMMY CROSS | DOT COMPLIANCE MANAGER | jimmy.cross@enablemidstream.com | 3184293664 |  |  |  |  | JOHNNY CAVITT | SENIOR MANAGER OF DOT COMPLIANCE PROGRAMS | 3184293606 | johnny.cavitt@enablemidstream.com | PUBLIC NOTIFIED COMPANY EMPLOYEE OF POSSIBLE RELIEF THAT WAS VENTING AT DUNN STATION. EMPLOYEE INVESTIGATED AND FOUND A 6 INCH RELIEF VENTING ON THE SUCTION HEADER OF THE STATION. HE SECURED THE VENT AT 08:25. AT 8:50 EMPLOYEE CONTACTED SYSTEM CONTROL TO REPORT OUT THE EVENT. HE FOUND ICE AND TRASH IN THE REGULATOR. IT WAS CLEANED AND THEN RETURNED TO SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160010 | 17032 | 2016-01-27 11:56 | SUPPLEMENTAL FINAL | 2564 | COLORADO INTERSTATE GAS CO | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2016-01-02 02:53 | 2016 |  |  | 39.6077 | -104.1757 | 1137113 | 2016-01-02 06:36 |  | NATURAL GAS |  | 35392 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-01-02 03:35 | 2016-01-07 10:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-01-02 02:53 | 2016-01-02 03:24 | ONSHORE | CO | 80103 | Not Within a Municipality | ARAPAHO | MILEPOST | MP 5 PLUS 498 | LATIGO STORAGE | LATIGO LATERAL LINE - LINE 0103A | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | INSTRUMENTATION | [38 empty] | 1976 |  | CARBON STEEL |  | OTHER | [8 empty] | CONDENSATE IN INSTRUMENT AIR LINES FROZE CAUSING MALFUNCTION OF VENT VALVES | CLASS 1 LOCATION | NO |  | 342 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 130000 | 133504.043126685 | 14000 | 15160.5054696341 | 1000 | 1082.89324783101 | 0 | 0 |  |  | 145000 | 145865.852127204 | 149747.44184415 | [8 empty] | 798 |  | 960 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | FROZEN INSTRUMENT AIR PIPING AT FACILITY; NOT A CONTROL ROOM ISSUE; | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | YES | [31 empty] | YES | [164 empty] | WM MARTIN MULLER | SPECIALIST PIPELINE TECHNICAL | martin.muller@kindermorgan.com | 205 325 3863 | 205 325 3508 |  |  |  | REJI GEORGE | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713 420 5433 | reji_george@kindermorgan.com | 02:53 CIG TOTEM STATION NOTICED PRESSURE CHANGE AT LATIGO STATION AND CALLED OUT TECHNICIANS TO RESPOND; CIG GAS CONTROL ALSO NOTICED PRESSURE CHANGE; 03:24 TECHNICIANS ARRIVED AT LATIGO STATION AND CONFIRMED TWO 6-INCH VENT VALVES WERE RELEASING NATURAL GAS; TECHNICIANS ATTEMPTED TO STOP THE NATURAL GAS RELEASE BY USE OF STATION ESD SYSTEM; STATION ESD SYSTEM DID NOT FUNCTION PROPERLY; 03:30 A LOCAL FIRE CHIEF ARRIVED, NOTIFIED BY LANDOWNERS; BY THIS TIME LANDOWNERS HAD ALSO CALLED CIG GAS CONTROL; 03:34 TECHNICIANS COMPLETED CLOSING STATION BLOCK VALVE THUS STOPPING THE RELEASE OF NATURAL GAS; WITH THE VALVE CLOSURE, THE STATION WAS SHUT IN AND ISOLATED; INVESTIGATION FOUND FROZEN AIR SUPPLY LINES INCLUDING FROZEN INSTRUMENT AIR LINES; SAID FROZEN LINES ALLOWED THE TWO 6-INCH VENT VALVES TO OPEN; SAID FROZEN LINES PREVENTED THE ESD SYSTEM FROM PROPER FUNCTION; THE AIR SUPPLY SYSTEM WAS FLUSHED; A NEW AIR DRYER WAS INSTALLED IN THE AIR SUPPLY SYSTEM; LATIGO STATION SHUT IN WAS TERMINATED 10:00, 01/07/2016;
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160011 | 17163 | 2016-01-27 19:49 | SUPPLEMENTAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2015-12-28 05:55 | 2015 |  |  | 35.7451 | -94.0448 | 1136804 | 2015-12-28 14:00 |  | NATURAL GAS |  | 46086 | 8484 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-12-28 07:11 | 2015-12-31 08:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-12-28 05:55 | 2015-12-28 07:05 | ONSHORE | AR | 72959 | Not Within a Municipality | CRAWFORD | SURVEY STATION NO. | 2108+60 | ENABLE GAS TRANSMISSION | OM-1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 20 |  | 0.281 | 60000 | API 5L X60 | FLASH WELDED |  | AO SMIITH | COAL TAR | [28 empty] | 1986 | 1968 | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | INITIATED IN THE CIRCUMFERENTIAL ORIENTATION AND THEN INTERSECTS LONG SEAM OF THE PIPE | 336 | 50 |  | CLASS 1 LOCATION | NO |  | 436 |  | NO | NO | NO |  | 0 | 0 | 18402 | 20111.3701341963 | 99964 | 89404.4225352113 | 500000 | 546445.226991529 | 1000 | 1092.89045398306 | 0 | 0 |  |  | 619366 | 353255.717684298 | 657053.91011492 | [8 empty] | 853 |  | 1000 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 95040 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [5 empty] | YES | MAOP WAS NOT EXCEEDED. NO SET POINTS WERE CHANGED NOR ANY HORSEPOWER BY CONTROLLER | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [52 empty] | HEAVY RAINS/FLOODS |  | MUDSLIDE |  |  |  | YES |  |  |  | YES | REPEATED HEAVY RAIN EVENTS | [301 empty] | JIMMY CROSS | DOT COMPLAINCE MANAGER | jimmy.cross@enablemidstream.com | 405 576-8230 |  |  |  |  | JIMMY CROSS | DOT COMPLIANCE MANAGER | 405 576-8230 | jimmy.cross@enablemidstream.com | ON DECEMBER 28, 2015 AT 05:55 HRS. SCADA INDICATED THAT A LEAK WAS OCCURRING ON ENABLE GAS TRANSMISSIONS OM-1 PIPELINE. THE ENABLE CONTROLLER INITIATED THE EMERGENCY PLAN AND NOTIFIED FIELD PERSONNEL TO RESPONSE TO KEY LOCATIONS TO CLOSE MAINLINE VALVES. MAINLINE VALVE WERE CLOSED AT 07:11 HOURS TO ISOLATE THE LEAK. NOTE: AFTER VALIDATING THIS EVENT ENABLE ATTEMPTED TO CONTACT NRC TO REPORT IT FOUR TIMES . THERE WAS NO ANSWER AND OPTION TO LEAVE A MESSAGE. NRC CONTACT WAS MADE LATER IN THE DAY AT 2PM. FOLLOWING THE INCIDENT ENABLE TOOK THE FOLLOWING ACTIONS: 1. IMPLEMENTED EARTH MOVEMENT P&M MEASURES REQUIRING QUARTERLY LINE PATROLS AND ADDITIONAL LINE PATROLS TRIGGERED BY SIGNIFICANT RAINFALL EVENTS OR EARTHQUAKES IN THE AREA. 2. COMPARED 2008 ILI DATA TO 2015 ILI DATA TO SEE IF THERE WAS ANY INDICATIONS THAT RIPPLES HAD GROWN. NO GROWTH NOTED. 3. REVIEWED ILI DATA LOOKING SPECIFICALLY FOR RIPPLE INDICATIONS. 4. THE ILI VENDOR DID NOT REPORT ANY RIPPLES DUE TO THEIR SMALL SIZE. THEY WERE NOT DETECTED BY HR DEFORMATION TOOL. 5. ENABLE ILI ANALYSTS REVIEWED THE RAW DATA AND WERE ABLE TO IDENTIFY SOME MINOR RIPPLES. 6. COMPARED RIPPLE LOCATIONS TO TERRAIN & ELEVATION CHANGES. 7. OVERLAID RIPPLE LOCATIONS OVER TOPOGRAPHICAL PROFILE & HAD SES SOILS EXPERT EVALUATE RESULTS. 8. SES SOILS EXPERT PERFORMED A FIELD VISIT TO SPECIFICALLY LOOK FOR EARTH MOVEMENT AND SOIL STABILITY IN VICINITY OF RIPPLES 9. UPDATED P&M MEASURES BASED ON SES SOILS EXPERT INPUT 10. REMOVED 450 FEET OF PIPE IN AN AREA OF EARTH MOVEMENT DISCOVERED DURING LINE PATROL. 11. REMEDIATED AND STABILIZED THE EARTH MOVEMENT AREA. 12. SELECTED A JOINT OF PIPE WITH RIPPLES TO BE ANALYZED AND TESTED TO FAILURE BY SES. 13. SELECTED A JOINT OF PIPE WITH GIRTH WELD TO BE ANALYZED AND TESTED TO FAILURE BY SES. 14. PIPE JOINTS AT SES AND ANALYSIS COMPLETED. 15. NO ADDITIONAL ACTIONS WARRANTED AT THIS TIME.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160012 | 17224 | 2016-02-04 17:40 | SUPPLEMENTAL FINAL | 31978 | ATMOS PIPELINE - TEXAS | 5420 LBJ FREEWAY, SUITE 1800 | DALLAS | TX | 75240 | 2016-01-09 15:55 | 2016 |  |  | 31.0348 | -96.1607 | 1137697 | 2016-01-09 18:15 |  | NATURAL GAS |  | 195573 | 329 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-01-09 19:10 | 2016-02-13 17:00 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 6 | 2016-01-09 16:46 | 2016-01-09 17:02 | ONSHORE | TX | 77856 | Not Within a Municipality | ROBERTSON | SURVEY STATION NO. | 676537 | V | 1794 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 |  | 0.333 | 60000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | US STEEL | COAL TAR | [28 empty] | 1967 | 1967 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 540 | 30 |  | CLASS 1 LOCATION | NO |  | 641 |  | NO | NO | NO |  | 252730 | 273679.61052433 | 664 | 719.041116559789 | 471330 | 484034.312668464 | 2478671 | 2684136.08949453 | 8125 | 8798.50763862693 | 0 | 0 |  |  | 3211520 | 1863904.61011763 | 3451367.56144251 | [8 empty] | 866 |  | 958 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | YES | NO | STATE |  |  | MANUAL | MANUAL | 68640 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE WAS OPERATING AT NORMAL OPERATING PRESSURE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [10 empty] | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 1584498847 | TEXAS811 | CONTRACT LOCATOR | YES | YES | YES | 838 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | EXCAVATION PRACTICES NOT SUFFICIENT (OTHER) | [263 empty] | JOSHUA NORTON | OPERATIONS MANAGER | josh.norton@atmosenergy.com | 979-774-2506 | 979-774-2521 |  |  |  | ANDY TREADWAY | COMPLIANCE DIRECTOR | 972-855-4014 | andy.treadway@atmosenergy.com | PIPELINE FAILED DURING A DUCTILE OVERLOAD EVENT. THE RUPTURE WAS CAUSED BY MECHANICAL GOUGES ON THE PIPE FROM A SECOND PARTY CONTRACTOR'S TRACKHOE THAT GOT STUCK IN THE MUD NEAR THE PIPELINE, APPROXIMATELY ONE MONTH PRIOR TO THE INCIDENT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160013 | 17003 | 2016-02-08 20:14 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2016-01-07 13:11 | 2016 |  |  | 34.7479 | -116.2954 | 1137597 | 2016-01-08 10:51 |  | NATURAL GAS |  | 0 | 11500 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-01-10 06:00 | 2016-01-11 06:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-01-07 13:11 | 2016-01-07 13:21 | ONSHORE | CA | 92338 | Not Within a Municipality | SAN BERNARDINO | MILEPOST | 108.44 | L-300A | 139.2 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 34 |  | 0.3 | 52000 | API 5L X-52 | DSAW |  | UNKNOWN | ASPHALT | [28 empty] | 1950 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 639 |  | NO | NO | NO |  | 0 | 0 | 31000 | 33569.6906827612 | 0 | 0 | 100000 | 108289.324783101 | 0 | 0 | 0 | 0 |  |  | 131000 | 65117.0313089401 | 141859.015465862 | [8 empty] | 546 |  | 688 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | MANUAL | 48840 | NO |  | YES |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DISCOVERED THROUGH LEAK SURVEY | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | YES | [7 empty] | YES | POROSITY | [19 empty] | YES | POROSITY | [55 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | STEPHEN RAMOS | COMPLIANCE ENGINEER | s3rc@pge.com | 9253286107 |  |  |  |  | LARRY DENISTON | MANAGER OF REGULATORY COMPLIANCE | 9253285756 | lcd1@pge.com | ON JANUARY 7, 2016 AT APPROXIMATELY 1311 HOURS, DURING A ROUTINE LEAK SURVEY, PG&E DISCOVERED A GRADE 1 LEAK ON TRANSMISSION L-300A MILE POINT 108.44, APPROXIMATELY 6 MILES WEST OF LUDLOW, SAN BERNARDINO COUNTY. PG&E CREWS ISOLATED AND DEPRESSURIZED THE LINE SECTION ON 1/10/16 AT 0600 HOURS AND COMPLETED THE REPAIR BY INSTALLING A REPAIR SLEEVE. THE COST ESTIMATE OF THE CONTROLLED BLOWDOWN TO FACILITATE THE REPAIR OF THE PIPELINE IS $31,000. PG&E HAD AN EMPLOYEE STANDBY AT ALL TIMES OVERSEEING THE REPAIRS, INCLUDING AFTER-HOURS TO KEEP THE PUBLIC A SAFE DISTANCE FROM THE LEAK. ULTRASONIC SHEARWAVE INSPECTION WAS PERFORMED ON THE ENTIRE LEAK AREA; THE CAUSE OF THE LEAK IS DUE TO POROSITY AT THE SEAM OF THE DOUBLE SUBMERGED ARC WELD (DSAW). NO OTHER INDICATIONS WERE FOUND. THE LINE WAS PUT BACK INTO SERVICE ON 1/11/16 AT 0630 HOURS. THERE WAS NO CUSTOMER IMPACT. THERE ARE NO INJURIES, FATALITIES, OR IGNITION ASSOCIATED WITH THIS INCIDENT. THERE WERE NO POLICE, FIRE, OR MEDIA ON SITE. THIS INCIDENT IS BEING REPORTED TO THE DOT AND CPUC DUE TO REPAIR COSTS EXCEEDING $50,000, WHICH WAS DETERMINED ON 1/8/16.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160014 | 17100 | 2016-02-09 12:03 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2015-11-24 12:25 | 2015 |  |  | 41.5128 | -77.9848 | 1134223 | 2015-11-24 12:36 |  | NATURAL GAS |  | 0.01 | 214.2 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2015-11-20 08:15 | 2015-12-04 04:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2015-11-20 08:00 | 2015-11-20 08:00 | ONSHORE | PA | 16720 | AUSTIN | POTTER | MILEPOST | 500+39 | STATION 535 | 20" REGULATOR BYPASS PIPING | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 20 |  | 0.593 | 52000 | API 5L | SEAMLESS |  | NATIONAL TUBE | COAL TAR | [28 empty] | 1964 | 1963 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 276 |  | NO | NO | NO |  | 0 | 0 | 528 | 577.046159703055 | 0 | 0 | 224000 | 244807.461692205 | 0 | 0 | 0 | 0 |  |  | 224528 | 112637.964023984 | 245384.507851908 | [8 empty] | 840 |  | 1021 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE SYSTEM WAS OPERATING NORMALLY. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | GENERAL CORROSION |  |  |  | YES |  |  |  | YES |  | YES | LAB TEST | YES | [5 empty] | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | JOHNNY LOPEZ | SAFETY AND REGULATORY COMPLIANCE SPECIALIST | johnny.lopez@williams.com | 7132152995 | 7132152000 |  |  |  | MARIE SOTAK | MANAGER PIPELINE SAFETY | 7132152111 | marie.sotak@williams.com | 11/20/2015 AT 8:00 AM A TRANSCO STATION OPERATOR SMELLED A GAS ODOR NEAR THE REGULATOR BUILDING IN THE STATION YARD. GAS CONTROL WAS CONTACTED. THE POWER GAS LINES NEXT TO THE BUILDING WHERE THE ODOR WAS COMING FROM WERE BLOWN DOWN AND ISOLATED IN ORDER TO BEGIN THE INVESTIGATION. 11/21/2015 THE OPERATIONS CREW BEGAN THE EXCAVATION BY HAND IN THE AREA WHERE THE SUSPECTED LEAK WAS IDENTIFIED. THE LINES WERE EXPOSED AND THE LEAKING PIPE WAS LOCATED. 11/23/2015 A CONTRACTOR ARRIVED ON SITE TO EVALUATE THE SITUATION AND PREPARED A SAFE EXCAVATION PLAN FOR THE REPAIR OF THE LEAKING PIPE. 11/24/2015 DURING EXCAVATION IT WAS DETERMINED THAT THE COST OF REPAIRS WOULD EXCEED THE $50,000 THRESHOLD OUTLINED IN CFR PART 191. LOCAL OPERATIONS PERSONNEL NOTIFIED GAS CONTROL THAT THIS WOULD NOW BE A DOT REPORTABLE INCIDENT. PIPELINE CONTROL CALLED IN TO THE NRC TO REPORT THE INCIDENT. 12/4/2015 THE FAILED SEGMENT OF PIPE WAS REMOVED AND A NEW PIPE WAS INSTALLED. THE INTEGRITY SME IDENTIFIED THE CAUSE OF LEAK AS POSSIBLE INTERNAL CORROSION DUE TO THE LEAK LOCATION ON THE PIPE (6 O'CLOCK POSITION) . 5/25/2016 RCA HAS DETERMINED THAT LIQUIDS HAD ACCUMULATED IN THIS DEAD LEG SECTION OF PIPE (PIPE WAS SHUT IN). THE LIQUIDS CONTAINED HIGH LEVELS OF BACTERIA WHICH CONTRIBUTED TO THE INTERNAL CORROSION AND EVENTUAL FAILURE OF THE PIPE. CORRECTIVE ACTIONS: REMOVED DEAD LEG SECTION OF PIPE THAT ACCUMULATED LIQUIDS ONE MORE SECTION OF PIPE THAT IS CONSIDERED A DEAD LEG WILL BE REMOVED IN THE FUTURE LINE WILL BE SWEPT ON A REGULAR BASIS TO HELP PREVENT ACCUMULATION OF LIQUIDS IN REMAINING DEAD LEG SECTION UNTIL IT IS REMOVED LIQUID SAMPLES WILL BE TAKEN AT STATION 535 AND TESTED FOR BACTERIA
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160015 | 17244 | 2016-02-16 12:08 | SUPPLEMENTAL FINAL | 2620 | COLUMBIA GULF TRANSMISSION, LLC | 700 LOUISIANA ST. SUITE 700 | HOUSTON | TX | 77002 | 2016-01-20 13:50 | 2016 |  |  | 29.7675 | -92.692 | 1138531 | 2016-01-20 14:59 |  | NATURAL GAS |  | 355 | 726 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | ISOLATED AND PRESSURE REDUCED FROM APPROXIMATELY 800 PSIG DOWN TO 200 PSIG | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-01-20 13:50 | 2016-01-20 15:30 | ONSHORE | LA | 70643 | GRAND CHENIER | CAMERON PARRISH | MILEPOST | STATION 1+50 | 16-IN AMOCO FIELD LINE | SPLASPL 100-001 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 72 |  | NO | [22 empty] | INTERSTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | PIPE | PIPE BODY | 16 |  | 0.375 | 52000 | UNKNOWN | SEAMLESS |  | US STEEL | OTHER | SOMASTIC WITH CONCRETE COATING | [27 empty] | 1973 | 1973 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 350 |  | NO | NO | NO |  | 0 | 0 | 1692 | 1832.25537533006 | 827 | 849.291105121294 | 282082 | 305464.693134666 | 0 | 0 | 0 | 0 | NO ADDITIONAL COSTS IN ADDITION TO THE REPAIR OF THE PIPELINE. |  | 284601 | 141937.906611552 | 308146.239615118 | [8 empty] | 800 |  | 1000 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [8 empty] | YES | ROOT CAUSE ANALYSIS INEVSTIGATION IS AWAITING FIELD DATA | [19 empty] | YES | PINHOLE IN A GIRTH WELD | [55 empty] | NO | [63 empty] | YES | 1973 | 1500 | NO | [13 empty] | NO | [63 empty] | GEORGE HAMATY | ENGINEER | george_hamaty@transcanada.com | (304)357-3728 |  |  |  |  | LEE ROMACK | MANAGER US REGULATORY COMPLIANCE | (832)320-5315 | lee_romack@transcanada.com | ON JANUARY 20, 2016, COLUMBIA GULF TRANSMISSION, LLC (COLUMBIA) OPERATIONS PERSONNEL WERE PERFORMING ROUTINE PREVENTIVE MAINTENANCE TO A COLUMBIA PIPELINE FACILITY. UPON COMPLETING THE TASK AND DEPARTING THE AREA VIA BOAT, IT WAS NOTED THAT A FEW BUBBLES WERE EMANATING FROM THE BOTTOM OF THE MARSHLAND. NOTING THAT COLUMBIA HAS A PIPELINE FACILITY NEARBY, COLUMBIA PERSONNEL STOPPED AND STARTED INVESTIGATING. GAS SAMPLES WERE COLLECTED FROM THE IDENTIFIED BUBBLES LOCATION AND FROM THE CLOSEST MEASURING STATION. THE TWO SAMPLES WERE SENT TO THE LABORATORY FOR ANALYSIS TO DETERMINE IF THE DISCOVERED RELEASE WAS FROM A COLUMBIA PIPELINE OR OTHER OPERATORS IN THE AREA. MEANWHILE, COLUMBIA OPERATIONS PERSONNEL WERE DISPATCHED TO THE CLOSEST CRITICAL VALVES TO REDUCE THE PRESSURE FROM THE VALVES' OPERATING VALUE OF 800 PSIG DOWN TO APPROXIMATELY 200 PSIG. AFTER THE RESULTS WERE RECEIVED FROM THE LABORATORY, IT WAS CONFIRMED THAT THE VISIBLE BUBBLES WERE EMANATING FROM A COLUMBIA PIPELINE. ACCORDINGLY, A CONTRACTOR WAS ASSIGNED TO EXCAVATE AND COMPLETE THE NECESSARY REPAIR WHICH WAS IDENTIFIED TO BE FROM A PINHOLE LEAK IN A GIRTH WELD. A LEAK CLAMP WAS INSTALLED AND THE PIPELINE OPERATING PRESSURE WAS RAISED TO ITS NORMAL OPERATING PRESSURE ON FEBRUARY 15, 2016. KEY LESSONS LEARNED FROM THIS INCIDENT WERE THAT MAINTENANCE PIGGING ARE RECOMMENDED TO BE PERFORMED ON MORE ROUTINE SCHEDULED BASIS TO REMOVE TRAPPED LIQUIDS DUE TO LOW FLOW IN PIPELINE. ALSO TO PERFORM MAINTENANCE BATCH TREATMENT ON MORE ROUTINE SCHEDULED BASIS DUE TO LIQUID AND LOW FLOW CONDITIONS.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20160016 | 17061 | 2016-02-26 11:30 | SUPPLEMENTAL FINAL | 30629 | ONEOK FIELD SERVICES COMPANY, L.L.C. | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2016-01-13 13:15 | 2016 |  |  | 35.5329 | -97.9782 | 1137973 | 2016-01-13 16:00 |  | NATURAL GAS |  | 5 | 5 | 1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-01-13 14:30 | 2016-02-05 16:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-01-13 13:15 | 2016-01-13 13:30 | ONSHORE | OK | 73036 | EL RENO | CANADIAN | MILEPOST | 4 MILE CREEK | EL RENO GATHERING | LINE 203 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | UNDERWATER NATURAL BOTTOM | 18 |  | YES | [6 empty] | YES | UNCASED | 4 MILE CREEK | 18 | BELOW WATER, PIPE BURIED BELOW BOTTOM (NOT IN BORED/DRILLED CROSSING) | [11 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6.625 |  | 0.141 | 42000 | API 5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | REPUBLIC | OTHER | TF-3 | [27 empty] | 1980 | 1980 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | NO |  | 92 |  | NO | NO | NO |  | 0 | 0 | 12 | 12.9947189739721 | 12 | 12.3234501347709 | 170503 | 184636.54743493 | 0 | 0 | 0 | 0 |  |  | 170527 | 84771.7884455442 | 184661.865604039 | [8 empty] | 68 |  | 500 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 3000 | NO | YES | [6 empty] | YES |  | YES | YES |  |  |  | TYPE A GATHERING | NO |  |  |  |  | OTHER | LOCAL DISTRIBUTION COMPANY EMPLOYEE |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | LOCALIZED PITTING; PIPE WAS NOT CUT OPEN |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KAREN A PEREZ | REGULATORY COMPLIANCE COORDINATOR | karen.perez@oneok.com | 918-595-1703 |  |  |  |  | GEOFF A SANDS | VP NATURAL GAS GATHERING AND PROCESSING | 918-588-7935 | geoff.sands@oneok.com | CITY OF EL RENO OKLAHOMA EMPLOYEE CONTACTED ONEGAS EMPLOYEE OF POSSIBLE LEAK AT ADAMS PARK ONEGAS EMPLOYEE NOTIFIED ONEOK FIELD SERVICES PIPELINE CONTROL 01/13/2016 13:14 OFS PIPELINE CONTROL CONTACTED FIELD PERSONNEL 01/13/2016 13:15 OFS FIELD PERSONNEL ARRIVED ON SITE AND ISOLATED EFFECTED SEGMENT OF PIPE 01/13/2016 14:30 02/26/2016 PROPERTY DAMAGE ESTIMATES HAVE EXCEEDED $50,000 01/13/2016 NRC #1137973 WAS MADE DUE TO OKLAHOMA CORPORATION COMMISSION OIL & GAS DIVISION PETROLEUM PRODUCTS RELEASE REQUIREMENTS 04/05/2016 UPDATED PROPERTY DAMAGES (D7B) AND CHANGED TIME THAT OFS FIELD PERSONNEL ARRIVED ON SITE AND ISOLATED EFFECTED SEGMENT OF PIPE TO 14:30 FINAL REPORT SUBMITTED
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160017 | 17038 | 2016-03-03 19:00 | ORIGINAL FINAL | 30782 | HARVEST PIPELINE COMPANY | 1111 TRAVIS | HOUSTON | TX | 77002 | 2016-02-03 16:00 | 2016 |  |  | 29.7161 | -92.0169 | 1139701 | 2016-02-03 17:05 |  | NATURAL GAS |  | 10 | 3500 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-02-03 16:00 | 2016-02-05 14:50 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-02-03 16:00 | 2016-02-01 10:00 | ONSHORE | LA | 70510 | Not Within a Municipality | VERMILION (IN VERMILION BAY) | MILEPOST | VERMILION BAY | REDFISH GAS PIPELINE | 12" PIPELINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | IN STATE WATERS (WATER DEPTH: 10 FEET) | 60 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12.75 |  | 0.25 | 42000 | API 5L X42 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | STUPP CORPORATION | OTHER | CONCRETE | [27 empty] | 1967 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 292 |  | NO | NO | NO |  | 0 | 0 | 7000 | 7580.25273481705 | 20 | 20.5390835579515 | 138000 | 149439.268200679 | 0 | 0 | 0 | 0 |  |  | 145020 | 72097.3971577628 | 157040.060019054 | [8 empty] | 750 |  | 1100 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 77500 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | NO | NO | OTHER | PHONE CALL FROM THE US COAST GUARD |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE EFFECT OF THE PINHOLE LEAK ON THE PIPELINE PRESSURE WAS WITHIN THE NORMAL PRESSURE FLUCTUATION RANGE; THEREFORE NO ALARMS WERE GENERATED. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING | [5 empty] | YES | UNKNOWN | YES | [7 empty] | YES | GENERAL LINE PIPE SEGMENT. FAIRLY EVEN PROFILE. | NO | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | YES |  |  | 2016 | [6 empty] | YES | [53 empty] | JACQUES ROTOLO | REGULATORY COMPLIANCE SPECIALIST | jrotolo@hilcorp.com | 985-438-0040 |  |  |  |  | JACQUES ROTOLO | REGULATORY COMPLIANCE SPECIALIST | 985-438-0040 | jrotolo@hilcorp.com | 2/1/2016: THE COAST GUARD CALLED AND REPORTED BUBBLES IN VERMILLION BAY IN LOUISIANA. HARVEST DISPATCHED OPERATORS TO INVESTIGATE THE REPORT. THE OPERATORS VERIFIED BUBBLES IN THE BAY. GPS COORDINATES INDICATED THE BUBBLES TO BE APPROXIMATELY 150 FEET FROM THE HARVEST REDFISH PIPELINE. IN ORDER TO DETERMINE IF THE HARVEST REDFISH PIPELINE WAS THE SOURCE OF THE LEAK, THE VALVES WERE CLOSED TO BLOCKED-IN THE PIPELINE. IF THE PIPELINE WAS THE SOURCE OF THE LEAK, THE BUBBLES WOULD DECREASE AS THE PIPELINE PRESSURE DECREASED. THE PIPELINE PRESSURE WAS APPROXIMATELY 750 PSI BEFORE CLOSING THE VALVES. THE BUBBLES REMAINED STEADY AFTER VALVES WERE CLOSED. 2/2/2016: ROUGH SEAS HAMPERED THE OPERATION. THE SURVEY CREW COULD NOT MARK THE PIPELINE BECAUSE OF THE ROUGH SEAS. OPERATIONS CONTINUED BLEED-DOWN OF PIPELINE. 2/3/2016: 9:00 AM ROUGH SEAS CONTINUE TO HAMPER THE OPERATION. THE SURVEY CREW COULD NOT MARK THE PIPELINE BECAUSE OF THE ROUGH SEAS. THE PIPELINE PRESSURE WAS DOWN TO 250 PSI. 1:00 PM THE SURVEY CREW COULD NOT MARK THE PIPELINE BECAUSE OF THE ROUGH SEAS. THEREFORE, IT WAS NOT SAFE TO BRING THE WORK BARGE OUT TO THE LOCATION AND SPUD DOWN IN ROUGH SEAS WITHOUT THE EXACT LOCATION OF THE PIPELINE. THE BUBBLES SEEMED TO DECREASE SOME. OPERATIONS CONTINUED BLEED-DOWN OF PIPELINE. 2:30 PM THE BUBBLES CONTINUED TO DECREASE. 4:00 PM THE BLEED-DOWN WAS NEARLY COMPLETE, AND THE BUBBLES CONTINUE TO DECREASE. THE DETERMINATION WAS MADE THAT THE LEAK WAS ON THE HARVEST REDFISH PIPELINE. LDNR AND OTHER AGENCIES WERE NOTIFIED THAT THE LEAK WAS ON THE HARVEST PIPELINE. 5:05 PM THE NRC WAS NOTIFIED THAT THE LEAK WAS ON THE HARVEST PIPELINE. 2/4/2016: 9:00 AM THE DIVERS JETTED DOWN TO AND AROUND THE PIPELINE AT THE LEAK LOCATION AND REMOVED THE CONCRETE COATING. 5:00 PM A PINHOLE IN THE PIPELINE WAS FOUND NEAR THE 6 O'CLOCK POSITION. 2/5/2016: 7:00 AM THE CLEANING AND PREPARATION OF THE PIPE WAS PERFORMED FOR THE INSTALLATION OF A 12-INCH PLIDCO HEAVY DUTY SPLIT SLEEVE. 9:10 AM A UT OF THE PIPELINE AROUND THE PINHOLE CONFIRMED GOOD WALL THICKNESS. 10:30 AM THE SPLIT SLEEVE WAS INSTALLED AND THE FASTENERS WERE TORQUED. 11:00 AM THE SEALANT PACKING OF THE SPLIT SLEEVE WAS BEGUN. 2:50 PM OPERATIONS BEGAN TO PRESSURE-UP THE PIPELINE. (NO LEAK VISIBLE) 7:00 PM THE PIPELINE PRESSURE WAS AT 570 PSI. (NO LEAKS) 8:30PM THE PIPELINE PRESSURE EQUALIZED AT 750 PSI. (NO LEAKS) 2/6/2016: 7:00 AM THE PIPELINE PRESSURE WAS APPROXIMATELY 750 PSI. (NO LEAKS) THE PIPELINE AND SPLIT SLEEVE WERE WRAPPED. 8:00 AM THE BARGE AND EQUIPMENT WAS DEMOBILIZED OFF LOCATION.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160018 | 17041 | 2016-03-04 14:57 | ORIGINAL FINAL | 38987 | KINETICA ENERGY EXPRESS LLC | 1001 MCKINNEY STREET, SUITE 900 | HOUSTON | TX | 77002 | 2016-02-03 09:30 | 2016 |  |  | 28.5775 | -91.2558 | 1139650 | 2016-02-03 10:40 |  | NATURAL GAS |  | 500 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-02-03 12:10 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-02-03 09:00 | 2016-02-03 09:00 | OFFSHORE | [28 empty] | 106 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SHIP SHOAL | 198 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 |  | 0.375 | 52000 | 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | US STEEL | OTHER | FIBERGLASS/CONCRETE | [27 empty] | 1970 | 1970 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 1125 | 1155.32345013477 | 75000 | 81216.9935873255 | 5000 | 5414.46623915503 | 0 | 0 |  |  | 81125 | 40963.9022705158 | 87786.7832766153 | [8 empty] | 725 |  | 1200 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | CHECK VALVE | 6048 | NO |  | YES |  | YES |  | YES | PRODUCER PLATFORM PIPING TO SUBSEA TIE-IN. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE WAS BELOW MAOP WITH NO UNUSUAL OPERATING CIRCUMSTANCES AND WAS LOCATED SUBSEA. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  | YES | YES | [5 empty] | YES | UNABLE TO VISUALLY INSPECT DUE TO LOCATION BEING SUBSEA. | YES |  |  |  | YES | 6:00 POSITION | YES | NO | NOT APPLICABLE - NOT MAINLINE PIPE | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KURT J. CHERAMIE | SR. DIRECTOR | kurt.cheramie@kineticallc.com | 9852092283 |  |  |  |  | KURT J. CHERAMIE | SR. DIRECTOR | 9852092283 | kurt.cheramie@kineticallc.com | ON 2/3/16, HELICOPTER OVERFLIGHT BY OPERATOR PERSONNEL RESULTED IN A LEAK BEING IDENTIFIED ON THE KINETICA 523M-1100 PIPELINE IN SHIP SHOAL BLOCK 198. COORDINATES WERE REPORTED AND PLOTTED. LEAK PLOTTED APPROXIMATELY 500' SSW OF KINETICA PIPELINE. LINE WAS IMMEDIATELY ISOLATED BY OPERATOR PERSONNEL AT THE PRODUCER PLATFORM. DUE TO ROUGH SEAS, OPERATOR WAS UNABLE TO DISPATCH DIVE VESSEL TO CLOSE SSTI VALVE. CHECK VALVE AT SSTI. ON 2/5/15, DIVE VESSEL ARRIVED AT LOCATION TO CLOSE SSTI VALVE. ON 2/6/16, DIVE VESSEL LOCATED AND CLOSED VALVE AT SSTI TO TOTALLY ISOLATE PIPELINE. DIVE VESSEL EXCAVATED LEAK LOCATION AND IDENTIFIED A PINHOLE LEAK AT THE 6:00 POSITION. DUE TO NO FLOW ON PIPELINE AND NO FUTURE PLANS FOR FLOW ON SAID LINE, IN LIEU OF MAKING REPAIRS, KINETICA MADE THE DCISION TO START THE PROCESS TO ABANDON THE PIPELINE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160019 | 17315 | 2016-03-11 15:18 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2016-02-10 04:49 | 2016 |  |  | 42.5312 | -83.1839 | 1140177 | 2016-02-10 09:43 |  | NATURAL GAS |  | 4200 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELIEF VALVE ACTIVATED - SHUT-DOWN NOT REQUIRED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-02-10 04:49 | 2016-02-10 05:53 | ONSHORE | MI | 48073 | ROYAL OAK | OAKLAND | MILEPOST | COOLIDGE CG | COOLIDGE CITY GATE | LINE 1017 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1985 |  | CARBON STEEL |  | OTHER | [8 empty] | REGULATION EQUIPMENT FAILURE - 6" FISHER EZR REGULATOR | CLASS 3 LOCATION | YES | METHOD2 | 143 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 31332 | 32176.5283018868 | 4563 | 4941.24188985289 | 200 | 216.578649566201 | 7976 | 8637.15654470011 | LABORATORY ANALYSIS |  | 44071 | 39691.1264118916 | 45971.505386006 | [8 empty] | 318 |  | 300 | 192.619(A)(2) |  |  |  | PRESSURE EXCEEDED MAOP, BUT DID NOT EXCEED THE APPLICABLE ALLOWANCE IN 192.201 | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL ROOM OPERATOR IDENTIFIED THE PRESSURE INCREASE AND NOTIFIED THE APPROPRIATE PERSONNEL | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [25 empty] | YES | DIMENSIONAL ANOMALY WITH THE REGULATOR DIAPHRAGM AND THE REGULATOR BODY | [161 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST I | carmella.king@cmsenergy.com | 517-788-0509 |  |  |  |  | AMANDA L. WARD | GAS REGULATORY SERVICES LEAD | 517-545-8746 | amanda.ward@cmsenergy | ON FEBRUARY 10, 2016 AT APPROXIMATELY 04:49 CONSUMERS ENERGY GAS CONTROL RECEIVED A SCADA ALARM IDENTIFYING A POSSIBLE OVER PRESSURE EVENT ON THE ADAMS RD. OUTLET AT THE COOLIDGE CITY GATE. THE COOLIDGE CITY GATE IS LOCATED AT 4600 COOLIDGE HWY., (OAKLAND COUNTY) ROYAL OAK, MICHIGAN. AN INSTRUMENT MECHANIC (IM) WAS DISPATCHED AT APPROXIMATELY 04:52 AND ARRIVED ON LOCATION AT APPROXIMATELY 05:53 TO DISCOVER A FAILURE OF THE PRIMARY REGULATOR (P2). THE REGULATOR FAILURE CAUSED THE RELIEF VALVE (RV- 6) SERVING THE ADAMS RD., OUTLET TO ACTIVATE AND REMAIN OPEN UNTIL APPROXIMATELY 06:18. THE RESPONDING IM PERFORMED A VALVING OPERATION TO ISOLATE THE FAILED REGULATOR ALLOWING THE STANDBY REGULATOR (S2) TO FEED. THE PRESSURE ON THE ADAMS RD. OUTLET INCREASED TO A MAXIMUM OF 318.37 PSIG AND APPROXIMATELY 4.2 MMCF OF NATURAL GAS WAS VENTED TO THE ATMOSPHERE AS A RESULT OF THE INCIDENT. THE INITIAL INVESTIGATION OF THE FAILURE SUGGESTED THE INLET SCREEN ON THE ADAMS RD. OUTLET MAIN RUN REGULATOR (P2) WAS PARTIALLY DISINTEGRATED CAUSING METAL DEBRIS TO CONTAMINATE THE REGULATORS INTERNAL COMPONENTS CAUSING IT TO FAIL OPEN. THE P2 REGULATOR WAS CLEANED OF DEBRIS AND THE INLET SCREEN AND REGULATOR DIAPHRAGM WERE REPLACED. THE EQUIPMENT WAS TESTED AND RETURN TO SERVICE. THE IMPACTED RELIEF VALVE WAS ALSO DISASSEMBLE AND CHECKED FOR DAMAGE AND DEBRIS WITH NEGATIVE RESULTS. AT APPROXIMATELY 04:42 THE FOLLOWING DAY THE P2 REGULATOR EXPERIENCED ANOTHER FAILURE. THE RELIEF VALVE OPERATED AS A RESULT OF THE EXCEEDANCE. HOWEVER, HYDRATES ENTRAINED IN THE GAS STREAM WERE FOUND TO HAVE PRECIPITATED OUT AND FROZE IN THE RELIEF VALVE'S PILOT RESULTING IN DELAYED ACTIVATION. THE PRESSURE ON THE ADAMS RD. OUTLET INCREASED TO A MAXIMUM OF 338 PSIG FOR APPROXIMATELY TWO MINUTES BEFORE RETURNING TO A STEADY RELIEF PRESSURE BELOW 110% OF MAOP. THE RELIEF VALVE WAS CLEANED, REBUILT, INSPECTED AND RETURN TO SERVICE. REGULATOR P2 HAS BEEN REMOVED FROM SERVICE UNTIL FURTHER INVESTIGATION AND LAB ANALYSIS IS COMPLETE AND APPROPRIATE REMEDIATION ACTIONS IDENTIFIED. A SAFETY RELATED CONDITION REPORT DETAILING THE FAILURE THAT OCCURRED ON FEBRUARY 11TH WAS REPORTED TO PHMSA ON FEBRUARY 18, 2016 (SCRC 20160022). A MOBILE AND WALKING SURVEY WAS PERFORMED ON APPROXIMATELY 1.5 MILES OF 12" STEEL HIGH PRESSURE DISTRIBUTION PIPING (300 PSIG MAOP) OPERATING AT > 20% SMYS AND ASSOCIATED SERVICE LINES BETWEEN THE COOLIDGE CITY GATE AND MAPLE RD., TROY, MICHIGAN AND NO LEAKS WERE DETECTED. THE REGULATION EQUIPMENT (REGULATOR P2) REMOVED FROM SERVICE ON FEBRUARY 11, 2016 WAS REPLACED WITH A MOONEY FLOWGRID REGULATOR ON AUGUST 8, 2016 AND RETURNED TO NORMAL OPERATIONS. THE REGULATOR, DIAPHRAGM AND CAGE WERE EXAMINED BY CONSUMERS ENERGY LABORATORY SERVICES, IN SEPTEMBER 2016. THE INVESTIGATION FOUND THE DIAPHRAGM DIMENSIONS WERE INCONSISTENT WITH THE DIMENSIONS OF THE CAGE, PREVENTING A SECURE FIT DURING ASSEMBLY. IN ADDITION, MEASUREMENT DATA INDICATED THE O-RING ASSEMBLED ON THE BONNET WAS NOT SUBJECT TO COMPRESSION DURING ASSEMBLY. THE INVESTIGATION WAS INCONCLUSIVE AS TO WHY THE DIAPHRAGM WAS OUT OF POSITION, AND NO FAILURE CAUSE WAS IDENTIFIED. A SAFETY-RELATED CONDITION REPORT "RETURN TO SERVICE" NOTICE DETAILING REMEDIATION ACTIVITIES WAS SUBMITTED ON FEBRUARY 28, 2017.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160020 | 17084 | 2016-03-11 16:22 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2016-02-14 00:15 | 2016 |  |  | 42.1223 | -72.0034 | 1140425 | 2016-02-14 01:33 |  | NATURAL GAS |  | 6176 | 1804 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-02-14 00:15 | 2016-02-15 08:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-02-14 00:15 | 2016-02-14 00:15 | ONSHORE | MA | 01507 | CHARLTON | WORCESTER | SURVEY STATION NO. | STATION 264 | TENNESSEE GAS PIPELINE | TGP COMPRESSOR STATION 264 | YES | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | PLC FAILURE CAUSED UNIT TO SHUT IN.THE UNIT DID NOT SHUT DOWN IN SAFE MODE AND AS A RESULT THE UNIT SUCTION AND DISCHARGE VALVES REMAINED OPEN. | CLASS 2 LOCATION | NO |  | 53 |  | NO | NO | NO |  | 0 | 0 | 3752 | 4063.01546586194 | 12846 | 13192.2533692722 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 16598 | 15542.0393951934 | 17255.2688351342 | [8 empty] | 591 |  | 650 | OTHER | PRESSURE TEST |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS CONTROL DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | YES | [23 empty] | YES | [172 empty] | VALERIE BERGMAN | CODES AND STANDARDS PIPELINE ENGINEER | valerie_bergman@kindermorgan.com | 7134204810 |  |  |  |  | VALERIE BERGMAN | CODES AND STANDARDS PIPELINE ENGINEER | 7134204810 | valerie_bergman@kindermorgan.com | ON 2/13/2016 TGP PERSONNEL RECEIVED NOTIFICATION THAT A UNIT IN STATION 264 FELL OFFLINE. AFTER PERSONNEL ARRIVED ON SITE, THEY VERIFIED THAT GAS WAS VENTING. PERSONNEL THEN SHUT-IN THE STATION AND THIS ACTION STOPPED THE RELEASE OF GAS. IT WAS DISCOVERED THAT THERE WERE RELAY ISSUES WITHIN THE PLC AND THIS CAUSED THE UNIT TO NOT PROPERLY SHUT DOWN IN "SAFE MODE", AND AS A RESULT THE UNIT SUCTION AND DISCHARGE VALVES REMAINED OPEN. TGP PERSONNEL CONFIRMED THE WIRING AND INSTALLATION OF THE BACKUP RELAY LOGIC CONTROL OF THE UNIT AND REPLACED PLC COMPONENTS IN THE UNIT VALVE CIRCUITRY PORTION OF THE BACK UP RELAY SYSTEM.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160021 | 17436 | 2016-03-16 13:57 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2016-02-24 09:12 | 2016 |  |  | 34.3438 | -88.2303 | 1141243 | 2016-02-24 10:34 |  | NATURAL GAS |  | 32 | 23229 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-02-24 10:46 | 2016-03-01 09:48 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-02-24 09:12 | 2016-02-24 09:12 | ONSHORE | MS | 38876 | Not Within a Municipality | ITAWAMBA | MILEPOST | 121 | 36-INCH LINE 25 | EGYPT-BARTON | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 36 |  | 0.39 | 60000 | API-5L | DSAW |  | KAISER STEEL | COAL TAR | [28 empty] | 1965 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 760 |  | NO | NO | NO |  | 0 | 0 | 46458 | 50309.0545077329 | 64 | 65.7250673854447 | 109360 | 118425.205582799 | 0 | 0 | 0 | 0 |  |  | 155882 | 77521.6179059726 | 168799.985157917 | [8 empty] | 843 |  | 936 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 47995 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK RESULTED FROM A PINHOLE LEAK WHICH COULD NOT BE DISCOVERED BY CONTROL INSTRUMENTS. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [8 empty] | YES | POROSITY IN SEAM WELD | [19 empty] | YES | POROSITY IN SEAM WELD. | [55 empty] | YES | YES |  |  | YES |  |  |  | 2009 | [31 empty] | 2009 | [23 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | deteschendorf@spectraenergy.com | 713-627-5573 |  |  |  |  | NATHAN ATANU | MANAGER | 713-627-5008 | nyatanu@spectraenergy.com | A SPECTRA ENERGY EMPLOYEE DISCOVERED BUBBLES IN PONDING WATER OVER TEXAS EASTERN TRANSMISSION, LP 36-INCH LINE 25 NEAR TREMONT, MISSISSIPPI IN ITAWAMBA COUNTY ON FEBRUARY 24, 2016. THE PIPELINE WAS EXCAVATED AND A PINHOLE LEAK IN THE DSAW LONG SEAM WELD WAS OBSERVED. METALLURGICAL ANALYSIS WAS PERFORMED, AND THE LEAK WAS THE RESULT OF A PINHOLE LEAK WITH A DIAMETER OF APPROXIMATELY 0.043'. THE PINHOLE WAS DUE TO POROSITY IN THE SEAM WELD. THE PIPE HAD BEEN HYDROSTATIC TESTED IN 1965 TO 1,378 PSIG (1.47 X MAOP) WITH NO LEAK DETECTED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160022 | 17115 | 2016-03-21 09:27 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2016-02-27 11:30 | 2016 |  |  | 28.8782 | -93.0317 | 1141517 | 2016-02-27 12:45 |  | NATURAL GAS |  | 3007 | 22713 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-03-01 15:00 | 2016-03-05 20:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-02-27 11:30 | 2016-02-27 15:00 | OFFSHORE | [28 empty] | 85 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST CAMERON | 273 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 24 |  | 0.462 | 52000 | API-5L | SEAMLESS |  | U.S. STEEL | OTHER | CONCRETE AND SOMASTIC | [27 empty] | 1973 | 1973 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 629 |  | NO | NO | NO |  | 0 | 0 | 45426 | 49191.5086759713 | 6014 | 6176.10242587601 | 404800 | 438355.186721992 | 0 | 0 | 0 | 0 |  |  | 456240 | 230199.843822857 | 493722.797823839 | [8 empty] | 821 |  | 1440 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 137122 | NO |  |  |  | YES |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | PLATFORM OPERATOR'S HELICOPTER DISCOVERED LEAK |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS TOO SMALL TO BE IDENTIFIED BY CONTROL ROOM PERSONNEL. A REVIEW OF OPERATING RECORDS FOUND ABNORMAL OPERATING CONDITIONS DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | YES | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | deteschendorf@spectraenergy.com | 713-627-5573 |  |  |  |  | NATHAN ATANU | MANAGER | 713-627-5008 | nyatanu@spectraenergy.com | INDICATIONS OF BUBBLES ON THE WATER SURFACE IN WEST CAMERON 273 WERE REPORTED BY A PLATFORM OPERATOR'S HELICOPTER ON FEBRUARY 27, 2016. UPON INVESTIGATION, IT WAS DETERMINED THE LEAK WAS CAUSED BY A PINHOLE LEAK RESULTING FROM INTERNAL CORROSION ON TEXAS EASTERN TRANSMISSION, L.P. 24-INCH LINE 41-A NATURAL GAS PIPELINE. REPAIR BY INSTALLATION OF A CLAMP WAS COMPLETED MARCH 5, 2016.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160023 | 17050 | 2016-03-24 14:56 | ORIGINAL FINAL | 13769 | NORTHERN BORDER PIPELINE COMPANY | 700 LOUISIANA STREET | HOUSTON | TX | 77002 | 2016-02-25 12:12 | 2016 |  |  | 46.5146 | -100.8007 | 1141369 | 2016-02-25 14:25 |  |  |  | 0 | 476 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-02-25 12:12 | 2016-03-06 09:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-02-25 12:12 | 2016-02-25 12:12 | ONSHORE | ND | 58566 | Not Within a Municipality | MORTON | MILEPOST | ND 203.4 | NORTHERN BORDER PIPELINE | CS 07 SAINT ANTHONY COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | FLOOR TRENCH AND ELECTRICAL WIRING | 1998 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | OILY DEBRIS AND ELECTRICAL WIRE | OTHER | [8 empty] | FIRE DAMAGE TO COMPRESSOR UNIT CONTROL WIRING. | CLASS 1 LOCATION | NO |  | 1158 |  | NO | NO | NO |  | 0 | 0 | 762 | 825.164654847227 | 0 | 0 | 291906 | 316103.036401358 | 949 | 1027.66569219163 | 0 | 0 |  |  | 293617 | 145950.132685779 | 317955.866748397 | [8 empty] | 1145 |  | 1440 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM ACTIONS COULD NOT HAVE AFFECTED THIS EVENT. | [12 empty] | YES | 3 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | FIRE IN COMPRESSOR BUILDING CAUSED BY WELDING SPARKS. |  |  | YES |  |  | OTHER MAINTENANCE | NO | [150 empty] | KURT SMITH | COMPLIANCE SPECIALIST | kurt_smith@transcanada.com | (509) 533-2848 | (509) 533-2993 |  |  |  | KURT SMITH | COMPLIANCE SPECIALIST | (509) 533-2848 | kurt_smith@transcanada.com | REPAIRS TO A BUILDING ROOF VENT WERE BEING CARRIED OUT BY COMPANY PERSONNEL. THE WORK INVOLVED GRINDING AND WELDING. IN SPITE OF SAFETY PRECAUTIONS IN PLACE, SPARKS FROM THE WORK STARTED A FIRE IN OILY RESIDUE IN A COVERED TRENCH DESIGNED TO CATCH OIL, WATER, AND OTHER LIQUIDS. THE FIRE CAUSED DAMAGE TO ELECTRICAL WIRING AND CABLE SUPPORTS. DAMAGE TO THE WIRING CAUSED THE UNIT RECYCLE VALVE TO OPEN AND GAS CIRCULATING THROUGH THE COMPRESSOR HEATED UP TO THE POINT WHERE THE UNIT SHUT DOWN AUTOMATICALLY ON HIGH COMPRESSOR DISCHARGE TEMPERATURE. PERSONNEL ON SITE SAW SMOKE COMING FROM THE COMPRESSOR BUILDING AND INITIATED A STATION EMERGENCY SHUTDOWN. THIS ACTION ISOLATED THE COMPRESSOR STATION PIPING FROM THE MAINLINE AND VENTED GAS WITHIN THE STATION. PERSONNEL CALLED THE FIRE DEPARTMENT WHICH RESPONDED AND EXTINGUISHED THE FIRE. THE EVENT IS CONSIDERED AN INCIDENT BECAUSE TRANSCANADA JUDGES IT TO BE SIGNIFICANT IN THAT THE COST TO REPAIR THE DAMAGE IS CONSIDERABLE, THE COMPRESSOR UNIT IS OUT OF SERVICE FOR AN EXTENDED TIME PERIOD, AND THE UNAVAILABILITY OF THE COMPRESSION FACILITIES RESULTED IN A RESTRICTION TO THROUGHPUT CAPACITY THAT IMPACTS DOWNSTREAM CUSTOMERS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160024 | 17241 | 2016-03-24 15:52 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2016-02-25 06:40 | 2016 |  |  | 30.7099 | -91.4398 | 1141321 | 2016-02-25 07:29 |  | NATURAL GAS |  | 0.5 | 15440 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-02-25 07:35 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-02-25 07:15 | 2016-02-29 08:00 | ONSHORE | LA | 70748-4020 | NEW ROADS | POINTE COUPEE | MILEPOST | 577.74 | MAINLINE "C" | 50C50 TO 50C60 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 42 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 36 |  | 0.406 | 52000 | API 5L | DSAW |  | NATIONAL TUBE | ASPHALT | [28 empty] | 1961 | 1961 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | YES | METHOD2 | 694 |  | NO | NO | NO |  | 0 | 0 | 30880 | 33439.7434930215 | 2 | 2.05390835579515 | 175000 | 189506.318370426 | 0 | 0 | 0 | 0 |  |  | 205882 | 102340.254615814 | 222948.115771804 | [8 empty] | 542.6 |  | 780 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | AUTOMATIC | 53064 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) |  | YES | [13 empty] | YES | HARD SPOT ON PIPE | [6 empty] | YES | [63 empty] | YES | YES | [6 empty] | 2013 | [55 empty] | YES | 1969 | 1268 | NO | [13 empty] | NO | [63 empty] | SHANE FRASIER | PIPELINE SAFETY ENGINEER | shane.frasier@williams.com | 7132153051 |  |  |  |  | MARIE SOTAK | PIPELINE SAFETY MANAGER | 7132152111 | marie.sotak@williams.com | AT 2:40AM ON 2/25/2016, WILLIAMS PIPELINE CONTROL RECEIVED A CALL FROM WYATT BENTON WHO WAS HUNTING IN THE AREA OF OUR PIPELINE RIGHT OF WAY. MR BENTON STATED THAT HE WANTED TO REPORT A POSSIBLE LEAK AROUND THE WILLIAMS PIPELINE. PIPELINE CONTROL IMMEDIATELY CALLED THE STATION 60 ON CALL PERSON TO REPORT THE POSSIBLE LEAK. PERSON ON CALL CALLED A SECOND EMPLOYEE TO ASSIST WITH INVESTIGATION, DROVE TO STATION TO PICK UP A GAS DETECTOR AND SECOND EMPLOYEE, AND DROVE OVER TO THE SITE IN QUESTION. AFTER ARRIVING THE TWO EMPLOYEES BEGAN SCANNING THE RIGHT OF WAY AND DISCOVERED BUBBLES WITHIN THE RIGHT OF WAY LIMITS. AT THIS TIME THE LEAD RIGHT OF WAY EMPLOYEE ARRIVED ON SITE AND BEGAN THE PROCESS OF ELIMINATING POTENTIAL FOREIGN LINE CROSSINGS BEING THE SOURCE OF THE LEAK. RIGHT OF WAY LEAD CALLED DISTRICT MANAGER AND REPORTED HIS FINDINGS OF NO KNOWN FOREIGN LINE CROSSINGS AND HE WAS PICKING UP A SMALL GAS LEAK LOCATED ABOVE THE MAIN LINE C PIPE. DISTRICT MANAGER BEGAN MAKING CALLS TO PIPELINE CONTROL, CYPRESS DIVISION DIRECTOR, AND THE CYPRESS DIVISION MANAGER ENGINEERING WHO ASSISTED BY PIPELINE SAFETY. PIPELINE CONTROL CALLED AND REPORTED THE POSSIBLE LEAK TO THE NRC AND THE LOUISIANA STATE POLICE. DISTRICT MANAGER INSTRUCTED RIGHT OF WAY LEAD TO ISOLATE THE C LINE PIPING SECTION BETWEEN THE 50C50 AND 50C60 AS A PRECAUTIONARY MEASURE AND TO CONTINUE TO VERIFY IF THE LEAK WAS IN FACT COMING FROM OUR LINE. AFTER ISOLATION THE STATION CREW MEMBERS INSTALLED GAUGES AT THE 50C50 AND 50C60 AND BEGAN TO MONITOR FOR ANY LOSS IN PRESSURE ON THE C LINE SECTION. OTHER CREW MEMBERS CONTINUED TO INVESTIGATE RECORDS FOR ANY FOREIGN LINE CROSSINGS AND CONTINUED UPDATING PIPELINE CONTROL AND CYPRESS DIVISION. AFTER MONITORING PRESSURES FOR A PERIOD OF TIME SHOWED NO DROP IN PRESSURE THE DISTRICT MANAGER DISCUSSED WITH THE DIVISION DIRECTOR THE NEED TO BLOW DOWN THE C LINE SECTION TO VERIFY THAT THE LEAK WAS EMANATING FROM THIS SECTION OF LINE. DIRECTOR AGREED, SAFE BLOW DOWN PROCEDURES WERE DISCUSSED WITH THE STATION CREW, AND THE 50C50 TO 50C60 LINE SECTION WAS BLOWN DOWN. DISTRICT MANAGER AND DIVISION SAFETY EMPLOYEE ARRIVED AT LEAK SITE WITH APPROX. 100 PSI REMAINING ON THE LINE SECTION. AT THIS TIME THE BUBBLES WERE VERIFIED TO HAVE STOPPED. STATION EMPLOYEES CONTINUED BLOW DOWN TO 0 PSI, SECURED ALL VALVES AND SITES, AND BEGAN SCHEDULING FOR INVESTIGATORY DIGS TO DETERMINE THE SOURCE OF THE LEAK. ***UPDATE PER SUPPLEMENTAL REPORT 5/16/2016*** METALLURGICAL ANALYSIS HAS CONCLUDED THAT THE LEAKING SECTION OF PIPE WAS MANUFACTURED WITH AN AREA OF VARYING HARDNESS. RCA INDICATES THAT THIS AREA OF PARTICULARLY HARDER STEEL WAS THE MAIN CAUSE OF THE CRACK FORMATION. THE INSPECTION OF AFFECTED PIPE SAMPLE WAS COMPLETED BY ANDERSON AND ASSOCIATES IN HOUSTON ON 4/15/16. INSPECTIONS INDICATED ONLY THIS LOCALIZED AREA BECAME SUSCEPTIBLE TO EITHER HYDROGEN EMBRITTLEMENT OR HIGH PH SCC MECHANISMS; WITHOUT THE HARD SPOT, THE LAB SAID THERE IS NO EVIDENCE CRACKING WOULD HAVE OCCURRED. UPON REVIEW OF THE 2013 ILI, TWO ADDITIONAL INVESTIGATION DIGS WILL BE CONDUCTED IN 2016 TO SEARCH FOR ADDITIONAL AREAS OF ELEVATED HARDNESS. ONCE THESE TWO DIGS ARE EITHER REPAIRED OR CLEARED WITH REGARD TO HARD SPOTS, MAIN LINE 'C' FROM 50C41 TO 50C60 CAN BE CONSIDERED AT VERY LOW RISK FOR CRACKING SUSCEPTIBILITY DUE TO HARD SPOTS. ***UPDATE PER SUPPLEMENTAL REPORT 12/1/2016*** THE TWO ADDITIONAL INVESTIGATION DIGS REFERENCED ABOVE CAME BACK NEGATIVE FOR INDICATIONS OF THE SAME DEFECT THAT APPARENTLY CAUSED THIS INCIDENT. THE INVESTIGATION HAS BEEN CONCLUDED WITH NO FURTHER ACTION DEEMED NECESSARY.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160025 | 31460 | 2016-03-25 15:56 | SUPPLEMENTAL FINAL | 32379 | COBRA PIPELINE COMPANY, LTD. | PO BOX 1420 | MENTOR | OH | 44061 | 2016-02-22 13:26 | 2016 |  |  | 41.4116 | -80.9526 | 1141236 | 2016-02-24 11:14 |  | NATURAL GAS |  | 2888 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-02-23 19:00 | 2016-02-25 15:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-02-22 13:26 | 2016-02-25 14:40 | ONSHORE | OH | 44491 | WEST FARMINTON | TRUMBULL | SURVEY STATION NO. | KV 35 | COBRA PIPELINE CO LTD, NORTH TRUMBULL | V341 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 39 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10 |  | 0.188 | 42000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COLD APPLIED TAPE | [28 empty] | 1974 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 5 | 1 | [7 empty] | CLASS 2 LOCATION | NO |  | 190 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 11552 | 11863.3746630728 | 62228 | 67386.2810260279 | 28517 | 30880.8667483968 | 0 | 0 |  |  | 102297 | 57406.5129786248 | 110130.522437498 | [8 empty] | 325 |  | 500 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 79200 | NO |  |  |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | TRENCHER | DRAINAGE | YES | 604400038 | CITY WIDE TELEMESSAGING | UTILITY OWNER | YES | YES | YES | 27 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO MAINTAIN CLEARANCE | [263 empty] | WILLIAM HUNTER | GIS MANAGER | whunter@cobrapipeline.com | 440-255-1945 | 440-255-1985 |  |  |  | WILLIAM HUNTER | GIS MANAGER | 440-255-1945 | whunter@cobrapipeline.com | ON 2/22/2016 A THIRD PARTY OPERATOR DAMAGED THE PIPELINE WHILE INSTALLING DRAIN TILE IN A FARM FIELD. COBRA WAS NOTIFIED OF THE DAMAGE AND DISPATCHED PERSONNEL TO THE SCENE. THE PERSONNEL ASSESSED THE DAMAGE AND GAS SUPPLY WAS ISOLATED AT 3 PM USING A KEY VALVE A FEW HUNDRED YARDS NORTH OF THE INCIDENT AREA AND A KEY VALVE SOUTH OF THE INCIDENT AREA. AT THIS POINT THE LINE WAS MANUALLY REGULATED DOWN TO 80 PSI TO MINIMIZE GAS LOST WHILE ALLOWING UTILITY GAS CUSTOMERS TO MAINTAIN SERVICE. A LINE STOPPLE WAS INSTALLED A FEW HUNDRED YARDS SOUTH OF THE INCIDENT AREA TO FULLY ISOLATE THE DAMAGED SECTION. THIS COMPLETELY STOPPED THE RELEASE OF GAS AND ALLOWED THE REST OF THE SYSTEM OUTSIDE THE INCIDENT AREA TO RETURN TO NORMAL OPERATING PRESSURE WHILE THE REPAIRS WERE MADE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160026 | 17054 | 2016-03-28 09:37 | ORIGINAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2016-03-18 05:32 | 2016 |  |  | 32.1493 | -88.8427 | 1143155 | 2016-03-18 07:20 |  | NATURAL GAS |  | 9825 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | STATION WAS ALREADY OFFLINE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-03-18 07:17 | 2016-03-18 07:15 | ONSHORE | MS | 39439 | HEIDELBERG | JASPER | MILEPOST | 41.189 | MS100-001 | CS105 COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2002 |  | CARBON STEEL |  | OTHER | [8 empty] | STATION DISCHARGE STACK VENTED BECAUSE OF ESD | CLASS 1 LOCATION | NO |  | 146 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 17136 | 17597.8867924528 | 7800 | 8446.56733308186 | 1000 | 1082.89324783101 | 0 | 0 |  |  | 25936 | 22618.802160808 | 27127.3473733657 | [8 empty] | 1075 |  | 1249 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | STATION WAS OFFLINE | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [52 empty] | LIGHTNING |  |  | DIRECT HIT |  |  | YES |  |  |  | YES | SEVERE THUNDERSTORMS | [301 empty] | SHANNON MATTINGLY | OQ AND PA COORDINATOR | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 2706886361 | jeff.mcmaine@bwpmlp.com | LIGHTNING FROM A SEVERE THUNDERSTORM MOVING THROUGH THE AREA STRUCK THE GENERATOR TRANSFER SWITCH. THE GENERATOR COULD NOT START UPON LOSS OF POWER TO THE STATION. ESD ACTIVATED RESULTING IN THE STATION BLOWING DOWN THROUGH THE BLOW DOWN STACK/SILENCER. DISCHARGE VALVE DID NOT FULLY SEAT RESULTING IN GAS LOSS THROUGH THE BLOW DOWN SYSTEM.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160027 | 30269 | 2016-03-28 09:50 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2015-10-01 12:00 | 2015 |  |  | 30.3664 | -92.2431 | 1141845 | 2016-03-02 16:20 |  | NATURAL GAS |  | 132285 | 91 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-03-04 13:00 | 2016-03-04 16:49 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-03-02 16:15 | 2016-03-02 16:20 | ONSHORE | LA | 70525 | CHURCHPOINT | ACADIA | MILEPOST | 10.55 | INDEX 205-5 | OPELOUSAS 6" | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 1 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | UNKNOWN |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 112 |  | NO | NO | NO |  | 0 | 0 | 159 | 173.769582183306 | 297221 | 265824.415492958 | 118350 | 129343.585228895 | 1000 | 1092.89045398306 | 0 | 0 |  |  | 416730 | 335545.790751393 | 396434.660758019 | [8 empty] | 445 |  | 595 | 192.619(A)(4) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 12408 | NO |  | YES |  | YES |  | YES | GAS FLOW AND PHYSICAL CONFIGURATION OF PIPE ENDS | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [7 empty] | CONTRACTOR | BACKHOE/TRACKHOE | DRAINAGE | YES | 150431480 | LOUISIANA ONE CALL 811 | UTILITY OWNER | NO | NO | NO |  | LOCATING PRACTICES NOT SUFFICIENT |  | FACILITY MARKING OR LOCATION NOT SUFFICIENT | [264 empty] | SHANNON MATTINGLY | PA OQ AND EVENT SUPPORT PROGRAM LEADER | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | DARRAL WARD | MANAGER PIPELINE SAFETY | 2706886356 | darral.ward@bwpmlp.com | CONTRACTOR, WHO WAS CLEANING DITCH BY EXCAVATION, GRABBED A ONE-INCH TAP VALVE WHICH PULLED THE THREADS CAUSING LEAK. 2-15-18 REVISE PER PHMSA'S INSTRUCTIONS. *APPROXIMATELY 10-1-2015, RANDY'S DIRT SERVICES (WICKOFF DRAINAGE DISTRICT/CITY OF) APPARENTLY DAMAGED A 1" BRANCH CONNECTION. *ON 3-2-16 AT 16:15, FARMER NOTIFIED GULF SOUTH OF POTENTIAL LEAK. *ON 3-2-16 AT 16:20, LEAK CONFIRMED AND CONFIRMED DISCOVERY THAT REPORTING CRITERIA WAS MET (SINCE SMALL GAS LEAK OF UNKNOWN DURATION, ASSUMED 3 MMCF GAS LOSS). DUE TO THE LIMITED NATURE OF GAS LOSS COMING THROUGH THE 1" BRANCH CONNECTION, PRESSURE WAS LOWERED BY 20% AND REPAIR WAS SCHEDULED. *ON 3-4-16 AT 13:00, PIPELINE WAS SHUT DOWN AND REPAIRED. 3-5-2018 REVISE IN RESPONSE TO PHMSA EMAIL. GULF SOUTH ASSUMES THAT THE DAMAGE TO THE PIPE OCCURRED AS PART OF EXCAVATION THAT OCCURRED ON 10-1-2015, BUT THAT IS ONLY AN ASSUMPTION. IN OUR OPINION, THE SUB-CAUSE IS BY PREVIOUS DAMAGE DUE TO EXCAVATION. BASED ON THE FACT THAT WE ASSUME POSSIBLE LEAKAGE OCCURRED AS EARLY AS 10-1-2015, GULF SOUTH ASSUMED THE GAS LOSS EXCEEDED 3 MMCF, THEREFORE, CREATING AN INCIDENT. THE DATA PROVIDED IS ATTEMPTING TO REFLECT THIS UNDERSTANDING OF THIS INCIDENT. A PIPELINE MARKER WAS LOCATED WITHIN APPROXIMATELY 10-FEET OF THE DAMAGED PIPE. 5-2-18 REVISE IN RESPONSE TO PHMSA EMAIL. GULF SOUTH'S ASSETS WERE CLEARLY MARKED WITH PIPELINE MARKERS BUT THE ONE CALL WAS IMPROPERLY CLEARED. THE ONE CALL TICKET WAS RECEIVED ON 10-1-2015 AND THE POSITIVE RESPONSE WAS DELIVERED ON 10-2-2015 SO THE BEST SPECULATION IS THAT THIS INCIDENT OCCURRED ON 10-2-2015. RESPONSES TO PART G HAVE BEEN REVISED TO PROPERLY REFLECT THIS. PART A HAS BEEN REVISED TO REFLECT THAT THE DATE AND TIME OF THE INCIDENT WAS 10-2-2015 WHEN WE BELIEVE THE DAMAGE LIKELY OCCURRED. THE TIME IS 12:00 BECAUSE WE HAVE NO WAY TO DETERMINE THE CORRECT TIME SINCE WE DIDN'T KNOW UNTIL 3-2-2016 THAT DAMAGE HAD OCCURRED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160028 | 17170 | 2016-03-31 15:37 | SUPPLEMENTAL FINAL | 32163 | ROCKIES EXPRESS PIPELINE LLC | 370 VAN GORDON ST | LAKEWOOD | CO | 80228 | 2016-03-01 10:45 | 2016 |  |  | 39.8318 | -80.8778 | 1141733 | 2016-03-01 12:32 |  | NATURAL GAS |  | 911 | 67902 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-03-01 11:40 | 2016-03-03 08:22 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-03-01 10:45 | 2016-03-01 10:45 | ONSHORE | OH | 43915 | Not Within a Municipality | MONROE | MILEPOST | INTERCONNECT | REX BEARWALLOW | REX BEARWALLOW | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2015 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 796 |  | NO | NO | NO |  | 0 | 0 | 135954 | 147223.668615617 | 1731 | 1777.6576819407 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 137685 | 69422.5270975404 | 149001.326297557 | [8 empty] | 1054 |  | 1480 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 107433 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | [8 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | GASKET |  |  |  | YES |  |  |  | YES | [172 empty] | TIM ARNOLD | COMPLIANCE ENGINEER | tim.arnold@tallgrassenergylp.com | 3037633315 |  |  |  |  | JENNIFER ECKELS | COMPLIANCE MANAGER | 3037633486 | jennifer.eckels@tallgrassenergylp.com | AT APPROXIMATELY 10:45 A.M. CST ON 3/1/16 TALLGRASS FIELD PERSONNEL DISCOVERED A GAS LEAK AT THE SITE OF A HOT TAP ASSEMBLY. ALL PERSONS WERE KEPT AT A SAFE DISTANCE WHILE THE LINE PRESSURE WAS DECREASED TO THE POINT WHERE THE LEAK STOPPED. THE MAINLINE OF THE HOT TAP WAS FULLY BLOWN DOWN IN ORDER FOR THE HOT TAP ASSEMBLY TO BE REPAIRED. THE MAINLINE WAS PLACED BACK IN SERVICE ON THE MORNING OF 3/3/2016. THE GASKET LOCATED IN THE HOT TAP ASSEMBLY BETWEEN THE TOP OF THE SANDWICH VALVE AND THE SPOOL FAILED, CAUSING THE RELEASE OF GAS. THE GASKET MATERIAL HAS A MAXIMUM PRESSURE RATING OF 1400 PSIG WHICH IS BELOW THE PIPELINE MAOP OF 1480 PSIG. THE 1400 PSIG MAX PRESSURE OF THE GASKET WAS EXCEEDED FOR APPROXIMATELY 4 HOURS AND 40 MINUTES ON FEBRUARY 20, 2016, WITH A PEAK OF 1452 PSIG. THIS WAS THE FIRST AND ONLY TIME THE PRESSURE EXCEEDED 1400 PSIG. THE GASKET SUPPLIED BY THE HOT TAP CONTRACTOR WAS NOT ADEQUATE FOR THE ESTABLISHED MAOP OF THE PIPELINE, AND THE SPECIFICATIONS OF THE MATERIALS USED WERE NOT VERIFIED BY ANYONE ON SITE. DURING THE INCIDENT INVESTIGATION IT WAS NOTED THAT WHEN REMOVING THE BOLTS THE HOT TAP CONTRACTOR SAID THEY APPEARED TO BE OVER-TORQUED, WHICH MAY HAVE LED TO INADEQUATE SEALING OVER TIME BETWEEN THE FLANGES AND THE GASKET IN QUESTION.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160029 | 17062 | 2016-04-07 16:32 | ORIGINAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2016-03-14 09:55 | 2016 |  |  | 30.7233 | -92.7123 | 1142772 | 2016-03-14 10:47 |  | NATURAL GAS |  | 2923 | 6 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-03-15 12:30 | 2016-03-16 17:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-03-14 09:55 | 2016-03-14 09:55 | ONSHORE | LA | 71463 | OAKDALE | ALLEN | MILEPOST | 30 | INDEX 202 | MARKSVILLE LINE | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | IN OR SPANNING AN OPEN DITCH |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 |  | 0.188 | 35000 | API 5L, B | SEAMLESS |  | UNKNOWN | COAL TAR | [28 empty] | 1931 | 1931 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 102 |  | NO | NO | NO |  | 0 | 0 | 10 | 10.8289324783101 | 5094 | 5231.30458221024 | 68000 | 73636.7408525085 | 3000 | 3248.67974349302 | 0 | 0 |  |  | 76104 | 40720.9385793491 | 82127.55411069 | [8 empty] | 450 |  | 606 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 10348 | NO |  | YES | YES | YES |  | YES | DRESSER COUPLINGS, CHILL RINGS, MUELLER STOPPLES, MAIN LINE PLUG VALVES, BENDS AND SIPHONS | YES | YES | YES | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  | YES | [5 empty] | YES |  |  |  | YES | [5 empty] | NO | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | SHANNON MATTINGLY | PA OQ AND EVENT SUPPORT PROGRAM LEADER | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 2706886361 | jeff.mcmaine@bwpmlp.com | GULF SOUTH PIPELINE WAS NOTIFIED OF A LEAK ON ITS INDEX 202, IOWA-MARKSVILLE 6-4-3" LINE AT MP 30.84. THE SECTION WAS ISOLATED AND BLOWN DOWN AND NEW PIPE WAS INSTALLED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160030 | 17205 | 2016-04-07 18:24 | SUPPLEMENTAL FINAL | 6141 | NEW MEXICO GAS COMPANY | 7120 WYOMING BLVD NE SUITE 20 | ALBUQUERQUE | NM | 87109 | 2016-03-10 10:38 | 2016 |  |  | 35.8225 | -107.3515 | 1142456 | 2016-03-10 12:07 |  | NATURAL GAS |  | 4907 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-03-10 12:09 | 2016-03-10 20:32 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 20 | 2016-03-10 10:38 | 2016-03-10 11:38 | ONSHORE | NM | 87013 | Not Within a Municipality | MCKINLEY COUNTY | MILEPOST | MP 3.56 G/GML | SAN JUAN TRANSMISSION | GRANTS/GALLUP ML | YES | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 10 |  | YES |  |  |  |  | YES | UNCASED | [16 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 |  | 0.156 | 42000 | X42 | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1976 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 9 | 6 | [7 empty] | CLASS 1 LOCATION | NO |  | 148 |  | NO | NO | NO |  | 2000 | 2165.78649566201 | 0 | 0 | 12685 | 13026.9137466307 | 10385 | 11245.846378725 | 1750 | 1895.06318370426 | 0 | 0 |  |  | 26820 | 20531.7703778059 | 28333.609804722 | [8 empty] | 450 |  | 720 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 52800 | NO |  | YES |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EVENT WAS CAUSED BY A THIRD-PARTY DAMAGE TO PIPELINE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO | YES | OTHER | [6 empty] | YES |  |  | UNKNOWN/OTHER | GRADER/SCRAPER | GRADING | NO |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO |  | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | GARY ROYBAL | MANAGER DOT PIPELINE SAFETY COMPLIANCE | ggroybal@tecoenergy.com | 505-697-3636 | 505-697-4481 |  |  |  | EDWARD KACER | V.P. OPERATIONS AND ENGINEERING | 505-697-3303 | ejkacer@tecoenergy.com | A ROAD GRADER SCRAPED THE PIPELINE WITH THE BLADE AND GOUGED A HOLE APPROXIMATELY 6" X 9". GRADER OPERATOR DID NOT CALL THE NM ONE-CALL NOTIFICATION CENTER FOR A LOCATE REQUEST.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160031 | 17065 | 2016-04-12 15:29 | ORIGINAL FINAL | 31451 | KINDER MORGAN TEXAS PIPELINE CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2016-03-22 11:00 | 2016 |  |  | 30.2644 | -98.1125 | 1143459 | 2016-03-22 12:50 |  | NATURAL GAS |  | 1395 | 4320 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-03-22 11:15 | 2016-03-24 19:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 1 | 2016-03-22 11:00 | 2016-03-22 11:30 | ONSHORE | TX | 78620 | DRIPPING SPRINGS | HAYS | MILEPOST | 256.25 | HILL COUNTRY PIPELINE | RANCHO | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 15 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 |  | 0.312 | 52000 | API 5LX | FLASH WELDED |  | A.O. SMITH | ASPHALT | [28 empty] | 1952 | 1951 | CARBON STEEL |  | MECHANICAL PUNCTURE | 5 | 6.3 | [7 empty] | CLASS 1 LOCATION | NO |  | 431 |  | NO | NO | NO |  | 0 | 0 | 7776 | 8420.57789513391 | 2511 | 2578.68194070081 | 35000 | 37901.2636740852 | 1000 | 1082.89324783101 | 0 | 0 |  |  | 46287 | 24433.4607995152 | 49983.416757751 | [8 empty] | 650 |  | 676 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 29938 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CAUSE WAS THIRD PARTY DAMAGE SO GAS CONTROL HAD NO EFFECT ON THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  | YES | PRIVATE LANDOWNER | [7 empty] | OCCUPANT | UNKNOWN/OTHER | ELECTRIC | NO | [5 empty] | NO |  | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | KENNETH PETERS | SR. ENGINEER | ken_peters@kindermorgan.com | 2053257554 | 2053253508 |  |  |  | REJI GEORGE | DIRECTOR CODES STANDARDS | 7134205433 | reji_george@kindermorgan.com | AN ELECTRICAL CONTRACTOR EMPLOYED BY THE LAND OWNER WAS EXCAVATING TO INSTALL A NEW ELECTRIC FACILITY. THE CONTRACTOR DID NOT MAKE A ONE CALL NOTIFICATION. HIS ROCK SAW STRUCK THE 24" KINDER MORGAN TEXAS PIPELINE (KMTP) AND CAUSED A RELEASE OF NATURAL GAS. THE LAND OWNER CONTACTED KMTP GAS CONTROL WHO DISPATCHED KMTP FIELD OPERATIONS PERSONNEL. THE PIPELINE WAS THEN ISOLATED AND BLOWN DOWN. THERE WAS NO FIRE, NO FATALITIES, AND NO INJURIES. THERE WAS NO PROPERTY DAMAGE EXCEPT FOR THE PIPE. REPAIRS WERE MADE AND THE PIPELINE WAS PLACED BACK INTO SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160032 | 17204 | 2016-04-15 12:35 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2016-03-14 16:50 | 2016 |  |  | 45.0244 | -94.0726 | 1142832 | 2016-03-14 18:46 |  | NATURAL GAS |  | 7376 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE LEAK CONTINUED UNTIL STOPPLE AND BYPASS WERE INSTALLED. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-03-14 17:12 | 2016-03-14 18:53 | ONSHORE | MN | 55349 | Not Within a Municipality | WRIGHT | MILEPOST | MILEPOST 10.2 | HOWARD LAKE BRANCH LINE | MNB75801 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 3.5 |  | 0.216 | 35000 | 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | CANADIAN MILL | COAL TAR | [28 empty] | 1961 | 1961 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 74 |  | NO | NO | NO |  | 0 | 0 | 20000 | 21657.8649566201 | 100000 | 102695.417789757 | 20000 | 21657.8649566201 | 160000 | 173262.919652961 | 0 | 0 |  |  | 300000 | 205884.317670899 | 319274.067355959 | [8 empty] | 883 |  | 950 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 200 | NO | YES | [6 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS IDENTIFIED BY THE PUBLIC AND AN EMERGENCY RESPONDER WITHIN MINUTES OF THE OCCURRENCE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [64 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | [10 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [7 empty] | FARMER | FARM EQUIPMENT | AGRICULTURE | NO |  |  |  | NO | NO |  |  | PREVIOUS DAMAGE | [121 empty] | NO | [62 empty] | NO | NO |  |  | NO | [13 empty] | NO | [63 empty] | JOHN GORMLEY | SR CORROSION SPECIALIST | john.gormley@nngco.com | 402-398-7494 |  |  |  |  | THOMAS CORRELL | SR DIRECTOR PIPELINE SAFETY & RISK | 402-398-7715 | thomas.correll@nngco.com | ON MARCH 14, 2016 AT ABOUT 17:00 HOURS LOCAL RESIDENTS AND EMERGENCY RESPONDERS NOTIFIED THE OPERATIONS COMMUNICATION CENTER OF A VISIBLE AND AUDIBLE LEAK IN THE MIDDLE OF A FARM FIELD ABOUT 1.5 MILES SOUTH OF HOWARD LAKE, MINNESOTA. THE LEAK WAS CAUSED BY A CRACK IN THE 3-INCH BRANCH LINE. THE BRANCH LINE CONTAINED OBVIOUS THIRD PARTY DAMAGE. WE BELIEVE THE LANDOWNER WAS DEEP TILLING IN THE LATE 1960'S OR 70'S WHEN HE STRUCK AND BENT THE BRANCH LINE. AFTER NEARLY 50 YEARS, THE DAMAGE FINALLY REACHED CRITICAL FLAW SIZE AND A 1/16-INCH WIDE BY 2-INCH LONG CRACK OPENED. GAS PRESSURE IN THE PIPELINE DROPPED TO AS LOW AS 611 PSI WHERE IT REMAINED. NORTHERN LET THE LEAK CONTINUE UNTIL THE SECTION COULD BE ISOLATED AND BYPASSED USING LINE STOPPING EQUIPMENT. THE SECTION OF PIPE WAS REPLACED AND THE LINE RETURNED TO SERVICE ON MARCH 18, 2016 WITHOUT ANY INTERRUPTION OF SERVICE TO CUSTOMERS. A SECTION OF THE DAMAGED SECTION WAS SENT TO A METALLURGICAL LABORATORY FOR ANALYSIS BUT IT IS HIGHLY UNLIKELY THEY WILL BE ABLE TO DETERMINE WHEN THE DAMAGE OCCURRED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160033 | 17184 | 2016-04-15 16:21 | SUPPLEMENTAL FINAL | 4060 | DOMINION EAST OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2016-03-16 14:30 | 2016 |  |  | 40.3458 | -81.4975 | 1143026 | 2016-03-16 16:32 |  |  |  | 2.25 | 4405.79 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-03-16 18:00 | 2016-03-19 21:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-03-16 14:00 | 2016-03-16 14:30 | ONSHORE | OH | 43837 | PORT WASHINGTON | TUSCARAWAS | SURVEY STATION NO. | 2424+00 | L#259 | 2591966429029688071 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION | [19 empty] | FILLET WELD | [18 empty] | 1957 |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 2 LOCATION | NO |  | 470 |  | NO | NO | NO |  | 0 | 0 | 13738 | 14876.7874387024 | 7 | 7.18867924528302 | 96805 | 104829.480856281 | 5000 | 5414.46623915503 | 0 | 0 |  |  | 115550 | 57441.1715212487 | 125127.923213383 | [8 empty] | 595 |  | 675 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 48582 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DEO DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER'S ACTIONS OR CONTROL ROOM WAS NECESSARY. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [7 empty] | YES | [21 empty] | YES | SETTLEMENT OF THE BRANCH CONNECTION DUE TO IMPROPER SUPPORT. | [55 empty] | YES | YES | [6 empty] | 2010 | [55 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | LAUREN L SKUFCA | ENGINEER | lauren.l.skufca@dom.com | 2166338865 |  |  |  |  | LAUREN L SKUFCA | ENGINEER | 2166338865 | lauren.l.skufca@dom.com | ON MARCH 16, 2016, DOMINION EMPLOYEES WERE NOTIFIED OF A POTENTIAL GAS LEAK IN PORT WASHINGTON, OHIO. DOMINION REPRESENTATIVES REPORTED TO THE AREA AND VERIFIED A LEAK. GAS CONTROL WAS NOTIFIED TO BEGIN PRESSURE REDUCTIONS IN THE LINE BEGINNING AT APPROXIMATELY 14:00, AND A BLOW DOWN PROCEDURE WAS COMPLETED AROUND 18:00 ON THE SAME DAY. THE SITE WAS EXCAVATED ON MARCH 17, 2016 AND THE LEAK WAS VALIDATED. THE LEAK WAS REPAIRED BY REPLACEMENT OF THE AFFECTED SECTION OF PIPE ON MARCH 19, 2016 AND THE LINE RESTORED TO SERVICE. THE SECTION OF PIPE THAT LEAKED WAS ANALYZED INTERNALLY DUE TO THE CIRCUMSTANTIAL SIMILARITIES FROM A RECENTLY REPORTED FAILURE, WHICH WAS SENT TO A 3RD PARTY LABORATORY FOR ANALYSIS. AFTER COMPLETION OF THE INTERNAL ANALYSIS, IT WAS CONFIRMED THAT THE CONDITIONS SURROUNDING THIS FAILURE ARE IDENTICAL. THE PREVIOUS FAILURE ANALYSIS DETERMINED THAT THE FAILURE WAS CAUSED BY DUCTILE OVERLOAD OF THE PIPE WALL AT THE WELD TOE. THE PRIMARY FACTOR TO THE FAILURE WAS SETTLEMENT OF THE BRANCH CONNECTION DUE TO IMPROPER SUPPORT. THE SETTLEMENT CAUSED BENDING STRESSES IN THE CARRIER PIPE AT THE SADDLE REINFORCEMENT FILLET WELD WHICH RESULTED IN THE FORMATION OF A CRACK. THE GEOMETRY OF THE FILLET WELD THAT ATTACHED THE SADDLE REINFORCEMENT PAD TO THE CARRIER PIPE WAS ALSO A CONTRIBUTING FACTOR TO THE FAILURE. THE SADDLE THICKNESS WAS 2.5 TIMES THE THICKNESS OF THE CARRIER PIPE WHICH CONTRIBUTED TO A STRESS CONCENTRATION IN THE THINNER PIPE AT THE FILLET WELD TOE. UNDERCUT AT THE TOE OF THE FILLET WELD FURTHER CONCENTRATED THE STRESS AND CONTRIBUTED TO THE FORMATION OF A CRACK.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160034 | 17256 | 2016-04-27 17:43 | SUPPLEMENTAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2016-03-28 20:16 | 2016 |  |  | 35.2547 | -93.1109 | 1143941 | 2016-03-28 21:06 |  | NATURAL GAS |  | 130 | 37 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | FIRST PUT A SLEEVE ON IT, BUT CONTINUED TO LEAK AT A SLOWER RATE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-03-28 20:16 | 2016-03-28 21:02 | ONSHORE | AR | 72801 | RUSSELLVILLE | POPE | SURVEY STATION NO. | 3338+68 | ENABLE GAS TRANSMISSION | LINE B | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | IN OR SPANNING AN OPEN DITCH |  |  |  | YES | [6 empty] | YES | UNCASED | UNKNOWN | 4 | BELOW WATER, PIPE ON OR ABOVE BOTTOM | [11 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10 |  | 0.279 | 24000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | NONE | [28 empty] | 1928 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 2 LOCATION | NO |  | 154 |  | NO | NO | NO |  | 0 | 0 | 63 | 68.2222746133534 | 1200 | 1232.34501347709 | 118123 | 127914.599113542 | 2275 | 2463.58213881554 | 0 | 0 |  |  | 121661 | 61155.9693186521 | 131678.748540448 | [8 empty] | 460 |  | 500 | 192.619(A)(4) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL |  | NO | YES | [6 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL ROOM DID NOT CONTRIBUTE TO THE LEAK. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  |  | YES |  |  |  | YES | SUBMERGED IN SEASONAL CREEK. |  |  | YES |  |  |  | NO | [11 empty] | YES | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE MANAGER | casey.roberts@enablemidstream.com | 4055584647 |  |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE MANAGER | 4055584647 | casey.roberts@enablemidstream.com | ON 3/28/2016 AT 20:16 CENTERPOINT ENERGY-ARKLA NOTIFIED EGT OF A POSSIBLE GAS LEAK IN A CREEK WITHIN THE CITY LIMITS OF RUSSELLVILLE AR. AT 21:02, ENABLE GAS TRANSMISSION FIELD PERSONNEL CONFIRMED A LEAK ON EGT'S LINE B IN RUSSELLVILLE IN A CREEK CROSSING. THE PIPE WAS SUBMERGED IN 3 TO 5 FEET OF WATER. THE NEAREST STREETS ARE ASHBROOK DRIVE ON ONE SIDE AND E. 22ND ON THE OTHER. THE LEAK SITE WAS NOT WITHIN 220 YARDS OF ANY BUILDING INTENDED FOR HUMAN OCCUPANCY OR OUTDOOR PLACE OF ASSEMBLY. THE PRESSURE ON THE LINE (LINE B) WAS 464 PSIG, AND FIELD PERSONNEL COORDINATED WITH ENABLE SYSTEM CONTROL TO PLAN TO REDUCE THE PRESSURE TO 340 PSIG. THE LEAK WAS MONITORED OVERNIGHT. ON 3/29/2016 WE WERE ABLE TO INSTALL A 10X18 PLIDCO BOLT ON SLEEVE AND SLOWED THE LEAK DOWN TO A TRICKLE THAT WOULD ALLOW US TO SAFELY MONITOR IT UNTIL WE DEVELOPED A PROJECT TO REPLACE THE PIPE IN THE CREEK CROSSING. UNTIL A PERMANENT REPAIR COULD BE MADE A MANUAL BLOCK VALVE AT 2790+72 IS CLOSED AND ONE AT 3950+38 CLOSED TO ISOLATE 115,966 FEET AT LOWER PRESSURE AND FEEDING THIS SECTION FROM LINE BM-20 300 PSIG) TO KEEP THE CITY OF RUSSELLVILLE AND TOWNS WEST OF THERE IN SERVICE. THE LEAK SITE WAS MONITORED DAILY AND MATERIAL WAS ORDERED IN EARLY APRIL FOR THE REPAIR. WORK AND WELDING BEGAN ON JUNE 27TH, 2016. THE REPLACEMENT SECTIONS WAS HYDROSTATIC TESTED AND INSTALLED WITH WORK COMPLETE ON JULY 14TH, 2016. THE REPLACEMENT SECTION WAS 150 FEET IN LENGTH. THE REMOVED SECTION AND THE EXISTING SECTIONS WERE EXAMINED FOR INTERNAL CORROSION, WITH NONE FOUND. THE REMOVED SECTION WAS BROUGHT TO THE RUSSELLVILLE OPERATIONS WAREHOUSE WHERE THE PLIDCO SLEEVE WAS REMOVED FOR BETTER EXAMINATION OF THE LEAK AREA. THE EXTERNAL PIPE EXAMINATIONS SHOW EXTENSIVE ATMOSPHERIC CORROSION OF THE TOP PORTION OF THE LINE B CROSSING PIPE FOR APPROXIMATELY 11 FEET. THE LEAK AREA WAS AT THE 10 O'CLOCK POSITION FACING UPSTREAM IN THE CREEK.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160035 | 17285 | 2016-05-06 12:27 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2016-04-09 22:50 | 2016 |  |  | 38.7003 | -82.8338 | 1144866 | 2016-04-10 00:50 |  | NATURAL GAS |  | 3800 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-04-09 23:29 | 2016-04-10 19:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-04-09 10:50 | 2016-04-09 11:00 | ONSHORE | OH | 45694 | Not Within a Municipality | SCIOTO | MILEPOST | 563.72 | WHEELERSBURG OHIO COMPRESSOR STATION | OWIN-WHEE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | INSTRUMENTATION | [38 empty] | 2015 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL | OTHER | [8 empty] | UNINTENDED GAS RELEASE | CLASS 1 LOCATION | NO |  | 634 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 7600 | 7804.85175202156 | 15000 | 16243.3987174651 | 0 | 0 | 0 | 0 |  |  | 22600 | 15547.7928280128 | 24048.2504694867 | [8 empty] | 749 |  | 936 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER COULD NOT HAVE CAUSED OR CONTRIBUTED TO THE EVENT BECAUSE THE ESD WAS INITIATED BY A FAILURE OF A SOLENOID AT THE COMPRESSOR STATION. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | INSTRUMENTATION MALFUNCTION | [161 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | deteschendorf@spectraenergy.com | 713-627-5573 |  |  |  |  | NATHAN ATANU | MANAGER | 713-627-5008 | nyatanu@spectraenergy.com | TEXAS EASTERN'S WHEELERSBURG COMPRESSOR STATION EXPERIENCED AN INADVERTENT NATURAL GAS RELEASE APRIL 9, 2016 WHICH WAS CAUSED BY A 3 WAY SOLENOID VALVE MALFUNCTION. THE MALFUNCTION WAS THE RESULT OF A SUPPLY GAS PRESSURE LEAK. THE SUPPLY GAS PRESSURE LEAK CAUSED THE FLEX FLOW VALVE TO OPEN WHICH ACTIVATED THE ESD VALVES RELEASING NATURAL GAS TO ATMOSPHERE.
2021-02-26 10:37 | YES | YES | GT (Gas Transmission) | 20160036 | 17174 | 2016-05-06 13:50 | SUPPLEMENTAL FINAL | 32513 | AMEREN ILLINOIS COMPANY | 10 EXECUTIVE DR. | COLLINSVILLE | IL | 62234 | 2016-04-06 13:45 | 2016 |  |  | 38.7385 | -89.9698 | 1144632 | 2016-04-06 15:00 |  | NATURAL GAS |  | 1305 | 0 | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | NO | [5 empty] | 0 |  | YES |  | 2016-04-06 14:35 | 2016-04-08 16:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2016-04-06 13:48 | 2016-04-06 14:02 | ONSHORE | IL | 62062 | MARYVILLE | MADISON COUNTY | SURVEY STATION NO. | SEE GPS COORD | SYSTEM # 1997 | G3 FID # 6247543 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 11 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10 |  | 0.25 | 42000 | API 5LX-42 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1962 | 1963 | CARBON STEEL |  | MECHANICAL PUNCTURE | 8 | 4 | [7 empty] | CLASS 3 LOCATION | NO |  | 238 |  | NO | NO | NO |  | 2000000 | 2165786.49566201 | 0 | 0 | 4919 | 5051.58760107817 | 96401 | 104391.991984157 | 103 | 111.538004526594 | 0 | 0 |  |  | 2101423 | 1047360.23777937 | 2275341.61325178 | [8 empty] | 600 |  | 850 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 13200 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY DAMAGE WAS THE SOURCE OF THE INCIDENT, THE CONTROL ROOM OBSERVED AND COMMUNICATED THE ALARMS OBSERVED. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | YES | [7 empty] | YES |  |  |  | DEVELOPER | MILLING EQUIPMENT | SITE DEVELOPMENT | YES | 762657 | J.U.L.I.E. - ILLINOIS ONE CALL SYSTEM | CONTRACT LOCATOR | YES | YES | YES | 51 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO VERIFY LOCATION BY TEST-HOLD (POT-HOLING) | [263 empty] | JOHN W BOZARTH | MGR GAS COMPLIANCE AND TRAINING | jbozarth@ameren.com | 217-625-6854 |  |  |  |  | JOHN W BOZARTH | MGR GAS COMPLIANCE AND TRAINING | 217-625-6854 | jbozarth@ameren.com | A THIRD PARTY EXCAVATOR WAS WORKING ON THE DEVELOPMENT OF A NEW SUBDIVISION ROADWAY ENTRANCE NEAR 6327 STATE ROUTE 162 IN MARYVILLE, IL. WHILE USING A CATERPILLAR ROAD RECLAIMER MACHINE TO WORK THE SOIL FOR THE NEW ROADWAY ENTRANCE , THE EXCAVATOR STRUCK AN AMEREN ILLINOIS 10" ST TRANSMISSION GAS MAIN. THE BLOWING GAS IGNITED INJURING THE ROAD RECLAIMER OPERATOR, WHO WAS ADMITTED TO THE HOSPITAL WITH BURNS. THE INJURED OPERATOR SUBSEQUENTLY PASSED AWAY A FEW WEEKS LATER. THE FIRE RESULTED IN DAMAGE TO MULTIPLE EXCAVATION EQUIPMENT UNITS AND TRUCKS ASSOCIATED WITH THE EXCAVATION COMPANY. AMEREN ILLINOIS ISOLATED THE DAMAGED SEGMENT BY CLOSING SYSTEM VALVES RESULTING IN A LOSS OF SERVICE TO 14 CUSTOMERS. THE DAMAGED LINE WAS PROPERLY LOCATED WHEN THE DAMAGE OCCURRED. THIS REPORT ORIGINALLY SHOWED ONE HOSPITALIZATION AND ONE FATALITY. IT IS BEING REVISED TO SHOW ONE FATALITY AND NO INJURIES, SINCE THE INJURED PARTY PASSED AWAY WITHIN 30 DAYS OF THE INCIDENT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160037 | 30900 | 2016-05-10 15:13 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2016-04-27 09:15 | 2016 |  |  | 30.7231 | -91.7933 | 1146335 | 2016-04-27 12:50 |  | NATURAL GAS |  | 17.6 | 164 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-04-27 10:30 | 2016-04-27 10:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-04-27 09:15 | 2016-04-27 09:15 | ONSHORE | LA | 71353 | MELVILLE | SAINT LANDRY | MILEPOST | 1.7 | TRANSCO | SHELL-ELBA 6" LATERAL | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | CREEK CROSSING | 120 |  | YES | [6 empty] | YES | UNCASED | UNKNOWN | 3 | BELOW WATER, PIPE BURIED BELOW BOTTOM (NOT IN BORED/DRILLED CROSSING) | [11 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 |  |  |  | U/K | OTHER | U/K | U/K | OTHER | U/K | [27 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO | NO |  | 0 | 0 | 495 | 536.032157676348 | 53 | 54.4285714285714 | 808220 | 875215.980761976 | 0 | 0 | 0 | 0 |  |  | 808768 | 402049.710823409 | 875806.441491081 | [8 empty] | 643 |  | 780 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 20380 | NO | [5 empty] | YES | NO LAUNCHER/RECEIVER FACILITIES EXIST | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | NO |  |  |  |  | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NOT INVOLVED IN THE INCIDENT | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [146 empty] | EDGAR RODRIGUEZ | REGULATORY COMPLIANCE SPECIALIST SR. | edgar.x.rodriguez@williams.com | 7132152846 |  |  |  |  | CLINT RATKE | MANAGER PIPELINE SAFETY | 918-573-6724 | clint.ratke@williams.com | 4-27-16 OPERATIONS SET OUT TO PERFORM ANNUAL R.O.W. PATROL. 9:15 AM COORDINATOR OF MAINTENANCE RECEIVED A CALL FROM OPERATIONS TECHNICIAN STATING THAT BUBBLES WERE OBSERVED IN A CREEK NEAR THE PIPELINE CROSSING. COM INSTRUCTED OPERATIONS TECHNICIAN TO VERIFY THE ATMOSPHERE UTILIZING A GAS DETECTOR 10:00 AM DISTRICT MANAGEMENT NOTIFIED PIPELINE CONTROL AND OPERATIONS DIRECTOR OF POSSIBLE LEAK AND WAITING VERIFICATION. 11:11 AM CREW PERFORMED TAILGATE WITH JSA AND REVIEWED SHUT-IN PROCEDURE WITH DRAWINGS AND EPPM. 11:50 AM CREW CLOSED LC-8 12:00 PM CREW CLOSED LC-120 12:37 PM CONFIRMED INDEED WE HAVE A LEAK AND DOT REPORTABLE INCIDENT AS COST WILL EXCEED $50,000 TO REPAIR CREEK CROSSING. AT THIS TIME IT WAS AGREED TO COMPLETE THE PIPELINE PATROL AND VERIFY THERE WERE NOT ANY OTHER POTENTIAL LEAKS 3:15 PM CREW INSTALLED ABSORBENT BOOMS TO CATCH ANY POTENTIAL LIQUIDS. OPERATIONS TECHNICIANS COMPLETED PATROL AND NO OTHER POTENTIAL LEAKS FOUND 5:15 PM OPERATIONS TECHNICIAN WAS ON SITE OF LEAK TO VERIFY STATUS OF BUBBLES ONCE BLOW DOWN BEGINS 5:15 PM SECOND OPERATIONS TECHNICIAN IS AT BLOW DOWN VALVE AND BEGAN BLOWING DOWN LATERAL 7:15 PM PRESSURE IS DOWN TO 100 PSI AND BUBBLES ARE REDUCED TO HALF. 7:50 PM PRESSURE IS AT 0 PSI AND BUBBLES HAVE COMPLETELY STOPPED. 8:00 PM GAS CONTROL WAS NOTIFIED THAT LATERAL HAS BEEN BLOWN DOWN AND BUBBLES COMPLETELY STOPPED INVESTIGATION PENDING TO DETERMINE CAUSE OF LEAK. REPAIR PLAN IS ALSO BEING DISCUSSED AT THE TIME OF THIS REPORT UPDATE 6/14/2017 AS OF THIS DATE THE SITE REMAINS SECURE AND THE PIPELINE SECTION REMAINS ISOLATED. WILLIAMS LOCAL OPERATIONS CONTINUES TO PATROL THE AREA. THE DIVISION ENGINEERING DEPARTMENT IS CURRENTLY WORKING ON A NUMBER OF OPTIONS TO REMEDY THIS SITUATION: 1. WORKING TOWARDS ESTIMATES TO INVESTIGATE AND REPAIR THE LEAKING SECTION OF PIPE. 2. THEY ARE COORDINATING WITH THE SINGLE SMALL PRODUCER ON POSSIBLY RETIRING THIS SECTION OF PIPE. 3. THERE IS ALSO A POTENTIAL FOR THE PIPELINE TO BE SOLD TO THE PRODUCER LATER THIS YEAR, AT THAT POINT THEY WOULD BE RESPONSIBLE FOR THE REPAIRS. UPDATE 8/31/2018 AS OF THIS DATE THE SITE REMAINS ISOLATED AND BLOWN DOWN. THERE ARE NO PLANS OF BRINGING THIS LINE BACK INTO SERVICE. IF WILLIAMS DECIDES TO BRING IT BACK INTO SERVICE AT A FUTURE DATE IT WILL BE REPAIRED AND TESTED BEFORE BROUGHT BACK INTO SERVICE. UPDATE 09/05/2018 SHELL ELBA WAS DEACTIVATED, DEPRESSURIZED AND TAKEN OUT OF SERVICE ON THE DATE OF LEAK DISCOVERY. CATHODIC PROTECTION HAS BEEN MAINTAINED TO DATE AND THE LINE HAS REMAINED WITH 0 PRESSURE SINCE BEING DEPRESSURIZED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160038 | 17245 | 2016-05-10 17:22 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2016-04-14 13:32 | 2016 |  |  | 37.7414 | -84.1467 | 1145294 | 2016-04-14 18:34 |  | NATURAL GAS |  | 3242 | 1308 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-04-14 15:15 | 2016-04-15 03:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 30 | 2016-04-14 13:30 | 2016-04-14 13:30 | ONSHORE | KY | 40385 | RICHMOND | MADISON COUNTY | MILEPOST | VS-6024 | LINE KA-1-N | VS-6024 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 20 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | TAP FITTING(STOPPLE, THREAD-O-RING, WELD-O-LET, ETC.) | [38 empty] | 2016 |  | CARBON STEEL |  | OTHER | [8 empty] | STOPPLE FITTING PLUG FAILURE | CLASS 1 LOCATION | NO |  | 328 |  | NO | NO | NO |  | 5800 | 6280.78083741984 | 2513 | 2721.31073179932 | 6063 | 6226.42318059299 | 51265 | 55514.5223500566 | 1341 | 1452.15984534138 | 25000 | 27072.3311957752 | OPERATOR COSTS FOR FAILURE ANALYSIS |  | 91982 | 49163.5378703149 | 99267.5281409853 | [8 empty] | 688 |  | 939 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 32477 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE SEGMENT OF THE LINE INVOLVED IN THIS INCIDENT WAS SUBJECT TO A WIRELINE. | [12 empty] | NO |  |  | YES | 1 | 0 | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | THE SEAL OF THE STOPPLE PLUG FAILED AFTER THE WIRELINE INSPECTION WAS COMPLETED AND BEFORE A PRE-TESTED SPOOL PIECE WAS WELDED BACK INTO THE PIPELINE. | [15 empty] | YES | MECHANICAL DAMAGE TO SEAL ELEMENT ON PLUGGING HEAD OF FITTING | [161 empty] | MARK NEWMAN | COMPLIANCE SPECIALIST | mark_newman@transcanada.com | (304)722-8475 | (304)722-8420 |  |  |  | HOWARD ROMACK | MANAGER | (832)320-5315 | lee_romack@transcanada.com | ON APRIL 14, 2016, WHILE A CONTRACTOR WAS PREPARING A STOPPLE FOR REMOVAL AFTER SUCCESSFULLY COMPLETING AN IN-LINE INSPECTION (ILI) RUN, THE STOPPLE PLUG FAILED LEADING TO AN UNINTENDED RELEASE OF NATURAL GAS (MATERIAL) INTO ATMOSPHERE. THE MATERIAL RELEASE WAS RECORDED AT 13:32 EASTERN STANDARD TIME (EST) ON LINE KA-1-N NEAR THE TOWN OF RICHMOND, MADISON COUNTY, KENTUCKY. LINE KA-1-N IS A 12 INCH TRANSMISSION PIPELINE THAT IS OWNED, OPERATED AND MAINTAINED BY COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA). LINE KA-1-N CRITICAL VALVES WERE MANUALLY OPERATED BY COLUMBIA OPERATIONS PERSONNEL TO ISOLATE THE AFFECTED SEGMENT TO ENSURE THAT THE AREA WAS SAFE. AFTER THE VERTICAL VALVES WERE FULLY CLOSED, THE MATERIAL STOPPED VENTING INTO ATMOSPHERE. AS A PRECAUTIONARY MEASURE, A NEARBY SHOP AND A BANK WERE TEMPORARILY EVACUATED. THE OCCUPANTS WERE CLEARED TO RETURN TO THEIR BUSINESSES AFTER THE AREA WAS MADE SAFE. AFTER IDENTIFYING THE PROBABLE CAUSE OF THIS UNINTENDED RELEASE (THE STOPPLE PLUG), THE STOPPLE WAS CUT AND REMOVED BY THE CONTRACTOR FOR FURTHER INVESTIGATIONS. THEREAFTER, A PRE-TESTED SECTION OF PIPE WAS INSTALLED, WELDED AND NON-DESTRUCTIVELY TESTED, AFTER WHICH THE LINE WAS RETURNED BACK INTO SERVICE ON APRIL 15, 2016, AT 03:00. COLUMBIA AND THE CONTRACTOR CONDUCTED INDEPENDENT INVESTIGATION TO IDENTIFY THE ROOT CAUSE BEHIND THE STOPPLE PLUG FAILURE. THE INVESTIGATION CONCLUDED THAT THE CAUSE WAS DUE TO EQUIPMENT FAILURE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160039 | 17318 | 2016-05-13 15:27 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2016-04-13 16:47 | 2016 |  |  | 42.7153 | -84.6031 | 1146998 | 2016-05-05 12:27 |  | NATURAL GAS |  | 231 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | IN-SERVICE REPAIR | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-04-13 16:47 | 2016-04-13 17:08 | ONSHORE | MI | 48917 | LANSING | EATON | MILEPOST | H2-L | 12 " HP TOD | LINE 1026 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 204 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | MUELLER PRESSURE CONTROL FITTING | 2010 |  | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 3 LOCATION | YES | METHOD2 | 166 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 1723 | 1769.44204851752 | 76215 | 82532.7088834402 | 343 | 371.432384006035 | 0 | 0 |  |  | 78281 | 39889.6493359064 | 84673.5833159638 | [8 empty] | 395 |  | 400 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 1800 | NO |  | YES | YES | YES |  |  |  | YES |  | YES | YES |  |  |  | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WOULD NOT HAVE BEEN DETECTABLE USING SCADA TECHNOLOGY | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | OTHER | THREADED CONNECTION/COUPLING FAILURE DUE TO LOOSE BOLTS | [8 empty] | YES | [172 empty] | KARLI MCNEILL | G ENGINEER I | karli.mcneill@cmsenergy.com | 734-524-6350 |  |  |  |  | AMANDA L. WARD | GAS REGULATORY SERVICES LEAD | 517-545-8746 | amanda.ward@cmsenergy | ON WEDNESDAY, APRIL 13, 2016 WHILE PERFORMING A MOBILE LEAK SURVEY, CONSUMERS ENERGY'S CONTRACTOR, URG, DISCOVERED NATURAL GAS READINGS NEAR 1701 S. WAVERLY RD., (EATON COUNTY) LANSING, MICHIGAN. THE URG REPRESENTATIVE COMMUNICATED THEIR FINDINGS TO CONSUMERS ENERGY GAS DISPATCH AT APPROXIMATELY 16:47 AND EMERGENCY RESPONSE PERSONNEL ARRIVED ON-SITE AT APPROXIMATELY 17:08. THE DISTRIBUTION CREW ARRIVED AT THE SCENE AT APPROXIMATELY 17:47 AND BEGAN LEAK PINPOINTING; ISOLATING THE LEAK LOCATION APPROXIMATELY 500 FEET NORTH OF THE INTERSECTION OF WAVERLY RD. AND OLD LANSING HWY. NEAR CONSUMERS ENERGY'S LINE 1026. LINE 1026 IS A HIGH PRESSURE TRANSMISSION PIPELINE OPERATING AT 20% SMYS. ON APRIL 19, 2016 THE PRESSURE ON LINE 1026 WAS REDUCED TO 315 PSIG, ALLOWING CREWS TO CONTINUE THE LEAK INVESTIGATION. THE TRANSMISSION PIPELINE WAS DETERMINED TO BE APPROXIMATELY 17 FEET DEEP AND BECAUSE OF SOIL CONDITIONS AND PIPELINE DEPTH, ADDITIONAL RESOURCES AND SHORING EQUIPMENT WERE NECESSARY TO MAINTAIN A SAFE EXCAVATION AND CONTINUE WORKING TO IDENTIFIED THE SOURCE AND PERFORM THE NEEDED REMEDIAL ACTION. ON APRIL 19, 2016 LOOSEN BOLTS ON THE LID OF A MUELLER PRESSURE CONTROL FITTING INSTALLED IN 2010 WERE DETERMINE TO BE THE SOURCE OF THE LEAK. THE FLANGES ON THE CONTROL FITTING WERE CLEANED, A NEW GASKET WAS INSTALLED AND BOLTS WERE TIGHTEN TO THE PROPER SPECIFICATION ON THURSDAY, APRIL 21, 2016 ELIMINATING THE LEAK. THE LEAK LOCATION WAS CONTINUOUSLY MONITORED BY CONSUMERS ENERGY PERSONNEL AT DISCOVERY UNTIL THE SOURCE WAS IDENTIFIED AND REPAIRED. THE PIPELINE WAS NOT ISOLATED WHILE REMEDIAL WORK WAS BEING PERFORMED TO MINIMIZE OUTAGE IMPACT TO SEVERAL CRITICAL CUSTOMERS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160040 | 17155 | 2016-05-23 15:58 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2016-04-26 15:35 | 2016 |  |  | 44.6528 | -91.153 | 1146233 | 2016-04-26 17:32 |  | NATURAL GAS |  | 6172 | 2.5 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-04-28 08:37 | 2016-04-29 18:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-04-26 15:35 | 2016-04-26 18:00 | ONSHORE | WI | 54722 | Not Within a Municipality | EAU CLAIRE | MILEPOST | 18.04 | AUGUSTA WI 3-INCH BRANCH LINE | WIB19901 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 38 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 3.5 |  | 0.156 | 35000 | 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | LONE STAR STEEL | EXTRUDED POLYEHYLENE | [28 empty] | 1966 | 1966 | CARBON STEEL |  | MECHANICAL PUNCTURE | 2.1 | 2.1 | [7 empty] | CLASS 1 LOCATION | NO |  | 59 |  | NO | NO | NO |  | 1000 | 1082.89324783101 | 12 | 12.9947189739721 | 11788 | 12105.7358490566 | 80000 | 86631.4598264806 | 10000 | 10828.9324783101 | 0 | 0 |  |  | 102800 | 57790.4992704782 | 110662.016120652 | [8 empty] | 800 |  | 950 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 106709 | NO |  | YES |  |  |  | YES | NO TOOL FOR 3-INCH PIPE | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A THIRD PARTY LINE HIT WHERE THE EXCAVATOR CALLED BEFORE WE HAD ANY INDICATION IN GAS CONTROL | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | NO |  |  |  |  | YES | [6 empty] | FARMER | FARM EQUIPMENT | AGRICULTURE | YES | 20161800916 |  | UTILITY OWNER | NO | NO | YES | 34 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | EXCAVATION PRACTICES NOT SUFFICIENT (OTHER) | [263 empty] | JOHN A GORMLEY | SR CORROSION SPECIALIST | john.gormley@nngco.com | 402-398-7494 |  |  |  |  | THOMAS CORRELL | SR DIRECTOR PIPELINE SAFETY AND RISK | 402-398-7715 | thomas.correll@nngco.com | ON APRIL 26, 2016, NORTHLAND EXCAVATION, A THIRD PARTY EXCAVATOR, STRUCK THE AUGUSTA BRANCH LINE (WIB19901) WITH A DEEP RIPPER ATTACHED TO A BULLDOZER. ALTHOUGH A ONE-CALL TICKET HAD BEEN MADE, IT WAS NOT SCHEDULED TO CLEAR UNTIL APRIL 28, 2016, AT 07:49. NORTHERN HAD PLANS TO LOCATE THE LINE ON APRIL 27, 2016. WISCONSIN HAS A 3-DAY WAIT PERIOD FOR ONE-CALL TICKETS. THE AUGUSTA #1 TBS HAS AN ALTERNATIVE FEED WITH VIKING GAS TRANSMISSION. WE ENERGIES SWITCHED OVER AND MAINTAINED SERVICE. NORTHERN STOPPLED THE AUGUSTA 3-INCH BRANCH LINE UPSTREAM OF THE FAILURE SITE AND REPAIRED THE DAMAGED SECTION OF THE LINE. THE DAMAGED SECTION WAS SENT TO A LABORATORY FOR ANALYSIS.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160041 | 17312 | 2016-05-27 07:48 | SUPPLEMENTAL FINAL | 4070 | EAST TENNESSEE NATURAL GAS, LLC (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2016-04-28 21:50 | 2016 |  |  | 35.5202 | -87.2485 | 1146482 | 2016-04-29 00:10 |  | NATURAL GAS |  | 4639 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-04-28 23:00 | 2016-04-29 12:40 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 100 | 2016-04-28 21:50 | 2016-04-28 23:00 | ONSHORE | TN | 38474 | Not Within a Municipality | MAURY | MILEPOST | 6.38 | MT. PLEASANT REDUCING STATION | M&R 58800 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1997 |  | CARBON STEEL |  | OTHER | [8 empty] | NATURAL GAS RELEASE FROM RELIEF VALVE | CLASS 1 LOCATION | NO |  | 72 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 9278 | 9528.08086253369 | 1000 | 1082.89324783101 | 0 | 0 | 0 | 0 |  |  | 10278 | 10375.2706449583 | 10610.9741103647 | [8 empty] | 663 |  | 670 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER COULD NOT REMOTELY ACTUATE DEVICES AT THE INCIDENT LOCATION | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [25 empty] | YES | TEAR IN REGULATOR DIAPHRAGM | [161 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | deteschendorf@spectraenergy.com | 713-627-5573 |  |  |  |  | NATHAN ATANU | MANAGER | 713-627-5008 | nyatanu@spectraenergy.com | AT 9:50 PM ON APRIL 28, 2016 A REGULATOR DIAPHRAGM AT THE EAST TENNESSEE NATURAL GAS MT. PLEASANT REDUCING STATION IN MAURY COUNTY, TENNESSEE DEVELOPED A TEAR WHICH CAUSED THE DOWNSTREAM PRESSURE TO INCREASE ABOVE THE RELIEF VALVE SET POINT PRESSURE RESULTING IN A RELEASE OF NATURAL GAS. APPROXIMATELY 100 PEOPLE WERE EVACUATED FROM THE VICINITY BY EMERGENCY RESPONSE OFFICIALS AS A PRECAUTION. SPECTRA ENERGY PERSONNEL SUBSEQUENTLY ISOLATED THE FACILITIES HALTING THE NATURAL GAS DISCHARGE.
2021-02-26 10:37 | YES | YES | GT (Gas Transmission) | 20160042 | 31657 | 2016-05-27 12:03 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2016-04-29 08:13 | 2016 |  |  | 40.3968 | -79.5235 | 1146495 | 2016-04-29 09:15 |  | NATURAL GAS |  | 208425 | 27775 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 |  | YES |  | 2016-04-29 09:12 |  | YES |  |  |  | YES |  |  |  |  | YES | [6 empty] | 12 | 2016-04-29 08:13 | 2016-04-29 08:25 | ONSHORE | PA | 15601 | Not Within a Municipality | WESTMORELAND | MILEPOST | 2 | LINE 27 | DELMONT TO ARMAGH | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 57 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 |  | 0.404 | 65000 | API - 5LX | DSAW |  | US STEEL | EPOXY | [28 empty] | 1981 | 1981 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 1213 | 94 |  | CLASS 1 LOCATION | NO |  | 671 |  | YES | NO | NO |  | 2350000 | 2544799.13240287 | 55550 | 60154.7199170124 | 406850 | 417816.307277628 | 624000 | 675725.386646548 | 0 | 0 | 0 | 0 |  |  | 3436400 | 1939087.47488615 | 3698495.54624406 | [8 empty] | 1039 |  | 1050 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 79411 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | YES | 5 | 0 | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [9 empty] | YES |  |  | YES | YES | 1981 |  | YES | YES |  |  |  | 2016 |  |  |  | YES | [190 empty] | YES | YES |  |  | YES |  |  |  | 2012 | [31 empty] | 2012 | [23 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | MAYRA SALINAS | ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | AT APPROXIMATELY 8:13 A.M. EST ON APRIL 29, 2016, TETLP'S 30-INCH DIAMETER LINE 27 TRANSPORTING NATURAL GAS FROM DELMONT COMPRESSOR STATION TO ARMAGH COMPRESSOR STATION IN PENNSYLVANIA FAILED AT MP 2.07. THE FAILURE RESULTED IN AN EXPLOSION AND FIRE. TETLP PERSONNEL WERE IMMEDIATELY DISPATCHED TO CLOSE MAINLINE BLOCK VALVES WITHIN THE DELMONT COMPRESSOR STATION AND AT THE CONEMAUGH RIVER MAINLINE VALVES AT MP 15.45. FIRST RESPONDERS EVACUATED THE PUBLIC FROM 9 STRUCTURES. METALLURGICAL ANALYSIS CONCLUDED THE FAILURE OCCURRED AT THE 5:30 O'CLOCK ORIENTATION AT A REGION OF EXTERNAL METAL LOSS NEAR A GIRTH WELD THAT HAD BEEN COATED WITH POLYETHYLENE TAPE. THE FAILURE INITIATED IN THE AXIAL DIRECTION AND PROPAGATED AXIALLY AND CIRCUMFERENTIALLY. THE PRESENCE OF EXTERNAL CORROSION AT THE FAILURE LOCATION INDICATES THAT THE FIELD JOINT COATING WAS COMPROMISED. THIS NARRATIVE DESCRIPTION HAS BEEN UPDATED SINCE FILING OF THE ORIGINAL REPORT TO REFLECT THE COMPANY'S FAILURE ANALYSIS. SUPPLEMENTAL REPORT: TETLP HAS MADE THE DECISION TO ABANDON THE IDLED SECTION OF LINE 27. TETLP HAS COMMENCED WORK ON THE REQUIRED FERC ABANDONMENT FILING.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160043 | 17250 | 2016-05-31 17:29 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2016-05-04 11:20 | 2016 |  |  | 38.7474 | -84.2031 | 1146921 | 2016-05-04 12:34 |  | NATURAL GAS |  | 11461 | 5398 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-05-04 12:11 | 2016-05-05 18:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-05-04 11:20 | 2016-05-04 11:20 | ONSHORE | KY | 41043 | FOSTER | BRACKEN | MILEPOST | VS- 6070 | LINE E-LOOP | VS- 6070 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 48 |  | NO | [22 empty] | INTERSTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | PIPE | PIPE BODY | 20 |  | 0.375 | 45000 | API-5L | LONGITUDINAL ERW - LOW FREQUENCY |  | YOUNGSTOWN SHEET & TUBE COMPANY | NONE | [28 empty] | 1951 | 1951 | CARBON STEEL |  | MECHANICAL PUNCTURE | 8 | 2 | [7 empty] | CLASS 1 LOCATION | NO |  | 521 |  | NO | NO | NO |  | 0 | 0 | 10094 | 10930.7244436062 | 21432 | 22009.6819407008 | 15000 | 16243.3987174651 | 0 | 0 | 0 | 0 | PRESENTED DAMAGE COST IS PRELIMINARY |  | 46526 | 35292.0762276555 | 49183.8051017721 | [8 empty] | 750 |  | 1000 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | NO | NO | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | BEING INITIATED BY A SECOND PARTY CONTRACTOR, GAS CONTROLLER WAS NOT MANIPULATING OR COMMANDING ANY VALVES CHANGES. HENCE, WAS NOT INVOLVED IN THIS INCIDENT | [12 empty] | NO |  |  | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [10 empty] | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 1604040288 | STATE ONLY | CONTRACT LOCATOR | YES | YES | NO |  | OTHER |  |  |  | ROOT CAUSE INVESTIGATION HAS NOT BEEN FINALIZED. | [262 empty] | GEORGE HAMATY | ENGINEER | george_hamaty@transcanada.com | (304)357-3728 |  |  |  |  | LEE ROMACK | MANAGER US REGULATORY COMPLIANCE | (832)320-5315 | lee_romack@transcanada.com | ON MAY 4, 2016, A CONTRACTOR PERFORMING A CONSTRUCTION ACTIVITY WITHIN THE RIGHT-OF-WAY OF LINE E-LOOP, DAMAGED A TRANSMISSION PIPELINE THAT WAS CAUSED BY THE RIPPER ON A DOZER PUNCTURING THE PIPELINE. LINE E-LOOP IS A TRANSMISSION PIPELINE THAT IS OWNED, OPERATED AND MAINTAINED BY COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA). THE PIPELINE WAS OPERATING AT APPROXIMATELY 750 PSIG WITH 1,000 PSIG BEING ITS MAOP, PIPELINE DIAMETER IS 20-INCHES WITH 0.375-INCH WALL THICKNESS, AND ITS GRADE IS X45. THERE WERE NO REPORTED FATALITIES, INJURIES OR ANY NEARBY ROADS THAT WERE SHUT DOWN. FURTHERMORE, THE UNINTENDED RELEASE OF NATURAL GAS (MATERIAL) DID NOT IGNITE. INITIAL INFORMATION INDICATED THAT THE LINE WHERE THE INCIDENT TOOK PLACE IS A CLASS 1 LOCATION SOUTH OF EDEN RIDGE ROAD NEAR THE TOWN OF FOSTER IN BRACKEN COUNTY, KY. COLUMBIA OPERATIONS PERSONNEL WHO RESPONDED TO THE INCIDENT AREA WENT TO THE NEAREST CRITICAL VALVES AND OPERATED THEM TO ISOLATE THE AFFECTED SEGMENT OF LINE E-LOOP. THE TWO CRITICAL VALVES WERE FULLY CLOSED AT 12:08 PM AND 12:11 PM RESPECTIVELY PREVENTING ADDITIONAL RELEASE OF MATERIAL INTO ATMOSPHERE. THEREAFTER, THE LINE WAS BLOWN DOWN TO ATMOSPHERIC PRESSURE AND INVESTIGATION INTO THE INCIDENT WAS INITIATED AFTER THE AREA WAS FULLY SECURED. A PRE-TESTED PIPE JOINTS WITH THE FOLLOWING CHARACTERISTICS 20-IN DIAMETER WITH 0.375-IN WT, GRADE X-65, TESTED TO A CLASS 3 LOCATION TEST PRESSURE WAS INSTALLED AND REPLACED THE DAMAGED SECTION. THE TIE-IN WELDS WERE NON-DESTRUCTIVELY EXAMINED (NDE). AFTER CONFIRMING THAT THE NDE RESULTS HAD NO ABNORMAL INDICATIONS AND THAT ALL WELDS WERE WITHIN CODE REQUIREMENTS, THE LINE WAS RETURNED BACK INTO SERVICE. AN INVESTIGATION CONDUCTED BY THE CONTRACTOR, CONCLUDED THAT ADDITIONAL SAFETY MEASURES HAVE TO BE ADDED TO THEIR PRACTICE AND EVALUATED ACTIONS WITH THEIR PERSONNEL TO PREVENT EVENTS SIMILAR FROM OCCURRING ON OTHER WORK LOCATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160044 | 17109 | 2016-06-02 12:50 | ORIGINAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2016-05-03 07:30 | 2016 |  |  | 32.3031 | -87.722 | 1146909 | 2016-05-04 10:14 |  | NATURAL GAS |  | 8.4 | 12069 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-05-03 11:45 | 2016-05-31 18:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-05-03 09:39 | 2016-05-03 07:30 | ONSHORE | AL | 36748 | LINDEN | MARENGO | MILEPOST | MP 826.30 | 90-10 VALVE SITE | 90D10 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | MAINLINE | GATE |  | DANIEL - M&J SERIAL #M3 (36-IN DIAMETER) |  |  |  | 1996 | 1995 | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 820 |  | NO | NO | NO |  | 0 | 0 | 5071 | 5491.35165975104 | 20 | 20.5390835579515 | 0 | 0 | 0 | 0 | 594000 | 643238.589211618 | ESTIMATE OF VALVE REPLACEMENT AND CONTRACTOR |  | 599091 | 297805.454588921 | 648750.479954927 | [8 empty] | 770 |  | 800 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | AUTOMATIC | 168960 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | O-RING | [17 empty] | YES | EQUIPMENT AGE | [161 empty] | TIMOTHY HUGGINS | PRINCIPAL ENGINEER | timothy.n.huggins@williams.com | 713-215-2889 |  |  |  |  | MARIE SOTAK | MANAGER PIPELINE SAFETY | 713-215-2111 | marie sotak | ON MAY 3, 2016: STATION 90 EMPLOYEE'S WERE GREASING VALVES AT THE 90-10 VALVE SITE AND NOTICED THAT THERE WERE BUBBLES IN THE WATER ACCUMULATED AROUND GROUND LEVEL OF THE MAIN LINE BLOCK VALVE 90D10. MANAGER DUANE NELSON WAS ON SITE AT THE TIME OF DISCOVERY AND NOTIFIED PIPELINE CONTROL OF THE SMALL LEAK AT APPROXIMATELY 07:30 A.M. EMPLOYEE HAND DUG APPROXIMATELY ONE FOOT IN DEPTH BEFORE DETERMINING MORE EXCAVATION WAS NEEDED TO VERIFY THE LEAK SOURCE. MANAGER INSTRUCTED THE EMPLOYEE TO START LOWERING PRESSURE ON 'D' LINE FROM THE STATION 90D0 VALVE TO THE 90D20 VALVE SITE. AFTER LOWERING PRESSURE TO STATION 90 SUCTION PRESSURE (628 PSI), STATION 90 EMPLOYEES BEGAN EXCAVATION FOR FURTHER INVESTIGATION. AT APPROXIMATELY 9:39 A.M, THE INVESTIGATION REVELED THAT THE SOURCE OF THE LEAK WAS A FAILED VALVE BODY FLANGE O-RING SEAL. THE PIPELINE SEGMENT WAS CLOSED OFF AT STATION 90 AT APPROXIMATELY 11:00 A.M AND THE PRESSURE WAS DRAWN DOWN, AND THEN SHUT-IN BLOCK VALVE 90D20 AT 11:45 A.M. THE PIPELINE WAS ISOLATED FROM 90D0 TO 90D20 AND THE PRESSURE WAS LOWERED TO 627 PSI. THE SMALL LEAK WAS DETERMINED TO BE NON-HAZARDOUS. ON MAY 4, 2016: AFTER FURTHER REVIEW WITH OPERATIONS AND DISCUSSION WITH PIPELINE SAFETY, THE SMALL LEAK WAS DETERMINED TO BE AN INCIDENT BASED ON THE RECOMMENDED VALVE REPLACEMENT COST. PIPELINE CONTROL NOTIFIED THE NRC AT 10:14 A.M. OF THE SMALL 'O' RING LEAK ON TOP OF THE GATE VALVE BODY. THE VOLUME OF THE GAS RELEASED BY THE SMALL LEAK COULD NOT BE DETERMINED. ON MAY 9, 2016: GAS RECOMPRESSION SERVICE WAS COMMENCED AT 5:20 P.M. ON THE PIPELINE SEGMENT FOR THE PLANNED OUTAGE TO REMOVE AND REPLACE THE EXISTING 36-INCH DIAMETER GATE VALVE WITH A NEW BLOCK VALVE. ON MAY 13, 2016: RECOMPRESSION WAS COMPLETED TO A PRESSURE OF 111 PSI. ON MAY 19, 2016: THE PIPELINE SECTION WAS BLOWN DOWN TO 1 PSI . ON MAY 31, 2016: VALVE WAS REPLACED AND THE PIPELINE SECTION WAS PLACED BACK INTO SERVICE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160045 | 17156 | 2016-06-02 17:25 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2016-05-06 18:30 | 2016 |  |  | 43.1569 | -96.0669 | 1147151 | 2016-05-06 20:00 |  | NATURAL GAS |  | 340 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-05-06 20:15 | 2016-05-07 14:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-05-06 18:48 | 2016-05-06 20:00 | ONSHORE | IA | 51234 | Not Within a Municipality | SIOUX | MILEPOST | MILE POST 3.9 | BOYDEN 2-INCH BRANCH LINE | IAB66701 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 2.375 |  | 0.154 | 35000 | UNKNOWN | LONGITUDINAL ERW - LOW FREQUENCY |  | REPUBLIC STEEL | COAL TAR | [28 empty] | 1954 | 1954 | CARBON STEEL |  | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 1 LOCATION | NO |  | 46 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 640 | 657.250673854447 | 19915 | 21565.8190305545 | 38435 | 41621.0019803848 | 0 | 0 |  |  | 58990 | 29685.8197613473 | 63844.0716847937 | [8 empty] | 746 |  | 800 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 41184 | NO | [5 empty] | YES | THERE ARE NO 2-INCH TOOLS AVAILABLE. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OBVIOUS THIRD PARTY DAMAGE CAUSED BY A THIRD PARTY DRAIN TILE INSTALLER. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [7 empty] | FARMER | FARM EQUIPMENT | DRAINAGE | NO |  |  | UNKNOWN/OTHER | NO | NO | YES | 20 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | JOHN A GORMLEY | SR CORROSION SPECIALIST | john.gormley@nngco.com | 402-398-7494 |  |  |  |  | THOMAS CORRELL | SR DIRECTOR PIPELINE SAFETY AND RISK | 402-398-7715 | thomas.correll@nngco.com | ON MAY 6, 2016 AT 18:33 SCOTT DOORENBOS NOTIFIED NORTHERN'S OPERATIONS COMMUNICATION CENTER (OCC) THAT HE HAD STRUCK AND COMPLETELY SEVERED THE 2-INCH BOYDEN, IOWA (IAB66701) BRANCH LINE NEAR THE INTERSECTION OF 330TH AND JACKSON AVENUE. THE APPROXIMATE MILE POST ON THE PIPELINE IS 3.91. DOORENBOS WAS INSTALLING AGRICULTURAL DRAIN TILE WITHOUT MAKING A ONE-CALL. SERVICE TO THE TOWN OF BOYDEN WAS COMPLETELY LOST. APPROXIMATELY 60-FEET OF 2-INCH PIPE WAS REPLACED AND SERVICE TO THE TOWN OF BOYDEN WAS RESTORED. MIDAMERICAN ENERGY ESTIMATED THAT 276 CUSTOMERS WOULD NEED A RELIGHT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160046 | 17438 | 2016-06-06 19:50 | SUPPLEMENTAL FINAL | 32414 | MARKWEST OKLAHOMA GAS COMPANY, LLC | 1515 ARAPAHOE ST TOWER 1, SUITE 1600 | DENVER | CO | 80202 | 2016-05-09 19:30 | 2016 |  |  | 33.9807 | -96.0069 | 1147380 | 2016-05-10 12:00 |  | NATURAL GAS |  | 32.46 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-05-09 20:45 | 2016-05-10 13:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-05-09 19:30 | 2016-05-09 19:30 | ONSHORE | OK | 74723 | BENNINGTON | BRYAN | MILEPOST | BENNINGTON | AKROMA/BENNINGTON DELIVERY | BENNINGTON DELIVERY | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | PLUG | 2009 |  | CARBON STEEL |  | OTHER | [8 empty] | A TORNADO AFFECTED THE MEASUREMENT SKID AND BUILDING AT A DELIVERY POINT. THE DEBRIS IMPACT CAUSED A PLUG TO RELEASE GAS. | CLASS 1 LOCATION | NO |  | 628 |  | NO | NO | NO |  | 89700 | 97135.5243304413 | 0 | 0 | 58 | 59.5633423180593 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 89758 | 44649.5207880666 | 97195.0876727594 | [8 empty] | 1098 |  | 1440 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A SCADA COMMUNICATION LOSS RESULTED IN DISPATCHING PERSONNEL ONSITE. THERE WAS NO INDICATION THAT THE ACTIONS OF THE CONTROLLER(S) OR CONTROL ROOM WERE THE CAUSE OF, OR A CONTRIBUTING FACTOR TO, THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [52 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | ,,,,,,A TORNADO AFFECTED THE MEASUREMENT SKID AND BUILDING AT A DELIVERY POINT. THE DEBRIS IMPACT CAUSED A PLUG TO RELEASE GAS. | YES |  |  | YES | [303 empty] | MATT CARNES | SENIOR PIPELINE INTEGRITY ENGINEER | No Email Address | 303-925-9219 | 303-825-0920 |  |  |  | GREGORY FLOERKE | EXECUTIVE VICE PRESIDENT CHIEF OPERATING OFFICER | 303-476-5680 | gregory.floerke@markwest.com | A TORNADO AFFECTED THE MEASUREMENT SKID AND BUILDING AT A DELIVERY POINT. THE DEBRIS IMPACT CAUSED A PLUG TO RELEASE GAS. THE SECTION WAS ISOLATED AND THE PLUG REPLACED. AFTER FURTHER INVESTIGATION THE NEXT DAY, THE COST OF THE MEASUREMENT BUILDING DAMAGE WAS ESTIMATED AT GREATER THAN $50,000 WHICH QUALIFIES AS AN INCIDENT AND THE TELEPHONIC NRC REPORT WAS FILED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160047 | 17169 | 2016-06-10 11:56 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2016-05-21 23:00 | 2016 |  |  | 32.1788 | -91.7266 | 1148443 | 2016-05-21 23:15 |  | NATURAL GAS |  | 428 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-05-21 23:15 | 2016-05-21 23:25 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 24 | 2016-05-21 23:00 | 2016-05-21 23:15 | ONSHORE | LA | 70538 | WINNSBORO | FRANKLIN | MILEPOST | 14.52 | WINNSBORO TOWN BORDER STATION | INDEX 381-22-1 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | DRAIN LINES | [38 empty] | 1966 |  | CARBON STEEL |  | OTHER | [8 empty] | 1" NIPPLE ON RISER WAS BROKEN OFF | CLASS 3 LOCATION | NO |  | 12 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 873 | 896.530997304582 | 7500 | 8121.69935873255 | 1500 | 1624.33987174651 | 0 | 0 |  |  | 9873 | 5403.16356742764 | 10642.5702277836 | [8 empty] | 265 |  | 322 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 5 | NO | YES | YES | [5 empty] | YES |  |  |  |  | YES | 1" RISER | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RECEIVED CALL FROM SHERIFF'S OFFICE CONCERNING CAR HITTING OUR METER STATION | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [260 empty] | SHANNON MATTINGLY | PA OQ AND EVENT SUPPORT PROGRAM LEADER | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | JEFFREY B. MCMAINE | MANGER CODES AND STANDARDS | 2706886361 | jeff.mcmaine@bwpmlp.com | A VEHICLE VEERED OFF THE ROAD AND HIT GULF SOUTH'S WINNSBORO TOWN BORDER METER STATION FACILITY. THE VEHICLE WENT THROUGH FENCING AND SHEERED OFF A 1" PIPE RISER. NO FIRE OCCURRED. BECAUSE 24 PEOPLE WERE EVACUATED IN THE MIDDLE OF THE NIGHT AND 2 INDIVIDUALS, AS GULF SOUTH UNDERSTANDS, WERE TAKEN TO THE EMERGENCY ROOM AND THEN RELEASED, GULF SOUTH CONSIDERS THIS A SIGNIFICANT EVENT AND ELECTED TO SUBMIT AN INCIDENT REPORT PER 49 CFR 191.5(A)(3). 8-19-16 REVISED TO CORRECT LATITUDE AND LONGITUDE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160048 | 17123 | 2016-06-10 15:53 | ORIGINAL FINAL | 31470 | VECTREN ENERGY DELIVERY OF OHIO | 211 NW RIVERSIDE DRIVE | EVANSVILLE | IN | 47708 | 2016-05-11 13:26 | 2016 |  |  | 39.9233 | -84.2952 | 1147502 | 2016-05-11 15:20 |  | NATURAL GAS |  | 9701 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-05-11 15:12 | 2016-05-12 06:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-05-11 13:48 | 2016-05-11 14:15 | ONSHORE | OH | 45383 | UNION | MIAMI | SURVEY STATION NO. | 144249.52 | A-97 | OGA097 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 12 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.25 | 42000 | X42 | SEAMLESS |  | NATIONAL TUBE | COAL TAR | [28 empty] | 1963 | 1962 | CARBON STEEL |  | MECHANICAL PUNCTURE | 16 | 6 | [7 empty] | CLASS 1 LOCATION | NO |  | 242 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 8461 | 8689.05929919137 | 92116 | 99751.794417201 | 552 | 597.757072802716 | 0 | 0 |  |  | 101129 | 55071.4343587987 | 109038.610789195 | [8 empty] | 309 |  | 480 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 56059 | NO |  |  | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS CAUSED BY THIRD PARTY DAMAGE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  | YES | PRIVATE BUSINESS | YES | [6 empty] | OCCUPANT | GRADER/SCRAPER | GRADING | NO | [5 empty] | YES | 15 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | JOHN SPINKS | MANAGER GAS COMPLIANCE AND QMP | jaspinks@vectren.com | 937-440-1844 | 937-440-1818 |  |  |  | JIM FRANCIS | VICE PRESIDENT SAFETY AND SYSTEM INTEGRITY | 812-491-4369 | jmfrancis@vectren.com | ON MAY 11, 2016, AT APPROXIMATELY 1:26 PM, AN EMPLOYEE OF PHILLIPS SAND AND GRAVEL OPERATING A BULLDOZER STRUCK VECTREN'S 16" STEEL TRANSMISSION LINE, A-97. THE EMPLOYEE OF PHILLIPS WAS GRADING A DIRT AND GRAVEL ROADWAY ON PHILIP'S PROPERTY WHEN THE INCIDENT OCCURRED. AT THE TIME OF THE INCIDENT, PHILLIPS TOLD VECTREN THEY HAD BEEN GRADING THIS ROADWAY FOR ABOUT FIVE YEARS. AT THE TIME OF THE INCIDENT VECTREN CHECKED AND THERE WERE NO REQUESTS MADE TO THE OHIO UTILITY PROTECTION SERVICE FOR A LOCATE. IN ADDITION, VECTREN ALSO CHECKED AND THERE WERE NO LOCATES REQUESTED FOR THE PREVIOUS FIVE YEARS. THE VECTREN TRANSMISSION LINE, OPERATING AT APPROXIMATELY 309 PSIG AT THE TIME OF THE DAMAGE, WAS MARKED BY PLASTIC LINE MARKERS WITHIN EYESIGHT OF THE INCIDENT SITE. THE LINE MARKERS STATED, AMONG OTHER THINGS, WARNING GAS PIPELINE IN AREA AND PROVIDED THE 811 NUMBER. THE BULLDOZER, EQUIPPED WITH A BLADE, STRUCK THE TRANSMISSION LINE AND CAUSED A PUNCTURE / GASH THAT UNINTENTIONALLY RELEASED NATURAL GAS. A LOCATE REQUEST WOULD HAVE RESULTED IN A VECTREN TECHNICIAN ON SITE, DURING THE WORK, TO OBSERVE THE PROXIMITY OF THE WORK TO THE TRANSMISSION LINE AND THE DEPTH OF THE TRANSMISSION LINE. VECTREN DID NOT LEARN OF THE WORK THE EMPLOYEE OF PHILLIPS WAS PERFORMING UNTIL AFTER THE INCIDENT. VECTREN WAS NOTIFIED OF THE INCIDENT, AND RESPONDING CREWS ISOLATED THE DAMAGED TRANSMISSION LINE BY OPERATING VALVES UPSTREAM AND DOWNSTREAM AND CONTROLLING THE BLOW DOWN OF THE PIPE SEGMENT. VECTREN LOST SERVICE TO 182 CUSTOMERS. THE DAMAGED TRANSMISSION LINE WAS REPLACED BY 16.5' OF NEW 16" STEEL PIPE. THE AFFECTED CUSTOMERS WERE THEN PUT BACK INTO SERVICE. THE EMPLOYEE OF PHILLIPS OPERATING THE BULLDOZER SOUGHT MEDICAL ATTENTION, WAS EVALUATED AT A LOCAL HOSPITAL, AND RETURNED TO PHILLIPS LATER THAT DAY.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160049 | 17190 | 2016-06-13 19:31 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2016-05-13 14:45 | 2016 |  |  | 35.1603 | -118.8042 | 1147779 | 2016-05-14 13:15 |  | NATURAL GAS |  | 7990 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | CLOSED VALVE BY REMOTELY LOWERING PRESSURE OF MAINLINE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-05-13 14:45 | 2016-05-13 17:40 | ONSHORE | CA | 93203 | ARVIN | KERN COUNTY | MILEPOST | PLS4 | L-300A | MP 256.2 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2014 |  | CARBON STEEL |  | OTHER | [8 empty] | PRESSURE RELIEF VALVE UNINTENTIONALLY VENTED NATURAL GAS | CLASS 1 LOCATION | NO |  | 650 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 26000 | 26700.8086253369 | 5000 | 5414.46623915503 | 0 | 0 | 0 | 0 |  |  | 31000 | 30167.3235751956 | 32115.274864492 | [8 empty] | 734 |  | 757 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | REMOTELY CONTROLLED |  | NO |  | YES |  |  |  | YES | A PIG LAUNCHER IS INSTALLED AT PLS-4, WHICH ALLOWS INSPECTION ON L-300A BETWEEN MP 256.21-299.00 (PLS-4 TO PLS-5). HOWEVER, THE SECTION OF L-300A SOUTH OF PLS-4 IS NOT CURRENTLY PIGGABLE DUE TO LACK OF A LAUNCHER/RECEIVER AND PLUG VALVES REQUIRING REPLACEMENT | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA-RELATED EQUIPMENT OPERATED AS INTENDED | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [13 empty] | YES | [177 empty] | STEPHEN RAMOS | COMPLIANCE ENGINEER | s3rc@pge.com | 925-328-6107 |  |  |  |  | SUSIE RICHMOND | MANAGER REGULATORY COMPLIANCE | 925-328-5776 | gsr8@pge.com | ON MAY 13, 2016 AT 1445 HOURS AN 8-INCH PRESSURE RELIEF VALVE (AT PRESSURE LIMITING STATION PLS4, OFF OF TRANSMISSION LINE L-300A) IN ARVIN, KERN COUNTY, MALFUNCTIONED RESULTING IN AN UNINTENTIONAL RELEASE OF GAS TO THE ATMOSPHERE. THE APPARENT CAUSE OF THE RELIEF VALVE MALFUNCTION WAS DUE TO EXCESS VIBRATION. PRESSURE IN L-300A DID NOT EXCEED THE MAOP OF 757 PSIG. OPERATION OF THE PRESSURE RELIEF VALVE WAS OBSERVED ON SCADA BY GAS CONTROL ROOM PERSONNEL AT THE TIME OF THE RELEASE, SO THE MAIN LINE REGULATOR SET POINT WAS REMOTELY LOWERED WHICH ALLOWED THE PRESSURE RELIEF VALVE TO RE-SEAT ITSELF. PG&E PERSONNEL WERE ON-SCENE AT 1740 HOURS AND THE RELEASE OF GAS WAS STOPPED AT 1800 HOURS BY REPLACING THE PILOT VALVE. THERE WERE NO INJURIES, NO FATALITIES, NO MEDIA AND NO IGNITION ASSOCIATED WITH THIS INCIDENT. THERE WAS NO CUSTOMER IMPACT. A NOTIFICATION WAS MADE TO THE NRC ON MAY 14, 2016 AT 1315 HOURS; ONCE IT WAS DETERMINED THE UNINTENTIONAL RELEASE OF GAS WAS ESTIMATED TO BE ABOVE 3 MILLION CUBIC FEET (MMCF). THE TOTAL ESTIMATED VOLUME RELEASE IS APPROXIMATELY 7.99 MMCF. LOCAL AGENCIES WERE NOTIFIED SEPARATELY ON MAY 13, 2016 BY PG&E'S ENVIRONMENTAL GROUP. THIS INCIDENT WAS REPORTED TO THE DOT & CPUC BECAUSE OF THE VOLUME OF GAS UNINTENTIONALLY RELEASED WAS ESTIMATED TO EXCEED 3 MMCF. A SPECIAL LEAK SURVEY WAS CONDUCTED FOLLOWING THE INCIDENT, AND NO LEAKS WERE IDENTIFIED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160050 | 17150 | 2016-06-16 17:41 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2016-05-21 15:52 | 2016 |  |  | 35.0242 | -87.7577 | 1148432 | 2016-05-21 19:15 |  | NATURAL GAS |  | 32147 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-05-21 15:56 | 2016-05-22 01:03 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-05-21 15:52 | 2016-05-21 16:30 | ONSHORE | TN | 38452 | Not Within a Municipality | WAYNE | MILEPOST | STATION 555 | COLLINWOOD COMPRESSOR STATION | 500-LINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | OTHER | COMPRESSOR STATION ESD ISOLATION VALVE |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 2013 |  | CARBON STEEL |  | OTHER | [8 empty] | EMERGENCY SHUTDOWN (ESD) DUE TO A FAILED GAS DETECTOR AND A ESD ISOLATION VALVE OPERATION FAILURE RESULTING IN THE UNINTENTIONAL RELEASE OF NATURAL GAS THROUGH THE ESD BLOW DOWN VENT. | CLASS 1 LOCATION | NO |  | 633 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 55085 | 56569.7708894879 | 0 | 0 | 1350 | 1461.90588457186 | 0 | 0 |  |  | 56435 | 59319.5035108554 | 58031.6767740597 | [8 empty] | 458 |  | 936 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | OTHER | FAULTY GAS DETECTOR TRIGGERED AUTOMATIC EMERGENCY SHUT-DOWN OF THE STATION. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EVENT CAUSED BY FAULTY GAS DETECTOR AND AUTOMATIC SHUTDOWN OF THE FACILITY. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | YES | [10 empty] | YES | EMERGENCY SHUTDOWN DOWN AND RELEASE OF NATURAL GAS DUE TO A FAILED GAS DETECTOR AND A ESD ISOLATION VALVE OPERATIONAL FAILURE. | [12 empty] | YES | [9 empty] | YES | THE ESD ISOLATION VALVE POWER-GAS LINE WAS IMPROPERLY CONNECTED. | [161 empty] | STEPHEN DINES | ENGINEER | stephen_dines@kindermorgan.com | 7193514199 | 7193514199 |  |  |  | REJI GEORGE | DIRECTOR OF ENGINEERING CODES AND STANDARDS | (713) 420-5433 | reji_george@kindermorgan.com | ON MAY 21, 2016, AN UNINTENTIONAL RELEASE OF NATURAL GAS OCCURRED AT THE TGP COLLINWOOD COMPRESSOR STATION 555 IN WAYNE COUNTY, TENNESSEE WHEN THE STATION EXPERIENCED AN EMERGENCY SHUT-DOWN (ESD) DUE TO A FAILED GAS DETECTOR AND SUBSEQUENT FAILURE OF AN ESD ISOLATION VALVE TO PROPERLY CLOSE. THIS RESULTED IN A RELEASE OF 32,147 MCF OF NATURAL GAS. STATION EMPLOYEES RESPONDED AND SHUT IN THE AFFECTED VALVE. A FAILED GAS DETECTOR WAS IDENTIFIED AS THE CAUSE OF THE ESD. THE REPORTABLE RELEASE OF NATURAL GAS RESULTED WHEN THE ESD ISOLATION VALVE FAILED TO CLOSE. FAILURE OF THE ESD ISOLATION VALVE TO PROPERLY CLOSE RESULTED FROM THE IMPROPER INSTALLATION OF THE UNIT POWER GAS LINES. PRIOR TO RETURNING THE STATION BACK TO SERVICE, THE POWER GAS LINES WERE PROPERLY RE-INSTALLED AND THE GAS DETECTOR COMPONENTS WERE REPLACED (CONTROLLER AND SENSORS). THE VALVE AND GAS DETECTOR WERE TESTED AND THE STATION WAS RETURNED TO SERVICE AT 1:03 AM CST THE FOLLOWING DAY.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160051 | 17141 | 2016-06-18 22:25 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2012-07-13 11:30 | 2012 |  |  | 41.6229 | -88.5801 | NRC NOTIFICATION REQUIRED BUT NOT MADE |  |  | NATURAL GAS |  | 1 | 5 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | EVENT OCCURRED INSIDE COMPRESSOR STATION; DID NOT REQUIRE INTERRUPTION | [6 empty] | YES |  |  |  |  | YES | [6 empty] | 0 | 2012-07-13 11:30 | 2012-07-13 11:30 | ONSHORE | IL | 60548 | Not Within a Municipality | KENDALL | MILEPOST | 795.4 | SANDWICH COMPRESSOR STATION | SOUTHWEST MAINLINE (100 LINE) | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | COMPRESSOR EXHAUST VENT SILENCER | 1981 |  | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 483 |  | NO | NO | NO |  | 0 | 0 | 35 | 40.1905 | 3 | 2.41649048625793 | 298000 | 342193.4 | 0 | 0 | 0 | 0 |  |  | 298038 | 157096.753785412 | 342236.006990486 | [8 empty] | 700 |  | 850 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE UNIT START-UP WAS INITIATED LOCALLY. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | SEAL FAILURE | [21 empty] | YES | LIQUID BUILD-UP ON VALVE SEATING SURFACE | [161 empty] | JOHN CHIN | SR. REGULATORY COMPLIANCE SPECIALIST | john_chin@transcanada.com | (248) 205-4522 | (248) 205-4622 |  |  |  | JOHN CHIN | SR. REGULATORY COMPLIANCE SPECIALIST | (248) 205-4522 | john_chin@transcanada.com | UNIT 1009 WAS STARTED AT ABOUT 0820 THE MORNING OF JULY 13 2012. UNIT WENT DOWN AT 0900 DUE TO HIGH DISCHARGE TEMPERATURES. ON-SITE STAFF WAS IN MEETING AND DID NOT KNOW UNIT WENT DOWN UNTIL GAS CONTROL CALLED AT 1030. BY THAT TIME HIGH TEMPERATURES HAD DISSIPATED. HIGH TEMP ALARMS WERE RESET. AT 1130 A LOCAL START OF THE UNIT WAS INITIATED. WHEN TECHNICIAN RETURN TO CONTROL ROOM AFTER HALTING START-UP OF NEARBY UNIT, HE HEARD AND FELT AN EXPLOSION. EXPLOSION OCCURRED INSIDE BLOWDOWN EXHAUST SILENCER, DAMAGING SILENCER AND NEARBY CONNECTING FACILITIES. NO PERSONNEL WERE INJURED AS A RESULT OF THE EXPLOSION. IT WAS BELIEVED THAT GAS LEAKED BY A FUEL LINE BLOCK/BLEED VALVE AND SOME ACCUMULATED GAS IN THE SILENCER IGNITED. IGNITION WAS PROBABLY INITIATED FROM MECHANICAL SPARK FROM TURBOCHARGER, A NORMAL OCCURRENCE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160052 | 17159 | 2016-06-19 00:17 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2013-08-09 13:30 | 2013 |  |  | 41.6229 | -88.5801 | NRC NOTIFICATION REQUIRED BUT NOT MADE |  |  | NATURAL GAS |  | 0.1 | 20 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | UNIT WAS ALREADY SHUT DOWN FOR MAINTENANCE | [6 empty] | NO |  |  |  |  | YES | [6 empty] | 0 | 2013-08-09 13:30 | 2013-08-09 13:30 | ONSHORE | IL | 60548 | Not Within a Municipality | KENDALL | MILEPOST | 795.4 | SANDWICH COMPRESSOR STATION | SOUTHWEST MAINLINE (100 LINE) | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 1981 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | CAST ALUMINUM | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 483 |  | NO | NO | NO |  | 0 | 0 | 69 | 77.8011586802828 | 1 | 0.780737704918033 | 624643 | 704318.103790259 | 0 | 0 | 0 | 0 |  |  | 624713 | 323337.116574698 | 704396.685686645 | [8 empty] | 5 |  | 850 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | TECHNICIANS ASSIGNED WORK HAD LIMITED HOT WORK EXPERIENCE; DEFICIENT IN RECOGNIZING PRESSURES AND IN PROPER MONITORING OF HAZARDOUS ENVIRONMENTS. | YES | YES |  | YES | INADEQUATE HOT WORK AND GAS DETECTION TRAINING. | OTHER MAINTENANCE | NO | [150 empty] | JOHN CHIN | SR. REGULATORY COMPLIANCE SPECIALIST | john_chin@transcanada.com | (248) 205-4522 | (248) 205-4622 |  |  |  | JOHN CHIN | SR. REGULATORY COMPLIANCE SPECIALIST | (248) 205-4522 | john_chin@transcanada.com | AT APPROXIMATELY 13:38 AUGUST 9, 2013, GAS THAT HAD LEAKED INTO THE CRANKCASE OF UNIT 1009 IGNITED, CAUSING AN EXPLOSION THAT DAMAGED THE ENGINE AND THE BUILDING. THREE TECHNICIANS RECEIVED FIRST AID ATTENTION FOR THEIR MINOR INJURIES AT A LOCAL MEDICAL CLINIC AND WERE SENT HOME. THE TECHNICIANS WERE PERFORMING MAINTENANCE TO REPLACE A WATER PUMP SHAFT SLEEVE IN THE UNIT. AFTER NUMEROUS UNSUCCESSFUL ATTEMPTS TO REMOVE THE EXISTING SLEEVE ON AUGUST 8, IT WAS DECIDED TO APPLY HEAT TO THE SLEEVE USING AN OXY-ACETYLENE TORCH TO TRY TO LOOSEN IT ENOUGH FOR REMOVAL. ON THE MORNING OF AUGUST 9, TWO ATTEMPTS USING HEAT WERE NOT SUCCESSFUL. THE OIL SEAL WAS REMOVED TO PROVIDE MORE WORKING ROOM. THE CREW LEFT FOR LUNCH AFTER COMPLETING THE REMOVAL OF THE OIL SEAL. UPON RETURNING, THEY APPLIED HEAT TO THE WATER PUMP SHAFT SLEEVE FOR THE THIRD TIME, IGNITING GAS THAT HAD MIGRATED INTO THE CRANKCASE IN THE ABSENCE OF THE OIL SEAL. THE EXPLOSION DAMAGED THE ENGINE AND THE BUILDING.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160053 | 17177 | 2016-06-29 10:19 | SUPPLEMENTAL FINAL | 4900 | KINDER MORGAN TEJAS PIPELINE | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2016-06-03 07:00 | 2016 |  |  | 26.6907 | -99.1021 | 1149590 | 2016-06-03 09:38 |  | NATURAL GAS |  | 9585 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | ISOLATION VALVE BENEATH RELIEF VALVE WAS CLOSED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-06-03 07:00 | 2016-06-03 07:00 | ONSHORE | TX | 78564 | Not Within a Municipality | ZAPATA COUNTY | SURVEY STATION NO. | 26+14 | STARR TEJAS 423-200-0 | STARR TEJAS 423-200-0 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1961 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE RELEASED NATURAL GAS AT A PRESSURE BELOW MAOP AND SET POINT. | CLASS 1 LOCATION | NO |  | 354 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 25910 | 26608.3827493261 | 100 | 108.289324783101 | 100 | 108.289324783101 | 0 | 0 |  |  | 26110 | 27685.5339133582 | 26824.9613988923 | [8 empty] | 1003 |  | 1025 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 1 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELIEF VALVE PREMATURELY RELEASED NATURAL GAS AT A PRESSURE BELOW MAOP. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | RELIEF VALVE SET POINT DRIFTED TO A LOWER PRESSURE | [161 empty] | WILLIAM MARTIN MULLER | SPECIALIST - PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205 325 3863 | 205 325 3508 |  |  |  | REJI GEORGE | DIRECTOR COMPLIANCE CODES AND STANDARDS | 7134205433 | reji_george@kindermorgan.com | 06/02/2016 10:23 AM ZAPATA FIRE DEPARTMENT CALLED KINDER MORGAN; NO LEAK AND NO VENTING FOUND BY KINDER MORGAN OPERATIONS SPECIALIST INVESTIGATING THE CALL; THERE ARE OTHER PIPELINE COMPANIES WITH FACILITIES IN THE AREA. 06/03/2016 12:50 AM SHERIFF DEPARTMENT CALLED KINDER MORGAN; NO LEAK AND NO VENTING FOUND BY KINDER MORGAN OPERATIONS SPECIALIST INVESTIGATING THE CALL. 06:45 AM KINDER MORGAN CONTRACTOR IN THE VICINITY REPORTED NOISE, POSSIBLE RELIEF VALVE ACTION. 07:00 AM KINDER MORGAN OPERATIONS SPECIALIST ARRIVED ON SITE, CONFIRMED RELIEF VALVE VENTING PREMATURELY BELOW MAOP; AFTER SAFELY VERIFYING PRESSURE, OPERATIONS SPECIALIST BEGAN CLOSING ISOLATION VALVE LOCATED BENEATH SAID RELIEF VALVE. 07:25 AM THE ISOLATION VALVE WAS FULLY CLOSED AND RELIEF VALVE VENTING WAS TERMINATED. PIPELINE SYSTEM PRESSURE WAS MONITORED. MAOP WAS NOT EXCEEDED. INVESTIGATION BY KINDER MORGAN OPERATION SPECIALIST FOUND THE RELIEF VALVE SET POINT HAD DRIFTED TO 1,003 PSIG ALLOWING THE PREMATURE VENTING TO OCCUR. THE SET POINT OF THE RELIEF VALVE WAS RESET TO 104% MAOP (1,066 PSIG) ACCORDING TO KINDER MORGAN PROCEDURE. SAID RELIEF VALVE IS A 3X4 ANDERSON GREENWOOD RELIEF VALVE. PIPELINE MAOP = 1,025 PSIG; HIGHEST PIPELINE PRESSURE DURING VENTING WAS 1,003 PSIG.
2021-02-26 10:37 | YES | YES | GT (Gas Transmission) | 20160054 | 31659 | 2016-06-30 19:05 | SUPPLEMENTAL FINAL | 31594 | SOUTHCROSS CCNG TRANSMISSION LTD | 2103 CITYWEST BLVD. SUITE 900 | HOUSTON | TX | 77042 | 2016-04-12 12:15 | 2016 |  |  | 28.1735 | -97.2832 | 1145117 | 2016-04-12 18:00 |  | NATURAL GAS |  | 738 | 0 | 0 | YES | 1 | 1 | 0 | 0 | 0 | 2 | YES | 0 | 1 | 0 | 0 | 0 | 1 |  | NO | INCIDENT OCCURED ON A LATERAL TAP THAT CONTAINED AN ISOLATION VALVE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-04-12 12:20 | 2016-04-12 12:20 | ONSHORE | TX | 78393 | WOODSBORO | REFUGIO | MILEPOST | VALVE 16 1C | WOODSBORO PLANT | WOODSBORO PLANT RESIDUE GAS PIPELINE | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 40 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.375 | 52000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | TUBULAR PRODUCTS | EPOXY | [28 empty] | 2016 | 2011 | CARBON STEEL |  | OTHER | [8 empty] | PRESSURE RELEASE VIA CONTRACTORS HOT TAP MACHINE FAILURE. THE PIPING DID NOT FAIL. | CLASS 1 LOCATION | NO |  | 100 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 1845 | 1894.73045822102 | 0 | 0 | 0 | 0 | 0 | 0 | ONLY DAMAGE WAS TO 3RD PARTY HOT TAP EQUIPMENT. COST UNAVAILABLE - LITIGATION |  | 1845 | 1964.35309973046 | 1894.73045822102 | [8 empty] | 850 |  | 975 | OTHER | HYDROTEST PRESSURE AND LIMITING MAOP PRESSURES OF DOWNSTREAM PIPE SEGMENTS |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 1 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ACTIONS OF THE CONTROL ROOM WERE REVIEWED. THE RELEASE WAS THE RESULT OF AN INTERNAL FAILURE WITHIN THE HOT TAP EQUIPMENT. THE PIPELINE SYSTEM WAS OPERATING WITHIN THE PARAMETERS OF THE HOT TAP EQUIPMENT. THE RELEASE WAS MANUALLY ISOLATED AT THE SOURCE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | HOT TAP EQUIPMENT | [15 empty] | YES | INTERNAL WORN COMPONENTS WITHIN HOT TAP EQUIPMENT | [161 empty] | CODY MEEK | INTEGRITY ENGINEERING SPECIALIST | cody.meek@southcrossenergy.com | 214-979-3740 |  |  |  |  | MICHAEL MAYO | DIRECTOR EHS | 713-935-8443 | michael.mayo@southcrossenergy.com | THE INCIDENT OCCURRED DURING THE COMPLETION OF THE 8 INCH HOT TAP AND INSERTION OF PIG GUIDE BARS. THE HOT TAP EQUIPMENT WAS BEING OPERATED BY A THIRD PARTY CONTRACTOR. DESCRIPTIONS OF THE EVENTS ARE AS FOLLOWS: HOT TAP FITTING WAS WELDED TO THE 16 INCH PRESSURIZED PIPELINE. THE 8 INCH HOT TAP VALVE AND HOT TAP MACHINE, CONTAINING THE CUTTER, WAS ATTACHED TO THE HOT TAP FITTING. THE CUTTING OF THE 16 INCH PIPELINE WAS COMPLETED, THE HOT TAP VALVE WAS CLOSED, AND THE RESIDUAL PRESSURE WAS BLED DOWN ON THE HOT TAP MACHINE. THE CUTTER HEAD AND CUT COUPON WERE REMOVED FROM THE HOT TAP MACHINE AND THE PIG GUIDE BARS FITTING WAS ATTACHED TO THE MACHINE. THE HOT TAP MACHINE CONTAINING THE PIG GUIDE BAR FITTING WAS ATTACHED TO THE HOT TAP VALVE AND THE VALVE WAS OPENED TO BEGIN INSERTION OF THE PIG GUIDE BAR FITTING. DURING THE PIG BAR FITTING INSERTION PROCESS, THE HOT TAP MACHINE SEPARATED, ALLOWING PIPELINE PRESSURE TO ESCAPE AND PROPELLED PARTS OF THE HOT TAP MACHINE TOWARDS ONSITE PERSONNEL. THE 8 INCH HOT TAP VALVE WAS IMMEDIATELY CLOSED BY ONSITE PERSONNEL FOLLOWING THE INCIDENT. BASED UPON MECHANICAL AND STRESS ANALYSIS THE FAILURE WAS THE RESULT OF THE INTERNAL BORING BAR NUT WITHIN THE HOT TAP EQUIPMENT. ALTHOUGH NOT DIRECTLY RELATED TO THE FAILURE, SOUTHCROSS HAS INITIATED HOT TAP PRACTICES WHICH INCLUDE AN EVALUATION OF THE CIRCUMSTANCES AND PRACTICES ASSOCIATED WITH HOT TAPS. THESE PRACTICES INCLUDE A REVIEW OF THE INTEGRITY PROCESSES OF CONTRACTORS PERFORMING HOT TAPS. A FAILURE ANALYSIS IS ATTACHED. DRUG TEST WERE NOT CONDUCTED BECAUSE THE SOUTHCROSS EMPLOYEE RECEIVED A FATAL INJURY. CONTRACTOR TESTING WAS NOT CONDUCTED DUE TO A FATAL INJURY. BECAUSE OF ONGOING LITIGATION ACCESS TO OTHER CONTRACT EMPLOYEES WAS LIMITED
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160055 | 17275 | 2016-07-05 16:26 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2016-06-09 13:15 | 2016 |  |  | 31.7559 | -94.1411 | 1150139 | 2016-06-09 13:20 |  | NATURAL GAS |  | 714 | 338 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-06-09 22:49 | 2016-06-11 07:25 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-06-09 13:00 | 2016-06-09 14:00 | ONSHORE | TX | 75935 | CENTER | SHELBY | MILEPOST | 2186+59 | INDEX 63 | LATEX TO MAGASCO CS MAIN LINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 1 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.25 | 30000 | UNKNOWN | LAP WELDED |  | UNKNOWN | ASPHALT | [28 empty] | 1924 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 192 |  | NO | NO | NO |  | 0 | 0 | 675 | 730.95294228593 | 1426 | 1464.43665768194 | 154951 | 167795.391644662 | 0 | 0 | 0 | 0 |  |  | 157052 | 78876.2870203077 | 169990.78124463 | [8 empty] | 160 |  | 302 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 41942 | NO | [5 empty] | YES | DRESSER COUPLINGS, ACETYLENE WELDED PIPE, NO PIG TRAPS INSTALLED | YES |  | YES | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS CALLED IN TO GAS CONTROL BY THIRD PARTY AND THEN CONFIRMED BY LOCAL AREA PERSONNEL. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  |  | YES | [7 empty] | YES |  |  |  | NO | [11 empty] | YES | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | SHANNON MATTINGLY | PA OQ AND EVENT SUPPORT PROGRAM LEADER | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 2706886361 | jeff.mcmaine@bwpmlp.com | GULF SOUTH EXPERIENCED A LEAK ON ITS INDEX 63 PIPELINE NEAR CENTER, TX. GULF SOUTH REMOVED CUSTOMERS FROM THE LINE AND BOTTLE FED CENTER TBS SO THE LINE COULD BE REMOVED FROM SERVICE AND REPAIRED. OPERATIONS HAVE BEEN RESTORED. FINAL REPORT TO BE SUBMITTED AFTER ALL INVOICES ARE RECEIVED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160056 | 17525 | 2016-07-05 20:01 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2016-06-05 05:16 | 2016 |  |  | 37.4354 | -121.1343 | 1149746 | 2016-06-05 07:12 |  | NATURAL GAS |  | 129000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-06-05 09:54 | 2016-11-05 18:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-06-05 05:16 | 2016-06-05 06:08 | ONSHORE | CA | 95363 | PATTERSON | STANISLAUS | MILEPOST | MP 1.79 | L-215 | 103 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 42 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 |  | 0.219 | 52000 | API 5LX-X52 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | US STEEL | COLD APPLIED TAPE | [28 empty] | 1972 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 120 | 12 |  | CLASS 1 LOCATION | NO |  | 278 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 340000 | 349164.420485175 | 773015 | 837092.723972086 | 3226 | 3493.41361750283 | 0 | 0 |  |  | 1116241 | 747845.826723832 | 1189750.55807476 | [8 empty] | 857 |  | 890 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 24352 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL ROOM OPERATED AS INTENDED | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED | YES | YES | YES | FRACTOGRAPHIC | [13 empty] | STRESS CORROSION CRACKING | [5 empty] | YES | [63 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | STEPHEN RAMOS | GAS ENGINEER | s3rc@pge.com | 9254137311 |  |  |  |  | SUSIE RICHMOND | MANAGER REGULATORY COMPLIANCE | 9253285776 | gsr8@pge.com | ON JUNE 5, 2016 AT 0516 HOURS, PG&E WAS NOTIFIED OF A TRANSMISSION LINE LEAK ON L-215 AT APPROXIMATELY MILE POINT (MP) 1.79. THE NEAREST ADDRESS IS 1607 WEST MARSHALL RD, PATTERSON. PG&E'S GAS SERVICE REPRESENTATIVE (GSR) ARRIVED ON-SITE AT 0608 HOURS AND REPORTED GAS BLOWING FROM THE 12 INCH TRANSMISSION LINE. THE DIRECT CAUSE OF THE FAILURE IS STRESS CORROSION CRACKING. THE OPERATIONS EMERGENCY CENTER (OEC) WAS ACTIVATED AND PG&E CREWS ISOLATED THE LINE BY 0954 HOURS BY CLOSING MANUAL VALVES. TWENTY SIX CUSTOMERS WERE IMPACTED AS A RESULT OF THIS INCIDENT. PG&E DEPLOYED MOBILE NATURAL GAS SERVICE TO SUPPORT THE IMPACTED CUSTOMERS DURING THE REPAIRS. SERVICE WAS RESTORED TO THE CUSTOMERS BY 6/7/16 AT 0940 HOURS. THE PIPE WAS RE-INSTALLED AND THE SITE WAS RESTORED BY 6/14/16. THE VOLUME OF NATURAL GAS UNINTENTIONALLY RELEASED IS APPROXIMATELY 129 MMCF. THERE WERE NO INJURIES, FATALITIES, OR IGNITION ASSOCIATED WITH THIS INCIDENT. THIS INCIDENT WAS REPORTED TO THE DOT AND CPUC DUE TO THE UNINTENTIONAL RELEASE OF GAS, REPAIR COSTS EXCEEDING $50K AND RELEASE OF GAS ESTIMATED WAS GREATER THAN 3 MILLION CUBIC FEET. PG&E TIED IN THE EASTERN SECTION OF L-215 AT MP 4.89 ON SEPTEMBER 26, 2016 AT APPROXIMATELY 2130 HOURS. THE WESTERN SECTION OF L-215, MP 0.278, WAS TIED BACK INTO THE SYSTEM ON NOVEMBER 5, 2016, AT APPROXIMATELY 1800 HOURS. THE LINE WAS RE-PRESSURIZED AT A REDUCED PRESSURE 600 PSIG UNTIL STRENGTH TESTING CAN BE COMPLETED. TO MITIGATE THE THREAT OF SCC, A HYDROSTATIC RETEST PROGRAM WAS IMPLEMENTED ON LINE 215 AND COMPLETED IN MAY 2017. EACH SECTION OF HTE LINE WITH THE IDENTIFIED THREAT WAS SPIKE TESTED TO NO LESS THAN 100% OF THE SPECIFIED MINIMUM YIELD STRENGTH (SMYS). ALL HYDROSTATIC TESTS WERE SUCESSFUL WITH NO FAILURES OF ANY KIND. FURTHER, PG&E HIRED A THIRD PARTY, KIEFNER AND ASSOCAITES, WHO CONDUCTED A FITNESS FOR SERVICE (FFS) ASSESSMENT OF LINE 215, AND THE FINDINGS REFLECT THAT "THE 2016 HYDROSTATIC PRESSURE SPIKE TEST CONFIRMED THE FITNESS FOR SERVICE OF LINE 215 FOR ITS MAOP OF 890 AT THE TIME OF THE TEST AND CONTINUES TO BE A VALID STRENGTH TEST AT PRESENT TIME." BASED ON THE COMPLETION OF ASSESSMENT ACTIVITIES, PG&E IS PLANNING TO RESTORE PRESSURE DURING THE WEEK OF DECEMBER 18, 2017.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160057 | 17136 | 2016-07-06 16:05 | ORIGINAL FINAL | 31451 | KINDER MORGAN TEXAS PIPELINE CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2016-06-19 22:35 | 2016 |  |  | 26.5982 | -99.086 | 1151086 | 2016-06-19 23:50 |  | NATURAL GAS |  | 6107 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | VALVES CLOSED TO ISOLATE VENTING GAS ALLOWING STATION TO REMAIN IN SERVICE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-06-19 22:35 | 2016-06-19 22:50 | ONSHORE | TX | 78545 | Not Within a Municipality | STARR | SURVEY STATION NO. | 123+33 | BOB WEST COMPRESSOR STATION | 582 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2014 |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENTIONAL REPORTABLE VOLUME OF GAS RELEASED THROUGH A BLOWDOWN/VENT LINE. | CLASS 1 LOCATION | NO |  | 687 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 12214 | 12543.218328841 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 12214 | 13004.1239892183 | 12543.218328841 | [8 empty] | 795 |  | 1100 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER(S) WERE NOT INVOLVED IN ANY ACTION THAT CAUSED THE VENT VALVE TO OPEN. IT WAS TOTALLY INADVERTENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  | YES | [7 empty] | YES | VENT VALVE | [22 empty] | YES | COMMUNICATION FAILURE BETWEEN CONTROLLING SOFTWARE AND VENT VALVE | [161 empty] | KENNETH PETERS | SR. ENGINEER | ken_peters@kindermorgan.com | 2053257554 | 2053253508 |  |  |  | REJI GEORGE | DIRECTOR CODES AND STANDARDS | 7134205433 | reji_george@kindermorgan.com | ON JUNE 19, 2016, UNIT #8 GUARDIAN PANEL LOST COMMUNICATION AT BOB WEST COMPRESSOR STATION AND CAUSED A VENT VALVE TO OPEN. NATURAL GAS WAS RELEASE TO THE ATMOSPHERE THROUGH THE VENT STACK OF A SUFFICIENT QUANTITY TO REQUIRE NOTIFICATION TO THE NRC. THE VENT VALVE WAS ISOLATED FROM SUCTION/DISCHARGE HEADER SO THAT THE REMAINDER OF THE COMPRESSOR STATION COULD REMAIN IN SERVICE. THERE WERE NO INJURIES, FATALITIES, OR PROPERTY DAMAGES.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160058 | 32185 | 2016-07-07 09:19 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2016-06-09 12:30 | 2016 |  |  | 28.532 | -93.1734 | 1150159 | 2016-06-09 14:49 |  | NATURAL GAS |  | 1676 | 5866 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-06-24 14:10 | 2016-07-05 14:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-06-24 12:30 | 2016-06-24 12:53 | OFFSHORE | [28 empty] | 145 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST CAMERON | 480 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 |  | 0.438 | 42000 | API 5L | DSAW |  | US STEEL | OTHER | SEMASTIC WITH CONCRETE | [27 empty] | 1976 | 1976 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 419 |  | NO | NO | NO |  | 0 | 0 | 17598 | 19056.7553753301 | 5028 | 5163.525606469 | 916400 | 992363.372312335 | 0 | 0 | 0 | 0 |  |  | 939026 | 469621.788237872 | 1016583.65329413 | [8 empty] | 681 |  | 1440 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 62917 | YES | [7 empty] | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | NOTIFICATION BY BSSE HELICOPTER THAT OBSERVED BUBBLES |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS TOO SMALL TO BE IDENTIFIED BY THE CONTROLL ROOM PERSONNEL. A REVIEW OF OPERATING RECORDS FOUND ABNORMAL OPERATING CONDITIONS DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | deteschendorf@spectraenergy.com | 713-627-5573 |  |  |  |  | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 713-627-5008 | nyatanu@spectraenegry.com | BUBBLES ON THE SURFACE OF THE WATER IN THE GULF OF MEXICO AT WEST CAMERON BLOCK 480 WERE OBSERVED BY A BSSE EMPLOYEE FLYING IN A HELICOPTER ON JUNE 9, 2016 AT 12:30 PM. TEXAS EASTERN PERSONNEL CONFIRMED THE DISCOVERY WAS ASSOCIATED WITH A TEXAS EASTERN PIPELINE ON JUNE 9, 2016 AT 12:53 PM. THE PIPELINE SEGMENT WAS SHUT IN. A DIVE BOAT WAS DISPATCHED TO THE LOCATION WHERE THE BUBBLES WERE OBSERVED. DIVERS CONFIRMED THE LEAK WAS COMING FROM A PIN HOLE LEAK DUE TO INTERNAL CORROSION IN TEXAS EASTERN 16-INCH LINE 41-A-8. A LEAK CLAMP WAS INSTALLED AND THE PIPELINE WAS RETURNED TO SERVICE JULY 5, 2016.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160059 | 17160 | 2016-07-07 15:00 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2016-06-10 20:39 | 2016 |  |  | 39.8989 | -95.5932 | 1150315 | 2016-06-11 10:29 |  | NATURAL GAS |  | 1005 | 207 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-06-14 07:30 | 2016-06-16 14:36 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-06-10 20:39 | 2016-06-10 22:31 | ONSHORE | KS | 66534 | Not Within a Municipality | BROWN COUNTY | SURVEY STATION NO. | 100/187+07 | LINE ER | SABETHA TAP | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | IN OR SPANNING AN OPEN DITCH |  |  |  | YES | [6 empty] | YES | UNCASED | WALNUT CREEK | 6 | BELOW WATER, PIPE ON OR ABOVE BOTTOM | [11 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 |  | 0.188 | 35000 | API 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | INTERLAKE STEEL | COAL TAR | [28 empty] | 1969 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 1 | 0.1 | [7 empty] | CLASS 1 LOCATION | NO |  | 102 |  | NO | NO | NO |  | 10000 | 10828.9324783101 | 447 | 484.05328178046 | 2171 | 2229.51752021563 | 195000 | 211164.183327046 | 10000 | 10828.9324783101 | 0 | 0 |  |  | 217618 | 109405.09887613 | 235535.619085663 | [8 empty] | 350 |  | 500 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 26300 | NO | [5 empty] | YES | NO LAUNCHER OR RECEIVER. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [52 empty] | HEAVY RAINS/FLOODS |  | OTHER |  |  | HEAVY RAINS CAUSED EXTREMELY HIGH WATER AND NUMEROUS TREES AND BRANCHES TO BE WASHED DOWN THE CREEK. THE DEBRIS GOT CAUGHT ON THE PIPELINE AND CAUSED A BEND IN THE PIPE TO KINK AND THEN CRACK. | YES |  |  |  | YES | FLOODING DUE TO HEAVY RAINFALL | [301 empty] | DAVID COOMES | PIPELINE COMPLIANCE ENGINEER | david.coomes@sscgp.com | 270.852.4391 |  |  |  |  | DAVID L. SINCLAIR | PIPELINE COMPLIANCE MANAGER | 270.852.4424 | david.l.sinclair@sscgp.com | ON JUNE 10 AT 8:39 PM SOUTHERN STAR RECEIVED A CALL FROM PUBLIC STATING THERE WAS A PLASTIC (DETERMINED TO BE STEEL) LINE IN WALNUT CREEK THAT WAS BUBBLING AND PROBABLY CAUSED BY DEBRIS IN THE CREEK. AT 8:30 PM SSC OPERATIONS WERE NOTIFIED TO REPORT TO THE LOCATION OF THE POSSIBLE LEAK. AFTER OPERATIONS NOTIFICATION SSC GAS CONTROL ATTEMPTED TO CONTACT THE LOCAL EMERGENCY RESPONSE (PSAP) BETWEEN THE TIMES OF 8:40-9:49. CONTACT WITH PSAP WAS MADE AT 9:49 PM. SSC OPERATIONS ARRIVED ON SCENE AT 10:31 PM AND AT 11:15 THE LINE WAS DETERMINED TO BE SOUTHERN STAR'S. IT WAS DECIDED TO HAVE OPERATIONS PERSONNEL STAY ON SITE TO MONITOR THE SCENE AND WAIT UNTIL MORNING TO INVESTIGATE FURTHER BECAUSE OF WATER OVER THE PIPELINE AND WET, DARK CONDITIONS. BY 9:15 AM ON JUNE 11 THE LEAK HAD BEEN INVESTIGATED AND DETERMINED THERE WAS A KINK IN THE LINE AND A CRACK APPROXIMATELY 1" LONG. THE KINK IN THE LINE WOULD NOT ALLOW A LEAK CLAMP TO BE INSTALLED. THE WORK SCHEDULED WAS TO FEED THE TOWN BORDERS WEST OF HAMLIN MLG WITH TANK TRUCKS AND ISOLATE THE SEGMENT FROM THE TAP TO THE HAMLIN MLG TO LOWER THE PRESSURE AND REMOVED THE DEBRIS FROM THE PIPELINE AND MAKE A REPLACEMENT OF THE LEAK SECTION OF PIPE. THE LINE WAS ISOLATED AT 7:30 AM ON JUNE 14. UNTIL THAT TIME THE SEGMENT WAS MONITORED 24/7 BY OPERATIONS PERSONNEL TO MAKE SURE THE LEAK DID NOT GET WORSE. THE REPLACEMENT SECTION WAS COMPLETE AND THE LINE WAS BACK IN SERVICE ON JUNE 16 AT 12:36 PM.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160060 | 34720 | 2016-07-26 16:50 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2016-07-01 09:28 | 2016 | CENTRAL | NO | 42.3443 | -96.4802 | 1152204 | 2016-07-01 12:32 |  | NATURAL GAS |  | 9737 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2016-07-01 09:28 | 2016-07-01 10:28 |  | NO |  |  | NO | [11 empty] | 0 | 2016-07-01 09:28 | 2016-07-01 09:28 | ONSHORE | NE | 68030 | Not Within a Municipality | DAKOTA | MILEPOST | 53.6 | HOMER COMPRESSOR STATION | NE-047 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2014 | 2014 | CARBON STEEL |  | OTHER | [8 empty] | UNINTENTIONAL OPENING OF BLOW DOWN VALVE BY EMPLOYEE. | CLASS 1 LOCATION | NO |  | 436 |  | NO | NO |  |  | 0 | 0 | 0 | 0 | 31645 | 32497.9649595687 | 0 | 0 | 1000 | 1082.89324783101 | 0 | 0 |  | 3.25 | 32645 | 34189.1924778424 | 33580.8582073997 | 0 | 0 | 0 | 0 | NO |  |  |  | 721 | 100 | 1000 | 192.619(A)(2) |  | 2014-11-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 1 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | A ERROR IN THE COMPUTER PROGRAM THAT CONTROLS THE GAS DETECTION SYSTEM. |  |  | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | DAVID CULLISON | SR. PIPELINE SAFETY ENGINEER | j.cullison@nngco.com | 402-398-7439 | 402-548-5267 |  |  |  | THOMAS CORRELL | VICE PRESIDENT OF PIPELINE SAFETY AND RISK | 402-398-7615 | thomas.correll@nngco.com | ON JULY 1, 2016, A NORTHERN EMPLOYEE INADVERTENTLY OPENED A MAINLINE BLOW DOWN VALVE RELEASING 9.7 MMCF OF NATURAL GAS TO ATMOSPHERE. THE EMPLOYEE WAS ASSIGNED TO CALIBRATE THE FIRE AND GAS DETECTION SYSTEMS ON THE TWO TURBINE UNITS IN BUILDING 1 SO THE BUILDING HAD BEEN PLACED IN BYPASS MODE. BYPASS MODE PREVENTS THE EMERGENCY SYSTEM FROM PERFORMING A BUILDING SHUTDOWN OR AN EMERGENCY SHUTDOWN WHILE THE TECHNICIANS WORK ON THE GAS DETECTION SYSTEMS. WHILE THE EMPLOYEE WAS TESTING THE FIRE AND GAS DETECTION SYSTEM ON UNIT 2, THE DISPLAY SHOWED ALARMS FOR GAS DETECTION ON UNIT 1 WHICH WAS UNEXPECTED. SHORTLY AFTER SEEING THE VISUAL ALARM, THE EMPLOYEE HEARD THE VENTING OF GAS OCCURRING OUTSIDE THE BUILDING, WHICH WAS NOT EXPECTED, AND ASSUMED AN EMERGENCY SHUTDOWN HAS COMMENCED. THIS INITIAL VENTING WAS CAUSED BY AN ERROR IN THE BYPASS MODES CODE, WHICH FAILED TO PREVENT THE VENTING OF GAS WHEN THE GAS DETECTION HEAD ON THE UNITS DETECTED GAS. IN RESPONSE TO HEARING THE VENTING OF GAS, THE EMPLOYEE LOOKED ON ANOTHER VISUAL DISPLAY WITHIN THE BUILDING TO CONFIRM THE ALARMS SIGNALED AN EMERGENCY SHUTDOWN, THEN PROCEEDED OUTSIDE TO ATTEMPT TO MANUALLY CLOSE THE CLOSEST OF THE THREE SHUTDOWN VALVES. THE VALVE, HOWEVER, WAS CLOSED AND THE EMPLOYEES ACTIONS OPENED THE VALVE CAUSING ADDITIONAL GAS TO VENT. 12/3/20 UPDATE - CORRECTED PART G APPARENT CAUSE TO ERROR IN THE PROGRAM VERSUS VALVE POSITION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160061 | 30728 | 2016-07-28 08:38 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2016-07-15 10:35 | 2016 |  |  | 28.532 | -93.1734 | 1153456 | 2016-07-15 11:40 |  | NATURAL GAS |  | 200 | 3100 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-07-15 17:15 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-07-15 10:35 | 2016-07-15 10:35 | OFFSHORE | [28 empty] | 145 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST CAMERON | 480 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 |  | 0.438 | 42000 | API 5L | DSAW |  | US STEEL | OTHER | SEMASTIC WITH CONCRETE | [27 empty] | 1976 | 1976 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 419 |  | NO | NO | NO |  | 0 | 0 | 9300 | 10070.9072048284 | 600 | 616.172506738545 | 500000 | 541446.623915503 | 0 | 0 | 0 | 0 |  |  | 509900 | 253799.913601235 | 552133.70362707 | [8 empty] | 680 |  | 1440 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 62917 | YES | [7 empty] | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS TOO SMALL TO BE IDENTIFIED BY THE CONTROL ROOM PERSONNEL. A REVIEW OF OPERATING RECORDS FOUND ABNORMAL OPERATING CONDITIONS DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES | [5 empty] | YES | RECENT HISTORY OF THE PIPELINE | YES | [5 empty] | NO | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | deteschendorf@spectraenergy.com | 713-627-5573 |  |  |  |  | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 713-627-5008 | nyatanu@spectraenergy.com | BUBBLES ON THE SURFACE OF THE WATER IN THE GULF OF MEXICO AT WEST CAMERON BLOCK 480 WERE OBSERVED BY A SPECTRA ENERGY EMPLOYEE FLYING IN A HELICOPTER ON JULY 15, 2016. A LEAK IN 16" LINE 41-A-8 WAS CONFIRMED AND THE PIPELINE WAS SHUT IN. SPECTRA ENERGY DOES NOT PLAN TO RETURN THE LINE TO SERVICE AND IS ABANDONING THE PIPELINE IN 2018. SPECTRA ENERGY DOES NOT PLAN TO HAVE DIVERS CONFIRM THE CAUSE OF THE INCIDENT. BASED ON THE PIPELINE'S RECENT HISTORY, THERE IS GOOD REASON TO BELIEVE THE CAUSE OF THE LEAK IS A PINHOLE RESULTING FROM INTERNAL CORROSION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160062 | 17291 | 2016-07-29 16:37 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2016-06-30 13:22 | 2016 |  |  | 39.3775 | -85.9095 | 1152118 | 2016-06-30 15:23 |  | NATURAL GAS |  | 100 | 24000 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-06-30 15:10 | 2016-08-31 13:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-06-30 13:22 | 2016-06-30 14:20 | ONSHORE | IN | 46124 | Not Within a Municipality | SHELBY | MILEPOST | MP 733.45 | ANR MAINLINE LOOP 2 2-501 | 8256501 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 42 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 36 |  | 0.33 | 65000 | API 5LX | DSAW |  | ITALSIDER | COAL TAR | [9 empty] | PIPE GIRTH WELD | [18 empty] | 1973 | 1972 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 788 |  | NO | NO | NO |  | 2500 | 2707.23311957752 | 58000 | 62807.8083741984 | 290 | 297.816711590297 | 350000 | 379012.636740852 | 0 | 0 | 0 | 0 |  |  | 410790 | 204358.694094991 | 444825.494946219 | [8 empty] | 756 |  | 858 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 58344 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SMALL SIZE OF THE LEAK | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | YES | [6 empty] | YES | YES | WELD IMPERFECTIONS | [12 empty] | YES | YES | [5 empty] | YES | POROSITY | [55 empty] | YES | [6 empty] | YES | [50 empty] | COMBINATION TOOL | 2011 |  |  |  |  | NO |  |  | Yes, but the point of the Accident was not identified as a dig site |  | 2014 | [11 empty] | NO | [63 empty] | ROGER R. STREET | FIELD COMPLIANCE SPECIALIST | roger_street@transcanada.com | 615-465-5123 |  |  |  |  | ROGER STREET | FIELD COMPLIANCE SPECIALIST | 6154655123 | roger_street@transcanada.com | ON 30 JUNE 2016 AT 13:22 EASTERN TIME (ET), ANR PERSONNEL RECEIVED A CALL FROM A LEASEHOLDER FARMER CONCERNING AN AREA OF DEAD VEGETATION AND POSSIBLE GAS RELEASE NEAR THE PIPELINE RIGHT OF WAY. AN ANR TECHNICIAN WAS DISPATCHED TO THE REPORTED LOCATION TO INVESTIGATE. THE ANR TECHNICIAN ARRIVED AT THE LOCATION AT 14:20 ET. FOLLOWING THE ARRIVAL AND INVESTIGATION OF THE SITE, THE TECHNICIAN CONCLUDED THAT DEAD VEGETATION AND ELEVATED LEVELS OF METHANE, AS MEASURED BY A GAS DETECTOR, IN THE VICINITY OF THE PIPELINE WAS LIKELY DUE TO A GAS RELEASE. THE SUSPECTED GAS RELEASE PROMPTED A CALL TO THE NATIONAL RESPONSE CENTER (NRC) AND AN INCIDENT REPORT (NRC #1152118) WAS FILED AT 15:23 ET ON 30 JUNE 2016. THE SECTION OF PIPE WAS ISOLATED AND THE PRESSURE REDUCED TO ATMOSPHERIC PRESSURE. FOLLOWING EXCAVATION OF THE LOCATION, A GIRTHWELD FEATURE WAS DISCOVERED AND PRESUMED TO BE THE SOURCE OF THE GAS RELEASE. A 14 FOOT SECTION INCLUDING THE GIRTH WELD WAS CUT OUT AND REPLACED WITH NEW PIPE. THE PIPE SECTION CONTAINING THE GIRTH WELD WAS SUBMITTED TO A LABORATORY FOR ANALYSIS. THE PIPELINE WAS PLACED BACK INTO SERVICE ON 31 AUGUST 2016 AT 13:30 LOCAL TIME. LABORATORY ANALYSIS DETERMINED THAT LEAKING FLAW WAS A CONSEQUENCE OF AN INCOMPLETE FUSION ALONG THE ROOT PASS COUPLED WITH POROSITY IN FILL AND CAP FILL PASSES DURING INITIAL FABRICATION. THE INCOMPLETE FUSION AND POROSITY, IN COMBINATION, RESULTED IN AN AREA WHERE THE LOCAL TENSILE CAPACITY WAS LIMITED. DUE TO THE LIMITED BONDING BETWEEN THE WELD SURFACES, MINOR FLUCTUATIONS IN THE TEMPERATURE DURING OPERATIONS CREATED TENSILE STRESSES THAT CONTRIBUTED EXTENSION OF THE WELD IMPERFECTION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160063 | 17316 | 2016-08-09 16:03 | SUPPLEMENTAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2016-07-13 01:20 | 2016 |  |  | 32.6724 | -92.6296 | 1153153 | 2016-07-13 02:03 |  | NATURAL GAS |  | 23728 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-07-13 01:59 | 2016-08-03 09:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-07-13 01:15 | 2016-07-13 01:44 | ONSHORE | LA | 71235 | DUBACH | LINCOLN | MILEPOST | 36+2320 | GUTHRIE-LISBON 20" LINE | GUL 20" | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | EXPOSURE | 1 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.25 | 45000 | API 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | YOUNGSTOWN | COAL TAR | [28 empty] | 1947 | 1947 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 75 | 41 |  | CLASS 1 LOCATION | NO |  | 393 |  | NO | NO | NO |  | 7500 | 8121.69935873255 | 0 | 0 | 70602 | 72505.0188679245 | 404133 | 437632.896925688 | 1000 | 1082.89324783101 | 0 | 0 |  |  | 483235 | 280279.443604407 | 519342.508400176 | [8 empty] | 791 |  | 810 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 63280 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM PERSONNEL ACTED APPROPRIATELY. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | NO |  | NO | YES | YES |  |  |  | 2015 |  |  |  | YES | [190 empty] | YES | YES | [5 empty] | YES | 1987 |  | HARD SPOTS | [47 empty] | DUMMY PIG BEFORE MFL | 1987 |  |  |  |  | YES | 1993 | 1117 | NO | [13 empty] | NO | [63 empty] | SHANNON MATTINGLY | PA OQ AND EVENT SUPPORT PROGRAM LEADER | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 2706886361 | jeff.mcmaine@bwpmlp.com | TEXAS GAS EXPERIENCED A PIPELINE FAILURE ON ITS GUTHRIE-LISBON 20" PIPELINE IN LINCOLN PARISH, LA. THERE WERE NO INJURIES OR FIRE. THE CAUSE APPEARS TO BE EXTERNAL CORROSION. TEXAS GAS HAS REPLACED THE SECTION OF PIPE AND RETURNED THE FACILITY TO SERVICE. TEXAS GAS WILL OPERATE THE PIPELINE AT 80% OF FAILURE PRESSURE UNTIL AN ILI HAS BEEN PERFORMED AND ANY ANOMALIES HAVE BEEN ADDRESSED. 4-4-17 UPDATED WITH FINAL COST FOR THE PIPELINE RUPTURE. THIS IS THE FINAL REPORT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160064 | 17460 | 2016-08-16 11:33 | SUPPLEMENTAL FINAL | 4900 | KINDER MORGAN TEJAS PIPELINE | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2016-07-18 09:20 | 2016 |  |  | 27.4677 | -98.0502 | 1153701 | 2016-07-18 10:41 |  | NATURAL GAS |  | 142450 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-07-18 09:20 | 2016-07-31 10:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2016-07-18 09:20 | 2016-07-18 09:32 | ONSHORE | TX | 78375 | Not Within a Municipality | KLEBERG | MILEPOST | MP 0 - 0+00 | 520-100 | 520-100, MP 0, STATION 0+00 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | ABOVE GROUND PIPING, APPURTENANCES, ETC | 1964 |  | CARBON STEEL |  | OTHER | [8 empty] | INCIDENT IN FACILITIES OF ADJACENT 3RD PARTY (HEAT FROM FIRE) SPREAD TO KM TEJAS FACILITIES. | CLASS 1 LOCATION | NO |  | 752 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 380000 | 390242.587601078 | 13461000 | 14576826.0090532 | 1000 | 1082.89324783101 | 0 | 0 |  |  | 13842000 | 7096227.06124221 | 14968151.4899021 | [8 empty] | 808 |  | 915 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 15 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT IN FACILITIES OF ADJACENT 3RD PARTY (HEAT FROM FIRE) SPREAD TO KM TEJAS FACILITIES. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [103 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [261 empty] | WILLIAM MARTIN MULLER | SPECIALIST - PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205 325 3863 | 205 325 3508 |  |  |  | REJI GEORGE | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713 420 5433 | reji_george@kindermorgan.com | 07/18/2016; 09:20 HOURS; KM TEJAS MANAGER REPORTED FIRE OBSERVED IN THE DISTANCE, APPROXIMATELY IN THE VICINITY OF THE KM TEJAS KING RANCH FACILITIES. SAID SITE IS A JUNCTION FOR KM TEJAS FACILITIES AND FACILITIES OF AN ADJACENT THIRD PARTY. KM TEJAS EMERGENCY RESPONSE BEGAN AT 09:26 HOURS INCLUDING DIRECTING EMPLOYEES TO CLOSE MAIN LINE BLOCK VALVES AND ISOLATING ALL INLETS AND OUTLETS. THE KM TEJAS INVOLVEMENT INCLUDED MULTIPLE PIPELINES; THE LARGEST DIAMETER KM TEJAS PIPELINE IS THE 36-INCH TEJAS 520-100 LINE (MUSTANG MAIN LINE 01; SAID PIPE DATA FOR THIS REPORT). INCIDENT BEGAN WITHIN THE FACILITIES OF AN ADJACENT THIRD PARTY; HEAT FROM FIRE SPREAD TO KM TEJAS FACILITIES. THE GAS LOST AND OTHER APPLICABLE DATA WITHIN THIS REPORT IS CUMULATIVE FOR ALL KM TEJAS INVOLVED FACILITIES. THE THIRD PARTY FACILITY PERSONNEL WERE EVACUATED; THERE WERE NO GENERAL PUBLIC EVACUATIONS. THE KM TEJAS FACILITY IS NOT MANNED; THERE WERE NO PERSONNEL EVACUATION. IT WAS SEVERAL HOURS BEFORE THE INCIDENT SITE WAS DEEMED SAFE FOR KM TEJAS EMPLOYEES TO ENTER AND BEGIN AN INVESTIGATION. INVOLVED KM TEJAS FACILITIES WERE RESTORED TO RESUME NATURAL GAS FLOW (SOUTH FLOW) ON 07/31/2016. ADDITIONAL RECONSTRUCTION OF DAMAGED KM TEJAS FACILITIES CONTINUED INTO THE WEEK OF 08/28/2017 WITH THE INSTALLATION OF VALVE OPERATORS TO COMPLETE THE PROJECT WITH NATURAL GAS FLOW AS NEEDED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160065 | 17164 | 2016-08-16 19:42 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2016-07-16 06:59 | 2016 |  |  | 38.3186 | -121.7964 | 1153551 | 2016-07-16 08:35 |  | NATURAL GAS |  | 12398 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-07-16 08:22 | 2016-07-18 21:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-07-16 06:59 | 2016-07-16 07:31 | ONSHORE | CA | 95620 | DIXON | SOLANO | MILEPOST | MP 5.15 | L-220 | 107 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10.75 |  | 0.259 |  | UNKNOWN | SEAMLESS |  | UNKNOWN | ASPHALT | [28 empty] | 1937 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 10 | 24 |  | CLASS 1 LOCATION | NO |  | 209 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 33000 | 33889.4878706199 | 188587 | 204219.588928706 | 0 | 0 | 0 | 0 |  |  | 221587 | 128876.950915893 | 238109.076799326 | [8 empty] | 650 |  | 796 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 25000 | NO | YES |  | YES |  |  | YES | WRINKLE BENDS, BELL AND SPIGOT JOINTS, PLUG VALVES | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY DIG-IN INCIDENT | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | YES |  |  | YES | PRIVATE LANDOWNER | YES | [6 empty] | FARMER | FARM EQUIPMENT | AGRICULTURE | YES | 616600507 | N/A | UTILITY OWNER | YES | YES | NO |  | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO MAINTAIN THE MARKS | [263 empty] | STEPHEN RAMOS | COMPLIANCE ENGINEER | s3rc@pge.com | 9254137311 |  |  |  |  | SUSIE RICHMOND | MANAGER REGULATORY COMPLIANCE | 9253285776 | gsr8@pge.com | ON JULY 16, 2016 AT 0659 HOURS, PG&E WAS NOTIFIED OF A THIRD PARTY DIG IN AT 5555 ROBBEN ROAD IN DIXON. A THIRD PARTY EXCAVATOR, ATKINSON HAY COMPANY, STRUCK A 10' STEEL TRANSMISSION LINE (LINE 220 MILE POINT 5.15) WITH FARMING EQUIPMENT. THE EQUIPMENT OPERATOR WENT TO THE HOSPITAL AND WAS RELEASED WITH NO INJURIES. THERE WAS A VALID USA TICKET (#W616600507) AND PG&E FACILITIES WERE PROPERLY LOCATED AND MARKED. IT WAS DETERMINED THAT THE USA TICKET BELONGED TO THE LAND OWNER, NOT FOR ATKINSON HAY COMPANY. IN ADDITION, THE EXCAVATOR FAILED TO MAINTAIN THE MARKS. PG&E'S GAS SERVICE REPRESENTATIVE (GSR) ARRIVED ON SITE AT 0731 HOURS. PG&E REPAIR CREWS ARRIVED ON-SITE AND STOPPED THE FLOW OF GAS AT 0822 HOURS BY CLOSING VALVES. THE SACRAMENTO OEC WAS ACTIVATED. REPAIRS TO THE PIPELINE WERE COMPLETED AND THE LINE WAS RESTORED ON 7/18/16 AT 2130 HOURS. FIRE DEPARTMENT AND POLICE DEPARTMENT WERE REPORTED ON SITE. THERE WAS NO CUSTOMER IMPACT. THERE WERE NO INJURIES, NO FATALITIES, AND NO IGNITION ASSOCIATED WITH THIS INCIDENT. THE VOLUME OF GAS UNINTENTIONALLY RELEASE WAS ESTIMATED TO BE GREATER THAN 3 MMCF. ESTIMATED DAMAGES TO THE PIPELINE WERE GREATER THAN $50,000. THIS INCIDENT WAS REPORTED TO THE DOT AND CPUC DUE TO THE UNINTENTIONAL RELEASE OF GAS, VOLUME OF GAS RELEASE ESTIMATED TO BE GREATER THAN 3 MMCF, AND DAMAGES TO THE PIPE GREATER THAN $50,000.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160066 | 17232 | 2016-08-17 20:48 | SUPPLEMENTAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2016-07-18 09:00 | 2016 |  |  | 27.468 | -98.0499 | 1153696 | 2016-07-18 09:50 |  | NATURAL GAS |  | 30000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-07-18 13:00 | 2016-08-16 11:00 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 0 | 2016-07-18 09:00 | 2016-07-18 09:00 | ONSHORE | TX | 78363 | KINGSVILLE | KLEBERG | SURVEY STATION NO. | 0+00 | KR04 | 30" RESIDUE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | SCRAPER/PIG TRAP | [38 empty] | 1958 |  | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 240 | 113 |  | CLASS 1 LOCATION | NO |  | 662 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 46500 | 47753.3692722372 | 2300000 | 2490654.47001132 | 6000 | 6497.35948698604 | 0 | 0 |  |  | 2352500 | 1195766.66792067 | 2544905.19877054 | [8 empty] | 850 |  | 915 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | MANUAL | 147100 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLERS' ACTIONS WERE CONSISTENT WITH EMERGENCY SHUTDOWN PROCEDURES FOR THIS TYPE OF AN INCIDENT.' | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | THE 30" RESIDUE LINE SUSTAINED COLLATERAL DAMAGE FROM AN ADJACENT NON-REGULATED GATHERING PIPELINE THAT EXPERIENCED A RELEASE AND FIRE. | [147 empty] | DANNY NICHOLS | DIRECTOR REGULATORY COMPLIANCE | danny.nichols@energytransfer.com | 7139897232 |  |  |  |  | DANNY NICHOLS | DIRECTOR REGULATORY COMPLIANCE | 7139897232 | danny.nichols@energytransfer.com | AT APPROXIMATELY 9:00 A.M. ON JULY 18TH, 2016, ETC OPERATIONS OBSERVED A FIRE EAST OF AND ADJACENT TO THE ETC KING RANCH GAS PLANT (KRGP). THE LOCATION OF THE FIRE WAS WITHIN A FENCED PIPELINE TERMINAL FACILITY CONTAINING INCOMING GATHERING PIPELINES, SCRUBBERS, MEASUREMENT EQUIPMENT AND DEPARTING RESIDUE PIPELINES (TERMINAL). THIS TERMINAL CONTAINS SEVERAL ETC AND THIRD PARTY PIPELINE ASSETS. AT APPROXIMATELY 9:02 AM, ETC OPERATIONS INITIATED AN ESD AT THE PLANT. THE PLANT PERSONNEL WERE EVACUATED TO THEIR ESTABLISHED MUSTER POINT. AT 9:15 A.M., THE CORPORATE EMERGENCY NOTIFICATION MATRIX WAS INITIATED. DURING THE CALL, ETC GAS CONTROL VERIFIED VIA THE SCADA SYSTEM THAT THEY WERE MONITORING PRESSURE LOSSES ON SEVERAL ASSETS AT THE TERMINAL. NOTIFICATIONS WERE MADE TO THIRD PARTY PIPELINE ASSET OWNERS, LOCAL, STATE, AND FEDERAL AGENCIES. OPERATIONS MANAGEMENT DISPATCHED PERSONNEL TO SHUT IN ALL PIPELINE INLET & OUTLETS TO THE PLANT AND ISOLATE THE TERMINAL AS WELL. OPERATIONS UTILIZED THE SCADA SYSTEM TO MONITOR AND VERIFY PIPELINE PRESSURES. ONCE THE REMOTE VALVES WERE CLOSED ON AFFECTED PIPELINES TO ISOLATE THE TERMINAL, OPERATIONS MONITORED THE LOCATION UNTIL THE FIRE SUBSIDED. ON THE MORNING OF JULY 19TH, OPERATIONS AND OTHER COMPANY REPRESENTATIVES ACCESSED THE TERMINAL TO INITIATE OUR PRELIMINARY INVESTIGATION THAT IS STILL ONGOING. ALTHOUGH THE INVESTIGATION IS ONGOING, IT APPEARS THAT THE FIRE ORIGINATED FROM AN ADJACENT GATHERING SYSTEM THAT EXPOSED THE REGULATED TRANSMISSION PIPELINE TO EXCESSIVE HEAT AND ULTIMATELY CAUSED IT TO FAIL. SUPPLEMENTAL/FINAL DATED 12/7/2016 REVISED LATITUDE IN PART A TO REFLECT CORRECT COORDINANCE: LATITUDE 27.46800000 LONG -98.04990000 TO REFLECT KLEBERG COUNTY TX.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160067 | 17168 | 2016-08-19 15:28 | ORIGINAL | 31088 | DESTIN PIPELINE COMPANY, LLC | THIRD COAST MIDSTREAM, LLC PO BOX 1227 | HOUSTON | TX | 77251 | 2016-07-20 09:11 | 2016 |  |  | 29.3428 | -88.067 | 1153911 | 2016-07-20 11:26 |  |  |  | 0 | 0 | 0.04 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-07-20 09:12 | 2016-07-25 14:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2016-07-20 09:11 | 2016-07-20 09:11 | OFFSHORE | [28 empty] | 300 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | MAIN PASS | 260 | PLATFORM | INTERSTATE | OFFSHORE PLATFORM, INCLUDING PLATFORM-MOUNTED EQUIPMENT AND PIPING | FILTER/STRAINER/SEPARATOR | [38 empty] | 1998 |  | CARBON STEEL |  | OTHER | [8 empty] | INCIDENT DID NOT INVOLVE AN UNINTENDED RELEASE OF GAS. A FAILED LEVEL SWITCH PERMITTED ACCUMULATED LIQUIDS IN A GAS SCRUBBER TO RISE TO THE POINT WERE LIQUIDS WERE EXPELLED FROM THE PLATFORM WITH FLARE GAS. THE EXPELLED LIQUIDS WERE IGNITED BY THE FLARE TIP. | CLASS 1 LOCATION | NO |  | 1039 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 2707.23311957752 | 0 | 0 | 0 | 0 |  |  | 2500 | 1242.69143719351 | 2707.23311957752 | [8 empty] | 28 |  | 150 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | WHILE THE FACILITY IS MONITORED BY A CONTROLLER VIA SCADA, THE LOCAL INSTRUMENTATION THAT WAS RELAYED TO THE CONTROLLER WAS NOT PREVIOUSLY CAPABLE OF ENABLING REMOTE DETECTION OF THE ISSUE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | YES | [29 empty] | YES | [166 empty] | MIKE SANDERS | DOT TEAM LEADER | michael.sanders@bp.com | 630-649-8016 |  |  |  |  | MIKE SANDERS | DOT TEAM LEADER | 630-649-8016 | michael.sanders@bp.com | A SMALL AMOUNT OF CONDENSATE WAS RELEASED THROUGH THE MP260 PLATFORM FLARE. AS THE CONDENSATE EXITED THE FLARE TOWER IT IGNITED ON THE TIP. THE EXPELLED CONDENSATE FELL TO THE SURFACE WATERS OF THE GULF OF MEXICO. THE CONDENSATE SELF-EXTINGUISHED WITHIN AN ESTIMATED 2-3 MINUTES. ESD OF THE PLATFORM WAS INITIATED AT FIRST DETECTION. NO FURTHER SHEEN OR DEBRIS WAS NOTED IN THE WATER AFTER THE FIRE BURNED OUT. NO GAS WAS UNINTENTIONALLY RELEASED. NO INJURIES RESULTED FROM THE LOSS OF CONTAINMENT AND ALL PERSONNEL WERE ACCOUNTED FOR. A MALFUNCTIONING LEVEL SWITCH IN A SCRUBBER IS BELIEVED TO HAVE PERMITTED THE COLLECTED LIQUID TO ACCUMULATE ABOVE THE DESIGN LEVEL, A PORTION OF WHICH BECAME EXPELLED WITH FLARE GAS.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160068 | 30327 | 2016-08-25 15:47 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2016-08-09 20:57 | 2016 |  |  | 32.3012 | -90.0921 | 1155783 | 2016-08-09 21:35 |  | NATURAL GAS |  | 15307 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-08-09 20:57 | 2016-08-09 21:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-08-09 20:57 | 2016-08-09 21:35 | ONSHORE | MS | 39232 | FLOWOOD | RANKIN | MILEPOST | 12566+40 | JACKSON COMPRESSOR STATION | INDEX 130 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1954 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVES OPENED | CLASS 1 LOCATION | NO |  | 87 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 41646 | 42768.5336927224 | 0 | 0 | 1160 | 1256.15616748397 | 0 | 0 |  |  | 42806 | 44916.6896893915 | 44024.6898602063 | [8 empty] | 787 |  | 1000 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | MAOP WAS NOT EXCEEDED | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | HIGH FLOW RATE FROM STORAGE FIELD | [161 empty] | SHANNON MATTINGLY | PA OQ AND EVENT SUPPORT PROGRAM LEADER | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | DARRAL WARD | MANAGER PIPELINE SAFETY | 2706886356 | darral.ward@bwpmlp.com | HIGH FLOW RATE FROM STORAGE FIELD WITHDRAW PACKED PIPELINE CAUSING PRESSURE INCREASE THAT TRIPPED TWO OPP VALVES. MAOP WAS NOT EXCEEDED. RELIEF VALVES WERE RESET TO STOP VENTING GAS. 5-16-18 REVISED BASED ON PHMSA INSTRUCTIONS INCLUDING CHANGING PART G - APPARENT CAUSE TO EQUIPMENT FAILURE AND ANSWERING SUBSEQUENT QUESTIONS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160069 | 17407 | 2016-08-29 12:24 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2016-08-01 14:30 | 2016 |  |  | 37.918 | -83.9828 | 1155035 | 2016-08-01 15:19 |  | NATURAL GAS |  | 48266 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-08-01 14:30 | 2016-08-03 13:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-08-01 14:30 | 2016-08-01 14:30 | ONSHORE | KY | 40312 | Not Within a Municipality | POWELL | MILEPOST | 17, 8+75 | TGP LINE 800-2 | LINE 800-2, MP 17, STATION 08+75 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1951 |  | CARBON STEEL |  | OTHER | [8 empty] | HEAVY THUNDER STORM PASSED OVER TGP STATION 106; LIGHTNING STRIKE CAUSED STATION ESD SYSTEM TO ACTIVATE; VALVE HELD OPEN; ON SITE EMPLOYEE CLOSED VALVE AND STOPPED GAS RELEASE EVENT; | CLASS 2 LOCATION | NO |  | 794 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 108600 | 111527.223719677 | 30000 | 32486.7974349302 | 150 | 162.433987174651 | 0 | 0 |  |  | 138750 | 130612.195659777 | 144176.455141781 | [8 empty] | 694 |  | 750 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | ESD SYSTEM OF STATION 106 ACTIVATION BY LIGHTNING STRIKE; EMPLOYEE ON SITE; |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ESD SYSTEM OF STATION 106 ACTIVATION BY LIGHTNING STRIKE; | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [52 empty] | LIGHTNING |  |  | DIRECT HIT |  |  | NO | [306 empty] | WILLIAM MARTIN MULLER | SPECIALIST - PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 2053253863 | 2053253508 |  |  |  | REJI GEORGE | DIRECTOR COMPLIANCE CODES AND STANDARDS | 7134205433 | reji_george@kindermorgan.com | A HEAVY THUNDER STORM PASSED OVER TGP COMPRESSOR STATION 106 WITH LIGHTNING STRIKE CAUSING STATION ESD SYSTEM TO ACTIVATE. YARD VALVE 106-1D (24-INCH VALVE AND 24" PIPE) DID NOT CLOSE PROPERLY; LIGHTNING CAUSED EXTENSIVE DAMAGE TO STATION HARDWARE; (INPUT / OUTPUT CARDS, CONTROLS, COMPONENTS); DAMAGE RESULTED IN SIGNAL LOST TO ESD SOLENOID ALLOWING REPORTABLE AMOUNT OF NATURAL GAS TO BE RELEASED TO ATMOSPHERE; ON SITE EMPLOYEE MANUALLY CLOSED VALVE TO STOP THE GAS RELEASE EVENT; OTHER REPLACEMENTS INCLUDED JACKET WATER PUMP MOTOR, LIGHTING, POWER SUPPLIES, AND FUSES. IT IS BELIEVED THE LIGHTNING STRIKE WAS A DIRECT HIT ON THE FACILITY. KINDER MORGAN ENVIRONMENTAL GROUP REPORTED AN OIL MIST SPRAY EVENT TO THE STATE OF KENTUCKY, KEEC, REPORT NUMBER 2414873; SAID SPRAY EVENT THE RESULT OF THE LIGHTNING STRIKE. THERE WAS NO IMPACT TO ANY WATER BODY. (LAT / LONG OF VALVE 106-1D IS 37.917951 AND -83.982775) (42-INCH YARD PIPE AND 750 PSIG MAOP EQUAL PIR OF 794-FEET)
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160070 | 17212 | 2016-09-07 18:07 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2016-08-04 08:09 | 2016 |  |  | 34.0681 | -113.6106 | 1155885 | 2016-08-10 15:39 |  | NATURAL GAS |  | 14807.5 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-08-04 08:09 | 2016-08-04 09:38 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-08-04 08:30 | 2016-08-04 09:20 | ONSHORE | AZ | 85357 | WENDEN | LA PAZ | MILEPOST | MP 37+5084.14 | ALAMO LAKE COMPRESSOR STATION | LINE 1104 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1993 |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENTIONAL GAS LOSS > 3000MCF FROM A SUCTION-VENT-VALVE THAT FAILED TO CLOSE | CLASS 1 LOCATION | NO |  | 589 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 43650 | 44826.5498652291 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 43650 | 46473.7196765499 | 44826.5498652291 | [8 empty] | 660 |  | 809 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL DID NOT CONTRIBUTE TO NOR HAVE THE CAPABILITY TO RESOLVE THE STATION MALFUNCTION | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | OTHER | SUCTION-VALVE FAILED TO CLOSE AND ISOLATE THE FACILITY FROM THE PIPELINE | [20 empty] | YES | AT LEAST 2 LOW-RESISTANCE TO GRND FAULTS ON THE STN'S 135VDC CONTROL SYSTEM | [161 empty] | KRISTIN VAN DER LAAN | SENIOR PIPELINE ENGINEER | kristin_vanderlaan@kindermorgan.com | 303-914-7753 |  |  |  |  | REJI GEORGE | DIRECTOR COMPLIANCE-CODES AND STANDARDS | 713-420-5433 | reji_george@kindermorgan.com | ON AUGUST 4, 2016 AT APPROXIMATELY 8:30AM LOCAL TIME (MT), EL PASO NATURAL GAS (EPNG) PHOENIX BASED EPNG OPERATIONS SUPERVISOR RECEIVED A TEXT MESSAGE FROM THE STATIONS CONTROL SYSTEM OF A UNIT-SHUTDOWN ALARM AT THE ALAMO LAKE STATION. HE CONTACTED A WENDEN, AZ BASED TECHNICIAN TO CHECK ON THE ALARM. THE TECHNICIAN WAS ALREADY EN ROUTE TO THE ALAMO LAKE STATION TO CONDUCT ROUTINE MAINTENANCES AND WAS INSTRUCTED TO EVALUATE THE SITUATION AND RESTART THE COMPRESSORS. HE ARRIVED AT APPROXIMATELY 9:20AM MT AND FOUND THE COMPRESSORS OFF-LINE WITH BOTH THE SUCTION AND DISCHARGE VENT VALVES OPEN. THE TECHNICIAN CLOSED THE VALVES AND PROCEEDED TO INVESTIGATE THE CAUSE OF THE STATION SHUTDOWN. AN INVESTIGATION OF THE CAUSE OF THE STATION SHUTDOWN FOUND THAT THERE WERE TWO EQUIPMENT ISSUES. THE STATION'S SUCTION-VENT-VALVE HAD A SHORTED CLOSE-SOLENOID AND THE MOMENTARY-CLOSE PUSH-BUTTON THAT OPENS THE STATION SUCTION VALVE WAS STUCK CLOSED. BOTH OF THESE COMPONENTS WERE REPAIRED AND THE COMPRESSOR UNITS AT THE STATION RETURNED TO SERVICE. THE QUANTITY OF GAS LOSS WAS NOT DETERMINED BY THE TECHNICIAN DURING THE AUGUST 4, 2016 EVENT. ON AUGUST 10, 2016, DURING THE EVALUATION OF GAS LOSS EVENTS IN THE AREA, EPNG PHOENIX AREA OPERATIONS MANAGEMENT BECAME AWARE THAT THE QUANTITY OF GAS RELEASED FOR THIS EVENT MET THE REPORTING CRITERIA FOR AN INCIDENT, UNINTENTIONAL GAS LOSS GREATER THAN 3000MCF, UNDER 49 CFR 191.5 AT WHICH TIME THE NRC WAS NOTIFIED IMMEDIATELY. IMMEDIATELY AFTER THE NRC REPORT WAS SUBMITTED, EPNG ALSO NOTIFIED THE PHMSA WESTERN REGION AND THE ARIZONA CORPORATION COMMISSION PIPELINE SAFETY DIVISION. FURTHER INVESTIGATION DETERMINED THAT THE CAUSE OF THE UNINTENTIONAL GAS RELEASE WAS AT LEAST TWO LOW-RESISTANCE TO GROUND FAULTS ON THE STATIONS 135 VDC CONTROL SYSTEM. BASED ON THIS FINDING, THE FIELD WIRING FOR BOTH THE STATION'S HIGH DISCHARGE PRESSURE SWITCH CIRCUIT AND THE STATION'S DISCHARGE LOADING VALVE CIRCUIT WILL BE REPLACED AS SOON AS POSSIBLE AND THE REMAINDER OF THE STATION'S DC SYSTEM WILL BE EVALUATED FOR ADDITIONAL LOW-RESISTANCE GROUND AND/OR DETERIORATION. UPDATE: COST TO HYDRO-VAC AND INSTALL A NEW CONDUIT LINE = $11,200. COST FOR THE INSTALLATION WILL BE REFLECTED ON PHMSA REPORT NO: 20160071 (THIS INCIDENT, 20160070, AND 20160071 OCCURRED ON THE SAME FACILITY).
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160071 | 17214 | 2016-09-07 18:07 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2016-08-03 22:15 | 2016 |  |  | 34.0681 | -113.6106 | 1155884 | 2016-08-10 15:33 |  | NATURAL GAS |  | 23540 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-08-03 22:15 | 2016-08-04 12:42 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-08-03 22:15 | 2016-08-04 00:05 | ONSHORE | AZ | 85357 | WENDEN | LA PAZ | MILEPOST | MP 37+5084.14 | ALAMO LAKE COMPRESSOR STATION | LINE 1104 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1993 |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENTIONAL GAS LOSS > 3000MCF FROM A SUCTION-VENT-VALVE THAT FAILED TO CLOSE | CLASS 1 LOCATION | NO |  | 589 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 69391 | 71261.3773584906 | 11200 | 12128.4043757073 | 0 | 0 | 0 | 0 |  |  | 80591 | 79447.1632990043 | 83389.7817341978 | [8 empty] | 645 |  | 809 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL DID NOT CONTRIBUTE TO NOR HAVE THE CAPABILITY TO RESOLVE THE STATION MALFUNCTION | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | OTHER | SUCTION-VALVE FAILED TO CLOSE AND ISOLATE THE FACILITY FROM THE PIPELINE | [20 empty] | YES | AT LEAST 2 LOW-RESISTANCE TO GRND FAULTS ON THE STN'S 135VDC CONTROL SYSTEM | [161 empty] | KRISTIN VAN DER LAAN | SENIOR PIPELINE ENGINEER | kristin_vanderlaan@kindermorgan.com | 303-914-7753 |  |  |  |  | REJI GEORGE | DIRECTOR COMPLIANCE-CODES AND STANDARDS | 713-420-5433 | reji_george@kindermorgan.com | ON AUGUST 3, 2016 AT APPROXIMATELY 10:15 P.M. LOCAL TIME (MT), EL PASO NATURAL GAS (EPNG) GAS-CONTROL NOTIFIED A PHOENIX BASED EPNG TECHNICIAN THAT THERE WAS A COMPRESSOR UNIT SHUTDOWN AT THE ALAMO LAKE STATION. AFTER CONFIRMING THE SHUTDOWN REMOTELY, THE TECHNICIAN DROVE TO THE SITE AND FOUND THAT THE COMPRESSOR UNITS WERE NOT RUNNING, THE STATION SUCTION VALVE WAS OPEN AND THE SUCTION-VENT-VALVE WAS OPEN AND VENTING GAS. THE STATION DISCHARGE AND VENT VALVES WERE CLOSED. THE TECHNICIAN CLOSED THE STATION SUCTION VALVES, STOPPING THE VENTING OF GAS, AND PROCEEDED TO CHECK THE STATUS OF THE COMPRESSOR STATION. AFTER REVIEWING THE STATUS, THE COMPRESSORS WERE RESTARTED AND THE TECHNICIAN REMAINED AT THE STATION FOR A COUPLE MORE HOURS TO MONITOR THE STATION. THE QUANTITY OF GAS LOSS WAS NOT DETERMINED BY THE TECHNICIAN DURING THE AUGUST 3, 2016 EVENT. ON AUGUST 4, 2016 AN INVESTIGATION OF THE CAUSE OF THE STATION SHUTDOWN FOUND THAT THERE WERE TWO EQUIPMENT ISSUES. THE STATION'S SUCTION-VENT-VALVE HAD A SHORTED CLOSE-SOLENOID AND THE MOMENTARY-CLOSE PUSH-BUTTON THAT OPENS THE STATION SUCTION VALVE WAS STUCK CLOSED. BOTH OF THESE COMPONENTS WERE REPAIRED AND THE COMPRESSOR UNITS AT THE STATION RETURNED TO SERVICE. ON AUGUST 10, 2016, DURING THE EVALUATION OF GAS LOSS EVENTS IN THE AREA, EPNG PHOENIX AREA OPERATIONS MANAGEMENT BECAME AWARE THAT THE QUANTITY OF GAS RELEASED FOR THIS EVENT MET THE REPORTING CRITERIA FOR AN INCIDENT, UNINTENTIONAL GAS LOSS GREATER THAN 3000MCF, UNDER 49 CFR 191.5 AT WHICH TIME THE NRC WAS NOTIFIED IMMEDIATELY. IMMEDIATELY AFTER THE NRC REPORT WAS SUBMITTED, EPNG ALSO NOTIFIED THE PHMSA WESTERN REGION AND THE ARIZONA CORPORATION COMMISSION PIPELINE SAFETY DIVISION. FURTHER INVESTIGATION DETERMINED THAT THE CAUSE OF THE UNINTENTIONAL GAS RELEASE WAS AT LEAST TWO LOW-RESISTANCE TO GROUND FAULTS ON THE STATIONS 135 VDC CONTROL SYSTEM. BASED ON THIS FINDING, THE FIELD WIRING FOR BOTH THE STATION'S HIGH DISCHARGE PRESSURE SWITCH CIRCUIT AND THE STATION'S DISCHARGE LOADING VALVE CIRCUIT WILL BE REPLACED AS SOON AS POSSIBLE AND THE REMAINDER OF THE STATION'S DC SYSTEM WILL BE EVALUATED FOR ADDITIONAL LOW-RESISTANCE GROUND AND/OR DETERIORATION. UPDATE: COST TO HYDRO-VAC AND INSTALL A NEW CONDUIT LINE = $11,200.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160072 | 17183 | 2016-09-08 13:16 | ORIGINAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2016-08-12 10:45 | 2016 |  |  | 28.7447 | -99.0159 | 1156063 | 2016-08-12 13:20 |  | NATURAL GAS |  | 14000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-08-11 03:00 | 2016-08-11 07:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-08-11 03:22 | 2016-08-11 04:45 | ONSHORE | TX | 78017 | DILLY | FRIO | MILEPOST | MP 52.06 | PEARSALL COMPRESSOR STATION | DIMMIT COUNTY MAINLINE LID 287-1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2012 |  | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 457 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 35840 | 36806.0377358491 | 500 | 541.446623915504 | 0 | 0 | 0 | 0 |  |  | 36340 | 38407.0288534764 | 37347.4843597646 | [8 empty] | 918 |  | 1100 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER RECEIVED NON-CRITICAL ALARM, DISPATCHING OPERATIONS. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | THE SUPPLY GAS VALVE WAS FOUND TO BE IN THE CLOSED POSITION. IT IS NOT KNOWN HOW THE NORMALLY OPEN VALVE WAS INADVERTENTLY CLOSED. |  | YES |  |  |  | NORMAL OPERATING CONDITIONS | NO | [150 empty] | MICHAEL D. SMITH | SPECIALIST PIPELINE COMPLIANCE | mdsmith@eprod.com | 713-381-5650 |  |  |  |  | MICHAEL D. SMITH | SPECIALIST PIPELINE COMPLIANCE | 713-381-5650 | mdsmith@eprod.com | ON 8/11/2016 AT 03:00 AM, GAS CONTROL NOTIFIED FIELD OPERATIONS THE PEARSALL COMPRESSOR STATION SHUT DOWN AND THE STATION WAS BLOWING DOWN. OPERATIONS ARRIVED ONSITE AT 04:59 AM AND FOUND THE COMPRESSOR SUCTION AND DISCHARGE VALVES CLOSED AND BLOWDOWN VALVE PARTIALLY OPEN. OPERATIONS DISCOVERED A 3/8"BALL VALVE WAS CLOSED, CUTTING OFF SUPPLY GAS TO THE BETTIS ACTUATOR. GAS SLOWLY LEAKED OUT OF THE BETTIS ACTUATOR CYLINDER THROUGH A PORT RESULTING IN THE BLOW DOWN VALVE OPENING PARTIALLY IN THE FAIL-SAFE POSITION. THE INITIAL GAS LOSS WAS ESTIMATED TO BE 321.70 MSCF BASED ON THE NORMAL ESTIMATED BLOW DOWN FOR THE STATION. ON 8/12/2016 AT 10:45 AM, OPERATIONS CONFIRMED THE AMOUNT OF GAS BLOWN DOWN TO BE 14 MMSCF. NOTIFICATIONS WERE THEN MADE TO THE TCEQ, NRC, AND RRC. THE SUPPLY GAS VALVE WAS FOUND TO BE IN THE CLOSED POSITION. IT IS NOT KNOWN HOW THE NORMALLY OPEN VALVE WAS INADVERTENTLY CLOSED. TO PREVENT RECURRENCE, THE VALVE WAS LOCKED OPEN AND WILL BE REPOSITIONED SO THE VALVE HANDLE IS PROTECTED FROM BEING INADVERTENTLY OPERATED WHEN THE VALVE IS OPEN. ADDITIONALLY, THE PORT PLUG LOCATED ON THE BACK OF THE ACTUATOR WAS REMOVED, TEFLON TAPPED, RE-INSTALLED AND CHECKED FOR LEAKS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160073 | 17225 | 2016-09-09 13:03 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2016-08-10 23:32 | 2016 |  |  | 42.8092 | -82.8648 | 1155919 | 2016-08-11 08:38 |  | NATURAL GAS |  | 18000 | 826 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-08-11 00:33 | 2016-08-11 16:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-08-10 23:32 | 2016-08-11 00:06 | ONSHORE | MI | 48005 | ARMADA | MACOMB | MILEPOST | GV-007 | RAY COMPRESSOR STATION | PLANT II UNIT C2-7 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1995 |  | CARBON STEEL |  | OTHER | [8 empty] | COMPLETE LOSS OF POWER SUPPLY CAUSING VALVE TO FAIL OPEN AND RELEASE GAS TO ATMOSPHERE | CLASS 1 LOCATION | NO |  | 702 |  | NO | NO | NO |  | 0 | 0 | 2378 | 2575.12014334213 | 51840 | 53237.3045822102 | 0 | 0 | 2000 | 2165.78649566201 | 0 | 0 |  |  | 56218 | 57369.7322421179 | 57978.2112212144 | [8 empty] | 1418 |  | 1800 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE APPROPRIATE ACTIONS WERE TAKEN BY CONTROL ROOM OPERATOR | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | AN INCIDENT INVESTIGATION DETERMINED GENERATOR 2-7 CONTROL PANEL WAS IN THE "OFF" POSITION. THE CONTROL PANEL IN THE "OFF" POSITION PREVENTED AUTOMATIC OPERATION OF THE UNIT. | YES |  |  |  |  | ROUTINE MAINTENANCE | NO | [150 empty] | CARMELLA Q. KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 734-513-6256 |  |  |  |  | AMANDA L. WARD | GAS REGULATORY SERVICES LEAD | 517-545-8746 | amanda.ward@cmsenergy.com | ON AUGUST 10, 2016 AT APPROXIMATELY 22:43 CONSUMERS ENERGY RAY COMPRESSOR STATION EXPERIENCED AN EVENT WHEREBY POWER SUPPLIED BY THE UTILITY SUPPLIER WAS BELOW NORMAL LEVELS. THE CONTROL SYSTEM RECOGNIZED A UTILITY SOURCE PHASE SEQUENCE LOSS AS WELL AS A STATION UNINTERRUPTIBLE POWER SUPPLY (UPS) ALARM. AT APPROXIMATELY 22:44, THE COMMERCIAL UTILITY BREAKERS TRIPPED OPEN AND PLANT 3 EMERGENCY SYSTEM TRANSFERRED POWER FROM THE UTILITY OVER TO GENERATOR 3-00-01. THE SYSTEM ATTEMPTED TO TRANSFER POWER TO THE C2-7 GENERATOR SET FOR PLANTS 1 AND 2; HOWEVER, THE SYSTEM DID NOT START AND PLANTS 1, 2 AND THE CONTROL ROOM REMAINED ON UPS POWER. AT APPROXIMATELY 22:44, UTILITY POWER AT THE STATION WAS RESTORED TO ACCEPTABLE LEVELS ACROSS ALL THREE LEGS, AB, BC AND CA. PLANT 3 TRANSFERRED BACK TO UTILITY POWER, HOWEVER, PLANT 1, 2 AND THE CONTROL ROOM REMAINED ON UPS POWER. AT APPROXIMATELY 22:52, UNIT 2-7 INITIATED IT'S SHUTDOWN SEQUENCE DUE TO HIGH CRANKCASE OIL TEMPERATURE, HIGH JACKET WATER TEMPERATURE, LOW ENGINE LUBE OIL PRESSURE AND LOW TURBOCHARGER OIL PRESSURE ALARMS. AT APPROXIMATELY 23:32 THE 2-7 UPS WAS DEPLETED WHICH SUPPLIED POWER TO VENT VALVE GV-007. VENT VALVE GV-007 FAILED OPEN, AS DESIGNED IN THE EVENT OF A POWER LOSS, RESULTING IN A RELEASE OF NATURAL GAS INTO THE ATMOSPHERE. THE ON-CALL OPERATOR ARRIVED AT THE LOCATION ON AUGUST 11, 2016 AT APPROXIMATELY 00:06. AT APPROXIMATELY 00:14 THE ON-CALL OPERATOR REPORTED VENTING GAS AT THE THE SOUTHWEST CORNER OF THE PLANT, VALIDATED THE VENTING GAS WAS COMING FROM PLANT 2 AT APPROXIMATELY 00:20. AT APPROXIMATELY 00:28 A PLANT 2 FIREGATE OPERATION WAS INITIATED AND VENTING GAS WAS STOPPED AT APPROXIMATELY 00:33. THE ON-SITE TEAM BEGAN INVESTIGATING THE CAUSE OF THE VENT VALVE OPENING AND GATHERING DATA. IT WAS DETERMINED THAT GENERATOR 2-7 CONTROL PANEL WAS IN THE "OFF" POSITION. THE CONTROL PANEL IN THE "OFF" POSITION PREVENTS AUTOMATIC OPERATION OF THE UNIT. ON AUGUST 11, 2016 AFTER COMPLETING THE INVESTIGATION, PLANT 2 WAS PLACED BACK INTO SERVICE AT APPROXIMATELY 16:00.
2021-02-26 10:37 | YES | YES | GT (Gas Transmission) | 20160074 | 17186 | 2016-09-14 14:01 | ORIGINAL FINAL | 31286 | ONEOK GAS TRANSPORTATION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2016-08-17 09:25 | 2016 |  |  | 34.7109 | -97.4437 | 1156515 | 2016-08-17 10:41 |  | NATURAL GAS |  | 10611 | 567.8 | 0 | NO | [5 empty] | 0 | YES | 0 | 1 | 0 | 0 | 0 | 1 |  | YES |  | 2016-08-17 10:23 | 2016-08-18 18:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-08-17 09:25 | 2016-08-17 09:40 | ONSHORE | OK | 73433 | Not Within a Municipality | GARVIN | MILEPOST | 22.55 | OGT A-500 | 12 INCH | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | PIPE EXPOSED IN DRY WASH |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 |  | 0.25 | 35000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1949 | 1948 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 36 | 12 |  | CLASS 1 LOCATION | NO |  | 234 |  | NO | NO | NO |  | 2000 | 2165.78649566201 | 0 | 0 | 27952 | 28705.423180593 | 26611 | 28816.8722180309 | 500 | 541.446623915504 | 0 | 0 |  |  | 57063 | 44230.6118046793 | 60229.5285182014 | [8 empty] | 700 |  | 800 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 78288 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OPERATOR'S CONTRACTOR | [260 empty] | PATRICK VAUGHAN | MANAGER REGULATORY COMPLIANCE | pat.vaughan@oneok.com | 9185887734 | 9187321311 |  |  |  | WESLEY DUNBAR | VP NATURAL GAS PIPELINE OPS | 918-588-7424 | wesley.dunbar@oneok.com | AT 09:25 ON 08/17/2016, ONEOK GAS TRANSPORTATION, L.L.C. PIPELINE A-500 RUPTURED AT M.P. 22.55 WHEN STRUCK BY CONTRACTOR OPERATED RIGHT OF WAY CLEARING EQUIPMENT. THE CLEARING EQUIPMENT TIPPED INTO A DRY WASH AND STRUCK THE PIPELINE WHERE IT WAS EXPOSED IN THE BOTTOM OF THE WASH. THE PIPELINE WAS ISOLATED BY 10:23 AND WAS BLOWN DOWN FOR INSPECTION AND REPAIRS. REPAIRS WERE COMPLETED AND THE LINE RETURNED TO SERVICE AT 18:30 ON 08/18/2016.THE CONTRACT EMPLOYEE WHO WAS OPERATING THE RIGHT OF WAY CLEARING EQUIPMENT WAS TRANSPORTED TO A HOSPITAL AND DIAGNOSED WITH SOME BROKEN BONES, ABRASIONS, AND CONTUSIONS. THE INJURIES REQUIRED HOSPITALIZATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160075 | 30243 | 2016-09-16 14:00 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2016-08-21 11:48 | 2016 |  |  | 31.9128 | -88.794 | 1156946 | 2016-08-22 01:44 |  | NATURAL GAS |  | 53804 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-08-22 01:13 | 2016-08-22 07:17 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-08-21 23:40 | 2016-08-21 23:55 | ONSHORE | MS | 39355 | QUITMAN | CLARKE | MILEPOST | 4390+22 | DESTIN COMPRESSOR STATION | INDEX 818-01 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2008 |  | CARBON STEEL |  | OTHER | [8 empty] | BLOW OFF VALVE OPENED UNINTENTIONALLY | CLASS 1 LOCATION | NO |  | 159 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 146386 | 150331.714285714 | 1500 | 1624.33987174651 | 960 | 1039.57751791777 | 0 | 0 |  |  | 148846 | 157078.522659913 | 152995.631675379 | [8 empty] | 1100 |  | 1480 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS CONTROLLER PROPERLY IDENTIFIED THE SITUATION AND PROPERLY RESPONDED TO THE EVENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | DISCHARGE BLOW DOWN VALVE OPENED WHILE BLOCK VALVE REMAINED OPENED AS WELL. | [15 empty] | YES | WATER IN ELECTRICAL BOX ON BLOW DOWN VALVE CAUSED SOLENOID TO DE-ENERGIZE | [161 empty] | SHANNON MATTINGLY | PA OQ AND EVENT SUPPORT PROGRAM LEADER | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | DARRAL WARD | MANAGER PIPELINE SAFETY | 2706886356 | darral.ward@bwpmlp.com | GAS CONTROL RECEIVED A SCADA UNACKNOWLEDGED ALARM FOR THE DESTIN COMPRESSOR STATION AND DISPATCHED OPERATIONS PERSONNEL TO INVESTIGATE. THE STATION DISCHARGE BLOW DOWN VALVE WAS OPEN AND SIDE GATE VALVES WERE OPEN AS WELL. STATION PERSONNEL ACTIVATED THE ESD SYSTEM IN ORDER TO CLOSE THE SIDE GATE VALVES AND STOP THE GAS RELEASE. 3-2-18 UPDATE PER PHMSA INSTRUCTION. *ON 8-21-16 AT 23:44 GAS CONTROL NOTIFIED ON-CALL PERSONNEL OF SCADA ALARM *ON 8-21-16 AT 23:55 PERSONNEL ARRIVED ONSITE *ON 8-22-16 AT 01:00 CRITERIA FOR REPORTING EVENT WAS MET *ON 8-22-16 AT 01:13 EVENT CEASED *ON 8-22-16 AT 01:44 NRC CALL WAS MADE 4-26-18 REVISED A19A TO REFLECT THE TIME WHEN SCADA ALARM WAS RECEIVED WHICH WAS ON 8-21-16 AT 23:40. PHMSA REQUESTED THAT WE CHANGE A4 TO THE TIME THE EVENT IS ESTIMATED TO HAVE RESULTED IN 3 MMCF OF GAS RELEASED; HOWEVER, WE DO NOT HAVE DATA TO SUPPORT CHANGING THIS TIME. 4-27-18 REVISED A4 USING CALCULATION GUIDANCE PROVIDED BY PHMSA.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160076 | 17361 | 2016-09-23 08:05 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2016-08-25 13:20 | 2016 |  |  | 38.877 | -98.0343 | 1157323 | 2016-08-25 14:12 |  | NATURAL GAS |  | 60 | 1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-08-25 15:43 | 2016-09-17 12:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-08-25 13:10 | 2016-08-25 14:00 | ONSHORE | KS | 67425 | Not Within a Municipality | LINCOLN | MILEPOST | 30.14 | KSM20601 | M640A BUSHTON TO TESCOTT A-LINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 26 |  | 0.312 | 40000 | 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | YOUNGSTOWN | NONE | [28 empty] | 1963 | 1958 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 108 | 70 |  | CLASS 1 LOCATION | NO |  | 409 |  | NO | NO | NO |  | 2000 | 2165.78649566201 | 2520 | 2728.89098453414 | 168000 | 172528.301886792 | 50000 | 54144.6623915503 | 20000 | 21657.8649566201 | 0 | 0 |  |  | 242520 | 215910.070888166 | 253225.506715159 | [8 empty] | 476 |  | 520 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 82980 | NO |  | YES |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLERS DETECTED THE FAILURE | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [8 empty] | YES |  |  |  | YES | YES |  | NO | YES | YES | YES |  |  | 2016 | 2010 |  |  | NO | [190 empty] | NO | [63 empty] | YES | 1963 |  | NO | [13 empty] | NO | [63 empty] | JOHN A GORMLEY | SR. CORROSION SPECIALIST | john.gormley@nngco.com | 402-398-7494 | x |  |  |  | THOMAS CORRELL | VP PIPELINE SAFETY AND RISK | 402-398-7715 | thomas.correll@nngco.com | ON AUGUST 25, 2016 AT APPROXIMATELY 1310 HOURS THE OPERATIONS COMMUNICATION CENTER RECEIVED A CALL FROM THE LINCOLN COUNTY, KANSAS DISPATCH OF BLOWING GAS IN LINCOLN COUNTY, KANSAS. SCADA READINGS INDICATED A RAPID DECREASE IN PRESSURE ON THE KSM20601-M640A BUSHTON TO TESCOTT A-LINE. FIELD OPERATIONS CONFIRMED THE PIPELINE HAD FAILED APPROXIMATELY 200-YARDS NORTH OF INTERSTATE HIGHWAY 70. THE HIGHWAY WAS BLOCKED OFF BY EMERGENCY RESPONDERS. AT APPROXIMATELY 1543-HOURS THE MAINLINE BLOCK VALVES WERE CLOSED UPSTREAM AND DOWNSTREAM OF THE SITE AND THE PRESSURE DECREASED TO 0-PSIG. PHMSA ACCIDENT INVESTIGATORS FROM THE CENTRAL REGION AND SOUTHWEST REGION ARRIVED ON SITE BY 20:30 AND AT 13:00 ON AUGUST 26, 2016, RESPECTIVELY. INITIAL EXAMINATION SHOWED THE PIPELINE RUPTURED DUE TO ISOLATED GENERAL EXTERNAL CORROSION. THE FAILED PIECE WAS 9-FEET LONG WITH ABOUT 18 SQUARE FEET OF THINNER WALL PIPE. THE SURROUNDING PIPE APPEARS TO BE IN GOOD CONDITION. THE FAILED PIECES WERE SENT FOR LABORATORY EXAMINATION. **UPDATE** NORTHERN HAS BEEN PROVIDING QUARTERLY UPDATES TO THE SOUTHWEST REGION PHMSA THAT CONTAINS MORE INFORMATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160077 | 17551 | 2016-09-23 11:50 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2016-08-25 04:55 | 2016 |  |  | 39.4803 | -80.5382 | 1157264 | 2016-08-25 08:16 |  | NATURAL GAS |  | 19234 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-08-25 05:30 | 2016-08-25 09:20 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-08-25 04:25 | 2016-08-25 04:55 | ONSHORE | WV | 26437 | SMITHFIELD | WETZEL COUNTY | MILEPOST | PNEUMATIC SYS | SMITHFIELD COMPRESSOR STATION | C75-32, C75-33, C75-34 AND C75-35 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 1967 |  | CARBON STEEL |  | LEAK |  |  | OTHER | PNEUMATIC SYS. P-DIFFERENTIAL | [5 empty] | CLASS 1 LOCATION | NO |  | 150 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 49816 | 51158.7493261456 | 0 | 0 | 0 | 0 | 0 | 0 | NO FIRE OR DAMAGE TO ANY OF THE COMPRESSOR STATION FACILITY COMPONENTS |  | 49816 | 53038.5983827493 | 51158.7493261456 | [8 empty] | 933 |  | 960 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) | [6 empty] | YES | [6 empty] | YES | 2 | 0 | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | OTHER | ESD PNEUMATIC SYSTEM | [15 empty] | YES | YES | [166 empty] | GEORGE HAMATY | ENGINEER | george_hamaty@transcanada.com | (304) 553-8306 |  |  |  |  | LEE ROMACK | US REGULATORY COMPLIANCE MANAGER | (713)386-3404 | lee_romack@transcanada.com | ON AUGUST 25, 2016 AT 04: 25 AM, AN ALARM WAS ACKNOWLEDGED BY COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA) GAS CONTROL (GC) PERSONNEL TRIGGERED FROM SMITHFIELD COMPRESSOR STATION (CS). FOLLOWING THE GC PROTOCOLS, OPERATIONS PERSONNEL WERE NOTIFIED TO INVESTIGATE THIS ALARM AT THE CS. SMITHFIELD CS (LOCATED IN WETZEL COUNTY, WEST VIRGINIA) IS A TRANSMISSION CS THAT IS OPERATED AND MAINTAINED BY COLUMBIA. UPON ARRIVING AT THE CS, COLUMBIA PERSONNEL IDENTIFIED THE SOURCE OF THE NOISE FROM THE RELEASED NATURAL GAS (MATERIAL) INTO ATMOSPHERE AND MANUALLY CLOSED THE PROPER VALVES ON SITE TO CONTROL THE MATERIAL RELEASE. DUE TO THE UNINTENDED RELEASE OF MATERIAL THAT EXCEEDED 3,000 MCF, IT WAS REPORTED TO THE NATIONAL RESPONSE CENTER AS AN INCIDENT. THE INVESTIGATION INTO THE PROBABLE CAUSE BEHIND THE EMERGENCY SHUTDOWN (ESD) ACTIVATION AT SMITHFIELD CS HAS BEEN TRACED TO A PROGRAMMABLE LOGIC CONTROLLER (PLC) ERROR THAT RESULTED IN A FAULTY SIGNAL TO THE PNEUMATIC SYSTEM, CAUSING THE ESD VENT VALVES TO OPEN. THE ESD SYSTEM WAS INSPECTED WITH ITS RESPECTIVE COMPONENTS AND THE CS WAS RETURNED BACK INTO SERVICE ON AUGUST 25, 2016 AT 09:20 AM. SUBSEQUENTLY, THE PLC PROGRAM AND ESD SYSTEMS HAVE BEEN REVIEWED AND MODIFIED TO PREVENT RE-OCCURRENCE. THE ROOT CAUSE ANALYSIS INVESTIGATION NOTED CERTAIN KEY COMPONENTS THAT WERE IDENTIFIED AS CONTRIBUTING FACTORS THAT MAY HAVE LED TO THE UNINTENDED ESD OF THE SMITHFIELD CS. THEY WERE: (I) ALARMS AND SYSTEM FAULTS WERE TO BE INVESTIGATED PRIOR TO ACKNOWLEDGEMENT AND CLEARING. NOTIFICATION PROCESS AND PROCEDURES MUST BE FOLLOWED. (II) ESD PILOT AIR SYSTEM TO BE TESTED AND INSPECTED TO ENSURE THAT IT FUNCTION AS REQUIRED. (III) AFTER AN ESD SYSTEM MALFUNCTION, THE ESD SYSTEM DESIGN MAY NEED TO BE RE-EVALUATED TO ENSURE THAT IT PERFORMS AS REQUIRED AND EXPECTED. (IV) ALARMS THAT DISABLE ESSENTIAL STATION COMPONENTS NEED TO BE FULLY VETTED AND INVESTIGATED TO IDENTIFY THE SOURCE AND TO REMEDY THE ISSUE. THE LISTED FOUR ITEMS IN THE RCA REPORT WERE IMPLEMENTED AND COMPLETED WHERE THE FACILITY DID NOT EXPERIENCE ANY SIMILAR INDICATIONS THAT MAY POTENTIALLY INITIATE AN ESD SYSTEM FAILURE, SUBJECT TO THE CORRECTED KEY ITEMS IN THE RCA REPORT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160078 | 17193 | 2016-09-26 20:24 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2016-08-27 07:11 | 2016 |  |  | 36.9364 | -121.8021 | 1157492 | 2016-08-27 12:36 |  | NATURAL GAS |  | 232 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-08-27 19:00 | 2016-08-31 11:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-08-27 07:11 | 2016-08-27 07:45 | ONSHORE | CA | 95076 | WATSONVILLE | SANTA CRUZ | MILEPOST | MP 4.45 | 1816-01 | 941348 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 22 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | CAP FOR 3/4" MUELLER SERVICE TEE | UNKNOWN |  | CARBON STEEL |  | MECHANICAL PUNCTURE | 1 | 0.3 | [7 empty] | CLASS 3 LOCATION | NO |  | 144 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 1000 | 1026.95417789757 | 450000 | 487301.961523953 | 0 | 0 | 0 | 0 |  |  | 451000 | 224749.148721786 | 488328.915701851 | [8 empty] | 227 |  | 242 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 18374 | NO | [5 empty] | YES | NOT PIGGABLE WITH TODAY'S TECHNOLOGY": NO STUDY HAS BEEN DONE ON THIS SECTION OF THIS LINE TO DETERMINE WHICH FEATURES THEREIN MIGHT LIMIT INTERNAL INSPECTION TOOLS | YES |  | YES |  |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK TO THE LINE WAS A 1" BY 0.25" CRACK NEAR THE CAP OF THE 3/4" MUELLER SERVICE TEE . THE LEAK SHOWED A MINOR PRESSURE DROP IN THE SYSTEM. THE MINOR PRESSURE DROP WAS INDICATIVE OF A MORNING LOAD DROP, WHICH WAS CONSISTENT FOR THE SYSTEM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  | YES | PRIVATE LANDOWNER | YES | [6 empty] | FARMER | FARM EQUIPMENT | AGRICULTURE | NO | [5 empty] | YES | 14 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | STEPHEN RAMOS | GAS ENGINEER | s3rc@pge.com | 925-413-7311 |  |  |  |  | SUSIE RICHMOND | MANAGER OF REGULATORY COMPLIANCE | 925-328-5776 | gsr8@pge.com | ON AUGUST 27, 2016, AT 0711 HOURS, PG&E WAS NOTIFIED OF A GAS LEAK NEAR 677 BEUNA VISTA DR, WATSONVILLE. PG&E GAS SERVICE REPRESENTATIVE (GSR) ARRIVED ON-SITE AT 0745 HOURS. UPON ARRIVAL, THE GSR OBSERVED A DIG-IN ON EITHER DFM 1816-01 (MP 4.45) OR A 3/4" SERVICE LINE FROM 1817-01 FROM AGRICULTURE WORK THAT OCCURRED ON 8/26/16. THE OEC WAS ACTIVATED AND THE LINE WAS SHUT-IN BY 1900 HOURS TO DETERMINE THE LOCATION OF THE DIG-IN. ON 8/28/16 AT 0048 HOURS, THE DIG-IN LOCATION WAS CONFIRMED TO BE ON LINE DFM 1816-01. THE CAP OF A 3/4" MUELLER SERVICE TEE WAS STRUCK, CAUSING A CRACK ABOVE THE BRANCH WELD MEASURING APPROXIMATELY 1" IN LENGTH AND 1/4" WIDE AT THE WIDEST POINT ALONG ITS LENGTH. THE EXCAVATOR FARMING COMPANY THAT CAUSED THE DIG-IN WAS INTERRUPCION SOCIAL ENTERPRISE. THE EXCAVATOR DID NOT HAVE A USA TICKET. THERE WERE VISIBLE PG&E MARKERS ON THE PROPERTY. APPROXIMATELY 60 CUSTOMERS WERE IMPACTED AS A RESULT OF THIS INCIDENT. CNG WAS PROVIDED TO THE IMPACTED CUSTOMERS. MAJORITY OF THE CUSTOMERS WERE RESTORED BY 8/28/16 AT 1148 HOURS. THE REMAINING CUSTOMERS WERE RESTORED SHORTLY AFTER. REPAIRS TO THE PIPELINE WERE COMPLETED AND THE PIPELINE WAS RESTORED TO NORMAL OPERATIONS ON 8/31/16 AT 1100 HOURS. FIRE DEPARTMENT WAS REPORTED ON SITE. THERE WERE NO INJURIES, FATALITIES OR IGNITION ASSOCIATED WITH THE INCIDENT. ESTIMATED UNINTENTIONAL VOLUME OF GAS RELEASE IS LESS THAN 3 MMCF. THIS INCIDENT WAS REPORTED TO THE DOT AND CPUC DUE TO THE UNINTENTIONAL RELEASE OF GAS AND ESTIMATED DAMAGES EXCEEDING $50,000.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160079 | 30729 | 2016-10-05 17:15 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2016-09-08 10:38 | 2016 |  |  | 28.5321 | -93.172 | 1158513 | 2016-09-08 16:01 |  | NATURAL GAS |  | 571 | 82668 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-09-08 16:05 | 2016-11-29 12:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-09-08 10:38 | 2016-09-08 14:30 | OFFSHORE | [28 empty] | 140 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EAST CAMERON | 293 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 |  | 0.375 | 52000 | API 5LX | SEAMLESS |  | U.S. STEEL | OTHER | CONCRETE AND SOMASTIC | [27 empty] | 1975 | 1975 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 419 |  | NO | NO | NO |  | 0 | 0 | 248004 | 268561.857035081 | 1713 | 1759.17250673854 | 1200000 | 1299471.89739721 | 0 | 0 | 0 | 0 |  |  | 1449717 | 721592.682744954 | 1569792.92693903 | [8 empty] | 829 |  | 1440 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 59717 | NO |  |  |  | YES |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | NOTIFICATION FROM THIRD PARTY THAT SPOTTED THE BUBBLES ON THE SURFACE |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS TOO SMALL TO BE IDENTIFIED BY THE CONTROL ROOM PERSONNEL. A REVIEW OF OPERATING RECORDS FOUND ABNORMAL OPERATING CONDITIONS DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NOT APPLICABLE - NOT MAINLINE PIPE | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | deteschendorf@spectraenergy.com | 713-627-5573 |  |  |  |  | NATHAN ATANU | MANAGER | 713-627-5008 | nyatanu@spectraenergy.com | SURFACE BUBBLES WERE DISCOVERED IN EAST CAMERON BLOCK 293 AT 10:38 AM, SEPTEMBER 8, 2016 BY A THIRD PARTY FLYING IN A HELICOPTER. SPECTRA ENERGY CONFIRMED THE DISCOVERY AS BEING ASSOCIATED WITH ONE OF THEIR TEAS EASTERN PIPELINES AT 2:30 PM, SEPTEMBER 8, 2016. SPECTRA ENERGY DETERMINED THE LEAK WAS COMING FROM 16-INCH TEXAS EASTERN TRANSMISSION L.P. LINE 41-A-5 NATURAL GAS PIPELINE. THE PIPELINE SEGMENT WAS SHUT IN AT 4:05 PM, SEPTEMBER 8, 2016. AT 8:45 AM, SEPTEMBER 10, 2016 A LIGHT SHEEN DUE TO LESS THAN ONE GALLON OF CONDENSATE RELEASE WAS OBSERVED BY HELICOPTER AT THE SITE. THE APPARENT CAUSE OF THE INCIDENT WAS INTERNAL CORROSION. THE PIPELINE WAS RETURNED TO SERVICE NOVEMBER 29, 2016.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160080 | 17219 | 2016-10-06 09:34 | SUPPLEMENTAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2016-09-13 20:46 | 2016 |  |  | 32.7877 | -84.2543 | 1158934 | 2016-09-13 22:37 |  | NATURAL GAS |  | 9372 | 50 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | REMAINDER OF STATION WAS AVAILABLE FOR SERVICE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-09-13 20:46 | 2016-09-13 20:41 | ONSHORE | GA | 30286 | Not Within a Municipality | UPSON | MILEPOST | 346.954 | THOMASTON COMPRESSOR STATION | SOUTH MAIN LINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2003 |  | CARBON STEEL |  | OTHER | [8 empty] | UNIT #3 SUCTION VALVE DID NOT FULLY CLOSE WHEN UNIT WAS BROUGHT OFF LINE MANUALLY; AUTOMATIC 3-INCH VENT VALVE LATER OPENED TO BLOW DOWN UNIT #3 PIPING FOR SAFETY; GAS RELEASE CONTINUED BECAUSE SUCTION VALVE WAS NOT FULLY CLOSED; | CLASS 1 LOCATION | NO |  | 431 |  | NO | NO | NO |  | 0 | 0 | 140 | 151.605054696341 | 26115 | 26818.9083557951 | 0 | 0 | 150 | 162.433987174651 | 0 | 0 |  |  | 26405 | 27948.5322606228 | 27132.9473976661 | [8 empty] | 810 |  | 1440 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | NO | NO | NO | NO | OTHER | KINDER MORGAN CONTRACT SECURITY GUARD ON SITE |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | KINDER MORGAN CONTRACT SECURITY GUARD ON SITE NOTIFIED KINDER MORGAN STATION OPERATOR OF THE GAS RELEASE; | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [30 empty] | YES | VALVE INDICATOR SHOWED SUCTION VALVE CLOSED BUT VALVE DID NOT FULLY CLOSE | [161 empty] | WM. MARTIN MULLER | SPECIALIST - PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205 325 3863 | 205 325 3508 |  |  |  | REJI GEORGE | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713 420 5433 | reji_george@kindermorgan.com | UNIT #3 TAKEN OFF LINE MANUALLY; LATER AUTOMATIC 3-INCH VENT VALVE OPENED TO BLOW DOWN UNIT #3 PIPING FOR STATION SAFETY; NORMALLY A RELEASE OF 50MCF NATURAL GAS; WHEN UNIT #3 WAS COMING OFF LINE, 18-INCH SUCTION VALVE HAD NOT FULLY CLOSED EVEN THOUGH LIMIT SWITCHES WERE MET ALLOWING GAS SUPPLY TO THE VENT SYSTEM; CONSTRUCTION IN PROGRESS AT STATION, LOCAL MANUAL, THEREFORE SCADA WAS TEMPORARILY DISABLED; ON SITE CONSTRUCTION SECURITY GUARD NOTIFIED STATION OPERATOR OF THE VENTING; STATION OPERATOR RETURNED TO STATION YARD AND MANUALLY CLOSED SUCTION VALVE; SAID 18-INCH VALVE IS CURRENTLY OPERATING WITH NO ISSUES.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160081 | 17198 | 2016-10-07 14:00 | ORIGINAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2016-09-14 11:05 | 2016 |  |  | 29.8676 | -95.2024 | 1158980 | 2016-09-14 13:15 |  | NATURAL GAS |  | 63 | 806 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-09-14 13:25 | 2016-09-15 01:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 750 | 2016-09-14 10:51 | 2016-09-14 11:05 | ONSHORE | TX | 77044 | HOUSTON | HARRIS | SURVEY STATION NO. | 455+24 | EAST TEXAS 12" | ACCOUNT 3016 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12.75 |  | 0.25 | 52000 | API5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | REPUBLIC STEEL | COAL TAR | [28 empty] | 1979 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 1 | 0.1 | [7 empty] | CLASS 1 LOCATION | NO |  | 285 |  | NO | NO | NO |  | 0 | 0 | 1249 | 1352.53366654093 | 97 | 99.6145552560647 | 44132 | 47790.244813278 | 2000 | 2165.78649566201 | 0 | 0 |  |  | 47478 | 23655.2601268809 | 51408.179530737 | [8 empty] | 606 |  | 938 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 21839 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CAUSE OF THE INCIDENT WAS FROM A THIRD PARTY CONTRACTOR. THE CONTROLLERS ACTIONS WERE APPROPRIATE FOR THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | NO |  |  | YES | PRIVATE LANDOWNER | YES | [6 empty] | CONTRACTOR | TRENCHER | NATURAL GAS | YES | 1675020412 | LONE STAR | UTILITY OWNER | NO | NO | YES | 14 | LOCATING PRACTICES NOT SUFFICIENT |  | FACILITY WAS NOT LOCATED OR MARKED | [264 empty] | DANNY NICHOLS | DIRECTOR REGULATORY COMPLIANCE | danny.nichols@energytransfer.com | 7139897232 |  |  |  |  | DANNY NICHOLS | DIRECTOR REGULATORY COMPLIANCE | 7139897232 | danny.nichols@energytransfer.com | AT APPROXIMATELY 10:57 HOURS ON SEPTEMBER 14, 2016, ENERGY TRANSFER SUSTAINED A PIPELINE STRIKE FROM A THIRD PARTY CONTRACTOR CROSSING THE EASEMENT ON ITS EAST TEXAS 12" TRANSMISSION LINE, ACCOUNT #3016. (RRC SYSTEM ID: 530733). THIS EVENT OCCURRED IN A CLASS 1 LOCATION IN NORTHEAST HOUSTON IN HARRIS COUNTY NEAR THE INTERSECTION OF EAST LITTLE YORK ROAD AND PRIMROSE MARK LANE. THERE WERE NO FIRES OR INJURIES. NOTIFICATIONS WERE MADE TO THE NRC AND RRC AT APPROXIMATELY 1315 HOURS. THE LINE WAS ISOLATED, BLOWN DOWN, AND THE DAMAGED SECTION WAS REMOVED AND REPLACED. THE LINE WAS RETURNED TO SERVICE SEPTEMBER 15, 2016 AT APPROXIMATELY 0115 HOURS. THIS OCCURRED ON AN INTRASTATE GAS TRANSMISSION PIPELINE UNDER JURISDICTION OF THE TEXAS RAILROAD COMMISSION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160082 | 30536 | 2016-10-07 23:57 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2016-09-07 12:50 | 2016 |  |  | 35.4962 | -99.3114 | 1158405 | 2016-09-07 14:16 |  | NATURAL GAS |  | 1847 | 4933 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-09-07 14:00 | 2016-09-19 17:20 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-09-07 12:50 | 2016-09-07 13:40 | ONSHORE | OK | 73639 | Not Within a Municipality | CUSTER | MILEPOST | MP 0.00 | TAP VALVE FOR ABANDONED LATERAL (496-0601A) | LATERAL 496-0601 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | DRAIN LINES | [38 empty] | UNKNOWN |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | 1/2 INCH BODY BLEED ON VALVE | CIRCUMFERENTIAL |  | 0.62 | 0.62 | CONTACT OF CULTIVATING EQUIPMENT ON A HIGH-HEAD VALVE EXTENSION CAUSED THE 1/2 INCH BODY BLEED TO BREAK FROM THE VALVE, CREATING A LEAK. | CLASS 1 LOCATION | NO |  | 135 |  | NO | NO | NO |  | 0 | 0 | 4933 | 5341.91239155036 | 5209 | 5349.40431266846 | 93995 | 101786.550829876 | 30408 | 32928.6178800453 | 0 | 0 |  |  | 134545 | 69835.8662387484 | 145406.48541414 | [8 empty] | 955 |  | 1050 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | AUTOMATIC | 60000 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS NOT LARGE ENOUGH ON THE 6 INCH TAP FACILITIES (THROUGH A 1/2 INCH BODY BLEED LINE OF A 6 INCH VALVE) OF AN ABANDONED LATERAL TO AFFECT OPERATION ON THE 16 INCH TRUNK TO WHICH IT WAS ATTACHED TO BE REASONABLY DETECTABLE BY SCADA ON THE 16 INCH PIPELINE | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [260 empty] | JOHN S CHIN | SR. REGULATORY COMPLIANCE SPECIALIST | john_chin@transcanada.com | 248-205-4522 | 248-205-4622 |  |  |  | JOHN S CHIN | SR. REGULATORY COMPLIANCE SPECIALIST | 248-205-4522 | john_chin@transcanada.com | AFTER RUNNING OVER A PIPE GUARD AND A HIGH-HEAD VALVE EXTENSION WITH CULTIVATING EQUIPMENT, THE PROPERTY OWNER CALLED TRANSCANADA GAS CONTROL TO REPORT LEAKING GAS AT 12:50 CT ON SEPTEMBER 7, 2016. FIELD PERSONNEL WERE DISPATCHED TO INVESTIGATE. IT WAS CONFIRMED THAT THE AFFECTED FACILITIES WERE ON ANR'S 496-0601 TAP TO THE 496-1601 LINE. THE 6" SIDE VALVE ASSEMBLY WAS WHAT REMAINED OF THE 496-0601 LATERAL THAT WAS ABANDONED IN 1998. VALVES ON THE 496-1601 LINE ON EACH OF THE TAP WERE USED TO ISOLATE AND BLOW DOWN THE LEAKING FACILITY. IT WAS DETERMINED AFTER BLOWING DOWN THIS SEGMENT THAT THE EQUIPMENT STRIKE CAUSED A 1/2-INCH BODY BLEED ON THE6" SIDE VALVE TO BREAK AND LEAK. NECESSARY REPAIRS WERE MADE AND THE FACILITY WAS RETURNED TO SERVICE ON SEPTEMBER 19, 2016. THERE WAS NOT IGNITION OF THE LEAKING GAS. THERE WAS NO EVIDENCE OF LIQUID HYDROCARBONS FROM THE LEAK. THERE WERE NO INJURIES. AS A PRECAUTION THE CLOSEST RESIDENTS WERE ASKED TO NOT RETURN TO THEIR HOMES UNTIL THE BLOWDOWN WAS COMPLETED AND THE FACILITY WAS MADE SAFE. THE CLOSEST OF THE TWO RESIDENCES WAS 300 FEET FROM THE LOCATION OF THE LEAK, SIGNIFICANTLY OUTSIDE THE PIR OF 135 FEET.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160083 | 17200 | 2016-10-11 07:41 | ORIGINAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2016-09-23 10:08 | 2016 |  |  | 30.3872 | -99.8971 | 1159819 | 2016-09-23 17:09 |  | NATURAL GAS |  | 24879 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-09-23 10:08 | 2016-09-23 12:13 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-09-23 10:08 | 2016-09-23 10:08 | ONSHORE | TX | 76849 | JUNCTION | KIMBLE | MILEPOST | MP 301.8 | JUNCTION COMPRESSOR STATION | OASIS ACCOUNT 3952 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 1972 |  | CARBON STEEL |  | OTHER | [8 empty] | THE POWER SUPPLY ON THE STATION CONTROL BOARD FAILED, STATION SHUT DOWN. (BLOW DOWN OPENED AND THE SUCTION BLOCK VALVE FAILED TO CLOSE DUE TO THE PRESSURE DROP ACROSS THE VALVES AND HAD TO BE CLOSED MANUALLY. | CLASS 1 LOCATION | NO |  | 671 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 62197 | 63873.4690026954 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 62197 | 66220.525606469 | 63873.4690026954 | [8 empty] | 870 |  | 1050 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PROBLEM WAS WITH THE CONTROL BOARD AT THE STATION, AND DUE TO THE PRESSURE DROP, THE SUCTION VALVE WOULD NOT SET PROPERLY. SCADA NOTIFIED OPERATIONS OF THE INCIDENT AND OPERATIONS WAS ALREADY AT THE COMPRESSOR STATION BECAUSE IT IS MANNED 8 HOURS A DAY. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | YES | [6 empty] | YES | [27 empty] | YES | FAULTY ELECTRICAL PANEL | [161 empty] | DANNY NICHOLS | DIRECTOR REGULATORY COMPLIANCE | danny.nichols@energytransfer.com | 7139897232 |  |  |  |  | DANNY NICHOLS | DIRECTOR REGULATORY COMPLIANCE | 7139897232 | danny.nichols@energytransfer.com | AT 6:30AM, JUNCTION COMPRESSOR STATION SHUTDOWN. AT 10:00AM I/E AND FIELD OPERATOR WENT TO TROUBLESHOOT WHY THE STATION SHUTDOWN. WHILE TROUBLESHOOTING THE ELECTRICAL PANEL, THE I/E FOUND A BAD POWER SUPPLY. WHEN I/E DISCONNECTED THE POWER SUPPLY, THE STATION BEGAN ITS VALVE SEQUENCE TO SHUT DOWN. (STATION WAS NOT RUNNING WHILE TROUBLESHOOTING, BUT WAS PRESSURED UP.) BLOW DOWNS OPENED ON THE COMPRESSOR STATIONS, DISCHARGE VALVE CLOSED, BUT THE SUCTION VALVE WOULD NOT FULLY CLOSE. THE FIELD OPERATOR CLOSED THE SUCTION VALVES ON BOTH COMPRESSORS MANUALLY AND ALLOWED COMPRESSOR STATION TO BLOW DOWN COMPLETELY. POWER SUPPLY WAS REPLACED AT 11:30AM. ALL SYSTEMS WERE RETESTED FOR RELIABILITY AND STATION WAS PUT BACK ONLINE AT 12:13PM. THIS OCCURRED ON AN INTRASTATE GAS TRANSMISSION SYSTEM UNDER JURISDICTION OF THE TX RRC. (SYSTEM ID 230998)
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160084 | 17309 | 2016-10-15 09:04 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2016-09-15 08:16 | 2016 |  |  | 42.2069 | -83.9691 | 1159095 | 2016-09-15 16:58 |  | NATURAL GAS |  | 3484 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE FACILITY WAS ISOLATED DUE TO THE WORK BEING PERFORMED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-09-15 08:16 | 2016-09-15 08:16 | ONSHORE | MI | 48158 | MANCHESTER | WASHTENAW | MILEPOST | FREEDOM CS | FREEDOM COMPRESSOR STATION | PLANT 2 PILOT GAS | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 1 |  | 0.179 | 35000 | A106 GRADE B | SEAMLESS |  | UNKNOWN | PAINT | [28 empty] | 1952 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | DUE TO AN INADEQUATE PROCEDURE, THE PILOT LINE DESCRIBED WAS BLOWN DOWN BEFORE THE POWER LINE WAS BLOWN DOWN, RESULTING IN ACTIVATION OF A FIREGATE VALVE. | CLASS 3 LOCATION | NO |  | 96 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 10068 | 10339.3746630728 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 10068 | 10719.2991913747 | 10339.3746630728 | [8 empty] | 190 |  | 200 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS NOT DETERMINED TO BE AT FAULT OF THE CONTROL ROOM OPERATOR. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [204 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE |  |  |  | YES |  |  |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | KARLI MCNEILL | G ENGINEER I - GAS REG SERVICES INCIDENT SUPPORT | karli.mcneill@cmsenergy.com | 734-524-6350 |  |  |  |  | AMANDA WARD | SR ENGINEER LEAD - MPSC GAS REGULATORY SERVICES | 248-431-0888 | amanda.ward@cmsenergy.com | AT 0816 HOURS ON THURSDAY, SEPTEMBER 15, 2016, TWO EMPLOYEES WERE FOLLOWING A PROCEDURE TO REPLACE A SECTION OF PIPE AT FIREGATE BOX 2-4 AT FREEDOM COMPRESSOR STATION. TO ISOLATE THE LINE TO BE WORKED ON, THE PILOT GAS LINES BETWEEN THE PILOT ISOLATION VALVE AND PILOT GAS SOLENOID WERE REQUIRED TO BE VENTED. IN ORDER TO PERFORM THIS TASK, THE FIREGATE VENT VALVES NEEDED TO BE IMMOBILIZED, TO PREVENT THE UNINTENDED RELEASE OF GAS. THE NORMAL PROCEDURE TO COMPLETE THIS TASK IS TO ISOLATE THE LOCAL POWER GAS AT THE ACTUATOR, AND VENT THE LINE BETWEEN THE ISOLATION VALVE AND THE ACTUATOR, THEN ISOLATE THE PILOT GAS AT THE ACTUATOR, AND VENT THE LINE BETWEEN THE ISOLATION VALVE AND THE ACTUATOR. ALL POWER GAS LINES AND PILOT GAS LINES TO THE EMERGENCY SHUTDOWN VALVE ACTUATORS WERE ISOLATED, AND THE CREW BEGAN TO VENT THE PILOT LINES ON TWO OF THE VALVES, VALVE 612 AND VALVE 614. THIS RESULTED (AS DESIGNED) IN TWO FIREGATE VALVES (612 AND 614) TRAVELING TO 100% OPEN AND VENTING 3.484 MMCF OF NATURAL GAS FROM A 620 PSI LINE TO ATMOSPHERE THROUGH THE 16-FOOT VENT STACK, FROM 0816 HOURS TO 0825 HOURS. THE OPENED VALVES WERE MANUALLY CLOSED BY STATION PERSONNEL. AFTER RE-ASSESSMENT OF THE PROCEDURE AND SITUATION, STATION PERSONNEL RELIEVED PRESSURE OFF OF THE POWER GAS BETWEEN THE ISOLATION VALVE AND FIREGATE VENT VALVE ACTUATORS, AND THEN RELIEVED PRESSURE OFF THE PILOT GAS. THE REQUIRED SEQUENCE TO ISOLATE FIREGATE VALVES IS TO ISOLATE POWER GAS AND THEN PILOT GAS. THIS SEQUENCE WAS NOT OUTLINED IN THE PROCEDURE PROVIDED. A DETAILED REVIEW OF THE PROCEDURE WAS NOT COMPLETED BY ADDITIONAL ENGINEERING REPRESENTATION FROM GAS COMPRESSION OPERATIONS, AND A PHYSICAL WALK-DOWN OF THE EQUIPMENT WAS NOT PERFORMED BY THE SITE FIELD LEADER, PRINCIPAL FIELD LEADER, OR BY ASSIGNED CREW PRIOR TO PROCEDURE APPROVAL OR WORK PERFORMANCE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160085 | 17379 | 2016-10-20 16:37 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2016-09-22 08:33 | 2016 |  |  | 42.7196 | -82.7133 | 1159709 | 2016-09-22 16:36 |  | NATURAL GAS |  | 3680 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE CAUSE OF FAILURE WAS IDENTIFIED, CORRECTED AND RETURNED TO NORMAL OPERATIONS | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-09-22 08:55 | 2016-09-22 09:50 | ONSHORE | MI | 48023 | IRA | ST. CLAIR COUNTY | MILEPOST | VALVE #604 | ST. CLAIR COMPRESSOR STATION PLANT II | ST. CLAIR COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2016 |  | CARBON STEEL |  | OTHER | [8 empty] | FIREGATE BLOCK VALVE UNEXPECTEDLY FAILED CLOSED DUE TO LOSS OF ELECTRIC POWER | CLASS 3 LOCATION | YES | METHOD2 | 681 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 10635 | 10921.6576819407 | 0 | 0 | 65 | 70.3880611090154 | 0 | 0 |  |  | 10700 | 11355.2884140247 | 10992.0457430497 | [8 empty] | 1430 |  | 1440 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONDITION WAS AUDIBLE AT THE LOCATION AND NO INVESTIGATION OF CONTROL ROOM ACTIONS WAS NECESSARY | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | LOSS OF LOCAL POWER - THE PRIMARY CAUSE OF LOSS OF LOCAL POWER WAS ON-SITE ELECTRICAL RE-WORK BEING COMPLETED BY A SECOND PARTY CONTRACTOR INVOLVED IN THE CURRENT STATION UPGRADE PROJECT. |  |  |  | YES | LACK OF TRANSITIONAL PROCEDURE | CONSTRUCTION | NO | [150 empty] | CARMELLA KING | SENIOR ENGINEER TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 734-513-6256 |  |  |  |  | JASON PIONK | SR. ENG. TECH ANAL LEAD - GAS REGULATORY SERVICES | 989-791-5749 | jason.pionk@cmsenergy.com | ON SEPTEMBER 22, 2016 AT APPROXIMATELY 08:33 THE ST. CLAIR PLANT II DISCHARGE HEADER FIREGATE BLOCK VALVE #604 AT CONSUMERS ENERGY ST. CLAIR COMPRESSOR STATION PLANT II UNEXPECTEDLY FAILED TO THE CLOSED POSITION DUE TO LOCAL LOSS OF ELECTRIC POWER TO THE ACTUATOR CONTROLS. CONSUMERS ENERGY 'S ST. CLAIR COMPRESSOR STATION IS LOCATED IN IRA, MICHIGAN (ST. CLAIR COUNTY). THE VALVE CLOSURE RESULTED IN A BLOCKED DISCHARGE FROM UNIT 2-4, WHILE IT WAS OPERATING. AS PRESSURE ON THE DISCHARGE LINE INCREASED TO 1430 PSIG, THE RELIEF VALVE ON THE DISCHARGE OF THE UNIT OPENED RELIEVING PRESSURE ON THE LINE TO 1255 PSIG. THE RELIEF VALVE CYCLED FOR APPROXIMATELY ONE HOUR PRIOR TO THE BLOCK VALVE BEING IDENTIFIED AS THE CAUSE OF THE FAILURE. THE VALVE WAS RETURNED TO THE OPEN POSITION, AND NORMAL OPERATION WAS CONTINUED AT APPROXIMATELY 10:06. A LOCAL INVESTIGATION DETERMINE A LOSS OF POWER CAUSED THE EMERGENCY SHUT DOWN (ESD) TO OPERATE AT THE STATION. THE ESD OPERATION TRIGGERED GATE VALVE #604 TO TRAVEL WHEN NOT INTENDED LEADING TO AN UNPLANNED GAS RELEASE. ADDITIONAL INCIDENT ANALYSIS CONCLUDED THE PRIMARY CAUSE OF THE POWER OUTAGE WAS ON-SITE ELECTRICAL RE-WORK BEING PERFORMED BY A SECOND PARTY CONTRACTOR INVOLVED IN THE STATION UPGRADE PROJECT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160086 | 17227 | 2016-10-26 17:54 | SUPPLEMENTAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2016-10-08 14:06 | 2016 |  |  | 32.909 | -81.9659 | 1161070 | 2016-10-08 16:02 |  | NATURAL GAS |  | 79937 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-10-08 16:26 | 2016-10-17 14:25 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-10-08 14:06 | 2016-10-08 14:39 | ONSHORE | GA | 30442 | Not Within a Municipality | JENKINS | MILEPOST | 35 / 09+20 | WRENS SAVANNAH 2ND LOOP LINE | WRENS SAVANNAH 2ND LOOP LINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 54 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.406 | 52000 | API-5L | SEAMLESS |  | UNITED STATES STEEL | COAL TAR | [28 empty] | 1977 | 1977 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 144.9 | 62.8 |  | CLASS 1 LOCATION | NO |  | 478 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 227820 | 233960.700808625 | 125000 | 135361.655978876 | 400 | 433.157299132403 | 0 | 0 |  |  | 353220 | 304891.084430327 | 369755.514086634 | [8 empty] | 1170 |  | 1200 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 49827 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | MAOP WAS NOT EXCEEDED; SNG FIELD EMPLOYEES VERIFIED THE INCIDENT; | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED |  | YES | [15 empty] | STRESS CORROSION CRACKING | [12 empty] | YES | STRESS CORROSION CRACKING | [55 empty] | YES | [6 empty] | YES | [50 empty] | COMBINATION TOOL | 2010 |  |  |  |  | NO |  |  | Yes, but the point of the Accident was not identified as a dig site |  | 2012 | [11 empty] | NO | [63 empty] | WILLIAM MARTIN MULLER | SPECIALIST - PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 2053253863 | 2053253508 |  |  |  | REJI GEORGE | DIRECTOR COMPLIANCE CODES AND STANDARDS | 7134205433 | reji_george@kindermorgan.com | 10/08/2016; 2:06 PM EDST; SNG CONFIRMED A FAILURE HAD OCCURRED ON THE SNG 20-INCH WRENS SAVANNAH 2ND LOOP LINE AT MILEPOST 35 AND CHAIN STATION 9+20. SNG EMPLOYEES ISOLATED THE AFFECTED VALVE SECTION WITH THE UPSTREAM AND DOWNSTREAM MAIN LINE VALVES. PIPE MATERIAL WAS COLLECTED AND SHIPPED FOR LAB ANALYSIS. THE ANALYSIS RESULTS WILL SHOW THE CAUSE OF THE FAILURE TO LIKELY BE STRESS CORROSION CRACKING. THE PIPELINE WAS REPAIRED AND RETURNED TO A DETERMINED LOWER OPERATING PRESSURE, AGREED UPON BY PHMSA, ON 10/17/2016. SNG IS DEVELOPING PLANS TO PRESSURE TEST THE AFFECTED SEGMENT. SNG IS ALSO DEVELOPING PLANS TO INSPECT THE AFFECTED SEGMENT WITH ILI EMAT TOOL.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160087 | 17321 | 2016-10-27 12:58 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2016-09-27 14:53 | 2016 |  |  | 42.3531 | -83.4101 | 1160164 | 2016-09-27 17:41 |  | NATURAL GAS |  | 2637 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-09-28 15:20 | 2016-09-29 07:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-09-27 14:53 | 2016-09-27 15:06 | ONSHORE | MI | 48150 | LIVONIA | WAYNE | MILEPOST | E/HS35 | LINE 1019 | LINE 1019 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTRASTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | PIPE | PIPE BODY | 10 |  | 0.25 | 35000 | API 5L | OTHER | UNKNOWN | UNKNOWN | OTHER | WAX COATING | [27 empty] | 1951 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | YES | METHOD2 | 127 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 7620 | 7825.39083557951 | 53469 | 57901.2190682761 | 145 | 157.019520935496 | 0 | 0 |  |  | 61234 | 34763.201490868 | 65883.6294247911 | [8 empty] | 206 |  | 340 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | YES | NO | NOT MANDATED | [20 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PIPELINE WAS DAMAGED BY A SECOND PARTY CONTRACTOR EXCAVATING NEAR THE PIPELINE. THE CONTRACTOR REALIZE HE MADE CONTACT WITH THE PIPELINE AND IMMEDIATE PRECAUTIONARY MEASURES WE TAKEN AND NOTIFICATION WAS MADE TO THE THE OPERATOR. | [12 empty] | NO |  |  | YES | 4 | 1 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [10 empty] | YES | YES | CITY STREET | [9 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 62631465 |  | UNKNOWN/OTHER | YES | YES | NO |  | DATA NOT COLLECTED |  |  |  | INCIDENT INVESTIGATION UNDERWAY TO DETERMINE INCIDENT CAUSE. | [262 empty] | CARMELLA KING | SENIOR ENGINEER TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 734-513-6256 |  |  |  |  | AMANDA WARD | SR. ENGINEER LEAD - GAS REGULATORY SERVICES | 517-545-8746 | amanda.ward@cmsenergy.com | ON TUESDAY, SEPTEMBER 27, 2016 AT APPROXIMATELY 14:53 A SECOND PARTY CONTRACTOR PERFORMING PIPELINE INTEGRITY WORK DAMAGED A 10" STEEL HIGH PRESSURE PIPELINE AT THE NORTHEAST CORNER OF NEWBURGH ROAD AND JOY ROAD, LIVONIA, MICHIGAN (WAYNE COUNTY). THE CONTRACT CREW HAD THE NORTH SIDE OF THE 10" ST PIPELINE EXPOSED AND WAS EXCAVATING ON THE SOUTH SIDE OF THE PIPE WHEN THE EXCAVATOR MADE CONTACT WITH A 4" ST BY-PASS WELDED TO THE 10" PIPELINE, CAUSING THE WELD TO CRACK AND GAS TO BLOW. IMMEDIATE PRECAUTIONARY MEASURES WERE TAKEN AND NOTIFICATION WAS MADE TO THE OPERATOR. CONSUMERS ENERGY PERSONNEL ARRIVED ONSITE AT APPROXIMATELY 15:06, CONFIRMING THE DAMAGE AND CONTINUED PRECAUTIONARY MEASURES TO PROTECT THE PUBLIC. LOCAL POLICE AND FIRE WERE ONSITE AND THE TRAFFIC ON JOY ROAD WAS BLOCKED AND REMAINED BLOCKED UNTIL THE BLOWING GAS WAS SHUT-DOWN AND REPAIRS TO THE PIPELINE WERE COMPLETE. AT APPROXIMATELY 16:10 A GAS DISTRIBUTION CREW BEGAN DIGGING A SEPARATE EXCAVATION IN PREPARATION FOR INSTALLATION OF A MUELLER CONTROL FITTING TO ISOLATE THE DAMAGED PIPELINE AND MAKE THE NEEDED REPAIRS. THE CONTROL FITTING WAS INSTALLED AND THE VALVING OPERATION WAS COMPLETED ON SEPTEMBER 28, 2016 AT APPROXIMATELY 15:45 STOPPING THE BLOWING GAS. HOWEVER, TRACES OF GAS CONTINUED TO LEAK THROUGH REQUIRING ADDITIONAL STOPPLING AT THE EXISTING CONTROL FITTING. THE PIPELINE SECTION WAS COMPLETELY ISOLATE AT 20:45. REPAIRS TO THE DAMAGED PIPELINE WERE COMPLETED ON SEPTEMBER 29, 2016 AT APPROXIMATELY 05:30 AND THE PIPELINE RETURNED TO NORMAL OPERATIONS AT 07:30.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160088 | 17619 | 2016-11-07 18:30 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2016-10-09 04:02 | 2016 |  |  | 37.6546 | -82.0355 | 1161104 | 2016-10-09 05:45 |  | NATURAL GAS |  | 3083 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-10-09 04:59 | 2016-10-10 11:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-10-09 04:02 | 2016-10-09 04:09 | ONSHORE | WV | 25670 | DELBARTON | MINGO | MILEPOST | BLOWDOWN VLV | GRANT COMPRESSOR STATION | SM-116/SM-123 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1997 |  | CARBON STEEL |  | OTHER | [8 empty] | MALFUNCTION OF THE 4-IN BLOWDOWN VALVE ACTUATOR | CLASS 2 LOCATION | NO |  | 159 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 8571 | 8802.02425876011 | 0 | 0 | 0 | 0 | 0 | 0 | NONE WERE IDENTIFIED |  | 8571 | 9125.45822102426 | 8802.02425876011 | [8 empty] | 936 |  | 1183 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE BLOWDOWN VALVE ACTUATOR ACTIVATION WAS NOT DUE TO ANY INVOLVEMENTS BY GAS CONTROL PERSONNEL. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | IDENTIFIED CLOGGED FILTER IN THE GAS SUPPLY REGULATOR | [161 empty] | MARK NEWMAN | COMPLIANCE SPECIALIST | mark_newman@transcanada.com | (304) 722-8475 |  |  |  |  | LEE ROMACK | MANAGER | (832) 320-5315 | lee_romack@transcanada.com | ON OCTOBER 9TH, 2016, GRANT COMPRESSOR STATION (CS) WAS SUBJECT TO AN UNINTENDED EMERGENCY SHUTDOWN (ESD) EVENT THAT WAS DUE TO A FAULTY 4 INCH BLOWDOWN VALVE ACTUATOR. GRANT IS A TRANSMISSION CS THAT IS OPERATED AND MAINTAINED BY COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA). GRANT CS IS LOCATED IN MINGO COUNTY, NEAR THE TOWN OF DELBARTON, WEST VIRGINIA. AFTER THE UNINTENDED RELEASE OF NATURAL GAS (MATERIAL) INTO ATMOSPHERE INITIATION, THE BLOWDOWN VALVE CONTINUED FLOWING MATERIAL UNTIL IT WAS MANUALLY SHUT CLOSED POSITION. COLUMBIA PERSONNEL INSPECTED THE FACILITY AND SECURED OTHER VALVES UNTIL FURTHER INVESTIGATION STARTS. COLUMBIA'S ENGINEERING SERVICES INVESTIGATED THE EVENT AND CAUSAL ANALYSIS INVESTIGATION INDICATED THAT THE 4 INCH BLOWDOWN VALVE FAILED TO REMAIN SHUT DUE TO A FAULTY ACTUATOR ON THIS VALVE. HENCE, RELEASING MATERIAL INTO ATMOSPHERE. THE AMOUNT OF MATERIAL RELEASED INTO ATMOSPHERE WAS CALCULATED TO BE 3,083 MCF. THE INVESTIGATION TEAM FOUND THAT THE VALVE'S ACTUATOR HAD A FAULTY SIGNAL THAT MAY HAVE INITIATED THE UNINTENDED SIGNAL TO OPEN THE VALVE AND START THE ESD SEQUENCE. SEVERAL COMPONENTS WERE REPLACED INCLUDING BUT NOT LIMITED TO THE RELIEF VALVE, THE REGULATOR (FOR THE POWER GAS SYSTEM) AND A RESETTING TO THE RELIEF VALVE'S SET-POINT TOO. THE VALVES WERE TESTED AND THE FACILITY WAS RETURNED BACK IN SERVICE AND WAS MONITORED THROUGHOUT THE DAY FOR ANY ABNORMAL FUNCTIONALITY OF ANY OF THE INVOLVED COMPONENTS IN THIS INCIDENTS. NO FURTHER ISSUES WERE IDENTIFIED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160089 | 17217 | 2016-11-09 07:39 | ORIGINAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 4720 PIEDMONT ROW DR. | CHARLOTTE | NC | 28210 | 2016-08-02 12:22 | 2016 |  |  | 34.8217 | -79.011 | NRC NOTIFICATION REQUIRED BUT NOT MADE |  |  | NATURAL GAS |  | 1272.88 | 4932.42 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THERE WAS A CONTROLLED RELEASE UNTIL A BYPASS COULD BE INSTALLED. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-08-02 12:20 | 2016-08-02 12:40 | ONSHORE | NC | 28384 | SAINT PAULS | ROBESON | SURVEY STATION NO. | 36015.6518 | LINE 33 | LINE 33 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 3 |  | 0.156 | 35000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | BETHLEHEM STEEL CORP | COAL TAR | [28 empty] | 1959 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 4 | 1.5 | [7 empty] | CLASS 3 LOCATION | YES | METHOD2 | 115 |  | NO | NO | NO |  | 0 | 0 | 11098 | 12017.9492644285 | 2864 | 2941.19676549865 | 10909 | 11813.2824405885 | 76078 | 82384.3525084874 | 0 | 0 |  |  | 100949 | 51805.028084047 | 109156.780979003 | [8 empty] | 470 |  | 718 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 43613 | NO | [5 empty] | YES | DIAMETER TOO SMALL TO ACCOMMODATE TOOLS. | YES |  |  |  |  | YES | DIAMETER TOO SMALL TO ACCOMMODATE TOOLS. | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CAUSE OF INCIDENT WAS THIRD-PARTY DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  | YES | PRIVATE BUSINESS | YES | [6 empty] | CONTRACTOR | GRADER/SCRAPER | DRIVEWAY | NO | [7 empty] | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | FARRIS BERRY | MANAGER - PIPELINE SAFETY | farris.berry@piedmontng.com | 704-731-4618 |  |  |  |  | FARRIS BERRY | MANAGER - PIPELINE SAFETY | 704-731-4618 | farris.berry@piedmontng.com | WHILE GRADING A DRIVEWAY FOR PAVING, A THIRD-PARTY CONTRACTOR HIT AND PUNCTURED THE 3" TRANSMISSION LINE. ONE BUSINESS WAS EVACUATED, BUT NUMBER OF EMPLOYEES AFFECTED IS UNKNOWN. PRIOR NOTIFICATION OF INCIDENT WAS NOT MADE AS IT WAS NOT THOUGHT TO BE REPORTABLE. IT WAS NOT UNTIL FINAL BILLS FROM CONTRACTORS FOR EMERGENCY RESPONSE AND REPAIR WERE RECEIVED THAT IT WAS DETERMINED TO BE REPORTABLE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160090 | 17287 | 2016-11-12 13:44 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2016-10-14 13:17 | 2016 |  |  | 31.3503 | -109.5975 | 1161587 | 2016-10-14 16:16 |  | NATURAL GAS |  | 8490 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELEASE RESULTED FROM A RELIEF VALVE. THE VALVE WAS ISOLATED AND RESET. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-10-14 13:17 | 2016-10-14 13:28 | ONSHORE | AZ | 85607 | Not Within a Municipality | COCHISE COUNTY | MILEPOST | MP 226+1584 | EPNG VALVE 31 REGULATING STATION | LINE 2003 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | RELEASE OF NATURAL GAS THROUGH RELIEF VALVE. | CLASS 1 LOCATION | NO |  | 189 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 25470 | 26156.5229110512 | 500 | 541.446623915504 | 0 | 0 | 0 | 0 |  |  | 25970 | 27366.1932739616 | 26697.9695349667 | [8 empty] | 579.5 |  | 650 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 5 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | KMI NOTIFIED BY THIRD PARTY TECHNICIAN THAT GAS WAS VENTING FROM RELIEF VALVE. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE ROOT CAUSE OF THE INCIDENT INVOLVING THE REPORTABLE RELEASE OF NATURAL GAS WAS A FAILURE OF A NITRILE COMPONENT ON THE MAIN STEM OF THE PILOT VALVE. THIS PREVENTED THE RELIEF VALVE FROM CLOSING WHEN THE PRESSURE DROPPED TO BELOW THE SET-POINT OF 550 PSIG. THE INVESTIGATION CITED THAT THE PILOT VALVE STEM BECAME STUCK PREVENTING IT FROM PROPERLY CLOSING. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES |  |  | YES | [25 empty] | YES | THE RELIEF VALVE FAILED TO CLOSE DUE TO THE FAILURE OF A NITRILE COMPONENT ON TH | [161 empty] | STEPHEN R. DINES | ENGINEER | stephen_dines@kindermorgan.com | (719) 329-5633 |  |  |  |  | REJI GEORGE | DIRECTOR OF ENGINEERING CODES AND STANDARDS | (713) 420-5433 | reji_george@kindermorgan.com | ON 10-14-2016 AT APPROXIMATELY 1:17 PM MST A KINDER MORGAN TECHNICIAN WAS NOTIFIED BY A SOUTHWEST GAS (SWG) TECHNICIAN THAT HE THOUGHT THE EPNG RELIEF VALVE LOCATED AT VALVE 31 NEAR MONUMENT 90 METER STATION WAS VENTING. UPON INVESTIGATION, IT WAS DETERMINED THAT THE PRIMARY REGULATOR ON LINE 2003 NEAR VALVE 31 FAILED TO COMPLETELY CLOSE CAUSING THE DOWNSTREAM PRESSURE TO RISE ABOVE THE RELIEF VALVE SET-POINT OF 550 PSIG. THE RELIEF VALVE ACTUATED AND REDUCED THE LINE PRESSURE AS INTENDED AVOIDING PRESSURES EXCEEDING THE ESTABLISHED MAOP OF DOWNSTREAM FACILITIES, HOWEVER THE RELIEF VALVE FAILED TO CLOSE WHEN THE LINE PRESSURE REACHED THE RELIEF VALVE RESET PRESSURE DUE TO A FAILED INTERNAL SEATING COMPONENT AND RESULTED IN THE RELEASE OF APPROXIMATELY 8.49 MMSCF OF NATURAL GAS. THE AFFECTED REGULATOR AND RELIEF VALVE WERE REPAIRED FOLLOWING THE INCIDENT AND RETURNED TO SERVICE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160091 | 17226 | 2016-11-18 10:45 | SUPPLEMENTAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2016-10-25 03:50 | 2016 |  |  | 32.1511 | -88.8434 | 1162438 | 2016-10-25 06:29 |  | NATURAL GAS |  | 12781 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-10-25 04:07 | 2016-10-25 06:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-10-25 03:50 | 2016-10-25 04:00 | ONSHORE | MS | 39330 | Not Within a Municipality | CLARKE | MILEPOST | MILEPOST 67.2 | ENTERPRISE COMPRESSOR STATION | SOUTH MAIN LINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1959 |  | CARBON STEEL |  | OTHER | [8 empty] | WHILE COMPRESSOR STATION ENGINES WERE RUNNING, OPERATOR ON STATION YARD CONTROL VALVE MALFUNCTIONED AND OPERATION OF STATION BLOW DOWN SYSTEM COMMENCED. | CLASS 1 LOCATION | NO |  | 478 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 36425 | 37406.8059299191 | 3110 | 3367.79800075443 | 1200 | 1299.47189739721 | 0 | 0 |  |  | 40735 | 40923.7342695275 | 42074.0758280708 | [8 empty] | 1100 |  | 1200 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM PERSONNEL WERE AWARE OF THE DROPPING PRESSURE BY ALARM AT THE SAME TIME LOCAL EMPLOYEE WAS TELEPHONING THE CONTROL ROOM PERSONNEL. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | YES | [34 empty] | YES | POSSIBLE SMALL LEAK IN PILOT VALVE OR MANUAL SELECTOR BLOCK COMPONENTS | [161 empty] | WM. MARTIN MULLER | SPECIALSIT - PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 2053253863 | 2053253508 |  |  |  | REJI GEORGE | DIRECTOR COMPLIANCE CODES AND STANDARDS | 7134205433 | reji_george@kindermorgan.com | 10/25/2016; 3:50 AM, EMPLOYEE WHO LIVES NEAR THE COMPRESSOR STATION, AWAKENED BY A NOISE, CALLED GAS CONTROL; EMPLOYEE LEARNS THERE IS AN ESD ALARM AND THE COMPRESSOR STATION IS RUNNING; EMPLOYEE LEAVES HOME TO CHECK THE COMPRESSOR STATION; WHILE IN ROUTE EMPLOYEE CALLS OTHER EMPLOYEES TO COME ASSIST AS NEEDED; EMPLOYEE ARRIVES AT COMPRESSOR STATION AT 3:58 AM AND FINDS ENGINES RUNNING AND THREE STATION YARD BLOW-OFFS VENTING; 4:03 AM GAS CONTROL CONFIRMS OTHER EMPLOYEES ARE IN ROUTE; 4:05 AM ANOTHER EMPLOYEE ARRIVES AT COMPRESSOR STATION; 4:06 AM EMPLOYEES BEGIN TAKING COMPRESSOR ENGINES OFF-LINE; 4:07 AM AS THE FIRST ENGINE WAS BEING TAKEN OFF-LINE, ALL REMAINING ENGINES WERE IMMEDIATELY SHUT DOWN BY THE STATION CONTROL SYSTEM; WITH ALL ENGINES SHUT DOWN, EMPLOYEES BEGIN TO ADJUST VALVES AS NEEDED TO BYPASS STATION; IN DOING SO EMPLOYEES NOTICE TWO 8-INCH STATION YARD BLOW-OFFS HAD STOPPED VENTING; EMPLOYEES FOUND MAIN LINE VALVES IN THE STATION YARD HAD PROPERLY OPENED FOR STATION BYPASS DURING THE EVENT AND NEEDED NO INTERVENTION; 4:25 AM EMPLOYEES CLOSED STATION VALVES WHICH CEASED THE GAS SUPPLY TO A 4-INCH STATION YARD BLOW-OFF; AT THIS TIME, EMPLOYEES THOUGHT THE GAS RELEASE WAS BELOW 3,000 MCF; AS PERSONNEL BECAME AVAILABLE TO CONSULT, MANAGERS DISCUSSED THE EVENT AND DETERMINED THE GAS RELEASE COULD BE A REPORTABLE VOLUME AND BEGAN CONTACTING OTHERS FOR INFORMATION AND REPORTING PURPOSES; 6:29 AM NRC TELEPHONE NOTIFICATION; DURING AND AFTER THE EVENT, CLARKE COUNTY, MISSISSIPPI EMA EMPLOYEES CONTACTED SNG EMPLOYEES CONCERNING THE EVENT AS THEY HAD RECENT TRAINING WITH A SNG EMPLOYEE; THE COMPRESSOR STATION RETURNED TO SERVICE 10/25/2016, 6:30 AM; INVESTIGATION LED TO THE INSTALLATION OF REBUILD KITS IN THE PILOT VALVE AND MANUAL SELECTOR BLOCK OF A CONTROL VALVE OPERATOR AS A SMALL LEAK IN EITHER COMPONENT WOULD HAVE CAUSED THE EVENT; REPAIR ALSO INCLUDED REPLACEMENT OF SAID VALVE OPERATOR'S ESD SWITCH.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160092 | 17359 | 2016-12-05 09:14 | SUPPLEMENTAL FINAL | 30782 | HARVEST PIPELINE COMPANY | 1111 TRAVIS | HOUSTON | TX | 77002 | 2016-11-21 16:30 | 2016 |  |  | 29.7179 | -92.0218 | 1164729 | 2016-11-22 16:00 |  | NATURAL GAS |  | 10 | 4700 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-11-21 16:30 | 2016-11-26 11:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-11-21 16:30 | 2016-11-22 06:00 | ONSHORE | LA | 70510 | Not Within a Municipality | VERMILLION (IN VERMILLION BAY) | MILEPOST | IN VERMILLION | REDFISH GAS PIPELINE | 12" PIPELINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | IN STATE WATERS (WATER DEPTH 10') | 84 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 |  | 0.25 | 42000 | API 5L X42 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | STUPP CORPORATION | OTHER | CONCRETE | [27 empty] | 1967 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 292 |  | NO | NO | NO |  | 0 | 0 | 11000 | 11911.8257261411 | 25 | 25.6738544474394 | 115000 | 124532.723500566 | 0 | 0 | 0 | 0 |  |  | 126025 | 62658.2656852269 | 136470.223081154 | [8 empty] | 800 |  | 1100 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 87101 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | NO | NO | AIR PATROL |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE EFFECT OF THE PINHOLE LEAK ON THE PIPELINE PRESSURE WAS WITHIN NORMAL PRESSURE FLUCTUATION RANGE; THEREFORE NO LARMS WERE GENERATED. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING | [5 empty] | YES | UNKNOWN | YES | [7 empty] | YES | GENERAL LINE PIPE SEGMENT | NO | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | YES |  |  | 2016 | [6 empty] | YES | [53 empty] | TROY S. BROWN | SR. REGULATORY COMPLIANCE SPECIALIST | trbrown@hilcorp.com | 7132892688 |  |  |  |  | TROY S. BROWN | SR. REGULATORY COMPLIANCE SPECIALIST | 7132892688 | trbrown@hilcorp.com | AIR PATROL NOTIFIED PIPELINE OPERATOR OF POSSIBLE BUBBLES IN VICINITY OF PIPELINE. OPERATOR WAS DISPATCHED TO AREA AND DID CONFIRM BUBBLES FROM OUR ROW. SURVEY CREW WAS DISPATCHED TO AREA TO LOCATE PIPELINE, PIPELINE WAS BLOCKED IN AT THE SAME TIME. WORK CREW WAS SET UP TO BLOW DOWN THE PIPELINE. WORK BARGE WAS THEN DISPATCHED TO LEAK SITE AND BEGAN JETTING COVER LOCATE THE LEAK. ONCE LOCATED EXCAVATION AND REPAIR BEGAN. A PLIDCO SPLIT SLEEVE WAS INSTALLED OVER THE PIN HOLE FOR REPAIR.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160093 | 17352 | 2016-12-13 17:41 | SUPPLEMENTAL FINAL | 38987 | KINETICA ENERGY EXPRESS LLC | 1001 MCKINNEY STREET, SUITE 900 | HOUSTON | TX | 77002 | 2016-11-13 17:33 | 2016 |  |  | 29.375 | -92.1314 | 1164025 | 2016-11-14 09:20 |  | NATURAL GAS |  | 541 | 8858 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-11-14 09:00 | 2016-12-15 02:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-11-14 08:25 | 2016-11-14 08:25 | OFFSHORE | [28 empty] | 18 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SOUTH MARSH ISLAND | 220 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 |  | 0.375 | 52000 | 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | KAISER | OTHER | CONCRETE | [27 empty] | 1979 | 1978 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 390 |  | NO | NO | NO |  | 0 | 0 | 25245 | 27337.6400414938 | 1540 | 1581.50943396226 | 150000 | 162433.987174651 | 5000 | 5414.46623915503 | 0 | 0 |  |  | 181785 | 91235.1898802873 | 196767.602889262 | [8 empty] | 776 |  | 1250 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 172181 | NO |  | YES |  | YES |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE WAS BELOW MAOP WITH NO UNUSUAL OPERATING CIRCUMSTANCES AND WAS LOCATED SUBSEA | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  | YES | 6 O'CLOCK POSITION | NO | YES | NOT APPLICABLE - NOT MAINLINE PIPE | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KURT CHERAMIE | SR. DIRECTOR | kurt.cheramie@kineticallc.com | 9852092283 |  |  |  |  | KURT CHERAMIE | SR. DIRECTOR | 9852092283 | kurt.cheramie@kineticallc.com | BUBBLES 6' IN DIAMETER REPORTED TO USCG BY OUTSIDE PARTY ON 11/13. USCG NOTIFIED KINETICA OPERATIONS REGARDING LEAK AT 17:33 ON 11/13. OPERATIONS AND GAS CONTROL VIEWED SCADA BUT DID NOT SEE ANY LOSS OF LINE PRESSURE. OPERATIONS INFORMED USCG THAT MORNING OVERFLIGHT WOULD BE CONDUCTED. 11/14 OVERFLIGHT VERIFIED COORDINATES AND LOCATION OF LEAK IN PROXIMITY TO KINETICA'S PIPELINE. OPERATIONS SHUT-IN PRODUCTION AND CLOSED ONSHORE VALVE TO ISOLATE SEGMENT. DSV MOBILIZED AND ARRIVED ON LOCATION ON 11/15. CONFIRMED PINHOLE LEAK AT 6 O'CLOCK POSITION. PRESSURE NEEDED TO BE REDUCED IN ORDER TO INSTALL REPAIR CLAMP. WHILE REDUCING PRESSURE PRIOR TO INSTALLING CLAMP, WEATHER WORSENED AND WAS NOT CONDUCIVE FOR DIVING OPERATIONS UNTIL 12/13. DIVERS ON LOCATION ON 12/13 TO INSTALL REPAIR CLAMP. WILL SUBMIT SUPPLEMENTAL REPORT UPON COMPLETION OF CLAMP INSTALLATION. REPAIR CLAMP INSTALLED AT 2:00AM ON 11/15. PIPELINE PLACED BACK IN SERVICE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20160094 | 17235 | 2016-12-14 10:41 | ORIGINAL FINAL | 31727 | KINDER MORGAN KEYSTONE GAS STORAGE, LLC | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2016-11-27 08:45 | 2016 |  |  | 31.9831 | -102.9586 | 1165423 | 2016-12-02 13:16 |  | NATURAL GAS |  | 21040 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-11-27 07:10 | 2016-12-02 13:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-11-27 07:00 | 2016-11-27 06:55 | ONSHORE | TX | 79745 | KERMIT | WINKLER | MILEPOST | 0 | KINDER MORGAN KEYSTONE GAS STORAGE | SITE ID 1015 UNIT C3 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2004 |  | CARBON STEEL |  | LEAK |  |  | OTHER | LEAK THRU FAILED RELIEF VALVE | [5 empty] | CLASS 1 LOCATION | NO |  | 330 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 46221 | 47466.8490566038 | 1581 | 1712.05422482082 | 0 | 0 | 0 | 0 |  |  | 47802 | 49996.9158007302 | 49178.9032814246 | [8 empty] | 750 |  | 1900 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS CONTROL PERSONNEL HAD TAKEN NO ACTION PRIOR TO THE EVENT AND THE PRESSURES WERE WITHIN NORMAL OPERATING RANGES. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | RELIEF VALVE INTERNAL COMPONENTS FAILED | [161 empty] | KENNETH PETERS | SR ENGINEER | ken_peters@kindermorgan.com | 2053257554 | 2053253508 |  |  |  | REJI GEORGE | DIRECTOR CODES STANDARDS | 7134205433 | reji_george@kindermorgan.com | ON NOVEMBER 27, 2016 WHEN KINDER MORGAN KEYSTONE GAS STORAGE (KMKGS) PERSONNEL ARRIVED AT THE SITE FOR WORK, A CHECK OF THE GAS BALANCE BETWEEN GAS COMING INTO THE COMPRESSOR STATION AND GAS GOING INTO STORAGE REVEALED A 20 MMCF SHORTFALL GOING INTO STORAGE. IT WAS DETERMINED THAT A RELIEF VALVE BETWEEN STAGE 1 COMPRESSION AND STAGE 2 COMPRESSION ON UNIT 3C HAD FAILED, LEAKING GAS OUT THROUGH ITS VENT STACK. THE RELIEF VALVE WAS REPAIRED AND WAS ULTIMATELY PLACED BACK INTO SERVICE WITH UNIT 3C DECEMBER 2, 2016.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160095 | 17257 | 2016-12-14 16:19 | SUPPLEMENTAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2016-11-28 06:35 | 2016 |  |  | 33.0614 | -83.0549 | 1165037 | 2016-11-28 09:35 |  | NATURAL GAS |  | 41058 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELEASE OF GAS WAS ABLE TO BE ISOLATED WITHOUT FACILITY SHUTDOWN. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-11-28 06:35 | 2016-11-28 06:35 | ONSHORE | GA | 31061 | MILLEDGEVILLE | BALDWIN | MILEPOST | 420.2 | HALL GATE COMPRESSOR STATION | UNIT NO. 3 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | SOLENOID FOR SUCTION VALVE | 2004 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | SEAT FOR PILOT IN SOLENOID WAS BAD. | OTHER | [8 empty] | GAS RELEASE DUE TO SOLENOID FAILURE | CLASS 1 LOCATION | NO |  | 382 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 89917 | 92340.6388140162 | 6000 | 6497.35948698604 | 0 | 0 | 0 | 0 |  |  | 95917 | 98716.1926029032 | 98837.9983010022 | [8 empty] | 892 |  | 1200 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS CONTROL PERSONNEL HAD TAKEN NO RECENT ACTION RELATIVE TO THIS STATION'S OPERATION. MOREOVER, PRESSURES REMAINED WITHIN NORMAL OPERATIONAL LIMITS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | SEAT FOR THE PILOT IN A SOLENOID WAS BAD. | [15 empty] | YES | SOLENOID SEAT FAILURE LIKELY DUE TO DEBRIS GETTING THROUGH THE FILTER. | [161 empty] | KENNETH PETERS | SR ENGINEER | ken_peters@kindermorgan.com | 2053257554 | 2053253508 |  |  |  | REJI GEORGE | DIRECTOR CODES STANDARDS | 7134205433 | reji_george@kindermorgan.com | KINDER MORGAN SOUTHERN NATURAL GAS (SNG) COMPANY GAS CONTROL PERSONNEL RECEIVED A UNIT MALFUNCTION ALARM FOR HALL GATE COMPRESSOR STATION (BALDWIN COUNTY, GA) ON NOVEMBER 28, 2016. UPON ARRIVAL AT THE STATION BY LOCAL SNG OPERATIONS EMPLOYEE, IT WAS DETERMINED THAT GAS WAS BLOWING THROUGH THE SUCTION VALVE OF UNIT NO. 3, RELEASING SAFELY THROUGH THE UNIT VENT VALVE AND OUT THE STATION'S BLOWDOWN PIPING. EMPLOYEE ISOLATED THE SOURCE AND STOPPED THE NATURAL GAS RELEASE. INVESTIGATION RESULTED IN THE PROBABLE CAUSE BEING FAILURE OF THE SEAT FOR THE PILOT IN A SOLENOID THAT CAUSED UNIT NO. 3 SUCTION VALVE TO OPEN, RELEASING GAS. A CONTRIBUTING FACTOR TO THE SOLENOID SEAT FAILURE IS LIKELY DEBRIS THAT GOT INTO THE SYSTEM. VERY SMALL PARTICLES, LESS THAN 25 MICRONS, CAN GET THROUGH THE FILTER AND CAUSE FAILURE/LEAKAGE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160096 | 17306 | 2016-12-19 13:01 | SUPPLEMENTAL FINAL | 2620 | COLUMBIA GULF TRANSMISSION, LLC | BANK OF AMERICA CENTER - 700 LOUISIANA STREET | HOUSTON | TX | 77252 | 2016-11-25 15:35 | 2016 |  |  | 29.6923 | -91.376 | 1164905 | 2016-11-25 16:38 |  | NATURAL GAS |  | 982 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-11-25 15:35 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-11-25 15:35 | 2016-11-25 15:35 | ONSHORE | LA | 70392 | PATTERSON | ST. MARYS | SURVEY STATION NO. | EL100-007 | PIPELINE | EL-100 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | NAVIGABLE WATERWAY |  |  | YES | [6 empty] | YES | UNCASED | WAX LAKE OUTLET | 90 | BELOW WATER, PIPE ON OR ABOVE BOTTOM | [11 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.5 | 42000 | API-5LX | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | NATIONAL TUBE CO. | OTHER | SOMASTIC COATING UNDERNEATH CONCRETE COATED | [27 empty] | 1954 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 438 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 2622 | 2692.67385444744 | 0 | 0 | 0 | 0 | 1500000 | 1624339.87174651 | COSTS ASSOCIATED WITH THE ABANDONMENT AND REMOVAL OF EL100 IN WAX LAKE OUTLET |  | 1502622 | 748406.479566781 | 1627032.54560096 | [8 empty] | 32 |  | 877 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 967 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS CONTROL WERE NOT MANIPULATING ANY VALVES OR WERE INVOLVED IN ANY OTHER OPERATIONAL ACTIVITY THAT MAY HAVE CONTRIBUTED IN THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION | [6 empty] | YES | THE POINT OF FAILURE WAS SUBJECT TO EXTERNAL CORROSION DUE TO A COMBINATION OF ITEMS SUCH AS LOCALIZED PITTING, COATING DAMAGE, AND ENVIRONMENTAL FACTORS. |  |  | YES | YES |  |  | NO | [11 empty] | YES | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | CODY BOWERS | U.S. REGULATORY COMPLIANCE SPECIALIST | cody_bowers@transcanada.com | 304-550-8163 |  |  |  |  | HOWARD ROMACK | MANAGER - U.S. REGULATORY COMPLIANCE | 832-584-3178 | lee_romack@transcanada.com | ON NOVEMBER 24, 2016, AN OFFICER WITH THE LOCAL SHERIFF'S DEPARTMENT, CONTACTED COLUMBIA GULF TRANSMISSION, LLC (COLUMBIA) OPERATIONS PERSONNEL TO REPORT THE SIGHTING OF BUBBLES IN THE WAX LAKE OUTLET, ST. MARY PARRISH, IN THE STATE OF LOUISIANA. THE LOCATION OF THESE BUBBLES WERE EMANATING IN THE PROXIMITY OF COLUMBIA'S LINE EL-100 AS WELL AS OTHER PIPELINE OPERATORS IN THE REGION. DUE TO THE VARIOUS CROSSING OF PIPELINES ALONG THE RIVER, THE INITIAL ASSUMPTION WAS THAT THE SOURCE OF THESES BUBBLES OF UNINTENDED RELEASE WAS FROM ANOTHER PIPELINE OPERATOR OTHER THAN COLUMBIA. COLUMBIA OPERATES AND MAINTAINS A SYSTEM OF PIPELINES IN THE AREA. HOWEVER, IT WAS IDENTIFIED THAT THESE RIVER CROSSINGS WERE ABANDONED BACK IN THE EARLY 80'S AND WERE KEPT IN IDLE STATUS WITH ABOUT 32 PSIG BLANKET PRESSURE. UPON FURTHER INVESTIGATION AND DISCUSSIONS WITH OTHER OPERATORS WHO DO HAVE PIPELINES CROSSING THE RIVER, IT WAS RULED OUT THAT THEIR PIPELINES WERE NOT INVOLVED IN THIS RELEASE. HENCE, COLUMBIA IDENTIFIED THAT THESE BUBBLES WERE EMANATING FROM COLUMBIA'S LINE EL-100. THEREAFTER, THE NATIONAL RESPONSE CENTER (NRC) WAS NOTIFIED. THE REPORT TO THE NRC WAS MADE DUE TO THE EXPECTED COST TO ABANDON AND REMOVE LINE EL-100 SECTIONS OF PIPELINE CROSSING THE WAX LAKE OUTLET WOULD EXCEED $50,000. THE UNINTENDED RELEASE OF MATERIAL DID NOT EXCEED 3,000 MCF. PLANS WERE SET FORTH TO ABANDON AND REMOVE THIS SECTION OF PIPELINE IN A TIMELY MANNER. AFTER REMOVING THE FAILED SECTION OF LINE EL-100 FROM THE RIVER, AN ENGINEERING ASSESSMENT WAS CONDUCTED TO THE FAILED SECTION OF LINE EL-100 BY A METALLURGICAL FAILURE ANALYSIS CONSULTANT. THE ASSESSMENT CONCLUDED THAT THE FAILED SECTION WAS LIKELY SUBJECT TO LONGITUDINAL AND BENDING STRESSES IN CONJUNCTION WITH WALL LOSS DUE TO EXTERNAL CORROSION AT THE 6 O'CLOCK POSITION. THIS RIVER-CROSSING SECTION OF LINE EL-100 WILL NOT BE REPLACED OR RETURNED BACK TO SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20160097 | 17520 | 2016-12-31 13:05 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2016-12-03 14:15 | 2016 |  |  | 37.1268 | -120.2607 | 1165501 | 2016-12-03 17:36 |  | NATURAL GAS |  | 3500 | 100 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-12-03 18:20 | 2016-12-07 14:55 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-12-03 14:15 | 2016-12-03 14:34 | ONSHORE | CA | 93610 | CHOWCHILLA | MADERA | MILEPOST | MP 29.18 | LINE 118B | 147 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 |  | 0.219 | 42000 | API 5L X-42 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | ASPHALT | [28 empty] | 1962 | 1962 | CARBON STEEL |  | MECHANICAL PUNCTURE | 1 | 3 | [7 empty] | CLASS 3 LOCATION | YES | METHOD2 | 166 |  | NO | NO | NO |  | 0 | 0 | 450 | 487.301961523953 | 9500 | 9756.06469002695 | 92000 | 99626.1788004526 | 0 | 0 | 0 | 0 | N/A |  | 101950 | 56069.2846034808 | 109869.545452004 | [8 empty] | 380 |  | 400 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 9082 | NO | YES | YES | YES | YES |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM OPERATED AS INTENDED | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  | YES | PRIVATE LANDOWNER | [7 empty] | CONTRACTOR | GRADER/SCRAPER | GRADING | NO | [5 empty] | NO |  | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | STEPHEN RAMOS | GAS ENGINEER | s3rc@pge.com | 925-413-7311 |  |  |  |  | SUSIE RICHMOND | MANAGER REGULATORY COMPLIANCE | 925-328-5776 | gsr8@pge.com | ON DECEMBER 3, 2016 AT APPROXIMATELY 1415 HOURS, PG&E WAS NOTIFIED OF A THIRD-PARTY DIG IN ON LINE 118B AT APPROXIMATELY MILE POINT 29.18. THE NEAREST ADDRESS IS 4 KINGS AVE, CHOWCHILLA. LASER PRECISION LAND LEVELING WAS GRADING LAND WITH A SCRAPER AND PUNCTURED THE LINE. THE EXCAVATOR DID NOT HAVE A USA NOTIFICATION. PG&E GAS SERVICE REPRESENTATIVE ARRIVED ON-SITE AT 1434 HOURS. THE FLOW OF GAS WAS STOPPED BY CLOSING VALVES AND ISOLATING THE DAMAGED LINE. REPAIRS WERE COMPLETED AND THE LINE WAS RESTARTED BY 12/7/16 AT 1455 HOURS. THERE WERE NO GAS SERVICE INTERRUPTIONS TO CUSTOMERS. POLICE AND FIRE DEPARTMENT WERE REPORTED ON SITE. THERE WERE NO REPORTS OF INJURY, IGNITION, OR MEDIA. THIS INCIDENT IS BEING REPORTED TO DOT AND THE CPUC DUE TO DAMAGES ESTIMATED TO EXCEED $50K, AND THE LOSS OF GAS EXCEEDING 3 MILLION CUBIC FEET.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170001 | 31846 | 2017-01-11 08:03 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2016-12-12 15:07 | 2016 |  |  | 41.5129 | -77.9845 | 1166219 | 2016-12-12 16:01 |  |  |  | 6654 | 542384 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-12-12 15:07 | 2019-02-27 12:00 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 0 | 2016-12-12 15:07 | 2016-12-12 15:07 | ONSHORE | PA | 16720 | AUSTIN | POTTER COUNTY | MILEPOST | MP 203.54 | STATION 535 | 20" HEADER | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 72 |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 20 |  | 0.5 | 52000 | API 5L | SEAMLESS |  | NATIONAL TUBE | COAL TAR | [28 empty] | 1964 | 1963 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 600 | 20 |  | CLASS 1 LOCATION | NO |  | 478 |  | NO | NO | NO |  | 0 | 0 | 2021388 | 2188947.41644662 | 24752 | 25419.1698113208 | 64000000 | 69305167.8611844 | 0 | 0 | 0 | 0 |  |  | 66046140 | 32844038.6232394 | 71519534.4474424 | [8 empty] | 1085 |  | 1200 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | GENERAL CORROSION |  |  | YES |  |  | YES | SALT WATER CORROSION | YES | YES |  |  | YES | [5 empty] | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NO | [168 empty] | NO | [63 empty] | NO |  |  | Yes, and an investigative dig was cunducted at the point of the Accident | 2015 | [12 empty] | YES |  |  | 2015 | 2015 | [5 empty] | YES | YES | [52 empty] | MARK CLARKE | SENIOR ENGINEER | mark.clarke@williams.com | 7132153051 |  |  |  |  | CLINT RATKE | MANAGER PIPELINE SAFETY | 9185736724 | clint.ratke@williams.com | TIMELINE FOR TRANSCO STATION 535 INCIDENT: 12/12/2016 ALL TIMES ARE EST 3:07 PM: 20 GAS PIPELINE LEADING TO DEHYDRATORS EXPERIENCES A FAILURE RESULTING IN A RUPTURE AND FIRE. 3:08 PM: PLANT PERSONNEL ESD THE STATION AND PERSONNEL EVACUATE TO MUSTER POINT 3:11 PM: LOCAL FIRE DEPARTMENTS RECEIVED NOTIFICATION 3:15 PM: LOCAL RESPONDERS DISPATCHED 3:17 PM: WILLIAMS SECURITY OPERATIONS CENTER NOTIFIED. 3:40PM: LOCAL FIRE DEPARTMENT ARRIVE 4:00 PM: NRC NOTIFICATION COMPLETED 4:30 EMERGENCY SERVICES CONTROLLING FROM OUTSIDE FENCE AND ALL OPERATIONS PERSONNEL ACCOUNTED FOR AND NO REPORTED INJURIES. 6:55PM: MAIN FIRE EXTINGUISHED AND LINES AFFECTED ISOLATED, FUEL GAS LINE WAS CONTROLLED BURN AND DECISION WAS MADE TO LET IT BURN OVERNIGHT. 8:23PM: LOCAL FIRE DEPARTMENTS LEAVE SITE 12/13/2016 APPROXIMATE 11:00: FIRE FROM FUEL GAS LINE EXTINGUISHED. ADDITIONAL INFORMATION / ADDITIONAL ROOT CAUSES: THE INCIDENT INVESTIGATION AND ASSOCIATED ANALYSIS PROVIDED THE CONCLUSION THAT INTERNAL CORROSION CAUSED THE PIPING RUPTURE. THINNING OF THE PIPE WALL WAS CAUSED BY SALT WATER CORROSION, ULTIMATELY LOWERING RUPTURE RESISTANCE. ON NOVEMBER 19, 2015, EMPLOYEES AT STATION 535 DISCOVERED GAS LEAKING UP THROUGH THE GROUND IN THE STATION YARD AND UPON FURTHER INVESTIGATION DETERMINED THE SOURCE TO BE THE 20 INCH UNDERGROUND LINE ON THE INLET SIDE OF STATION'S DEHYDRATION. THIS LINE WAS BLOWN DOWN AND TAKEN OUT OF SERVICE AS PLANS WERE PUT INTO PLACE FOR REPAIRS. IT WAS IMMEDIATELY CONFIRMED THAT THE LEAK WAS CAUSED BY INTERNAL CORROSION. THE REPAIR CONSISTED OF REMOVING CORRODED PIPING UNTIL PIPING OF SUFFICIENT INTEGRITY WAS FOUND TO TIE NEW PIPING BACK INTO. THIS REPAIR WORK WAS ALSO USED AS AN OPPORTUNITY TO REMOVE DEAD HEADS AND OTHER PIPING IN THE IMMEDIATE VICINITY THAT WERE NO LONGER USED OR NOT NEEDED FOR THE PROCESS. THE STATION WAS OUT OF SERVICE FOR APPROXIMATELY 6 WEEKS IN AN EFFORT TO IDENTIFY AND REPAIR AREAS OF CONCERN. IT WAS RECOGNIZED THAT ADDITIONAL DEAD HEADS EXISTED IN THE STATION AND A PROJECT WAS PLANNED FOR 2016 TO INVESTIGATE OTHER POTENTIAL DEAD HEADS FOR INTERNAL CORROSION. THE 2016 PROJECT WAS DELAYED TO COINCIDE WITH A COMPREHENSIVE PLANNED MECHANICAL INTEGRITY ASSESSMENT OF THE STATION VESSELS AND BELOW GROUND PIPING IN 2017. THE UNDERGROUND PIPING IN THE YARD AND ABOVE GROUND HEADERS HAVE BEEN REPLACED. A FEW PIPES CONNECTING TO NATIONAL FUEL GAS WERE INSPECTED AND LEFT IN PLACE. THE DEHYDRATORS HAVE BEEN REMOVED AND REPLACED. FILTER SEPARATORS HAVE BEEN INSPECTED. GAS WAS INJECTED INTO THE SYSTEM ON 02/27/2019.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170002 | 17408 | 2017-01-11 11:52 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2016-12-19 03:20 | 2016 |  |  | 35.0242 | -87.7576 | 1166707 | 2016-12-19 04:57 |  | NATURAL GAS |  | 24861 | 1755 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | COMPRESSOR STATION WAS NOT ON LINE AT THE TIME OF THE EVENT | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-12-19 03:20 | 2016-12-19 03:50 | ONSHORE | TN | 38452 | Not Within a Municipality | WAYNE | MILEPOST | MP 10, 1480' | TGP STATION 555, COLLINWOOD COMPRESSOR STATION | 500 SYSTEM | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1960 |  | CARBON STEEL |  | OTHER | [8 empty] | WEATHER - FROZEN VALVE OPERATOR GEAR BOX ON VALVE AD-1 | CLASS 1 LOCATION | NO |  | 760 |  | NO | NO | NO |  | 0 | 0 | 4390 | 4753.90135797812 | 62155 | 63830.3369272237 | 0 | 0 | 250 | 270.723311957752 | 0 | 0 |  |  | 66795 | 68482.2439327681 | 68854.9615971596 | [8 empty] | 621 |  | 936 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | WEATHER - FROZEN VALVE OPERATOR GEAR BOX ON VALVE AD-1 | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | NO | [306 empty] | WILLIAM MARTIN MULLER | SPECIALIST - PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 2053253863 | 2053253674 |  |  |  | REJI GEORGE | DIRECTOR COMPLIANCE CODES AND STANDARDS | 7134205433 | reji_george@kindermorgan.com | 12/19/2016; TGP STATION 555 IS OFF LINE; 3:20 AM, A FAULT OCCURRED IN "B" BUILDING RESULTING WITH AN ESD OF STATION 555 YARD PIPING; NOTIFIED BY GAS CONTROL, COMPANY EMPLOYEES ARRIVED AT STATION 555 AT 3:50 AM AND BEGAN CLOSING VALVES; VALVE AD-1 FOUND NOT CLOSED FOLLOWING ESD FUNCTION; WITH THE COLD WEATHER, FREEZING WATER IN VALVE OPERATOR GEAR BOX OF VALVE AD-1 ALLOWED REPORTABLE VOLUME OF NATURAL GAS RELEASED TO ATMOSPHERE. VALVE AD-1 WAS CLOSED AT 4:05 AM. GREASE WAS PLACED IN THIS GEAR BOX AS WELL AS THOSE OF OTHER APPLICABLE VALVES TO PREVENT SIMILAR EVENTS IN THE FUTURE. (PIR CALCULATED ON 36-INCH PIPE)
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170003 | 17263 | 2017-01-12 09:30 | SUPPLEMENTAL FINAL | 31531 | ONEOK WESTEX TRANSMISSION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2016-12-14 14:28 | 2016 |  |  | 31.9892 | -102.4847 | 1166388 | 2016-12-14 15:20 |  | NATURAL GAS |  | 12890 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE COMPRESSOR STATION WAS NOT RUNNING AT THE TIME OF THE INCIDENT. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-12-14 12:59 | 2016-12-14 12:59 | ONSHORE | TX | 79741 | Not Within a Municipality | ECTOR | MILEPOST | MP 0.00 | ONEOK WESTEX RED RIVER PIPELINE | ECTOR COUNTY COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2016 |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENDED OPENING OF VALVES. | CLASS 1 LOCATION | NO |  | 476 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 47693 | 48978.525606469 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 47693 | 50778.2614555256 | 48978.525606469 | [8 empty] | 903 |  | 1188 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | YES | ESD SYSTEM VALVES DID NOT COMPLETELY CYCLE. PLC PROGRAM DID NOT INCLUDE A MANUAL RESET IN THE EMERGENCY SHUTDOWN LOGIC THAT WOULD HAVE ASSURED A COMPLETE CYCLING OF STATION ESD VALVES. | [22 empty] | YES | PLC PROGRAM DID NOT INCLUDE A MANUAL RESET IN THE EMERGENCY SHUTDOWN LOGIC THAT | [161 empty] | PATRICK VAUGHAN | MANAGER REGULATORY COMPLIANCE | pat.vaughan@oneok.com | 9185887734 | 9185915032 |  |  |  | WESLEY DUNBAR | VP NATURAL GAS PIPELINE OPERATIONS | 9185887424 | wesley.dunbar@oneok.com | ON 12/14/2016, AT THE RECENTLY CONSTRUCTED ECTOR COUNTY COMPRESSOR STATION, THE STATION EMERGENCY SHUTDOWN SYSTEM BLOW-DOWN VALVES OPENED UNEXPECTEDLY ALLOWING RELEASE OF NATURAL GAS TO THE STATION VENT LINE. GAS VENTED FOR AROUND 33 MINUTES UNTIL STATION ISOLATION VALVES WERE CLOSED TO SHUT OFF THE FLOW OF GAS FROM THE RED RIVER PIPELINE ALLOWING 12.89 MMCF TO VENT TO ATMOSPHERE. PARTIAL OPERATION OF THE VALVES HAS BEEN ATTRIBUTED TO A MOMENTARY LOSS OF OUTPUT FROM A DIGITAL OUTPUT CARD ON THE STATION PLC TO THE VALVES. THE STATION PLC PROGRAM WAS REVISED TO PREVENT THE RECURRENCE OF A PARTIAL ESD. ONEOK PERSONNEL FIRST BECAME AWARE OF GAS VENTING THROUGH THE STATION BLOW DOWN SYSTEM AT 12:59 PM. IT WASN'T UNTIL 14:28 THAT IT WAS DETERMINED THAT THE GAS RELEASE HAD EXCEEDED 3,000 MCF. DIFFICULTY IN ESTIMATING THE FLOW RATE DUE TO THE STATION BLOW DOWN PIPING CONFIGURATION WAS THE PRIMARY CAUSE OF THE DELAY.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170004 | 17261 | 2017-01-12 17:44 | ORIGINAL FINAL | 14210 | OKLAHOMA NATURAL GAS COMPANY, A DIVISION OF ONE GAS, INC. | 401 N. HARVEY AVE | OKLAHOMA CITY | OK | 73102 | 2016-12-14 15:12 | 2016 |  |  | 35.5419 | -97.3956 | 1166413 | 2016-12-14 16:07 |  | NATURAL GAS |  | 6431 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-12-14 21:01 | 2016-12-15 01:27 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 1 | 2016-12-14 15:12 | 2016-12-14 15:12 | ONSHORE | OK | 73141 | OKLAHOMA CITY | OKLAHOMA | SURVEY STATION NO. | 388.5 + 00 | A-455 NORTH | NONE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8.625 |  | 0.188 | 24000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1948 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 4.5 | 4.5 | [7 empty] | CLASS 2 LOCATION | NO |  | 95 |  | NO | NO | NO |  | 45000 | 48730.1961523953 | 0 | 0 | 26065 | 26767.5606469003 | 9334 | 10107.7255752546 | 11728 | 12700.1720105621 | 0 | 0 |  |  | 92127 | 60589.0182421118 | 98305.6543851123 | [8 empty] | 231 |  | 255 | 192.619(A)(4) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 4229 | NO | YES | YES | YES |  |  |  |  | YES |  |  |  |  | YES | NOT PIGGABLE. | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE WAS THE RESULT OF 2ND PARTY DAMAGE. | [12 empty] | NO |  |  | YES | 2 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [10 empty] | NO |  |  | YES | PRIVATE EASEMENT | [7 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 16120817532454 |  | CONTRACT LOCATOR | NO | YES | YES | 24 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | IMPROPER BACKFILLING | [263 empty] | RANDY BLAIR JR | SUPERVISOR TRANSMISSION | randy.blair@onegas.com | 405-388-5239 |  |  |  |  | SEAN BLAIR | DIRECTOR - ENGINEERING | 405-530-2560 | sean.blair@onegas.com | ONG CONTRACTOR DAMAGED ONG'S 8 INCH STEEL TRANSMISSION LINE WHILE BACKFILLING A NEWLY CONSTRUCTED 12 INCH STEEL LINE. THE DAMAGED LINE RUNS PARALLEL TO THE NEWLY CONSTRUCTED LINE. REPAIRS WERE COMPLETED AND SERVICE TO THE ONE IMPACTED CUSTOMER WAS RESTORED THE FOLLOWING DAY.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170006 | 17456 | 2017-01-17 11:47 | SUPPLEMENTAL FINAL | 2564 | COLORADO INTERSTATE GAS CO | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2016-12-18 09:15 | 2016 |  |  | 37.115 | -102.1835 | 1166663 | 2016-12-18 10:04 |  | NATURAL GAS |  | 4000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-12-18 08:35 | 2016-12-19 12:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-12-18 08:35 | 2016-12-18 08:35 | ONSHORE | CO | 81090 | Not Within a Municipality | BACA | MILEPOST | MP 4, 3993FT. | FLANK CS UNIT CG5; STATION 4940 | CIG LINE 119A | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COOLER OR HEATER | [38 empty] | 1993 |  | CARBON STEEL |  | OTHER | [8 empty] | SEVERE COLD WEATHER, -15 DEGREES, CAUSED GAS COOLER TO FREEZE ALLOWING RELIEF VALVE TO VENT; MAOP NOT EXCEEDED; | CLASS 1 LOCATION | NO |  | 140 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 10000 | 10269.5417789757 | 0 | 0 | 250 | 270.723311957752 | 0 | 0 |  |  | 10250 | 10771.1694132611 | 10540.2650909335 | [8 empty] | 729 |  | 935 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE GAS COOLER, RELATED PIPING, AND RELIEF VALVE SERVING UNIT CG5 IS NOT MONITORED BY SCADA NOR THE CONTROL ROOM. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | YES |  |  |  | YES | EXTREME LOW TEMPERATURE COLD FRONT; -15 DEGREES F EXPERIENCED; | [301 empty] | WILLIAM MARTIN MULLER | SPECIALIST-PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 2053253863 | 2053253764 |  |  |  | REJI GEORGE | DIRECTOR COMPLIANCE CODES AND STANDARDS | 7134205433 | reji_george@kindermorgan.com | 12/18/2016, 08:35 HOURS MOUNTAIN, EMPLOYEE ARRIVED ON SITE AND BEGAN MAKING INSPECTIONS AND FOUND A RELIEF VALVE VENTING TO ATMOSPHERE. APPROPRIATE VALVES WERE IMMEDIATELY CLOSED AND COMPRESSOR UNIT WAS SHUT DOWN. VENTING WAS TERMINATED. INVESTIGATION FOUND THE GAS COOLER FOR UNIT CG5, WHICH IS COMPRESSING UNPROCESSED WET GAS, HAD FROZEN DURING THE EXTREME WEATHER TEMPERATURES OF -15 DEGREES CAUSING THE RELIEF VALVE TO OPEN. MAOP WAS NOT EXCEEDED. 12/18/2016, 09:15 HOURS MOUNTAIN, IT WAS DETERMINED THE GAS RELEASE VOLUME WAS A REPORTABLE VOLUME. WITH THE UNIT OFF LINE, A BYPASS LINE WAS OPENED TO ALLOW THE GAS COOLER TO THAW. PIPING AND EQUIPMENT WAS COVERED TO PROVIDE WINTER WEATHER PROTECTION TO ASSIST THAWING. THE UNIT CG5 WAS RETURNED TO SERVICE 12/19/2016 AT 12:00 HOURS MOUNTAIN. FURTHER ANALYSIS OF DATA INDICATES VENTING BEGAN 12/17/2016, 17:31 HOURS MOUNTAIN. AT THE TIME OF THIS EVENT AND PRIOR TO THE EVENT, THIS PORTION OF THE FACILITY WAS NOT CONTROL ROOM MONITORED. FOLLOWING THIS EVENT, CIG HAS INSTALLED MONITORING ON THE VENT OF THE RELIEF VALVE AND RELATED CONTROL ROOM ALARMS HAVE BEEN INSTALLED; ALL TO ALERT OPERATIONS PERSONNEL OF ANY FUTURE VENTING EVENT.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20170007 | 31563 | 2017-01-25 11:25 | SUPPLEMENTAL FINAL | 15350 | PEOPLES NATURAL GAS COMPANY LLC | 375 NORTH SHORE DRIVE SUITE 600 | PITTSBURGH | PA | 15212 | 2016-12-26 13:54 | 2016 |  |  | 40.8014 | -79.3515 | 1167205 | 2016-12-26 14:52 |  | NATURAL GAS |  | 69.6 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-12-26 15:09 | 2017-09-28 12:40 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2016-12-26 13:54 | 2016-12-26 14:12 | ONSHORE | PA | 16201 | COWANSHANNOCK | ARMSTRONG | SURVEY STATION NO. | G259 0+00 | ST-430 VILLAGE COMPRESSOR | G226 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 1974 |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 2 LOCATION | NO |  | 660 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 161 | 165.339622641509 | 400000 | 433157.299132403 | 6655 | 7206.65456431535 | 0 | 0 |  |  | 406816 | 202310.089651111 | 440529.29331936 | [8 empty] | 38 |  | 40 | 192.619(A)(4) |  |  |  | PRESSURE DID NOT EXCEED MAOP | YES | NO | NOT MANDATED | [20 empty] | TYPE B GATHERING | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT DID NOT OCCUR DUE TO A LACK OF OVERSIGHT FROM THE SCADA OPERATORS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [13 empty] | APPURTENANCE FAILURE |  | THREADED FITTING |  |  |  |  | YES | [177 empty] | WAYNE DADIG | MANAGER PROCESS WORK MANAGEMENT | wayne.dadig@peoples-gas.com | 412-258-4604 |  |  |  |  | PAUL BECKER | VICE PRESIDENT CONSTRUCTION | 412-258-4406 | paul.becker@peoples-gas.com | THERE WAS A FIRE AT THE VILLAGE COMPRESSOR STATION AT APPROXIMATELY 1:55 PM ON MONDAY, DECEMBER 26, 2016. NO EMPLOYEES WERE IN THE COMPRESSOR STATION AT THE TIME OF THE INCIDENT. NO ONE WAS INJURED. THE COMPRESSOR STATION AND THE COMPRESSOR ENGINE WERE DESTROYED. CURRENTLY, PEOPLES NATURAL GAS IS CONDUCTING A ROOT CAUSE ANALYSIS BY AN INDEPENDENT THIRD PARTY INVESTIGATOR. PLANS ARE BEING MADE TO REMOVE WHAT IS LEFT OF THE EXISTING STRUCTURE AND THEN REBUILD THE STRUCTURE AND REPLACE THE ENGINE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170008 | 17472 | 2017-01-25 11:34 | SUPPLEMENTAL FINAL | 38987 | KINETICA ENERGY EXPRESS LLC | 1001 MCKINNEY STREET, SUITE 900 | HOUSTON | TX | 77002 | 2016-12-26 14:30 | 2016 |  |  | 28.5757 | -91.97 | 1167217 | 2016-12-26 17:58 |  | NATURAL GAS |  | 8986 | 276 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-12-27 10:45 | 2017-02-22 06:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-12-26 17:58 | 2016-12-27 10:45 | OFFSHORE | [28 empty] | 150 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SOUTH MARSH ISLAND | 75 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | FLANGE ASSEMBLY | [38 empty] | 1977 |  | CARBON STEEL |  | LEAK |  |  | OTHER | O-RING | [5 empty] | CLASS 1 LOCATION | NO |  | 732 |  | NO | NO | NO |  | 0 | 0 | 786 | 851.154092795172 | 25610 | 26300.2964959569 | 400000 | 433157.299132403 | 5000 | 5414.46623915503 | 0 | 0 |  |  | 431396 | 228973.426603499 | 465723.21596031 | [8 empty] | 815 |  | 1250 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 35798 | NO |  |  | YES |  |  | YES | OFFSHORE PLATFORM TO SUB-SEA TIE-IN | YES |  |  | YES |  | YES | OFFSHORE PLATFORM TO SUB-SEA TIE-IN | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE WAS BELOW MAOP WITH NO UNUSUAL OPERATING CIRCUMSTANCES | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | O-RING | [17 empty] | YES | DETERIORATION OF METAL O-RING OVER TIME. NEW O-RING INSTALLED 2/22/17. | [161 empty] | KURT CHERAMIE | SR. DIRECTOR | kurt.cheramie@kineticallc.com | 985-209-2283 |  |  |  |  | KURT CHERAMIE | SR. DIRECTOR | 985-209-2283 | kurt.cheramie@kineticallc.com | ON 12/26/2016, ENBRIDGE REPRESENTATIVE REPORTED A LEAK IN THE SMI 75 AREA AT 2:30 PM. COORDINATES WERE PLOTTED AND DETERMINED TO BE IN CLOSE PROXIMITY TO TWO KINETICA PIPELINES AND OTHER 3RD PARTY PIPELINES. ON THE AFTERNOON OF 12/27/2016 (DUE TO FOG IN THE AM), KINETICA DISPATCHED A HELICOPTER TO VERIFY COORDINATES AND SHUT OFF SOURCE OF PRODUCTION. DSV WAS MOBILIZED TO INVESTIGATE LEAK AND DETERMINED IT TO BE A LEAKING 30" FLANGE. AN ATTEMPT WAS MADE TO TORQUE THE FLANGE BOLTS TO STOP THE LEAK, BUT THAT ATTEMPT DID NOT WORK. ORDERED NEW BOLTS AND O-RING, AND PLANS ARE TO MOBE DSV TO LOCATION WHEN WORKING PRESSURE ON PIPELINE REACHES BOTTOM PRESSURE (APPROXIMATELY 75#). KINETICA PERSONNEL CONTINUE TO WORK WITH PRODUCER TO REDUCE PRESSURE ON LINE BY VENTING AND USING PRODUCER'S EQUIPMENT ON PLATFORM. SUPPLEMENTAL REPORT WILL BE SUBMITTED WHEN ALL REPAIRS ARE COMPLETED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170009 | 30008 | 2017-01-29 17:49 | SUPPLEMENTAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2016-12-30 15:08 | 2016 |  |  | 33.1989 | -87.603 | 1167504 | 2016-12-30 16:46 |  | NATURAL GAS |  | 4335 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-12-30 16:41 | 2016-12-31 00:04 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-12-30 14:40 | 2016-12-30 16:35 | ONSHORE | AL | 35487 | TUSCALOOSA | TUSCALOOSA | MILEPOST | MP 17.593 | MONTGOMERY COLUMBUS LINE | TUSCALOOSA #1 METER STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1981 |  | CARBON STEEL |  | OTHER | [8 empty] | OIL ENTERED REGULATOR PILOT AND BODY OF REGULATOR CAUSING MALFUNCTION OF THE REGULATOR ALLOWING PRESSURE TO INCREASE RESULTING IN RELIEF VALVE ACTION; MAOP NOT EXCEEDED; | CLASS 3 LOCATION | NO |  | 236 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 16083 | 16516.5040431267 | 1465 | 1586.43860807243 | 200 | 216.578649566201 | 0 | 0 |  |  | 17748 | 17951.0422006749 | 18319.5213007653 | [8 empty] | 421 |  | 506 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM WAS NOT THE REASON FOR REGULATOR MALFUNCTION AND RELIEF VALVE VENTING. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [25 empty] | YES | OIL ENTERED REGULATOR PILOT AND BODY OF REGULATOR | [161 empty] | WILLIAM MARTIN MULLER | SPECIALIST - PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 2053253863 | 2053253592 |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | 12/30/2016, 15:08, CITY OF TUSCALOOSA FIRE DEPARTMENT REPORTED A NATURAL GAS RELEASE TO SOUTHERN NATURAL GAS COMPANY (SNG) GAS CONTROL; 15:20, SNG TECHNICIAN CONFIRMED WITH SNG GAS CONTROL HE WAS IN ROUTE TO THE SNG TUSCALOOSA #1 METER STATION; CUSTOMER (ALAGASCO) TECHNICIAN ARRIVED AT SNG METER STATION AND AT 15:52 CUSTOMER (ALAGASCO) TECHNICIAN CONTACTED SNG GAS CONTROL AND CONFIRMED GAS VENTING FROM SNG METER STATION RELIEF VALVE; APPROXIMATELY 16:35 SNG TECHNICIAN ISOLATED FAILED REGULATOR, THE RELIEF VALVE THEN RESET; 16:41, SNG TECHNICIAN REPORTED TO SNG GAS CONTROL HE HAD ISOLATED THE REGULATOR AND VENTING OF NATURAL GAS WAS TERMINATED; INVESTIGATION FOUND OIL HAD ENTERED REGULATOR PILOT AND BODY OF REGULATOR WHICH CAUSED THE REGULATOR TO FAIL OPEN AS DESIGNED; THE RESULTING INCREASED PRESSURE CAUSED VENTING AT THE RELIEF VALVE; REGULATOR EQUIPMENT WAS CLEANED INTERNALLY AND REPAIRED BY REPLACING SOFT-GOODS; TUSCALOOSA #1 METER STATION WAS RETURNED TO SERVICE 12/31/2016, 00:04; DOCUMENTATION FROM THE CITY OF TUSCALOOSA FIRE DEPARTMENT NOTES THE FIRE DEPARTMENT CONDUCTED AN EVACUATION ON 51ST AVENUE; THIS EVACUATION WAS BASED UPON FIRE DEPARTMENT CRITERIA AND THEIR EVENT KNOWLEDGE AT THE TIME OF THE ALARM. THE DOCUMENTATION DOES NOT SPECIFICALLY IDENTIFY THE EVACUEES NOR DOES THE DOCUMENTATION PROVIDE THE EVACUATION POPULATION; ALL TIMES IN THIS REPORT ARE CST;
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170010 | 31474 | 2017-01-31 15:52 | SUPPLEMENTAL FINAL | 15105 | PANHANDLE EASTERN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2017-01-02 02:48 | 2017 |  |  | 39.8035 | -87.3495 | 1167624 | 2017-01-02 11:45 |  | NATURAL GAS |  | 13000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE ONLY EQUIPMENT REMOVED TEMPORARILY FROM SERVICE WAS THE RELIEF VALVE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-01-02 03:02 | 2017-01-02 03:30 | ONSHORE | IN | 47862 | MONTEZUMA | PARKE | MILEPOST | MONTEZUMA CS | MONTEZUMA COMPRESSOR STATION | 1303AB | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2009 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE | CLASS 1 LOCATION | NO |  | 137 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 49436 | 45276.7211538462 | 0 | 0 | 1000 | 1063.63467951093 | 0 | 0 |  |  | 50436 | 47428.6690761536 | 46340.3558333571 | [8 empty] | 670 |  | 900 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO INVESTIGATION WAS PERFORMED OTHER THAN CONFIRMING PROPER RESPONSE TO THE HI YARD NOISE STATUS ALARM WAS TAKEN, SINCE THE PRESSURE WAS WELL BELOW THE MAOP. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES |  |  |  |  | YES | A ROOT CAUSE COULD NOT BE DETERMINED. THE RELIEF VALVE WAS REMOVED, DISMANTLED, REBUILT AND RE-INSTALLED. THE SUPPLY GAS LINE WAS BLOWN TO REMOVE ANY POTENTIAL DEBRIS OR LIQUIDS. FITTINGS WERE REPLACED AND TIGHTENED AND THE VALVE WAS THEN RETURNED TO SERVICE WITH NO FURTHER ISSUES IDENTIFIED. THE ONLY INDICATIONS SUGGEST THAT THERE MAY HAVE BEEN A BLOCKAGE OF SOME SORT AND POTENTIAL FOR LEAKAGE FROM A FITTING OR FITTINGS. | [22 empty] | YES | A ROOT CAUSE COULD NOT BE DETERMINED, SEE ABOVE. | [161 empty] | NATHAN HLAVATY | DIRECTOR - REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | (713)857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - REGULATORY COMPLIANCE | (713)857-5479 | nathan.hlavaty@energytransfer.com | A HIGH NOISE ALARM WAS RECEIVED BY GAS CONTROL FROM THE MONTEZUMA COMPRESSOR STATION. GAS CONTROL CONTACTED THE ON-CALL STATION PERSONNEL. STATION PERSONNEL ARRIVED ON SITE AND VERIFIED THAT THE 1303 AB WAS RELEASING GAS AND WAS IMMEDIATELY ISOLATED BY CLOSING THE ISOLATION VALVE BELOW IT. THE RELIEF VALVE WAS REMOVED, DISMANTLED, REBUILT AND REINSTALLED. THE SUPPLY GAS LINE WAS BLOWN DOWN TO REMOVE ANY POTENTIAL DEBRIS OR LIQUIDS. FITTINGS WERE REPLACED AND TIGHTENED AND THE VALVE WAS THEN RETURNED TO SERVICE WITH NO FURTHER ISSUES IDENTIFIED. ONCE IT WAS DETERMINED THAT ESTIMATES OF POTENTIAL GAS LOSS WERE GREATER THAN 3 MMCF, THE DIRECTOR OF REGULATORY COMPLIANCE WAS NOTIFIED TO MAKE A TELEPHONIC REPORT TO THE NATIONAL RESPONSE CENTER. THIS SUPPLEMENTAL FINAL REPORT CORRECTED THE LAT/LONG COORDINATES IN PART A(5), AND FINAL UPDATES WERE MADE TO PART G(6). SUPPLEMENTAL REPORT SUBMITTED 01/11/19 TO CORRECT TIMELINE OF EVENTS FOR A-4.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170011 | 17273 | 2017-02-03 11:59 | ORIGINAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2017-01-07 02:21 | 2017 |  |  | 38.8845 | -86.398 | 1167977 | 2017-01-07 03:00 |  | NATURAL GAS |  | 9601 | 42 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | ONLY ENGINE 4 WAS SHUTDOWN; ENGINE 5 REMAINED IN SERVICE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-01-07 02:21 | 2017-01-07 02:54 | ONSHORE | IN | 47421 | BEDFORD | LAWRENCE | MILEPOST | 77.84 | LEESVILLE COMPRESSOR STATION | HAB 10 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1989 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE ACTIVATED PREMATURELY | CLASS 1 LOCATION | NO |  | 91 |  | NO | NO | NO |  | 0 | 0 | 168 | 178.690626157836 | 38449 | 35214.1081730769 | 200 | 212.726935902186 | 2000 | 2127.26935902186 | 0 | 0 |  |  | 40817 | 37664.2086607932 | 37732.7950941588 | [8 empty] | 901 |  | 1080 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE RELIEF VALVE OPENED PREMATURELY | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | NO | [306 empty] | SHANNON MATTINGLY | PA OQ AND EVENT SUPPORT PROGRAM LEADER | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 2706886361 | jeff.mcmaine@bwpmlp.com | RELIEF VALVE ON LEESVILLE COMPRESSOR STATION'S #4 ENGINE VENTED PREMATURELY. BOARDWALK PERSONNEL CHECKED THE SET POINT WHICH WAS CORRECT AND CHECKED FOR REPEATABILITY WHICH DID NOT OCCUR. THE ENGINE WAS RETURNED TO SERVICE AND THE EVENT REOCCURRED APPROXIMATELY 1 HOUR LATER. BOARDWALK PERSONNEL THEN REBUILT AND TESTED RELIEF VALVE AND PILOT AND RETURNED ENGINE TO SERVICE WITH NO ADDITIONAL INTERRUPTIONS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170012 | 17274 | 2017-02-03 13:16 | ORIGINAL FINAL | 2564 | COLORADO INTERSTATE GAS CO | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2017-01-06 01:50 | 2017 |  |  | 41.6809 | -107.9829 | 1167908 | 2017-01-06 06:02 |  | NATURAL GAS |  | 29825 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-01-06 01:55 | 2017-01-06 14:05 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-01-06 01:55 | 2017-01-06 04:45 | ONSHORE | WY | 82336 | WAMSUTTER | SWEETWATER | MILEPOST | MP 26 | WAMSUTTER COMPRESSOR STATION | VALVES V014, V026, AND V039 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1974 |  | CARBON STEEL |  | OTHER | [8 empty] | RELEASE OF NATURAL GAS TO ATMOSPHERE THROUGH THREE VENT VALVES | CLASS 1 LOCATION | NO |  | 483 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 100498 | 92042.6394230769 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 100498 | 95424.7836538462 | 92042.6394230769 | [8 empty] | 755 |  | 850 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLERS ACTIONS WERE APPROPRIATE TO THE SITUATION. VALVE ALARMS CAME INTO GAS CONTROL AND THE CONTROLLER DISPATCHED ON-CALL PERSONNEL TO RESPOND LOCALLY. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | OTHER | PNEUMATIC CONTROL MALFUNCTION CAUSED BY THE EXTREME COLD TEMPERATURES. AMBIENT TEMPERATURE WAS -40 F. | YES |  |  |  | YES | EXTREME LOW TEMPERATURES IN THE WAMSUTTER, WY AREA. | [301 empty] | KRISTIN VAN DER LAAN | SENIOR PIPELINE ENGINEER | kristin_vanderlaan@kindermorgan.com | [5 empty] | REJI GEORGE | DIRECTOR - COMPLIANCE CODES AND STANDARDS | 713-420-5433 | reji_george@kindermorgan.com | JANUARY 6, 2017: THERE WERE -40 F AMBIENT TEMPERATURES IN WAMSUTTER WY. COLORADO INTERSTATE GAS (CIG) WAMSUTTER COMPRESSOR STATION VENT VALVES (VO14, VO26, AND VO39) OPENED DUE TO A PNEUMATIC CONTROL MALFUNCTION CAUSED BY THE EXTREME COLD TEMPERATURES. 1:50 / 1:55A - VO14 AND VO26 VALVE ALARMS CAME INTO CIG GAS CONTROL. 2:02A - WAMSUTTER STATION UNIT #2 SHUTDOWN ON LOW SUCTION. 2:03A - GAS CONTROL DISPATCHED ON-CALL PERSONNEL. 2:30A - OPERATOR ARRIVED AT THE RAWLINS STATION AND ATTEMPTED TO CLEAR THE ALARMS. 4:45A - OPERATIONS PERSONNEL ARRIVED ON-SITE (WAMSUTTER STATION), ASSESSED THE SITUATION, DETERMINED THAT THE THREE VENT VALVES WERE RELEASING GAS. 4:50A - ALL VENT VALVES MANUALLY CLOSED. 5:26AM THE RELEASE WAS ESTIMATED TO EXCEED THE REPORTABLE UNINTENTIONAL GAS LOSS AMOUNT OF 3,000MCF. OPERATIONS SUPERVISOR CALLED GAS CONTROL TO INITIATE AN EMERGENCY RESPONSE LINE (ERL) CALL. THE INVESTIGATION DETERMINED THAT EXTREME COLD TEMPERATURES CAUSED THE PNEUMATIC CONTROL SYSTEM TO FAIL ON THREE WAMSUTTER STATION VENT VALVES. THE POWER GAS MIGRATED PAST THE INTERNAL COMPONENTS AND PRESSURED UP THE BACK SIDE OF THE CONTROL BLOCK, WHICH CAUSED THE VALVES TO OPEN. CIG WILL INSTALL HEAT TRACE AND BLANKETS ON THE ESD BLOCK VALVES AND VENTS TO PREVENT A REOCCURRENCE. NOTE THAT THE DATE OF INSTALLATION (PART C-4), PIR QUESTION (PART D-3), AND MAOP ESTABLISHED (PART E-2(A)) ARE BASED ON VALVE VO14, THE LARGEST VALVE. THE OTHER TWO VALVE INFORMATION IS AS FOLLOWS: V026 WAS INSTALLED IN 1996, AND VO39 WAS INSTALLED IN 2000. THE MAOP FOR THE ASSOCIATED PIPELINE FOR EACH VALVE WAS ESTABLISHED USING 49CFR 192.619(A)(2).
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170013 | 17276 | 2017-02-03 16:48 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2017-01-07 15:43 | 2017 |  |  | 35.848 | -87.4499 | 1168043 | 2017-01-07 20:04 |  | NATURAL GAS |  | 7456 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-01-07 15:43 | 2017-01-08 01:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-01-07 15:46 | 2017-01-07 16:01 | ONSHORE | TN | 37033 | NUNELLY | HICKMAN | MILEPOST | MP 559 | CENTERVILLE STATION 860 | BLOCK VALVE ABS-500-2-R | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | TUBING | [38 empty] | 2015 |  | CARBON STEEL |  | OTHER | [8 empty] | NATURAL GAS RELEASE THROUGH COMPRESSOR STATION BLOWOFF VALVE | CLASS 2 LOCATION | NO |  | 760 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 25350 | 23217.1875 | 300 | 319.090403853279 | 0 | 0 | 0 | 0 |  |  | 25650 | 24216.7834151538 | 23536.2779038533 | [8 empty] | 461 |  | 936 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATIONS PERSONNEL WERE ON-SITE WHEN THE STATION ESDED. THE ACTIVATION, CAUSE OF THE ESD, AND CAUSE OF THE NATURAL GAS RELEASE WAS UNRELATED TO CONTROLLERS ACTIONS OR CONTROL ROOM ACTIVITIES. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | YES |  |  |  | YES | EXTREME COLD TEMPERATURES IN THE NUNELLY TN AREA. | [301 empty] | KRISTIN VAN DER LAAN | SENIOR PIPELINE ENGINEER | kristin_vanderlaan@kindermorgan.com | [5 empty] | REJI GEORGE | DIRECTOR - COMPLIANCE CODES AND STANDARDS | 713-420-5433 | reji_george@kindermorgan.com | ON JANUARY 7, 2017 AT 3:43 PM TGP CENTERVILLE STATION 860 EXPERIENCED AN ESD DUE TO ACTIVATION OF A UVIR DETECTOR IN "A" COMPRESSOR BUILDING WHEN A SMALL AMOUNT OF GLYCOL LEAKING ON THE SPARK PLUG PORTS IGNITED BRIEFLY. ON-SITE PERSONNEL DETERMINED THAT A BLOCK-VALVE FAILED TO CLOSE UPON ACTIVATION OF THE ESD. THEY SHUT-IN THE BLOWDOWN VALVES TO STOP THE RELEASE AND BEGAN INVESTIGATING TO DETERMINE WHY THE BLOCK-VALVE DID NOT CLOSE. THE INVESTIGATION FOUND THAT DISTILLATE HAD FROZEN IN THE OPERATOR CONTROL-LINE FOR VALVE ABS5002R. THIS PREVENTED THE VALVE OPERATOR FROM PROPERLY ACTUATING TO SHUT THE VALVE RESULTING IN A TOTAL UNINTENTIONAL GAS LOSS OF 7,456 MCF TO ATMOSPHERE. FOLLOWING THE EVENT, PERSONNEL VERIFIED THAT ALL ESD SYSTEM-VALVES OPERATED PROPERLY AND THE CONTROL LINES ARE CLEAR OF LIQUIDS. GOING FORWARD THE STATION WINTERIZATION PLAN WILL INCLUDE A PROCESS TO ENSURE LIQUIDS ARE REMOVED FROM CONTROL LINES.
2021-02-26 10:37 | YES | NO | UNGS (Underground Natural Gas Storage) | 20170014 | 31529 | 2017-02-07 11:24 | SUPPLEMENTAL FINAL | 7050 | HAMPSHIRE GAS CO | 1000 MAINE AVENUE SW | WASHINGTON | DC | 20024 | 2017-01-08 04:00 | 2017 |  |  | 39.3167 | -78.6371 | 1168056 | 2017-01-08 08:30 |  | NATURAL GAS |  | 4 | 10 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-01-08 04:10 | 2018-03-01 08:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2017-01-08 04:00 | 2017-01-08 04:10 | ONSHORE | WV | 26704 | Not Within a Municipality | HAMPSHIRE | MILEPOST | WELL#1MCBRIDE | WELL #1 MCBRIDE | REBOILER | NO | OPERATOR-CONTROLLED PROPERTY | BELOWGROUND STORAGE OR ABOVEGROUND STORAGE VESSEL, INCLUDING ATTACHED APPURTENANCE |  |  |  |  | NO | [22 empty] | INTERSTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 2005 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | A0380 DIECAST ALUMINUM | OTHER | [8 empty] | REGULATOR BODY FRACTURE | CLASS 1 LOCATION | NO |  | 69 |  | NO | NO | NO |  | 0 | 0 | 45 | 47.8635605779918 | 18 | 16.4855769230769 | 300000 | 319090.403853279 | 0 | 0 | 0 | 0 |  |  | 300063 | 146509.977137188 | 319154.75299078 | [8 empty] | 600 |  | 200 | 192.619(A)(1) |  |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 | NO | [22 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LOCALIZED EQUIPMENT FAILURE. CONTROL ROOM ACTIONS WERE NOT CONTRIBUTING FACTORS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES |  |  | YES | [11 empty] | YES | [176 empty] | SHANNON B. MALONEY | SUPERVISOR - PIPELINE SAFETY AND COMPLIANCE | smaloney@washgas.com | 703-750-5558 |  |  |  |  | KRISTOPHER KELLEY | DIRECTOR - SAFETY QUALITY AND DOT PIPELINE SAFETY | 703-750-7710 | kristopherkelley@washgas.com | ON JANUARY 8, 2017, AT 4:00 AM AN ALARM WAS RECEIVED FROM HAMPSHIRE GAS WELL SITE #1. HAMPSHIRE GAS PERSONNEL ARRIVED ON SITE AT 4:10 AM AND OBSERVED A FIRE AT THE DEHYDRATOR FACILITIES AT THE SITE. THE REBOILER UNIT HAD CAUGHT FIRE. THE RESPONDING PERSONNEL MADE THE AREA SAFE BY VALVING OFF THE GAS TO THE INVOLVED FACILITY. THE INCIDENT INVESTIGATION INDICATED THAT A PRESSURE REGULATING DEVICE FAILED TO REDUCE THE INCOMING PRESSURE TO THE LOWER SET POINT. THE PRESSURE RELIEF DEVICE DOWNSTREAM OF THE REGULATOR ALSO FAILED TO ACTIVATE TO RELIEVE THE OVERPRESSURE CONDITION. THESE FAILURES ALLOWED 600 PSI NATURAL GAS PRESSURE TO REACH THE LOW PRESSURE REGULATORS UTILIZED FOR INSTRUMENT GAS AND BURNER FUEL GAS IN THE DEHYDRATOR EQUIPMENT. THESE FIVE LOW PRESSURE DEVICES EXPERIENCED BRITTLE METAL FAILURE FROM THE HIGH PRESSURE GAS AND LOW AMBIENT TEMPERATURES. THE FRACTURED METAL AND STEEL SET SCREWS FROM THE LOW PRESSURE REGULATORS STRUCK THE CONCRETE PAD AND STEEL SKID SUPPORT STRUCTURE CREATING SPARKS THAT MAY HAVE PROVIDED A POSSIBLE IGNITION SOURCE FOR THE ESCAPING NATURAL GAS. THE NOTICE OF THE INCIDENT CAME FROM AN ALERTS FROM SCADA. INSTRUMENT FAULT ALERTS AND ABNORMAL VALUES AROUND THE REBOILER WERE NOTICED. FURTHER ANALYSIS OF THE EQUIPMENT FAILURE FOUND THAT HIGHER MOISTURE CONTENT GAS CAUSED HYDRATES TO FORM AND FREEZE INSIDE THE REGULATOR AND RELIEF VALVE BODY. THE HYDRATES FREEZING CAUSED THE FAILURE OF THE EQUIPMENT THAT WAS LOCATED ON THE FUEL TRAIN FOR THE REBOILER.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170015 | 17471 | 2017-02-07 19:51 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2017-01-08 13:47 | 2017 |  |  | 38.0259 | -121.8867 | 1168106 | 2017-01-08 20:05 |  | NATURAL GAS |  | 50 | 1.7 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-01-12 08:00 | 2017-01-12 11:53 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-01-08 13:47 | 2017-01-08 13:52 | ONSHORE | CA | 94565 | PITTSBURG | CONTRA COSTA | MILEPOST | MP 0.93 | DFM 3015-01 | 27402 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 35 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | MAINLINE | OTHER | UNKNOWN | NORDSTROM |  |  |  | 1952 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | LEAK FROM BOLTED BODY OF VALVE | [5 empty] | CLASS 3 LOCATION | YES | METHOD2 | 146 |  | NO | NO | NO |  | 0 | 0 | 5 | 5.31817339755465 | 150 | 137.379807692308 | 293406 | 312076.796776584 | 3362 | 3575.93979251575 | 0 | 0 |  |  | 296923 | 145037.804227705 | 315795.43455019 | [8 empty] | 172 |  | 175 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 370 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | FAILURE OF EQUIPMENT BODY (EXCEPT COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL | MATERIAL/WELD/EQUIP FAILURE | FAILURE OF EQUIPMENT BODY | [166 empty] | FAILURE OF EQUIPMENT BODY (EXCEPT COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL | [19 empty] | FAILED FLANGE GASKET AND/OR MISSING TWO BOLTS FROM INITIAL INSTALLATION OF THE VALVE | [5 empty] | YES | [9 empty] | YES | FAILED FLANGE GASKET AND/OR MISSING TWO BOLTS FROM INITIAL INSTALLATION OF THE V | [161 empty] | STEPHEN RAMOS | GAS ENGINEER | s3rc@pge.com | 925-413-7311 |  |  |  |  | SUSIE RICHMOND | MANAGER REGULATORY COMPLIANCE | 925-328-5776 | gsr8@pge.com | ON JANUARY 8, 2017 AT 1347 HOURS, PG&E WAS NOTIFIED OF A GAS ODOR AT 310 CENTRAL AVENUE IN PITTSBURG. PG&ES GAS SERVICE REPRESENTATIVE (GSR) ARRIVED ON-SITE AT 1352 HOURS AND MEASURED 100% GAS IN AIR IN THE VALVE VAULT. AFTER VENTING THE VAULT FOR ABOUT AN HOUR, ANOTHER READING WAS TAKEN WHICH MEASURED 2% GAS IN AIR. THE LEAK ORIGIN IS THE UPSTREAM FLANGE OF THE 8-INCH STEEL TRANSMISSION VALVE, A-85, ON DFM 3015-01 (MILE POINT 0.93). PG&E REPAIR CREWS STOPPED THE LEAK AND COMPLETED REPAIRS ON JANUARY 12, 2017 AT 1153 HOURS BY ISOLATING THE LINE AND REPLACING THE VALVE. A PG&E REPRESENTATIVE WAS ON-SITE CONTINUOUSLY MONITORING THE LEAK AND ENSURED THE AREA WAS SAFE UNTIL THE REPAIRS WERE COMPLETED. NO POLICE, NO FIRE AND NO MEDIA WERE OBSERVED ON SCENE. THERE WAS NO REPORTED IGNITION, INJURIES, OR FATALITIES. THERE WAS NO CUSTOMER IMPACT. THE VALVE IS LOCATED IN A CHURCH PARKING LOT WHICH GENERATED PUBLIC ATTENTION FROM THE CHURCH CONGREGATION DUE TO THE GAS ODOR. THIS INCIDENT WAS REPORTED TO DOT AT 2005 HOURS (DOT #1168106) AFTER THE COST OF REPAIRS WAS ESTIMATED ABOVE $50,000 AND WAS SUBSEQUENTLY REPORTED TO THE CPUC DUE TO THE COST OF DAMAGES AND PUBLIC ATTENTION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170017 | 31113 | 2017-02-10 12:37 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2017-01-10 08:00 | 2017 |  |  | 32.9394 | -112.0868 | 1168334 | 2017-01-11 11:17 |  | NATURAL GAS |  | 3764 | 22851.6 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-01-11 14:30 | 2017-01-12 19:57 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2017-01-10 11:50 | 2017-01-10 12:30 | ONSHORE | AZ | 85239 | Not Within a Municipality | PINAL | MILEPOST | MP 578+1278 | EPNG LINE 1600 | L1600 CASA GRANDE TO WENDEN | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 72 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 |  | 0.45 | 60000 | API 5L | DSAW |  | US STEEL | COAL TAR | [28 empty] | 1969 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | 3/8" DIAMETER HOLE. | [5 empty] | CLASS 1 LOCATION | NO |  | 680 |  | NO | NO | NO |  | 0 | 0 | 72371 | 76976.3053908855 | 11921 | 10918.03125 | 43000 | 45736.29121897 | 1500 | 1595.45201926639 | 0 | 0 |  |  | 128792 | 68379.8931664505 | 135226.079879122 | [8 empty] | 950 |  | 1080 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL |  | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | LANDOWNER FOREMAN WORKING ON NEAR THE ROW OBSERVED LEAK. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE RESULTING LEAK WAS NOT DETECTED BY GAS CONTROLLERS SINCE IT DID NOT RESULT A MEASURABLE DROP IN LINE PRESSURE. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING | [6 empty] | YES | THE ROOT CAUSE WAS A FAILURE OF THE PIPELINE DUE TO EXTERNAL CORROSION. |  |  | YES |  |  |  | YES | YES |  | YES | YES | YES | YES |  |  | 2016 | 2017 |  |  | NO | [190 empty] | YES | YES |  |  | YES |  |  | YES | 2017 | [31 empty] | 2017 | [17 empty] | COMBINATION TOOL | 2017 |  |  |  |  | NO |  |  | NO | [13 empty] | YES | [5 empty] | MFL AFTER REPAIR | 2017 | [5 empty] | YES | [50 empty] | STEPHEN R. DINES | ENGINEER | stephen_dines@kindermorgan.com | (719) 329-5633 |  |  |  |  | JAIME A. HERNANDEZ | DIRECTOR OF ENGINEERING CODES AND STANDARDS | (713) 369-9443 | jaime_hernandez@kindermorgan.com | ON JANUARY 10, 2017, EL PASO NATURAL GAS COMPANY, LLC ("EPNG") GAS CONTROL WAS NOTIFIED BY A LOCAL LANDOWNER REPRESENTATIVE OF A NATURAL GAS LEAK AND SMALL FIRE AT APPROXIMATELY 11:50 AM MST. EPNG DISPATCHED OPERATING PERSONNEL TO THE SITE IMMEDIATELY. UPON THEIR ARRIVAL THEY MET WITH LOCAL FIRE AUTHORITIES, SECURED THE AREA, AND CONTACTED OTHER PIPELINE OPERATORS WITH PIPELINES KNOWN TO BE IN OR NEAR THE RIGHT-OF-WAY REGARDING THE OBSERVED LEAK. EPNG BEGAN INVESTIGATING THE SOURCE OF THE LEAK ONCE THE FIRE WAS EXTINGUISHED THAT SAME DAY. EPNG DETERMINED THE LOCATION OF THE LEAK ON LINE 1600 AT MILEPOST 578+1712 IN PINAL COUNTY, AZ, ON JANUARY 11, 2017 AT 10:00 AM MST AND AT 11:00 AM MST DURING THE EMERGENCY RESPONSE LINE (ERL) CALL IT WAS DETERMINED THAT THE RELEASE WOULD BE IN EXCESS OF 3,000 MCF REPORTING CRITERIA. AT THE CONCLUSION OF ITS INVESTIGATION, EPNG ESTIMATED THE UNINTENTIONAL RELEASE OF NATURAL GAS TO BE 3,764 MCF. EPNG COMPLETED ALL REPAIRS ON JANUARY 12, 2017 AND RETURNED LINE 1600 TO SERVICE ON JANUARY 12, 2017 AT 7:57 PM MST. THE ROOT CAUSE WAS A FAILURE OF THE PIPELINE DUE TO EXTERNAL CORROSION RESULTING IN LOCALIZED PITTING. THIS 30-DAY INCIDENT REPORT WAS UPDATED TO CORRECT THE TYPOGRAPHIC ERROR IN THE NRC REPORT DATE PROVIDED IN PART A, QUESTION 7 FROM 01/10/17 TO 01/11/17 AND CORRECT THE TIME ZONE FROM 13:17 PM EST TO 11:17 AM MST. ALSO, THIS REPORT INCLUDES A CHANGE IN THE TIME REPORTED IN RESPONSE TO PART A, QUESTION NO. 19B FROM 12:40 TO 12:30 AM MST AND THE RESPONSE TO PART A, QUESTION NO. 15A FROM 14:35 TO 14:30 PM MST AS THE TIME THE LINE SEGMENT WAS ISOLATED. THESE TIMES REFLECT THOSE REPORTED IN OUR FINAL INCIDENT TIMELINE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170018 | 17283 | 2017-02-10 13:26 | ORIGINAL | 30851 | ALBEMARLE CORPORATION | 2270 HIGHWAY 79S PO BOX 729 | MAGNOLIA | AR | 71753 | 2016-11-20 11:30 | 2016 |  |  | 33.2201 | -93.2345 | NRC NOTIFICATION NOT REQUIRED |  |  | NATURAL GAS |  | 113 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2016-11-20 12:15 | 2016-12-23 13:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-11-20 11:45 | 2016-11-20 11:55 | ONSHORE | AR | 71753 | Not Within a Municipality | COLUMBIA | SURVEY STATION NO. | PETA-TP-6 | ALBEMARLE | PETROCHEM GAS LINE | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 3 |  | 0.216 | 35000 | 3"-40 A106 GRADE B | SEAMLESS |  | UNKNOWN | PAINT | [28 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 0.1 | 0.6 | [7 empty] | CLASS 1 LOCATION | NO |  | 5097 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 673 | 691.140161725067 | 14486 | 15686.79158808 | 0 | 0 | 0 | 0 |  |  | 15159 | 7917.18765181425 | 16377.931749805 | [8 empty] | 330 |  | 681.8 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 56865 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | 3RD PARTY OBVIOUSLY CAUSED THE INCIDENT AND SELF REPORTED IT. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | HUNTER SHOT THE PIPELINE WITH A RIFLE BULLET. | [147 empty] | WILLIAM WRIGHT | AREA ENGINEER | william.wright@albemarle.com | 870-235-6592 | 870-235-6078 |  |  |  | WILLIAM WRIGHT | AREA ENGINEER | 870-235-6592 | william.wright@albemarle.com | DEER HUNTER WAS HUNTING IN WHITING ROW APPROXIMATELY 300 YARDS FROM THE ALBEMARLE ROW. HE SHOT AT A DEER AND MISSED BUT THE BULLET HIT THE PETROCHEM GAS PIPELINE WHICH IS ABOVE GROUND AT THIS POINT TO MAKE A TIE-IN TO THE WHITING GAS LINE. THE BULLET PUNCTURED THE PIPELINE CAUSING 330 PSIG NATURAL GAS TO ESCAPE TO ATMOSPHERE. THE HUNTER IDENTIFIED THE OWNER OF THE PIPELINE (ALBEMARLE) FROM THE PIPELINE MARKERS AND CALLED SOUTH PLANT SECURITY TO NOTIFY OF THE INCIDENT. PETROCHEM WAS CALLED TO SHUTDOWN SENDING GAS TO ALBEMARLE. THE PIPELINE WAS BLOCKED AT THE WEST PLANT AND SOUTH PLANT. KENNY KENDRICK WAS NOTIFIED AS WELL AS LARRY TAYLOR (COLUMBIA COUNTY OEM) AND PLANT MANAGEMENT. THE BRINEFIELD PUMPERS AND SUPERVISORS WENT TO THE SCENE AND INSTALLED BARRICADE TAPE AT THE ROW ENTRANCES NORTH AND SOUTH TO PREVENT ENTRY. THE LINE WAS BLED DOWN AND SECURED. AN EMAIL WAS SENT TO THE PUBLIC SERVICE COMMISSION CHIEF INFORMING THEM OF THE INCIDENT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170019 | 17286 | 2017-02-14 13:30 | ORIGINAL FINAL | 38987 | KINETICA ENERGY EXPRESS LLC | 1001 MCKINNEY STREET, SUITE 900 | HOUSTON | TX | 77002 | 2017-02-06 15:50 | 2017 |  |  | 29.415 | -92.17 | 1170394 | 2017-02-06 16:45 |  | NATURAL GAS |  | 2037 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-02-06 15:50 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-02-06 16:45 | 2017-02-07 12:09 | OFFSHORE | [28 empty] | 20 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | VERMILLION | 51 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 |  | 0.375 | 52000 | 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | KAISER | OTHER | CONCRETE | [27 empty] | 1979 | 1978 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 390 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 6111 | 5596.85336538462 | 100000 | 106363.467951093 | 5000 | 5318.17339755465 | 0 | 0 |  |  | 111111 | 57067.332323047 | 117278.494714032 | [8 empty] | 250 |  | 1250 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 172181 | NO |  | YES |  | YES |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE WAS BELOW MAOP WITH NO UNUSUAL OPERATING CIRCUMSTANCES AND WAS LOCATED SUBSEA | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | NO | YES | NOT APPLICABLE - NOT MAINLINE PIPE | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KURT CHERAMIE | SR. DIRECTOR | kurt.cheramie@kineticallc.com | 9852092283 |  |  |  |  | KURT CHERAMIE | SR. DIRECTOR | 9852092283 | kurt.cheramie@kineticallc.com | BUBBLES 3' IN DIAMETER REPORTED TO KINETICA GAS CONTROL BY DONALD DUET WITH TALOS AT 15:50 ON 2/6/17. CHESTER FRUGE WITH TALOS WAS IN HELICOPTER AND VIEWED THE LEAK, THEN REPORTED TO DONALD DUET. KINETICA OPERATIONS AND GAS CONTROL VIEWED SCADA BUT DID NOT SEE ANY LOSS OF LINE PRESSURE. OPERATIONS INFORMED USCG THAT MORNING OVERFLIGHT WOULD BE CONDUCTED. 2/7/17 OVERFLIGHT VERIFIED COORDINATES AND LOCATION OF LEAK IN PROXIMITY TO KINETICA'S PIPELINE. THIS PIPELINE SEGMENT HAD BEEN ISOLATED SINCE AN EARLIER LEAK IN 11/17. DSV WAS MOBILIZED AND ARRIVED ON LOCATION ON 2/10/17. CONFIRMED PINHOLE LEAK AT 7 O'CLOCK POSITION. REPAIR CLAMP INSTALLED AT 4:00 AM ON 2/11/17. PIPELINE TO REMAIN OUT OF SERVICE AND PREPARE FOR ABANDONMENT IN 2018. PRESSURE ON PIPELINE AS OF 2/13/17 IS 95#.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170020 | 17353 | 2017-02-17 15:53 | SUPPLEMENTAL FINAL | 39519 | KINETICA DEEPWATER EXPRESS LLC | 1001 MCKINNEY STREET SUITE 900 | HOUSTON | TX | 77002 | 2017-01-18 14:26 | 2017 |  |  | 29.3749 | -93.5441 | 1169041 | 2017-01-20 08:31 |  | NATURAL GAS |  | 555 | 0 | 0.1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | PIPELINE WAS ALREADY SHUT-IN AND ISOLATED AS WC 165A PLATFORM WAS NOT PRODUCING | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-01-19 14:40 | 2017-01-19 14:40 | OFFSHORE | [28 empty] | 50 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST CAMERON | 165 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 10 |  | 0.365 | 42000 | 5L | SEAMLESS |  | UNKNOWN | EPOXY | [28 empty] | 2006 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 267 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 1665 | 1524.91586538462 | 100000 | 106363.467951093 | 5000 | 5318.17339755465 | 0 | 0 |  |  | 106665 | 52845.769823047 | 113206.557214032 | [8 empty] | 705 |  | 1300 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 22228 | NO |  |  | YES |  |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | OTHER | CALL FROM BSEE OFFICE AFTER RECEIPT OF ORIGINAL NRC REPORT FROM 3RD PARTY |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE WAS BELOW MAOP WITH NO UNUSUAL OPERATING CIRCUMSTANCES AND WAS LOCATED SUBSEA | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NOT APPLICABLE - NOT MAINLINE PIPE | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KURT CHERAMIE | SR. DIRECTOR | kurt.cheramie@kineticallc.com | 9852092283 |  |  |  |  | KURT CHERAMIE | SR. DIRECTOR | 9852092283 | kurt.cheramie@kineticallc.com | 14:26 ON 1/18/17, BSEE CALLED REGARDING NRC REPORT #1168876 IN THE VICINITY OF KINETICA LINE IN WC 165. REPORT CALLED IN BY ERA PILOT WITH BUBBLES AND 1 MI X 15 MI SHEEN. UPON RECEIPT OF NOTICE, KINETICA HELICOPTER COULD NOT FLY TO LOCATION DUE TO WEATHER. DSV WORKING IN THE SHIP SHOAL AREA WAS DISPATCHED, ARRIVED ON LOCATION AT 14:40 ON 1/19/17 AND CONFIRMED COORDINATES. DSV REPORTED 5' - 6' BUBBLE FIELD AND STREAKY SHEENING. ESTIMATE ON CONDENSATE SPILLED WAS 5 - 10 GALLONS. AT 14:54 NRC WAS CALLED TO UPDATE EXISTING REPORT AND TAKE OWNERSHIP OF LEAK. THEY TOLD ME I COULD NOT AMEND REPORT AND THAT I NEEDED TO CALL THE LOCAL USCG OFFICE (PORT ARTHUR) REGARDING OWNERSHIP. PIPELINE WAS NOT FLOWING AS PLATFORM HAD RECENTLY BEEN SHUT IN PREPARING FOR REMOVAL OF STRUCTURE. 1/20/17 RECEIVED CALL FROM DAVID YORK (PHMSA) REQUESTING THAT I CALL IN ANOTHER NRC REPORT TO CLAIM OWNERSHIP, WHICH I DID AT 08:31 ON 1/20/17 (REPORT #1169041). PRESSURE WAS REDUCED ON THE LINE AND DSV INSTALLED REPAIR CLAMP. DIVER FOUND TWO SMALL HOLES AT 7 O'CLOCK POSITION ASSUMED TO BE CORROSION PITTING. LINE WILL NOT BE RETURNED TO SERVICE AND HAS BEEN PLACED ON 2017 ABANDONMENT LIST.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170021 | 30170 | 2017-03-07 16:41 | SUPPLEMENTAL FINAL | 32645 | HILCORP ALASKA, LLC | 3800 CENTERPOINT DR. SUITE 1400 | ANCHORAGE | AK | 99503 | 2017-02-07 15:23 | 2017 |  |  | 60.7803 | -151.4392 | 1170504 | 2017-02-07 15:49 |  | NATURAL GAS |  | 500 | 47178 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | SHUTTING DOWN COMPLETELY INCURRS A HIGH RISK OF ADVERSE IMPACTS. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-02-07 15:23 | 2017-02-07 15:23 | ONSHORE | AK | 99635 | Not Within a Municipality | KENAI PENINSULA BOROUGH | SURVEY STATION NO. | 5M FROM SHORE | MIDDLE GROUND SHOAL | A-LINE | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | OTHER | SUBMERGED PIPE RESTING BOTTOM |  |  | YES | [6 empty] | YES | UNCASED | COOK INLET | 80 | BELOW WATER, PIPE ON OR ABOVE BOTTOM | [11 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 |  | 0.594 | 35000 | API 5L | SEAMLESS |  | N/A | OTHER | X-TRU COAT (WEIGHT COAT) | [27 empty] | 1965 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | EXTERNAL PIPE WALL ABRASION | [5 empty] | CLASS 1 LOCATION | NO |  | 145 |  | NO | NO | NO |  | 0 | 0 | 178804 | 190182.135235272 | 1895 | 1735.56490384615 | 2280000 | 2425087.06928492 | 80000 | 85090.7743608744 | 5500000 | 5849990.73731012 | ENVIRONMENTAL MONITORING, INTEGRITY INVESTIGATIONS, ADDITIONAL INSPECTIONS |  | 8040699 | 3926635.93434801 | 8552086.28109503 | [8 empty] | 195 |  | 695 | 192.619(A)(4) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 37193 | YES | [7 empty] | YES |  |  |  |  | YES | SUBSEA MANIFOLD | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | OTHER | METER DISCREPANCY |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS NOT CAUSED BY OPERATOR ACTIVITIES | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [52 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | ABRASION OF THE PIPE BODY FROM CONTACT WITH A SUBMERGED ROCK RESTING ON THE SEA FLOOR | NO | [306 empty] | JUSTIN SELVIK | REGULATORY COMPLIANCE SPECIALIST | jselvik@hilcorp.com | 907-602-5026 |  |  |  |  | ERIN MCKAY | REGULATORY COMPLIANCE MANAGER | 907-777-8430 | emckay@hilcorp.com | ON FEBRUARY 7, 2017, HILCORP ALASKA, LLC (HILCORP) DISCOVERED A NATURAL GAS LEAK FROM AN 8-INCH FUEL GAS PIPELINE ("A" PIPELINE) SERVING PLATFORMS IN COOK INLET'S MIDDLE GROUND SHOAL (MGS) FIELD. THE LEAK WAS CONFIRMED BY AN AERIAL PATROL DISPATCHED BY PIPELINE OPERATORS, AND WAS PROMPTLY REPORTED TO THE NATIONAL RESPONSE CENTER, THE DEPARTMENT OF ENVIRONMENTAL CONSERVATION, THE PHMSA ANCHORAGE OFFICE, AND OTHERS. PIPELINE PRESSURE WAS REDUCED, AND INSPECTION AND REPAIR PLANNING INITIATED. THE CAUSE OF THE NATURAL GAS LEAK WAS A PIPE BODY FAILURE DUE TO MECHANICAL ABRASION. THE MECHANICAL ABRASION RESULTED FROM THE CONTACT BETWEEN THE PIPELINE AND A SUBMERGED ROCK RESTING ON THE SEAFLOOR. INSPECTION AND REPAIR OF THE LEAK WERE COMPLICATED BY WINTER CONDITIONS IN COOK INLET. LARGE FLOATING ICE PANS, BROKEN UP ICE AND LIMITED DAYLIGHT PREVENTED THE IMMEDIATE DISPATCH OF DIVERS TO INSPECT AND CONTAIN THE LEAK. IN RESPONSE TO THE GAS LEAK, HILCORP IMPLEMENTED A MULTI-COMPONENT ENVIRONMENTAL SAMPLING AND MONITORING WORK PLAN TO QUANTIFY ANY POTENTIAL ENVIRONMENTAL IMPACTS ASSOCIATED WITH THE GAS LEAK. HILCORP SUBMITTED WEEKLY SAMPLING AND MONITORING DATA SUMMARY REPORTS TO ALASKA DEPARTMENT OF ENVIRONMENTAL CONSERVATION (ADEC) FOR TEN CONSECUTIVE WEEKS. THE RESULTS FROM THE SAMPLING AND MONITORING PROGRAM DID NOT IDENTIFY ANY SIGNIFICANT CHANGES THAT WOULD SUGGEST HARM TO THE ENVIRONMENT OR WILDLIFE AS A RESULT OF THE LEAK. HILCORP DETERMINED THAT SHUTTING IN THE PIPELINE WOULD CAUSE SEAWATER TO ENTER THE DEPRESSURIZED PIPELINE THROUGH THE LEAK, LIKELY DISPLACING AND MOBILIZING RESIDUAL OIL REMAINING IN PIPELINE FROM A PRIOR OPERATOR'S 2005 CONVERSION OF SERVICE FROM CRUDE OIL TO NATURAL GAS. THE GAS PIPELINE SUPPLIES HEAT, LIGHT AND POWER TO MGS PLATFORMS, LOSS OF WHICH WOULD ELIMINATE NAVIGATIONAL AID LIGHTING AND CATHODIC PROTECTION FOR THE FUEL LINE, PLATFORMS, AND ASSOCIATED PIPELINES. A LACK OF FUEL GAS COULD PUT THE HEALTH AND SAFETY OF PLATFORM OPERATORS AT RISK AND LEAD TO DAMAGE TO THE PLATFORMS AND OTHER INFRASTRUCTURE, AND COULD HAVE CAUSED PRODUCTION LINES TO FREEZE, CREATING A POTENTIAL SOURCE FOR AN OIL SPILL WHEN THE LINES THAWED. ON MARCH 25, 2017, HILCORP REDUCED PIPELINE PRESSURE FROM 145 PSI TO 65 PSI; THE PRESSURE CALCULATED TO BE PROPORTIONAL TO THE DIFFERENTIAL PRESSURE OF WATER AT THE PIPE WALL. MAINTAINING POSITIVE PRESSURE IN THE PIPELINE WAS NECESSARY TO AVOID THE LIKELY RELEASE OF RESIDUAL HYDROCARBONS INSIDE THE PIPELINE. HILCORP CONTRACTED A DIVE TEAM WHO STOPPED THE LEAK BY INSTALLING A TEMPORARY CLAMP ON APRIL 13, 2017. BY LETTER DATED MARCH 3, 2017, PHMSA ISSUED A NOTICE OF PROPOSED SAFETY ORDER TO HILCORP RELATED TO THE MGS FUEL GAS LINE. PHMSA AND HILCORP ENTERED INTO A CONSENT AGREEMENT AND ORDER, EFFECTIVE APRIL 12, 2017. PHMSA APPROVED A LEAK INSPECTION AND PERMANENT REPAIR PLAN ON MAY 9 AND DIVERS INSTALLED A PERMANENT REPAIR CLAMP IN PLACE OF THE TEMPORARY CLAMP. DIVERS SUCCESSFULLY TESTED THE PERMANENT CLAMP SEAL ON MAY 20, COMPLETING THE REPAIR PROCESS. THE CAUSE OF THE LEAK WAS CONFIRMED BY DIVERS TO BE EXTERNAL FORCE DAMAGE; ABRASION OF THE PIPELINE BODY FROM CONTACT WITH A SUBMERGED ROCK RESTING ON THE SEAFLOOR. TO MITIGATE THE RISK OF FUTURE ABRASION OF THE PIPELINE, DIVERS STABILIZED THE PIPE AT THE LEAK LOCATION TO PREVENT PIPE MOVEMENT. HILCORP PERFORMED A SONAR INSPECTION OF THE SUBMERGED PIPELINE ROW ON JUNE 21. AN ILI ASSESSMENT OF THE 8-INCH "A" PIPELINE, FROM MGS PLATFORM A TO SHORE, WAS COMPLETED JULY 19. HILCORP SUCCESSFULLY PERFORMED A PRESSURE TEST OF THE LINE ON SEPTEMBER 9, AND NORMAL FUEL GAS OPERATIONS RESUMED ON SEPTEMBER 16. HILCORP WILL CONTINUE VARIOUS INSPECTIONS, IN ACCORDANCE WITH THE APRIL 12, 2017 CONSENT AGREEMENT AND ORDER. HILCORP INTEGRATED SONAR AND ILI DATA TO PRIORITIZE DIVER INSPECTIONS AND MITIGATION MEASURES. DIVERS COMPLETED INSPECTIONS THEN ARMORED AND STABILIZED THE PIPELINE AT LOCATIONS IDENTIFIED BY DATA INTEGRATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170022 | 17348 | 2017-03-14 18:42 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2017-02-14 09:54 | 2017 |  |  | 38.0611 | -83.8596 | 1171048 | 2017-02-14 11:39 |  | NATURAL GAS |  | 15024 | 17362 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-02-14 12:35 | 2017-02-20 21:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 19 | 2017-02-14 10:32 | 2017-02-14 10:45 | ONSHORE | KY | 40353 | Not Within a Municipality | MONTGOMERY | SURVEY STATION NO. | 500+33 | LINE EM-7 | LINE EM-7 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 120 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 |  | 0.312 | 65000 | X-65 | DSAW |  | REPUBLIC | EPOXY | [28 empty] | 1969 | 1969 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 2 LOCATION | NO |  | 752 |  | NO | NO | NO |  | 20000 | 21272.6935902186 | 54864 | 58355.2530566877 | 47486 | 43490.7836538462 | 500000 | 531817.339755465 | 0 | 0 | 100000 | 106363.467951093 | OTHER COSTS INCLUDE GEOTECHNICAL AND METALLURGICAL INVESTIGATIONS. |  | 722350 | 374582.029140066 | 761299.53800731 | [8 empty] | 790 |  | 1000 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 73656 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | YES | 3 | 0 | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES | [6 empty] | YES | [14 empty] | YES | [63 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DAVID ANDERSON | REGULATORY SPECIALIST | david_anderson@transcanada.com | 724-223-2766 |  |  |  |  | HOWARD LEE ROMACK | MANAGER | 832-320-5215 | lee_romack@transcanada.com | ON FEBRUARY 14, 2017 AN ODOR OF GAS COMPLAINT WAS CALLED IN AT 09:54 AM TO THE LOCAL DISTRIBUTION COMPANY (COLUMBIA GAS OF KENTUCKY) MONITORING CENTER BY A LANDOWNER ON HARPER RIDGE ROAD. THE LDC MONITORING CENTER DISPATCHED AN EMPLOYEE WHO ARRIVED AT THE SITE AT APPROXIMATELY 10:13 AM. AFTER ASSESSING THE SITUATION, THE LDC EMPLOYEE NOTIFIED THE LDC MONITORING CENTER TO ALERT THE FIRE DEPARTMENT AND CALLED A COLUMBIA GAS TRANSMISSION LLC EMPLOYEE AT 10:20AM. THE COLUMBIA GAS TRANSMISSION EMPLOYEE RESPONDED AND NOTIFIED THE COLUMBIA GAS TRANSMISSION MONITORING CENTER AT 10:32 AM OF THE POTENTIAL LEAK. THE EMPLOYEE ARRIVED ON SITE AT 10:45 AM AND DETERMINED THAT THE LEAK WAS ON 30" LINE EM-7 OWNED AND OPERATED BY COLUMBIA GAS TRANSMISSION LLC. COLUMBIA GAS TRANSMISSION FIELD EMPLOYEES WERE NOTIFIED AND RESPONDED. THE LOCAL FIRE DEPARTMENT ALSO RESPONDED AND EVACUATED 6 FAMILIES. COLUMBIA GAS TRANSMISSION CALLED THE NATIONAL RESPONSE CENTER AT 11:39 AM ON FEBRUARY 14, 2017, AND WAS PLACED ON HOLD UNTIL 12:01 PM. THE PIPELINE WAS REMOVED FROM SERVICE. THE PIPELINE WAS EXCAVATED AND A CRACK FOUND ON A WELD ELBOW FITTING NEAR A GIRTH WELD. THE PIPELINE WAS REPAIRED WITH REPLACEMENT PIPE AND AN WELD ELBOW FITTING, AND PLACED BACK INTO SERVICE ON FEBRUARY 20, 2017. THE METALLURGICAL AND GEOTECHNICAL ANALYSES HAVE BEEN PROVIDED TO PHMSA.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170023 | 30723 | 2017-03-17 16:27 | SUPPLEMENTAL FINAL | 4900 | KINDER MORGAN TEJAS PIPELINE | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2017-02-15 00:22 | 2017 |  |  | 28.4014 | -97.067 | 1171099 | 2017-02-15 01:46 |  | NATURAL GAS |  | 138587 | 33046 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-02-15 01:36 | 2017-12-01 21:36 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 0 | 2017-02-15 00:22 | 2017-02-15 01:48 | ONSHORE | TX | 78377 | Not Within a Municipality | REFUGIO | MILEPOST | 89.6 | MUSTANG LINE 1 | LINE 520-100 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 36 |  | 0.422 | 60000 | 5L | FLASH WELDED |  | AO SMITH | ASPHALT | [28 empty] | 1964 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 2892 | 36 |  | CLASS 1 LOCATION | NO |  | 787 |  | NO | NO | NO |  | 101096 | 107529.211559837 | 101121 | 107555.802426825 | 424076 | 388396.528846154 | 581000 | 617971.74879585 | 7500 | 7977.26009633197 | 18152 | 19307.0967024824 | DIRT AND WATER PURCHASE |  | 1232945 | 797587.592872717 | 1248737.64842748 | [8 empty] | 802 |  | 1004 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | YES | NO | NOT MANDATED |  |  | MANUAL | MANUAL | 74290 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | [6 empty] | YES | WHILE NOT A CAUSE OF THE EVENT, THE INVESTIGATION DETERMINED THAT THE SENDING OF THE ERL+ NOTIFICATION BY GC WAS DELAYED. THIS DELAY, HOWEVER, DID NOT HINDER THE RESPONSE TO THE PIPELINE FAILURE BUT WAS A FACTOR IN THE TIMING OF THE REPORT TO THE NRC. | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | OTHER | SELECTIVE SEAM |  |  |  |  | YES |  |  |  |  | YES | YES | YES | INTEGRATED DATA FROM THE METALLURGICAL REPORT, INCIDENT REPORT, RAW DATA FROM THE ROSEN AXIAL FLAW DETECTION (AFD) ILI TOOL, INTERVIEWS WITH THE NON-DESTRUCTIVE FIELD TECHNICIAN, AND PHOTOGRAPHS OF THE FAILURE AREA. | YES | YES | 1964 | YES | YES | YES | YES |  |  | 2016 | 2015 |  |  | YES | [190 empty] | YES | YES | YES |  | YES |  |  | YES | 2015 | [11 empty] | 2015 | [19 empty] | 2015 | [17 empty] | COMBINATION TOOL | 2015 |  |  |  |  | NO |  |  | NO | [13 empty] | YES | [5 empty] | PIT GAUGE | 2017 | [5 empty] | YES | [50 empty] | KRISTIN VAN DER LAAN | ENGINEERING MANAGER -COMPLIANCE CODES AND STDS | kristin_vanderlaan@kindermorgan.com | 303-914-7753 |  |  |  |  | JORGE TORRES | VICE PRESIDENT ENGINEERING - KMI PIPELINE | 713-369-9232 | jorge_torres@kindermorgan.com | ON FEBRUARY 15, 2017 AT 12:22 AM, KINDER MORGAN TEJAS PIPELINE (KM TEJAS) GAS CONTROL SAW A LINE BREAK INDICATION ON THE KM TEJAS PIPELINE SYSTEM BETWEEN STATION 2 AND STATION 3 NEAR REFUGIO, TEXAS AND CONTACTED FIELD PERSONNEL TO INVESTIGATE CAUSE OF THE LINE BREAK. KM TEJAS FIELD PERSONNEL VERIFIED A FAILURE ON THE KM TEJAS PIPELINE AND IMMEDIATELY ISOLATED THE LINE. POST-INCIDENT, KM TEJAS PERFORMED AN INVESTIGATION INCLUDING ENGAGED THIRD-PARTY COMPANIES TO PERFORM MECHANICAL LOAD AND METALLURGICAL EVALUATIONS. BASED SOLELY ON THE SESI MECHANICAL LOAD EVALUATIONS AND EN ENGINEERING METALLURGICAL EVALUATIONS THE IMMEDIATE CAUSE OF THE INCIDENT COULD NOT BE DETERMINED. BASED ON THE SESI REPORT, THE INCIDENT WAS MOST LIKELY CAUSED BY SOME COMBINATION OF STRESS FACTORS ON THE PIPELINE. AT PHMSA'S REQUEST, KM TEJAS IS ESTIMATING REPLACEMENT COSTS FOR THE PRIVATE PROPERTY DAMAGE OF WHICH IT IS AWARE INCLUDING TWO DAMAGED PIECES OF PRODUCTION EQUIPMENT (ESTIMATED TO BE APPROXIMATELY $23,775) AND THE COST FOR DAMAGE TO 1,406 TREES (ESTIMATED TO BE $77,321). THIS INFORMATION IS PROVIDED IN PART D 7A "ESTIMATED COST OF PUBLIC AND NON-OPERATOR PRIVATE PROPERTY DAMAGE". ADDENDUM EFFECTIVE JULY 12, 2018: KM TEJAS CONTINUED TO REVIEW THE INFORMATION RELATED TO THE FAILURE AND TO CONDUCT ADDITIONAL ANALYSIS TO DETERMINE WHETHER ANY ADDITIONAL CONCLUSIONS OR CONTRIBUTING FACTORS COULD BE IDENTIFIED. THROUGH CONTINUED ANALYSIS OF THE INFORMATION, KM TEJAS HAS CONCLUDED THAT V-GROOVE CORROSION (ALSO CALLED "SELECTIVE SEAM WELD CORROSION") IS THE IMMEDIATE CAUSE OF THE FAILURE. ADDITIONALLY, KM TEJAS CONCLUDED THAT CATHODIC PROTECTION LEVELS, THE PRESENCE OF FERROMAGNETIC MATERIAL, AND LOW SEAM TOUGHNESS EXPERIENCED AT LOWER AMBIENT TEMPERATURES WERE CONTRIBUTING FACTORS. NOTE THAT THE DAMAGE REFERENCED IN THIS FORM, PHMSA F 7100.2, PART G1 QUESTION 5 THE COATING WAS NOT DAMAGED BY THIRD-PARTY, MECHANICAL, NATURAL FORCES, ETC. BUT WAS LIKELY DAMAGED FROM SOIL STRESSES.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170024 | 17301 | 2017-03-22 13:00 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2017-01-11 19:45 | 2017 |  |  | 39.0563 | -97.8566 | 1168497 | 2017-01-13 11:35 |  | NATURAL GAS |  | 4900 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-01-11 20:45 | 2017-01-12 11:27 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-01-11 19:45 | 2017-01-11 20:30 | ONSHORE | KS | 67467 | Not Within a Municipality | OTTAWA | MILEPOST | 0 | TESCOTT COMPRESSOR STATION | KS-040 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2006 |  | CARBON STEEL |  | OTHER | [8 empty] | THE UNIT 5 DISCHARGE RELIEF VALVE OPENED INTERMITTENTLY BELOW THE 1030 SET POINT. | CLASS 1 LOCATION | YES | METHOD2 | 173 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 16200 | 14837.0192307692 | 200 | 212.726935902186 | 1000 | 1063.63467951093 | 0 | 0 |  |  | 17400 | 15968.0951990766 | 16113.3808461823 | [8 empty] | 921 |  | 991 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE RELIEF VALVE FOR UNIT 5 IS NOT CONTROLLABLE BY GAS CONTROL OR A GAS CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [22 empty] | YES | [168 empty] | JOHN GORMLEY | SR CORROSION SPECIALIST - PIPELINE SAFETY | john.gormley@nngco.com | 402-398-7494 |  |  |  |  | THOMAS CORRELL | VP PIPELINE SAFETY AND RISK | 402-398-7715 | thomas.correll@nngco.com | ON JANUARY 11, 2017, AT 1945 HOURS, THE OPERATIONS COMMUNICATION CENTER RECEIVED A CALL FROM A TENANT NEAR THE TESCOTT COMPRESSOR STATION STATING THERE WAS A LOUD NOISE NEAR THE STATION. A NORTHERN NATURAL GAS TECHNICIAN ARRIVED AT THE STATION AT APPROXIMATELY 2030 HOURS AND DID NOT NOTICE ANY ABNORMAL CONDITIONS. UNIT 5 WAS ON LINE ON THE E MAINLINE WITH A MAOP OF 991 PSIG. HE FOUND THE RELIEF VALVE RAIN CAP WAS OFF. WHEN THE TECHNICIAN CHECKED THE PRESSURE TRENDS, HE FOUND THAT THE DISCHARGE RELIEF VALVE APPEARED TO HAVE OPENED AND CLOSED SEVERAL TIMES AT PRESSURES BELOW THE MAOP RANGING FROM 862 PSIG TO 921 PSIG. THE RELIEF VALVE IS INTENDED TO RELIEVE PRESSURE AT 1030 PSIG. GAS CONTROL DID NOT NEED THE UNIT AND IT WAS SHUT DOWN. ON JANUARY 12, 2017, TECHNICIANS BENCH TESTED THE RELIEF VALVE PILOT. A NEW SOFT GOODS KIT WAS INSTALLED IN THE PILOT AND THE PRESSURE WAS SET AT 1,030-PSIG. THE PILOT WAS INSTALLED ON THE RELIEF VALVE AND THE RELIEF VALVE LIFTED OFF THE SEAT AT 1030-PSIG WHEN TESTED. UNIT 5 WAS PLACED ON LINE AT 1127 HOURS. ON JANUARY 13, 2017, THE FACILITY PLANNING DEPARTMENT WAS CONTACTED TO CALCULATE THE GAS LOSS. FIELD OPERATIONS INDICATED THAT IT DID NOT SEEM THAT THE RELIEF VALVE WAS FULL OPEN DURING VENTING. THE RELIEF INCIDENT OCCURRED BETWEEN 19:10 AND 20:06. FLOW THROUGH THE LINE WAS CONSTANT DURING THE PERIOD AS MEASURED BY THE FLOW METER AT THE CLIFTON COMPRESSOR STATION 47.5 MILES DOWNSTREAM. THE INITIAL ESTIMATE INDICATED A GAS LOSS OF 6 MMCF. FACILITY PLANNING NOTIFIED FIELD OPERATIONS AND AN URGENT OPERATIONS COMMUNICATION CENTER CALL WAS INITIATED WITH THE PIPELINE SAFETY AND ENVIRONMENTAL DEPARTMENTS. THE NATIONAL RESPONSE CENTER WAS NOTIFIED IMMEDIATELY AFTER THE URGENT OPERATIONS COMMUNICATION CENTER CALL OF THE INCIDENT DUE TO THE GAS LOSS IN EXCESS OF 3 MMCF. ON JANUARY 17, 2017, A THOROUGH GAS LOSS ANALYSIS WAS COMPLETED BY FACILITY PLANNING. LIMITED WORK OCCURRED ON JANUARY 16, 2017, DUE TO THE ICE STORM. THE ESTIMATED GAS LOSS FROM THE INCIDENT IS 4.9 MMCF.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170025 | 17302 | 2017-03-24 15:49 | ORIGINAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2017-03-04 12:33 | 2017 |  |  | 31.7033 | -105.4565 | 1172477 | 2017-03-04 05:35 |  | NATURAL GAS |  | 3130 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | FAILED COMPONENT WAS ISOLATED, REPAIRED, AND PLACED BACK INTO SERVICE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-03-04 12:33 | 2017-03-04 12:11 | ONSHORE | TX | 79847 | CORNUDAS | HUDSPETH | MILEPOST | 144 | CORNUDAS COMPRESSOR STATION | EPNG 1100 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 2004 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | REGULATOR'S INTERNAL SOFT GOODS (BOOT) | OTHER | [8 empty] | RELIEF VALVE RELEASE DUE TO UPSTREAM REGULATOR FAILURE | CLASS 1 LOCATION | NO |  | 172 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 7500 | 6868.99038461538 | 250 | 265.908669877733 | 0 | 0 | 0 | 0 |  |  | 7750 | 7243.4533267307 | 7134.89905449312 | [8 empty] | 175 |  | 837 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS DUE TO A MECHANICAL FAILURE WITH WHICH CONTROLLERS HAD NO INFLUENCE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [19 empty] | YES | [5 empty] | YES | REGULATOR'S INTERNAL BOOT CONTAMINATED WITH PIPELINE SLUDGE. | [161 empty] | KENNETH C PETERS | SENIOR ENGINEER CODES AND STANDARDS | ken_peters@kindermorgan.com | 2053257554 | 2053253508 |  |  |  | REJI GEORGE | DIRECTOR CODES AND STANDARDS | 7134205433 | reji_george@kindermorgan.com | ON MARCH 4, 2017, AN EL PASO NATURAL GAS COMPANY OPERATIONS EMPLOYEE RESPONDED TO A REQUEST TO RESTART A COMPRESSOR ENGINE AT THE CORNUDAS COMPRESSOR STATION IN HUDSPETH COUNTY, TEXAS. UPON ARRIVAL, THE EMPLOYEE FOUND A 2" X 3" RELIEF VALVE RELEASING NATURAL GAS TO THE ATMOSPHERE. INVESTIGATION REVEALED THAT THE UPSTREAM REGULATOR HAD FAILED DUE TO ITS INTERNAL BOOT BEING CONTAMINATED BY PIPELINE SLUDGE. THE REGULATOR WAS PROMPTLY ISOLATED, REPAIRED, AND PLACED BACK INTO SERVICE WITH THE COMPRESSOR STATION RETURNING TO NORMAL OPERATION.
2021-02-26 10:37 | YES | YES | GT (Gas Transmission) | 20170026 | 17565 | 2017-03-29 14:12 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2017-02-27 12:10 | 2017 |  |  | 38.6714 | -121.1708 | 1172063 | 2017-02-27 14:10 |  | NATURAL GAS |  | 0.22 | 2.63 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 |  | YES |  | 2017-03-01 17:47 | 2017-03-02 03:13 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-02-27 12:10 | 2017-02-27 12:10 | ONSHORE | CA | 95630 | FOLSOM | SACRAMENTO | MILEPOST | MP 11.77 | DFM 0617-06 | ROUTE ID 23128 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | SAVE A VALVE, BLOWDOWN ASSEMBLY | 2017 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STEEL SAVE A VALVE, ALUMINUM ASSEMBLY | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | YES | METHOD2 | 197 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 15954.5201926639 | 0 | 0 | 0 | 0 | N/A |  | 15000 | 7323.54575768804 | 15954.5201926639 | [8 empty] | 485 |  | 500 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL |  | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER WAS NOT INVOLVED | [12 empty] | YES | 3 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | BLOWDOWN ASSEMBLY BECAME LOOSE AND INJURED AN EMPLOYEE |  | YES |  | YES | THE PROCEDURE DID NOT RESTRICT THE CONFIGURATION OF THE BLOWDOWN ASSEMBLY | CONSTRUCTION | NO | [150 empty] | STEPHEN RAMOS | REGULATORY COMPLIANCE | s3rc@pge.com | 925-413-7311 |  |  |  |  | SUSIE RICHMOND | MANAGER REGULATORY COMPLIANCE | 925-328-5776 | gsr8@pge.com | ON MONDAY, FEBRUARY 27, 2017, AT 1215 HOURS, PG&E WAS NOTIFIED OF AN INCIDENT AT 990 RILEY STREET IN FOLSOM. AS PART OF PG&ES PIPELINE REPAIR OF THREE INDICATIONS IDENTIFIED ON DFM 0617-06 AT MILE POINT (MP) 11.77, THE CREW WELDED A SAVE A VALVE (SAV) ON THE 12-INCH STEEL TRANSMISSION PIPE. THE CREW CONNECTED THE SAV TO AN ASSEMBLY WHICH CONSISTED OF A 2-INCH DIAMETER 90 DEGREE ELBOW TO A 2-INCH DIAMETER NIPPLE, TO A 2-INCH DIAMETER 90 DEGREE ELBOW, WHICH CONNECTED TO A 4 TO 6-FEET LONG 2-INCH DIAMETER ALUMINUM STACK. IN THE PROCESS OF CLEARING THE FITTING OF METAL SHAVINGS FROM THE TAPPING PROCESS, A PORTION OF THE ASSEMBLY CAME LOOSE AND INJURED AN EMPLOYEE. THE EMPLOYEE WAS TAKEN TO THE HOSPITAL AND IS IN STABLE CONDITION. THE APPARENT CAUSE OF THE INCIDENT IS INCORRECT OPERATIONS. THE ROOT CAUSE THAT THERE IS NO STANDARD PROCEDURE TO REMOVE METAL SHAVINGS AND THE PROCEDURE DID NOT ADEQUATELY ADDRESS TEMPORARY VENT STACK CONFIGURATIONS. AS A RESULT OF THE INCIDENT, A SMALL GAS LEAK WAS BEING RELEASED TO ATMOSPHERE FROM THE SAV. THE FLOW OF GAS WAS STOPPED ON 3/1/17 AT 1747 HOURS. REPAIRS TO THE LEAK AND IN THE COURSE, THE THREE INDICATIONS WERE REMOVED BY REPLACING A SECTION OF PIPE, ON 3/2/17 AT 0313 HOURS. THE USE OF A BYPASS DURING THE REPAIRS RESULTED IN NO CUSTOMER IMPACT. POLICE DEPARTMENT, FIRE DEPARTMENT & MEDIA (FOX 40) WAS REPORTED ON-SITE. THE EVENT WAS REPORTED TO THE DOT (NRC# 1172063) AND CPUC DUE TO INJURY AND MEDIA PRESENCE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170027 | 17311 | 2017-03-29 20:42 | SUPPLEMENTAL FINAL | 31531 | ONEOK WESTEX TRANSMISSION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2017-03-02 19:53 | 2017 |  |  | 31.4327 | -102.949 | 1172420 | 2017-03-03 17:20 |  | NATURAL GAS |  | 69217 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THERE WAS NO NEED TO SHUTDOWN THE FACILITY TO STOP THE GAS RELEASE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-03-03 06:30 | 2017-03-03 06:58 | ONSHORE | TX | 79730 | Not Within a Municipality | WARD | MILEPOST | 0 | ONEOK WESTEX RED RIVER PIPELINE | WICKETT II TURBINE COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2016 |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENDED CLOSING/OPENING OF VALVES. | CLASS 1 LOCATION | NO |  | 68 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 179039 | 163975.622596154 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 179039 | 170000.973557692 | 163975.622596154 | [8 empty] | 767 |  | 1069 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES |  | YES |  |  |  | YES | YES | CONTROLLER DID NOT RESPOND APPROPRIATELY TO THE ALARM. | YES | 1 | 0 | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [204 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | [5 empty] | YES |  |  | OTHER MAINTENANCE | YES | NO, THEY WERE NOT QUALIFIED FOR THE TASK(S) NOR WERE THEY PERFORMING THE TASK(S) UNDER THE DIRECTION AND OBSERVATION OF A QUALIFIED INDIVIDUAL | [149 empty] | C. ROSS MOHR | REGULATORY COMPLIANCE SPECIALIST | charles.mohr@oneok.com | 8175984601 | 9185915032 |  |  |  | WESLEY DUNBAR | VP NATURAL GAS PIPELINE OPERATIONS | 9185887424 | wesley.dunbar@oneok.com | ON 2 MARCH 2017 AT 15:45 P.M. MAINTENANCE CONCERNS REGARDING FILTERS AT THE RECENTLY CONSTRUCTED WICKETT II TURBINE COMPRESSOR STATION PROMPTED AN INSPECTION, DURING WHICH A CONSTRUCTION INSPECTOR CLOSED THREE VALVES TO FACILITATE THE MAINTENANCE INSPECTION. THE VALVE CLOSURES RESULTED IN ISOLATING THE GAS SUPPLY LINES THAT SUPPLIED THE ACTUATOR FOR THE SUCTION PIPING ESD VENT VALVE. A PRESSURE REGULATOR ON THE GAS SUPPLY LINE ASSOCIATED WITH THE SUCTION PIPING ESD VENT VALVE SUBSEQUENTLY MALFUNCTIONED CAUSING THE VENT VALVE TO FAIL OPEN AT APPROXIMATELY 19:53 P.M. THE CONTROLLER OBSERVED THE SCADA ALARM AND ACKNOWLEDGED THE EVENT IN THE SYSTEM BUT HE FAILED TO RECOGNIZE THE POTENTIAL CAUSE AND MISINTERPRETED THE ALARM. HE DID NOT CALL OUT ANY FIELD EMPLOYEES TO INVESTIGATE THE CAUSE OF THE ALARM AND SUBSEQUENTLY, 69,217 MCF OF GAS VENTED TO ATMOSPHERE. THE VENT REMAINED OPEN UNTIL AN EMPLOYEE ARRIVED ON LOCATION AT 06:30 A.M. ON 3 MARCH 2017. AT APPROXIMATELY 06:58 A.M. THE EMPLOYEE RESTORED PRESSURE TO THE GAS SUPPLY LINES AND CLOSED THE VENT VALVE STOPPING THE VENTING OF GAS. IN THE IMMEDIATE AFTERMATH OF THE INCIDENT DIFFICULTY IN DETERMINING THE START TIME OF THE VENTING WAS THE PRIMARY CAUSE OF THE DELAY FOR DETERMINING THIS RELEASE EXCEEDED 3,000 MCF. TO CORRECT THE SITUATION OPERATIONS PERSONAL HAVE AUGMENTED THE LOGIC OF THE PLC SYSTEM TO ESD THE ENTIRE STATION WHEN EITHER THE DISCHARGE PIPING OR SUCTION PIPING ESD VENT VALVES OPEN FOR ANY REASON.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170028 | 17588 | 2017-03-30 16:04 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2017-02-28 10:59 | 2017 |  |  | 39.3695 | -123.2394 | 1172145 | 2017-02-28 17:15 |  | NATURAL GAS |  | 3995 | 0.6 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-03-03 08:00 | 2017-03-14 01:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 1 | 2017-02-28 10:59 | 2017-02-28 11:27 | ONSHORE | CA | 95470 | REDWOOD VALLEY | MENDOCINO | MILEPOST | MP 130 | LINE 21E | ROUTE ID 32661 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 |  | 0.172 | 42000 | API 5L X-42 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COLD APPLIED TAPE | [28 empty] | 1972 | 1972 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 2 LOCATION | NO |  | 160 |  | NO | NO | NO |  | 0 | 0 | 2 | 2.12726935902186 | 12000 | 10990.3846153846 | 400000 | 425453.871804372 | 0 | 0 | 0 | 0 | N/A |  | 412002 | 206689.760780346 | 436446.383689116 | [8 empty] | 400 |  | 720 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 100 | NO |  |  | YES | YES |  | YES | LAUNCHER AND RECEIVER INSTALLATION | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WEREN'T ANY ALARMS. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED |  | YES | [15 empty] | STRESS CORROSION CRACKING | [12 empty] | YES | SECTION OF PIPE WAS LOCATED IN A GEOLOGICALLY UNSTABLE AREA WITH A HISTORY OF LANDSLIDES (LAND MOVEMENT) | [55 empty] | NO | [63 empty] | YES | 1972 | 1525 | Yes, and an investigative dig was cunducted at the point of the Accident | 2017 | [12 empty] | YES | 2017 |  |  | 2017 |  |  |  | YES |  |  | YES | [52 empty] | STEPHEN RAMOS | GAS ENGINEER | s3rc@pge.com | 925-413-7311 |  |  |  |  | SUSIE RICHMOND | MANAGER REGULATORY COMPLIANCE | 925-328-5776 | gsr8@pge.com | ON TUESDAY, FEBRUARY 28, 2017, AT 1059 HOURS, PG&E WAS NOTIFIED OF A GAS ODOR NEAR 16500 TOMKI ROAD, REDWOOD VALLEY. PG&ES GAS SERVICE REPRESENTATIVE (GSR) WAS ON SITE APPROXIMATELY AT 1127 HOURS. THE GSR MEASURED 20% GAS IN AIR AT THE LOCATION. PG&E CREWS ARRIVED ON-SITE AND CLASSIFIED THE LEAK AS GRADE 1. THE LEAK WAS ALONG LINE 21E AT MILE POINT (MP) 130. THE OPERATING PRESSURE OF THE SYSTEM WAS LOWERED FROM 400 TO 240 PSIG. LNG WAS USED FOR SUPPORT. ON 3/3/17, THE LEAK WAS EXCAVATED AND THE SOURCE OF LEAK WAS DETERMINED. THE CLEARANCE WAS EXECUTED ON 3/3/17 BY 0800 HOURS TO ISOLATE THE LEAK. THE LEAK WAS CONTINUOUSLY MONITORED UNTIL THE REPAIRS WERE COMPLETED. FOLLOWING THE REPAIR OF THIS LEAK, THE PIPE WAS CUT OUT AND METALLURGICAL TESTING WAS PERFORMED. THE DIRECT CAUSE OF THE LEAK WAS DETERMINED TO BE NEAR NEUTRAL PH (NNPH) SCC IN THE CIRCUMFERENTIAL DIRECTION. THIS SECTION OF PIPE WAS LOCATED IN A GEOLOGICALLY UNSTABLE AREA WITH A HISTORY OF LANDSLIDES. APPROXIMATELY 100 FEET OF PIPE WAS REPLACED AND THE SYSTEM WAS RESTORED TO NORMAL OPERATIONS ON 3/14/17 BY 0100 HOURS. THERE WAS NO CUSTOMER IMPACT. THERE WERE NO INJURIES OR FATALITIES REPORTED. THERE WAS NO MEDIA, POLICE OR FIRE DEPARTMENT REPORTED. THIS INCIDENT WAS REPORTED TO THE DOT AND CPUC ONCE IT WAS DETERMINED THAT REPAIRS TO GAS FACILITIES WOULD EXCEED $50,000 ON 2/28/17 AT APPROXIMATELY 1700 HOURS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170029 | 30831 | 2017-04-03 17:36 | SUPPLEMENTAL FINAL | 21252 | VIKING GAS TRANSMISSION CO | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2017-03-03 20:45 | 2017 |  |  | 45.3136 | -92.5877 | 1172444 | 2017-03-04 10:02 |  | NATURAL GAS |  | 23989 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-03-03 20:45 | 2017-03-04 01:48 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-03-03 20:45 | 2017-03-03 20:58 | ONSHORE | WI | 54020 | Not Within a Municipality | POLK | MILEPOST | CS 2222 | OSCEOLA COMPRESSOR STATION | CS 2222 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1967 |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENDED EMERGENCY SHUTDOWN OF THE COMPRESSOR STATION. ICE IN VALVE ACTUATOR BARRED CLOSURE OF THE DISCHARGE BLOCK VALVE ALLOWING GAS TO CONTINUE TO VENT. | CLASS 1 LOCATION | NO |  | 490 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 60000 | 54951.9230769231 | 0 | 0 | 1000 | 1063.63467951093 | 0 | 0 |  |  | 61000 | 57459.3902299997 | 56015.557756434 | [8 empty] | 745 |  | 877 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. THE CONTROLLER TOOK APPROPRIATE ACTIONS WHEN STATION ALARMED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES |  |  | YES |  |  | YES | [24 empty] | YES | FROZEN VALVE OPERATOR | [161 empty] | DUANE FOURNIER | REGULATORY COMPLIANCE COORDINATOR | duane.fournier@oneok.com | 515-491-3551 |  |  |  |  | DUANE FOURNIER | REGULATORY COMPLIANCE COORDINATOR | 515-491-3551 | duane.fournier@oneok.com | THE INITIAL TRIGGER FOR THE EVENT WAS A BLOWN CIRCUIT PROTECTION FUSE. THE LOSS OF POWER ON THE CIRCUIT RESULTED IN AN UNINTENDED EMERGENCY SHUTDOWN OF THE OSCEOLA COMPRESSOR STATION. THE ESD ACTIVATED AND OPERATED AS DESIGNED. OPERATIONS PERSONNEL WERE NOTIFIED IMMEDIATELY AND ARRIVED ON SITE TO FIND GAS BLOWING FROM THE STATION DISCHARGE BLOW OFF. OPERATIONS ASSESSED THE SITUATION ON THE GROUND TO DETERMINE SAFETY OF THE ENVIRONMENT AND DETERMINE CAUSE OF THE ESD. ATTEMPTS WERE MADE TO CLOSE THE DISCHARGE BLOCK VALVE BUT THE ACTUATOR DID NOT FUNCTION. OPERATORS ISOLATED THE ESD SYSTEM TO ALLOW USE OF REVERSING GAS AND CLOSED THE DISCHARGE AND SUCTION BLOW OFF VALVES. THE DISCHARGE BLOCK VALVE ACTUATOR WAS FOUND TO CONTAIN ICE WHICH IMPEDED FUNCTION. THE ACTUATOR WAS THAWED, WATER DRAINED, TESTED AND RETURNED TO SERVICE. THIS REPORT WAS SUBMITTED IN MAY OF 2017 BUT WAS NOT ACCEPTED BY THE SYSTEM FOR UNKNOWN REASON.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170030 | 17428 | 2017-04-07 11:27 | SUPPLEMENTAL FINAL | 18152 | SEA ROBIN PIPELINE CO | 800 E. SONTERRA BLVD | SAN ANTONIO | TX | 78258 | 2017-03-09 10:40 | 2017 |  |  | 28.6722 | -90.6646 | 1172831 | 2017-03-09 11:03 |  | NATURAL GAS |  | 2110 | 6509 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-03-09 11:30 | 2017-08-13 18:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-03-10 19:00 | 2017-03-10 19:00 | OFFSHORE | [28 empty] | 68 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SOUTH TIMBALIER | 100 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 18 |  | 0.438 | 52000 | API 5LX | SEAMLESS |  | U.S STEEL | COAL TAR | [28 empty] | 1972 | 1972 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 439 |  | NO | NO | NO |  | 0 | 0 | 19332 | 20562.1856243053 | 6267 | 5739.72836538462 | 266243 | 283185.287977029 | 0 | 0 | 0 | 0 |  |  | 291842 | 145378.742336015 | 309487.201966718 | [8 empty] | 753 |  | 1200 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 55281 | NO |  |  | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS DUE TO A SMALL PIN HOLE LEAK | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | PIN HOLE LEAK |  |  |  |  | YES | LOW FLOW |  |  | YES | HISTORICAL DATA |  |  |  |  | YES | PINHOLE AT THE 3:30 CLOCK POSITION | YES | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | (713)857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | (713)857-5479 | nathan.hlavaty@energytransfer.com | AT APPROXIMATELY 10:40 AM ON 3/9/2017, AERIAL OBSERVATION REPORTED BUBBLES WITH A SLIGHT SILVER SHEEN IN THE AREA NEAR A SEA ROBIN PIPELINE IN THE SOUTH TIMBALIER 100 AREA. THE NRC WAS NOTIFIED (NRC #1172831), AT 11:03 AM ON 3/9/17 OF A POSSIBLE LEAK. WE WERE ABLE TO MAKE A SECOND FLIGHT ON 3/9/2017 AND OBSERVED BUBBLES WITH NO SHEEN AND BASED ON THE COORDINATES FOR THE LEAK, WE SHUT DOWN THE PIPELINE AT 11:30 AM ON 3/9/17. A DIVE VESSEL WAS DISPATCHED ON 3/9/2017 AND WAS ABLE TO ASSESS THE LEAK ON 3/10/2017. THE PIPELINE REMAINED SHUT IN UNTIL REPAIRS WERE COMPLETED. SUPPLEMENT/FINAL SUBMITTED ON 09/08/17 CREATED TO CORRECT PART A, QUESTION 5; LATITUDE AND LONGITUDE, QUESTION 15B; FACILITY RESTART; PART D, QUESTION 7B COSTS; PART E, QUESTION 1; CORRECTING THE PRESSURE WAS 753 PSIG NOT 780 PSIG, QUESTION 6D; ANSWER SHOULD HAVE BEEN NO.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170031 | 30636 | 2017-04-21 16:37 | SUPPLEMENTAL FINAL | 4070 | EAST TENNESSEE NATURAL GAS, LLC (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2017-03-17 06:17 | 2017 |  |  | 36.4225 | -86.5081 | 1173451 | 2017-03-17 13:11 |  | NATURAL GAS |  | 6649 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THIS IS A MAIN LINE RELIEVE VALVE. THE LINE & METER STATION REMAINED IN SERVICE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-03-17 06:17 | 2017-03-17 07:00 | ONSHORE | TN | 37066 | GALLATIN | SUMNER | MILEPOST | 101 | GALLATIN WEST M&R 59025 | LINE 3100 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | RELIEF VALVE | 2000 |  | CARBON STEEL |  | LEAK |  |  | OTHER | RELIEF VALVE BLEW TO ATMOSPHER | [5 empty] | CLASS 1 LOCATION | NO |  | 407 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 19947 | 18268.7668269231 | 1003 | 1066.82558354946 | 0 | 0 | 0 | 0 |  |  | 20950 | 19429.7611891513 | 19335.5924104725 | [8 empty] | 717 |  | 720 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE MALFUNCTION OF THE RELIEF VALVE COULD NOT BE ASSOCIATED WITH THE ROLES AND RESPONSIBILITIES OF A CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | RELIEF VALVE PILOT FAILED DUE TO FREEZING IN THE DEVICE | [161 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | dwayne.teschendorf@enbridge.com | 713-627-5573 |  |  |  |  | NATHAN ATANU | SUPERVISOR OPERATIONAL COMPLIANCE | 713-627-5008 | nathan.atanu@enbridge.com | A NATURAL GAS RELEASE THROUGH A RELIEF VALVE AT THE EAST TENNESSEE M&R 59025 OCCURRED AT 6:17 AM ON MARCH 17, 2017. THE AMOUNT OF GAS RELEASED WAS 6649 MCF. ROOT CAUSE FOR THE GAS RELEASE WAS THE RELIEF VALVE PILOT FROZE AND RESEAT DID NOT OCCUR.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170032 | 30290 | 2017-04-23 14:34 | SUPPLEMENTAL FINAL | 189 | AMERICAN MIDSTREAM (ALATENN), LLC | BLACK BEAR TRANSMISSION, LLC 1501 MCKINNEY, SUITE 800 | HOUSTON | TX | 77010 | 2017-02-27 15:51 | 2017 |  |  | 34.7271 | -87.8487 | 1174017 | 2017-03-24 14:40 |  | NATURAL GAS |  | 549 | 1282 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-03-08 10:30 | 2017-03-09 13:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-02-27 15:51 | 2017-02-27 17:30 | ONSHORE | AL | 35674 | Not Within a Municipality | COLBERT COUNTY | MILEPOST | STATION #832 | ALATENN | ML 101 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PULSATION BOTTLE OR DRIP/DRIP COLLECTION DEVICE | [38 empty] | 1956 |  | CARBON STEEL |  | LEAK |  |  | OTHER | FRACTURED WELD-OUTSIDE FORCE | [5 empty] | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO | NO |  | 0 | 0 | 3584 | 3812.06669136717 | 1535 | 1405.85336538462 | 56000 | 59563.5420526121 | 6000 | 6381.80807706558 | 0 | 0 |  |  | 67119 | 33478.0070173782 | 71163.2701864295 | [8 empty] | 690 |  | 800 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 28407 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | APPARENT CAUSE WAS DUE TO FRACTURE ON A DRIP LEG, CONTROLLER ACTIONS DID NOT AFFECT OR CAUSE LEAK, NO INVESTIGATION INTO CONTROLLERS OR CONTROL ROOM ISSUES NECESSARY. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [103 empty] | OTHER OUTSIDE FORCE DAMAGE | [9 empty] | THE METALLURGICAL ANALYSIS BY STRESS ENGINEERING CONCLUDED: THE FRACTURE ORIGINATED AT THE OUTSIDE SURFACE FROM AN OVERLOAD DUE TO UNDETERMINED EXTERNAL FORCES. THERE WERE NO INDICATIONS OF WHAT INDUCED THE FORCES ON THIS DRIP LEG TO CAUSE THE FAILURE. ALTHOUGH 3RD PARTY MECHANICAL DAMAGE WAS NOT AN APPARENT CAUSE, CREWS HAVE BEEN REMINDED TO OBSERVE ROWS FOR ENCROACHMENTS AND THE POTENTIAL FOR THIRD PARTY DAMAGE TO OUR LINES THROUGH AERIAL PATROLS AND CONTINUING SURVEILLANCE. | [251 empty] | MIKE MYERS | MANAGER PIPELINE TRANSPORTATION COMPLIANCE | mmyers@americanmidstream.com | 3462413557 |  |  |  |  | RENE CASADABAN | VP AND COO | 3462413546 | No Email Address | OPERATIONS PERSONNEL AND CONTRACTORS FOUND A SMALL LEAK ON A DRIP LEG OFF THE MAINLINE. EXCAVATION OF THE LEAK IDENTIFIED APPARENT FAILURE AT A WELDMENT ON THE SMALL BORE DRIP PIPING. ADDITIONAL METALLURGICAL ANALYSIS BY STRESS ENGINEERING IN HOUSTON, TX FOUND THE FOLLOWING CONCLUSIONS: 1) THE PIPE ADJACENT TO THE SOCKOLET WELD FRACTURED. THE FRACTURE ORIGINATED AT THE OUTSIDE SURFACE FROM AN OVERLOAD DUE TO UNDETERMINED EXTERNAL FORCES. THE FRACTURE SURFACE PREDOMINANTLY EXHIBITED DUCTILE DIMPLES AND 45 DEGREE SHEAR LIPS. A FLAT REGION ON THE FRACTURE SURFACE EXHIBITED A BRITTLE-CLEAVAGE TYPE FRACTURE. SUMMARY OF OTHER CONCLUSIONS: 2) THERE WAS SOME INTERNAL CORROSION PITS AND EROSION NOTED IN THE SAMPLE. 3) METALLOGRAPHY THE PIPE AND SHOWED ELONGATED GRAINS AT THE FRACTURE ON BOTH OUTSIDE AND INSIDE SURFACES. THE PIPE AND SOCKOLET HAD A FERRITE-PEARLITE STRUCTURE, TYPICAL OF CARBON STEELS. 4) THE PIPE HAD AN AVG. HARDNESS OF 93 HRB, WITH MECHANICAL AND CHEMICAL PROPERTIES TO ASTM A106 GRADE B. TWO NRC REPORTS WERE FILED FOR THIS INCIDENT: 1) INITIAL NRC REPORT 1174017 MADE 3/25/2017 AT 14:22 CST WHEN COST OF REPAIRS DISCOVERED TO EXCEED $50,000. 2) SUPPLEMENTAL NRC REPORT 117064 MADE 3/25/3027 AT 12:15 CST TO UPDATE RELEASE QUANTITY OF GAS TO 2,125MCF. THE FINAL VOLUME CALCULATIONS SHOW A TOTAL OF 1831MCF WAS RELEASED, 549MCF UNINTENTIONALLY AS A RESULT OF THE LEAK AND 1242 MCF TO BLOW THE LINE DOWN FOR REPAIR & 40 MCF TO PURGE IT TO PUT IT BACK INTO SERVICE. SUPPLEMENTAL 30 DAY REPORT TO CORRECT GPS COORDINATES: LATITUDE: 34.727073, LONGITUDE: -87.85006. MAY 9 2018: REPORT CLOSED AS FINAL, NO UPDATE REQUIRED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170033 | 31835 | 2017-04-28 11:01 | SUPPLEMENTAL | 32420 | GRAMA RIDGE STORAGE AND TRANSPORTATION, LLC | 10375 RICHMOND AVENUE SUITE 1900 | HOUSTON | TX | 77042 | 2017-04-07 11:08 | 2017 |  |  | 32.4226 | -103.4638 | 1175143 | 2017-04-08 08:28 |  | NATURAL GAS |  | 1284 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-04-07 11:08 | 2017-04-28 08:15 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 0 | 2017-04-07 11:08 | 2017-04-08 00:20 | ONSHORE | NM | 88231 | EUNICE | LEA COUNTY | SURVEY STATION NO. | FACILITY | GRAMA RIDGE STORAGE AND TRANSPORTATION | COMPRESSOR UNIT C203 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | OTHER | COMPRESSOR BUILDING WITH OPEN WALLS |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2006 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | CAST IRON | OTHER | [8 empty] | THE FLANGE ON THE PACKING CASE OF COMPRESSOR NUMBER 203 FAILED. THIS FAILURE CAUSED THE RELEASE OF NATURAL GAS FROM THE PACKING CASE AND INTO THE ATMOSPHERE. THE GAS ENCOUNTERED AN IGNITION SOURCE AND IGNITED RESULTING IN AN EXPLOSION AND FIRE. THE FACILITY EMERGENCY SHUT DOWN (ESD) SYSTEM CORRECTLY CLOSED VALVES THEREBY STOPPING THE FLOW OF GAS. THE FIRE WAS EXTINGUISHED DUE TO THE LACK OF GAS TO FUEL IT. | CLASS 1 LOCATION | NO |  | 271 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 700 | 641.105769230769 | 1821766 | 1937693.49555391 | 0 | 0 | 0 | 0 |  |  | 1822466 | 890117.107514892 | 1938334.60132314 | [8 empty] | 3342 |  | 3850 | OTHER | OEM RATING |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE FLANGE ON THE PACKING CASE OF COMPRESSOR NUMBER 203 FAILED. THIS FAILURE CAUSED THE RELEASE OF NATURAL GAS FROM THE PACKING CASE AND INTO THE ATMOSPHERE. THE GAS ENCOUNTERED AN IGNITION SOURCE AND IGNITED RESULTING IN AN EXPLOSION AND FIRE. THE FACILITY EMERGENCY SHUT DOWN (ESD) SYSTEM CORRECTLY CLOSED VALVES THEREBY STOPPING THE FLOW OF GAS. THE FIRE WAS EXTINGUISHED DUE TO THE LACK OF GAS TO FUEL IT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | OTHER | PACKING FLANGE FAILURE | [13 empty] | YES | [169 empty] | SHERRI PEEBLES | DIRECTOR ENVIRONMENTAL HEALTH AND SAFETY | sherri.peebles@enstorinc.com | (281) 374-3081 |  |  |  |  | SHERRI PEEBLES | DIRECTOR ENVIRONMENTAL HEALTH AND SAFETY | (281) 374-3081 | sherri.peebles@enstorinc.com | ON APRIL 7, 2017 AT 11:08 PM MT AT THE ENSTOR GRAMA RIDGE GAS STORAGE FACILITY, THE OPERATOR ON-CALL RECEIVED AN ALARM INDICATING THAT COMPRESSOR UNIT C203 HAD SHUT DOWN. SHORTLY THEREAFTER, MULTIPLE OTHER ALARMS WERE RECEIVED. THE OPERATOR ARRIVED AT THE FACILITY AT 12:20 AM MT, AND OBSERVED A SMALL FIRE INSIDE THE COMPRESSOR BUILDING THAT EXTINGUISHED ITSELF SHORTLY THEREAFTER. THE OPERATOR NOTED THAT THE FACILITY HAD ACTIVATED THE EMERGENCY SHUT-DOWN SYSTEM PROPERLY AND AS DESIGNED. COMPANY MANAGEMENT AND SAFETY PERSONNEL WERE IMMEDIATELY NOTIFIED AND FACILITY PERSONNEL TOOK THE NECESSARY STEPS TO ENSURE CONDITIONS WERE SAFE TO BEGIN INVESTIGATING THE CAUSE OF THE FAILURE. THE NATIONAL RESPONSE CENTER AND THE STATE OF NEW MEXICO PRC WERE NOTIFIED AS SOON AS OPERATIONS PERSONNEL AND ENSTOR MANAGEMENT DETERMINED THE CONDITIONS AT THE FACILITY ADEQUATELY STABLE, SAFE AND MET THE DEFINITION OF THE INCIDENT AS DEFINED BY 49 CFR 191.3 AND STATE ADOPTED AMENDMENTS TO THE FEDERAL REGULATIONS. INDUSTRY EXPERTS WERE ENGAGED TO REVIEW AND DOCUMENT ALL PHYSICAL EVIDENCE AND SYSTEM DATA PERTAINING TO THE INCIDENT TO DETERMINE THE CAUSE AND MAKE RECOMMENDATIONS FOR FUTURE SAFE OPERATIONS AND REPAIRS. INDUSTRY EXPERTS WERE ENGAGED TO REVIEW AND DOCUMENT ALL PHYSICAL EVIDENCE AND SYSTEM DATA PERTAINING TO THE INCIDENT TO DETERMINE THE CAUSE AND MAKE RECOMMENDATIONS FOR FUTURE SAFE OPERATIONS AND REPAIRS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170034 | 17511 | 2017-04-28 16:08 | SUPPLEMENTAL FINAL | 13845 | NORTHWEST PIPELINE LLC | 295 CHIPETA WAY | SALT LAKE CITY | UT | 84108 | 2017-03-31 02:59 | 2017 |  |  | 41.6983 | -110.3824 | 1174510 | 2017-03-31 10:25 |  | NATURAL GAS |  | 6394 | 8760 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-03-31 09:33 | 2017-11-08 10:13 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 3 | 2017-03-31 07:09 | 2017-03-31 09:27 | ONSHORE | WY | 83101 | KEMMERER | LINCOLN | MILEPOST | 51.17 | N2 | EAST PAINTER LATERAL TO IGNACIO SUMAS MAIN LINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1989 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 350 |  | NO | NO | NO |  | 0 | 0 | 22951 | 24411.4795294554 | 16752 | 15342.5769230769 | 262150 | 278831.83123379 | 5000 | 5318.17339755465 | 0 | 0 |  |  | 306853 | 157544.209343917 | 323904.061083877 | [8 empty] | 704 |  | 850 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 2 | 0 | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | GASKET | [7 empty] | YES | [172 empty] | JOSH KUSHLAN | PIPELINE SAFETY ENGINEER | josh.kushlan@williams.com | (801) 584-6261 |  |  |  |  | JASON LAMBERT | MANAGER PIPELINE SAFETY | (801) 584-6657 | jason.lambert@williams.com | GAS CONTROL CALLED KEMMERER/MOXA DISTRICT TEAM LEAD AT 0835 ON MARCH 31, 2017 TO INFORM THAT THERE WAS A HIGH BOARD TEMPERATURE OF THE ROC CONTROLLER AT THE N2 SITE. THE GAS CONTROLLER FURTHER INFORMED THE TEAM LEAD THAT THE DOWNSTREAM PRESSURE TRANSMITTER WAS READING A -250 VALUE. THE TEAM LEAD IMMEDIATELY INSTRUCTED A TECHNICIAN TO GO TO THE N2 SITE TO INVESTIGATE THE ISSUE. ONCE THE TECHNICIAN ARRIVED CLOSE ENOUGH (APPROXIMATELY 1 MILE AWAY) TO SEE THE N2 SITE AT 0927 ON MARCH 31, 2017 THE TECHNICIAN NOTICED THAT ONE OF THE STRUCTURES AT THE N2 SITE WAS ON FIRE. THE TECHNICIAN IMMEDIATELY CALLED THE TEAM LEAD TO INFORM OF THE ISSUE. THE TEAM LEAD CALLED THE KEMMERER/MOXA DISTRICT MANAGER TO INFORM HIM OF THE FINDINGS. THE TEAM LEAD FURTHER INFORMED THE DISTRICT MANAGER THAT THE DISTRICT IS IN THE PROCESS OF ISOLATING THE SECTIONS OF THE PIPELINE TO ISOLATE THE GAS LEAK AND FIRE. FURTHER DISCUSSION WAS MADE IN REFERENCE THAT NOBODY WAS GOING TO GO DOWN TO THE N2 SITE UNTIL IT WAS MADE SAFE. THE DISTRICT UTILIZED MANUAL AND AUTOMATED VALVES UPSTREAM AND DOWNSTREAM OF THE N2 SITE TO ISOLATE THE N2 SITE. THE TEAM LEAD INSTRUCTED DISTRICT TECHNICIANS WHICH VALVE SITE TO REPORT TO AND THAT THEY NEEDED TO STAY TOGETHER AS TWO MAN TEAMS. WITH THE HELP OF GAS CONTROL THE DISTRICT WAS ABLE TO ISOLATE AND BLOWDOWN THE 1400 MAINLINE FROM MUDDY CREEK C/S TO MAINLINE BLOCK VALVE 6-4. ALSO IN CONJUNCTION WITH THE MAINLINE BEING BLOWN DOWN THE DISTRICT WAS ABLE TO ISOLATE MAINLINE BLOCK VALVE 98-3 ON THE EAST PAINTER LATERAL. ISOLATION WAS COMPLETE AT 1030 ON MARCH 31, 2017. THE SITE WAS CONFIRMED SAFE TO ENTER AT 1700 ON MARCH 31, 2017. AT THE TIME OF THE INCIDENT WILLIAMS RECOMMENDED THAT NO ONE BE EVACUATED. LATER IT WAS FOUND THAT LOCAL ENFORCEMENT HAD NOTIFIED RESIDENTS ON WAGONWHEEL ROAD AND REQUESTED THEY EVACUATE THE AREA. IT WAS CONFIRMED THAT 3 INDIVIDUALS DID LEAVE THEIR HOME AND WENT INTO TOWN FOR A FEW HOURS. SITE INVESTIGATION REVEALED AN INITIAL FAILURE OF ONE OF THE GASKETS ON ONE OF THE 6" CONTROL VALVES IN THE ANALYZER BUILDING AS THE LEADING CAUSE OF THE GAS RELEASE. BASED ON AVAILABLE EVIDENCE, THE SOURCE OF IGNITION IS INCONCLUSIVE. THE FAILED GASKET WAS NOT A MATERIAL ORIGINALLY SPECIFIED IN THE SITE DESIGN. NOR WAS IT A SUITABLE SUBSTITUTE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170035 | 17325 | 2017-05-05 14:02 | ORIGINAL FINAL | 2564 | COLORADO INTERSTATE GAS CO | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2017-05-01 09:35 | 2017 |  |  | 37.7507 | -102.7453 | 1177294 | 2017-05-01 10:15 |  | NATURAL GAS |  | 21047 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-05-01 09:45 | 2017-05-01 15:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-05-01 09:35 | 2017-05-01 09:35 | ONSHORE | CO | 81052 | LAMAR | PROWERS | MILEPOST | M.P. 151 | SPRINGFIELD COMPRESSOR STATION | 0003-A FOURWAY - KIT CARSON MAINLINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1995 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | REGULATOR INTERNAL SOFT GOODS (RUBBER) | OTHER | [8 empty] | FUEL GAS REGULATOR FAILURE WITH GAS RELEASE TO THE ATMOSPHERE | CLASS 1 LOCATION | NO |  | 420 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 67350 | 61683.5336538462 | 400 | 425.453871804372 | 0 | 0 | 0 | 0 |  |  | 67750 | 64145.414745846 | 62108.9875256505 | [8 empty] | 715 |  | 936 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE COMPRESSOR STATION WAS OFFLINE AT THE TIME OF THE REGULATOR FAILURE AND ALL PRESSURES REMAINED WITHIN NORMAL PARAMETERS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [25 empty] | YES | RUBBER BOOT FAILED DUE TO NORMAL WEAR AND TEAR, RESULTING IN CRACKS IN MATERIAL | [161 empty] | KENNETH PETERS | SENIOR PIPLINE ENGINEER | ken_peters@kindermorgan.com | 2053257554 | 2053253508 |  |  |  | REJI GEORGE | DIRECTOR CODES AND STANDARDS | 7134205433 | reji_george@kindermorgan.com | ON MONDAY, MAY 1, 2017, COLORADO INTERSTATE GAS (CIG) PERSONNEL ARRIVED AT THE SPRINGFIELD (CO) COMPRESSOR STATION AND FOUND NATURAL GAS VENTING TO ATMOSPHERE FROM THE FIRST CUT FUEL GAS RELIEF VALVE. THE FIRST CUT FUEL GAS PRESSURE REGULATOR HAD FAILED DUE TO A FAILURE OF ITS INTERNAL SOFT GOODS (RUBBER BOOT). THE VENTING GAS WAS STOPPED BY CLOSING ISOLATION VALVES AND THE FAILED REGULATOR WAS REPAIRED. IT WAS RETURNED TO SERVICE MONDAY, MAY 1, 2017, AT 3:00 PM MDT. SCADA INFORMATION REVEALED THAT THE REGULATOR HAD FAILED AT THIS UNMANNED STATION ON APRIL 29, 2017, AT APPROXIMATELY 7:00 PM MDT. HOWEVER, THIS FUEL GAS SCADA DATA IS NOT PART OF THE INFORMATION DELIVERED TO CIG'S GAS CONTROL. IT WAS DETERMINED THAT A VOLUME OF 21,047 MCF OF NATURAL GAS HAD BEEN RELEASED, THUS MEETING PHMSA INCIDENT REPORTING CRITERIA.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170036 | 31779 | 2017-05-15 16:17 | SUPPLEMENTAL FINAL | 4070 | EAST TENNESSEE NATURAL GAS, LLC (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2017-04-20 02:15 | 2017 |  |  | 35.3077 | -84.7541 | 1176152 | 2017-04-20 09:07 |  | NATURAL GAS |  | 9000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-04-20 09:05 | 2017-04-20 09:10 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-04-20 02:15 | 2017-04-20 09:05 | ONSHORE | TN | 37309 | CALHOUN | MCMINN | MILEPOST | 199.51 | M&R 59008 | BOWATER METER STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 2017 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VENTING INCIDENT | CLASS 1 LOCATION | NO |  | 141 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 27000 | 24728.3653846154 | 1500 | 1595.45201926639 | 0 | 0 | 0 | 0 |  |  | 28500 | 26369.373806538 | 26323.8174038818 | [8 empty] | 199 |  | 649 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  |  |  | YES | [6 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [25 empty] | YES | REGULATOR DIAPHRAGM FAILED | [161 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | dwayne.teschendorf@enbridge.com | 713-627-5573 |  |  |  |  | NATHAN ATANU | SUPERVISOR OPERATIONAL COMPLIANCE | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: AT APPROXIMATELY 2:15 A.M. ON APRIL 20, 2017 AT ETNG'S BOWATER METER AND REGULATING STATION, A REGULATOR FAILURE CAUSED AN INCREASE IN PRESSURE RESULTING IN THE ACTIVATION OF A RELIEF VALVE. AN ALARM WAS TRIGGERED IN THE CONTROL ROOM, WHICH WAS ACKNOWLEDGED BY THE CONTROL ROOM OPERATOR. THE CONTROL ROOM OPERATOR ASSUMED IT WAS AN ERRONEOUS READING, AND THUS DID NOT FOLLOW PROCEDURES WHICH REQUIRED AN IMMEDIATE NOTIFICATION TO FIELD PERSONNEL TO CONDUCT A FOLLOW-UP FIELD INVESTIGATION. CONTROL ROOM SHIFT CHANGE OCCURRED AT APPROXIMATELY 7:00 A.M. , AND THE CONTROL ROOM OPERATOR LEAVING DID NOT VERBALLY DISCUSS THE ALARM WITH THE ONE COMING ON SHIFT, THOUGH IT WAS IN THE SHIFT LOG. AT APPROXIMATELY 6:45 A.M., THE LOCAL FIRE DEPARTMENT CALLED THE CONTROL ROOM TO REPORT THE GAS VENTING FROM THE RELIEF VALVE. THE CONTROL ROOM OPERATOR NOW ON SHIFT CALLED FIELD OPERATIONS, AND A TECHNICIAN WAS DISPATCHED TO THE SITE, SHUTTING OFF THE FLOW OF GAS. THE ESTIMATED GAS LOSS WAS 9 MMSCF DUE TO THE EXTENDED DURATION OF THE RELEASE. SUPPLEMENTAL REPORT: CONTROL ROOM SHIFT CHANGE OCCURRED AT APPROXIMATELY 5:10 A.M., AND THE CONTROL ROOM OPERATOR LEAVING DID NOT VERBALLY DISCUSS THE ALARM WITH THE ONE COMING ON SHIFT, THOUGH IT WAS IN THE SHIFT LOG.
2021-02-26 10:37 | YES | NO | UNGS (Underground Natural Gas Storage) | 20170037 | 31350 | 2017-05-18 12:36 | SUPPLEMENTAL FINAL | 2392 | CITIZENS GAS & COKE UTILITY | 2020 NORTH MERIDAN ST | INDIANAPOLIS | IN | 46202 | 2017-04-18 17:30 | 2017 |  |  | 39.0665 | -87.0344 | 1176036 | 2017-04-18 20:29 |  | NATURAL GAS |  | 41524 | 2010 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | STORAGE WELL BLOWOUT; FACILITIES WERE NOT IN USE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 20 | 2017-04-18 17:30 | 2017-04-18 17:30 | ONSHORE | IN | 47465 | WORTHINGTON | GREENE COUNTY | SURVEY STATION NO. | WELLHEAD | CITIZENS GAS - DIXON STORAGE FIELD | EVANS #4 WELL | NO | PIPELINE RIGHT-OF-WAY | BELOWGROUND STORAGE OR ABOVEGROUND STORAGE VESSEL, INCLUDING ATTACHED APPURTENANCE |  |  |  |  | NO | [22 empty] | INTRASTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | UNDERGROUND GAS STORAGE OR CAVERN | [38 empty] | 2017 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | TEMPORARY LIQUID AND GEL PLUG | OTHER | [8 empty] | WELL WAS TEMPORARILY KILLED WITH A LIQUID AND GEL PLUG WELL KICKED LIQUID AND GEL AND LEAKED | CLASS 1 LOCATION | NO |  | 47 |  | NO | NO | NO |  | 24474 | 26031.3951463505 | 6875 | 7312.48842163764 | 142098 | 130142.639423077 | 0 | 0 | 38473 | 40921.217024824 | 65813 | 70000.9891626528 | LOCAL EMERGENCY RESPONSE ESCALATION TO WELLL BLOWOUT CONTRACTOR |  | 277733 | 201146.725576781 | 274408.729178542 | [8 empty] | 660 |  | 750 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | [204 empty] | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | [5 empty] | YES |  |  | OTHER MAINTENANCE | NO | [150 empty] | MICHAEL W BARTONE | DIRECTOR GAS SUPPLY | mbartone@citizensenergygroup.com | 3179276111 | 3179276111 |  |  |  | CHRISTOPHER H BRAUN | VICE PRESIDENT OF ENERGY OPERATIONS | 3179274604 | cbraun@citizensenergygroup.com | THE EVENING OF APRIL 18, 2017, A CONTRACTOR FOR CITIZENS GAS WAS PERFORMING MAINTENANCE ON A NATURAL GAS WELL THAT IS PART OF CITIZENS' UNDERGROUND STORAGE FACILITIES NEAR WORTHINGTON, INDIANA. AT APPROXIMATELY 5:30 P.M., THE CONTRACTORS FLUID AND GEL PLUG THAT WAS SET TO TEMPORARILY CONTAIN THE WELL PRESSURE FAILED AND GAS BEGAN VENTING FROM THE WELL. - CITIZENS IMMEDIATELY IMPLEMENTED ITS WELL CONTROL CONTINGENCY PLAN AND BEGAN WORKING WITH LOCAL FIRE, POLICE AND OTHER AGENCIES TO TAKE MAKE-SAFE ACTIONS AND TO CONTROL THE WELL AND RESUME NORMAL OPERATIONS AS QUICKLY AS POSSIBLE. - AS A PRECAUTIONARY MEASURE TO AVOID ANY ACCIDENTAL IGNITION SOURCES, ELEVEN (11) NEARBY HOMES WERE EVACUATED AND ELECTRIC POWER WAS SHUT OFF TO APPROXIMATELY 50 HOMES. ADDITIONALLY, PORTIONS OF STATE ROAD 67 AND LOCAL ROADS NEAR THE WELL SITE WERE CLOSED TEMPORARILY. - BY THE EVENING OF APRIL 19, STEPS WERE TAKEN TO REDUCE THE FLOW FROM THE WELL. A VALVE WAS INSTALLED BRINGING THE WELL UNDER CONTROL AND NORMAL, SAFE OPERATIONS RESUMED. ALL RESIDENTS THAT WERE EVACUATED FROM THEIR HOMES WERE ALLOWED TO RETURN AND THE LOCAL ROADS THAT WERE CLOSED HAD REOPENED TO TRAFFIC. POWER HAS ALSO BEEN RESTORED TO ALL HOMES AFFECTED BY THE INCIDENT. - NO INJURIES OR FIRE OCCURRED AS A RESULT OF THE INCIDENT. NRC REFERENCE NUMBERS 1) 1176036 - INITIAL REPORT 4/18/2017 @ 8:29PM 2) CALL MADE ON 4/19/2017 @ ~6PM TO NOTIFY THAT ISSUE HAD BEEN RESOLVED (NO REFERENCE NUMBER) 3) 1176216 - 48 HOUR FOLLOW-UP 4/20/2017 @ 3:44PM -AFTER ACTION REVIEW HELD WITH EXTERNAL EMERGENCY RESPONDERS AND LOCAL AUTHORITIES (5/19/2017) -ROOT CAUSE ANALYSIS REPORT INVESTIGATION COMPLETE (7/27/2017) -DEBRIEFING WITH STATE REGULATORY COMMISSION PIPELINE SAFETY DEPARTMENT (8/31/2017) -WELL REMAINED OUT OF SERVICE FROM APRIL 2017 (POST-INCIDENT) THROUGH MAY 2018 -APPROVED PLAN FROM CONTINUED WORK TO REMOVE LEGACY TUBING FROM WELL (4/10/2018) -REMOVED OLD COIL TUBING; INSTALLED NEW TUBING; SUCCESSFULLY LOGGED THE WELL (MAY 2018) -WELL PLACED BACK IN SERVICE (5/14/2018)
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170038 | 17330 | 2017-05-18 16:19 | ORIGINAL FINAL | 13845 | NORTHWEST PIPELINE LLC | 295 CHIPETA WAY | SALT LAKE CITY | UT | 84108 | 2017-03-29 10:01 | 2017 |  |  | 47.2357 | -122.2257 | 1177100 | 2017-03-29 09:26 |  | NATURAL GAS |  | 21000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELIEF VALVE OPENED AS DESIGNED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-03-29 10:01 | 2017-03-29 11:15 | ONSHORE | WA | 98390 | SUMNER | PIERCE | MILEPOST | 0.84 | NORTH TACOMA METER STATION | NORTH TACOMA LATERAL/LOOP | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | OTHER | RELIEF VALVE VENT PIPE |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1992 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | SOFT RUBBER REGULATOR PARTS | OTHER | [8 empty] | FLOW CONDITIONS CAUSED VIBRATION WHICH LED TO A HEAT EFFECTED ZONE WHERE THE REGULATOR FAILED ON A MANUFACTURING INCLUSION. | CLASS 3 LOCATION | NO |  | 230 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 68250 | 62507.8125 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 68250 | 64804.6875 | 62507.8125 | [8 empty] | 313 |  | 546 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER REACTED CORRECTLY | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [10 empty] | YES |  |  | YES | [174 empty] | JOSH KUSHLAN |  | josh.kushlan@williams.com | 8015846261 |  |  |  |  | JARED ELLSWORTH | MANAGER PIPELINE SAFETY | 8015846539 | jared.ellsworth@williams.com | AT 10:01 AM MARCH 29 2017 GAS CONTROL RECEIVED A HIGH PRESSURE ALARM AT THE NORTH TACOMA METER STATION. THIS WAS DUE TO AN 8 INCH SINGER AXIAL FLOW REGULATOR SLEEVE THAT FAILED BY RUPTURING. AT 11:15 AM THE FAILED REGULATOR RUN 1 WAS ISOLATED ALLOWING THE STATION TO FLOW ONLY THROUGH REGULATOR RUN 2 AT WHICH POINT THE RELIEF VALVE CLOSED. AT 12:14 PM NORTH TACOMA METER STATION WAS RETURNED TO NORMAL OPERATIONS. GAS LOSS WAS CALCULATED AS 21 MMSCF. ALTHOUGH THE RELEASE EXCEED 3 MMSCF, THE INITIAL NRC NOTIFICATION WAS NOT MADE BECAUSE THE RELIEF SYSTEM OPERATED AS DESIGNED. THIS ACTION MATCHED WILLIAMS' PHILOSOPHY AND PROCEDURES AND WAS SUPPORTED BY AN INTERNAL WHITE PAPER. PHMSA AGREED TO REVIEW THE INTERNAL WHITE PAPER AND CONSIDER THE MERITS OF WILLIAMS' POSITION WHILE DELAYING A DECISION ON THE NEED FOR AN NRC REPORT. THREE WEEKS LATER AND AFTER ADDITIONAL DISCUSSION WITH PHMSA AND WUTC, PHMSA DETERMINED AN NRC NOTIFICATION AND INCIDENT REPORT WOULD BE REQUIRED FOR THIS EVENT. INITIAL NRC REPORT (#1177100) AND FOLLOW UP REPORT (#1177126) WERE MADE ON MAY 1, 2017.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20170039 | 30487 | 2017-05-19 11:55 | SUPPLEMENTAL | 32296 | TARGA RESOURCES OPERATING LLC | 811 LOUISIANA ST SUITE 2100 | HOUSTON | TX | 77002 | 2017-05-08 13:30 | 2017 |  |  | 29.5663 | -93.1935 | 1177785 | 2017-05-08 15:29 |  | NATURAL GAS |  | 600 | 0 | 1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | PIPELINE SHUT DOWN PRIOR TO INCIDENT. NOT FLOWING. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-05-08 13:30 | 2017-05-09 06:00 | OFFSHORE | [29 empty] | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST CAMERON | 101 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12 |  | 0.375 | 52000 | API5L | SEAMLESS |  | UNKNOWN | OTHER | CONCRETE | [27 empty] | 1970 | 1969 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 120 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 2000 | 1831.73076923077 | 129000 | 137208.87365691 | 0 | 0 | 0 | 0 |  |  | 131000 | 64881.5319776556 | 139040.604426141 | [8 empty] | 174 |  | 1240 | 192.619(A)(4) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 110544 | NO |  |  | YES |  |  |  |  | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | NO |  |  |  |  | OTHER | REPORT FROM BSEE. |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES | [5 empty] | YES | FIELD EXPERIENCE. | YES | [5 empty] | NO | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | TIM HUFFER | MANGER REGULATORY COMPLIANCE | thuffer@targaresources.com | 3375835200 | 3375834630 |  |  |  | TIM HUFFER | MANAGER REGULATORY COMPLIANCE | 3375835200 | thuffer@targaresources.com | TARGA RECEIVED NOTIFICATION FROM THE BUREAU OF SAFETY AND ENVIRONMENTAL ENFORCEMENT OF A PIPELINE LEAK LOCATED NEAR TARGA'S PIPELINE. INVESTIGATION BY TARGA CONFIRMED A LEAK FROM TARGA'S PIPELINE. PIPELINE LEAK WAS REPAIRED BY INSTALLATION OF CLAMP.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170040 | 17332 | 2017-05-25 11:21 | ORIGINAL FINAL | 31531 | ONEOK WESTEX TRANSMISSION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2016-12-26 12:05 | 2016 |  |  | 31.2752 | -103.0734 | NRC NOTIFICATION REQUIRED BUT NOT MADE |  |  | NATURAL GAS |  | 92600 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE FACILITY WAS NOT IN OPERATION AT THE TIME OF THE RELEASE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-12-27 07:10 | 2016-12-27 06:30 | ONSHORE | TX | 79730 | Not Within a Municipality | PECOS | MILEPOST | ROADRUNNER CS | ROADRUNNER COMPRESSOR STATION | NONE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2016 |  | CARBON STEEL |  | OTHER | [8 empty] | O-RING FAILURE ON COMPRESSOR DISCHARGE RELIEF VALVE FAILED TO SEAL CAUSING THE VALVE TO OPEN. | CLASS 1 LOCATION | NO |  | 725 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 237514 | 243915.994609164 | 0 | 0 | 0 | 0 | 0 | 0 | REPAIR AND RE-TEST RELIEF VALVE - WARRANTY WORK |  | 237514 | 252878.787061995 | 243915.994609164 | [8 empty] | 1022 |  | 1226 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [16 empty] | YES | [174 empty] | PATRICK VAUGHAN | MANAGER REGULATORY COMPLIANCE | pat.vaughan@oneok.com | 9185887734 |  |  |  |  | WESLEY DUNBAR | VP NATURAL GAS PIPELINE OPERATIONS | 9185887424 | wesley.dunbar@oneok.com | DURING AN IN-DEPTH GAS VOLUME REVIEW IN APRIL OF 2017 FOR THE ONEOK WESTEX PIPELINE SYSTEM, WESTEX IDENTIFIED A RELEASE (DESCRIBED BELOW) THAT OCCURRED IN DECEMBER 2016 AT THE ROADRUNNER COMPRESSOR STATION THAT WESTEX OPERATES. THIS WAS NOT INITIALLY RECOGNIZED AND REPORTED BY OPERATIONS AS AN EVENT THAT EXCEEDED 3MMCF, AND THEREFORE NEITHER A CALL TO NRC NOR A 30-DAY REPORT WAS MADE. BECAUSE THE DISCOVERY IN APRIL 2017 WAS FOR AN EVENT THAT OCCURRED IN DECEMBER 2016, AN NRC REPORT ALSO WAS NOT MADE IN APRIL 2017. ON 12/26/2016, AN O-RING IN A DISCHARGE PRESSURE RELIEF VALVE (PRV) ON COMPRESSOR UNIT 200 FAILED. THE FAILED O-RING DID NOT ALLOW THE VALVE TO SEAL PROPERLY AND CAUSED THE PRV TO ACTUATE. THE OPENED VALVE VENTED TO ATMOSPHERE UNTIL AN EMPLOYEE ARRIVED ON LOCATION ON 12/27/2016. THE RELIEF VALVE WAS CLOSED, THE O-RING WAS REPAIRED, AND IT WAS RETURNED TO SERVICE ON 12/28/2106.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170041 | 17412 | 2017-05-31 09:19 | SUPPLEMENTAL FINAL | 2564 | COLORADO INTERSTATE GAS CO | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2017-05-05 08:45 | 2017 |  |  | 40.1704 | -103.8536 | 1177507 | 2017-05-05 09:46 |  | NATURAL GAS |  | 4600 | 4507 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-05-05 16:50 | 2017-05-11 15:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-05-05 08:45 | 2017-05-05 13:55 | ONSHORE | CO | 80701 | Not Within a Municipality | MORGAN | MILEPOST | 2 + 1840 | LINE 52A | 52A | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 16 |  | 0.203 | 56000 | API 5L OR EQUIVALENT | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | YOUNGSTOWN STEEL | COLD APPLIED TAPE | [28 empty] | 1967 | 1967 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 349 |  | NO | NO | NO |  | 0 | 0 | 14329 | 15240.8213227121 | 14628 | 13397.2788461538 | 26155 | 27819.3650426084 | 400 | 425.453871804372 | 0 | 0 |  |  | 55512 | 33850.6236248468 | 56882.9190832787 | [8 empty] | 783 |  | 1000 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 85470 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS SO SMALL, GAS CONTROL COULD NOT SEE ANY PIPELINE PRESSURE CHANGE IN SCADA. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | YES | [14 empty] | YES | LACK OF WELD FUSION IN PIPE LONG SEAM | [6 empty] | YES | YES | [62 empty] | YES | YES |  |  | YES |  |  |  | 2009 | [31 empty] | 2009 | [23 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KENNETH C PETERS | SENIOR ENGINEER CODES AND STANDARDS | ken_peters@kindermorgan.com | 2053257554 | 2053253508 |  |  |  | REJI GEORGE | DIRECTOR CODES AND STANDARDS | 7134205433 | reji_george@kindermorgan.com | COLORADO INTERSTATE GAS (CIG) TRANSMISSION PERSONNEL, WHILE INSTALLING PIPELINE MARKERS, DISCOVERED AN AREA OF DEAD VEGETATION AND DISCOLORED SOIL IN THE VICINITY OF ITS 16" 52A PIPELINE IN MORGAN COUNTY, COLORADO. LEAK DETECTION EQUIPMENT CONFIRMED A NATURAL GAS LEAK. EXCAVATION REVEALED A VERY SMALL CRACK IN THE PIPE'S LONG SEAM TO BE THE SOURCE OF THE LEAK, ATTRIBUTABLE TO A LACK OF WELD FUSION IN THE LONG SEAM. THE ANOMALY WAS CUT OUT AND REPLACED WITH A NEW CYLINDER OF PIPE. THE PIPELINE WAS THEN PLACED BACK INTO OPERATION.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170042 | 17347 | 2017-06-01 08:54 | SUPPLEMENTAL FINAL | 19580 | TRANSCOLORADO PIPELINE CO. | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2017-05-06 19:20 | 2017 |  |  | 36.7348 | -107.9661 | 1177646 | 2017-05-06 20:34 |  | NATURAL GAS |  | 6244 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-05-06 20:50 | 2017-05-07 11:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-05-06 19:43 | 2017-05-06 19:41 | ONSHORE | NM | 87413 | BLOOMFIELD | SAN JUAN | MILEPOST | 1+156 | BLANCO COMPRESSOR STATION | STATION 5200 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2007 |  | CARBON STEEL |  | OTHER | [8 empty] | VALVE STUCK IN OPEN POSITION DURING ESD, RELEASING NATURAL GAS THROUGH VENT STACK SYSTEM | CLASS 1 LOCATION | YES | METHOD2 | 594 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 13362 | 12237.7932692308 | 1150 | 1223.17988143757 | 2897 | 3081.34966654316 | 0 | 0 |  |  | 17409 | 14663.3686069627 | 16542.3228172115 | [8 empty] | 900 |  | 1287 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | NO | NO | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE GAS RELEASE WAS INITIATED BY A LIGHTNING STRIKE THAT CAUSED A POWER OUTAGE & SUBSEQUENT ESD, DISABLING SCADA. WHEN SCADA RETURNED TO OPERATION, GAS CONTROL WAS ABLE TO SEE THAT AN ESD HAD OCCURRED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES |  |  | YES | [16 empty] | YES | [10 empty] | YES | VALVE STUCK IN OPEN POSITION DURING ESD. | [161 empty] | KENNETH C PETERS | SENIOR ENGINEER CODES AND STANDARDS | ken_peters@kindermorgan.com | 2053257554 | 2053253508 |  |  |  | REJI GEORGE | DIRECTOR CODES AND STANDARDS | 7134205433 | reji_george@kindermorgan.com | A LIGHTNING STRIKE AT TRANSCOLORADO GAS TRANSMISSION (TCGT) COMPANY'S BLANCO COMPRESSOR STATION IN BLOOMFIELD, NM, ON MAY 6, 2017, CAUSED A LOSS OF ELECTRICAL POWER THAT INITIATED A STATION EMERGENCY SHUTDOWN (ESD). GAS CONTROL CALLED OUT LOCAL OPERATIONS PERSONNEL TO RESPOND TO THE POWER OUTAGE. UPON ARRIVAL AT THE COMPRESSOR STATION, PERSONNEL DISCOVERED THAT A VALVE, INTENDED TO CLOSE DURING AN ESD, FAILED TO DO SO RESULTING IN A LOSS OF NATURAL GAS TO THE ATMOSPHERE THROUGH THE BLOWDOWN VENT SYSTEM IN EXCESS OF THE PHMSA INCIDENT REPORTABLE QUANTITY OF 3,000 MCF. THE POWER OUTAGE DISRUPTED SCADA BUT WHEN POWER WAS RESTORED, GAS CONTROL WAS ABLE TO SEE IN SCADA THE RECORD OF THE ESD, WHICH OPERATED AS DESIGNED AT 19:20 HOURS. THE GAS RELEASE WAS STOPPED BY THE RESPONDING PERSONNEL. THE FAULTY VALVE WAS REPAIRED AND THE STATION WAS MADE AVAILABLE FOR OPERATION THE FOLLOWING DAY. A 48-HOUR UPDATE TO THE NRC RESULTED IN REVISED REPORT NUMBER 1177727.
2021-02-26 10:37 | NO | NO | GG (Gas Gathering) | 20170043 | 31615 | 2017-06-01 10:31 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2017-05-07 20:15 | 2017 |  |  | 29.4761 | -96.9409 | 1177806 | 2017-05-08 17:04 |  | NATURAL GAS |  | 4.62 | 405.7 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-05-07 22:20 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-05-07 20:15 | 2017-05-07 20:30 | ONSHORE | TX | 77964 | HALLETTSVILLE | LAVACA | SURVEY STATION NO. | 1382.7 | HOWELL - SUPERIOR SOUR GAS LOOP | 307-1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 |  | 0.25 | 42000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1979 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | UNKNOWN | [5 empty] | CLASS 2 LOCATION | NO |  | 217 |  | NO | NO | NO |  | 0 | 0 | 1400 | 1489.0885513153 | 16 | 14.6538461538462 | 55000 | 58499.9073731012 | 500 | 531.817339755465 | 0 | 0 |  |  | 56916 | 27795.8425485223 | 60535.4671103258 | [8 empty] | 755 |  | 1324 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 21644 | YES | [7 empty] | NO | [6 empty] | TYPE A GATHERING | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A LEAK ON THE MAINLINE. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [146 empty] | NHAN TRUONG |  | nvtruong@eprod.com | [5 empty] | NHAN TRUONG |  | 7133812493 | nvtruong@eprod.com | ON 5/7/2017 AT 20:15, A LANDOWNER NOTIFIED THE OPERATIONS SUPERVISOR OF A STRONG ODOR AND OPERATIONS IMMEDIATELY RESPONDED. AT 20:30, A LEAK WAS IDENTIFIED ON THE ROW AND THE PIPELINE WAS DEPRESSURIZED AND ISOLATED. ON 5/8/2017 AT 16:50, ENTERPRISE DETERMINED THE COST OF REPAIRS IS ESTIMATED TO EXCEED $50,000 AND THE NRC WAS IMMEDIATELY NOTIFIED. THE PIPELINE WAS SHUT DOWN UNTIL A REMEDIAL ACTION PLAN COULD BE DEVELOPED. TRRC WAS NOTIFIED ON 5/8/2017 @ 17:04 HOURS AND INCIDENT #1563. ON 5/10/2017 @ 15:23 CONTACTED NRC REPORTING 48 UPDATE. NEW NRC # 1177977 1/11/2018. THE LINE IS NO LONGER OWNED OR OPERATED BY ENTERPRISE PRODUCTS. 2/5/2019 UPDATE -PART A4/A19 TIMES HAVE BEEN REVISED AND NARRATIVE UPDATED TO CLARIFY THE TIME OF THE INCIDENT AND WHEN THE INCIDENT WAS DETERMINED TO BE REPORTABLE. -PART C3 INFORMATION IS UPDATED BASED ON ALIGNMENT SHEET INFORMATION. THE DISPOSITION OF THE LEAK IS UNKNOWN. -PART G CAUSE IS UPDATED TO INVESTIGATION COMPLETE, CAUSE UNKNOWN.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20170044 | 17405 | 2017-06-01 17:18 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2017-05-11 11:37 | 2017 |  |  | 28.695 | -91.0029 | 1178097 | 2017-05-11 18:51 |  | NATURAL GAS |  | 72 | 2671.2 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-05-12 06:00 | 2017-05-13 06:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-05-12 06:00 | 2017-05-12 01:00 | OFFSHORE | [28 empty] | 48 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SHIP SHOAL | 158 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | WELD/FUSION |  | 10 |  | 0.365 | 35000 | API-5LX | SEAMLESS |  | VINSON SUPPLY | OTHER | SOMASTIC | [8 empty] | PIPE GIRTH WELD | [18 empty] | 1963 | 1963 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 258 |  | NO | NO | NO |  | 0 | 0 | 8550 | 9094.07650981845 | 231 | 211.564903846154 | 110000 | 116999.814746202 | 10000 | 10636.3467951093 | 15000 | 15954.5201926639 | CLAMP |  | 143781 | 70305.6718433822 | 152896.32314764 | [8 empty] | 697 |  | 1440 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | AUTOMATIC | 116107 | NO | [5 empty] | YES | PIGGING FACILITIES WERE DESTROYED DURING HURRICANE IKE. PIPELINE IS NOW CONNECTED SUB-SEA. | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | YES | YES | YES | NO | NO | OTHER | KINETICA PIPELINE OPERATORS DISCOVERED BUBBLES WHILE FLYING AND THEN REPORTED IT |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLERS WERE NOTIFIED BY KINETICA PIPELINE OPERATORS THAT WERE FLYING OVER WHEN THEY OBSERVED THE LEAK. LEAK WAS SO SMALL IT WOULD NOT BE DETECTCTED BY SCADA. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN | [5 empty] | YES | UNKOWN |  |  | YES | DIVERS INSPECTED | YES | [5 empty] | YES | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | EDGAR RODRIGUEZ | REGULATORY SPECIALIST SR. | edgar.x.rodriguez@williams.com | 713-215-2846 |  |  |  |  | LARRY LEGENDRE | MANAGER PIPELINE SAFETY | 713-215-2733 | larry.d.legendre@williams.com | ON MAY 11TH, 2017 KINETICA EMPLOYEES SPOTTED THE LEAK WHILE FLYING. THE LEAK WAS REPORTED TO PIPELINE CONTROL WHO THEN REPORTED IT THE SECURITY OPERATIONS CENTER. OPERATIONS WAS NOTIFIED BUT IT WAS TOO LATE IN THE DAY TO FLY OUT. OPERATIONS LOCATED A DIVE VESSEL IN THE AREA AND DISPATCHED IT TO THE REPORTED COORDINATES. AT FIRST LIGHT ON MAY 12TH, 2017 IT WAS CONFIRMED TO BE A WILLIAMS LEAK. OPERATIONS BEGAN EMERGENCY RESPONSE ACTIVITIES. A PLAN WAS DEVELOPED TO ISOLATE THE AFFECTED SECTION OF 10" PIPE. PRODUCERS WERE NOTIFIED AND SHUT IN PRODUCTION. THE SYSTEM WAS THEN BLOWN DOWN. A BOLT ON PIPE CLAMP WAS LOCATED AND INSTALLED BY 6:00AM MAY 13, 2017. THE SYSTEM WAS PARTIALLY PRESSURIZED AND CONTINUOUSLY INSPECTED FOR LEAKS. PRODUCTION RESUMED AND PRESSURES RETURNED TO NORMAL.
2021-02-26 10:37 | YES | NO | UNGS (Underground Natural Gas Storage) | 20170045 | 30084 | 2017-06-22 15:15 | SUPPLEMENTAL | 32655 | EAST CHEYENNE GAS STORAGE, LLC | 10375 RICHMOND AVE SUITE 1900 | HOUSTON | TX | 77042 | 2017-05-25 16:20 | 2017 |  |  | 40.9666 | -103.2211 | 1179372 | 2017-05-25 20:25 |  | NATURAL GAS |  | 91000 | 0 | 290 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | WELL WAS ISOLATED FROM SURFACE FACILITY SYSTEM AT TIME OF INCIDENT. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 16 | 2017-05-25 16:20 | 2017-05-25 16:20 | ONSHORE | CO | 80747 | Not Within a Municipality | LOGAN | MILEPOST | WP-D005-1 | WP-D005-1 | WP-D005-1 | NO | OPERATOR-CONTROLLED PROPERTY | BELOWGROUND STORAGE OR ABOVEGROUND STORAGE VESSEL, INCLUDING ATTACHED APPURTENANCE |  |  |  |  | NO | [22 empty] | INTERSTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | UNDERGROUND GAS STORAGE OR CAVERN | [38 empty] | 2012 |  | CARBON STEEL |  | OTHER | [8 empty] | LOSS OF CONTROL OF AN UNDERGROUND GAS STORAGE INJECTION / WITHDRAWAL WELL | CLASS 1 LOCATION | NO |  | 506 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 328000 | 300403.846153846 | 1720000 | 1829451.6487588 | 300000 | 319090.403853279 | 70000 | 74454.4275657651 | CONSULTANTS SUPPORTING RESPONSE AND REPAIRS |  | 2418000 | 1331856.34993017 | 2523400.32633169 | [8 empty] | 0 |  | 2100 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION IN STORAGE FIELD | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER DID NOT HAVE ACTIVE CONTROL OF THE SUBJECT WELL AT THE TIME OF THE INCIDENT AS WELL MAINTENANCE ACTIVITIES WERE BEING PERFORMED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | APPARENT CAUSE OF THE INCIDENT WAS DUE TO THE FAILURE OF A "BLANKING" PLUG SET IN A PROFILE NIPPLE INTEGRAL TO THE PRODUCTION PACKER. | [15 empty] | YES | SUBSURFACE BLANKING PLUG SET IN PROFILE NIPPLE | [161 empty] | RON RICHARDS | SENIOR VICE PRESIDENT | rrichards@mehllc.com | (713) 403-6479 |  |  |  |  | RON RICHARDS | SENIOR VICE PRESIDENT | (713) 403-6479 | rrichards@mehllc.com | WHILE PERFORMING MAINTENANCE ACTIVITIES ON THE WP-D005-1 INJECTION/WITHDRAWAL WELL THE WELL KICKED AND CONTROL OF WELL WAS LOST. WELL WAS ISOLATED FROM SURFACE FACILITY SYSTEM AT TIME OF INCIDENT. CONTROL OF WELL WAS REGAINED WITHIN 44 HOURS OF START OF INCIDENT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170046 | 30882 | 2017-06-26 12:25 | SUPPLEMENTAL FINAL | 12696 | CYPRESS GAS PIPELINE COMPANY | 1100 LOUISIANA ST. | HOUSTON | TX | 77002 | 2017-05-31 00:01 | 2017 |  |  | 30.0476 | -90.6607 | 1179788 | 2017-05-31 02:36 |  | NATURAL GAS |  | 21000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-05-31 01:19 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-05-31 01:05 | 2017-05-31 01:05 | ONSHORE | LA | 70069 | GRAMERCY | ST. JOHN THE BABTIST | MILEPOST | 1330+00 | LAKE BOEUF TO GRAMERCY | BRS 101 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | YES | [6 empty] | YES | UNCASED | MISSISSIPPI RIVER | 50 | BELOW WATER, PIPE ON OR ABOVE BOTTOM | [11 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 |  | 0.5 | 35000 | API 5L | SEAMLESS |  | YOUNGSTOWN STEEL | OTHER | CEMENT | [27 empty] | 1959 | 1959 | CARBON STEEL |  | OTHER | [8 empty] | SIDE SCAN SONAR INDICATED A BREAK IN THE PIPELINE. | CLASS 1 LOCATION | NO |  | 248 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 67000 | 61362.9807692308 | 70000 | 74454.4275657651 | 0 | 0 | 0 | 0 |  |  | 137000 | 97794.3353307493 | 135817.408334996 | [8 empty] | 750 |  | 900 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 4623 | NO | [5 empty] | YES | THERE ARE NO PIGGING FACILITIES ON THIS SECTION OF PIPELINE. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | POSSIBLE THIRD PARTY DAMAGE DUE TO A BARGE STRIKE IN MISSISSIPPI RIVER. | [12 empty] | YES | 1 | 0 | YES | 1 | 0 | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [146 empty] | NATHAN L. GRAY JR. | SENIOR PIPELINE COMPLIANCE SPECIALST | ngray@eprod.com | 9854934629 |  |  |  |  | NATHAN L. GRAY JR. | SENIOR PIPELINE COMPLIANCE SPECIALST | 9854934629 | ngray@eprod.com | AN UNKNOWN THIRD PARTY REPORTED TO NRC, #1179785, "THAT A BARGE BROKE FREE OF ITS MOORINGS AND COLLIDED WITH AN UNDERWATER PIPELINE IN THE MISSISSIPPI RIVER RESULTING IN A RELEASE OF NATURAL GAS." CYPRESS GAS PIPELINE MANUALLY ISOLATED THE MISSISSIPPI RIVER CROSSING ON THE EAST AND WEST BANK. A SIDE SCAN SONAR INVESTIGATION INDICATES THE PIPELINE TO BE BROKEN AT APPROXIMATELY 50 FEET BELOW THE CURRENT RIVER LEVEL. THE SONAR DATA DID NOT HAVE CLARITY DUE TO THE RIVER CONDITIONS TO DETERMINE WHAT MAY HAVE CAUSED THIS INCIDENT. THE PIPELINE HAS BEEN ABANDONED. CYPRESS GAS PIPELINE MADE A 48 HOUR NOTIFICATION UPDATE TO THE NRC, #1179998, ON JUNE 1, 2017 AT 18:09 UPDATING VOLUME RELEASED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170047 | 17383 | 2017-06-26 13:16 | SUPPLEMENTAL FINAL | 2564 | COLORADO INTERSTATE GAS CO | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2017-05-29 09:59 | 2017 |  |  | 39.6383 | -104.7037 | 1179650 | 2017-05-29 11:40 |  | NATURAL GAS |  | 6456 | 2495 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-05-31 08:00 | 2017-06-02 12:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-05-29 09:59 | 2017-05-29 11:00 | ONSHORE | CO | 80016 | Not Within a Municipality | ARAPHAHOE | MILEPOST | MP 101, 3471' | CIG LINE 0009-B | PUEBLOW - WATKINS LOOP | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 90 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | FLANGE ASSEMBLY | [38 empty] | 1971 |  | CARBON STEEL |  | LEAK |  |  | OTHER | BREAK IN GASKET MATERIAL | [5 empty] | CLASS 1 LOCATION | NO |  | 554 |  | NO | NO | NO |  | 0 | 0 | 7485 | 7961.30557613931 | 19365 | 17735.7331730769 | 26000 | 27654.5016672842 | 1000 | 1063.63467951093 | 0 | 0 |  |  | 53850 | 35224.2716007709 | 54415.1750960113 | [8 empty] | 500 |  | 820 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 47520 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | LDC (CUSTOMER) SAW DEAD VEGETATION AND INFORMED CIG |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GRADUAL LEAK IN UNDERGROUND FLANGE GASKET | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | GASKET | [17 empty] | YES | NONE IDENTIFIED | [161 empty] | WM. MARTIN MULLER | SPECIALIST-PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205 410 4383 | 205 3253508 |  |  |  | REJI GEORGE | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713 420 5433 | reji_george@kindermorgan.com | ORIGINAL NRC REPORT NUMBER 1179650; 9:59 AM M, LDC CALLED CIG TO REPORT DEAD VEGETATION, POSSIBLE LEAK SITE 25 FEET SOUTH OF QUINCY AVENUE, PIPELINE ROW, IN A WHEAT FIELD; 11:00 AM M, CIG EMPLOYEES ON SCENE AND CONFIRMED PIPELINE LEAK; 12:00 PM M, CIG EMPLOYEES BEGAN LOWERING THE PIPELINE OPERATING PRESSURE; EXCAVATION FOUND BURIED FLANGES WITH LEAKING GASKET MATERIAL; 05/31/2017, 8:00 AM M, CIG EMPLOYEES BEGAN PIPELINE VALVE SECTION ISOLATION AND PIPELINE VALVE SECTION BLOW DOWN TO CUT OUT FLANGED CONNECTION AND INSTALL LINE PIPE; MLV 10.1 IS MANUALLY OPERATED; MLV 11 IS REMOTE CONTROL BY GAS CONTROL; 06/02/2017, 12:00 PM M, PROJECT IS COMPLETE AND PIPELINE VALVE SECTION HAS BEEN RETURNED TO SERVICE. NOTE: NRC UPDATE REPORT NUMBER 1179812, 05/31/2017, 9:00 AM M; NOTE: PIR OF 554 FEET INCLUDES 40 FOOT BUFFER. NO ADDITIONAL INFORMATION CHANGE; SUBMITTING FINAL REPORT 07/21/2017;
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170048 | 30364 | 2017-06-26 17:43 | SUPPLEMENTAL FINAL | 32005 | ENLINK LIG, LLC | 1722 ROUTH ST., SUITE 1300 | DALLAS | TX | 75201 | 2017-05-29 04:00 | 2017 |  |  | 31.9015 | -93.2618 | 1179618 | 2017-05-29 05:05 |  | NATURAL GAS |  | 5873 | 127 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-05-29 04:30 | 2017-05-29 23:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-05-29 02:59 | 2017-05-29 03:25 | ONSHORE | LA | 71019 | Not Within a Municipality | NATCHITOCHES PARISH | MILEPOST | MP 47.8 (EST) | POWHATAN TO LAKE END 8" MAINLINE LOOP | POWHATAN TO LAKE END 8" MAINLINE LOOP/P1366 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 43 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 |  | 0.188 | 52000 | X-52 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1958 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 23 | 51 |  | CLASS 1 LOCATION | NO |  | 160 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 19381 | 17750.3870192308 | 25000 | 26590.8669877733 | 0 | 0 | 0 | 0 |  |  | 44381 | 30608.5418076852 | 44341.254007004 | [8 empty] | 452 |  | 720 | OTHER | WEAKEST ELEMENT. ANSI 300 FLANGES |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 44352 | NO | [5 empty] | YES | LINE IS NOT PRESENTLY CONFIGURED FOR PIGGING. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | NO | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RCA WAS DONE ON THIS INCIDENT AND DUE TO OPERATING CONDITIONS AT THE TIME OF THE INCIDENT IT WAS DETERMINED THAT CONTROLLER ACTIONS WERE NOT INVOLVED IN THE INCIDENT AND THAT FATIGUE WAS NOT AN ISSUE. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | GENERAL CORROSION |  |  | YES |  |  |  |  | YES | YES |  |  | YES |  |  |  | YES | RUPTURE WAS AT THE 7 O'CLOCK POSITION. | NO | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | CORDELL THERIOT | SR. DOT COMPLIANCE SPECIALIST | cordell.theriot@enlink.com | 337-937-3371 | 337-937-8524 |  |  |  | CORDELL THERIOT | SR. DOT COMPLIANCE SPECIALIST | 337-937-3371 | cordell.theriot@enlink.com | ENLINK OPERATOR WAS CALLED OUT FOR POWER AND SCADA COMMUNICATION PROBLEMS, DUE TO A STORM SYSTEM THAT MOVED THROUGH THE AREA. PIPELINE CONTROL INSTRUCTED THE OPERATOR AT 1:45 AM TO START THE ARMISTEAD COMPRESSOR, AFTER INTERNATIONAL PAPER - CAMPTI WENT DOWN. THE OPERATOR STARTED THE COMPRESSOR AT 2:47 AM PRESSURE WAS 463 PSIG (OPERATING PRESSURE WAS 500 PSIG) AND LEFT THE STATION. ON HIS WAY, BACK HOME, THE OPERATOR HEARD A LOUD NOISE AND TURNED HIS VEHICLE AROUND ON HWY 1 AND STARTED BACK TO ARMISTEAD STATION. HE CAME ACROSS A LARGE AREA OF MUD ON HIGHWAY 1 AND FOUND THE POWHATAN 8" MAINLINE RUPTURED ON THE SIDE OF HWY 1 WITH GAS BLOWING. THE OPERATOR NOTIFIED PIPELINE CONTROL AND HIS SUPERVISOR. THE PIPELINE WAS ISOLATED, BLOWN DOWN AND REPAIRED THE SAME DAY. A 16-FOOT SECTION OF PIPE CONTAINING THE 36-INCH SECTION THAT RUPTURED WAS CUT OUT AND SENT TO ELEMENT MATERIALS TECHNOLOGY. THE INVESTIGATION DID NOT FIND ANY PRESSURES OVER THE 500 PSIG "OPERATING PRESSURE" AND PIPELINE CONTROL ACTIONS DID NOT CONTRIBUTE TO THE EVENT. PIPELINE OPERATIONS PERSONNEL ARRIVED AT THE LOCATION AT 3:25 AM, BUT DUE TO SEVERE WEATHER CONDITIONS AT THE TIME OF THE INCIDENT HE WAS NOT ABLE TO MAKE A CONFIRMED DISCOVERY OF THE PIPELINE INVOLVED UNTIL 4:00 AM. THIS SUPPLEMENTAL WAS DONE TO CORRECT THE TIMES IN PART A, ITEM 4 AND 19A.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170049 | 17515 | 2017-06-27 17:49 | SUPPLEMENTAL FINAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2017-05-28 15:50 | 2017 |  |  | 32.4075 | -94.4298 | 1179595 | 2017-05-28 18:31 |  | NATURAL GAS |  | 24000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-05-28 16:10 | 2017-05-29 08:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-05-28 15:50 | 2017-05-28 16:05 | ONSHORE | TX | 75670 | MARSHALL | HARRISON | SURVEY STATION NO. | CS 304 | NGPL MARSHALL COMPRESSOR STATION #304 | CS 304-GULF COAST LINE #2 | YES | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | UNIT CONTROL LOGIC WAS NOT PROGRAMMED CORRECTLY CAUSING THE RELIEF VALVE TO REMAIN IN OPEN POSITION. | CLASS 1 LOCATION | NO |  | 879 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 75600 | 69239.4230769231 | 500 | 531.817339755465 | 300 | 319.090403853279 | 0 | 0 |  |  | 76400 | 72174.2429532305 | 70090.3308205318 | [8 empty] | 780 |  | 858 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER ACTION NOT A FACTOR IN ROOT CAUSE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | UNIT PROGRAMMING LOGIC ISSUE | [161 empty] | VALERIE BERGMAN | ENGINEER II | valerie_bergman@kindermorgan.com | 713-420-4810 |  |  |  |  | REJI GEORGE | DIRECTOR OF CODES AND STANDARDS | 713-420-5433 | reji_george@kindermorgan.com | ON MAY 28, 2017 AT 15:50, THE LOCAL FIRE DEPARTMENT NOTIFIED GAS CONTROL THAT NGPL STATION 304 WAS VENTING NATURAL GAS. NGPL OPS PERSONNEL WERE DISPATCHED TO STATION 304 AND VERIFIED AT 16:00 THAT A RELIEF VALVE IN STATION 304 WAS VENTING. OPS PERSONNEL IMMEDIATELY ADJUSTED THE RELIEF PILOT AND PROCEEDED TO THE UNIT PANEL AND SHUT DOWN THE UNIT. THE RELIEF VALVE STOPPED VENTING AT 16:05. THE ROOT CAUSES OF THIS INCIDENT WERE DUE TO THE RELIEF VALVE PILOT NOT BEING SECURED PROPERLY CAUSING THE RELIEF VALVE TO PREMATURELY OPEN AND A PROGRAMMING ERROR IN THE STATION'S UNIT CONTROL LOGIC CAUSING THE UNIT TO REMAIN ONLINE WHILE THE RELIEF VALVE ACTIVATED. CORRECTIVE ACTIONS INCLUDED PHYSICAL INSPECTION OF THE RELIEF VALVE AND A SET POINT RESET. THE STATION'S UNIT LOGIC WAS REPROGRAMED TO SHUT DOWN THE UNIT WHEN A RELIEF VALVE ACTIVATES.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170050 | 30704 | 2017-06-28 12:18 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2017-06-20 11:41 | 2017 |  |  | 43.0255 | -95.5361 | 1181745 | 2017-06-20 14:10 |  | NATURAL GAS |  | 6954 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-06-20 13:50 | 2017-06-20 21:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-06-20 12:30 | 2017-06-20 12:30 | ONSHORE | IA | 51245 | Not Within a Municipality | O'BRIEN | MILEPOST | 1.17 MILE POS | 179IAB71502 | SHELDON BRANCH LOOP | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2003 |  | CARBON STEEL | BLOWDOWN VALVE TO RISED | OTHER | [8 empty] | FARMER'S SPRAYER DISCONNECTED BLOW DOWN VALVE FROM RISER ON PIPELINE. | CLASS 1 LOCATION | NO |  | 130 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 18706 | 17132.1778846154 | 30000 | 31909.0403853279 | 10000 | 10636.3467951093 | 0 | 0 |  |  | 58706 | 37291.162084604 | 59677.5650650526 | [8 empty] | 700 |  | 1000 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 8781 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | FARMER'S SPRAYER CAUSED THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [260 empty] | KENTON ANDERSON | INTERNAL CORROSION SPECIALIST | ken.anderson@nngco.com | 402-398-7617 |  |  |  |  | KENTON ANDERSON | INTERNAL CORROSION SPECIALIST | 402-398-7617 | ken.anderson@nngco.com | A FARMER WAS SPRAYING HIS FIELD. HE WAS TURNING THE SPRAYER ATTACHED TO THE TRACTOR AND THE SPRAYER DISCONNECTED THE BLOW DOWN VALVE FROM THE RISER. THE BLOW DOWN VALVE WAS DISCONNECTED AT THE WELD TO THE RISER. THE RISER WAS PROTECTED BY APPROXIMATELY 4-FOOT HIGH PIPE FENCE. THE COMPANY RAISED THE PIPE FENCE AN ADDITIONAL 4 FEET TO PROTECT THE RISER AND BLOW-DOWN VALVE.
2021-02-26 10:37 | YES | NO | UNGS (Underground Natural Gas Storage) | 20170051 | 17450 | 2017-06-29 13:13 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2017-06-01 10:20 | 2017 |  |  | 41.8781 | -77.9807 | 1179928 | 2017-06-01 10:53 |  | NATURAL GAS |  | 40 | 249 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-06-01 14:00 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-06-01 10:20 | 2017-06-01 10:20 | ONSHORE | PA | 16915 | COUDERSPORT | POTTER | MILEPOST | WELL #5564 | HEBRON GAS STORAGE FIELD | STATION 313 | NO | OPERATOR-CONTROLLED PROPERTY | TRANSITION AREA | OTHER | WELL |  |  | NO | [22 empty] | INTERSTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | UNDERGROUND GAS STORAGE OR CAVERN | [38 empty] | UNKNOWN |  | CARBON STEEL |  | LEAK |  |  | OTHER | SUSPECTED COLLAR LEAK | [5 empty] | CLASS 1 LOCATION | NO |  | 230 |  | NO | NO | NO |  | 0 | 0 | 589 | 626.480826231938 | 95 | 87.0072115384615 | 436865 | 464664.764264542 | 32130 | 34174.5822526862 | 0 | 0 |  |  | 469679 | 229358.198398802 | 499552.834554999 | [8 empty] | 1382 |  | 2275 | OTHER | MAOP IS NOT APPLICABLE TO THE WELL. SEE PART H FOR MORE DETAIL. |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION IN STORAGE FIELD | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [146 empty] | ERIC GENTLES | PIPELINE ENGINEER II-COMPLIANCE | eric_gentles2@kindermorgan.com | 713-420-2389 |  |  |  |  | REJI GEORGE | DIRECTOR - COMPLIANCE - CODES AND STANDARDS | 713-420-5433 | reji_george@kindermorgan.com | AN INJECTION/WITHDRAWAL WELL WAS FOUND TO BE VENTING NATURAL GAS FROM THE 9-5/8" X 7" ANNULUS. BELOW IS A LIST OF ACTIONS TAKEN IN ORDER TO SECURE THE WELL: RETRIEVABLE BRIDGE PLUG SET AT 5,180' 7" CASING BLOWN DOWN CASING FILLED WITH 9.5 PPG BRINE CEMENT BOND LOG WAS RUN CASING INSPECTION LOG WAS RUN ON AUGUST 2, 2017 GAMMA-RAY, NEUTRON, TEMPERATURE LOG WAS RUN ON AUGUST 2, 2017 THE GAMMA-RAY, NEUTRON, TEMPERATURE LOG INDICATES THERE IS POSSIBLY A COLLAR LEAK AT 1010'. THE WELL IS SECURE. 49CFR 191.15 REQUIRES THE USE OF PHMSA FORM F 7100.2 FOR REPORTING INCIDENTS (AS DEFINED BY 49CFR 191.3) ON UNDERGROUND NATURAL GAS STORAGE FACILITIES. IN ORDER TO SUBMIT THE REPORT, FORM 7100.2 REQUIRES A MAOP AND PIR VALUE (FORM PART E2 AND PART D3, RESPECTIVELY) WHICH ARE NOT APPLICABLE IN THE CASE OF THIS REPORTABLE INCIDENT. THE MAOP ENTERED IN THIS REPORT IS FOR THE ASSOCIATED GATHERING SYSTEM. THE PIR HAS BEEN CALCULATED USING THE MAOP OF THE GATHERING SYSTEM AND CASING SIZE. TGP HAS PLUGGED THE WELL BUT, MAY REPAIR AND BRING IT BACK ONLINE IN THE FUTURE. ALTHOUGH REPORT FORM 7100.2 PART A, ITEM 15B REQUIRES A SUPPLEMENTAL REPORT, BECAUSE OF THE UNIQUE ATTRIBUTES OF UNDERGROUND STORAGE FACILITIES, THIS REPORT HAS BEEN SUBMITTED AS FINAL. UNLESS THERE ARE ADDITIONAL SIGNIFICANT CHANGES RELATED TO THE EVENT (NOT ANTICIPATED), ADDITIONAL SUPPLEMENTAL REPORTS WILL NOT BE SUBMITTED. FURTHER ACTIONS, SUCH AS WELL REACTIVATION, WILL BE REPORTED TO PHMSA UNDER EXISTING REGULATORY REPORTING REQUIREMENTS (E.G., ANNUAL REPORTS AND/OR 49CFR 191.22 REQUIREMENTS). THE INVESTIGATION HAS BEEN COMPLETED TO THE EXTENT POSSIBLE AND THE CAUSE OF THE LEAK IS UNKNOWN.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170052 | 17368 | 2017-07-03 10:53 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2017-06-07 07:37 | 2017 |  |  | 28.7002 | -96.9428 | 1180524 | 2017-06-07 16:25 |  | NATURAL GAS |  | 27450 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-06-07 07:37 | 2017-06-08 10:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-06-07 07:37 | 2017-06-07 07:37 | ONSHORE | TX | 77905 | VICTORIA | VICTORIA | SURVEY STATION NO. | 2021-09-01 | STATION 9 | 100-1 LINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | ESD SYSTEM | 1948 |  | CARBON STEEL |  | OTHER | [8 empty] | GAS RELEASE DURING COMPRESSOR STATION ESD. | CLASS 1 LOCATION | NO |  | 454 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 64508 | 59080.6442307692 | 0 | 0 | 3500 | 3722.72137828825 | 0 | 0 |  |  | 68008 | 62960.4138819221 | 62803.3656090575 | [8 empty] | 700 |  | 750 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE ESD WAS INITIATED SOLELY AT THE COMPRESSOR STATION WITH NO GAS CONTROL INVOLVEMENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | FAILURE OF ESD VALVE OVERRIDE | [161 empty] | KENNETH PETERS | SENIOR ENGINEER | ken_peters@kindermorgan.com | 2053257554 | 2053253508 |  |  |  | REJI GEORGE | DIRECTOR COMPLIANCE CODES AND STANDARDS | 7134205433 | reji_george@kindermorgan.com | THE EMERGENCY SHUTDOWN SYSTEM (ESD) FAILED TO OPERATE PROPERLY AT TENNESSEE GAS PIPELINE'S VICTORIA (TX) COMPRESSOR STATION #9 ON JUNE 6, 2017. THIS ALLOWED MORE GAS THAN NORMAL TO BE RELEASED TO ATMOSPHERE, PROMPTING INCIDENT NOTIFICATION TO THE NRC DUE TO THE VOLUME OF GAS LOST. SEVERAL VALVES IN THE ESD SYSTEM FAILED TO MOVE INTO THE APPROPRIATE ESD RESPONSE POSITION DUE TO FAULTY VALVE OVERRIDE. SINCE THIS IS A MANNED COMPRESSOR STATION, ON-SITE PERSONNEL RESPONDED AND MADE NECESSARY ADJUSTMENTS TO INSURE FUTURE CORRECT ESD OPERATION. THE STATION WAS AVAILABLE TO GO BACK INTO SERVICE THE NEXT DAY. THE NRC ISSUED INCIDENT NUMBER 1180635 FOR THE PHMSA PRESCRIBED 48-HOUR UPDATE ON JUNE 8, 2017.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170053 | 30894 | 2017-07-05 16:22 | SUPPLEMENTAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2017-06-17 04:01 | 2017 |  |  | 44.6428 | -93.1618 | 1181425 | 2017-06-17 09:24 |  | NATURAL GAS |  | 23700 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | BLOW DOWN ESD VALVE OPENED AND VENTED THROUGH SILENCER ON VENT STACK. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-06-17 06:30 | 2017-06-17 06:30 | ONSHORE | MN | 55024 | Not Within a Municipality | DAKOTA | SURVEY STATION NO. | FARMINGTO STA | FARMINGTON COMPRESSOR STATION | MN-080-MAOP | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | BLOW DOWN VALVE TO ESD SYSTEM | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | THE FARMINGTON B DISCHARGE BLOW DOWN VALVE OPENING EVENT WAS CAUSED BY THE PILOT CONTROLLED ESD 3-WAY POPPET VALVE TO IMPROPERLY SEAL/PREVENT POWER GAS FROM REACHING THE MAIN VALVE OPENING CONTROL CIRCUIT. | CLASS 1 LOCATION | NO |  | 510 |  | NO | NO | NO |  | 350 | 372.272137828826 | 0 | 0 | 62568 | 57303.8653846154 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 62918 | 59580.4019651153 | 57676.1375224442 | [8 empty] | 800 |  | 950 | 192.619(A)(4) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CAUSE OF THE INCIDENT WAS EQUIPMENT ERROR. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [12 empty] | YES | [174 empty] | KEN ANDERSON | INTERNAL CORROSION SPECIALIST | ken.anderson@nngco.com | 402-398-7617 |  |  |  |  | KEN ANDERSON | INTERNAL CORROSION SPECIALIST | 402-398-7617 | ken.anderson@nngco com | THE FARMINGTON B DISCHARGE BLOW DOWN VALVE OPENING EVENT ON 6/17/2017 WAS CAUSED BY THE PILOT CONTROLLED ESD 3-WAY POPPET VALVE TO IMPROPERLY SEAL/PREVENT POWER GAS FROM REACHING THE MAIN VALVE OPENING CONTROL CIRCUIT. THE PURPOSE OF THE PILOT VALVE IS TO CONNECT THE POWER GAS PORT TO THE OPENING CONTROL PORT ONLY IF/WHEN ESD PILOT IS REMOVED FROM THE CIRCUIT BLOCK. THE 'AS FOUND' CONDITION OF THE PILOT VALVE, CLEARLY TESTED AN OPEN PATH BETWEEN THE TWO PORTS, EVEN WITH NORMAL ESD PILOT GAS PRESENT (NON-ESD CONDITION). FURTHER REVIEW OF THE POPPET VALVE ASSEMBLY SUPPORTED THE FAILURE WAS DUE TO END OF LIFE-CYCLE FOR THE SOFT COMPONENTS (POPPET VALVE/O-RINGS). THE POPPET VALVE IS TUBED IN A DEAD-LEG CONFIGURATION AND ONLY FLOWS DURING ESD ACTUATION, LAST ACTUATION/TEST WAS SUCCESSFULLY DONE SO IN SEPTEMBER OF 2016. NORMALLY THE VALVE IS OPERATED ONCE YEAR DURING THE ANNUAL STATION ESD TEST. A NEW ESD CONTROL POPPET VALVE WAS INSTALLED AND TESTED ON THE ACTUATOR AND PLACED INTO SERVICE ON 6/17/2017.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170054 | 17400 | 2017-07-06 07:43 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2017-06-09 14:00 | 2017 |  |  | 28.9208 | -93.0317 | 1180720 | 2017-06-09 14:55 |  | NATURAL GAS |  | 11400 | 48500 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-06-09 14:00 | 2017-07-01 12:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-06-09 14:00 | 2017-06-09 14:00 | OFFSHORE | [28 empty] | 80 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST CAMERON | 272 | PLATFORM | INTERSTATE | OFFSHORE PLATFORM, INCLUDING PLATFORM-MOUNTED EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1978 |  | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 786 |  | NO | NO | NO |  | 0 | 0 | 145500 | 154758.84586884 | 34200 | 31322.5961538462 | 3000 | 3190.90403853279 | 0 | 0 | 0 | 0 |  |  | 182700 | 104976.660693419 | 189272.346061219 | [8 empty] | 900 |  | 1440 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE VALVE GREASE ZERK FAILURE COULD NOT BE ATTRIBUTED TO CONTROL ROOM ACTIONS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | OTHER | GREASE ZERK | [18 empty] | YES | EXTERNAL CORROSION IN THE THREADING | [161 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | dwayne.teschendorf@enbridge.com | 713-627-5573 |  |  |  |  | NATHAN ATANU | OPERATIONAL COMPLIANCE SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | ON JUNE 9, 2017 ENBRIDGE PERSONNEL WERE ABOARD THE WEST CAMERON BLOCK 272 PLATFORM WHEN A GAS RELEASE WAS DISCOVERED AT A 1/2-INCH DIAMETER ZERK ON A TEXAS EASTERN TRANSMISSION, LP 30-INCH LINE 41 CHECK VALVE. THE CAUSE OF THE LEAK WAS DUE TO EXTERNAL CORROSION IN THE THREADS ON THE ZERK. REPLACEMENT OF THE ZERK WAS PERFORMED AND THE PIPELINE WAS RETURNED TO SERVICE JULY 1, 2017.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170055 | 30320 | 2017-07-06 11:57 | SUPPLEMENTAL FINAL | 1217 | BEAR CREEK STORAGE CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2017-06-16 11:14 | 2017 |  |  | 32.3987 | -92.923 | 1181341 | 2017-06-16 12:58 |  | NATURAL GAS |  | 1765 | 10 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-06-16 13:00 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-06-16 11:14 | 2017-06-16 11:14 | ONSHORE | LA | 71008 | Not Within a Municipality | BIENVILLE | MILEPOST | MILEPOST 2 | BCS LINE 5/6-4 LATERAL | 5/6-4 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 62 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 |  | 0.375 | 52000 | API - 5LX | SEAMLESS |  | ARMCO STEEL, AMBRIDGE, PA | COAL TAR | [28 empty] | 1981 | 1981 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 331 |  | NO | NO | NO |  | 0 | 0 | 30 | 31.9090403853279 | 5295 | 4849.50721153846 | 55000 | 58499.9073731012 | 2000 | 2127.26935902186 | 0 | 0 |  |  | 62325 | 32871.825297653 | 65508.5929840468 | [8 empty] | 2435 |  | 3255 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 373 | NO | [5 empty] | YES | LATERAL LINE TO WELL DOES NOT CONTAIN TRAPS TO ACCOMMODATE ILI TOOL OR OTHER TOOLS; | YES |  |  |  |  | YES | LATERAL LINE DOES NOT CONTAIN TRAPS | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SLOW LEAK EVENT; JUNE 14, 2017, 10:00 AM CSDT; GROUND LEAK PATROL FOUND NO LEAK AT THAT TIME; LEAK DISCOVERED JUNE 16, 2017; 11:14 AM CSDT; | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1981 | NO | YES | YES |  |  |  | 2017 |  |  |  | NO | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | WM MARTIN MULLER | SPECIALIST-PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205 410 4383 | 205 325 3674 |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713 369 9443 | jaime_hernandez@kindermorgan.com | JUNE 14, 2017, GROUND PATROL EMPLOYEE FOUND NO LEAK ON BCS LINE 5/6-4 LATERAL; JUNE 16, 2017, BY VISUAL OBSERVATION, GROUND PATROL EMPLOYEE DISCOVERED LEAK ON SAID LATERAL LINE; LATERAL LINE PRESSURE WAS LOWERED TO 0 PSIG BY CLOSING APPROPRIATE VALVES ON JUNE 16, 2017; LATERAL LINE REMAINED OUT OF SERVICE AS PLANS WERE MADE TO COORDINATE LATERAL LINE REPLACEMENT WITH ANOTHER PLANNED AND BUDGETED PROJECT TO OCCUR LATER IN 2017 AND 2018 AS THE LATERAL LINE OUTAGE WAS DETERMINED TO NOT BE AN OPERATIONAL EMERGENCY; THE REPLACED BCS LINE 5/6-4 WAS RETURNED TO SERVICE ON MAY 11, 2018;
2021-02-26 10:37 | YES | NO | UNGS (Underground Natural Gas Storage) | 20170056 | 32312 | 2017-07-06 13:43 | SUPPLEMENTAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2017-06-19 09:25 | 2017 |  |  | 33.7424 | -88.674 | 1181561 | 2017-06-19 09:55 |  | NATURAL GAS |  | 1620 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-06-19 09:40 | 2019-06-18 14:30 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2017-06-19 09:25 | 2017-06-19 09:28 | ONSHORE | MS | 39756 | Not Within a Municipality | MONROE COUNTY | MILEPOST | STATION 10+57 | LINE 28-18 | LINE 28-18 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 56 |  | NO | [22 empty] | INTERSTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | UNDERGROUND GAS STORAGE OR CAVERN | [38 empty] | 1975 |  | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 134 | 21 |  | CLASS 1 LOCATION | NO |  | 306 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 4860 | 4451.10576923077 | 304000 | 323344.942571323 | 2000 | 2127.26935902186 | 0 | 0 |  |  | 310860 | 154014.996918374 | 329923.317699575 | [8 empty] | 2208 |  | 2640 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | STORAGE FIELD WAS IN INJECTION MODE WHEN PIPELINE FAILURE OCCURRED; | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  | YES | [5 empty] | YES |  |  | YES | [5 empty] | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | YES | [313 empty] | WM. MARTIN MULLER | SPECIALIST - PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205 410 4383 | 205 325 3674 |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713 369 9443 | jaime_hernandez@kindermorgan.com | JUNE 19, 2017, THREE ENGINES WERE RUNNING AS THE STORAGE FIELD WAS OPERATING IN ITS INJECTION MODE. 9:25 AM, EMPLOYEE HEARD A LOUD NOISE, CHECKING PLANT FACILITIES HE FOUND NO ISSUE WITH RELIEF VALVES OR VENTS. DISCOVERING THERE WERE FLAMES IN THE STORAGE FIELD, EMPLOYEES IMMEDIATELY STOPPED ALL ENGINES. THE EMPLOYEES ALSO CLOSED THE FIELD HEADER VALVES ISOLATING FIELD TRUNK LINE "A" WHICH FIELD LINE 28-18 IS ASSOCIATED. 9:50 AM, THE NATURAL GAS WAS DEPLETED IN THE FIELD LINE AND THE FIRE WAS OUT. THE FIRE FROM THE FIELD LINE RUPTURE DAMAGED THE NEARBY METER RUN AND WELL HEAD. FOLLOWING PREVIOUS FIELD LINE REPAIR, THE WELL HEAD REPLACEMENT PROJECT WAS COMPLETED NOVEMBER 19, 2018. FINAL REPLACEMENTS AND FABRICATIONS FOR THE METER RUN BEGAN JUNE 05, 2019 AND WERE COMPLETED JUNE 14, 2019. FACILITY WAS RETURNED TO SERVICE JUNE 18, 2019, 2:30 PM.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170057 | 17556 | 2017-07-13 14:11 | SUPPLEMENTAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2017-06-09 08:00 | 2017 |  |  | 35.2434 | -91.7027 | 1181336 | 2017-06-16 12:45 |  | NATURAL GAS |  | 52 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-11-28 12:00 | 2017-11-28 21:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-06-09 12:00 | 2017-06-09 12:00 | ONSHORE | AR | 72143 | SEARCY | WHITE | MILEPOST | JM-9 TAP | JM-8 | JM-8 AT THE TAP FOR JM-9 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | TAP FITTING(STOPPLE, THREAD-O-RING, WELD-O-LET, ETC.) | [20 empty] | TAP FITTING | [17 empty] | 1967 |  | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | YES | METHOD2 | 217 |  | NO | NO | NO |  | 0 | 0 | 500 | 531.817339755465 | 156 | 142.875 | 93500 | 99449.842534272 | 0 | 0 | 0 | 0 |  |  | 94156 | 46042.3450815117 | 100124.534874027 | [8 empty] | 675 |  | 988 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 4526 | NO |  | YES |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL ROOM DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [8 empty] | YES | LEAKING WELD | [19 empty] | YES | A TAP WAS PERFORMED IN 1967 ON 6 INCH PIPE. A HOLE WAS CUT IN THE 6 INCH, THEN A 3 INCH PIECE OF PIPE WAS INSERTED IN THE HOLE AND WELDED. THE 6" HOLE WAS LARGER ON ONE SIDE AND THE WELD LEAKED AND ALLOWED GAS PRESSURE TO SADDLE WELDS. | [55 empty] | NO | [63 empty] | NO |  |  | Yes, and an investigative dig was cunducted at the point of the Accident | 2017 | [12 empty] | YES |  |  | 2010 | [6 empty] | YES | [53 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558-4647 |  |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558-4647 | casey.roberts@enablemidstream.com | ON JUNE 9, 2017 AN EXTERNAL CORROSION DIRECT ASSESSMENT DIG WAS PERFORMED ON ENABLE GAS TRANSMISSION LINE JM-8 (AT THE TAP FOR JM-9) AND A MINOR LEAK WAS FOUND DURING THE RE-COATING PROCESS. THE LEAK IS IN A CLASS 3 HCA LOCATION. LEL LEVELS WERE MEASURED TO BE 18% DIRECTLY AT THE LEAK AND 0% WHEN INSTRUMENT IS REMOVED FROM THE WELD. THE LEAK IS FROM THE WELD OF THE SADDLE TO THE 6 INCH PIPE OF JM-8. IT IS WELDED AT THE NECK OF THE 3 INCH TAP FOR JM-9. THERE MUST BE A LEAKING WELD AT THE TAP FITTING WELD IN ORDER FOR IT TO BE LEAKING FROM THE SADDLE WELD. WE WILL NOT BE ABLE TO DETERMINE THE CAUSE OF THE LEAK UNTIL REPAIR IS COMPLETED. AS OF JULY 13, 2017 WE ARE WAITING ON PARTS FOR REPAIR AND MONITORING LEAK DAILY UNTIL REPAIRS ARE COMPLETED. THERE ARE SEVERAL DWELLINGS AND A CHURCH WITHIN 660FT OF THE LEAK SITE, WHICH PROMPTED A 20% DROP IN PRESSURE FROM 675 PSIG TO 540 PSIG OR LESS. WHILE PLANNING THE REPAIR IT WAS DETERMINED THAT THE ESTIMATED REPAIR COSTS COULD EXCEED $50,000, MEETING THE DEFINITION OF AN INCIDENT. DUE TO THIS, NOTIFICATION WAS PROVIDED TO THE NRC ON JUNE 16, 2017 (NRC #1181336). A FOLLOW UP CALL WAS PLACED TO THE NRC ON JUNE 18, 2017 (NRC #1181499). PLAN OF REPAIR INCLUDES REMOVAL OF THE ENTIRE SET UP AND RE-FABRICATE THE TAP AND RISER WHICH THE FABRICATION COULD BE DONE OFF SITE AND TESTED. WE WILL THEN INSTALL (2) 6 INCH STOPS AND HOSE BYPASS TO KEEP THE DOWNSTREAM CUSTOMERS ON JM-8 AND JM-9 IN SERVICE AND DROP IN THE NEW FABRICATION WITH 2 WELDS MINIMIZING BYPASS TIME. WHEN THE REPAIRS ARE COMPLETED, I WILL FOLLOW UP WITH A SUPPLEMENTAL REPORT. UPDATE 11/30/17 THE LEAK WAS STOPPED AND REPAIRED ON 11/28/17. THE FOLLOWING SECTIONS WERE UPDATED: A.15 UPDATED TO INDICATE SHUTDOWN TO REPAIR PIPELINE D.7 UPDATED TO REFLECT TOTAL COSTS UPDATE 1/9/18 FINAL COSTS AND ROOT CAUSE DETERMINED. A.10 GAS LOSS UPDATED D.7.B, D.7.F, D.7.G UPDATED TO REFLECT FINAL COST G.5.1, G.5.2, G.5.4 UPDATED TO REFLECT ROOT CAUSE UPDATE 1/10/18 CHANGES MADE TO INCORPORATE AID FEEDBACK A.4 DATE CHANGED A.7 TIME CHANGED A.8 INCIDENT RESULTED FROM: CHANGED TO UNINTENTIONAL RELEASE OF GAS
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170058 | 17424 | 2017-07-18 14:01 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2017-06-26 12:30 | 2017 |  |  | 28.5117 | -92.453 | 1182332 | 2017-06-26 14:30 |  | NATURAL GAS |  | 105 | 17660 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-06-26 17:31 | 2017-08-09 08:01 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-06-26 14:30 | 2017-06-26 14:30 | OFFSHORE | [28 empty] | 150 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | VERMILLION | 265 | BELOW WATER, PIPE ON OR ABOVE SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 20 |  | 0.406 | 52000 | API-5L | SEAMLESS |  | U.S. STEEL | OTHER | SOMASTIC AND CONCRETE | [27 empty] | 1971 | 1971 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 524 |  | NO | NO | NO |  | 0 | 0 | 52980 | 56351.3653204891 | 315 | 288.497596153846 | 600000 | 638180.807706558 | 0 | 0 | 0 | 0 |  |  | 653295 | 319107.692481368 | 694820.670623201 | [8 empty] | 761 |  | 1440 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 170024 | NO |  |  |  | YES |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | LOCATED BY THIRD PARTY PERSONNEL DURING ROUTINE FLY OVER |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS TOO SMALL TO BE IDENTIFIED BY THE CONTROL ROOM PERSONNEL. A REVIEW OF OPERATING RECORDS FOUND ABNORMAL OPERATING CONDITIONS DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES | [5 empty] | YES | RECENT HISTORY OF THE PIPELINE | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | dwayne.teschendorf@enbridge.com | 713-627-5573 |  |  |  |  | NATHAN ATANU | SUPERVISOR OPERATIONAL COMPLIANCE | 713-627-5008 | nathan.atanu@enbrdige.com | INDICATIONS OF BUBBLES ON THE WATER SURFACE IN VERMILION BLOCK 265 WERE REPORTED BY A THIRD PARTY HELICOPTER ON JUNE 26, 2017. UPON INVESTIGATION, IT WAS DETERMINED THE LEAK WAS CAUSED BY A PINHOLE LEAK RESULTING FROM INTERNAL CORROSION ON TEXAS EASTERN TRANSMISSION, L.P. 20-INCH LINE 41-A-2 NATURAL GAS PIPELINE. REPAIR BY INSTALLATION OF A LEAK CLAMP WAS COMPLETED AUGUST 9, 2017 AND THE PIPELINE WAS RETURNED TO SERVICE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170059 | 17384 | 2017-07-21 16:50 | ORIGINAL FINAL | 13845 | NORTHWEST PIPELINE LLC | 295 CHIPETA WAY | SALT LAKE CITY | UT | 84108 | 2017-06-23 10:00 | 2017 |  |  | 37.8832 | -109.0132 | 1182427 | 2017-06-27 12:32 |  | NATURAL GAS |  | 11327 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-06-23 22:15 | 2017-06-23 23:20 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-06-23 20:55 | 2017-06-23 21:45 | ONSHORE | CO | 81325 | EGNAR | SAN MIGUEL | MILEPOST | 0 | NUCLA REG STATION | 2401 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | UNKNOWN |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | MOONEY DIAPHRAGM SEAT | OTHER | [8 empty] | MOONEY DIAPHRAGM TEAR CAUSED PRESSURE DOWNSTREAM OF REGULATORS TO BUILD LEADING TO RELIEF VALVE VENTING TO ATMOSPHERE. | CLASS 1 LOCATION | NO |  | 79 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 33415 | 30603.6418269231 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 33415 | 31728.1850961538 | 30603.6418269231 | [8 empty] | 321 |  | 300 | 192.619(A)(3) |  |  |  | PRESSURE EXCEEDED MAOP, BUT DID NOT EXCEED THE APPLICABLE ALLOWANCE IN 192.201 | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [13 empty] | YES | [174 empty] | JOSH KUSHLAN | PIPELINE SAFETY ENGINEER | josh.kushlan@williams.com | 801-584-6261 |  |  |  |  | JASON LAMBERT | MANAGER PIPELINE SAFETY | 8015846657 | jason.lambert@williams.com | 8:55 PM 6-23-17 A LANDOWNER CALLED NOTIFYING GAS CONTROL THAT THERE WAS A BLOWING GAS SOUND COMPARED TO A JET ENGINE. GAS CONTROL NOTIFIED FIELD OPERATIONS. OPERATIONS RESPONDED WITHIN ONE HOUR AND FOUND RELIEF VALVE BLOWING AS DESIGNED. FIELD OPERATOR SHUT IN BOTH REGULATORS CAUSING RELIEF VALVES TO STOP BLOWING AT 10:15 PM. FIELD OPERATORS DISCOVERED THAT BOTH MOONEY REGULATORS ONSITE HAD TEARS IN THE DIAPHRAGM CAUSING THEM TO FAIL AND LET GAS PRESSURE PAST THEM. FIELD OPERATORS REPLACED THE DIAPHRAGMS AND DOUBLE CHECKED DELIVERY PRESSURE. PRESSURE SHOWED 295 PSI. RELIEF VALVES WERE SET AT 319 AND 321 PSI. NUCLA LATERAL OPERATES AT 300 PSI MAOP. EMPLOYEES VERIFIED DELIVER PRESSURE WAS CURRENT AND ALL VALVES AT STATION WERE LEFT IN NORMAL OPERATING POSITION. LINE PUT BACK IN SERVICE AT 11:20 PM 6-23-17. INITIAL CALCULATIONS OF GAS VOLUMES RELEASED USING TIME GAS CONTROL WAS NOTIFIED AS EVENT START WERE UNDER THE 3,000 MCF REPORTING CRITERIA SO AN NRC NOTIFICATION WAS NOT MADE. ON 6-27-17 IT WAS CONFIRMED WITH THE LANDOWNER THAT GAS WAS BLOWING AT THE LOCATION FROM APPROXIMATELY 10:00 AM 6-23-17 UNTIL THE REGULATORS WERE SHUT IN AT 10:15 PM. WITH THIS ADDITIONAL INFORMATION THE 3,000 MCF REPORTING CRITERIA WAS EXCEEDED BY GAS ESCAPING THE RELIEF VALVE AS DESIGNED. AT 12:32 PM 6-27-17 AN INITIAL NRC NOTIFICATION, # 1182427, WAS MADE, AT 10:02 AM 6-28-17 A FOLLOW UP NRC NOTIFICATION, # 1182511, WAS MADE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170060 | 17587 | 2017-07-21 18:31 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2017-06-22 12:12 | 2017 |  |  | 36.7003 | -121.2113 | 1181983 | 2017-06-22 15:03 |  | NATURAL GAS |  | 25000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELIEF VALVE OPENED, NO OVERPRESSURE EXCURSION | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-06-22 12:12 | 2017-06-22 13:39 | ONSHORE | CA | 95075 | PAICINES | SAN BENITO | MILEPOST | MILE POINT | L300A | 7947879 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2004 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE OPENED | CLASS 1 LOCATION | NO |  | 589 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 75000 | 68689.9038461538 | 0 | 0 | 0 | 0 | 0 | 0 | N/A |  | 75000 | 71213.9423076923 | 68689.9038461538 | [8 empty] | 610 |  | 625 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) | [9 empty] | YES |  |  |  | YES | 1 | 0 | NO |  |  | INCORRECT OPERATION | WRONG EQUIPMENT SPECIFIED OR INSTALLED | INCORRECT OPERATION | INCORRECT EQUIPMENT | [204 empty] | WRONG EQUIPMENT SPECIFIED OR INSTALLED | [5 empty] | YES | YES | THE OPERATOR REALIZED THAT THE SET POINT CHANGE WAS BEING PERFORMED ON A DIFFERENT STATION THAN REQUESTED. | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | STEPHEN RAMOS | GAS ENGINEER | s3rc@pge.com | 925-413-7311 |  |  |  |  | SUSIE RICHMOND | MANAGER REGULATORY COMPLIANCE | 925-328-5776 | gsr8@pge.com | ON JUNE 22, 2017 AT 1212 HOURS, A PG&E EMPLOYEE IN GAS CONTROL WAS PERFORMING A SET POINT CHANGE ON PRESSURE LIMITING STATION (PLS-6) IN PAICINES (OFF OF L-300A AT MILE POINT 436.74). AS THE OPERATOR WAS INCREASING THE SET POINT, THE RELIEF VALVE OPENED CAUSING AN UNINTENTIONAL RELEASE OF GAS. AT THAT POINT, THE OPERATOR REALIZED THAT THE SET POINT CHANGE WAS BEING PERFORMED ON A DIFFERENT STATION THAN REQUESTED. THE MAOP OF THE STATION IS 625 PSIG AND THE RELIEF VALVE OPENED AT 610 PSIG. THERE WAS NOT AN OVERPRESSURE. THE OPERATOR WAS RELIEVED OF THEIR DUTIES, TURNOVER SHIFT WAS COMPLETED, FATIGUE ASSESSMENT WAS PERFORMED AND THE EMPLOYEE WAS SENT FOR PAT TESTING. THE SET POINT AT THE STATION WAS CHANGED BACK TO ITS NORMAL SET POINT AND THE RELIEF VALVE CLOSED. THERE WERE NO INJURIES, FATALITIES OR IGNITION ASSOCIATED WITH THIS INCIDENT. PG&E TECH WAS DISPATCHED TO DO AN EVALUATION. THE TECH DETERMINED THAT THE EQUIPMENT WAS FUNCTIONING PROPERLY AND THERE WAS NO DAMAGE OBSERVED. THE ESTIMATED DURATION FOR UNINTENTIONAL RELEASE WAS 45 MINUTES. THE ESTIMATE OF GAS VOLUME THAT WAS UNINTENTIONALLY RELEASED IS 25 MMCF. THIS REPORT WAS SUBMITTED TO THE DOT (1181976/1182113) AND CPUC DUE TO SIGNIFICANT EVENT DETERMINED BY OPERATOR JUDGEMENT AND AN UNINTENTIONAL RELEASE OF GAS ABOVE 3 MMCF. THE SIGNIFICANT EVENT DETERMINED BY OPERATOR JUDGEMENT CRITERION WAS DETERMINED AT 1350 HOURS AND THE UNINTENTIONAL ESTIMATE RELEASE OF GAS ABOVE 3 MMCF CRITERION WAS DETERMINED AT 1440 HOURS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170061 | 17411 | 2017-07-24 15:33 | SUPPLEMENTAL FINAL | 18152 | SEA ROBIN PIPELINE CO | 800 E. SONTERRA BLVD | SAN ANTONIO | TX | 78258 | 2017-06-25 08:23 | 2017 |  |  | 28.195 | -91.6806 | 1182216 | 2017-06-25 08:23 |  | NATURAL GAS |  | 300 | 2038.9 | 3.57 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-06-25 08:40 | 2017-07-04 01:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-06-25 14:00 | 2017-06-25 14:00 | OFFSHORE | [28 empty] | 260 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EUGENE ISLAND | 338 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12.75 |  | 0.438 | 52000 | UNKNOWN | OTHER | UNKNOWN | UNKNOWN | OTHER | MASTIC AND CONCRETE | [27 empty] | 1973 | 1973 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 318 |  | NO | NO | NO |  | 0 | 0 | 5847 | 6219.07197110041 | 860 | 787.644230769231 | 398927 | 424312.591793257 | 176956 | 188216.538347536 | 0 | 0 |  |  | 582590 | 284838.338113119 | 619535.846342663 | [8 empty] | 1000 |  | 1306 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 31680 | NO | YES |  | YES |  |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | PRODUCER PLATFORM PERSONNEL. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS TOO SMALL FOR SCADA TO DETECT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | PIN-HOLE LEAK AT THE 2 O'CLOCK POSITION. | YES | [7 empty] | YES | LOW FLOW CONDITIONS. |  |  |  |  | YES | 2 O'CLOCK POSITION. | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713.857.5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | 713.857.5479 | nathan.hlavaty@energytransfer.com | THE INITIAL UNKNOWN SOURCE NRC #1182216 NOTIFICATION WAS MADE AT 08:23 ON 06/25/17. THE CONFIRMATION OF THE LEAK ON SEA ROBIN NRC #1182760 WAS MADE AT 13:58 ON 06/30/17. RELATED UPDATES TO THE NRC INCLUDE THE FOLLOWING NRC #1182770 AT 15:05 ON 06/30/17, AND NRC #1182773 AT 15:31 ON 06/30/17. THE 48 HOUR UPDATE NOTIFICATION TO THE NRC OCCURRED AT 10:53 ON 07/02/17. THE CENTRALIZED PHMSA ACCIDENT INVESTIGATION DIVISION WAS INITIALLY NOTIFIED ON 06/26/17, AND WAS PROVIDED DAILY UPDATES FROM 06/26/17 THROUGH THE RESTART OF THE LINE ON 07/03/17. 08/21/17 SUPPLEMENTAL/FINAL WAS CREATED TO CORRECT PART A, QUESTION 12; THE ORIGINAL/FINAL REPORT INCORRECTLY REPORTED GALLONS NOT BARRELS.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170062 | 17404 | 2017-07-25 11:21 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2017-07-16 13:20 | 2017 |  |  | 28.6999 | -96.9434 | 1184248 | 2017-07-16 13:50 |  | NATURAL GAS |  | 14992 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-07-16 13:20 | 2017-07-17 18:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-07-16 13:20 | 2017-07-16 13:20 | ONSHORE | TX | 77905 | Not Within a Municipality | VICTORIA | MILEPOST | MILEPOST 13 | STATION 9 - VICTORIA COMPRESSOR STATION | 100-1: 1-1D TO 9-1S | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1948 |  | CARBON STEEL |  | OTHER | [8 empty] | BEFORE STATION OPERATOR COULD BLOW STATION SYSTEM DOWN, GAS DETECTOR SAW PERCENTAGE OF GAS FROM A LEAKING VALVE CAP AND INITIATED ESD; THEN SUCTION SIDE VALVE DID NOT CLOSE COMPLETING ESD CYCLE BECAUSE OF STICKING ACTUATOR; | CLASS 1 LOCATION | NO |  | 454 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 48725 | 44625.5408653846 | 2500 | 2659.08669877733 | 350 | 372.272137828826 | 0 | 0 |  |  | 51575 | 47656.7982131915 | 47656.8997019908 | [8 empty] | 650 |  | 750 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | BEFORE STATION OPERATOR COULD BLOW STATION SYSTEM DOWN, GAS DETECTOR SAW PERCENTAGE OF GAS FROM A LEAKING VALVE CAP AND INITIATED ESD; THEN SUCTION SIDE VALVE DID NOT CLOSE COMPLETING ESD CYCLE BECAUSE OF STICKING ACTUATOR; | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | VALVE ACTUATOR FAILED TO CLOSE VALVE PROPERLY; REPAIR HAS BEEN MADE; | [161 empty] | WILLIAM MARTIN MULLER | SPECIALIST - PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205 325 3863 | 205 325 3508 |  |  |  | REJI GEORGE | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713 420 5433 | reji_george@kindermorgan.com | NRC REPORT 1184248; 13:50; 07/16/2017; NRC UPDATE REPORT 1184422; 10:58; 07/18/2017; ON 07/16/2017; STATION 9 SHUTDOWN ON A HIGH LIQUID LEVEL ALARM; WHILE STATION OPERATOR WAS INVESTIGATING, BEFORE SYSTEM COULD BE BLOWN DOWN, A COMPRESSOR VALVE CAP LEAKED; NATURAL GAS WAS DETECTED BY GAS DETECTION SYSTEM; AS DESIGNED, AN ESD OCCURRED; STATION OPERATOR HEARD THE ESD IN PROGRESS; THE ACTUATOR OF A 24-INCH SUCTION SIDE VALVE FAILED TO CLOSE SAID VALVE; STATION OPERATOR MANUALLY CLOSED VALVE; 14,992 MCF OF NATURAL GAS WAS RELEASED TO ATMOSPHERE; STATION WAS IMMEDIATELY TAKEN OFF LINE; NECESSARY REPAIRS WERE MADE; STATION 9 RETURNED TO SERVICE ON 07/17/2017; APPROXIMATELY 18:30 HOURS; PIR OF THE 24-INCH YARD PIPING CONTAINING SAID VALVE IS 454 FEET;
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170063 | 17390 | 2017-07-27 12:53 | ORIGINAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2017-06-29 10:20 | 2017 |  |  | 32.1587 | -92.0924 | 1182633 | 2017-06-29 11:15 |  | NATURAL GAS |  | 26710 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THIS EVENT CAUSED NO INTERRUPTION IN SERVICE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-06-29 10:20 | 2017-06-29 10:57 | ONSHORE | LA | 71418 | COLUMBIA | CALDWELL | MILEPOST | 59.4155 | COLUMBIA COMPRESSOR STATION | BAE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1968 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE VENTED PREMATURELY. | CLASS 1 LOCATION | NO |  | 157 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 86540 | 79258.9903846154 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 86540 | 82171.3942307692 | 79258.9903846154 | [8 empty] | 820 |  | 810 | 192.619(A)(1) |  |  |  | PRESSURE EXCEEDED MAOP, BUT DID NOT EXCEED THE APPLICABLE ALLOWANCE IN 192.201 | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [14 empty] | YES | [176 empty] | SHANNON MATTINGLY | PA OQ AND EVENT SUPPORT PROGRAM LEADER | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 2706886361 | jeff.mcmaine@bwpmlp.com | A RELIEF VALVE AT THE COLUMBIA COMPRESSOR STATION PREMATURELY ACTIVATED. MAOP OF 810 PSIG WAS EXCEEDED; RECORDED PRESSURE OF 820 PSIG WAS DOCUMENTED. MAOP EXCEEDANCE WAS NOT 110% OR MORE. RELIEF VALVE WAS SET AT 843 PSIG. THE OPERATOR AT THE STATION WORKED WITH CONTROLLER TO SHUT IN THE VALVE. THE RELIEF VALVE WILL BE REMOVED.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20170064 | 17416 | 2017-07-31 14:22 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2017-06-30 15:35 | 2017 |  |  | 29.2117 | -92.6078 | 1182837 | 2017-07-01 11:26 |  | NATURAL GAS |  | 218 | 0 | 2.98 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-06-30 19:00 | 2017-07-05 10:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-06-30 18:00 | 2017-07-02 22:15 | OFFSHORE | [28 empty] | 40 | IN STATE WATERS | LA | VERMILLION | 82 | VERMILLION |  |  |  | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 8 |  | 0.5 | 35000 | API5L GR.B | SEAMLESS |  | YOUNGSTOWN STEEL | OTHER | CONCRETE WEIGHT COATING | [27 empty] | 1970 | 1970 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 300 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 660 | 604.471153846154 | 300000 | 319090.403853279 | 0 | 0 | 0 | 0 |  |  | 300660 | 147097.597846068 | 319694.875007125 | [8 empty] | 900 |  | 1440 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 32000 | NO | YES | [6 empty] | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | NO |  |  |  |  | OTHER | B.S.E.E. |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN | [5 empty] | YES | UNKNOWN AT THIS TIME. |  |  | YES | EXAMINATION BY DIVER. |  |  |  |  | YES | 6 O'CLOCK POSITION ON PIPE | YES | NO | NOT APPLICABLE - NOT MAINLINE PIPE | YES | [168 empty] | NO | [63 empty] | YES | 1970 | 2220 | NO | [13 empty] | NO | [63 empty] | EDGAR RODRIGUEZ | SR. REGULATORY COMPLIANCE SPECIALIST | edgar.x.rodriguez@williams.com | 7132152846 |  |  |  |  | LARRY LEGENDRE | MANAGER PIPELINE SAFETY | 713-215-2733 | larry.d.legendre@williams.com | B.S.E.E. REPORTED BUBBLES IN THE VACITNITY OF VERMILION AREA (VA) BLOCKS 101 AND 81 LATE AFTERNOON ON 6/30/17. OPERATIONS MADE THE INTIAL FLIGHT OVER THE AREA AND THEN CLOSED THE TOPSIDE BLOCK VALVE AT THE VA-66 PLATFORM AND THE TOPSIDE BLOCK VALVE A THE VA-78 PLATFORM. A SECOND FLIGHT WAS MADE THE NEXT MORNING ON 7/1/17 AND BUBBLES WERE STILL PRESENT ALONG WITH A PRESSURE DROP ON THE SHUT IN PIPELINE. A DIVE BOAT WAS SECURED WITH PERSONNEL, TOOLS, AND A TEMPORARY BOLT ON LEAK CLAMP. DIVE BOAT AND PERSONNEL ARRIVED ON LOCATION AT VA-82 BUBBLES AT 22:15 ON 7/2/17. PIPE LEAK LOCATED BY DIVER AT 01:35 ON 7/3/17; COATING WAS REMOVED AND LEAK WAS MARKED WITH A BOUY. SUBSEA TIE-IN ASSEMBLY BALL VALVE WAS LOCATED IN VA-81 DOWNSTREAM OF THE LEAK AND CLOSED AT 07:07 ON 7/4/17. BOLT ON LEAK CLAMP WAS INSTALLED IN VA-82 AND LEAK STOPPED AT 18:45 ON 7/4/17. VA-66 AND VA-78 PLATFORM VAVLES WERE OPENED AT 10:00 ON 7/5/17.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170065 | 30166 | 2017-07-31 19:42 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2017-07-01 04:45 | 2017 |  |  | 38.8866 | -122.0718 | 1183035 | 2017-07-03 13:12 |  | NATURAL GAS |  | 3100 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | CONTROL ROOM OPERATOR ADJUSTED SET POINTS REMOTELY AND SYSTEM RETURNED TO NORMAL | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-07-01 04:45 | 2017-07-01 12:00 | ONSHORE | CA | 95937 | DUNNIGAN HILLS | YOLO | MILEPOST | 233.87 | 400 | BUCKEYE STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | MAINLINE | BALL |  | ROCKWELL |  |  |  | 1961 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | UNINTENTIONAL RELEASE OF GAS THROUGH A RELIEF VALVE DUE TO OPERATOR ERROR | CLASS 1 LOCATION | NO |  | 801 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 9300 | 8517.54807692308 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 9300 | 8830.52884615385 | 8517.54807692308 | [8 empty] | 950 |  | 975 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  | YES | THE INCIDENT OCCURRED FIVE DAYS AFTER THE EMPLOYEE PERFORMED THE SET POINT CHANGE. |  |  | YES | [6 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | OPERATOR CHANGED THE SET POINT OF THE MAIN LINE VALVE INSTEAD OF THE TRIMMER VALVE |  |  | YES |  |  | NORMAL OPERATING CONDITIONS | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | ENZA BARBATO |  | e1bo@pge.com | 925-357-7889 |  |  |  |  | SUSIE RICHMOND | GAS REGULATORY COMPLIANCE MANAGER | 925-328-5776 | gsr8@pge.com | ON JUNE 27, 2017 PG&E COMPLETED A SET POINT CHANGE ON A VALVE ON L400 NEAR MP 233.87. ON JULY 1, 2017, AT 0445 HRS, PG&E'S GAS CONTROL DETECTED RELIEF VALVE ACTIVATION AT BUCKEYE CREEK STATION (LINE 400, MP 233.87). THE RELIEF OPENED 3 TIMES WITH DURATIONS OF 3 MINUTES EACH DUE TO AN OSCILLATION OF A MAINLINE VALVE. THE SYSTEM DID NOT OVER PRESSURIZE. THE CONTROL ROOM ADJUSTED THE SET POINTS ON THE REGULATING VALVE AND MAINLINE VALVES REMOTELY AND THE SYSTEM RETURNED TO NORMAL OPERATIONS BY 1242 HOURS. THERE WAS NO CUSTOMER IMPACT. THERE WAS NO FIRE, POLICE OR MEDIA REPORTED. THERE WERE NO INJURIES, FATALITIES, OR IGNITION. ON 7/3/17 AT 1159 HOURS, IT WAS DETERMINED THAT THE UNINTENTIONAL RELEASE OF GAS EXCEEDED THE 3 MMCF CRITERIA. THE VOLUME ESTIMATE OF GAS UNINTENTIONALLY RELEASED IS 3.1 MMCF. COST OF GAS UNINTENTIONALLY RELEASED IS $9,300. THIS INCIDENT WAS REPORTED TO THE DOT AND CPUC DUE TO THE UNINTENTIONAL RELEASE OF GAS ESTIMATED TO BE GREATER THAN 3 MMCF. THE VOLUME ESTIMATE UPDATE WAS PROVIDED TO THE DOT (#1183141) ON 7/5/17. IT WAS LATER DETERMINED THAT THE SET POINT CHANGES MADE BY THE OPERATOR ON JUNE 27, 2017 SHOULD HAVE BEEN ON THE TRIMMER VALVE AND NOT THE MAIN LINE VALVE. THE GAS SYSTEM OPERATOR, ALONG WITH THE PG&E GAS TRANSMISSION CONTROL CENTER SYSTEM OPERATORS AND COORDINATORS, WERE RE-TRAINED IN SET POINT CHANGE OPERATION FOLLOWING THE INCORRECT OPERATION AT DUNNIGAN HILLS ON JULY 1, 2017.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170066 | 17547 | 2017-08-01 18:42 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2017-07-09 01:36 | 2017 |  |  | 32.2178 | -107.4222 | 1183527 | 2017-07-09 03:50 |  | NATURAL GAS |  | 0 | 586 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-07-09 01:36 | 2017-08-05 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-07-09 01:55 | 2017-07-09 01:55 | ONSHORE | NM | 88240 | Not Within a Municipality | LUNA | SURVEY STATION NO. | FLORIDA B | FLORIDA B STATION MP 271+0140 | 1600 LINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 1971 |  | CARBON STEEL |  | OTHER | [8 empty] | LEAKING COMPONENTS ON THE HYDRAULICALLY CONTROLLED NOZZLE ACTUATOR SYSTEM | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO | NO |  | 0 | 0 | 2000 | 2127.26935902186 | 0 | 0 | 84000 | 89345.3130789181 | 0 | 0 | 0 | 0 |  |  | 86000 | 41988.3290107447 | 91472.58243794 | [8 empty] | 794 |  | 1080 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE ALARMS WERE WORKING PROPERLY | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | THE SEAL BROKE FROM THE NOZZLE ACTUATOR ACCUMULATOR BOTTLE | [13 empty] | YES | [164 empty] | JORGE LOPEZ |  | jorge_lopez@kindermorgan.com | 701-609-6218 |  |  |  |  | REJI GEORGE | DIRECTOR-CODES AND STANDARDS | 713-420-5433 | reji_george@kindermorgan.com | THIS FIRE WAS ASSOCIATED TO A COUPLE OF LEAKING COMPONENTS ON THE HYDRAULICALLY CONTROLLED NOZZLE ACTUATOR SYSTEM. CONTROL OIL CONTINUED TO DRIP DOWN ONTO THE HOT DISCHARGE AIR PIPING BLANKETS UNTIL THEY WERE SATURATED, CAUSING THE LUBE OIL TO EXCEED THE 200 DEGREE AUTO-IGNITION FLASH POINT, AND BECOMING THE ORIGIN OF THIS FIRE. CORRECTIVE ACTIONS: "FLORIDA B" GE FRAME 3/5 TURBINES WITH MCO TYPE NOZZLE ACTUATORS (NON-REXA) WILL BE VISUAL INSPECTED. OPERATOR SHALL INSPECT FOR ANY INDICATIONS OF HYDRAULIC OIL LEAKAGE. AFTER A VISUAL INSPECTION IS COMPLETED, OPERATOR SHALL DISASSEMBLE AND REPLACE SEALS OR GASKETS AS NEEDED ON HIGH-PRESSURE COMPONENTS ASSOCIATED WITH THE NOZZLE ACTUATOR SYSTEM. PREVENTIVE MAINTENANCE: ALL "FLORIDA B" NOZZLE ACTUATORS SYSTEMS WILL HAVE ONE OF THE FOLLOWING TASKS PERFORMED DURING THE PREDETERMINED GAS TURBINE ROTATION COMPONENT OVERHAUL. A.- ENTIRE NOZZLE ACTUATOR SYSTEM WILL BE REPLACE WITH A TOTALLY REFURBISHED SYSTEM B.- ENTIRE NOZZLE ACTUATOR SYSTEM WILL BE REMOVED AND SENT OUT TO A VENDOR FOR TOTAL REFURBISHMENT AND RETURNED TO SERVICES. C.- ENTIRE SYSTEM WILL BE DISASSEMBLED ONSITE AND HAVE ALL PARTS AND MATERIALS CLEANED, INSPECTED, AND REPLACED. NOTE: ALL REPORTED TIME IN THIS REPORT ARE IN MST
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170067 | 31129 | 2017-08-04 16:07 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2017-07-04 08:05 | 2017 |  |  | 36.7464 | -99.3659 | 1183136 | 2017-07-05 09:57 |  | NATURAL GAS |  | 8070 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-07-05 08:55 | 2017-07-11 09:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-07-05 08:05 | 2017-07-05 08:55 | ONSHORE | OK | 73842 | Not Within a Municipality | HARPER | MILEPOST | MP 42.57 | ANR FACILITIES WITHIN DCP LOVEDALE COMP STATION | A461 LINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | UNKNOWN |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 12 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 24000 | 21980.7692307692 | 3500 | 3722.72137828825 | 100 | 106.363467951093 | 0 | 0 |  |  | 27600 | 24546.1125203067 | 25809.8540770086 | [8 empty] | 885 |  | 1170 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | OTHER | DCP - OPERATOR OF THE LOVEDALE STATION |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [103 empty] | OTHER OUTSIDE FORCE DAMAGE | [9 empty] | AS A RESULT OF A STORM ON JULY 3, 2017, A FIBERGLASS TANK IN THE DCP FACILITY BLEW OFF ITS SUPPORT, TRAVELED APPROXIMATELY 50 YARDS, HITTING AND COMING TO REST ON THE ANR PRESSURE REGULATING EQUIPMENT. CAUSING THE SENSING LINE TO SEPARATE AND LEAK. | [251 empty] | JOHN CHIN | SR. REGULATORY COMPLIANCE SPECIALIST | john_chin@transcanada.com | 248-205-4522 | 248-205-4622 |  |  |  | JOHN CHIN | SR. REGULATORY COMPLIANCE SPECIALIST | 248-205-4522 | john_chin@transcanada.com | AT 0805 HOURS CT ON JULY 5, 2017 THE ANR FIELD OFFICE IN MOORELAND, OK OFFICE WAS NOTIFIED BY DCP THAT REGULATING EQUIPMENT IN THEIR LOVEDALE STATION WAS DAMAGED AND THAT GAS WAS VENTING FROM A .5 INCH SENSE LINE. ANR TECHNICIANS ARRIVED AT 0855, VERIFIED THE EQUIPMENT WAS ANR'S AND GAS WAS VENTING, THUS ESTABLISHING TIME OF CONFIRMED DISCOVERY. THE FAILED .5 INCH LINE WAS THEN ISOLATED AND THE EQUIPMENT WAS SHUT IN. IT APPEARS THE REGULATOR AND LINE WAS DAMAGED WHEN THE CUSTOMER'S FIBERGLASS TANK BLEW OVER DURING A STORM ON JULY 3, 2017 AND TRAVELED APPROX. 50 YARDS STRIKING AND COMING TO REST AGAINST ANR'S EQUIPMENT. NRC NOTIFICATION WAS MADE AT 0957 ON JULY 5. FACILITIES WERE REPAIRED AND RETURNED TO SERVICE ON JULY 11, 2017. BASED ON THE INFORMATION AVAILABLE, IT IS ESTIMATED THAT THE AMOUNT OF GAS VENTED REACHED THE 3MMCF THRESHOLD AT 0805 ON JULY 4, 2017
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170068 | 17409 | 2017-08-21 15:59 | ORIGINAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2017-07-27 14:02 | 2017 |  |  | 35.6726 | -99.2719 | 1185443 | 2017-07-27 14:24 |  | NATURAL GAS |  | 4455 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | BLOCK VALVE BELOW RELIEF WAS CLOSED FOR REPAIR. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-07-27 10:01 | 2017-07-27 10:01 | ONSHORE | OK | 73625 | MCCLURE | CUSTER | MILEPOST | RED MOON CS | RED MOON COMPRESSOR STATION | RED MOON COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2001 |  | CARBON STEEL |  | OTHER | [8 empty] | GAS RELEASE | CLASS 1 LOCATION | NO |  | 524 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 13540 | 12400.8173076923 | 250 | 265.908669877733 | 250 | 265.908669877733 | 0 | 0 |  |  | 14040 | 13100.6085765383 | 12932.6346474478 | [8 empty] | 980 |  | 1000 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL ROOM DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | FAILURE OF RELIEF TO RE SEAT. | [161 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | ON JULY 27, 2017 AT 08:53, ENABLE GAS TRANSMISSIONS SYSTEM CONTROL RECEIVED A CALL FROM THE GENERAL PUBLIC REPORTING GAS VENTING AT THE RED MOON COMPRESSOR STATION IN MCCLURE, OKLAHOMA. AN ENABLE O&M TECHNICIAN ARRIVED AT THE RED MOON COMPRESSOR STATION AT 10:01 AND FOUND THE THERMAL RELIEF (3/4 MERCER VALVE 9100 SERIES THREADED WITH A D ORIFICE) ON THE KING TOOL SUCTION FILTER SEPARATOR WAS VENTING. THE COMPRESSORS AT RED MOON ARE NOT IN ACTIVE SERVICE. THE O&M TECHNICIAN INSTALLED A GAUGE TO CHECK THE PRESSURE AT THE RELIEF, AND FOUND IT TO BE 911 PSIG. THE MAOP FOR THE RED MOON COMPRESSOR STATION IS 1000 PSIG. THE THERMAL RELIEF IS SET AT 1000 PSIG. AT 10:05 THE O&M TECHNICIAN SHUT IN THE BLOCK VALVE BELOW THE RELIEF AND OPENED IT BACK UP TO SEAT THE RELIEF VALVE. AT THIS POINT, THE RELIEF VALVE SEATED OFF AND APPEARED TO BE WORKING NORMALLY. THE FILTER SEPARATOR IS NOT UNDER SCADA CONTROL. AT 10:12, SYSTEM CONTROL WAS CONTACTED TO REPORT FINDINGS AND THAT GAS WAS NO LONGER VENTING. SYSTEM CONTROL NOTIFIED THE ENABLE ON-CALL TEAM AND THE TEAM DECIDED THAT FURTHER INVESTIGATION WAS NECESSARY BEFORE CONFIRMING THE RELEASE WAS REPORTABLE. OPERATIONS AND ENGINEERING REVIEWED THE AVAILABLE INFORMATION AND CONFIRMED THE TIMING OF THE EVENT AND ESTIMATED THE GAS LOSS TOTAL ON JULY 27TH AT 14:02. A CALL WAS PLACED TO THE NRC AT 14:22 ON THE 27TH (NRC #1185443) AND A FOLLOW-UP WAS PROVIDED ON THE 28TH (NRC # 1185526) AT 10:48. AFTER CONFIRMING WITH SYSTEM CONTROL THE LEAK HAD STOPPED, THE O&M TECH TESTED THE RELIEF VALVE AND FOUND IT TO START SEEPING AT AROUND 980 PSIG. THE RELIEF VALVE WAS INSTALLED IN 2001, AND HAS BEEN INSPECTED EVERY YEAR WITH THE STATION RELIEF VALVES. A DECISION WAS MADE TO REPLACE THE VALVE. A REPLACEMENT WAS ORDERED ON JULY 27TH AND INSTALLED ON AUGUST 1ST. UPON INSPECTION, THE MALFUNCTIONING RELIEF VALVE DID NOT SHOW SIGNS OF INTERNAL FAILURE. IT WAS DETERMINED THE VALVE PREMATURELY LIFTED AND CONTINUED TO MALFUNCTION UNTIL THE O&M TECH CORRECTED THE PROBLEM. USING SCADA TRENDS, THE START OF THE RELEASE STARTED AROUND 965 PSIG ON JULY 26 AT 05:30 AND DID NOT CEASE UNTIL THE O&M TECHNICIAN CLOSED THE BLOCK VALVE ON JULY 27TH 10:05. THE TOTAL RELEASE TIME WAS ESTIMATED TO BE 28 1/2 HOURS RESULTING IN A GAS LOSS ESTIMATE OF 4,455 MCF.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170069 | 17410 | 2017-08-21 17:29 | ORIGINAL FINAL | 15931 | PUBLIC SERVICE CO OF COLORADO | 1800 LARIMER STREET | DENVER | CO | 80202 | 2017-08-17 10:28 | 2017 |  |  | 37.4848 | -106.5327 | 1187585 | 2017-08-17 12:50 |  | NATURAL GAS |  | 2951 | 467 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-08-17 11:57 | 2017-08-17 22:44 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-08-17 10:30 | 2017-08-17 11:26 | ONSHORE | CO | 81132-0000 | DEL NORTE | RIO GRANDE | MILEPOST | 3714888 | 8" IGNACIO-DEL NORTE | 710010 | YES | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 18 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8.625 |  | 0.188 | 42000 | UNKNOWN | OTHER | UNKNOWN | UNKNOWN | COLD APPLIED TAPE | [28 empty] | 1961 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 2.5 | 2.5 | [7 empty] | CLASS 1 LOCATION | NO |  | 167 |  | NO | NO | NO |  | 0 | 0 | 1400 | 1489.0885513153 | 8850 | 8105.40865384615 | 90000 | 95727.1211559837 | 5000 | 5318.17339755465 | 0 | 0 |  |  | 105250 | 55469.2325950495 | 110639.7917587 | [8 empty] | 530 |  | 915 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 31153 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS PROPERLY IDENTIFIED ON SCADA BY THE CONTROLLER AND PROMPT ACTION TAKEN. | [12 empty] | NO |  |  | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [10 empty] | NO | [8 empty] | YES |  |  | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 722300282 |  | UTILITY OWNER | NO | YES | YES | 10 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO USE HAND TOOLS WHERE REQUIRED | [263 empty] | BRANDON JOHNSON | SR ENGINEER | brandon.r.johnson@xcelenergy.com | 303-571-6677 | 303-571-0000 |  |  |  | MARK NOLAN | PRINCIPAL ENGINEER | 303-5713931 | mark.nolan@xcelenergy.com | ON 8/17/17, A SECOND PARTY MECHANICAL CONTRACTOR STRUCK THE XCEL/PSCO 8IN IGNACIO TO DEL NORTE TRANSMISSION GAS LINE APPROXIMATELY 16 MILES SOUTHWEST OF DEL NORTE, COLORADO. WHILE EXCAVATING A TRENCH INTENDED FOR ELECTRICAL CONDUIT FOR A NEW REMOTE-CONTROLLED VALVE, THE EQUIPMENT OPERATOR STRUCK A 2IN T.D. WILLIAMSON THREAD-O-RING FITTING AT THE 12:00 POSITION ON THE 8IN PIPELINE. AS A RESULT OF THE IMPACT, THE 8IN PIPELINE FAILED, OPENING A 2.5IN DIAMETER HOLE IN THE TOP OF THE PIPE. THE INCIDENT LOCATION IS A REMOTE AREA WITHOUT CELLULAR PHONE SERVICE. THE INCIDENT WAS INITIALLY DISCOVERED BY THE GAS CONTROLLER ON DUTY BY WAY OF SCADA ALARMS AND WAS IMMEDIATELY REPORTED TO OPERATING PERSONNEL. THE DAMAGED PIPELINE SEGMENT WAS ISOLATED BY CLOSING THE MANUALLY OPERATED UPSTREAM AND DOWNSTREAM MAINLINE VALVES. UPON COMPLETION OF THE ELECTRICAL WORK, THE FINAL GRADE OF THE LOCATION WILL BE RAISED TO REACH A MINIMUM OF 36IN OF COVER. THE INITIAL NRC NUMBER IS #1187585 AND THE 48-HR FOLLOW UP NUMBER IS #1187701.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170070 | 17495 | 2017-08-23 09:38 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2017-07-24 11:45 | 2017 |  |  | 40.6903 | -81.6491 | 1185105 | 2017-07-24 17:08 |  | NATURAL GAS |  | 10453 | 81 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-07-25 21:25 | 2017-07-26 16:26 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-07-24 11:45 | 2017-07-24 11:45 | ONSHORE | OH | 44659 | Not Within a Municipality | STARK | SURVEY STATION NO. | 0+40 | V-243 | V-243-O-PIPELINE P/L ID: 10615 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 6 |  | 0.219 |  | UNKNOWN | SEAMLESS |  | UNKNOWN | COAL TAR | [28 empty] | 1967 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 60 |  | NO | NO | NO |  | 6560 | 6977.4434975917 | 234 | 248.890515005558 | 29999 | 27475.0456730769 | 38289 | 40725.508243794 | 6127 | 6516.88968136347 | 81248 | 86418.190440904 | COSTS FOR LDC AND CNG TRUCKS |  | 162457 | 93155.4423353023 | 168361.968051736 | [8 empty] | 112 |  | 210 | 192.619(A)(4) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL |  | NO | YES | YES | YES | YES | YES |  |  | YES |  | YES | YES |  | YES | CHANGES IN PIPE DIAMTER | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | YES | 4 | 0 | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | [204 empty] | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | [6 empty] | YES | THE BELOW GROUND 2" KICKER BRACE THAT WAS CONNECTED TO OLD 4" PIPELINE AND TO LINE V-243 (AN ACTIVE LINE) WAS NOT KNOWN. | CONSTRUCTION | NO | [150 empty] | MARK NEWMAN | COMPLIANCE SPECIALIST SENIOR ENGINEER | mark_newman@transcanada.com | 304-722-8475 | 304-722-8420 |  |  |  | LEE ROMACK | MANAGER | 832-320-5315 | lee_romack@transcanada.com | ON 7/24/17 A GAS RELEASE OCCURRED ON PIPELINE V-243 A TRANSMISSION CARBON STEEL 6" DIAMETER PIPELINE LOCATED IN STARK COUNTY, OHIO. LINE V-243 IS A SIDELINE CONNECTION TO LINE V. A COMPANY CONTRACTOR WAS REMOVING THE BRIDAL SETTING THAT GOES AROUND THE MAINLINE VALVE TO LINE V AND THE GAUNTER REGULATOR STATION (RS) 02345 TO REPLACE WITH A NEW PREFABRICATED BRIDAL SETTING. THE OLD 4" PIPELINE WAS HAND SPOTTED AND THEN EXCAVATED EXPOSING BOTH THE TOP AND SIDES OF THE PIPELINE GOING INTO THE M&R BUILDING. SINCE WORK WAS NOT SCHEDULED ON LINE V-243 THIS PIPELINE WAS NOT EXPOSED. LINE V-243 RUNS PARALLEL TO THE 4" DIAMETER PIPELINE THAT WAS EXPOSED AND WAS BEING REMOVED. THE PLAN WAS TO REMOVE THE 4" PIPELINE AND THEN FINISH EXCAVATING. THE 4" PIPELINE WAS BLOWN DOWN AND THE BOLTS FROM TWO 4" FLANGES WERE REMOVED. THE KICK BRACE THAT WENT TO THE MAINLINE VALVE KICK BRACE WAS CUT, AND THE 4" DIAMETER PIPE UP TO THE M&R BUILDING WAS COLD CUT. A SLING WAS CONNECTED TO THE BRIDAL SETTING TO LIFT UP THE OLD BRIDAL SETTING. WHILE LIFTING UP THE BRIDAL SETTING THERE WAS A RELEASE OF GAS PRESSURE. THE GAS RELEASE WAS COMING FROM THE 6" PIPELINE (V-243). AFTER A SHORT TIME, THE GAS BLOWING FROM LINE V-243 UNCOVERED A 2" KICK BRACE THAT WAS RUNNING FROM THE OLD 4" PIPELINE TO LINE V-243 WAS DISCOVERED ABOUT 24" BELOW GROUND. THE CONTRACTOR DID NOT COME INTO CONTACT WITH LINE V-243. LINE V-243 DEPTH OF COVER WAS 60 INCHES. ON7/25/26 CNG TRUCKS WERE CONNECTED TO LINE-243 TO MAINTAIN MARKET DELIVERABILITY WHILE LINE V-243 WAS ISOLATED TO MAKE REPAIRS. LINE V-243 WAS SHUT IN AND THE AREA MADE SAFE ON 7/25/17 AT 21:25. THREE FARM TAPS WERE TAKEN OUT-OF-SERVICE WHILE REPAIRS WERE MADE. REPAIRS CONSISTED OF REMOVING THE DAMAGE SECTION OF LINE V-243 AND REPLACING IT WITH A NEW PRE-TESTED 10.5 INCH PIPELINE IN LENGTH, 6" IN DIAMETER, 0.280 WALL, X-52 PIPE AND NEW 6" IN DIAMETER 90 DEGREE ELBOW, 0.280 WALL, GRADE B. LINE V-243 WAS RETURNED TO SERVICE ON 7/26/17 AT 16:26. THE 2" KICK BRACE THAT WAS CONNECT TO LINE V-243 FROM THE OLD 4" PIPELINE WAS REMOVED.
2021-02-26 10:37 | NO | NO | GG (Gas Gathering) | 20170071 | 17426 | 2017-08-23 10:41 | SUPPLEMENTAL FINAL | 32296 | TARGA RESOURCES OPERATING LLC | 811 LOUISIANA ST SUITE 2100 | HOUSTON | TX | 77002 | 2017-07-25 15:15 | 2017 |  |  | 29.5462 | -93.1995 | 1185211 | 2017-07-25 15:28 |  | NATURAL GAS |  | 300 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | PIPELINE SHUT DOWN PRIOR TO INCIDENT. NOT FLOWING. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-07-25 15:15 | 2017-07-26 20:00 | OFFSHORE | [28 empty] | 55 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | WEST CAMERON | 101 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12 |  | 0.375 | 52000 | API 5L | SEAMLESS |  | UNKNOWN | OTHER | CONCRETE | [27 empty] | 1970 | 1969 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 61 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 1000 | 915.865384615385 | 62000 | 65945.3501296777 | 0 | 0 | 0 | 0 |  |  | 63000 | 31220.1750292131 | 66861.215514293 | [8 empty] | 34 |  | 1240 | 192.619(A)(4) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 110544 | NO |  |  | YES |  |  |  |  | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | NO |  |  |  |  | OTHER | REPORT FROM 3RD PARTY. |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES | [5 empty] | YES | FIELD EXPERIENCE. | YES | [5 empty] | NO | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | TIM HUFFER | MANAGER REGULATORY COMPLIANCE | thuffer@targaresources.com | 3375835200 | 3375834630 |  |  |  | TIM HUFFER | MANAGER REGULATORY COMPLIANCE | 3375835200 | thuffer@targaresources.com | TARGA RECEIVED NOTIFICATION FROM A 3RD PARTY OF A LEAK NEAR THE LOCATION OF TARGA'S PIPELINE. INVESTIGATION BY TARGA CONFIRMED THE LEAK WAS FROM TARGA'S PIPELINE. PIPELINE LEAK WAS REPAIRED BY INSTALLATION OF A CLAMP COMPLETED ON 07/27/2017.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170072 | 17444 | 2017-08-28 11:36 | SUPPLEMENTAL FINAL | 19580 | TRANSCOLORADO GAS TRANSMISSION COMPANY LLC | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2017-07-28 19:11 | 2017 |  |  | 36.7351 | -107.9664 | 1185613 | 2017-07-29 08:12 |  | NATURAL GAS |  | 27410 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | VALVE WAS RESET AND OPERATIONS CONTINUED. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-07-29 07:11 | 2017-07-29 07:36 | ONSHORE | NM | 87413 | BLOOMFIELD | SAN JUAN | MILEPOST | BLANCO CS | TCGT BLANCO | BLANCO COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2007 |  | CARBON STEEL |  | OTHER | [8 empty] | GAS RELEASE THROUGH VENT VALVE | CLASS 3 LOCATION | YES | METHOD2 | 660 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 74967 | 68659.6802884615 | 0 | 0 | 300 | 319.090403853279 | 0 | 0 |  |  | 75267 | 71329.0790882307 | 68978.7706923148 | [8 empty] | 1137 |  | 1287 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | NO | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) | [11 empty] | YES | ISSUE WAS A RESULT OF A POWER LOSS DURING ELECTRICAL STORM AND FAULTY UPS BATTERY BANK. HMI FAILED TO RESTART AFTER POWER WAS RESTORED. | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | 2" STATION DISCHARGE VENT LINE VALVE | [11 empty] | YES | [173 empty] | ERIC GENTLES | PIPELINE ENGINEER II-COMPLIANCE | eric_gentles2@kindermorgan.com | 713-420-2389 |  |  |  |  | REJI GEORGE | DIRECTOR - COMPLAIANCE - CODES AND STANDARDS | 713-420-5433 | reji_george@kindermorgan.com | BASED ON STATION PRESSURE AND FLOW TRENDS IT HAS BEEN DETERMINED THE 2" STATION DISCHARGE VENT VALVE MOST LIKELY OPENED DURING A POWER OUTAGE OCCURRING AT 7:23 PM ON 7/28/2017. ON SATURDAY MORNING 07/29/2017 A COMPANY EMPLOYEE WAS DRIVING BY THE TCGT BLANCO COMPRESSOR STATION ON HIS REGULAR DAY OFF. THE EMPLOYEE NOTICED WHAT LOOKED LIKE GAS VAPOR VENTING FROM THE STATION BLOWDOWN SILENCER. THE EMPLOYEE DROVE UP TO THE STATION AND VERIFIED GAS WAS VENTING FROM THE BLOWDOWN SILENCER. EMPLOYEE CALLED OPERATIONS MANAGER AT 7:11 AM LOCAL TIME TO REPORT THE ISSUE. OPERATIONS MANAGER CALLED OUT LOCAL E&C TECHNICIAN TO RESPOND TO THE FACILITY. E&C TECHNICIAN ARRIVED ON SITE AT 7:36 AM LOCAL TIME AND DISCOVERED 2" STATION DISCHARGE VENT VALVE WAS OPEN. DISCHARGE VENT VALVE CLOSED AT 7:37 AND STOPPED VENTING OF GAS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170073 | 30522 | 2017-08-29 13:31 | SUPPLEMENTAL FINAL | 32005 | ENLINK LIG, LLC | 1722 ROUTH STREET SUITE 1300 | DALLAS | TX | 75201 | 2017-07-31 23:22 | 2017 |  |  | 31.8492 | -93.0767 | 1185859 | 2017-08-01 01:52 |  | NATURAL GAS |  | 333 | 106 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-07-31 23:22 | 2017-08-12 17:05 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2017-07-31 23:38 | 2017-08-01 | ONSHORE | LA | 71411 | Not Within a Municipality | NATCHITOCHES PARISH | MILEPOST | MP53.7 (APP) | P1656/RED RIVER 24" | RED RIVER COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2009 |  | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 291 |  | NO | NO | NO |  | 0 | 0 | 309 | 328.663115968877 | 1000 | 915.865384615385 | 500000 | 531817.339755465 | 2000 | 2127.26935902186 | 1800 | 1914.54242311967 | FIRE DEPARTMENT |  | 505109 | 247073.874454926 | 537103.680038191 | [8 empty] | 979 |  | 1100 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  | YES | THE INCIDENT WAS CAUSED BY EQUIPMENT FAILURE. THE ONLY ALARM RECEIVED ON SCADA WAS THE SHUTDOWN OF THE COMPRESSOR. THERE WAS NO TYPE OF ALARM TO IDENTIFY A LEAK ON THE EQUIPMENT OR FIRE. THE CONTROLLER DID ACKNOWLEDGE THE ALARM AND CONTACTED THE ON-CALL OPERATIONS PERSONNEL TO INVESTIGATE THE CAUSE OF THE SHUTDOWN. | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | SEAL FAILURE | [6 empty] | YES | [177 empty] | CORDELL THERIOT | SR. DOT COMPLIANCE SPECIALIST | cordell.theriot@enlink.com | 337-937-3371 | 337-937-8524 |  |  |  | CORDELL THERIOT | SR. DOT COMPLIANCE SPECIALIST | 337-937-3371 | cordell.theriot@enlink.com | PIPELINE CONTROL NOTIFIED ENLINK OPERATOR THAT BOTH UNITS AT RED RIVER COMPRESSOR STATION WERE OFFLINE ON MONDAY 7/31/2017 AT 11:22 PM. AT 11:38 PM PIPELINE CONTROL RECEIVED NOTIFICATION FROM THE NATCHITOCHES SHERIFF AND FIRE DEPARTMENT OF A FIRE AT THE RED RIVER COMPRESSOR STATION. PIPELINE CONTROL NOTIFIED ENLINK OPERATOR OF FIRE AND ESD'D THE STATION AT 11:43 PM. ENLINK OPERATOR ARRIVED AT RED RIVER COMPRESSOR STATION AT 12:00 MIDNIGHT AND LED FIRE DEPARTMENT INTO STATION TO PUT OUT REMAINING OIL FIRE. OPERATOR CLOSED DAY TANK OIL VALVE TO STOP FLOW OF OIL TO COMPRESSOR AND THE FIRE. THE FIRE WAS OUT AT 12:41 AM 8/1/2017. 48-HOUR FOLLOW-UP NOTIFICATION WAS MADE ON 8/2/2017 @ 09:52. NRC INCIDENT # 1186003
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170074 | 17430 | 2017-08-29 14:00 | SUPPLEMENTAL FINAL | 26330 | ENABLE OKLAHOMA INTRASTATE TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2017-08-06 18:00 | 2017 |  |  | 36.2826 | -95.6616 | 1186432 | 2017-08-06 22:50 |  | NATURAL GAS |  | 6400 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-08-06 21:15 | 2017-08-06 22:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-08-06 20:30 | 2017-08-06 21:05 | ONSHORE | OK | 74019 | CLAREMORE | ROGERS | MILEPOST | CLAREMORE CS | CLAREMORE COMPRESSOR STATION | CLAREMORE COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | TUBING | [38 empty] | 2015 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO | NO |  | 0 | 0 | 20 | 21.2726935902186 | 13000 | 11906.25 | 558 | 593.508151167099 | 250 | 265.908669877733 | 0 | 0 |  |  | 13828 | 12748.0097258244 | 12786.9395146351 | [8 empty] | 550 |  | 1014 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL ROOM DID NOT CONTRIBUTE TO THE INCIDENT | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | THREADED FITTING |  |  |  |  | YES | [177 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | AT 20:30 ON 8/6/17 THE ENABLE OKLAHOMA INTRASTATE TRANSMISSION (EOIT) SYSTEM CONTROL RECEIVED A CALL ABOUT AN ODOR OF GAS AT THE CLAREMORE COMPRESSOR STATION IN CLAREMORE, OKLAHOMA. WHEN THE EOIT O&M TECHNICIAN ARRIVED AT THE STATION, HE PERFORMED A COMPLETE INSPECTION AND FOUND A RELIEF VALVE BLOWING ON COMPRESSOR UNIT 433. IT WAS DISCOVERED A 1/4" TUBING FITTING FAILED ON THE PILOT OF THE UNIT 433 DISCHARGE VALVE CAUSING THE RELIEF TO VENT. THE UNIT WAS ISOLATED AND ULTIMATELY SHUT DOWN FOR REPAIR. WHEN IT WAS SAFE TO DO SO, THE AMOUNT AND DURATION OF GAS LOSS WAS CALCULATED TO BE A LITTLE OVER 3 HOURS AND ESTIMATED AT 6,400 MCF. THESE TOTALS WERE CONFIRMED AT 22:18 AND A CALL WAS PLACED TO NRC AT 22:50 (NRC#1186432). A FOLLOW UP CALL WAS PLACED WITH THE NRC ON 8/8/17 AT 07:04 (NRC#1186560). IT WAS DETERMINED THE FITTING FAILURE OCCURRED DUE TO UNIT VIBRATION. THE FAILED FITTING AND TUBING WAS REPLACED BY A 2000 PSIG STAINLESS STEEL HOSE. THIS REPAIR WAS PERFORMED FOR ALL THREE UNITS AT THE COMPRESSOR STATION. AS A SECONDARY PROTECTION, THE COMPRESSOR LOGIC WAS MODIFIED TO SHUT DOWN WHEN UNIT PRESSURE DROPS MORE THAN 1 PSIG IN A 1/3 OF A SECOND. WHILE REOCCURRENCE OF THIS INCIDENT IS NOT EXPECTED TO OCCUR, THE UPDATED LOGIC WILL ALMOST IMMEDIATELY SHUT THE UNIT DOWN, GREATLY REDUCING THE AMOUNT OF GAS RELIEVED INTO THE ATMOSPHERE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170075 | 31282 | 2017-08-30 08:34 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2017-08-03 15:11 | 2017 |  |  | 29.3099 | -90.3976 | 1186485 | 2017-08-07 12:18 |  | NATURAL GAS |  | 24 | 1365 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-08-07 08:43 | 2018-08-24 14:50 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-08-03 15:11 | 2017-08-03 17:00 | ONSHORE | LA | 70377 | Not Within a Municipality | TERREBONNE PARISH | MILEPOST | 679+38 | INDEX 295 | 12" RACCOURCI | YES | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | MOUTH OF BAYOU JEAN LACROIX | 1 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 12 |  | 0.281 | 46000 | API 5L | SEAMLESS |  | NATIONAL TUBE | OTHER | SOMASTIC & CONCRETE | [8 empty] | PIPE GIRTH WELD | [18 empty] | 1952 | 1952 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 262 |  | NO | NO | NO |  | 0 | 0 | 4131 | 4393.87486105965 | 73 | 66.8581730769231 | 418000 | 444599.296035569 | 36900 | 39248.1196739533 | 0 | 0 |  |  | 459104 | 224184.950416999 | 488308.148743659 | [8 empty] | 716 |  | 1440 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 99905 | YES | [7 empty] | YES |  |  | YES |  | YES | MLV IS CLOSED, DIVERTING FLOW | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [7 empty] | YES | [14 empty] | YES | [63 empty] | NO | [63 empty] | YES | 1970 | 1600 | NO | [13 empty] | NO | [63 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | DARRAL WARD | MANAGER PIPELINE SAFETY | 2706886356 | darral.ward@bwpmlp.com | ON AUGUST 3, 2017, GULF SOUTH PIPELINE, LP RECEIVED A REPORT OF AN UNDERWATER LEAK (17-FEET DEEP) WITH A SMALL AREA OF BUBBLING. GULF SOUTH RESPONDED, FLAGGED THE AREA, BEGAN TO ORGANIZE A DIVE CREW AND OBTAIN A LEAK CLAMP TO SECURE A POTENTIAL LEAK. WEATHER DELAYED THE ABILITY TO MOBILIZE. THE DIVE CREW BEGAN JETTING THE LEAK AREA ON AUGUST 7, 2017 AND DISCOVERED A LEAK IN WELDS AT TWO SITES. THE LINE WAS ALSO EXPOSED AND PARTIALLY SUSPENDED SO THE DETERMINATION WAS MADE TO BEGIN TO LOWER THE PRESSURE FOR FURTHER INVESTIGATION. DISCOVERY OF AN INCIDENT OCCURRED AT THIS POINT. ONCE WE DISCOVERED THAT WE HAD LEAKS IN TWO WELDS, IT WAS RECOGNIZED THAT A SIGNIFICANT EXPENDITURE WOULD BE NECESSARY TO CORRECT THE ISSUE, THUS, IT WAS DETERMINED THAT AN INCIDENT HAD OCCURRED. SUSPECTED CAUSE OF WELD FAILURE IS EXCESSIVE STRESSES PLACED ON THE WELDS DUE TO THE PIPE NOT BEING FULLY SUPPORTED. A SUPPLEMENTAL REPORT WILL BE FILED ONCE COMPLETE ROOT CAUSE IS IDENTIFIED. 9-14-18 REVISED TO SUBMIT SUPPLEMENTAL REPORT; BECAUSE COSTS ARE ESTIMATES ONLY AT THIS POINT, A FINAL REPORT WILL BE REQUIRED. THE TIME SHOWN IN PART A, 15B REPRESENTS THE TIME ABANDONMENT WAS COMPLETE. GULF SOUTH ISOLATED ALL LATERALS FROM INDEX 295, INSTALLED A SUB-SEA PLIDCO FLANGE AND BLIND, PIGGED LINE SEGMENT AND FILLED WITH WATER. GULF SOUTH INTENDS TO FILE FOR FERC ABANDONMENT IN 2019. 12-6-18 GULF SOUTH HAS ABANDONED THIS PORTION OF ITS INDEX 295. UPDATED COSTS TO SUBMIT FINAL REPORT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170076 | 17550 | 2017-09-06 08:17 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2017-08-12 11:00 | 2017 |  |  | 37.5885 | -81.0921 | 1187079 | 2017-08-13 12:03 |  | NATURAL GAS |  | 61800 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-08-13 10:15 | 2017-08-13 11:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-08-13 10:00 | 2017-08-13 09:40 | ONSHORE | WV | 25841 | FLAT TOP | SUMMERS | MILEPOST | BLOWDOWN VLV | FLAT TOP COMPRESSOR STATION | LINE KA AND LINE KA-LOOP | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1998 |  | CARBON STEEL |  | OTHER | [8 empty] | PARTIAL CLOSURE OF A COMPRESSOR STATION UNIT'S 20 INCH BALL VALVE, RESULTING IN NATURAL GAS EXITING THROUGH A 3 INCH BLOW-OFF VALVE TO ATMOSPHERE | CLASS 2 LOCATION | NO |  | 521 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 171804 | 157349.336538462 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 171804 | 163131.201923077 | 157349.336538462 | [8 empty] | 770 |  | 1000 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE BALL VALVE PARTIAL CLOSURE WAS NOT DUE TO ANY INVOLVEMENTS BY GAS CONTROL PERSONNEL | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | WRONG EQUIPMENT SPECIFIED OR INSTALLED | INCORRECT OPERATION | INCORRECT EQUIPMENT | [204 empty] | WRONG EQUIPMENT SPECIFIED OR INSTALLED | [6 empty] | YES | VALVE OPERATOR DID NOT HAVE SUFFICIENT TORQUE TO RELIABLE CLOSE THE 20 INCH BALL VALVE. THIS VALVE CLOSES WHEN COMPRESSOR UNIT IS TAKEN OFF LINE/SHUTDOWN. | NORMAL OPERATING CONDITIONS | NO | [150 empty] | MARK NEWMAN | COMPLIANCE SPECIALIST - U.S. REGULATORY COMPLIANCE | mark_newman@transcanada.com | (304) 722-8475 | (304) 722-8420 |  |  |  | HOWARD ROMACK | MANAGER - U.S. REGULATORY COMPLIANCE | (832) 320-5315 | lee_romack@transcanada.com | ON AUGUST 12TH, 2017, FLAT TOP COMPRESSOR STATION (CS) WAS SUBJECT TO AN UNINTENTIONAL RELEASE OF NATURAL GAS (MATERIAL) RESULTING IN GAS LOSS OF MORE THAN 3,000 MCF. FLAT TOP IS A TRANSMISSION CS THAT IS MAINTAINED BY COLUMBIA GAS TRANSMISSION, LLC (TRANSCANADA). FLAT TOP CS IS LOCATED IN SUMMERS COUNTY, NEAR THE TOWN OF FLAT TOP, WEST VIRGINIA. AFTER THE REMOTE SHUTDOWN OF CS UNIT 3, MATERIAL PASSED THROUGH A SMALL OPENING OF A 20 INCH BALL VALVE. SUBSEQUENTLY, MATERIAL EXITED A 3 INCH BLOWDOWN STACK TO ATMOSPHERE BEGINNING ON AUGUST 12TH, 2017 AT APPROXIMATELY 11:00 ET. THE PRESSURE IN THE CS UNIT'S PIPING SLOWLY DECREASED FROM 770 PSIG UNTIL APPROXIMATELY 22:00 EST ON AUGUST 12TH, 2017. AT THIS TIME, THE PRESSURE STABILIZED AT 560 PSIG UNTIL THE LEAK WAS ISOLATED. AT APPROXIMATELY 09:00 EST ON AUGUST 13TH, 2017, A PASSERBY REPORTED TO TRANSCANADA THAT IT APPEARED THAT MATERIAL WAS VENTING THROUGH A BLOW-OFF VALVE AT FLAT TOP CS. IMMEDIATELY AFTER THIS WAS REPORTED, OPERATIONS PERSONNEL WERE DISPATCHED TO INVESTIGATE THE SITUATION. ON AUGUST 13TH, 2017, OPERATIONS PERSONNEL ARRIVED ON-SITE AT APPROXIMATELY 09:40 EST, THE UNINTENDED RELEASE OF MATERIAL WAS IDENTIFIED AND ISOLATED AT APPROXIMATELY 10:15 EST. ONCE OPERATIONS PERSONNEL HAD ISOLATED THE LEAK AND MADE THE AREA SAFE, GAS CONTROL WAS NOTIFIED AND IMMEDIATELY CONTACTED TRANSCANADA'S ON-CALL SPECIALIST AT 11:05 AM ON AUGUST 13TH. AFTER TRANSCANADA'S ON-CALL SPECIALIST HAD BEEN NOTIFIED, AND GAS LOSS CALCULATIONS WERE DETERMINED TO BE GREATER THAN 3,000 MCF, THE EVENT WAS REPORTED TO THE NATIONAL RESPONSE CENTER. BEFORE RETURNING THE UNIT BACK TO SERVICE, THE FAULTY VALVE WAS MANUALLY CYCLED FROM THE STATION PANEL AND FULL CLOSURE WAS ACHIEVED. THE OPERATOR THEN CYCLED THE VALVE ONCE MORE TO ENSURE PROPER FUNCTIONALITY. NO ISSUES WERE DISCOVERED ON THE FOLLOW UP INVESTIGATION. A RCA DISCOVERED A REPLACED VALVE ACTUATOR DID NOT HAVE THE REQUIRED TORQUE TO CLOSE A A 20" BALL VALVE. A NEW ACTUATOR WILL BE INSTALLED IN 2018. UNTIL A NEW ACTUATOR IS INSTALLED, SCADA WARNING TAGS WILL BE USED TO ALERT GAS CONTROL AN EMPLOYEE WILL NEED TO BE PRESENT TO OBSERVE THE VALVE CLOSURE WHEN UNIT 3 IS SHUTDOWN.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170077 | 17535 | 2017-09-11 19:19 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2017-08-14 14:03 | 2017 |  |  | 41.2445 | -74.646 | 1187184 | 2017-08-14 15:34 |  | NATURAL GAS |  | 2363 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-08-14 14:03 | 2017-08-20 16:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-08-14 14:20 | 2017-08-14 14:20 | ONSHORE | NJ | 07461 | SUSSEX | SUSSEX | MILEPOST | 325-1+0.00 | LIBERTYVILLE CS 325 | LINE 300-1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | ESD PIPING COMPONENTS | 1986 |  | CARBON STEEL |  | OTHER | [8 empty] | VENT VALVE COMPONENT FAILURE | CLASS 2 LOCATION | YES | METHOD2 | 204 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 6882 | 6302.98557692308 | 165000 | 175499.722119303 | 0 | 0 | 0 | 0 |  |  | 171882 | 87093.5946807222 | 181802.707696227 | [8 empty] | 1163 |  | 1170 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL ROOM ACTIONS WERE NOT A CAUSATIVE FACTOR | [12 empty] | YES | 4 | 0 | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | THREADED FITTING | [9 empty] | YES | [172 empty] | KRISTIN VAN DER LAAN | SENIOR PIPELINE ENGINEER | kristin_vanderlaan@kindermorgan.com | [5 empty] | REJI GEORGE | DIRECTOR - COMPLIANCE - CODES AND STANDARDS | 713-420-5433 | reji_george@kindermorgan.com | AUGUST 14, 2017: (2:03PM) TENNESSEE GAS PIPELINE (TGP) STATION 325 BUILDING A ESD SYSTEM WAS ACCIDENTALLY TRIGGERED WHILE LOCAL OPERATIONS PERSONNEL WERE PERFORMING WORK ON THE STATION. (2:05PM) TGP GAS CONTROL RECEIVED NOTIFICATION FROM LOCAL OPERATIONS THAT AN ESD HAD BEEN ACCIDENTALLY TRIGGERED . LOCAL OPERATIONS ON-SITE VERIFIED THE STATION ESD, ONCE INITIATED, ISOLATED THE STATION FROM THE MAINLINE AND EVACUATED THE GAS FROM THE STATION PIPING. (2:20PM) DURING THE INITIAL ESD INVESTIGATION, VENT PIPING TO THE SILENCER WAS FOUND DISCONNECTED FROM THE SILENCER PIPING AND IT WAS DETERMINED THAT THERE HAD BEEN A VENT PIPING COMPONENT FAILURE. (3:05PM) EMERGENCY RESPONSE LINE (ERL) CALL HELD WITH TGP CORPORATE AND LOCAL RESPONSE PERSONNEL. (3:30PM) DETERMINED REPORTABLE INCIDENT - REPAIR COSTS WERE ESTIMATED TO BE NEAR OR ABOVE $50,000 THEREFORE MEETING THE PHMSA 49CFR 191 REPORTING CRITERIA. (3:34PM) THE NRC AND (3:42PM) PHMSA WERE NOTIFIED OF THE REPORTABLE INCIDENT. POST-INCIDENT: SUBSEQUENT INVESTIGATION DETERMINED THAT AFTER THE 2017 ANNUAL STATION ESD TESTING THE PIPING COMPONENTS FROM THE ESD DISCHARGE OPERATOR TO THE STATION SILENCER WERE RECONNECTED IMPROPERLY. THERE WERE ALIGNMENT CONNECTION ISSUES WITH THE "HUBER-YALE" HAMMER UNION CONNECTIONS. CORRECTIVE ACTIONS INCLUDE UPDATING PROCEDURES FOR TESTING THE CURRENT ESD SYSTEM, AND REMOVING THE 8" HAMMER FITTINGS AND PIPE ASSEMBLY AND REPLACING THEM WITH A NEW PIPE ASSEMBLY AND VALVE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170078 | 17448 | 2017-09-18 14:18 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2017-03-20 12:20 | 2017 |  |  | 46.4959 | -88.7309 | NRC NOTIFICATION REQUIRED BUT NOT MADE |  |  | NATURAL GAS |  | 10 | 10000 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | A DOUBLE STOPPLE AND BYPASS WAS USED TO CONTINUE SERVICE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-03-20 12:20 | 2017-03-22 11:00 | ONSHORE | MI | 49961 | Not Within a Municipality | HOUGHTON | MILEPOST | 63.52 | WAKEFIELD TO MARQUETTE MAIN | MIM10101-M433B | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 16 |  | 0.203 | 60000 | 5LX | LONGITUDINAL ERW - LOW FREQUENCY |  | YOUNGSTOWN | COLD APPLIED TAPE | [9 empty] | PIPE GIRTH WELD | [18 empty] | 1965 | 1965 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 339 |  | NO | NO | NO |  | 2500 | 2659.08669877733 | 57 | 60.627176732123 | 3 | 2.74759615384615 | 997500 | 1060975.59281215 | 0 | 0 | 0 | 0 | MATTING, STOPPLE, PIPE CYLINDER, RESTORATION |  | 1000060 | 488267.061877441 | 1063698.05428382 | [8 empty] | 870 |  | 945 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 200 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | AIR PATROL |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE 111 PARTS PER MILLION LEAK DETECTED BY LIDAR IS TOO SMALL TO REGISTER ON ANY SCADA INSTRUMENTS. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES | [6 empty] | YES | [14 empty] | YES | [63 empty] | YES | YES | [6 empty] | 2014 | [55 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | JOHN A GORMLEY | SR. CORROSION SPECIALIST | john.gormley@nngco.com | 402-398-7494 |  |  |  |  | THOMAS CORRELL | VP PIPELINE SAFETY AND RISK | 402-398-7715 | thomas.correll@nngco.com | ON MARCH 20, 2017, DURING A LIDAR GAS LEAK SURVEY OF THE MARQUETTE MAINLINE (MIM10101-M433B) A VERY LOW LEVEL, 111 PART PER MILLION LEAK WAS DISCOVERED NEAR MP 62.53. THE AREA IS REMOTE, WOODED AND CLASS 1 WITH NO NEARBY ROADS OR STRUCTURES. THE LEAK CAUSE WAS FOUND TO BE A MINOR CRACK IN A GIRTH WELD. ALTHOUGH THE REPAIR COULD HAVE BEEN COMPLETED WITH A LEAK CLAMP OR SLEEVE, NORTHERN ELECTED TO CUT OUT THE GIRTH WELD AND SUBMIT IT FOR FURTHER ROOT CAUSE ANALYSIS AS A PREVENTIVE AND MITIGATIVE MEASURE. THIS ADDITIONAL WORK DROVE THE COST OVER THE $50,000 REPORTING LIMIT. THIS LEAK WAS CONSIDERED A GRADE 3 LEAK (IN ACCORDANCE WITH GPTC GUIDE MATERIAL FOR THE CLASSIFICATION OF LEAKS, WHICH ARE CONSIDERED NON-HAZARDOUS AND EXPECTED TO REMAIN SO AND COULD HAVE BEEN LEFT TO ON-GOING MONITORING) SO NO NRC REPORT WAS MADE AND THE REPAIR WAS NEVER HANDLED BY THE COMPANY AS ANYTHING BUT ROUTINE. NORTHERN IS SUBMITTING THIS REPORT ON THE RECOMMENDATION OF THE PHMSA ACCIDENT INVESTIGATION DIVISION. NORTHERN DISAGREES THAT THIS LEAK CONSTITUTED AN INCIDENT SINCE IT WAS A GRADE 3 LEAK. THE LEAK WAS FOUND BY A HELICOPTER BASED INSTRUMENT USING LIGHT DETECTION AND RANGING (LIDAR) TECHNOLOGY. THIS SURVEY IS A PREVENTIVE AND MITIGATING MEASURE NORTHERN CONDUCTS WHICH IS BEYOND PIPELINE SAFETY REGULATORY REQUIREMENTS. IT IS VERY ACCURATE AND CAN LOCATE LEAKS MUCH SMALLER THAN COULD BE DETECTED BY HAND-HELD INSTRUMENTS OR EMPLOYEE SURVEYS. IN THIS CASE, THE LEAK WAS SIZED AT 111 PARTS PER MILLION. NORTHERN REPAIRS ALL LEAKS, REGARDLESS OF CLASSIFICATION, SO FOLLOWING CONFIRMATION, A REPAIR PROJECT WAS IMPLEMENTED. NORTHERN HAD OTHER OPTIONS TO REPAIR THE LEAK INCLUDING RELATIVELY LOW COST INSTALLATION OF A LEAK CLAMP OR SLEEVE TO A MORE COSTLY CUT OUT AND REPAIR OPTION. NORTHERN CHOSE THE CUT OUT AND REPLACE OPTION BECAUSE ALTHOUGH MORE COSTLY, IT WOULD ALLOW THE COMPANY TO SEND THE GIRTH WELD TO A METALLURGICAL LABORATORY FOR FAILURE ANALYSIS. THIS INFORMATION IS THEN USED TO PREVENT OCCURRENCE OF A SIMILAR INCIDENT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170079 | 17453 | 2017-09-19 20:29 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2017-08-22 12:12 | 2017 |  |  | 36.7396 | -121.7393 | 1188088 | 2017-08-22 14:47 |  | NATURAL GAS |  | 6.1 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-08-22 13:16 | 2017-08-24 19:43 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-08-22 12:12 | 2017-08-22 13:16 | ONSHORE | CA | 93907 | SALINAS | MONTEREY | MILEPOST | 1.16 | L301F | MP 1.16 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.375 | 33000 | GRADE B | OTHER | AO SMITH SMAW ARC WELD (TYPE 1) | AO SMOTH | ASPHALT | [28 empty] | 1966 | 1929 | CARBON STEEL |  | MECHANICAL PUNCTURE | 15 | 3 | [7 empty] | CLASS 1 LOCATION | NO |  | 223 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 18432 | 16881.2307692308 | 54948 | 58444.5983697666 | 6146 | 6537.09874027418 | 0 | 0 |  |  | 79526 | 47329.852096218 | 81862.9278792715 | [8 empty] | 388 |  | 412 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 17794 | NO | [5 empty] | YES | SCHEDULED FOR 2020-2023 | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS CAUSED BY A CONFIRMED 3RD PARTY DIG-IN. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  | YES | PRIVATE LANDOWNER | [7 empty] | CONTRACTOR | FARM EQUIPMENT | AGRICULTURE | NO | [5 empty] | YES | 54 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | ENZA BARBATO | REGULATORY COMPLIANCE SENIOR PROGRAM MANAGER | e1bo@pge.com | 925-357-7889 |  |  |  |  | SUSIE RICHMOND | REGULATORY COMPLIANCE MANAGER | 925-786-0267 | gsr8@pge.com | ON AUGUST, 22, 2017, AT 1212 HOURS, PG&E WAS NOTIFIED OF A THIRD PARTY DIG-IN AT 1687 HWY 183, SALINAS. PG&E CREWS ARRIVED ON-SITE AND STOPPED THE FLOW OF GAS AT 1316 HOURS. THE PROPERTY AT THE DAMAGE SITE WAS LEASED BY THE 3RD PARTY EXCAVATOR FOR AGRICULTURAL PURPOSES. THEY WERE OPERATING A TRACTOR WITH A RIPPER FARMING IMPLEMENT THAT HIT A 16" TRANSMISSION LINE (LINE 301F MP 1.16). A USA TICKET NUMBER WAS NOT PROVIDED. THERE WAS 1 AFFECTED CUSTOMER. SERVICE TO THE CUSTOMER WAS RESTORED ON 8/24/17 AT 1943 HOURS. THERE WERE NO INJURIES, FATALITIES OR IGNITION REPORTED. THERE WAS NO MEDIA OR POLICE REPORTED ON SITE. THE FIRE DEPARTMENT WAS REPORTED ON SITE. AT 1447 HOURS THIS INCIDENT WAS REPORTED TO THE DOT (1188088) AND CPUC (170822-8472) DUE TO DAMAGES THAT ARE ESTIMATED TO EXCEED $50K.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170080 | 17614 | 2017-09-21 16:27 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2017-08-27 09:22 | 2017 |  |  | 28.7 | -96.9436 | 1188501 | 2017-08-27 10:17 |  | NATURAL GAS |  | 17810.566 | 18498.816 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE SYSTEM WAS SHUT DOWN IN PREPARATION FOR THE HARVEY HURRICANE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-08-27 09:22 | 2017-08-27 10:00 | ONSHORE | TX | 77905 | VICTORIA | VICTORIA | MILEPOST | COMPRESSOR | TENNESSEE GAS PIPELINE | COMPRESSOR STATION 9 | YES | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | OTHER | COMPRESSOR STATION |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2015 |  | CARBON STEEL |  | OTHER | [8 empty] | THE SYSTEM ESD BUT A BY-PASS VALVE WAS LEFT OPEN WHICH RELEASED GAS. | CLASS 1 LOCATION | NO |  | 1035 |  | NO | NO | NO |  | 0 | 0 | 55285 | 58803.0432567618 | 53229 | 48750.5985576923 | 0 | 0 | 400 | 425.453871804372 | 0 | 0 |  |  | 108914 | 77729.4021690726 | 107979.095686258 | [8 empty] | 741 |  | 750 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | SHERIFF DEPARTMENT REPORTED IT |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [204 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | [5 empty] | YES |  |  | ROUTINE MAINTENANCE | NO | [150 empty] | KRITI BHAYANI | PIPELINE ENGINEER - COMPLIANCE-CODES AND STANDARDS | kriti_bhayani@kindermorgan.com | 7134206633 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR OF COMPLIANCE-CODES AND STANDARDS | 7133699443 | jaime_ernandez@kindermorgan.com | ON 8/24/2017, AT 2:00PM TENNESSEE GAS PIPELINE COMPANY(TGP) COMPRESSOR STATION 9 WAS SHUT DOWN AND PLACED IN BY-PASS MODE AS A PRECAUTIONARY MEASURE DUE TO HURRICANE HARVEY. THE MAINLINE AT THIS STATION WAS STILL FREE FLOWING NATURAL GAS. ON 8/27/17 AT APPROXIMATELY 9:22AM, DUE TO A POWER LOSS EVENT ASSOCIATED WITH HURRICANE HARVEY, TGP'S COMPRESSOR STATION 9 VICTORIA EXPERIENCED AN EMERGENCY SHUT DOWN(ESD) WHICH CAUSED AN ESD VALVE TO OPEN AND RELEASE NATURAL GAS TO ATMOSPHERE. THE LOCAL SHERIFF'S OFFICE CONTACTED TGP GAS CONTROL AT 9:22 AM AND INFORMED THEM OF THE GAS RELEASE EVENT. AT 9:25AM TWO ELECTRONICS AND COMMUNICATION TECHNICIANS WERE CALLED OUT AND THEY ARRIVED ON SITE AT 9:39 AM. THE TECHNICIANS DETERMINED THERE WAS NO ISSUE WITH THE STATION PRESSURE AND IT WAS FOUND TO BE BELOW MAOP THEREFORE IN CONSULTATION WITH THE AREA MANAGER IT WAS DECIDED TO CLOSE THE BLOW OFF VALVE #9-B2D. THE TECHNICIANS WALKED THE ESD SYSTEM CHECKING THE VALVES FOR PROPER POSITION ACCORDING TO THE PROCEDURE. IT WAS DETERMINED THAT A BY-PASS VALVE AROUND THE ESD VALVE #9-BD5 WAS OPEN WHICH ALLOWED THE REPORTED 17,811 MCF RELEASE OF NATURAL GAS TO THE ATMOSPHERE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170081 | 31071 | 2017-09-22 14:22 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2017-08-24 13:27 | 2017 |  |  | 42.7185 | -82.7185 | 1188430 | 2017-08-26 11:45 |  | NATURAL GAS |  | 1417 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-08-24 13:30 | 2017-10-13 07:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2017-08-24 13:27 | 2017-08-24 13:27 | ONSHORE | MI | 48023 | IRA TOWNSHIP | ST. CLAIR | SURVEY STATION NO. | 0+00 | ST. CLAIR COMPRESSOR STATION PLANT 3 | PLANT 3 - BLOW DOWN SILENCER | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | DRAIN LINES | [38 empty] | 2015 |  | CARBON STEEL |  | OTHER | [8 empty] | COMPRESSOR STATION ENGINE BLOW-DOWN SILENCER IGNITED | CLASS 3 LOCATION | YES | METHOD2 | 666 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 4324 | 3960.20192307692 | 332430 | 353584.076509818 | 0 | 0 | 97000 | 103172.56391256 | THIRD PARTY SME ENVIRONMENTAL CLEAN-UP |  | 433754 | 213769.071468778 | 460716.842345456 | [8 empty] | 1060 |  | 1440 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS IMMEDIATELY IDENTIFIED BY ON-SITE PERSONNEL AND THE APPROPRIATE ACTIONS WERE TAKEN TO PROTECT LIFE AND PROPERTY | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | WEATHER CAPS WERE NOT SELECTED FOR THE DESIGN. UNAWARE OF THE POTENTIAL RISK OF WATER ACCUMULATION IN THE BOWL OF THE SILENCER. |  |  |  | YES | WEATHER CAPS WERE NOT SELECTED FOR THE DESIGN. UNAWARE OF THE POTENTIAL RISK OF WATER ACCUMULATION IN THE BOWL OF THE SILENCER. | COMMISSIONING | NO | [150 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmela.king@cmsenergy.com | 734-513-6253 |  |  |  |  | JASON PIONK | SENIOR ENGINEERING LEAD - GAS COMPLIANCE | 989-791-5749 | jason,pionk@cmsenergy.com | ON AUGUST 24, 2017 AT APPROXIMATELY 13:27 THE CONSUMERS ENERGY ST. CLAIR COMPRESSOR STATION PLANT 3 BLOW-DOWN SILENCER IGNITED. THE ST. CLAIR COMPRESSOR STATION IS LOCATED IN IRA TOWNSHIP (ST. CLAIR COUNTY) MICHIGAN. SHORTLY AFTER THE IGNITION, THE STATION WAS FIRE GATED. THE SITE WAS EVACUATED AND ALL SITE PERSONNEL WERE ACCOUNTED FOR.THERE WERE NO INJURIES THAT OCCURRED AS A RESULT OF THE IGNITION. AN INTERNAL TEAM WAS ASSEMBLED TO COMPLETE A ROOT CAUSE INVESTIGATION. THE INVESTIGATION BEGAN ON AUGUST 25, 2017 AND INCLUDED DEVELOPMENT OF THE SEQUENCE OF EVENTS, REVIEW OF THE SCENE, AND CONTRACTING WITH EXPONENT (THIRD PARTY CONSULTANT) TO COMPLETE AN EVALUATION OF VARIOUS IGNITION SCENARIOS. THE INVESTIGATION WAS COMPLETED AND THE CAUSE OF IGNITION WAS DUE TO ELECTROSTATIC DISCHARGE FROM ENTRAINED WATER DROPLETS IN THE GAS MIXTURE. SHORT TERM ACTIONS TO PREVENT RE-OCCURRENCE INCLUDE DRAINING WATER FROM ALL STATION BLOW DOWN SILENCERS WEEKLY. LONG TERM ACTIONS TO PREVENT RE-OCCURRENCE ARE BEING EVALUATED. FOLLOWING THE INCIDENT INVESTIGATION AND REMEDIAL ACTIVITIES, PLANT 1 WAS PLACED BACK INTO SERVICE AND NORMAL OPERATION RESUMED ON OCTOBER 13, 2018. ADDITIONAL ASSESSMENT OF THE SILENCERS AND THE VENT PIPING TO THE SILENCERS FOR PLANTS 3 AND 4, WHICH WERE UNDERGOING START-UP AND TESTING ACTIVITIES AT THE TIME THE INCIDENT OCCURRED, WERE COMPLETED TO CONFIRM THE INTEGRITY OF THE EQUIPMENT BEFORE INTRODUCING GAS INTO THE SYSTEM. ALL CORRECTIVE ACTIVITIES WERE COMPLETED AND PLANTS 3 AND 4 WERE PLACED IN-SERVICE IN APRIL 2018.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170082 | 17597 | 2017-09-25 09:16 | SUPPLEMENTAL FINAL | 32614 | WILLIAMS OLEFINS FEEDSTOCK PIPELINES, LLC | ONE WILLIAMS CENTER P.O. BOX 645 | TULSA | OK | 74172 | 2017-08-28 14:00 | 2017 |  |  | 29.6942 | -95.0289 | 1189587 | 2017-08-28 17:09 |  | OTHER GAS | HYDROGEN CHLORIDE GAS | 6.157 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | PIPELINE WAS PRESSURIZED BUT PRODUCT WAS NOT FLOWING AT TIME OF INCIDENT. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-08-28 16:10 | 2017-08-28 16:45 | ONSHORE | TX | 77520 | BAYTOWN | HARRIS | MILEPOST | FRED HARTMAN | HCL GAS PIPELINE | 18930 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | TUBING | [38 empty] | UNKNOWN |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | MONEL | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | YES | METHOD2 | 10 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 2 | 1.83173076923077 | 6000 | 6381.80807706558 | 0 | 0 | 0 | 0 |  |  | 6002 | 2931.31734153675 | 6383.63980783481 | [8 empty] | 96 |  | 673 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | AUTOMATIC | 38016 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SMALL RELEASE COULD NOT BE DETECTED BY PIPELINE CONTROL. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | DEFECTIVE OR LOOSE TUBING OR FITTING | MATERIAL/WELD/EQUIP FAILURE | DEFECTIVE OR LOOSE TUBING/FITTING | [166 empty] | DEFECTIVE OR LOOSE TUBING OR FITTING | [20 empty] | YES | [8 empty] | YES | [168 empty] | SHANE FRASIER | PIPELINE SAFETY ENGINEER | shane.frasier@williams.com | 7132153051 |  |  |  |  | SHANE FRASIER | PIPELINE SAFETY ENGINEER | 713-215-3051 | shane.frasier@williams.com | AT APPROXIMATELY 2PM ON 08/28/2017, THE PRESSURE TRANSMITTER AT LPT1 WENT TO 0 PSI, ON THE 893 HCL (HYDROGEN CHLORIDE GAS) PIPELINE . THIS PRESSURE DROP REPRESENTED A 3/8' TUBING FAILURE ON AN INSTRUMENTATION RACK AT THE MLV UNDER THE FRED HARTMAN BRIDGE, RESULTING IN A PRODUCT RELEASE. THIS RELEASE WAS NOT PICKED UP BY ON-SITE GAS DETECTION, LIKELY DUE TO WIND DIRECTION AND STRENGTH. WINDS ARE ESTIMATED TO BE 15-20MPH FROM THE NORTH/NORTHEAST. SPORADIC HEAVY RAIN IS PRESENT IN THE AREA FROM THE ONGOING TROPICAL STORM, HARVEY. AT 4:10PM, A PASSER-BY CALLED WILLIAMS PIPELINE CONTROL TO ALERT THEM TO A RELEASE RESULTING IN A PLUME FROM THE SITE. THAT PASSER-BY WAS JENNIFER OLIVER, CELL PHONE 713-392-6214. PIPELINE CONTROL ISOLATED THE RELEASE BY ACTUATING MAINLINE VALVES TO CLOSE. PIPELINE CONTROL ALERTED CHANNELVIEW OPERATIONS, MOBILIZING SEVERAL MEMBERS OF THE TEAM TO INVESTIGATE THE INCIDENT. JONATHON KEETH, CHARLIE SHAW AND JAMES SPARKS ATTEMPTED TO GET TO THE SITE. JONATHAN KEETH WAS FIRST TO ARRIVE AND CHARLIE SHAW ARRIVED ALMOST IMMEDIATELY AFTER, WHERE LA PORTE EMERGENCY RESPONSE TEAM WAS ON SITE AT APPROXIMATELY 4:45PM. AN INCIDENT COMMAND STRUCTURE WAS ESTABLISHED IMMEDIATELY INCIDENT COMMANDER CHAD KUKLA SAFETY OFFICER JONATHAN KEETH 1ST RESPONDERS MAINTAINED 100 YARDS DISTANCE FROM THE VALVE SITE, STAYING UPWIND, TO PROVIDE ADEQUATE SAFETY MARGIN. LA PORTE FIRE DEPARTMENT ISSUED A SHELTER-IN-PLACE ORDER FOR SURROUNDING AREA RESIDENTS AND SHUT DOWN BOTH DIRECTIONS OF HWY 146 AND HWY 225. THERE WERE NO NEARBY FIRE HYDRANTS SO A WATER FOG TO MITIGATE THE HCL PLUME WAS NOT POSSIBLE. HAZMAT UNITS FROM HARRIS COUNTY AND OXY VINYL RESPONDED TO THE SCENE, ARRIVING AT 6:21PM, BAYTOWN HAZMAT ATTEMPTED TO RESPOND BUT WAS UNABLE. THE BEST METHOD OF DEALING WITH THE LINE WAS DETERMINED TO BE HAVING OXY VINYL PULL THE LINE DOWN, WHICH WAS AT 95 PSI TO START. LINE FILL EXPOSURE WAS CALCULATED TO BE 57K LBS OF HCL. OVER THE COURSE OF 1.5 HOURS, OXY WAS ABLE TO PULL THE LINE DOWN TO 13 PSI, TAKING 38K LBS, WHEN HAZMAT TEAMS ENTERED THE SITE TO ISOLATE THE RELEASE. THE HAZMAT TEAM ENTERING THE SITE CONSISTED OF TWO HARRIS COUNTY TEAM MEMBERS LEADING THE ISOLATION EFFORTS, WITH THREE OXY VINYL TEAM MEMBERS ENTERING IN ASSISTANCE. JONATHAN KEETH PROVIDED DETAILED INSTRUCTION OF THE SYSTEM TO THE HAZMAT TEAMS, LAYING OUT THE CORRECT VALVES TO CLOSE AND NECESSARY KEYS FOR ENTRY. AT 7:01PM, SITE ENTRY OCCURRED BY THE HAZMAT TEAMS. AT 7:02PM, THE FIRST VALVE WAS CLOSED AND ISOLATION OCCURRED. THE HAZMAT TEAMS THEN CLOSED THE 3/4' VALVE ON THE TUBING TO PROVIDE ADDITIONAL ISOLATION OF THE RELEASE. AT 7:05PM, JONATHON ENTERED THE SITE TO DETERMINE THE NECESSARY TOOLS AND EQUIPMENT NEEDED TO PROVIDE POSITIVE ISOLATION. AT 7:13PM, AUTHORITIES RELEASED TRAFFIC IN BOTH DIRECTIONS OF HWY 146 AND HWY 225. JONATHON PLACED A TUBING PLUG AND THREADED FITTING WHERE THE TUBING FERAL FAILED AND LET GO. THE TUBING SECTION WHICH FAILED WAS REMOVED AND A NEW NUT, FERAL AND CAP WERE INSTALLED. THIS TRANSMITTER WILL REMAIN OUT OF SERVICE UNTIL THE WEATHER BREAKS OR A PLANNED REPAIR CAN TAKE PLACE ON THURSDAY, AUGUST 31, USING AN AWNING FOR SHELTER. THAT REPAIR TEAM IS SCHEDULED TO BE JONATHON KEETH AND CHARLIE SHAW. AT 7:25PM, ALL EMERGENCY RESPONDERS LEFT THE SITE. UPDATE 9/25/2017 TUBING CONNECTIONS HAVE BEEN REPLACED WITH NEW COMPONENTS. INITIAL INVESTIGATION SHOWS THAT THE TUBING FERULE FAILED, LIKELY DUE TO REACTION WITH HCL PRODUCT AND WATER IN ATMOSPHERE. NEW FITTINGS MANUFACTURED FROM HASTELLOY MATERIAL HAVE BEEN INSTALLED IN PLACE OF MONEL MATERIAL.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170083 | 17449 | 2017-09-27 15:05 | ORIGINAL FINAL | 38932 | BLUESTONE PIPELINE COMPANY OF PA, LLC | ONE ENERGY PLAZA - WCB 2130 | DETROIT | MI | 48226 | 2017-09-02 01:02 | 2017 |  |  | 41.9831 | -75.5499 | 1189642 | 2017-09-07 12:24 |  | NATURAL GAS |  | 10800 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-09-02 02:41 | 2017-09-02 03:43 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-09-02 01:02 | 2017-09-02 02:30 | ONSHORE | PA | 18847 | SUSQUEHANNA | SUSQUEHANNA | MILEPOST | MILEPOST 10.5 | HARMONY COMPRESSOR STATION | HARMONY COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2015 |  | CARBON STEEL |  | OTHER | [8 empty] | A PILOT THAT CONTROLS THE UNIT 2 DISCHARGE RELIEF VALVE FAILED. WHEN THE PILOT FAILED, IT ALLOWED THE RELIEF VALVE TO COME OFF ITS SEAT AND BLOW GAS. THE RELIEF VALVE FUNCTIONED EXACTLY HOW IT IS DESIGNED TO. | CLASS 1 LOCATION | NO |  | 628 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 32730 | 29976.2740384615 | 1015 | 1079.58919970359 | 306 | 325.472211930345 | 0 | 0 |  |  | 34051 | 31722.7246861373 | 31381.3354500955 | [8 empty] | 1240 |  | 1650 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE FAILURE WAS NOT A DIRECT RESULT OF CONTROLLER ERROR. HARMONY COMPRESSOR STATION, UNIT 2, HAD A PILOT VALVE THAT CONTROLLED THE OPERATION OF A RELIEF VALVE ON THE DISCHARGE PORTION OF UNIT 2. THE PILOT FAILED DUE TO VIBRATION COMING FROM UNIT 2 ITSELF. WHEN THE PILOT FAILED, IT CAUSED THE RELIEF VALVE TO OPEN AND FUNCTION AS IT SHOULD. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | APPURTENANCE FAILURE | [6 empty] | YES | [177 empty] | BRIAN MILLS |  | brian.mills@dteenergy.com | 570-396-1262 |  |  |  |  | BRIAN MILLS |  | 570-396-1262 | brian.mills@dteenergy.com | SECOND NRC REPORT NUMBER (48 HOUR) IS 1189751. HARMONY COMPRESSOR STATION (HCS) HAD AN UNINTENTIONAL RELEASE OF NATURAL GAS ON SEPTEMBER 2, 2017, FROM APPROXIMATELY 01:02 TO 02:41. A LOCAL NEIGHBOR TO HCS CONTACTED 911 TO REPORT THE EVENT. AFTER SUCH, 911 CONTACTED DTE GAS CONTROL AT 01:02. DTE GAS CONTROL CONTACTED THE ON CALL TECHNICIAN TO INFORM THEM THAT A REPORT OF BLOWING GAS HAD BEEN MADE. THE TECHNICIAN, UPON ARRIVAL AT HCS, DISCOVERED THAT THE PILOT FOR UNIT 2 RELIEF VALVE HAD FAILED. AT 02:41, THE TECHNICIAN PUSHED THE EMERGENCY SHUT DOWN BUTTON AND UNIT 2 BECAME INACTIVE. UPON TAKING UNIT 2 OUT OF SERVICE, THE TECHNICIAN REPAIRED THE PILOT AND THEN PLACED UNIT 2 BACK INTO SERVICE AT 03:43. AFTER INVESTIGATION INTO THE MATTER, IT WAS DISCOVERED THAT THE PILOT HAD FAILED DUE TO A PREVIOUS VIBRATION ISSUE ON UNIT 2. THE INCIDENT AND INVESTIGATION WAS DISCUSSED WITH THE PA PUBLIC UTILITIES COMMISSION AFTER THE FAILURE OCCURRED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170084 | 17451 | 2017-09-28 13:52 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2017-09-06 13:40 | 2017 |  |  | 28.6999 | -96.9434 | 1189566 | 2017-09-06 14:04 |  | NATURAL GAS |  | 3424 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-09-06 13:50 | 2017-09-06 15:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-09-06 13:40 | 2017-09-06 13:40 | ONSHORE | TX | 77905 | VICTORIA | VICTORIA | MILEPOST | MLV 9-1+000 | VICTORIA STATION 9 | DISCHARGE HEADER RELIEF VALVE 9-B2D | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1951 |  | CARBON STEEL |  | OTHER | [8 empty] | DISCHARGE RELIEF VALVE VENTED TO ATMOSPHERE PREMATURELY | CLASS 1 LOCATION | NO |  | 163 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 10581 | 9690.77163461538 | 4720 | 5020.35568729159 | 0 | 0 | 0 | 0 |  |  | 15301 | 12351.3387125217 | 14711.127321907 | [8 empty] | 746 |  | 750 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS CAUSED BY A LOCAL EQUIPMENT MALFUNCTION CAUSING GAS TO RELEASE MORE THAN 3000MCF AND WAS NOT ASSOCIATED WITH ANY CONTROLLER OR CONTROL ROOM ACTIONS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | RELIEF VALVE PILOT UNABLE TO HOLD SET PRESSURE | [161 empty] | KRISTIN VAN DER LAAN | SENIOR PIPELINE ENGINEER | kristin_vanderlaan@kindermorgan.com | 303-914-7753 |  |  |  |  | REJI GEORGE | DIRECTOR - COMPLIANCE - CODES AND STANDARDS | 713-420-5433 | reji_george@kindermorgan.com | TENNESSEE GAS PIPELINE COMPANY (TGP) VICTORIA STATION 9 WAS OFFLINE DURING HURRICANE HARVEY. AFTER THE HURRICANE IT WAS BROUGHT BACK ONLINE. WHEN THE PRESSURE ON THE DISCHARGE HEADER REACHED 746PSIG THE DISCHARGE HEADER RELIEF VALVE VENTED PREMATURELY. THE SET PRESSURE WAS 758PSIG (102%). OPERATING PERSONNEL WERE ONSITE, HEARD THE RELEASE AND RESPONDED BY SHUTTING THE STATION DOWN. THE RELIEF VALVE RELEASED APPROXIMATELY 3424MCF NATURAL GAS, MEETING AND EXCEEDING THE 3000MCF REQUIRED FOR INCIDENT REPORTING. FURTHER INVESTIGATION DETERMINED THAT THE PILOT COULD NOT HOLD THE SET PRESSURE. BASED ON AN EVALUATION OF THE OVERPRESSURE PROTECTION (OPP) REQUIRED BY 49CFR 192 IT WAS DETERMINED THAT THIS DEVICE WAS REDUNDANT AND IT WILL NOT BE PUT BACK INTO SERVICE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170085 | 30004 | 2017-09-29 22:31 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2017-09-02 04:29 | 2017 |  |  | 41.6216 | -88.5794 | 1189107 | 2017-09-02 06:34 |  | NATURAL GAS |  | 8900 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | VALVES REPOSITIONED TO STOP OVERPRESSURE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-09-02 04:20 | 2017-09-02 04:29 | ONSHORE | IL | 60548 | SANDWICH | KENDALL | MILEPOST | 795 | SANDWICH COMPRESSOR STATION | SOUTHWEST MAIN LINE SYSTEM - 100 LINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1949 |  | CARBON STEEL |  | OTHER | [8 empty] | GAS RELEASE DUE TO ACTIVATION OF A RELIEF VALVE | CLASS 1 LOCATION | NO |  | 518 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 25700 | 23537.7403846154 | 1000 | 1063.63467951093 | 2500 | 2659.08669877733 | 0 | 0 |  |  | 29200 | 26111.4715742298 | 27260.4617629036 | [8 empty] | 856 |  | 850 | 192.619(A)(2) |  |  |  | PRESSURE EXCEEDED MAOP, BUT DID NOT EXCEED THE APPLICABLE ALLOWANCE IN 192.201 | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES |  |  | YES |  |  |  |  | NO |  |  | NO |  |  | INCORRECT OPERATION | PIPELINE OR EQUIPMENT OVERPRESSURED | INCORRECT OPERATION | PIPELINE/EQUIPMENT OVERPRESSURED | [204 empty] | PIPELINE OR EQUIPMENT OVERPRESSURED |  |  |  |  | YES |  |  |  | NORMAL OPERATING CONDITIONS | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | JOHN CHIN | SR. REGULATORY COMPLIANCE SPECIALIST | john_chin@transcanada.com | 248-205-4522 | 248-205-4622 |  |  |  | JOHN CHIN | SR. REGULATORY COMPLIANCE SPECIALIST | 248-205-4522 | john_chin@transcanada.com | AT 4:20AM CT ON SEPTEMBER 2, 2017, THE AREA MANAGER RECEIVED A CALL FROM A NEIGHBORING RESIDENT THAT GAS WAS VENTING FROM THE COMPRESSOR STATION. PERSONNEL WERE DISPATCHED TO INVESTIGATE. SHORTLY AFTER 4:29AM, FIELD PERSONNEL IDENTIFIED TWO VALVES INCORRECTLY POSITIONED FROM A PREVIOUS OPERATION. AFTER THESE VALVES WERE CORRECTLY POSITIONED, THE RELIEF VALVES STOPPED VENTING. IT WAS DETERMINED THAT THE 6" RELIEF VALVES VENTED INTERMITTENTLY (DUE TO PRESSURE INCREASING AND DECREASING ABOVE AND BELOW THE SET POINT) FOR ABOUT 31 MINUTES WHEN THE PRESSURE IN THE PIPELINE REACHED 850 PSIG. THE EVENT MET THE DEFINITION OF INCIDENT BASED ON AN UNINTENDED GAS RELEASE EXCEEDING 3MMCF.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170087 | 17469 | 2017-10-10 14:49 | SUPPLEMENTAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2017-09-11 13:00 | 2017 |  |  | 32.9116 | -92.8159 | 1189935 | 2017-09-11 14:14 |  | NATURAL GAS |  | 3695 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | REPAIRED WITHOUT TAKING OUT OF SERVICE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-09-11 13:00 | 2017-09-11 13:38 | ONSHORE | LA | 71222 | BERNICE | CLAIBORNE | MILEPOST | 1351+52 | KT-1 | 1351+52 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | YES | [6 empty] | YES | UNCASED | UNKNOWN | UNKNOWN | SHORELINE/BANK/MARSH CROSSING | [11 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10 |  | 0.188 | 35000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | ASPHALT | [28 empty] | 1942 | 1942 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 141 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 10930 | 10010.4086538462 | 183000 | 194645.1463505 | 250 | 265.908669877733 | 0 | 0 |  |  | 194180 | 99847.5625320632 | 204921.463674224 | [8 empty] | 335 |  | 420 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL |  | NO | [5 empty] | YES | STOPPLES | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL ROOM DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  |  | YES | [7 empty] | YES |  |  |  | YES | YES |  | NO | YES |  | YES |  |  |  | 2017 |  |  | YES | [190 empty] | NO | [63 empty] | NO |  |  | Yes, but the point of the Accident was not identified as a dig site |  | 2017 | [11 empty] | YES |  |  | 2009 | [6 empty] | YES | [53 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | WHILE PERFORMING A CLOSE INTERVAL SURVEY, AN ENABLE DIRECT ASSESSMENT (DA) CREW, DISCOVERED A LEAK ON LINE KT-1. UPON DISCOVERY, THE DA CREW NOTIFIED THE LOCAL ENABLE MIDSTREAM OPERATING PERSONNEL WHO ASSESSED THE SITUATION AND CONFIRMED THE LEAK TO BE ON KT-1 AT 13:38. THE ENABLE MIDSTREAM ON-CALL TEAM WAS NOTIFIED AND A NOTIFICATION CALL WAS PLACED TO THE NRC (NRC# 1189935 9/11/2017 14:14 CST). A 48 HOUR FOLLOW UP CALL (NRC#1190154) WAS PLACED ON 9/13/17 AT 11:11 CST. AT THE LEAK LOCATION, KT-1 CONSISTS OF GRADE B STEEL, 10.75, .188 W.T. PIPE. IT WAS INSTALLED IN CLAIBORNE PARISH LA IN 1942. LINE KT-1 WAS REPAIRED WITHOUT BEING TAKEN OUT OF SERVICE, BY PLACING STOPPLES BOTH UPSTREAM AND DOWNSTREAM OF THE LEAK SITE WITH A BYPASS. WHEN COMPLETED, THE LEAKING SECTION OF PIPE WAS REMOVED AND INVESTIGATED FURTHER. THE LEAK WAS FOUND TO BE LOCATED AT A CIRCUMFERENTIAL GIRTH WELD AT A CREEK CROSSING. IT HAS BEEN DETERMINED THAT SEVERAL FACTORS CONTRIBUTED TO THE LEAK ON KT-1. - THIS PIPE HAS BEEN PREVIOUSLY EXPOSED IN A SEASONAL CREEK CROSSING AND WAS SUBJECT TO ATMOSPHERIC CORROSION WHEN THE WATER LEVEL RECEDED. - LOW CATHODIC PROTECTION LEVELS WERE PREVIOUSLY FOUND DUE TO THE PRESENCE OF NEARBY DRESSER COUPLINGS. ALTHOUGH THESE LOW LEVELS OF CP WERE REMEDIATED, CORROSION HAS PREVIOUSLY OCCURRED. - IN 2012, THE CREEK CROSSING WAS REMEDIATED BY ADDING GROUND COVER. THE PIPE APPEARS TO HAVE EXPERIENCED STRESS FROM ADDED WEIGHT ABOVE PIPE GRADE AND LACK OF SUPPORT BELOW PIPE GRADE. THE REMAINING WALL THICKNESS AT THE GIRTH WELD APPEARS TO HAVE MECHANICALLY FAILED DUE TO THIS STRESS. A FINAL REPAIR COST CANNOT BE PROVIDED AT THIS TIME AND A SUPPLEMENTAL REPORT WILL BE SUBMITTED WHEN IT CAN BE DETERMINED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170088 | 17466 | 2017-10-10 15:09 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2017-09-15 12:00 | 2017 |  |  | 35.1708 | -81.4097 | 1190605 | 2017-09-15 13:06 |  |  |  | 0 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE STATION WAS ALREADY OFFLINE TO ACCOMMODATE THE MAINTENANCE WORK TAKING PLACE | [6 empty] | YES |  |  |  |  | YES | [6 empty] | 0 | 2017-09-15 12:00 | 2017-09-15 12:00 | ONSHORE | NC | 28073 | GROVER | CLEVELAND | MILEPOST | 1247.08 | TRANSCO STATION 145 | VALVE 145-S6 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | PIPE | PIPE SEAM | 30 |  | 0.5 | 65000 | API-5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | JSW STEEL | EPOXY | [28 empty] | 2017 | 2015 | CARBON STEEL |  | OTHER | [8 empty] | ACCIDENTAL IGNITION. | CLASS 1 LOCATION | NO |  | 694 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 425.453871804372 | 23925 | 25447.459707299 | CONTRACTOR CRANE STAND BY COST DUE TO DELAY |  | 24325 | 11876.3500370508 | 25872.9135791034 | [8 empty] | 0 |  | 780 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | YES | NO | NOT MANDATED | [20 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | INADEQUATE PIPING PURGE AND FRESH AIR PORTS UTILIZED. | YES |  |  |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | SHANE FRASIER | PIPELINE SAFETY ENGINEER | shane.frasier@williams.com | 713-215-3051 |  |  |  |  | LARRY LEGENDRE | PIPELINE SAFETY MANAGER | 7132152733 | larry.d.legendre@williams.com | COMPRESSOR STATION SIDE GATE VALVE 145-S6 AND ASSOCIATED PIPING WAS BEING CUT OUT AND REPLACED AS PART OF THE ATLANTIC SUNRISE FLOW REVERSAL PROJECT AT STATION 145. DURING THE TIE IN WELDING ACTIVITIES ON THE STATION SIDE OF THE NEW VALVE, AN ACCIDENTAL IGNITION EVENT OCCURRED CAUSING A PRESSURE WAVE TO TRAVEL THROUGH THE SUBJECT PIPING AND EXIT THROUGH THE AIR MOVER AND 8 INCH ISOLATION BAG PORT NEAR SIDE GATE VALVE 145-S8. IT WAS DETERMINED THAT THE GAS HANDLING PROCEDURE THAT WAS CREATED FOR THIS PROJECT WAS NOT SUFFICIENT.
2021-02-26 10:37 | NO | NO | GG (Gas Gathering) | 20170089 | 30451 | 2017-10-11 11:29 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2017-09-15 19:00 | 2017 |  |  | 28.6997 | -91.0024 | 1190555 | 2017-09-16 15:52 |  | NATURAL GAS |  | 709 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-09-13 17:05 | 2017-09-15 12:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-09-11 16:50 | 2017-09-15 12:00 | OFFSHORE | [28 empty] | 48 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SHIP SHOAL | 158 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 10 |  | 0.365 | 35000 | API-5LX | SEAMLESS |  | UNKNOWN | COAL TAR | [28 empty] | 1963 | 1963 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 200 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 2335 | 2138.54567307692 | 81000 | 86154.4090403853 | 5000 | 5318.17339755465 | 0 | 0 |  |  | 88335 | 44205.4564145909 | 93611.1281110169 | [8 empty] | 526 |  | 1440 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | AUTOMATIC | 116107 | NO | [5 empty] | YES | UPSTREAM CONNECTION OF PIPELINE IS SUBSEA WITH NO PIGGING FACILITIES. | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | SHANE FRASIER | PIPELINE SAFETY ENGINEER | shane.frasier@williams.com | 713-215-3051 |  |  |  |  | LARRY LEGENDRE | PIPELINE SAFETY MANAGER | 7132152733 | larry.d.legendre@williams.com | 9/11/2017 WGP WAS NOTIFIED BY THIRD PARTY THAT BUBBLES WERE PRESENT IN SHIP SHOAL BLOCK 158. 9/13/2017 OPERATIONS INVESTIGATED AND DETERMINED THAT BUBBLES WERE LIKELY COMING FROM THE WGP 10' PIPELINE. THE SECTION OF 10' PIPELINE WAS ISOLATED. 9/15/2017 A DIVE BOAT WAS DISPATCHED AND UPON ARRIVING ON SITE TO INVESTIGATE THE LEAK A SECOND SET OF BUBBLES WERE DISCOVERED. DIVERS INVESTIGATED AND DETERMINED THAT BOTH LEAKS WERE ON THE WGP 10' PIPELINE. THE PIPELINE PRESSURE WAS REDUCED AND CLAMPS WERE INSTALLED. THE FIRST LEAK OCCURRED AT M.P. 17.029 AND THE SECOND LEAK OCCURRED AT M.P. 17.444. 9/15/2017 IT WAS DETERMINED THAT THE COST OF THE RESPONSE AND THE REPAIR WOULD EXCEED THE $50K THRESHOLD. NRC WAS NOTIFIED. 9/28/2017 THE PIPELINE REMAINS IDLE WITH MINIMAL PRESSURE. OPERATIONS AND CYPRESS DIVISION ARE WORKING TO ABANDON THE LINE. 10/19/2017 AT THE REQUEST OF BRIAN PIERZINA, PHMSA AID, THIS REPORT HAS BEEN SPLIT INTO TWO SEPARATE REPORTS DUE TO THE FACT THAT THERE WERE TWO LEAKS. THIS SUPPLEMENTAL REPORT CORRESPONDS TO THE LEAK AT M.P. 17.029. GAS VOLUME REPORTED ABOVE IS THE BEST ESTIMATE FOR THAT LOCATION ONLY. 6/5/2018 AS OF THIS DATE, THERE HAS BEEN NO CHANGE TO THE OPERATIONAL STATUS OF THIS PIPELINE. IT REMAINS ISOLATED WITH MINIMAL PRESSURE. WE ARE WORKING WITH OUR PRODUCER PARTNERS AS WELL AS THE OTHER REGULATORY AGENCIES FOR APPROVAL TO ABANDON THE LINE. THE FINAL ABANDONMENT IS SLATED TO TAKE PLACE IN 3Q 2019. AT THE REQUEST OF BRIAN PIERZINA, WE HAVE UPDATED THE "FACILITY RESTART" DATE TO 9/15/2017 AS THAT WAS THE POINT IN WHICH ACTIVITIES ASSOCIATED WITH THE RELEASE EVENT WERE ESSENTIALLY CONCLUDED. THIS REPORT WILL NOW BE MARKED AS "FINAL".
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170090 | 17467 | 2017-10-11 17:07 | SUPPLEMENTAL FINAL | 32557 | PAULSBORO NATURAL GAS PIPELINE COMPANY, LLC | 1 SYLVAN WAY SECOND FLOOR | PARSIPPANY | NJ | 07054 | 2014-08-04 21:15 | 2014 |  |  | 39.8513 | -75.2593 | 1091299 | 2014-08-05 01:06 |  | NATURAL GAS |  | 1563 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2014-08-04 22:00 | 2014-11-02 23:48 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2014-08-04 21:54 | 2014-08-04 22:00 | ONSHORE | PA | 19029 | TINICUM TOWNSHIP | DELAWARE COUNTY | SURVEY STATION NO. | 18+85 | PAULSBORO NATURAL GAS PIPELINE COMPANY LLC | DELAWARE RIVER CROSSING | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | UNDERWATER | 48 |  | YES | [6 empty] | YES | UNCASED | DELAWARE RIVER | 43 | BELOW WATER, PIPE BURIED BELOW BOTTOM (NOT IN BORED/DRILLED CROSSING) | [11 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 |  | 0.4 | 35000 | GRADE B | SEAMLESS |  | UNKNOWN | ASPHALT | [28 empty] | 1941 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 25.1 | 25.1 | [7 empty] | CLASS 1 LOCATION | NO |  | 163 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 3625 | 2418.78283712785 | 2579970 | 2853847.94432136 | 0 | 0 | 0 | 0 |  |  | 2583595 | 1312499.17244828 | 2856266.72715848 | [8 empty] | 565 |  | 870 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | REMOTELY CONTROLLED | 13992 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS CAUSED BY A THIRD PARTY, UNRELATED TO THE OPERATOR, OPERATING IN THE VICINITY OF THE PIPELINE WITHOUT THE OPERATOR'S KNOWLEDGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES | YES | OTHER |  |  | YES | [6 empty] | CONTRACTOR | VACUUM EQUIPMENT | WATERWAY IMPROVEMENTS | NO | [5 empty] | YES | 2162 | OTHER |  |  |  | CROSS-RIVER NATURAL GAS PIPELINE WAS STRUCK BY THIRD PARTY RIVER DREDGE VESSEL. | [262 empty] | ROBERT C. MUCHE | ENVIRONMENTAL MANAGER | robert.muche@pbfenergy.com | 856-224-6607 |  |  |  |  | ROBERT C. MUCHE | ENVIRONMENTAL MANAGER | 856-224-6607 | robert.muche@pbfenergy.com | AT APPROX. 9:56 PM ON 08/04/2014, LT. ERIC NIELSON OF THE UNITED STATES COAST GUARD NOTIFIED THE PAULSBORO NATURAL GAS PIPELINE COMPANY (PNGPC) OF A DREDGE VESSEL APPROXIMATE TO THE PAULSBORO REFINING COMPANY'S FACILITY REPORTING POSSIBLE DAMAGE TO THE GAS PIPELINE. OPERATING PERSONNEL ISOLATED THE PNGPC 8-INCH CROSS-RIVER NATURAL GAS PIPELINE BY APPROX. 10:00 PM. THE DREDGE WAS LATER REPORTED BY THE UNITED STATES COAST GUARD TO BE THE GREAT LAKES DREDGE & DOCK BARGE "PADRE ISLAND," WORKING UNDER THE UNITED STATES ARMY CORPS OF ENGINEERS, DREDGING IN THE BILLINGSPORT RANGE OF THE DELAWARE RIVER. THE BARGE CAME INTO CONTACT WITH THE PNGPC 8-INCH CROSS-RIVER NATURAL GAS PIPELINE. IN THAT CONTACT, THE PIPE WAS DAMAGED. DIVERS WERE SUBSEQUENTLY DISPATCHED TO SURVEY THE DAMAGE TO THE PNGPC NATURAL GAS PIPELINE. THE SURVEY INDICATES THAT THE PNGPC NATURAL GAS PIPELINE HAD BEEN SEVERED. AT THE TIME OF THIS REPORT (THE ORIGINAL GAS DISTRIBUTION REPORT ON 09/02/2014), PNGPC IS FORMULATING A REPAIR PLAN THAT THE COMPANY WILL INITIATE WITHIN 30 DAYS.
2021-02-26 10:37 | NO | NO | GG (Gas Gathering) | 20170091 | 17473 | 2017-10-13 15:41 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2017-09-13 10:13 | 2017 |  |  | 27.8861 | -95.9773 | 1190197 | 2017-09-13 15:22 |  | NATURAL GAS |  | 100 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | SHORT SPOOL PIECE, ISOLATED BY VALVE. INSTALLED CLAMP. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-09-13 10:13 | 2017-09-13 10:13 | OFFSHORE | [28 empty] | 185 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | BAA | 105 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 |  |  |  | UNKNOWN | OTHER | UNKNOWN | UNKNOWN | EPOXY | [28 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 331 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 329 | 301.319711538462 | 50000 | 53181.7339755465 | 5000 | 5318.17339755465 | 0 | 0 |  |  | 55329 | 27165.3929384459 | 58801.2270846396 | [8 empty] | 900 |  | 1440 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 3 | NO | [5 empty] | YES | SUBSEA VALVE ASSEMBLY | NO | [6 empty] | OFFSHORE GATHERING | YES | YES | YES | NO | NO | OTHER | THIRD PARTY DIVE TEAM WAS WORKING IN THE AREA. |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ROUTINE OR NORMAL FISHING OR OTHER MARITIME ACTIVITY NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | FISHING OR MARITIME ACTIVITY | [103 empty] | ROUTINE OR NORMAL FISHING OR OTHER MARITIME ACTIVITY NOT ENGAGED IN EXCAVATION | [261 empty] | SHANE FRASIER | PIPELINE SAFETY ENGINEER | shane.frasier@williams.com | 713-215-3051 |  |  |  |  | LARRY LEGENDRE | PIPELINE SAFETY MANAGER | 7132152733 | larry.d.legendre@williams.com | 9/13/2017 FIELDWOOD CONTRACT PERSONNEL WERE PERFORMING MAINTENANCE ON THE SUBSEA VALVE ASSEMBLY IN THIS LOCATION AND NOTICED THAT THERE WAS AN ABANDONED COMMERCIAL FISHING NET CAUGHT UP ON THE ASSEMBLY. THE DIVERS WORKING FOR FIELDWOOD REMOVED THE TRAUL BOARDS AND CHAINS AND DISCOVERED BUBBLES FROM A SMALL PINHOLE LEAK ON THE TRANSCO 16 INCH SPOOL PIECE. A BOLT ON CLAMP WAS LOCATED AND IMMEDIATELY SENT TO THE LOCATION. THE DIVE TEAM FROM FIELDWOOD INSTALLED THE CLAMP WHICH SUCCESSFULLY STOPPED THE LEAK. 10/18/2017 UPON FURTHER REVIEW OF DIVER LOGS. THE EXACT TIME THAT THE LEAK WAS DISCOVERED HAS BEEN UPDATED TO SHOW 10:13 AM. DIVERS ALSO REPORTED ON THE LOG THAT AFTER REMOVAL OF CHAINS FROM THE SHRIMP NETS, THEY COULD SEE AN AREA WHERE THE CHAINS HAD RUBBED AND REMOVED SOME OF THE METAL WALL OF THE PIPE BODY. THE AREA THAT HAD BEEN RUBBED WAS OBSERVED TO BE ROUGHLY 1 INCH LONG BY 3/4 INCH WIDE WITH A PINHOLE LEAK IN THE MIDDLE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170092 | 30533 | 2017-10-18 18:51 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2017-09-19 08:45 | 2017 |  |  | 31.9485 | -103.1089 | 1190872 | 2017-09-19 14:52 |  | NATURAL GAS |  | 15407 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE SYSTEM WAS SHUT DOWN FOR ANNUAL MAINTANENCE SHUTDOWN BEFORE THE INCIDENT | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-09-19 12:30 | 2017-09-19 08:45 | ONSHORE | TX | 79745 | KERMIT | WINKLER | MILEPOST | COMPRESSOR | KEYSTONE ML STATION | KEYSTONE STATION | YES | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEVE VALVE CHATTERING BECAUSE OF BACK PRESSURE ON SUCTION PIPING. | CLASS 1 LOCATION | NO |  | 1035 |  | NO | NO | NO |  | 15 | 15.9545201926639 | 0 | 0 | 46045 | 42171.0216346154 | 112 | 119.127084105224 | 0 | 0 | 0 | 0 |  |  | 46172 | 43782.6190015177 | 42306.1032389133 | [8 empty] | 580 |  | 575 | 192.619(C) |  |  |  | PRESSURE EXCEEDED MAOP, BUT DID NOT EXCEED THE APPLICABLE ALLOWANCE IN 192.201 | NO | [22 empty] | TRANSMISSION SYSTEM | YES | NO | NO | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SYSTEM WAS OFFLINE FOR ANNUAL MAINTENANCE SHUT DOWN. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [13 empty] | YES | [177 empty] | KRITI BHAYANI | PIPELINE ENGINEER - COMPLIANCE-CODES AND STANDARDS | kriti_bhayani@kindermorgan.com | 7134206633 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR OF COMPLIANCE-CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | KEYSTONE COMPRESSOR STATION WAS REMOVED FROM SERVICE FOR SCHEDULED ANNUAL CHECKS AND MAINTENANCE AT 8:00 AM. APPROXIMATELY 45 MINUTES AFTER THE STATION WAS OFF-LINE, THE PLANT B INLET SUCTION PIPING RELIEF VALVE (SET AT 580 PSIG) BEGAN RELIEVING PRESSURE INTERMITTENTLY. GAS CONTROL WAS NOTIFIED AT 9:40 AM. GAS CONTROL STATED THAT A SECOND UNIT HAD BEEN PLACED IN SERVICE TO MOVE GAS VOLUME OUT OF THE PERMIAN WHICH HELPED REDUCE THE PRESSURE AT THE KEYSTONE COMPRESSOR STATION. THE RELIEF VALVE CONTINUED TO RELIEVE PRESSURE INTERMITTENTLY AND AT THAT POINT GAS CONTROL WAS NOTIFIED AND THEY VERIFIED THROUGH SCADA SYSTEM THAT THE PRESSURE HAD CONTINUED TO DECREASE. ON SITE OPERATION PERSONNEL RESPONDED TO THE RELIEF VALVE AND VERIFIED THAT A MANUAL PRESSURE GAUGE NEAR THE RELIEF VALVE WAS SHOWING INCORRECT PRESSURE OF 580 PSIG WHEN COMPARED TO PRESSURE FROM GAS CONTROL. THE GAUGE WAS REMOVED AND REPLACED WITH A DIFFERENT ONE THAT INDICATED A PRESSURE OF 522 PSIG WHICH WAS CONFIRMED WITH WHAT GAS CONTROL WAS SEEING. OPERATIONS THEN ISOLATED THE RELIEF VALVE. INSPECTION OF THE RELIEF VALVE REVEALED THAT ITS SEAL WAS BROKEN AND LOCKING MECHANISM HAD BACKED OUT CAUSING IT TO RELIEVE AT PRESSURES LOWER THAN ITS NORMAL SET PRESSURE. THE MAINTENANCE CONTRACTOR SUCCESSFULLY CALIBRATED AND RESET THE RELIEF VALVE BY TESTING IT THREE (3) TIMES TO RELIEVE AT 580 PSIG. THE RELIEF VALVE WAS RESEALED AND RETURNED TO SERVICE.
2021-02-26 10:37 | NO | NO | GG (Gas Gathering) | 20170093 | 30452 | 2017-10-19 10:02 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2017-09-11 16:50 | 2017 |  |  | 28.6954 | -91.0028 | 1190555 | 2017-09-16 15:52 |  | NATURAL GAS |  | 237 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-09-13 17:05 | 2017-09-15 12:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-09-11 16:50 | 2017-09-15 12:00 | OFFSHORE | [28 empty] | 48 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SS | 158 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 10 |  | 0.365 | 35000 | API-5LX | SEAMLESS |  | UNKNOWN | COAL TAR | [28 empty] | 1963 | 1963 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 200 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 781 | 715.290865384615 | 81000 | 86154.4090403853 | 5000 | 5318.17339755465 | 0 | 0 |  |  | 86781 | 42729.9035299755 | 92187.8733033246 | [8 empty] | 526 |  | 1440 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | AUTOMATIC | 116107 | NO | [5 empty] | YES | UPSTREAM CONNECTION OF PIPELINE IS SUBSEA WITH NO PIGGING FACILITIES. | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | SHANE FRASIER | PIPELINE SAFETY ENGINEER | shane.frasier@williams.com | 713-215-3051 |  |  |  |  | LARRY LEGENDRE | PIPELINE SAFETY MANAGER | 7132152733 | larry.d.legendre@williams.com | 9/11/2017 WGP WAS NOTIFIED BY THIRD PARTY THAT BUBBLES WERE PRESENT IN SHIP SHOAL BLOCK 158. 9/13/2017 OPERATIONS INVESTIGATED AND DETERMINED THAT BUBBLES WERE LIKELY COMING FROM THE WGP 10' PIPELINE. THE SECTION OF 10' PIPELINE WAS ISOLATED. 9/15/2017 A DIVE BOAT WAS DISPATCHED AND UPON ARRIVING ON SITE TO INVESTIGATE THE LEAK A SECOND SET OF BUBBLES WERE DISCOVERED. DIVERS INVESTIGATED AND DETERMINED THAT BOTH LEAKS WERE ON THE WGP 10' PIPELINE. THE PIPELINE PRESSURE WAS REDUCED AND CLAMPS WERE INSTALLED. THE FIRST LEAK OCCURRED AT M.P. 17.029 AND THE SECOND LEAK OCCURRED AT M.P. 17.444. 9/15/2017 IT WAS DETERMINED THAT THE COST OF THE RESPONSE AND THE REPAIR WOULD EXCEED THE $50K THRESHOLD. NRC WAS NOTIFIED. 9/28/2017 THE PIPELINE REMAINS IDLE WITH MINIMAL PRESSURE. OPERATIONS AND CYPRESS DIVISION ARE WORKING TO ABANDON THE LINE. 10/19/2017 AT THE REQUEST OF BRIAN PIERZINA, PHMSA AID, THIS REPORT HAS BEEN SPLIT INTO TWO SEPARATE REPORTS DUE TO THE FACT THAT THERE WERE TWO LEAKS. THIS SUPPLEMENTAL REPORT CORRESPONDS TO THE LEAK AT M.P. 17.444. GAS VOLUME REPORTED ABOVE IS THE BEST ESTIMATE FOR THAT LOCATION ONLY. 6/5/2018 AS OF THIS DATE, THERE HAS BEEN NO CHANGE TO THE OPERATIONAL STATUS OF THIS PIPELINE. IT REMAINS ISOLATED WITH MINIMAL PRESSURE. WE ARE WORKING WITH OUR PRODUCER PARTNERS AS WELL AS THE OTHER REGULATORY AGENCIES FOR APPROVAL TO ABANDON THE LINE. THE FINAL ABANDONMENT IS SLATED TO TAKE PLACE IN 3Q 2019. AT THE REQUEST OF BRIAN PIERZINA, WE HAVE UPDATED THE "FACILITY RESTART" DATE TO 9/15/2017 AS THAT WAS THE POINT IN WHICH ACTIVITIES ASSOCIATED WITH THE RELEASE EVENT WERE ESSENTIALLY CONCLUDED. THIS REPORT WILL NOW BE MARKED AS "FINAL".
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170094 | 30875 | 2017-10-20 13:48 | SUPPLEMENTAL | 8310 | IROQUOIS GAS CORP | ONE CORPORATE DRIVE, SUITE 600 | SHELTON | CT | 06484 | 2017-09-22 14:25 | 2017 |  |  | 44.8393 | -75.2529 | 1191219 | 2017-09-22 15:05 |  | NATURAL GAS |  | 140 | 0.1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-09-22 14:35 | 2017-09-22 18:16 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 10 | 2017-09-22 14:25 | 2017-09-22 14:25 | ONSHORE | NY | 13694 | WADDINGTON | ST. LAWRENCE | MILEPOST | 1.28MP | MAINLINE VALVE #1 | MAINLINE VALVE #1 ABOVEGROUND POWER GAS | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | INSTRUMENTATION | [38 empty] | 2017 |  | CARBON STEEL |  | OTHER | [8 empty] | INTENTIONAL RELEASE THROUGH THE VENTS DURING VALVE ACTUATION AND THROUGH BLOW OFF VALVES WHILE PURGING. | CLASS 1 LOCATION | NO |  | 785 |  | NO | NO | NO |  | 0 | 0 | 1 | 1.06363467951093 | 395 | 361.766826923077 | 480000 | 510544.646165246 | 5000 | 5318.17339755465 | 0 | 0 |  |  | 485396 | 237170.194497784 | 516225.650024404 | [8 empty] | 1000 |  | 1440 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 20 | NO | [5 empty] | YES | SECTION OF PIPE WAS THE 2" POWER GAS AND INSTRUMENTATION TUBING. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT OCCURRED DURING LOCAL FIELD OPERATING PERSONNEL PERFORMING WORK ON SITE. THE CONTROLLER DID NOT HAVE THE ABILITY TO CONTROL THE VALVE ON THE 2" POWER GAS PIPING. | [12 empty] | YES | 2 | 0 | YES | 5 | 0 | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | ACCIDENTAL IGNITION DURING PURGING ACTIVITIES |  |  |  | YES | SPECIFIC CAUSE OF THE SOURCE OF IGNITION COULD NOT BE POSITIVELY DETERMINED. | COMMISSIONING | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | MICHAEL KINIK | DIRECTOR ENGINEERING SERVICES | michael_kinik@iroquois.com | 203-925-7223 | 203-925-7213 |  |  |  | PAUL AMATO | VP ENGINEERING OPERATIONS AND EHS | 203-925-7267 | paul_amato@iroquois.com | ON SEPTEMBER 22, 2017 AT APPROXIMATELY 02:25PM, A RELEASE OF GAS IGNITED DURING THE OPERATION OF A 12 INCH PLUG VALVE AT MLV1 IN WADDINGTON, NY. THE FIRE RESULTED IN ONE EMPLOYEE BEING TREATED FOR BURNS AT A NEARBY HOSPITAL AND RELEASED THAT DAY. IN ADDITION TWO VALVE ACTUATORS AND OTHER SMALL EQUIPMENT WAS DAMAGED AFTER INVESTIGATING, THE SOURCE OF THE INITIATING SPARK THAT IGNITED THE VENTING GAS WAS NOT ABLE TO BE POSITIVELY IDENTIFIED. IN ADDITION, THERE WAS NO INDICATIONS OF A COMPONENT FAILURE THAT COULD HAVE LEAD TO A SPARK. ALL REGULATORS AND RELIEF VALVES TESTED TO BE IN WORKING ORDER POST-INCIDENT. IROQUOIS IS UPDATING ITS OPERATING PROCEDURES AND ACTUATOR DESIGN SPECIFICATIONS TO ENSURE THE POSSIBLE CONTRIBUTING CAUSES ARE ADDRESSED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170095 | 30234 | 2017-10-23 09:21 | SUPPLEMENTAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2017-10-02 03:35 | 2017 |  |  | 32.9607 | -91.8533 | 1192048 | 2017-10-02 04:32 |  | NATURAL GAS |  | 51184 | 239 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | ISOLATED CHECK VALVE & EVACUATE REMAINING GAS; PIPELINE WAS UNAFFECTED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-10-02 03:35 | 2017-10-02 04:10 | ONSHORE | LA | 71220 | BASTROP | MOREHOUSE | MILEPOST | 55.73 | BASTROP COMPRESSOR STATION | MLS | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | MAINLINE | CHECK |  | WHEATLEY CHECK VALVE |  |  |  | 1997 | 1997 | CARBON STEEL |  | LEAK |  |  | OTHER | COMPONENT FAILURE | [5 empty] | CLASS 1 LOCATION | NO |  | 589 |  | NO | NO | NO |  | 9438 | 10038.5841052242 | 710 | 755.18062245276 | 152016 | 139226.192307692 | 176700 | 187944.247869581 | 500 | 531.817339755465 | 0 | 0 |  |  | 339364 | 235812.225425371 | 338496.022244706 | [8 empty] | 800 |  | 810 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [5 empty] | YES | [29 empty] | YES | FATIGUE ASSOCIATED WITH HOLDING PIN IN CLAPPER OF CHECK VALVE | [161 empty] | SHANNON MATTINGLY | PA OQ AND EVENT SUPPORT PROGRAM LEADER | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | DARRAL WARD | MANAGER PIPELINE SAFETY | 2706886356 | darral.ward@bwpmlp.com | TEXAS GAS'S CONTROL CENTER RECEIVED NOTIFICATION FROM THE PUBLIC THAT A LOUD NOISE WAS COMING FROM ITS BASTROP COMPRESSOR STATION. WHEN LOCAL PERSONNEL ARRIVED AT THE SITE, THEY DISCOVERED GAS BLOWING FROM A 26" CHECK VALVE LOCATED AT THE T3 TURBINE PIPING. AFTER SECURING THE AREA, FURTHER EXAMINATION REVEALED THAT BOLTS ON THE CHECK VALVE SHAFT WERE BROKEN. THE CAUSE IS CURRENTLY UNDER INVESTIGATION. 3-5-18 ROOT CAUSE WAS CONFIRMED AS FATIGUE OF BOLTS ON CHECK VALVE SHAFT FAILED. 4-25-18 UPDATED WITH FINAL COSTS AND SUBMITTED FINAL REPORT.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20170096 | 17570 | 2017-10-25 16:11 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2017-09-25 15:46 | 2017 |  |  | 28.471 | -90.8903 | 1191454 | 2017-09-25 16:13 |  | NATURAL GAS |  | 115 | 2145 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-09-25 17:45 | 2017-09-29 10:25 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-09-25 15:46 | 2017-09-27 08:00 | OFFSHORE | [28 empty] | 125 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SS | 232 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 |  | 0.438 | 42000 | API-5LX | SEAMLESS |  | KAISER | ASPHALT | [28 empty] | 1983 | 1983 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 200 |  | NO | NO | NO |  | 0 | 0 | 7079 | 7529.46989625787 | 373 | 341.617788461538 | 17236 | 18332.8073360504 | 117476 | 124951.547610226 | 0 | 0 |  |  | 142164 | 69581.6957749665 | 151155.442630996 | [8 empty] | 750 |  | 1440 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | AUTOMATIC | 33053 | NO | [5 empty] | YES | UPSTREAM END OF PIPELINE IS SUB-SEA WITH NO PIGGING FACILITIES. | NO | [6 empty] | OFFSHORE GATHERING | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | INSPECTED BY DIVERS. DISCOVERED PINHOLE LEAK. |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | SHANE FRASIER |  | shane.frasier@williams.com | 713-215-3051 |  |  |  |  | LARRY LEGENDRE | PIPELINE SAFETY MANAGER | 7132152733 | larry.d.legendre@williams.com | 9/25/2017 A THIRD PARTY HELICOPTER SPOTTED THE BUBBLES AND REPORTED THEM TO WGP PIPELINE CONTROL. PIPELINE CONTROL NOTIFIED WGP OPERATIONS. OPERATIONS FLEW OUT TO VERIFY COORDINATES. THE BUBBLES WERE IN THE VICINITY OF A WGP 16' PIPELINE. THE WILLIAMS SECURITY OPERATIONS CENTER WAS NOTIFIED OF THE POTENTIAL LEAK. THE 16' SECTION OF PIPELINE WAS ISOLATED AND PRODUCTION WAS SHUT IN. 9/26/2017 THE PRESSURE WAS REDUCED IN THAT SECTION OF 16'. DIVE BOAT WAS DISPATCHED AND DIVERS CONFIRMED THE LEAK WAS THE WGP 16' PIPELINE. THE SOC WAS NOTIFIED OF A CONFIRMED LEAK AND THEY NOTIFIED THE NRC. 9/27/2017 WGP OPERATIONS ACQUIRED A 16' PLIDCO CLAMP THAT WAS INSTALLED THE NEXT DAY. 9/29/2017 PIPELINE WAS PRESSURIZED TO CHECK FOR LEAKS. NO LEAKS WERE FOUND. THE SECTION OF WGP16' PIPELINE WAS RETURNED TO SERVICE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170097 | 17480 | 2017-10-26 15:46 | ORIGINAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2017-09-27 16:14 | 2017 |  |  | 37.6821 | -98.4682 | 1191957 | 2017-09-30 12:37 |  | NATURAL GAS |  | 100 | 1000 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-09-27 17:30 | 2017-09-29 17:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-09-27 16:14 | 2017-09-27 16:14 | ONSHORE | KS | 67035 | Not Within a Municipality | PRATT | MILEPOST | 36.97 | CUNNINGHAM UNDERGROUND STORAGE V1030 | KS-097 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 79 |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 2.375 |  | 0.218 | 35000 | 5LX | SEAMLESS |  | UNK | COAL TAR | [28 empty] | 1978 | 1978 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 55 |  | NO | NO | NO |  | 0 | 0 | 2880 | 3063.26787699148 | 288 | 263.769230769231 | 95982 | 102089.783808818 | 100 | 106.363467951093 | 0 | 0 |  |  | 99250 | 48590.3105566164 | 105523.18438453 | [8 empty] | 755 |  | 1000 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS GRADE 3 LEAK WAS DISCOVERED BY OPERATIONS PERSONNEL CONDUCTING A ROUTINE GAS LEAK DETECTION SURVEY. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  | YES | YES | [5 empty] | YES | CAUSE IS OUR BEST GUESS AS THE PIPE WAS ABANDONED IN PLACE WITHOUT AN EXAMINATION. |  |  |  |  | YES | BEST ESTIMATE AS THE PIPE WAS ABANDONED IN PLACE WITHOUT AN EXAMINATION. | YES | NO | NOT APPLICABLE - NOT MAINLINE PIPE | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | JOHN A GORMLEY | SR. CORROSION SPECIALIST | john.gormley@nngco.com | 402-398-7494 |  |  |  |  | THOMAS CORRELL | VP PIPELINE SAFETY AND RISK | 402-398-7715 | thomas.correll@nngco.com | ON SEPTEMBER 27, 2017 WHILE CUNNINGHAM PERSONNEL WERE PERFORMING THE ROUTINE ANNUAL GAS LEAK SURVEY THEY FOUND ELEVATED GAS LEVELS IN THE AREA OF THE MAINLINE DRIP IDENTIFIED AS V-1030. FURTHER INVESTIGATION FOUND THAT THE 2-INCH DRAIN LINE FOR V-1030 HAD BEEN LEAKING. THE LINE WAS REMOVED FROM SERVICE AND ABANDONED. A NEW LINE WAS INSTALLED ON SEPTEMBER 30, 2017. THE ABANDONED 2-INCH PIPE WAS NEVER EXCAVATED OR EXAMINED FOR THE EXACT CAUSE OF THIS GRADE 3 LEAK. WE SUSPECT INTERNAL CORROSION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170098 | 17509 | 2017-10-31 17:55 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2017-10-04 17:04 | 2017 |  |  | 41.501 | -75.0669 | 1192312 | 2017-10-04 18:03 |  | NATURAL GAS |  | 9242 | 149 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-10-04 18:26 | 2017-10-07 20:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 130 | 2017-10-04 17:20 | 2017-10-04 17:20 | ONSHORE | PA | 18428 | Not Within a Municipality | PIKE | SURVEY STATION NO. | STATION 69+10 | LINE 300-1 | VALVE SEGMENT 323-1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 24 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 |  | 0.375 | 52000 | API - 5LX | SEAMLESS |  | NATIONAL TUBE | COAL TAR | [28 empty] | 1955 | 1955 | CARBON STEEL |  | MECHANICAL PUNCTURE | 2.2 | 7 | [7 empty] | CLASS 2 LOCATION | NO |  | 566 |  | NO | NO | NO |  | 0 | 0 | 440 | 467.999258984809 | 27303 | 25005.8725961538 | 55000 | 58499.9073731012 | 500 | 531.817339755465 | 0 | 0 |  |  | 83243 | 53236.6668700302 | 84505.5965679953 | [8 empty] | 973 |  | 1170 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 7773 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EMPLOYEE AT NEARBY COMPRESSOR STATION IMMEDIATELY HEARD THE NATURAL GAS BLOWING FROM THE PIPELINE; | [12 empty] | NO |  |  | YES | 7 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [10 empty] | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 20171593582 | ONLY ONE SYSTEM; PENNSYLVANIA 811; NOTE: PIPELINE LOCATED BY PIPELINE OWNER / EMPLOYEE; PIPELINE STRUCK BY 2ND PARTY CONTRACTOR OF PIPELINE OWNER; | UTILITY OWNER | YES | YES | NO |  | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO MAINTAIN THE MARKS | [263 empty] | WILLIAM MARTIN MULLER | SPECIALIST-PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205 325 3863 | 205 325 3592 |  |  |  | REJI GEORGE | DIRECTOR NG COMPLIANCE CODES AND STANDARDS | 713 420 5433 | reji_george@kindermorgan.com | 10/04/2017; BETWEEN 17:04 HOURS AND 17:20 HOURS, STATION 323A COMPRESSOR STATION OPERATOR HEARD THE SOUND OF NATURAL GAS BLOWING NEARBY AND CONTACTED GAS CONTROL AND OPERATIONS SUPERVISION; OPERATIONS INSTRUCTED EMPLOYEES TO BEGIN CLOSING MAIN LINE VALVES AS PRESSURE DROP WAS BEGINNING. OPERATIONS DISPATCHED MORE EMPLOYEES TO CLOSE ADDITIONAL MAIN LINE VALVES AND TGP BEGAN NOTIFYING CUSTOMERS THE PIPELINE PRESSURE WOULD DECREASE; THE MAIN LINE VALVES ON LINE 300-1 AND LINE 300-2 WERE CONFIRMED CLOSED; AND IT WAS VERIFIED THE GAS RELEASE WAS FROM LINE 300-1 AND DETERMINED THE CAUSE OF RELEASE WAS BY 2ND PARTY DAMAGE; VALVE SECTION 323-1 OF LINE 300-1 IS SECURED; OPERATIONS CHECKED LINE 300-2 FOR IMPACT; OPERATIONS RETURNED LINE 300-2 TO SERVICE; DURING THE EVENT, IT WAS LEARNED THE LOCAL VOLUNTEER FIRE DEPARTMENT CLOSED SOME ROADS; THROUGH LOCAL NEWS MEDIA, IT WAS LATER LEARNED PIKE COUNTY EMA EVACUATED APPROXIMATELY 130 PERSONS; KINDER MORGAN BEGAN INTERNAL INVESTIGATION OF THE EVENT IMMEDIATELY ON 10/05/2017; IT WAS FOUND THE 2ND PARTY HEAVY EQUIPMENT STRUCK THE LINE 300-1 WHILE PERFORMING TASKS FOLLOWING THE REMOVAL OF ROAD BORE TRENCH BOXES RESULTING IN A PUNCTURE OF THE PIPELINE; PIPELINE DAMAGE WAS REPAIRED BY PIPE REPLACEMENT; VALVE SECTION 323-1 OF LINE 300-1 WAS RETURNED TO SERVICE ON 10/07/2017 AT 20:00 HOURS; THERE WAS NO INTERRUPTION OF SERVICE TO TGP CUSTOMERS; ADDITIONAL INFORMATION: PIR OF THE PIPELINE INCLUDING KINDER MORGAN BUFFER IS 606 FEET; ONE CALL TICKET NUMBERS FOR THE CONSTRUCTION PROJECT ARE 20171593582 AND 20171640580; ALL TIMES IN THIS REPORT ARE EASTERN TIME ZONE;
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170099 | 32053 | 2017-10-31 19:37 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2017-10-01 10:42 | 2017 |  |  | 34.7428 | -116.6735 | 1192024 | 2017-10-01 12:52 |  | NATURAL GAS |  | 29500 | 38000 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-10-01 10:42 |  | YES |  |  |  | YES |  |  |  |  | YES | [6 empty] | 0 | 2017-10-01 10:42 | 2017-10-01 10:42 | ONSHORE | CA | 92365 | NEWBERRY SPRINGS | SAN BERNARDINO | MILEPOST | 129.6 | 235 W | 9A413550F46440FFA9664F10F9F8A177 | YES | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 40 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 |  | 0.375 | 52000 | API 5LX | DSAW |  | CONSOLIDATED WESTERN STEEL | COAL TAR | [28 empty] | 1957 | 1956 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 732 | 30 |  | CLASS 1 LOCATION | NO |  | 633 |  | NO | NO | NO |  | 275500 | 293031.354205261 | 116246 | 123643.276954428 | 90243 | 82650.4399038462 | 1499500 | 1594920.20192664 | 40000 | 42545.3871804372 | 1225000 | 1302952.48240089 | FIRE SUPPRESSION COST AND L235 INVESTIGATION CHARGES |  | 3246489 | 1626681.5975103 | 3439743.1425715 | [8 empty] | 907 |  | 936 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | AUTOMATIC | 59740 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 7 | 0 | YES | 3 | 0 | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION | [6 empty] | YES | GENERAL |  |  | YES | YES |  |  | YES | YES | 1959 | NO | YES | YES |  |  |  | 2017 |  |  |  | NO | [190 empty] | YES | [6 empty] | YES | [50 empty] | COMBINATION TOOL | 2014 |  |  |  |  | NO |  |  | NO | [13 empty] | NO | [63 empty] | ALI MATIN | PIPELINE SAFETY AND COMPLIANCE ADVISOR | amatin@semprautilities.com | 909-919-0463 |  |  |  |  | TROY BAUER | PIPELINE SAFETY AND COMPLIANCE MANAGER | 909-376-7208 | tbauer@semprautilities.com | ON OCTOBER 1, 2017, SOCALGAS BECAME AWARE OF A PRESSURE DROP ALONG A TRANSMISSION LINE 235. SOCALGAS CREW DETERMINED THAT THERE WAS A RUPTURE, ISOLATED THE LINE WITH A COMBINATION OF AUTOMATIC AND REMOTELY CONTROLLED VALVES, AND REMOVED THE GAS WITHIN THE LINE. NO FURTHER DAMAGES OR INJURIES RESULTED FROM THIS INCIDENT. THE INVESTIGATION OF THE CAUSE OF THE RUPTURE IS COMPLETED. THIS INCIDENT WAS REPORTED TO THE DOT AND THE CPUC DUE TO THE RELEASE OF GAS AND THE ESTIMATED DAMAGE EXCEEDING $50,000. THE FINALIZED COST ASSOCIATED TO THIS INCIDENT WILL BE UPDATED ONCE AVAILABLE. THE 48-HOUR UPDATE WAS MADE TO THE DOT PER NRC #1192187. FOR ANY FURTHER QUESTIONS, PLEASE CONTACT IK SONG AT (818) 279-5388. UPDATE 5/01/2019: UPDATED YTD TOTAL COST INFORMATION (FINALIZED). FOR ANY FURTHER QUESTIONS, PLEASE CONTACT ALI MATIN AT (909) 919-0463.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170100 | 17502 | 2017-11-01 18:59 | SUPPLEMENTAL FINAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2017-10-04 15:19 | 2017 |  |  | 38.5373 | -98.7971 | 1192301 | 2017-10-04 16:04 |  | NATURAL GAS |  | 1488 | 12014 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-10-04 19:01 | 2017-10-24 17:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-10-04 15:19 | 2017-10-04 15:19 | ONSHORE | KS | 67544 | Not Within a Municipality | BARTON | MILEPOST | MP 252 | AMARILLO #2 LINE | CS 104 - SALINE RIVER | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 26 |  | 0.25 | 52000 | API-5LX | FLASH WELDED |  | A O SMITH | COAL TAR | [28 empty] | 1947 | 1947 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 479 |  | NO | NO | NO |  | 0 | 0 | 33647 | 35788.1160615043 | 4174 | 3822.82211538462 | 62100 | 66051.7135976287 | 250 | 265.908669877733 | 0 | 0 |  |  | 100171 | 50832.5214092827 | 105928.560444395 | [8 empty] | 489 |  | 712 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | AUTOMATIC | 92029 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | EMPLOYEES SURVEYING THE PIPELINE FOUND THE LEAK |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE UNINTENTIONAL GAS RELEASE WAS BY A LEAK FOUND BY EMPLOYEES | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING | [6 empty] | YES | DISBONDED COATING; |  |  | YES |  |  |  | YES | YES |  | YES | YES | YES | YES |  |  | 2017 | 2014 |  |  | NO | [190 empty] | YES | YES | [6 empty] | 2017 | [55 empty] | YES | 1991 | 927 | Yes, but the point of the Accident was not identified as a dig site |  | 2014 | [11 empty] | NO | [63 empty] | WILLIAM MARTIN MULLER | SPECIALIST PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205 325 3863 | 205 325 3592 |  |  |  | REJI GEROGE | DIRECTOR NG COMPLIANCE CODES AND STANDARDS | 713 420 5433 | reji_george@kindermorgan.com | 10/04/2017; EMPLOYEE PERFORMING CIVIL SURVEY TASKS ON NGPL AMARILLO #2 LINE FOUND THE LEAK BY OBSERVING A SMALL AMOUNT OF BLOWING SOIL; PIPELINE LEAK CONFIRMED WITH NATURAL GAS DETECTION EQUIPMENT. PIPELINE VALVE SECTION WAS ISOLATED, BLOWN DOWN AND SECURED SAME DAY. EXCAVATION OF THE LEAK SITE BEGAN ON 10/10/2017. REPAIR OF THE PIPELINE BY PIPE REPLACEMENT WAS COMPLETED ON 10/23/2017. THE PIPELINE VALVE SECTION WAS RETURNED TO SERVICE ON 10/24/2017. ALL TIMES IN THIS REPORT ARE CENTRAL TIME ZONE. PIR = 479 FEET; PIR WITH KM BUFFER = 519 FEET;
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170102 | 17489 | 2017-11-13 16:16 | SUPPLEMENTAL FINAL | 18152 | SEA ROBIN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2017-10-17 16:30 | 2017 |  |  | 28.2066 | -91.7014 | 1193533 | 2017-10-17 17:44 |  | NATURAL GAS |  | 300 | 2093 | 0.1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-10-17 17:30 | 2017-10-24 06:23 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-10-17 16:30 | 2017-10-19 10:32 | OFFSHORE | [28 empty] | 260 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EUGENE ISLAND | 338 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12 |  | 0.438 | 52000 | UNKNOWN | OTHER | UNKNOWN | UNKNOWN | OTHER | MASTIC AND CONCRETE | [27 empty] | 1973 | 1973 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 318 |  | NO | NO | NO |  | 0 | 0 | 6971 | 7414.59735087069 | 999 | 914.949519230769 | 300000 | 319090.403853279 | 75000 | 79772.6009633198 | 0 | 0 |  |  | 382970 | 187440.709485529 | 407192.5516867 | [8 empty] | 800 |  | 1306 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 30729 | NO | YES |  | YES |  |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | PRODUCER PLATFORM PERSONNEL |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS TOO SMALL FOR SCADA TO DETECT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | PINHOLE LEAK | YES | [7 empty] | YES | LOW FLOW CONDITIONS. |  |  |  |  | YES | 6 O'CLOCK | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713.857.5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | 713.857.5479 | nathan.hlavaty@energytransfer.com | THIS SUPPLEMENTAL WAS CREATED TO FURTHER CLARIFY AND CORRECT THE ITEMS NOTED BELOW. PART A QUESTION 4. TIME CORRECTED. QUESTION 5. COORDINATES WERE CORRECTED. QUESTION 7. TIME CORRECTED. PART B QUESTION 19A. TIME CORRECTED. PART C QUESTION 3A. CLARIFIED THE NOMINAL PIPE SIZE TO 12".
2021-02-26 10:37 | YES | NO | UNGS (Underground Natural Gas Storage) | 20170103 | 30756 | 2017-11-15 08:08 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2017-10-17 10:55 | 2017 |  |  | 39.64 | -79.2857 | 1193490 | 2017-10-17 11:23 |  | NATURAL GAS |  | 0.714 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-10-19 14:00 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-10-17 08:30 | 2017-10-17 08:30 | ONSHORE | MD | 21520 | Not Within a Municipality | GARRETT | MILEPOST | MILEPOST0.444 | ACCIDENT STORAGE FIELD | 6-INCH 49-B-18 (ACCIDENT WELL 67) | NO | PIPELINE RIGHT-OF-WAY | BELOWGROUND STORAGE OR ABOVEGROUND STORAGE VESSEL, INCLUDING ATTACHED APPURTENANCE |  |  |  |  | NO | [22 empty] | INTERSTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | UNDERGROUND GAS STORAGE OR CAVERN | [38 empty] | 1975 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 247 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 2 | 1.83173076923077 | 300000 | 319090.403853279 | 0 | 0 | 0 | 0 |  |  | 300002 | 146472.814192222 | 319092.235584048 | [8 empty] | 3077 |  | 3550 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATOR ON SITE OF INCIDENT AT THE TIME THE INCIDENT WAS DISCOVERED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | VALVE THREADS | [19 empty] | YES | ADDITIONAL FACTORS NOT YET DETERMINED | [161 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | dwayne.teschendorf@enbridge.com | 713-627-5573 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | ON OCTOBER 17, 2017 AN ENBRIDGE COMPANY EMPLOYEE RESPONDED TO NATURAL GAS RELEASE ON ABOVE GROUND FACILITIES ASSOCIATED WITH A ACCIDENT WELL 67 ADJACENT TO 6-INCH LINE 49-B-18 IN GARRETT COUNTY, MARYLAND. THE EMPLOYEE ATTEMPTED TO STOP THE NATURAL GAS RELEASE BY TIGHTENING A BLEEDER VALVE ON A TUBING HEAD. THE BLEEDER VALVE SNAPPED OFF DURING THE PROCESS. THE STORAGE WELL REMAINS ISOLATED FROM THE PIPELINE UNTIL REPAIRS CAN BE SCHEDULED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170104 | 17488 | 2017-11-15 14:58 | ORIGINAL FINAL | 18152 | SEA ROBIN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2017-10-19 15:02 | 2017 |  |  | 28.4306 | -91.0344 | 1193740 | 2017-10-19 15:21 |  | NATURAL GAS |  | 1820 | 25746 | 0.1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-10-23 08:00 | 2017-11-09 10:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-10-19 15:02 | 2017-10-31 09:15 | OFFSHORE | [28 empty] | 144 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SHIP SHOAL | 241 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | FLANGE ASSEMBLY | [38 empty] | 1992 |  | CARBON STEEL |  | LEAK |  |  | OTHER | RTJ RING | [5 empty] | CLASS 1 LOCATION | NO |  | 318 |  | NO | NO | NO |  | 0 | 0 | 84961 | 90367.4660059281 | 6006 | 5500.6875 | 2600 | 2765.45016672842 | 75000 | 79772.6009633198 | 0 | 0 |  |  | 168567 | 85071.0072943683 | 178406.204635976 | [8 empty] | 1000 |  | 1200 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 17600 | NO | YES | [6 empty] | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | PRODUCER PLATFORM PERSONNEL |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS TOO SMALL FOR SCADA TO DETECT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | OTHER | FLANGE RTJ RING | [16 empty] | YES | BREAK DOWN OF RTJ FLANGE GASKET DUE TO LIQUID ACCUMULATION. | [161 empty] | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713.857.5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | 713.857.5479 | nathan.hlavaty@energytransfer.com | AN NRC NOTIFICATION (NRC# 1193740) WAS MADE BASED ON AN OFFSHORE LEAK NEAR OUR FACILITIES LOCATED IN SHIP SHOAL 241 ON 10/19/17. LINE WAS ISOLATED AND DEPRESSURIZED UNTIL REPAIRS COULD BE MADE. THE 48 HR NRC# 1193922 REPORT WAS MADE ON 10/21. OFFSHORE WEATHER CONDITIONS CAUSED A DELAY IN DETERMINING THE SOURCE OF THE LEAK AND THE REPAIRS. A NEW NRC# 1194755 NOTIFICATION WAS MADE IDENTIFYING SEA ROBIN AS THE RESPONSIBLE PARTY ON 10/31, THE 48 HR NRC# 1194979 WAS MADE ON 11/02/17. THE CENTRALIZED PHMSA ACCIDENT INVESTIGATION DIVISION WAS PROVIDED DAILY UPDATES FROM 10/19/17 THROUGH THE RESTART OF THE LINE ON 11/09/17.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170105 | 30189 | 2017-11-16 16:56 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2017-10-28 14:45 | 2017 |  |  | 36.7005 | -121.2113 | 1194547 | 2017-10-28 15:57 |  | NATURAL GAS |  | 28500 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELIEF VALVE ACTIVATION, NO OVERPRESSURE EXCURSION | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-10-28 14:45 | 2017-10-28 15:10 | ONSHORE | CA | 95075 | PAICINES | SAN BENITO | MILEPOST | 436.85 | L300A | 7947879 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2004 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE ACTIVATION | CLASS 1 LOCATION | NO |  | 589 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 85500 | 78306.4903846154 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 85500 | 81183.8942307692 | 78306.4903846154 | [8 empty] | 602 |  | 631 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE RELIEF VALVE ACTIVATED BELOW THE SET POINT. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | PIPELINE OR EQUIPMENT OVERPRESSURED | INCORRECT OPERATION | PIPELINE/EQUIPMENT OVERPRESSURED | [204 empty] | PIPELINE OR EQUIPMENT OVERPRESSURED | [5 empty] | YES |  |  | NON-ROUTINE OPERATING CONDITIONS (ABNORMAL OPERATIONS OR EMERGENCIES) | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | ENZA BARBATO | SENIOR PROGRAM MANAGER | e1bo@pge.com | 925-357-7889 |  |  |  |  | SUSIE RICHMOND | MANAGER OF GAS OPS COMPLIANCE AND RISK | 925-786-0267 | gsr8@pge.com | ON 10/28/17 AT 14:45, RELIEF VALVE M AT PRESSURE-LIMITING STATION 6AB ON L300A MP 436.85 ACTIVATED AND BEGAN VENTING GAS. THE RELIEF VALVE CLOSED AT 15:53. THE MAOP OF THIS SECTION OF L300A IS 631 PSIG AND THE RELIEF VALVE OPENED AT 602 PSIG. THE FIRE DEPARTMENT RESPONDED TO THE RELIEF VALVE ACTIVATION. THE INITIAL INVESTIGATION DETERMINED THE RELIEF VALVE ACTIVATED BELOW THE SET POINT OF 615 PSIG. THIS INCIDENT IS BEING REPORTED DUE TO THE EARLY ACTIVATION OF THE RELIEF VALVE AND UNINTENTIONAL RELEASE OF GAS OVER 3MMCF. THE INCIDENT WAS DUE TO OPERATOR ERROR. THE OPERATOR INPUT A REGULATION SET POINT MEANT FOR PLS4 INTO PLS6 CAUSING THE PRESSURE TO RISE AND THE OVER PRESSURE PROTECTION RELIEF VALVE TO ACTIVATE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170107 | 30198 | 2017-11-17 09:16 | SUPPLEMENTAL FINAL | 26330 | ENABLE OKLAHOMA INTRASTATE TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2017-10-21 00:15 | 2017 |  |  | 35.3078 | -99.2738 | 1193884 | 2017-10-21 02:28 |  | NATURAL GAS |  | 10000 | 7000 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-10-21 00:45 | 2017-11-07 11:00 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 0 | 2017-10-21 00:15 | 2017-10-21 00:26 | ONSHORE | OK | 73626 | CANUTE | WASHITA | MILEPOST | LINE 25 | LINE 25 | LINE 25 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | YES | [6 empty] | YES | UNCASED | GEORGE CREEK | UNKNOWN | SHORELINE/BANK/MARSH CROSSING | [11 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.257 | 65000 | UNKNOWN | LONGITUDINAL ERW - HIGH FREQUENCY |  | STUPP | EPOXY | [28 empty] | 1980 | 1980 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 14 | 0.5 |  | CLASS 1 LOCATION | NO |  | 478 |  | NO | NO | NO |  | 17000 | 18081.7895516858 | 21277 | 22630.9550759541 | 30396 | 27838.6442307692 | 550000 | 584999.073731011 | 5000 | 5318.17339755465 | 0 | 0 |  |  | 623673 | 318521.003637387 | 658868.635986975 | [8 empty] | 750 |  | 1200 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 67196 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL ROOM DID NOT CONTRIBUTE TO THE INCIDENT | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES | [7 empty] | YES | EXCESSIVE BENDING LOADS | [13 empty] | YES |  |  |  | YES | [58 empty] | YES | [6 empty] | YES | [50 empty] | COMBINATION TOOL | 2017 |  |  |  |  | NO |  |  | NO | [13 empty] | YES | 2017 |  | 2017 |  |  |  |  | YES |  | YES | [53 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | ON OCTOBER 21, 2017 AT 00:15 ENABLE OKLAHOMA INTRASTATE TRANSMISSION LINE 25 EXPERIENCED A FAILURE IN WASHITA COUNTY OKLAHOMA. THE FAILURE OCCURRED AT THE GEORGE CREEK CROSSING IN THE SW 1/4 SECTION 25 T10N-R20W. THE FAILED SECTION OF LINE 25 WAS REMOVED AND SENT TO STRESS ENGINEERING SERVICES (SES) FOR METALLURGICAL ANALYSIS. AS OF THE DUE DATE FOR THIS REPORT, ENABLE MIDSTREAM PARTNERS HAS NOT RECEIVED THE RESULTS OF THE SES ANALYSIS FOR LINE 25. THE NRC WAS NOTIFIED ON 10/21/17 (NRC # 1193884). A 48 HR FOLLOW UP CALL WAS PROVIDED TO THE NRC ON 10/23/17 (NRC # 1194020) THE FAILURE INVESTIGATION IS ON-GOING. UPDATE 1/30/2018 A.18 EVACUATED CHANGED FROM 1 TO 0 C.3.B CHANGED .250 TO .257 C.3.E CHANGED LONGITUDINAL ERW - UNKNOWN FREQUENCY TO LONGITUDINAL ERW - HIGH FREQUENCY C.3.F UNKNOWN CHANGED TO STUPP D.7.A CHANGED 20,000 TO 17,000 D.7.B CHANGED 447,718 TO 550,000 D.7.C CHANGED 10,000 TO 5,000 E.5.C CHANGED FROM UNKNOWN TO 67,196 A FAILURE INVESTIGATION IS STILL ON-GOING. UPDATE 4/16/18 G5.1 CHANGED FROM "FIELD EXAMINATION" TO "DETERMINED BY METALLURGICAL ANALYSIS" G5.2 CHANGED FROM OTHER "CONSTRUCTION" TO OTHER "EXCESSIVE BENDING LOADS" G5.4 CHANGED "LACK OF FUSION" TO "MISALIGNMENT" G5.A CHANGED FROM "OTHER - MFL COMBO" TO "COMBINATION TOOL" G8.A CHANGED FROM "NO" TO "YES" "RADIOGRAPHY (2017)" AND "HANDHELD ULTRASONIC TOOL (2017)" THE INVESTIGATION IS COMPLETE. A METALLURGICAL ANALYSIS WAS PERFORMED INCLUDING VISUAL, FRACTOGRAPHIC, AND METALLOGRAPHIC EXAMINATION. VISUAL EXAMINATION REVEALED THAT THE MAJORITY OF THE FRACTURE OCCURRED ALONG THE EDGE OF THE GIRTH WELD IN THE HEAT AFFECTED ZONE. THE PIPES ON BOTH SIDES OF THE GIRTH WELD MEET THE DIMENSIONAL REQUIREMENTS OF API 5L AND NO SIGNIFICANT CORROSION WAS OBSERVED. THE SAMPLE CONTAINED A SAG BEND WHEREBY THE EXTRADOS OF THE BEND COINCIDED WITH THE 6:00 O'CLOCK ORIENTATION. THE FRACTURE PROPAGATED APPROXIMATELY TWO-THIRDS OF THE SAMPLE'S CIRCUMFERENCE AND ARRESTED IN THE BASE MATERIAL. FRACTOGRAPHIC AND METALLOGRAPHIC EXAMINATION REVEALED THAT THE SAMPLE FAILED DUE TO EXCESSIVE BENDING LOADS. THE TRANSITION WELD AND LACK OF PENETRATION DUE TO HIGH-LOW AT THE ROOT OF THE WELD ACTED AS A STRESS CONCENTRATOR AND THE FAILURE ULTIMATELY INITIATED AT THE BASE OF THIS FEATURE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170108 | 17558 | 2017-11-17 09:44 | SUPPLEMENTAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2017-10-10 11:00 | 2017 |  |  | 32.8682 | -94.5431 | 1194155 | 2017-10-24 11:47 |  | NATURAL GAS |  | 296000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | ADJUSTMENT WAS MADE TO BARTON CONTROLLER WHILE ONLINE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-10-17 11:35 | 2017-10-24 10:25 | ONSHORE | TX | 75630 | AVINGER | MARION | MILEPOST | INTERCONNECT | AM 199/AM 47 INTERCONNECT | AM 199/AM 47 INTERCONNECT | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 2007 |  | CARBON STEEL |  | OTHER | [8 empty] | EQUIPMENT FAILURE, MORE SPECIFICALLY THE LOOSE TENSION ON THE CONTROLLER ARM ALLOWING THE SET POINT TO MOVE CAUSING RELIEF VALVE TO VENT. | CLASS 1 LOCATION | NO |  | 123 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 905801 | 829591.78125 | 500 | 531.817339755465 | 0 | 0 | 0 | 0 |  |  | 906301 | 860319.586941923 | 830123.598589756 | [8 empty] | 496 |  | 500 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A RELIEF VALVE WAS FOUND BLOWING AND AFTER THE STATION WAS SECURED IT WAS DETERMINED THAT THE SETPOINT HAD BEEN RAISED LOCALLY; THERE IS NO SCADA DATA AT THIS STATION. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | O&M TECHNICIAN DID NOT VERIFY THE SPRING ON THE CONTROLLER ARM WAS TIGHTENED DURING ANNUAL TESTING. |  |  | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | ON 10/24/2017 AN ENABLE MIDSTREAM EMPLOYEE DISCOVERED A RELIEF VALVE BLOWING AT THE AM-199 TO AM-47 INTERCONNECT FACILITY LOCATED IN THE RURAL PART OF MARION COUNTY. THE FACILITY IS APPROXIMATELY 1.4 MILES SOUTH OF AVINGER, TEXAS. LINE AM-199 HAS A MAOP OF 1000 PSIG AND IS A SOURCE FOR LINE AM-47, WHICH HAS A MAOP OF 500 PSIG UPON ARRIVAL AT THE STATION ON THE 10/24/2017, THE O&M TECHNICIAN STOPPED THE VENTING AND INSPECTED THE STATION. HE DISCOVERED THE CONTROLLER WAS FOUND TO HAVE A SET POINT OF 500 PSIG. THE O&M TECHNICIAN MOVED THE CONTROLLER BACK TO THE REQUIRED SET POINT (470 PSIG) AND TIGHTENED THE CONTROLLER ARM, WHICH WAS LOOSE. AFTER THE COMPLETION OF ALL WORK, A TEST GAGE WAS INSTALLED AND THE PRESSURE WAS MONITORED. THE STATION OPERATED NORMALLY AT THE 470 PSIG SET POINT FOR 30 MINUTES. THE NRC WAS NOTIFIED ON 10/24/2017 AT 11:45 (NRC# 1194155). A FOLLOW UP CALL WAS PROVIDED TO THE NRC ON 10/26/2017 AT 09:00 (NRC# 1194335). WHILE THIS LOCATION DOES NOT HAVE MEASUREMENT FACILITIES, THERE IS A MEASUREMENT STATION 20 MILES UPSTREAM AND ANOTHER 12 MILES DOWNSTREAM. STARTING OCTOBER 17TH, SYSTEM CONTROL REPORTED AN INCREASE IN FLOW OF GAS IN THIS AREA BUT COULD NOT LOCATE THE SOURCE OF THE IMBALANCE. SYSTEM CONTROL IMMEDIATELY NOTIFIED THE LOCAL OPERATIONS WHO SYSTEMATICALLY STARTED BACKTRACKING STATIONS AND TROUBLESHOOTING UNTIL THE VENTING RELIEF VALVE WAS DISCOVERED ON 10/24/17. THE FINAL GAS LOSS CALCULATION WAS DETERMINED BY THE MEASUREMENT GROUP FOR THE AREA WHO DETERMINED THE RELIEF VALVE BLEW INTERMITTENTLY FOR 14 DAYS UNTIL DISCOVERY ON 10/24/2017. DURING THE INVESTIGATION, IT WAS DETERMINED ENABLE O&M TECHNICIANS WERE TESTING REGULATORS AT THIS INTERCONNECT ON 10/10/2017. AN OUTAGE PREVENTION FORM WAS UTILIZED AND TEST GAUGE WAS INSTALLED TO MONITOR PRESSURE AT THE STATION WHILE TESTING. AT THE TIME OF THEIR ARRIVAL, THE CONTROLLER NEEDLE INDICATED A SET POINT OF APPROXIMATELY 420 PSIG. ALTHOUGH THE TEST GAUGE READ A PRESSURE OF 470 PSIG, THE SET POINT ON THE CONTROLLER WAS WITHIN THE REQUIRED RANGE AND NO ADJUSTMENTS WERE MADE. AFTER TESTING WAS COMPLETED AND WHILE LOADING TOOLS, THE O&M TECHNICIANS MONITORED THE PRESSURE AT THE REGULATOR STATION WITH A TEST GAGE. AFTER MONITORING PRESSURE FOR 20 MINUTES, A FINAL READING OF APPROXIMATELY 470 PSIG WAS READ AND THE TECHNICIANS LEFT THE REGULATOR STATION. ALTHOUGH THE INVESTIGATION CITED EQUIPMENT FAILURE AS THE MOST LIKELY CAUSE (MORE SPECIFICALLY THE LOOSE TENSION ON THE CONTROLLER ARM ALLOWING THE SET POINT TO MOVE), THE DECISION WAS MADE TO IMMEDIATELY SUSPEND, AND ULTIMATELY DISQUALIFY, THE TWO O&M TECHNICIANS ON THEIR OQ TASKS FOR TESTING REGULATORS AND CONTROL VALVES. THIS DECISION WAS BASED UPON THE FACT THEY WERE TESTING AT THE LOCATION THE DAY THE EVENT BEGAN ON 10/10/2017. THE OPERATORS WILL BE REQUIRED TO BE RE-OBSERVED ON THEIR TASKS. THE DECISION HAS ALSO BEEN MADE TO REPLACE THE BARTON CONTROLLER AT THE STATION, WHICH WAS INSTALLED IN 2007. UPDATE 11/17/2017 - A SUPPLEMENTAL REPORT WAS SUBMITTED TO CORRECT LINE DESIGNATION ERROR IN PART B.7 AND PART B.8 UPDATE 11/27/17 - A SUPPLEMENTAL REPORT WAS SUBMITTED WITH UPDATES MADE TO THE FOLLOWING SECTIONS: A.4, UPDATED DATE AND TIME TO REFLECT THE ESTIMATION OF THE RELEASE REACHING 3 MMCF A.10, UPDATED ESTIMATED VOLUME OF RELEASE A.19, UPDATED TO REFLECT WHEN SCADA INDICATIONS WERE RECOGNIZED BY CONTROLLER E.8, UPDATED TO REFLECT LANGUAGE FROM SYSTEM CONTROL INCIDENT INVESTIGATION REPORT G, CAUSE CHANGED TO INCORRECT OPERATION G.7, UPDATED TO INCORRECT OPERATION G.7.3-5, UPDATED DUE TO SELECTION OF INCORRECT OPERATION UPDATE 1/10/18 B.5 CHANGED COUNTY UPDATE 1/10/18 MARKED FINAL
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170109 | 31560 | 2017-11-20 08:30 | SUPPLEMENTAL FINAL | 2714 | DOMINION ENERGY TRANSMISSION, INC. | 925 WHITE OAKS BOULEVARD | BRIDGEPORT | WV | 26330 | 2017-10-21 04:05 | 2017 |  |  | 39.1409 | -80.3925 | 1194074 | 2017-10-23 16:07 |  | NATURAL GAS |  | 36067 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-10-21 13:15 | 2018-12-05 10:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-10-21 03:15 | 2017-10-21 10:00 | ONSHORE | WV | 26378 | MCWHORTER | HARRISON | SURVEY STATION NO. | 22+50 | LOST CREEK STORAGE | H-20778 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 |  | 0.219 | 35000 | API 5L GRADE B | LONGITUDINAL ERW - HIGH FREQUENCY |  | BETHLEHEM STEEL | OTHER | POLYETHYLENE TAPE / SHRINK SLEEVE. | [27 empty] | 1977 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 9.8 | 0.5 |  | CLASS 1 LOCATION | NO |  | 174 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 38231 | 35014.4495192308 | 13180 | 14018.7050759541 | 26643 | 28338.4187662097 | 19805 | 21065.284827714 | THE COST OF THE INVESTIGATION OF THE SECTION OF PIPE CONTAINING THE RUPTURE. |  | 97859 | 65413.6288074999 | 98436.8581891085 | [8 empty] | 995 |  | 1050 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 954 | NO | YES | [6 empty] | NO | [6 empty] | TRANSMISSION IN STORAGE FIELD | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | YES | YES | SEVERAL OTHER ANALYSES WERE COMPLETED. |  |  |  |  | YES | YES | AXIAL TENSILE OVERLOAD. | [10 empty] | YES | [8 empty] | YES | EXTERNAL WALL LOSS DUE TO COATING FAILURE, CATHODIC PROTECTION SHIELDING, AND CORROSIVE ENVIRONMENT. | [55 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DANIEL STAHL | PIPELINE INTEGRITY ENGINEER | daniel.s.stahl@dominionenergy.com | 6818423365 |  |  |  |  | JEREMY ROSS | MANAGER PIPELINE INTEGRITY | 6818423582 | jeremy.ross@dominionenergy.com | THIS SUPPLEMENTAL REPORT CONTAINS THE COMPLETE FINDINGS FOR THIS INCIDENT. GAS CONTROL RECEIVED AN INITIAL CALL FROM A LANDOWNER REPORTING THAT A RELEASE OF GAS WAS AUDIBLE ON 10/21/17 AT 3:15 AM. THIS WAS THE INITIAL OPERATOR IDENTIFICATION OF THE INCIDENT. GAS CONTROL RELAYED THE INFORMATION TO THE ON-DUTY OPERATIONS SUPERVISOR. THE ON-DUTY OPERATIONS SUPERVISOR CONTACTED THE LANDOWNER ON 10/21/17 AT 3:20 AM. AT THAT POINT IN TIME, THE LANDOWNER STATED THAT A RELEASE OF GAS WAS INITIALLY AUDIBLE, BUT THE SOUND HAD SINCE SUBSIDED. GAS CONTROL RECEIVED ANOTHER CALL FROM A DIFFERENT LANDOWNER REPORTING THAT A RELEASE OF GAS WAS AUDIBLE ON 10/21/17 AT 8:45 AM. GAS CONTROL RELAYED THE INFORMATION TO THE ON-DUTY OPERATIONS SUPERVISOR. THE ON-DUTY OPERATIONS SUPERVISOR DISPATCHED EMPLOYEE PERSONNEL TO INVESTIGATE. EMPLOYEE PERSONNEL ARRIVED IN THE GENERAL AREA AND INITIATED A SEARCH TO DETERMINE THE EXACT LOCATION OF THE SOURCE OF THE SOUND ON 10/21/17 AT 10:00 AM. ONCE THE EXACT LOCATION OF THE SOURCE OF THE SOUND WAS DETERMINED, THE EMPLOYEE PERSONNEL VISUALLY CONFIRMED ON 10/21/17 AT 12:26 PM THAT GAS WAS BLOWING FROM TWO HOLES IN THE GROUND ON EITHER SIDE OF H-20778. H-20778 CONNECTS LOST CREEK STORAGE WELL CW224 TO TL-414. THIS LEAD TO THE INITIAL BELIEF THAT THERE WAS A MINOR LEAK ON H-20778. THE ESTIMATED PRESSURE ON H-20778 AT THE POINT AND TIME OF THE INCIDENT WAS 995 PSIG. THE EMPLOYEE PERSONNEL ISOLATED THE IMPACTED SEGMENT OF H-20778 BY CLOSING THE UPSTREAM AND DOWNSTREAM MANUAL VALVES ON 10/21/17 AT 1:15 PM. H-20778 WAS EXCAVATED AT THE LOCATION OF THE TWO HOLES IN THE GROUND AND IT WAS DISCOVERED THAT H-20778 HAD A CRACK IN IT ON 10/23/17 AT 1:00 PM. THIS DIFFERED FROM THE INITIAL BELIEF THAT THERE WAS A MINOR LEAK ON H-20778. IT WAS CONFIRMED THAT H-20778 HAD RUPTURED AND THAT THE UNINTENTIONAL ESTIMATED GAS LOSS OF THREE MILLION CUBIC FEET OR MORE THRESHOLD MAY HAVE POSSIBLY BEEN EXCEEDED ON 10/23/17 AT 3:30 PM. INITIAL TELEPHONIC NOTIFICATION WAS MADE TO THE NRC ON 10/23/17 AT 4:07 PM AND NRC REPORT NUMBER 1194074 WAS ISSUED. AN UPDATE NOTIFICATION WAS MADE TO THE NRC ON 10/25/17 AT 8:25 AM, BUT A SUBSEQUENT NRC REPORT NUMBER WAS NOT ISSUED. THE SECTION OF PIPE CONTAINING THE RUPTURE ON H-20778 WAS CUT OUT FOR FURTHER INVESTIGATION. H-20778 WAS NOT IMMEDIATELY RETURNED TO SERVICE AND DID NOT REPRESENT A SAFETY HAZARD. THE INVESTIGATION OF THE SECTION OF PIPE CONTAINING THE RUPTURE ON H-20778 WAS PERFORMED BY KIEFNER AND ASSOCIATES, INC. THE RESULTS OF THE INVESTIGATION INDICATED THAT THE RUPTURE WAS LIKELY THE RESULT OF AXIAL TENSILE OVERLOAD OF THE PIPE WHICH CREATED A CIRCUMFERENTIAL FRACTURE WHICH INITIATED AT THE 12:00 POSITION AND ARRESTED AT THE 3:00 AND 9:00 POSITIONS WITH A MAXIMUM WIDTH OF 0.5 INCHES AND LENGTH OF 9.8 INCHES. THE FRACTURE WAS LOCATED APPROXIMATELY 2.5 INCHES DOWNSTREAM FROM A GIRTH WELD. THE PIPE SURFACE AT AND ADJACENT TO THE GIRTH WELD, WHICH INCLUDED THE LOCATION OF THE FRACTURE, WAS COATED WITH A POLYETHYLENE TAPE / SHRINK SLEEVE WHICH HAD FAILED AT SOME POINT IN TIME AND RESULTED IN CATHODIC PROTECTION SHIELDING. THE PIPE EXHIBITED A BEND AT THE LOCATION OF THE FRACTURE WITH AN APPROXIMATE 3 DEGREE ANGLE OF DEFLECTION. THE PIPE WAS ORIGINALLY INSTALLED WITH NO ANGLE OF DEFLECTION. THIS IMPLIED THAT THE PIPE WAS AFFECTED BY A BENDING LOAD WHICH PLACED THE TOP OF THE PIPE IN TENSION AND THE BOTTOM OF THE PIPE IN COMPRESSION. BENDING OF THE PIPE MAY HAVE OCCURRED DUE TO SOIL MOVEMENT. ADDITIONALLY, THE PIPE SURFACE SURROUNDING THE RUPTURE EXHIBITED METAL LOSS THAT EXCEEDED HALF OF THE PIPE WALL THICKNESS IN SOME LOCATIONS. H-20778 IS LOCATED IN AN OLD STRIP MINE AREA THAT MAY HAVE SUBJECTED H-20778 TO ACID MINE DRAINAGE. BASED ON THE RESULTS OF THE INVESTIGATION AND ADDITIONAL FIELD OBSERVATIONS, A REMEDIATION PLAN WAS DEVELOPED WHICH ENTAILED REPLACING THE ENTIRE LENGTH OF H-20778. THIS WAS COMPLETED AND H-20778 WAS RETURNED TO SERVICE ON 12/5/18 AT APPROXIMATELY 10:30 AM.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170110 | 17498 | 2017-11-21 09:43 | ORIGINAL FINAL | 38987 | KINETICA ENERGY EXPRESS LLC | 1001 MCKINNEY STREET, SUITE 900 | HOUSTON | TX | 77002 | 2017-10-23 13:45 | 2017 |  |  | 28.8048 | -92.1285 | 1194067 | 2017-10-23 14:10 |  | NATURAL GAS |  | 411 | 6331 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-10-23 14:15 | 2017-11-07 13:20 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-10-23 13:45 | 2017-10-23 13:45 | OFFSHORE | [28 empty] | 150 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SMI | 42 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12.75 |  | 0.5 | 52000 | ASTM A106 | SEAMLESS |  | U.S. STEEL | OTHER | UNKNOWN | [27 empty] | 1978 | 1977 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO | NO |  | 0 | 0 | 21906 | 23299.9812893664 | 1422 | 1302.36057692308 | 341700 | 363443.969988885 | 10000 | 10636.3467951093 | 0 | 0 |  |  | 375028 | 183758.258769274 | 398682.658650284 | [8 empty] | 884 |  | 1250 | OTHER | NOT ON OMB-APPROVED FORM WHEN SUBMITTED |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 125695 | NO |  | YES |  | YES |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS LOCATED AT -150 DEPTH IN REMOTE LOCATION. BUBBLE ON WATER SURFACE WAS SPOTTED BY KINETICA PERSONNEL. PIPELINE PRESSURES WERE IN NORMAL OPERATING RANGE. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  |  | YES | [5 empty] | YES | LOW FLOW, NON-PIGGABLE SYSTEM |  |  |  |  | YES | BODY OF PIPE IN 6 O'CLOCK POSITION | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KURT CHERAMIE | SENIOR DIRECTOR | kurt.cheramie@kineticallc.com | 9852236165 |  |  |  |  | KURT CHERAMIE | SENIOR DIRECTOR | 9852236165 | kurt.cheramie@kineticallc.com | ON 10/23/2017 DURING ROUTINE OPERATIONS, KINETICA PERSONNEL IDENTIFIED BUBBLES IN SMI 42. LOCATION REPORTED TO KINETICA FIELD OFFICE AND COORDINATES PLOTTED. THE COORDINATES LOCATED NEAR LINE 523M-1300 INDICATING THIS LINE AS THE MOST LIKELY SOURCE OF THE RELEASE. UPON VERIFICATION KINETICA PERSONNEL INITIATED SHUT-IN OF THE PIPELINE AND PRODUCTION ISOLATED AT 14:15 ON 10/23/2017. DIVE VESSEL ISOLATED ENTIRE PIPELINE AT 21:00 ON 11/02/2017. STARTED BLOW DOWN AT 02:42 ON 11/03/17. REPAIRS COMPLETED AT 04:30 ON 11/07/2017 BY INSTALLATION OF A REPAIR CLAMP. VALVE OPENED AND PIPELINE BACK IN SERVICE AS OF 13:20 ON 11/07/2017.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170111 | 17582 | 2017-11-22 11:33 | SUPPLEMENTAL FINAL | 12696 | CYPRESS GAS PIPELINE COMPANY | 1100 LOUISIANA ST. | HOUSTON | TX | 77002 | 2017-10-28 02:00 | 2017 |  |  | 30.4929 | -91.2256 | 1194505 | 2017-10-28 04:19 |  | NATURAL GAS |  | 4000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | ISOLATED RELIEF VALVE, MONITORED PIPELINE PRESSURE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-10-28 02:00 | 2017-10-28 03:08 | ONSHORE | LA | 70767 | BATON ROUGE | WEST BATON ROUGE | MILEPOST | 81 | BATON ROUGE WEST | 580-0100 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2016 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE MALFUNCTIONED | CLASS 1 LOCATION | NO |  | 211 |  | NO | NO | NO |  | 600 | 638.180807706558 | 0 | 0 | 11000 | 10074.5192307692 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 11600 | 10737.6533687691 | 10712.7000384758 | [8 empty] | 344 |  | 366 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS DETERMINED TO BE A RELIEF VALVE MALFUNCTION. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | RELIEF VALVE MALFUNCTION | [161 empty] | NATHAN L. GRAY JR. | SENIOR PIPELINE COMPLIANCE SPECIALIST | ngray@eprod.com | 985-493-4629 |  |  |  |  | NATHAN L. GRAY JR. | SENIOR PIPELINE COMPLIANCE SPECIALIST | 985-493-4629 | ngray@eprod.com | AT 0200 PIPELINE CONTROL CENTER NOTICED A DROP IN PRESSURE ON BRW 1 PIPELINE NEAR THE BATON ROUGE GAS PLANT. PIPELINE CONTROL DISPATCHED A TECHNICIAN TO INVESTIGATE. TECHNICIAN ARRIVED ON SITE AT APPROXIMATELY 0310 AND FOUND A RELIEF VALVE RELIEVING TO ATMOSPHERE, VERIFIED PIPELINE PRESSURE WAS NOT EXCEEDING MAOP, AND CLOSED THE BLOCK VALVE UNDER THE RELIEF VALVE TO SECURE SITE. PIPELINE CONTROL CONTINUED MONITORING PIPELINE PRESSURE UNTIL A CERTIFIED TECHNICIAN ARRIVED TO MAKE REPAIRS. THE TECHNICIAN REPLACED THE PILOT ON THE RELIEF VALVE, SET NEW PILOT TO ESTABLISHED SETTING AND RETURNED THE SEGMENT TO NORMAL SERVICE. AT 0409 IT WAS DETERMINED THE VOLUME OF GAS RELEASED BY THE RELIEF VALVE EXCEEDED 3 MMSCF AND THE NRC WAS NOTIFIED AT 0419. VISUAL EXAMINATION OF THE RELIEF VALVE INDICATED FLUID BUILD-UP ON THE PILOT CAUSED IT TO RELIEF BELOW THE SET POINT. 48 HR. NRC NUMBER 1194628 INVESTIGATION OF THE RELIEF VALVE PILOT BY A THIRD PARTY VENDOR INDICATED THAT FLUID WAS PRESENT AND A FAILED O-RING SEAL WAS FOUND. THESE FACTORS CONTRIBUTED TO THE RELIEF VALVE LIFTING BELOW THE SET POINT. THE REPLACEMENT PILOT HAS BEEN OPERATING AS INTENDED FROM TIME OF INSTALLATION WITH NO ISSUES.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170112 | 17512 | 2017-11-29 13:14 | SUPPLEMENTAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2017-11-09 13:53 | 2017 |  |  | 32.5159 | -93.536 | 1196322 | 2017-11-09 14:52 |  | NATURAL GAS |  | 3342 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | PRESSURE REDUCED BY PRODUCER & RELIEF VALVE WAS RESET | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-11-09 13:53 | 2017-11-09 14:19 | ONSHORE | LA | 71037 | HAUGHTON | BOSSIER | MILEPOST | 3+25.51 | SLIGO RECEIPT METER STATION | BARKSDALE 10" | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ABOVEGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE VENTED | CLASS 1 LOCATION | NO |  | 211 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 9367 | 8578.91105769231 | 0 | 0 | 90 | 95.7271211559837 | 0 | 0 |  |  | 9457 | 8938.08790916151 | 8674.63817884829 | [8 empty] | 902 |  | 936 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | OTHER | NOTIFICATION FROM PRODUCER |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | PRODUCER'S PRESSURE CONTROL EQUIPMENT | [15 empty] | YES | UNKNOWN - PRODUCER'S EQUIPMENT | [161 empty] | SHANNON MATTINGLY | PA OQ AND EVENT SUPPORT PROGRAM LEADER | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 2706886361 | jeff.mcmaine@bwpmlp.com | PRODUCER HAD ISSUES WITH PRESSURE CONTROL WHICH ALLOWED A SWING IN THE PRESSURE COMING INTO THE TEXAS GAS METER STATION; THIS CAUSED THE RELIEF VALVE TO OPERATE. THE RELIEF VALVE OPERATED PROPERTY AND PROTECTED THE TEXAS GAS EQUIPMENT FROM ANY OVER-PRESSURING EVENTS. THIS IS A RECEIPT POINT TO TEXAS GAS. THE SYSTEM UPSET WAS ON THE PRODUCER'S ASSETS. TEXAS GAS REPORTED THE INCIDENT BECAUSE IT WAS OUR RELIEF VALVE THAT VENTED THE GAS. THE RELIEF VALVE OPERATED AS DESIGNED. 12-4-17 CREATED SUPPLEMENTAL TO REVISE PER PHMSA INSTRUCTION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170113 | 17506 | 2017-11-29 14:46 | SUPPLEMENTAL FINAL | 18152 | SEA ROBIN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2017-11-05 16:50 | 2017 |  |  | 28.2065 | -91.7014 | 1195323 | 2017-11-06 09:38 |  | NATURAL GAS |  | 300 | 1606 | 0.3 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-11-06 09:08 | 2017-11-11 01:58 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-11-05 16:50 | 2017-11-06 08:45 | OFFSHORE | [28 empty] | 260 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EUGENE ISLAND | 338 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12 |  | 0.438 | 52000 | UNKNOWN | OTHER | UNKNOWN | UNKNOWN | OTHER | MASTIC AND CONCRETE | [27 empty] | 1973 | 1973 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 318 |  | NO | NO | NO |  | 0 | 0 | 5059 | 5380.9278436458 | 945 | 865.492788461538 | 210000 | 223363.282697295 | 60000 | 63818.0807706558 | 0 | 0 |  |  | 276004 | 135191.107177338 | 293427.784100058 | [8 empty] | 754 |  | 1306 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 30729 | NO | YES | [6 empty] | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | PRODUCER PLATFORM PERSONNEL |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS TOO SMALL FOR SCADA TO DETECT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | PINHOLE LEAK | YES | [7 empty] | YES | LOW FLOW CONDITIONS. |  |  |  |  | YES | 6 O'CLOCK | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713.857.5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | 713.857.5479 | nathan.hlavaty@energytransfer.com | ON 11/5/17, A PRODUCER (FIELDWOOD) REPORTED BUBBLES FROM AN UNKNOWN SOURCE IN THE AREA. ON 11/6/17, SEA ROBIN PERSONNEL ARRIVED AND CLAIMED RESPONSIBILITY DUE TO THE PROXIMITY OF FACILITIES (NRC# 1195323). ON 11/8/17, THE 48 HOUR UPDATE WAS MADE TO THE NRC,(#1195759). DAILY UPDATES WERE PROVIDED TO THE PHMSA AID, FROM 11/6/17 THROUGH THE RESTART OF THE LINE. SUPPLEMENTAL REPORT SUBMITTED 11/30/17, CORRECTED PART A QUESTIONS - (4) AND (19A).
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170114 | 17508 | 2017-11-29 15:34 | SUPPLEMENTAL FINAL | 15105 | PANHANDLE EASTERN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2017-11-05 18:40 | 2017 |  |  | 39.7902 | -88.3589 | 1195292 | 2017-11-05 19:38 |  | NATURAL GAS |  | 5275 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | UNIT 1215 WAS SHUT DOWN DUE TO THE INCIDENT. FACILITY REMAINED ONLINE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-11-05 13:22 | 2017-11-05 13:36 | ONSHORE | IL | 61953 | TUSCOLA | DOUGLAS | SURVEY STATION NO. | 0+00 | TUSCOLA COMPRESSOR STATION | TUSCOLA COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1963 |  | CARBON STEEL |  | OTHER | [8 empty] | VALVE PLUNGER BECAME UNSEATED AND RELEASED GAS THROUGH VENT PIPING. | CLASS 1 LOCATION | NO |  | 72 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 16458 | 15073.3125 | 228 | 242.508706928492 | 0 | 0 | 0 | 0 |  |  | 16686 | 15738.5053955169 | 15315.8212069285 | [8 empty] | 895 |  | 898 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EQUIPMENT FAILURE IN THE FIELD. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [13 empty] | YES | [177 empty] | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713.857.5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | 713.857.5479 | nathan.hlavaty@energytransfer.com | AT APPROXIMATELY 13:13 PM CST ON SUNDAY, NOVEMBER 5TH, 2017, THE AUTOMATIC BLOW DOWN (ABD) FOR UNIT 1215 OPENED WHILE THE UNIT WAS RUNNING. THE UNIT WAS STOPPED BY STATION PERSONNEL AT 13:39 PM CST. ONCE THE VOLUME RELEASED WAS CONFIRMED, THE NRC WAS NOTIFIED (NRC# 1195292) AS WELL AS THE PHMSA AID. THE 48 HR NRC NOTIFICATION WAS MADE ON 11/7/17, (NRC# 1195625). THIS SUPPLEMENT HAS BEEN SUBMITTED TO CORRECT THE COORDINATES IN PART A, QUESTION #5.
2021-02-26 10:37 | YES | YES | GT (Gas Transmission) | 20170115 | 32529 | 2017-11-30 11:35 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2017-10-23 10:26 | 2017 |  |  | 40.6868 | -81.4512 | 1194041 | 2017-10-23 12:16 |  | NATURAL GAS |  | 12970 | 0 | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | NO | [5 empty] | 0 |  | YES |  | 2017-10-23 10:45 | 2018-10-25 11:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 3 | 2017-10-23 10:26 | 2017-10-23 10:45 | ONSHORE | OH | 44662 | NAVARRE | STARK COUNTY | MILEPOST | MS730886 | EDC-TIMKEN MEASURING STATION | 733886 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | METER | [38 empty] | 1989 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 190 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 35797 | 32785.2331730769 | 143000 | 152099.759170063 | 0 | 0 | 0 | 0 |  |  | 178797 | 103807.742793805 | 184884.99234314 | [8 empty] | 356 |  | 500 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE FAILURE AT THIS MEASURING STATION FACILITY TOOK PLACE DURING A ROUTINE PREVENTIVE MAINTENANCE PRACTICE WAS BEING FINALIZED AT THE MEASURING STATION FACILITY. | [12 empty] | YES | 2 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | THE CLOSURE SWING BOLT PIN FAILED AS A RESULT OF DOUBLE SHEAR FORCE WHILE TIGHTENING THE SWING BOLT NUT | YES |  |  |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | KAMRAN ROSTAMI ASRABADI | COMPLIANCE SPECIALIST | kamran_rostami@transcanada.com | (304)357-2351 |  |  |  |  | GEORGE HAMATY | US REGULATORY COMPLIANCE MANAGER EAST | (304)357-3728 | george_hamaty@transcanada.com | ON OCTOBER 23RD, 2017, A 8-INCH SINGLE BOLT HINGED CLOSURE FAILED AFTER AN UNINTENDED NATURAL GAS RELEASE WAS NOTED BY THE ONSITE COMPANY PERSONNEL. THE FACILITY IS KNOWN AS EDC-TIMKEN MEASURING STATION 730886. THE FACILITY IS OWNED BY EDC-TIMKEN, OPERATED AND MAINTAINED BY COLUMBIA GAS TRANSMISSION, LLC (COMPANY). THE TWO COMPANY PERSONNEL WERE PERFORMING ROUTINE PREVENTIVE MAINTENANCE TO THE MS. THE LINE WAS DEPRESSURIZED AND THE CLOSURE WAS OPENED IN ORDER TO PERFORM THE MAINTENANCE. AT THE COMPLETION OF THE MAINTENANCE ACTIVITY, THE CLOSURE WAS CLOSED AND SECURED WITH A SWING BOLT. THE LINE WAS PRESSURIZED AND AN UNINTENDED RELEASE WAS IDENTIFIED AT THE HEAD OF THE CLOSURE. UPON COMPLETING THE MAINTENANCE TASKS AND RETURNING THE FACILITY BACK INTO SERVICE BEFORE LEAVING THE SITE, THE SOUND OF A POTENTIAL RELEASE WAS HEARD BY ONE OF THE MEASUREMENT AND REGULATION (M&R) TECHNICIANS. BASED ON REPORTED WITNESS STATEMENTS, WHILE INVESTIGATING THE NATURE OF THE UNINTENDED RELEASE, THE SINGLE BOLT MAY HAVE BEEN IN THE PROCESS OF BEING TIGHTENED IN AN EFFORT TO STOP THE POTENTIAL LEAK AT THE TIME OF THE FAILURE. THE CLOSURE FAILURE FATALLY INJURED THE M&R TECHNICIAN INVESTIGATING THIS UNINTENDED RELEASE. THE FAILED SECTIONS WERE SENT TO A METALLURGICAL LABORATORY FOR FAILURE ANALYSIS INVESTIGATION, TO DETERMINE THE PROBABLE CAUSE BEHIND THE FAILURE OF THE SWING BOLT. THE LABORATORY REPORT IDENTIFIED THE INCIDENT WAS CAUSED DUE TO THE FAILURE OF THE SWING BOLT PIN. THE VERTICAL ORIENTATION OF THE DUCTILE SHEAR OBSERVED ON THE FRACTURE SURFACE OF THE SWING BOLT PIN IS CONSISTENT WITH A LOADING DIRECTION IMPACTED WHILE TIGHTENING THE SWING BOLT NUT AND PLACING THE SWING BOLT PIN INTO DOUBLE SHEAR. TWO SAFETY ALERTS WERE ISSUED COMPANY-WIDE AS A RESULT OF THIS INCIDENT, WITH CAREFUL ATTENTION PAID TO SIMILAR APPLICATIONS, WITH THE GOAL OF PREVENTING SIMILAR INCIDENTS FROM RE-OCCURRING. (INCIDENT NRC REPORT NO. 1194041 AND 48-HR NRC REPORT NO. 1194188)
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170116 | 17561 | 2017-12-06 13:39 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2017-09-21 17:15 | 2017 |  |  | 42.5404 | -83.3608 | 1196786 | 2017-11-10 14:10 |  | NATURAL GAS |  | 332 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-09-28 09:30 | 2017-09-29 01:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-09-21 17:31 | 2017-09-21 17:58 | ONSHORE | MI | 48322 | WEST BLOOMFIELD | OAKLAND | MILEPOST | HA66 | LINE 1014A | LINE 1014A | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 |  | 0.25 | 35000 | UNKNOWN | SEAMLESS |  | UNKNOWN | NONE | [28 empty] | 1980 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | SAW CUT THROUGH THE PIPELINE | [5 empty] | CLASS 3 LOCATION | YES | METHOD2 | 152 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 956 | 875.567307692308 | 105866 | 112602.748981104 | 52 | 55.3090033345684 | 0 | 0 |  |  | 106874 | 52620.7616888021 | 113533.625292131 | [8 empty] | 250 |  | 300 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 60 | NO | YES | YES | YES | YES |  |  |  | YES |  | YES |  |  |  |  | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PIPELINE WAS DAMAGED BY A THIRD PARTY PERFORMING SEWER WORK NEAR THE PIPELINE. THE CONTRACTOR REALIZED THE PIPELINE BEING CUT WAS LIVE AND IMMEDIATELY EVACUATED THE AREA AND NOTIFIED CONSUMERS ENERGY. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [103 empty] | OTHER OUTSIDE FORCE DAMAGE | [9 empty] | SAW CUT THROUGH THE PIPELINE RESULTING IN TWO 3/8" SLITS IN THE PIPELINE APPROXIMATELY 8' APART | [251 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  |  |  |  | JASON PIONK | SENIOR ENGINEERING TECHINICAL ANALYST LEAD | 989-791-5749 | jason,pionk@cmsenergy.com | ON SEPTEMBER 21, 2017 AT APPROXIMATELY 17:15 A THIRD PARTY CONTRACTOR PERFORMING SEWER WORK IN PREPARATION FOR A ROAD RECONSTRUCTION PROJECT DAMAGED A CONSUMERS ENERGY 12" HP NATURAL GAS PIPELINE IN TWO LOCATIONS. THE DAMAGE LOCATIONS WERE APPROXIMATE 8 FOOT APART AND WERE APPROXIMATELY 3/8 INCH IN SIZE. CONSUMERS ENERGY REVIEWED THE PROJECT WITH THE CONTRACTOR AND PROVIDED AS-BUILT PRINTS TO ENSURE THE ABANDONED AND LIVE PORTIONS OF THE PIPELINE WERE IDENTIFIED. THE CONTRACTOR'S EMPLOYEES RECOGNIZED THEY SAW CUT AN ACTIVE PIPELINE WHEN THEY HEARD GAS ESCAPING. THEY IMMEDIATELY EVACUATED THE AREA AND CONTACTED CONSUMERS ENERGY ADVISING OF THE DAMAGE. THERE WAS NO IGNITION, NO INJURIES OR NO FATALITIES THAT OCCURRED AS A RESULT OF THE DAMAGE. A TEMPORARY REPAIR USING PLIDCO BOLTED SLEEVES WERE INSTALLED AT EACH DAMAGE LOCATION STOPPING THE ESCAPING GAS ON SEPTEMBER 22, 2017 AT APPROXIMATELY 05:00. ON SEPTEMBER 28, 2017 A SECTION OF THE PIPELINE WAS ISOLATED AND APPROXIMATELY 10 FOOT OF 12 STEEL PIPE WAS CUT-OUT AND REPLACED TO PERMANENTLY REPAIR THE DAMAGE SECTION OF THE PIPELINE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170117 | 17516 | 2017-12-07 10:05 | ORIGINAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2017-11-11 20:30 | 2017 |  |  | 30.0299 | -99.8353 | 1197075 | 2017-11-11 22:38 |  | NATURAL GAS |  | 3790 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | FACILITY WAS ALREADY SHUT DOWN | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-11-11 19:20 | 2017-11-11 21:00 | ONSHORE | TX | 78873 | LEAKEY | REAL | SURVEY STATION NO. | 8687+62 | REAL COMPRESSOR STATION | UNIT 200 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2005 |  | CARBON STEEL |  | OTHER | [8 empty] | GAS WAS VENTING THROUGH THE 2" BLOW DOWN VALVE | CLASS 1 LOCATION | NO |  | 606 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 11870 | 10871.3221153846 | 0 | 0 | 200 | 212.726935902186 | 0 | 0 |  |  | 12070 | 11368.4405459999 | 11084.0490512868 | [8 empty] | 617 |  | 858 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER NOR CONTROL ROOM WERE A CONTRIBUTING FACTOR | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | YES | [33 empty] | YES | PLC ELECTRICAL FAILURE | [161 empty] | MICHAEL D. SMITH | PIPELINE COMPLIANCE SPECIALIST | mdsmith@eprod.com | 713-381-5650 |  |  |  |  | MICHAEL D. SMITH | PIPELINE COMPLIANCE SPECIALIST | 713-381-5650 | mdsmith@eprod.com | ON 11/11/17 AT 7:20 PM, GAS CONTROL RECOGNIZED THAT THE SUCTION PRESSURE WAS INCREASING ON UNIT 200 COMPRESSOR AND DISPATCHED OPERATIONS. THE TECHNICIAN ARRIVED AT 9:00 PM AND DETERMINED THAT THE CAT ENGINE PROGRAMMING ON UNIT 200 FAILED CAUSING THE UNIT TO SHUTDOWN AND LEAVING THE SUCTION VALVE ON UNIT 200 OPEN AND RELEASING GAS TO ATMOSPHERE THRU THE 2 INCH ENGINE BLOWDOWN STACK. OPERATIONS REPROGRAMED THE CPU AND AT 10:30 PM ON 11/11/17 RETURNED UNIT 200 BACK INTO SERVICE. AT APPROXIMATELY 10:15 PM IT WAS CALCULATED THAT THE AMOUNT OF NATURAL GAS VENTING THRU THE 2 INCH VALVE WAS APPROXIMATELY 3.79 MMSCF. THE NRC AND RRC (#16666) WERE IMMEDIATELY NOTIFIED. ON 11/13/2017 AT 4:54 PM, ENTERPRISE PROVIDED A 48 HOUR UPDATE TO THE NRC (#1197219).
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170118 | 32108 | 2017-12-07 10:25 | SUPPLEMENTAL FINAL | 31485 | ENBRIDGE OFFSHORE (GAS GATHERING) L.L.C. | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2017-11-08 01:20 | 2017 |  |  | 27.8758 | -91.9864 | 1196067 | 2017-11-09 10:40 |  | NATURAL GAS |  | 15 | 21000 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-11-08 01:30 | 2018-07-11 09:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2017-11-08 01:30 | 2017-11-08 01:30 | OFFSHORE | [28 empty] | 650 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | GARDEN BANKS | 128 | PLATFORM | INTERSTATE | OFFSHORE PLATFORM, INCLUDING PLATFORM-MOUNTED EQUIPMENT AND PIPING | OTHER | [37 empty] | LAUNCHER BARREL ENCLOSURE | 1997 |  | CARBON STEEL |  | OTHER | [8 empty] | LAUNCHER DOOR - INCOMPLETE CLOSURE OF THE CLAMP RINGS ONTO THE DOOR AND BARREL FLANGES. | CLASS 1 LOCATION | NO |  | 920 |  | NO | NO | NO |  | 28700000 | 30526315.3019637 | 63000 | 67008.9848091886 | 45 | 41.2139423076923 | 11075000 | 11779754.0755835 | 0 | 0 | 0 | 0 |  |  | 39838045 | 19450403.7880171 | 42373119.5762987 | [8 empty] | 400 |  | 1975 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | NOTIFIED BY THIRD PARTY CONTRACTOR PLATFORM OPERATOR |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | BASED ON INFORMATION KNOWN AT THE TIME OF THIS REPORTING THE CAUSE OF THE EVENT WOULD NOT HAVE BEEN DISCOVERABLE BY THE CONTROL ROOM. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | THE THIRD PARTY CONTRACTOR PLATFORM OPERATOR, WHILE PERFORMING PIGGING OPERATIONS ON THE ENBRIDGE 30-INCH PIPELINE, DID NOT FOLLOW THEIR PROCEDURES AND DID NOT COMPLETELY CLOSE THE CLAMP RINGS ONTO THE LAUNCHER DOOR AND BARREL FLANGES. |  |  | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | MAYRA SALINAS | SENIOR ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | RICK KIVELA | MANAGER | 713-627-6388 | rick.kivela@enbridge.com | ORIGINAL REPORT: PLATFORM PERSONNEL AT GARDEN BANKS BLOCK 128A PLATFORM BEGAN PIG LOADING OPERATIONS FOR ENBRIDGE 30-INCH PIPELINE SEGMENT NUMBER 10894 AT 12:00 AM, NOVEMBER 8, 2017. WHILE PRESSURING THE PIG BARREL, A RELEASE OF NATURAL GAS OCCURRED, WHICH RESULTED IN A FIRE AT 1:30 AM THE SAME DAY. TWO PLATFORM PERSONNEL RECEIVED MINOR INJURIES FOR WHICH THEY WERE TREATED AT A MEDICAL FACILITY AND RELEASED. ALL PLATFORM PERSONNEL WERE REMOVED FROM THE PLATFORM ON NOVEMBER 8, 2017. THE FIRE WAS SUBSEQUENTLY EXTINGUISHED ON NOVEMBER 9, 2017 BY LOWERING PRESSURE ON THE PIPELINE AND PERSONNEL RETURNED TO THE PLATFORM. THE ENBRIDGE 30-INCH PIPELINE HAS NOT RETURNED TO SERVICE. THE CAUSE OF THE INCIDENT IS UNDER INVESTIGATION. SUPPLEMENTAL REPORT: ENBRIDGE DID NOT OPERATE THE PLATFORM OR THE PIGGING OPERATIONS. THOSE ACTIVITIES WERE CONDUCTED BY THE THIRD PARTY CONTRACTOR PLATFORM OPERATOR USING THEIR PROCEDURES. THE PLATFORM PERSONNEL WHO WERE INJURED WERE EMPLOYED BY THE THIRD PARTY CONTRACTOR PLATFORM OPERATOR. GIVEN THIS EMPLOYMENT RELATIONSHIP, ENBRIDGE IS NOT AWARE OF WHETHER THE PLATFORM PERSONNEL RECEIVED DOT DRUG AND ALCOHOL TESTING. ADDITIONALLY, ENBRIDGE HAS LEARNED THAT ONE OF THE TWO INJURED PLATFORM PERSONNEL SUSTAINED INJURIES MORE SIGNIFICANT THAT ORIGINALLY REPORTED. FINALLY, SIX MEMBERS OF A PAINTING CREW HOUSED IN THE CREW QUARTERS AT THE TIME OF THE INCIDENT CLAIM EMOTIONAL AND/OR PHYSICAL INJURIES, BUT THOSE CLAIMS HAVE NOT BEEN VERIFIED. THE PRESSURE IN THE PIPELINE WAS A 1,086 PSIG AT THE TIME OF THE INCIDENT. IT IS ESTIMATED THAT THE PRESSURE WITHIN THE BARREL (AT THE POINT OF THE FAILURE) WAS 400 PSIG. THE RESULT OF THE METALLURGICAL INVESTIGATION INDICATED THAT THE CAUSE OF THE INCIDENT WAS INCOMPLETE CLOSURE OF THE CLAMP RINGS ONTO THE DOOR AND BARREL FLANGES WHICH OCCURRED WHILE THE THIRD PARTY CONTRACTOR PLATFORM OPERATOR WAS PERFORMING ROUTINE PIPELINE MAINTENANCE PIGGING OPERATIONS ON THE ENBRIDGE 30-INCH PIPELINE. THE ENBRIDGE 30-INCH PIPELINE WAS RETURNED TO SERVICE FOLLOWING THE INCIDENT ON JULY 11, 2018.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170119 | 17602 | 2017-12-08 14:31 | SUPPLEMENTAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2017-11-09 17:04 | 2017 |  |  | 30.1964 | -91.1009 | 1196419 | 2017-11-09 17:56 |  | NATURAL GAS |  | 11600 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-11-09 17:23 | 2017-11-10 09:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-11-09 17:04 | 2017-11-09 17:23 | ONSHORE | LA | 70788 | WHITE CASTLE | IBERVILLE | MILEPOST | 30.725 | WHITE CASTLE COMPRESSOR STATION | ENGINE #10 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1957 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 717 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 38253 | 35034.5985576923 | 400 | 425.453871804372 | 0 | 0 | 0 | 0 |  |  | 38653 | 36517.2536881537 | 35460.0524294967 | [8 empty] | 1101 |  | 1200 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO CONTROL ROOM ISSUES. INCIDENT WAS DUE TO A BROKEN NIPPLE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | PIPE NIPPLE |  |  |  |  | YES | [177 empty] | KRISTIN VAN DER LAAN | MANAGER-ENGINEERING COMPLIANCE-CODES AND STNDS | kristin_vanderlaan@kindermorgan.com | 303-914-7753 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR-ENGINEERING COMPLIANCE CODES AND STNDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | AT 5:04PM ENGINE #10 RELIEF VALVE BEGAN VENTING GAS DUE TO A BROKEN SENSING LINE. THE UNIT WAS EMERGENCY STOPPED AT 5:23PM. THE TOTAL AMOUNT OF UNINTENTIONALLY NATURAL GAS RELEASED WAS 11,600 MCF. THE INITIAL INVESTIGATION SHOWED THAT THE 1/4-INCH PIPE NIPPLE ON THE RELIEF VALVE PILOT TEST PORT BROKE CAUSING THE RELIEF VALVE TO VENT. UPON FURTHER INVESTIGATION IT WAS DETERMINED THAT VIBRATION AND THE WEIGHT OF THE TEST ASSEMBLY MAY HAVE CONTRIBUTED TO THE FAILURE OF THE PIPE NIPPLE. THE NIPPLE WAS REPLACED WITH A MALE X FEMALE THREAD VALVE AND THE ENGINE WAS RETURNED TO SERVICE. THE PIR IS BASED ON THE LARGEST DIAMETER PIPE INSIDE THE COMPRESSOR BUILDING, NOT THE NIPPLE THAT FAILED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170120 | 17529 | 2017-12-12 15:05 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2017-12-07 02:15 | 2017 |  |  | 43.2003 | -90.0733 | 1199048 | 2017-12-07 08:53 |  | NATURAL GAS |  | 3396 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELIEF VALVE STOPPED VENTING ON ITS OWN. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-12-07 03:57 | 2017-12-07 06:00 | ONSHORE | WI | 53588 | Not Within a Municipality | SAUK | MILEPOST | MP 40.75 | 179WIB14601 | NEW LISBON BL | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2014 |  | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 259 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 9621 | 8811.54086538462 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 9621 | 9135.32451923077 | 8811.54086538462 | [8 empty] | 798 |  | 865 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WAS NOTHING IN THE CAUSE THAT THE CONTROL ROOM WOULD HAVE BEEN ABLE TO DETECT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | ICED UP | [161 empty] | JEFFREY CULLISON | SR. PIPELINE SAFETY ENGINEER | j.cullison@nngco.com | 402-398-7439 | 402-548-5267 |  |  |  | THOMAS CORRELL | VICE PRESIDENT OF INTEGRITY AND RISK | 402-398-7715 | thomas.correll@nngco.com | ON DECEMBER 7, 2017, AT APPROXIMATELY 0357 HOURS, THE SAUK COUNTY SHERIFF'S OFFICE NOTIFIED THE OPERATIONS COMMUNICATION CENTER THAT A LOUD NOISE WAS OBSERVED AT THE SPRING GREEN COMPRESSOR STATION. OPERATIONS RESPONDED AND FOUND NO ISSUES WITH THE UNIT OR STATION THAT WOULD HAVE CAUSED A HIGH PRESSURE SITUATION. THE RELIEF VALVE IS SET AT 880 PSIG BUT ACTUATED AT 798 PSIG. THE VALVE WAS DISASSEMBLED FOR INSPECTION AND A BUILDUP OF ICE IN THE PILOT WAS DISCOVERED. THE RELIEF VALVE WAS REPAIRED AND PLACED BACK IN SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170121 | 17530 | 2017-12-15 14:32 | ORIGINAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2017-11-22 05:21 | 2017 |  |  | 36.5281 | -94.3823 | 1197895 | 2017-11-22 07:13 |  | NATURAL GAS |  | 21095 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | ADJUSTMENTS MADE TO PILOT TUBING CONNECTION WHILE ONLINE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-11-22 05:45 | 2017-11-22 07:21 | ONSHORE | MO | 64854 | NOEL | MCDONALD | MILEPOST | NA | JANE COMPRESSOR STATION | LINE OM-1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | TUBING | [38 empty] | UNKNOWN |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 436 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 67576 | 61890.5192307692 | 0 | 0 | 1000 | 1063.63467951093 | 0 | 0 |  |  | 68576 | 64652.9479223074 | 62954.1539102802 | [8 empty] | 821 |  | 1000 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | MALFUNCTION OF A COMPONENT CAUSED A VERSA VALVE TO FAIL OPEN. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | THREADED FITTING |  |  |  |  | YES | [177 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | DURING THE 06:00 SHIFT CHANGE ON 11/22/17, ENABLE GAS TRANSMISSION SYSTEM CONTROL BECAME AWARE OF AN UNUSUAL SITUATION WITH LINE OM-1. SYSTEM CONTROL DID NOT RECEIVE ANY ALERTS, SAFETY RELATED ALARMS, OR RATE OF CHANGE ALARMS TO NOTIFY THEM OF THE SITUATION BUT DID NOTICE AN INCREASE IN FLOW RATE INTO LINE OM-1 AND A DECREASE IN DISCHARGE PRESSURE AT DUNN STATION. SYSTEM CONTROL IMMEDIATELY DISPATCHED FIELD TECHNICIANS TO SURVEY LINE OM-1 TO INVESTIGATE THE SITUATION. AT APPROXIMATELY 06:44, A 911 OPERATOR CONTACTED SYSTEM CONTROL TO REPORT A LOUD NOISE, AND POSSIBLE GAS LEAK, NEAR HWY 90 NEAR NOEL, MISSOURI. AT 07:21, AN ENABLE FIELD TECHNICIAN DISCOVERED A BLOWDOWN VALVE RELEASING NATURAL GAS TO ATMOSPHERE AT THE JANE COMPRESSOR STATION. AFTER THE STATION WAS SECURED, SCADA DATA WAS CHECKED AND BY 08:01 THE ISSUE HAD BEEN CORRECTED. UPON INVESTIGATION, A VERSA VALVE ACTUATOR FOR THE BLOWDOWN VALVE FAILED OPEN DUE TO A LEAK IN THE PILOT TUBING. THE LOOSE FITTING WAS TIGHTENED ELIMINATING THE LEAK. THE REMAINING VALVE FITTINGS WERE CHECKED AT THE STATION FOR TIGHTNESS. ON THE MORNING OF 11/22/17 ENABLE MIDSTREAM REPORTED A POTENTIAL RELEASE TO THE NRC (NRC #1197895 07:13), AND FOLLOWED UP LATER WITH A LOCATION AND QUANTITY CHANGE (NRC# 1197919 12:17). THE 48 HOUR FOLLOW UP CALL WAS PLACED ON 11/24/17 (NRC# 1197992 07:10).
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170122 | 30469 | 2017-12-15 17:31 | SUPPLEMENTAL FINAL | 31978 | ATMOS PIPELINE - TEXAS | 5420 LBJ FREEWAY, SUITE 1800 | DALLAS | TX | 75240 | 2017-11-15 08:51 | 2017 |  |  | 33.4194 | -95.1813 | 1197363 | 2017-11-15 10:51 |  | NATURAL GAS |  | 4537 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-11-15 15:00 | 2017-11-15 21:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-11-15 09:15 | 2017-11-15 10:00 | ONSHORE | TX | 75417 | BOGATA | RED RIVER | SURVEY STATION NO. | 92+07 | O38-1 | O38-1 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 66 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 |  | 0.25 | 35000 | UNKNOWN | SEAMLESS |  | UNKNOWN | COAL TAR | [28 empty] | 1957 | 1957 | CARBON STEEL |  | MECHANICAL PUNCTURE | 2.5 | 2.5 | [7 empty] | CLASS 1 LOCATION | NO |  | 134 |  | NO | NO | NO |  | 1000 | 1063.63467951093 | 0 | 0 | 12658 | 11593.0240384615 | 0 | 0 | 61463 | 65374.1783067803 | 4000 | 4254.53871804372 | CNG NEEDED AFTER SHUTDOWN OF PIPELINE |  | 79121 | 44468.6692026249 | 82285.3757427965 | [8 empty] | 340 |  | 500 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 38086 | NO |  | YES | YES | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 4 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [10 empty] | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | BORING | NATURAL GAS | YES | 1782014994 | TEXAS811 | CONTRACT LOCATOR | NO | NO | YES | 6 | LOCATING PRACTICES NOT SUFFICIENT |  | FACILITY MARKING OR LOCATION NOT SUFFICIENT | [264 empty] | CHARLEY LEWIS | OPERATIONS SUPERVISOR | charley.lewis@atmosenergy.com | 903-249-1283 | 903-784-7654 |  |  |  | MARLO SUTTON | DIRECTOR REGULATORY AND COMPLIANCE | 214-206-2033 | marlo.sutton@atmosenergy.com | ADDITIONAL NRC REPORT NO. 1197541 ON NOVEMBER 15, 2017, AN ATMOS ENERGY CONTRACTOR HIT THE LINE AT THE JOHNTOWN BLOCK VALVE/JOHNTOWN TAP YARD. THE CONTRACTOR WAS HIRED BY ATMOS ENERGY TO DO THE BORES ON THE LINE O38-1 LINE REPLACEMENT. THE CONTRACTOR DRILLED A 2.5 INCH HOLE IN THE LINE AT THE STATION LISTED. AS PART OF ITS NORMAL OPERATIONS, ATMOS ENERGY HAS A PROGRAM IN PLACE TO MONITOR AND TAKE APPROPRIATE ACTION AS NEEDED WITH CONTRACTORS WHO DAMAGE COMPANY ASSETS DURING EXCAVATION. THIS DAMAGE PREVENTION PROGRAM IS APPLICABLE TO THIS CONTRACTOR AND WAS FOLLOWED AND APPLIED WITH REGARD TO THIS INCIDENT. THE PROGRAM INVOLVES, AMONG OTHER ACTIONS: (1) AUDITS OF CURRENT EXCAVATION PROJECTS OF 2ND PARTY CONTRACTORS TO REVIEW COMPLIANCE WITH PIPELINE LOCATING AND DAMAGE PREVENTION PROCEDURES; (2) MEETINGS WITH 2ND PARTY CONTRACTORS TO DISCUSS AT-FAULT DAMAGES AND DEVELOP ROOT-CAUSE ANALYSIS OF THE DAMAGES; (3) PROVISION OF COACHING TO CONTRACTORS OF DAMAGE PREVENTION MEASURES REGARDING THE IMPORTANCE OF PROPER LOCATING PROCEDURES AND SAFE EXCAVATION PRACTICES WITHIN THE TOLERANCE ZONE; AND (4) PUBLIC LIAISON MEETINGS AND MOCK LINE STRIKES CONDUCTED ANNUALLY FOR EMERGENCY RESPONDERS AND EXCAVATORS WITHIN OUR SERVICE AREA, EMPHASIZING PROPER USE OF THE 811 NOTIFICATION SYSTEM, SAFE EXCAVATION PRACTICES, AND RESPONSE ACTIONS TO TAKE IN THE EVENT OF A PIPELINE INCIDENT.
2021-02-26 10:37 | YES | NO | UNGS (Underground Natural Gas Storage) | 20170123 | 30480 | 2017-12-15 17:33 | SUPPLEMENTAL FINAL | 11824 | LOUISVILLE GAS & ELECTRIC CO | 220 W MAIN ST, PO BOX 32010 | LOUISVILLE | KY | 40202 | 2017-11-09 16:23 | 2017 |  |  | 37.1776 | -85.6871 | 1197549 | 2017-11-17 12:46 |  | NATURAL GAS |  | 676 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | N/A | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-11-09 16:23 | 2017-11-09 16:23 | ONSHORE | KY | 42746 | HARDYVILLE, KENTUCKY | METCALFE COUNTY | SURVEY STATION NO. | A.SCOTT1AWELL | CENTER GAS STORAGE FIELD | A. SCOTT 1-A WELL | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | OTHER | GAS STORAGE FIELD | 1440 |  | NO | [22 empty] | INTERSTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | UNDERGROUND GAS STORAGE OR CAVERN | [38 empty] | UNKNOWN |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | ANNULUS LEAK | OTHER | [8 empty] | ANNULUS LEAK | CLASS 1 LOCATION | NO |  | 1 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 212726.935902186 | 0 | 0 | 0 | 0 |  |  | 200000 | 97647.2767691738 | 212726.935902186 | [8 empty] | 0 |  | 0 | OTHER | NO MAOP ESTABLISHED BECAUSE THIS WAS A WELL AND NOT A PIPELINE |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION IN STORAGE FIELD | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | ANNULUS LEAK IN NEARBY OBSERVATION WELL | [147 empty] | BARRY WALKER | DIRECTOR GAS CONTROL AND STORAGE | barry.walker@lge-ku.com | 502-627-3038 |  |  |  |  | GREG CORNETT | ASSOCIATE GENERAL COUNSEL | 502-627-2756 | greg.cornett@lge-ku.com | GAS WAS DISCOVERED LEAKING AT THE SURFACE NEAR THE WELLHEAD OF THE A. SCOTT 1A OBSERVATION WELL ON OCTOBER 10TH, 2017. A CEMENT RETAINER WAS SET AT THE BOTTOM OF THE WELL AND CEMENT WAS PUMPED THROUGH THE PLUG TO FILL WELLBORE AND CASING BELOW THE PLUG ON OCTOBER 19TH, 2017 IN PREPARATION FOR WELL ABANDONMENT. A GEOPHONE ARRAY PRODUCTION SURVEY (GAPS) LOG WAS RUN ON A. SCOTT 1A OBSERVATION WELL ON NOVEMBER 7, 2017 AND A REPORT WAS RECEIVED ON NOVEMBER 9, 2017 INDICATING NO GAS WAS DETECTED LEAKING FROM THE STORAGE ZONE TO THE SURFACE. HOWEVER, GAS WAS DETECTED FLOWING FROM A POROUS ZONE AT APPROXIMATELY 120 FOOT IN DEPTH UP THE OUTSIDE OF WELL CASING TO THE SURFACE. ON NOVEMBER 8, 2017 LG&E WAS NOTIFIED BY THE LANDOWNER OF AN ADJACENT PROPERTY, OUTSIDE OF STORAGE LEASE AREA, OF THREE ABANDONED OIL WELL SITES LEAKING GAS TO THE SURFACE. A NEARBY OBSERVATION WELL (A. SCOTT 2A) RE-PLUGGED IN 2014 WAS RE-ENTERED (AFTER DRILLING OUT CEMENT) AND A GAPS LOG WAS RUN. THE GAPS LOG FOUND GAS FLOWING BEHIND THE CASING FROM THE BOTTOM OF THE WELL TO A POROUS FORMATION AT APPROXIMATELY 120 FEET IN DEPTH. THE A. SCOTT 2A WELL WAS PERFORATED AND CEMENT SQUEEZE PROCEDURE WAS PERFORMED ON NOVEMBER 27, 2017. THE WELL WAS RE-ENTERED (AFTER DRILLING OUT CEMENT AND PLUGS) AND CEMENT BOND AND GAPS LOGS WERE RUN ON DECEMBER 11TH, 2017. THE CEMENT BOND LOG INDICATED CEMENT FROM CEMENT SQUEEZE PROCEDURE WAS SUCCESSFULLY PLACED BEHIND APPROXIMATELY 100 FEET OF THE WELL CASING. THE LOG FOUND THE CEMENT SQUEEZE JOB SUCCESSFULLY SEALED OFF GAS PREVIOUSLY MITIGATING BEHIND CASING TO THE POROUS ZONE AT 120 FEET IN DEPTH (NEED TO VERIFY THIS IS CORRECT AFTER RECEIVING LOG REPORT FROM WEATHERFORD EXPECTED ON DECEMBER 13TH). LG&E IS CONTINUING TO MONITOR SURFACE GAS LEAKS TO VERIFY CORRECTIVE ACTIONS TAKEN HAVE ADDRESSED LEAKS FROM GAS STORAGE ZONE. THE ESTIMATE OF GAS LOSS IN PART A(10) ABOVE INCLUDES OUR BEST ESTIMATE OF GAS WHICH LEAKED FROM THE A SCOTT 2A WELL FROM THE DATE IT WAS RE-PLUGGED IN FEBRUARY 2014 (WHICH IS OUR BEST ESTIMATE OF THE DATE WHEN THE LEAK MAY HAVE STARTED) UNTIL THE LEAK WAS REMEDIATED ON NOVEMBER 27, 2017. NO LOSS IS ESTIMATED FROM THE A SCOTT 1A OBSERVATION WELL BECAUSE, AS NOTED ABOVE, IT WAS DETERMINED THAT NO GAS WAS LEAKING FROM THE STORAGE ZONE AT THAT LOCATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20170124 | 30752 | 2017-12-20 16:11 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2017-11-20 21:51 | 2017 |  |  | 42.7109 | -83.2915 | 1197815 | 2017-11-21 00:41 |  | NATURAL GAS |  | 341152 | 2848 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-11-20 23:07 | 2018-03-23 19:42 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2017-11-20 21:51 | 2017-11-20 22:43 | ONSHORE | MI | 48359 | ORION CHARTER TOWNSHIP | OAKLAND | SURVEY STATION NO. | 994+93 | LINE 600 | LINE 600 DIXIE-WATERFORD CG TO ORION CG | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 250 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 22 |  | 0.281 | 52000 | API5LX-52 | LONGITUDINAL ERW - HIGH FREQUENCY |  | YOUNGSTOWN SHEET & TUBE COMPANY | OTHER | TRENTON INNER-COAT, PRIME COAT AND MUMMY WRAP ALSO SOME NO-OX-ID 6X WAX | [27 empty] | 1951 | 1951 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 69.1 | 22 |  | CLASS 2 LOCATION | NO |  | 182 |  | NO | NO | NO |  | 300000 | 319090.403853279 | 8188 | 8709.04075583549 | 980812 | 898291.759615385 | 5966210 | 6345867.86124491 | 1500 | 1595.45201926639 | 0 | 0 |  |  | 7256710 | 3995421.60067475 | 7573554.51748867 | [8 empty] | 607 |  | 790 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 34320 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | APPROPRIATE RESPONSE PROTOCOLS WERE FOLLOWED IN RESPONSE TO ALARMS RECEIVED INDICATING A POSSIBLE PIPELINE RUPTURE. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | YES | [7 empty] | YES | OVERLOAD FAILURE DUE TO FILL MATERIAL PLACED OVER THE PIPELINE | [19 empty] | YES | OVERLOAD FAILURE DUE TO FILL MATERIAL PLACED OVER THE PIPELINE | [55 empty] | YES | YES | [5 empty] | YES | 2015 | [49 empty] | ELECTRO-MAGNETIC ACOUSTIC TRANDUCER (EMAT) INLINE INSPECTION | 2017 |  |  |  |  | YES | 1967 | 1035 | Yes, and an investigative dig was cunducted at the point of the Accident | 2009 | [12 empty] | YES | 2009 | [6 empty] | YES | [55 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  |  |  |  | JASON PIONK | SENIOR ENGINEERING TECHINICAL ANALYST LEAD | 989-791-5749 | jason.pionk@cmsenergy.com | ON NOVEMBER 20, 2017 AT 2150 HOURS, A BURIED 22-INCH-DIAMETER INTRASTATE NATURAL GAS TRANSMISSION PIPELINE (LINE 600), OWNED AND OPERATED BY CONSUMERS ENERGY RUPTURED IN ORION CHARTER TOWNSHIP (OAKLAND COUNTY) BETWEEN BALDWIN AND JOSLYN ROADS. LINE 600 STRETCHES APPROXIMATELY 34 MILES FROM THE CLARKSTON JUNCTION INTERCHANGE IN CLARKSTON, MI (OAKLAND COUNTY) TO THE UTICA CITY GATE, UTICA, MI (MACOMB COUNTY). CONSUMERS ENERGY EMPLOYEES ARRIVED ONSITE AT APPROXIMATELY 2243 HOURS AND BEGAN THE PROCESS OF ISOLATING THE 6.5 MILE SEGMENT OF LINE 600 UTILIZING EMERGENCY VALVES LOCATED AT ORION CITY GATE, ORION CHARTER TOWNSHIP, MI AND DIXIE-WATERFORD CITY GATE, CLARKSTON, MI. THE SEGMENT WAS FULLY ISOLATED AND CLOSED AT APPROXIMATELY 2307 HOURS. THE ESCAPING HIGH-PRESSURE NATURAL GAS IGNITED. FIRE DAMAGE EXTENDED ALONG THE PIPELINE RIGHT-OF-WAY AND DAMAGED SEVERAL TRACTOR TRAILERS PARKED AT THE REAR OF THE PROPERTY AT 693 BROWN ROAD. LOCAL POLICE AND FIRE PERSONNEL RESPONDED. THERE WERE NO FATALITIES OR INJURIES AS A RESULT OF THE RUPTURE. THE DAMAGED PIPELINE AND ASSOCIATED FRAGMENTS WERE SECURED AND TRANSPORTED TO CONSUMERS ENERGY'S TRAIL STREET LABORATORY FOR METALLURGICAL TESTING AND DETERMINATION OF A FAILURE MODE. A PRELIMINARY CAUSE OF FAILURE HAS BEEN IDENTIFIED AS OVERLOAD FAILURE DUE TO FILL MATERIAL PLACE OVER THE PIPELINE. AN INTERNAL TEAM WAS ASSEMBLED IMMEDIATELY FOLLOWING THE INCIDENT TO COMPLETE A ROOT CAUSE INVESTIGATION. THE INVESTIGATION INCLUDED DEVELOPING A SEQUENCE OF EVENTS, AND A REVIEW OF THE SCENE AND PERTINENT FACTS NEEDED TO IDENTIFY A ROOT CAUSE(S). COUNTERMEASURES WILL ALSO BE DEVELOPED TO PREVENT RE-OCCURRENCE. THE RUPTURED SEGMENT OF LINE 600 WILL NOT BE RETURNED TO SERVICE UNTIL THE INVESTIGATION AND APPROPRIATE REMEDIATION ACTIONS HAVE BEEN COMPLETED. CONSUMERS ENERGY LABORATORY SERVICES CONCLUDED THE RUPTURE ON CONSUMERS ENERGY LINE 600 WAS THE RESULT OF A TENSILE OVERLOAD THROUGH THE 22" OD X 0.281 WALL PIPE ADJACENT TO THE EAST END GIRTH WELD WHERE AN 11.8' SECTION OF 22" OD X 0.375 WALL PIPE WAS INSTALLED DURING REMEDIATION WORK IN 2009. THE INSTANTANEOUS NATURE OF OVERLOAD FAILURE AND THE TIME DURATION FROM WHEN THE PIPE WAS INSTALLED UNTIL THE FAILURE OCCURRED SUGGESTS LOADING CONDITIONS CHANGED OVER TIME; HOWEVER, THE EXACT CAUSE FOR THIS FAILURE COULD NOT BE DETERMINE FROM METALLOGRAPHIC ANALYSIS. CORROSION WAS NOT FOUND TO BE A CONTRIBUTING FACTOR IN THE FAILURE. THE RCA TEAM SIMILARLY DETERMINED THE ROOT CAUSE OF THE PIPELINE FAILURE TO BE OVERLOAD AS A RESULT OF APPROXIMATELY 21' OF FILL MATERIAL ON TOP OF THE GAS PIPELINE WHICH LACKED SUPPORT DUE TO THE PRESENCE OF HIGHLY COMPRESSIBLE SOILS BELOW THE PIPELINE. THE WELD ID OFFSET (HI-LO) WHICH EXCEEDED CODE ALLOWABLE 0.155" VERSUS 3/32" (.09375) AT THE 2009 REMEDIATION TIE-IN TO EXISTING PIPE WAS DETERMINE TO BE A CONTRIBUTING FACTOR BUT NOT A SECONDARY ROOT CAUSE. THE RCA TEAM ALSO IDENTIFIED HUMAN AND SYSTEMIC ROOT COMPONENTS THAT MAY HAVE CONTRIBUTED TO THE FAILURE. CORRECTIVE ACTIONS TO MINIMIZE THE POTENTIAL FOR REOCCURRENCE HAVE BEEN IMPLEMENTED. CONSUMERS ENERGY REPLACED APPROXIMATELY 1,200 FEET OF LINE 600 NORTH OF BROWN RD. AND WEST OF JOSLYN RD. IN LAKE ORION, MI. THE ENTIRE DISTANCE WAS REPLACED USING HORIZONTAL DIRECTIONAL DRILLING METHODS (HDD). THE HDD METHOD WAS SELECTED IN ORDER TO ACHIEVE DEPTHS BELOW THE COMPRESSIBLE ORGANIC SOIL LAYERS THAT CONTRIBUTED TO THE FAILURE OF THE PIPELINE. ALL REMEDIATION ACTIVITIES AND HYDROSTATIC TESTING WERE PERFORMED IN ACCORDANCE WITH APPLICABLE REGULATIONS AND THE RUPTURE SEGMENT OF THE PIPELINE WAS RETURNED TO NORMAL OPERATIONS ON FRIDAY, MARCH 23, 2018.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20170125 | 17559 | 2017-12-27 12:11 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2017-11-29 15:55 | 2017 |  |  | 42.386 | -73.3539 | 1198362 | 2017-11-29 16:36 |  | NATURAL GAS |  | 10960 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | NO, RELIEF VALVE WAS ISOLATED FOR INVESTIGATION AND CALIBRATION | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-11-29 15:55 | 2017-11-29 16:00 | ONSHORE | MA | 01201 | Not Within a Municipality | BERKSHIRE | SURVEY STATION NO. | 198+66 | TGP LINE 256-1 | 254-1 TO 261-1 SEGMENT | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1986 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE ACTIVATION | CLASS 2 LOCATION | NO |  | 448 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 31565 | 28909.2908653846 | 250 | 265.908669877733 | 250 | 265.908669877733 | 0 | 0 |  |  | 32065 | 30215.6927111537 | 29441.1082051401 | [8 empty] | 745 |  | 730 | 192.619(C) |  |  |  | PRESSURE EXCEEDED MAOP, BUT DID NOT EXCEED THE APPLICABLE ALLOWANCE IN 192.201 | NO |  |  |  |  | MANUAL | MANUAL | 2 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELIEF VALVE POPPED INTERMITTENTLY AND RESEATED EACH EVENT | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [23 empty] | YES | [167 empty] | WM MARTIN MULLER | SPECIALIST - PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 2053253863 | 2053253592 |  |  |  | REJI GEORGE | DIRECTOR COMPLIANCE CODES AND STANDARDS | 7134205433 | reji_george@kindermorgan.com | ALL TIMES ARE EASTERN STANDARD TIME; 48-HOUR UPDATE TO NRC WAS 12/01/2017 AT 13:55 EST; REPORT NUMBER 1198362; KM PIR = 488 FEET; PUBLIC AND LOCAL FIRE DEPARTMENT REPORTED RELIEF VALVE ACTIVATION; INTERMITTENT "POPS"; RELIEF VALVE WOULD RESEAT; LOCATED ON PIPELINE; NOT AT COMPRESSOR STATION; PROTECTING DOWNSTREAM 730 MAOP; 8-INCH PLUG VALVE BENEATH RELIEF VALVE WAS USED TO ISOLATE RELIEF VALVE; RELIEF VALVE WAS INSPECTED AND TESTED THEN RETURNED TO SERVICE;
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180001 | 30324 | 2018-01-02 12:28 | SUPPLEMENTAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2017-12-11 14:38 | 2017 |  |  | 30.2403 | -92.9035 | 1199394 | 2017-12-11 17:15 |  | NATURAL GAS |  | 21608 | 3980 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-12-11 17:48 | 2017-12-13 15:55 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-12-11 16:00 | 2017-12-11 17:03 | ONSHORE | LA | 70647 | LACASSINE | JEFFERSON DAVIS | MILEPOST | 3+2650 | WOODLAWN-LACASSINE JUNCTION | WLJ | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 84 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 14 |  | 0.312 | 35000 | API 5L | SEAMLESS |  | NATIONAL TUBE | COAL TAR | [28 empty] | 1949 | 1949 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 29 | 0.4 |  | CLASS 1 LOCATION | NO |  | 313 |  | NO | NO | NO |  | 0 | 0 | 12451 | 13243.3153945906 | 67598 | 61910.6682692308 | 43000 | 45736.29121897 | 2050 | 2180.45109299741 | 0 | 0 |  |  | 125099 | 92259.6812690598 | 123070.725975789 | [8 empty] | 796 |  | 1050 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 77649 | NO | YES | [6 empty] | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES |  |  |  | YES | OTHER | FAILURE SURFACE APPEARS TO BE FATIGUE; SEE NARRATIVE IN PART H. | [19 empty] | YES | [59 empty] | NO | [63 empty] | YES | 1977 | 1404 | NO | [13 empty] | NO | [63 empty] | SHANNON MATTINGLY | PA OQ AND EVENT SUPPORT PROGRAM LEADER | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | DARRAL WARD | MANAGER PIPELINE SAFETY | 2706886356 | darral.ward@bwpmlp.com | A POTENTIAL LEAK ON TEXAS GAS'S WLJ 14" LINE WAS REPORTED BY A LOCAL FARMER. OPERATIONS PERSONNEL CONFIRMED THE LEAK. THE LINE WAS ISOLATED AND REPAIRED AND RETURNED TO SERVICE. CAUSE REMAINS UNDER INVESTIGATION. 3-5-2018 *GAS CONTROL CENTER, THROUGH SCADA, IDENTIFIED A POTENTIAL SYSTEM UPSET AND CONTACTED FIELD OPERATIONS TO INVESTIGATE. CONCERN WAS POTENTIAL LOSS OF GAS. WHILE FIELD OPERATIONS WERE PERFORMING THEIR INVESTIGATION, A LAND OWNER NOTIFIED CONTROL CENTER THAT OUR PIPELINE WAS LEAKING. BASED ON THE FACT THAT OUR SCADA INDICATED A LOSS OF GAS AND WAS CONFIRMED BY A LAND OWNER, TEXAS GAS DECLARED DISCOVERY OF AN INCIDENT ON OUR SYSTEM WHICH WAS ON 12-11-17 AT 16:42. *FIELD PERSONNEL ARRIVED ONSITE ON 12-11-17 AT 17:03 AND RECONFIRMED PIPELINE LEAK WAS OURS. *NRC WAS CALLED ON 12-11-17 AT 17:15. *A DECISION WAS MADE TO BLOCK THE PIPELINE AND ALLOW THE GAS PRESSURE TO DISSIPATE THROUGH THE LEAK LOCATION. 5-9-18 REVISED TO UPDATE VARIOUS DETAILS INCLUDING A4 CALCULATION USING METHODOLOGY RECENTLY PROVIDED BY PHMSA. UPDATED COSTS. REPAIR WAS MADE BY REPLACING A PUP OF PIPE. IN REGARD TO PART G, THE METALLURGICAL REPORT INDICATED THAT THE FAILURE SURFACE WAS ASSOCIATED WITH FATIGUE. TEXAS GAS ENLISTED THE SERVICES OF STRESS ENGINEERING SERVICES, INC. TO EVALUATE EQUIPMENT LOADING, PRESSURE CYCLING, TEMPERATURE, AND OTHER SOURCES OF FATIGUE ON THE PIPELINE. WE ASSUME THAT THE POTENTIAL FOR FATIGUE OCCURRED DUE TO THE CONSTRUCTION METHODS USED AT THE TIME SINCE THIS LOCATION IS ASSOCIATED WITH A WRINKLE BEND. BASED ON OUR ANALYSIS, WE BELIEVE THIS IS A UNIQUE SITUATION AND IS NOT A SYSTEMIC ISSUE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180002 | 17596 | 2018-01-03 13:07 | SUPPLEMENTAL FINAL | 2620 | COLUMBIA GULF TRANSMISSION, LLC | 700 LOUISIANA ST. SUITE 700 | HOUSTON | TX | 77002 | 2017-12-09 20:44 | 2017 |  |  | 31.4377 | -92.2297 | 1199253 | 2017-12-09 21:55 |  | NATURAL GAS |  | 5229 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RESPONDING OPERATIONS PERSONNEL, WERE ABLE TO MANUALLY CLOSE THE ESD VALVE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-12-09 20:44 | 2017-12-09 21:03 | ONSHORE | LA | 71328 | HOLLOWAY | RAPIDES | MILEPOST | BLOWDOWN VLV | ALEXANDRIA COMPRESSOR STATION | ML 200 AND ML 300 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2015 |  | CARBON STEEL |  | OTHER | [8 empty] | MALFUNCTION OF A 12" ESD VALVE, RESULTING IN NATURAL GAS EXITING THROUGH THE ASSOCIATED 6 " BLOWDOWN PIPING | CLASS 2 LOCATION | NO |  | 337 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 15687 | 14367.1802884615 | 0 | 0 | 750 | 797.726009633197 | 0 | 0 |  |  | 16437 | 15261.2854609613 | 15164.9062980947 | [8 empty] | 777 |  | 1007 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE MALFUNCTION OF THE ESD VALVE ACTIVATION WAS NOT DUE TO ANY INVOLVEMENTS BY GAS CONTROL PERSONNEL | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | A SHORT IN THE POWER SUPPLY CONNECTION DUE TO CORRODED WIRES IN TERMINAL STRIPS | [161 empty] | CODY BOWERS | U.S. REGULATORY COMPLIANCE SPECIALIST | cody_bowers@transcanada.com | 304-357-2814 |  |  |  |  | LEE ROMACK | MANAGER - U.S. REGULATORY COMPLIANCE | 832-320-5315 | lee_romack@transcanada.com | ON DECEMBER 9TH, 2017, ALEXANDRIA COMPRESSOR STATION (CS) WAS SUBJECT TO AN UNINTENTIONAL RELEASE OF NATURAL GAS (MATERIAL) RESULTING IN MATERIAL LOSS EXCEEDING 3,000 MCF. ALEXANDRIA IS A TRANSMISSION CS THAT IS MAINTAINED BY COLUMBIA GULF TRANSMISSION, LLC (TRANSCANADA) AND IS LOCATED IN RAPIDES PARISH, NEAR THE TOWN OF HOLLOWAY, LOUISIANA. AT APPROXIMATELY 20:44 CST TRANSCANADA'S GAS CONTROL PERSONNEL NOTED VIA A SCADA ALARM OF A POTENTIAL PRESSURE DROP ON THE TURBINE PIPING ASSOCIATED WITH THE SUCTION SIDE OF LINE 200 AND 300 OF ALEXANDRIA'S CS. OPERATIONS PERSONNEL WERE IMMEDIATELY DISPATCHED TO INVESTIGATE THE EVENT. AT 21:03 CST, OPERATIONS PERSONNEL ARRIVED ON SITE WHERE THE UNINTENDED RELEASE OF MATERIAL WAS IDENTIFIED AND ISOLATED AT APPROXIMATELY 21:05 CST. ONCE OPERATIONS PERSONNEL ISOLATED THE LEAK AND MADE THE AREA SAFE, GAS CONTROL WAS NOTIFIED TO FOLLOW-UP ON THE NECESSARY FOLLOW-UP ACTIONS AND REQUIRED INVESTIGATIONS. THE PRELIMINARY MATERIAL LOSS CALCULATIONS WERE DETERMINED TO BE GREATER THAN 3,000 MCF, HENCE, THE EVENT WAS REPORTED TO THE NATIONAL RESPONSE CENTER AS AN INCIDENT. FURTHER INVESTIGATION DETERMINED THE PROBABLE CAUSE OF THE EVENT THAT LED TO A REPORTABLE INCIDENT INCLUDED CORRODED WIRES ON A VERSA VALVE SOLENOID CONNECTION IN CONJUNCTION WITH THE ASSOCIATED PLC LOGIC, IN WHICH WERE REMEDIATED BEFORE THE VALVE WAS RETURNED TO OPERATION. A 48-HR. UPDATE NOTICE WAS CALLED-IN TO THE NRC WHERE THE UPDATE REPORT NO. WAS 1199309.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180003 | 17615 | 2018-01-03 16:17 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2017-12-19 21:19 | 2017 |  |  | 37.5885 | -81.0921 | 1200116 | 2017-12-20 01:13 |  | NATURAL GAS |  | 8836 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-12-20 00:35 | 2017-12-21 08:46 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-12-19 22:52 | 2017-12-19 23:50 | ONSHORE | WV | 25841 | FLAT TOP | SUMMERS | MILEPOST | BLOWDOWN VLV | FLAT TOP COMPRESSOR STATION | LINE KA AND LINE KA-LOOP | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1998 |  | CARBON STEEL |  | OTHER | [8 empty] | PARTIAL CLOSURE OF A COMPRESSOR STATION UNIT'S 20" BALL VALVE, RESULTING IN NATURAL GAS EXITING THROUGH A 3-INCH BLOW-OF VALVE TO ATMOSPHERE. | CLASS 2 LOCATION | NO |  | 521 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 25713 | 23549.6466346154 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 25713 | 24414.9879807692 | 23549.6466346154 | [8 empty] | 813 |  | 1000 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE BALL VALVE PARTIAL CLOSURE WAS NOT DUE TO ANY INVOLVEMENTS BY GAS CONTROL PERSONNEL. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | WRONG EQUIPMENT SPECIFIED OR INSTALLED | INCORRECT OPERATION | INCORRECT EQUIPMENT | [204 empty] | WRONG EQUIPMENT SPECIFIED OR INSTALLED |  |  |  | YES |  | YES |  |  | NORMAL OPERATING CONDITIONS | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | MARK NEWMAN | COMPLIANCE SPECIALIST - US REGULATORY COMPLIANCE | mark_newman@transcanada.com | 304-722-8475 | 304-722-8420 |  |  |  | LEE ROMACK | MANAGER - US REGULATORY COMPLIANCE | 832-320-5315 | lee_romack@transcanada.com | ON DECEMBER 19, 2017, FLAT TOP COMPRESSOR STATION (CS) WAS SUBJECT TO AN UNINTENTIONAL RELEASE OF NATURAL GAS (MATERIAL) RESULTING IN GAS LOSS OF MORE THAN 3,000 MCF. FLAT TOP IS A TRANSMISSION CS THAT IS MAINTAINED BY COLUMBIA GAS TRANSMISSION, LLC (TRANSCANADA). FLAT TOP CS IS LOCATED IN SUMMERS COUNTY, NEAR THE TOWN OF FLAT TOP, WEST VIRGINIA. AFTER THE REMOTE SHUTDOWN OF CS UNIT# 3, MATERIAL PASSED THROUGH A SMALL OPENING OF A 20 INCH BALL VALVE. SUBSEQUENTLY, MATERIAL EXITED A 3 INCH BLOWDOWN STACK TO ATMOSPHERE BEGINNING ON DECEMBER 19, 2017 AT APPROXIMATELY 21:19 EST FOR ABOUT 164 MINUTES. THE PRESSURE IN THE CS UNIT'S PIPING SLOWLY DECREASED FROM APPROXIMATELY 813 PSIG TO 740-760 PSIG. THE 20 INCH BALL VALVE WAS CLOSED AT 00:35 EST ON DECEMBER 20, 2017. OPERATION PERSONNEL NOTICED UNIT# 3 WAS DOWN WHILE INVESTIGATING A NOTIFICATION OF A STATION MODE CHANGE. GAS CONTROL WAS CONTACTED TO SEE IF A CALLOUT WAS MADE. PERSONNEL WAS NOT DISPATCHED TO MONITOR THE VALVE OPERATION. LOCAL PERSONNEL REPORTED TO THE LOCATION TO CLOSE THE VALVE AND STOP THE RELEASE OF NATURAL GAS. SCADA UPGRADES PLACED INTO SERVICE ON 8/22/2017, SET WARNING TAG TO ALERT THE GAS CONTROLLER TO REQUEST A CALLOUT FOR LOCAL OPERATING PERSONNEL TO MONITOR THE 20 INCH BALL VALVE OPERATION ON UNIT# 3. THIS WAS SET UP AS AN INTERIM PROCESS UNTIL A NEW VALVE ACTUATOR WAS INSTALLED IN 2018. DURING THE SCADA UPGRADE THE WARNING TAG WAS INADVERTENTLY REMOVED FROM THE DISPLAY. IN ORDER TO PREVENT A REOCCURRENCE, PROCEDURE CHANGES HAVE BEEN IMPLEMENTED TO PREVENT A WARNING TAG FROM BEING REMOVED. ADDITIONALLY, A NOTIFICATION EMAIL HAS BEEN ESTABLISHED IF UNIT#3 GOES OUT OF RUN STATUS FOR ANY REASON, SEVERAL KEY OPERATORS ARE NOTIFIED OF THE STATUS CHANGE.
2021-02-26 10:37 | YES | YES | GT (Gas Transmission) | 20180005 | 30403 | 2018-01-03 21:00 | SUPPLEMENTAL FINAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2017-12-05 09:35 | 2017 |  |  | 41.8414 | -89.3855 | 1198853 | 2017-12-05 10:33 |  | NATURAL GAS |  | 12972 | 16538 | 0 | YES | 0 | 0 | 0 | 2 | 0 | 2 | YES | 0 | 0 | 0 | 2 | 0 | 2 |  | YES |  | 2017-12-05 10:44 | 2017-12-09 16:39 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 0 | 2017-12-05 09:35 | 2017-12-05 10:47 | ONSHORE | IL | 61057 | Not Within a Municipality | LEE | MILEPOST | STN: 2777+18 | ILLINOIS LATERAL NO. 1 | CS 110 TO GENOA CITY 2 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 45 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.281 | 40000 | API 5L | FLASH WELDED |  | AO SMITH | OTHER | CTE | [27 empty] | 1941 | 1940 | CARBON STEEL |  | MECHANICAL PUNCTURE | 12 | 12 | [7 empty] | CLASS 1 LOCATION | NO |  | 390 |  | NO | YES | NO |  | 650000 | 691362.541682104 | 47381 | 50396.0747499074 | 37160 | 34033.5576923077 | 226200 | 240594.164505372 | 5000 | 5318.17339755465 | 7500 | 7977.26009633197 | SURVEY AND METALLURGICAL EXAMINATION. |  | 973241 | 492312.937042209 | 1029681.77212358 | [8 empty] | 706 |  | 800 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | AUTOMATIC | 72108 | NO |  | YES | [5 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: THIRD-PARTY STRIKE ON PIPELINE FROM USE OF DRAIN TILING MACHINE ON RIGHT-OF-WAY. NO ONE-CALL NOTIFICATION PROVIDED/RECEIVED. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | YES | [6 empty] | FARMER | FARM EQUIPMENT | AGRICULTURE | NO | [5 empty] | YES | 102 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | STEPHEN R. DINES | PIPELINE ENGINEER | stephen_dines@kindermorgan.com | (719) 329-5633 |  |  |  |  | JAIME A. HERNANDEZ | DIRECTOR ENGINEERING - CODES AND STANDARDS | (713) 369-9443 | jaime_hernandez@kindermorgan.com | ON TUESDAY, DECEMBER 5, 2017 AT 9:35 AM LOCAL TIME, NATURAL GAS PIPELINE COMPANY OF AMERICA LLC'S (NGPL) 20-INCH PIPELINE, KNOWN AS THE ILLINOIS LATERAL NO. 1 IN LEE COUNTY, ILLINOIS, WAS STRUCK BY A THIRD PARTY OPERATING DRAIN TILE EQUIPMENT. THE INCIDENT OCCURRED AT APPROXIMATELY STATION 2777+18 ON THE ILLINOIS LATERAL NO. 1. UPON CONFIRMATION THAT THE THIRD-PARTY STRIKE CAUSED A RUPTURE AND FIRE RESULTING IN THE DEATHS OF TWO (2) PERSONS AND INJURIES TO TWO (2) OTHERS, WHO WERE IMMEDIATELY HOSPITALIZED, NGPL ISSUED A REVISED NRC NOTICE (NO. 1198866). ONE OF THE INJURED PERSONS WAS RELEASED ON DECEMBER 6, 2017, AND THE OTHER WAS LISTED AS BEING IN STABLE CONDITION ON THE DAY FOLLOWING THE INCIDENT. TWO AUTOMATIC VALVES (I-9 AND I-10) ON THE ILLINOIS LATERAL NO. 1 BEGAN TO CLOSE UPON THE DETECTION OF A PRESSURE LOSS AND ISOLATE THE DAMAGED PORTION OF PIPELINE, AS DESIGNED. VALVE I-9 REQUIRED ADDITIONAL MANUAL OPERATION TO FULLY CLOSE THE VALVE. THIS WAS COMPLETED BY 10:44 AM LOCAL TIME, WITH THE FLOW OF GAS SHUT OFF, THE FIRE CONTAINED, AND LATER EXTINGUISHED. AS A PRECAUTIONARY MEASURE, NGPL ALSO REDUCED THE PRESSURE OF THE ADJACENT ILLINOIS LATERAL NO. 2 TO 485 PSIG PENDING AN INVESTIGATION TO DETERMINE IF IT SUSTAINED ANY DAMAGE AS A RESULT OF THE INCIDENT. UPON ARRIVAL AT THE SITE, A PHMSA REPRESENTATIVE REQUESTED THAT NGPL FURTHER REDUCE THE OPERATING PRESSURE OF ILLINOIS LATERAL NO. 2 TO 450 PSIG, WHICH NGPL DID. RESULTS OF THE ILLINOIS LATERAL NO. 2 INVESTIGATION REVEALED THAT NO DAMAGE WAS SUSTAINED AND NGPL BEGAN RE-PRESSURING ILLINOIS LATERAL NO. 2 TO NORMAL OPERATING PRESSURE, CONSISTENT WITH PHMSA REGULATORY REVIEWS AND APPROVALS. ON WEDNESDAY, DECEMBER 6, 2017, NGPL BEGAN REPAIRS TO ILLINOIS LATERAL NO. 1. A FINAL 48-HOUR CONFIRMATION NRC REPORT NO. 1199018 WAS PROVIDED THAT SAME DAY WITH A FINAL ESTIMATED VOLUME OF THE RELEASE. REPAIR WORK CONSISTED OF THE REPLACEMENT OF 41 FEET OF 20-INCH PIPE ON THE ILLINOIS LATERAL NO. 1 WITH PRE-PRESSURE TESTED PIPE AND WAS COMPLETED ON DECEMBER 9, 2017, AND AT 4:39 PM CENTRAL TIME, NGPL PLACED ILLINOIS LATERAL NO. 1 BACK INTO FULL SERVICE. NGPL INITIATED AN INVESTIGATION INTO THE CAUSE OF THE INCIDENT AND CONCLUDED THAT THE LINE STRIKE AND RUPTURE RESULTED FROM M&R FARMS FAILING TO SUBMIT A LOCATE REQUEST TO JULIE AS REQUIRED BY ILLINOIS LAW PRIOR TO COMMENCING ITS EXCAVATION WORK RELATED TO THE INSTALLATION OF DRAINAGE TILE. BECAUSE M&R FARMS FAILED TO PROVIDE THE REQUISITE NOTIFICATION, NGPL WAS UNABLE TO RESPOND, AND SPECIFICALLY WAS UNABLE TO MARK THE LOCATION OF ITS PIPELINE FACILITIES AND FOLLOW PROCEDURES RELATED TO DAMAGE PREVENTION. NO OTHER POTENTIAL CAUSES WERE IDENTIFIED DURING THE INVESTIGATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180006 | 30429 | 2018-01-04 13:20 | SUPPLEMENTAL FINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2017-12-08 06:25 | 2017 |  |  | 35.5958 | -93.8292 | 1199139 | 2017-12-08 09:05 |  | NATURAL GAS |  | 33774 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-12-08 06:28 | 2017-12-08 08:14 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 0 | 2017-12-08 06:25 | 2017-12-08 06:25 | ONSHORE | AR | 72949-0000 | OZARK | FRANKLIN | MILEPOST | UNKNOWN | DRAKE COMPRESSOR | UNKNOWN | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 27 |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 12 |  | 0.21 | 24000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1972 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 24 | 12 |  | CLASS 1 LOCATION | NO |  | 223 |  | NO | NO | NO |  | 11414 | 12140.3262319378 | 0 | 0 | 100650 | 92181.8509615385 | 1415284 | 1505345.14375695 | 2100 | 2233.63282697295 | 0 | 0 |  |  | 1529448 | 793160.279343133 | 1611900.9537774 | [8 empty] | 655 |  | 866 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INTERNAL EROSION AND EXTERNAL CORROSION WAS DETERMINED TO BE THE CONTRIBUTING FACTOR TO THIS INCIDENT | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1972 | YES | YES | YES |  |  |  | 2017 |  |  |  | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | PRESTON WALKER | COMPLIANCE COORDINATOR | preston.walker@blackhillscorp.com | 479-575-1496 |  |  |  |  | BILL STEPHENS | SR MGR CODES AND STANDARDS | 303-566-3509 | bill.stephens@blackhillscorp.com | AT APPROXIMATELY 6:25 AM, THE 12" DISCHARGE PIPE FROM UNIT #13 & UNIT 14 BLEW OUT ON THE NORTHWEST CORNER OF THE COMPRESSOR BUILDING, FOLLOWED BY A LOUDER "BOOM" AND THEN A HUGE FIREBALL FOLLOWED. THERE WERE TWO COMPRESSOR OPERATOR WORKING (SCOTTY MAYFIELD AND TYLER DAHLEM), THAT WERE LOCATED JUST EAST OF THE BLOW OUT. THEY WERE NOT INJURED BUT WERE CLOSE ENOUGH TO FEEL THE PERCUSSION FROM THE BLAST. THEY IMMEDIATELY RAN TO THE MAIN ENTRY GATE OF THE STATION WHERE ONE OF THE THREE ESD ACTIVATION SITES ARE LOCATED AND ACTIVATED THE ESD FOR THE WHOLE STATION (6:33 A.M. ACCORDING TO THE HISTORY ON SCADA) SINCE IT WAS STILL UNCLEAR WHAT ALL WAS ON FIRE. THIS ONLY TOOK A COUPLE OF MINUTES. AFTER THE ESD WAS ACTIVATED THE BLOWING GAS AND FIRE IMMEDIATELY BEGAN TO DECREASE. THE OPERATORS DID NOT HAVE A CELL PHONE WITH THEM, SO SCOTTY, THE SENIOR OPERATOR INSTRUCTED TYLER, THE TRAINEE COMPRESSOR OPERATOR I, TO RUN OVER TO THE NEIGHBOR'S HOUSE AND CALL 911. SCOTTY WENT AROUND THE SOUTH FENCE OUT OF THE "HOT ZONE" TO GET BACK TO THE OFFICE AND THEN CALLED HIS SUPERVISOR, JUNIOR BOWEN AND JAMES DAHLEM. (JAMES DAHLEM AND TIM REYNOLDS WAS ALREADY AT THE OZARK OPERATIONS CENTER AND WENT IMMEDIATELY TO DRAKE STATION TO HELP. JUNIOR BOWEN WAS STILL AT HOME AND IMMEDIATELY HEADED THAT WAY WHILE CONTACTING 911, AMY YORK, KEITH MASINGALE, BJ WILLSON, GARY ENGLISH AND BRENT SAMPLEY) SCOTTY THEN CALLED GAS CONTROL AND RELAYED WHAT WAS HAPPENING AND ASKED THEM TO SHUT OFF THE WOOLSEY AND STOCKTON STORAGE. BY THIS TIME JAMES DAHLEM AND TIM REYNOLDS ARRIVED AND PARKED AT THE ENTRANCE AND STARTED MONITORING THE AIR FOR GAS LEL TO MAKE SURE IT WAS SAFE TO ENTER. THEY STARTED HELPING SCOTTY AND TYLER FIGURE OUT WHAT HAD ACTUALLY HAPPENED, HAD TO SHUT THE GAS OFF OF THE DUMP LINE AT UNIT #15 BECAUSE THE BLOWN OUT 12" LINE HAD BROKEN THE PLASTIC DUMP LINE AND IT WAS ON FIRE. BJ WILLSON, FIRE DEPARTMENT AND STATE POLICE ARRIVED RIGHT BEHIND JAMES DAHLEM AND WE ASKED THE POLICE AND FIRE DEPT. TO KEEP NON-BLACK HILLS PEOPLE AWAY. WE ALSO ASKED THE FIRE DEPARTMENT TO STAND-BY UNTIL WE HAD SECURED ALL BLOWING GAS. BRENT SAMPLEY ARRIVED AND THEN JUNIOR BOWEN ARRIVED. I (JUNIOR BOWEN) STARTED ACCESSING WHERE THE DAMAGE WAS AND BECAME THE ON-SEEN INCIDENT COMMANDER. I WAS COMMUTING VIA PHONE WITH GAS CONTROL AND THE ERL PHONE CALL TO COORDINATE GETTING GAS BACK INTO SERVICE AND GETTING CONSTRUCTION CREWS ON THE WAY TO HELP REPAIR THE BROKEN GAS LINE. AFTER WE WERE SURE ALL BLOWING GAS HAD BEEN SECURED I HAD THE COMPRESSOR OPERATORS START RETURNING UNITS BACK TO SERVICE. ACCORDING TO THE HISTORICAL DATA ON THE SCADA THE COMPRESSORS STARTED BACK IN SERVICE AT 8:14 AM. WE THEN ASKED THE FIRE DEPARTMENT TO COME INTO THE COMPRESSOR STATION AND PUT OUT THE SMALL FIRE (NONE GAS) ON THE #14 COMP. THE FIRE DEPARTMENT THEN WENT TO THE NORTH SIDE OF THE STATION OUTSIDE OUR PROPERTY AND PUT OUT A SMALL BRUSH FIRE. WITH THE DAMAGED PIPE ISOLATED THIS TOOK 5 COMPRESSORS OUT OF SERVICE. THE CONSTRUCTION CREWS REMOVED THE DAMAGED SECTION OF PIPE AND PIPELINE INTEGRITY GROUP ASSESSED THE REMAINING PIPE WE ABLE TO PUT THREE COMPRESSORS BACK INTO SERVICE. UNITS #13 AND #14 WERE NOT ABLE TO RETURN TO SERVICE BECAUSE OF EXTENSIVE DAMAGE. PHMSA/APSC REPORTING (PRESTON WALKER) O FIRST NOTIFICATION OF THIS INCIDENT TO MR. BOBBY HENRY (APSC) VIA E-MAIL @ 8:20 AM ON 12/08/2017. UPON APPROVAL I NOTIFIED THE NRC@ 8:55 AM AND TALKED TO BRENT AND GAVE A BRIEF DESCRIPTION OF THE INCIDENT. HE PROVIDED ME WITH A REPORT NUMBER# 1199139. I SENT ANOTHER E-MAIL TO MR. BOBBY HENRY @ 8:55 AM INFORMING HIM THAT THE NRC WAS NOTIFIED OF THIS INCIDENT. I RECEIVED A CALL FROM CHRIS RULE WITH THE NRC @ 9:50 AM AND HE WAS INQUIRING ABOUT AN UPDATE ON THE INCIDENT. I PROVIDED HIM WITH AN UPDATE AND HE STATED THAT HE WAS GOING TO CLOSE HIS REPORT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180007 | 31492 | 2018-01-05 17:31 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2017-12-06 12:23 | 2017 |  |  | 37.5569 | -121.906 | 1199008 | 2017-12-06 13:37 |  | NATURAL GAS |  | 1750 | 2670 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-12-06 13:05 | 2017-12-09 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-12-06 12:23 | 2017-12-06 12:40 | ONSHORE | CA | 94586 | SUNOL | ALAMEDA | MILEPOST | 45.31 | LINE 131 |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 24 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 |  | 0.375 | 60000 | API 5L X-60 | DSAW |  | BERG | ASPHALT | [28 empty] | UNKNOWN | 1944 | CARBON STEEL |  | MECHANICAL PUNCTURE | 2 | 4 | [7 empty] | CLASS 1 LOCATION | NO |  | 369 |  | NO | NO | NO |  | 0 | 0 | 11500 | 12231.7988143757 | 7500 | 6868.99038461538 | 314000 | 333981.289366432 | 50000 | 53181.7339755465 | 0 | 0 |  |  | 383000 | 190454.156364893 | 406263.81254097 | [8 empty] | 318 |  | 497 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | REMOTELY CONTROLLED | 2112 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS CAUSED BY 3RD PARTY DIG-IN. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  | YES | PRIVATE LANDOWNER | [7 empty] | DEVELOPER | BACKHOE/TRACKHOE | SITE DEVELOPMENT | NO | [5 empty] | YES | 47 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | ENZA BARBATO | PROGRAM MANAGER | e1bo@pge.com | 925-357-7889 |  |  |  |  | SUSIE RICHMOND | MANAGER GAS OPS COMPLIANCE AND RISK | 925-786-0267 | gsr8@pge.com | ON 12/06/17 AT APPROXIMATELY 1223 HOURS, PG&E WAS NOTIFIED OF A THIRD PARTY DIG IN AT 4255 SHERIDAN ROAD, SUNOL. THE PROPERTY OWNER WAS EXCAVATING A FIRE ROAD USING A D6 BULLDOZER AND STRUCK L-131 (MILE POINT 45.3), A 24' STEEL TRANSMISSION LINE, CAUSING AN UNINTENTIONAL RELEASE OF GAS. THE PROPERTY OWNER DID NOT HAVE A VALID USA TICKET. PG&E GSR ARRIVED ON SITE AT 1240 HOURS AND THE M&C SUPERVISOR ARRIVED ON-SITE AT 1250 HOURS. THE FLOW OF GAS WAS STOPPED AT APPROXIMATELY 1305 HOURS BY REMOTELY CLOSING ISOLATION VALVES LOCATED AT MP 38.72 AND 46.32. THE FIRE DEPARTMENT REMAINED ON SITE UNTIL THE RELEASE OF GAS STOPPED. APPROXIMATELY 11 SERVICES LOST GAS DUE TO THE DIG IN AND 80 CUSTOMERS WERE SHUT IN PROACTIVELY. CNG WAS BROUGHT IN TO SUPPLY AFFECTED CUSTOMERS. AS OF 12/9/17 ALL CUSTOMERS EXCEPT VACANT HOMES AND BUSINESS WERE RESTORED. ON 12/8/17, PG&E REMOVED THE DAMAGED PORTION OF PIPELINE . THESE SECTIONS OF PIPELINE WERE SENT TO AN INDEPENDENT ENGINEERING FIRM (EXPONENT) FOR METALLURGICAL ANALYSIS. THERE WERE NO INJURIES, NO FATALITIES, NO MEDIA AND NO IGNITION ASSOCIATED WITH THIS INCIDENT . THIS INCIDENT IS BEING REPORTED TO THE DOT (1199008) AND THE CPUC DUE TO DAMAGES ESTIMATED TO EXCEED $50,000. AN UPDATE WAS PROVIDED TO THE DOT (1199102) ON 12/7/17.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180008 | 30083 | 2018-01-10 15:49 | SUPPLEMENTAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2017-12-12 15:34 | 2017 |  |  | 33.0357 | -94.9438 | 1199503 | 2017-12-12 17:07 |  | NATURAL GAS |  | 6300 | 310 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-12-12 15:55 | 2017-12-13 16:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-12-12 15:34 | 2017-12-12 07:00 | ONSHORE | TX | 75686 | PITTSBURG | CAMP | MILEPOST | STA #193+55 | AM-53 | AM-53 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | DRESSER COUPLER | 1970 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 120 |  | NO | NO | NO |  | 5000 | 5318.17339755465 | 889 | 945.571230085217 | 18057 | 16537.78125 | 60751 | 64616.8704149685 | 30035 | 31946.2675991108 | 0 | 0 |  |  | 114732 | 64345.7211582994 | 119364.663891719 | [8 empty] | 240 |  | 300 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL |  | NO |  | YES |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE RELEASE WAS DUE TO A UNKNOWN, BURIED DRESSER COUPLING COMING LOOSE FROM THE IN-SERVICE LINE. | [12 empty] | YES | 2 | 0 | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | OTHER | 10"X 16" INSULATED SLEEVE |  |  |  | YES | [175 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | THE AM-53 PROJECT INVOLVED REPLACING APPROXIMATELY 10,000 FEET OF 10" DRESSER COUPLED PIPELINE ON THE EGT INTERSTATE SYSTEM. THE SOUTHERN END OF THE PROJECT WAS DESIGNED TO TIE INTO EXISTING PIPE INSTALLED IN 1994 WHILE THE NORTHERN END OF THE PROJECT WAS DESIGNED TO TIE INTO EXISTING PIPE INSTALLED IN 1970. DOING THIS WOULD REMOVE ALL THE ORIGINAL 1936 VINTAGE, DRESSER COUPLED PIPE IN THIS AREA. ON DEC 12, 2017, AFTER THE LINE REPLACEMENT WAS COMPLETED AND FLOWING GAS, CONSTRUCTION CREWS BEGAN TO COLD CUT AND CAP THE NOW OUT-OF-SERVICE SEGMENT CONTAINING THE DRESSER COUPLES. THE SOUTH END WAS CUT FIRST, REMOVING A SHORT SEGMENT OF 1936 VINTAGE PIPE, AND INSTALLING A WELD CAP. CONSTRUCTION CREWS MOVED TO THE NORTH END OF THE PROJECT TO COMPLETE THE SAME TASKS. A SHORT SECTION OF PIPE WAS REMOVED IN PREPARATION FOR A WELD CAP WHEN AN UNDETECTED DRESSER COUPLING ROUGHLY 20 FEET UPSTREAM OF THE STOPPLE SEPARATED FROM THE IN-SERVICE LINE. THE UNDETECTED COUPLING IS A 10X16 INSULATED SLEEVE INSTALLED IN 1970. THE 20' SECTION OF THE UNDERGROUND PIPE CAME LOOSE AND SHIFTED IN THE DITCH CAUSING ONE CONTRACTOR BE INJURED. THE CONTRACTOR WAS TRANSPORTED TO A LOCAL HOSPITAL WHERE THEY RECEIVED TREATMENT BEYOND FIRST AID. ANOTHER CONTRACTOR RECEIVED FIRST AID AT THE SCENE. ALMOST IMMEDIATELY, ALL SOURCES FOR AM-53 WERE CLOSED AND GAS FLOW WAS STOPPED, INTERRUPTING SERVICE IN TOTAL TO 5,400 CERC CUSTOMERS. SERVICE TO CERC WAS RESTORED AT APPROXIMATELY 4:30 PM ON DECEMBER 13TH. PHMSA WAS INITIALLY NOTIFIED 12/1217 AT 17:07 (NRC#1199503) AND A 48 HOUR FOLLOW UP WAS PROVIDED ON 12/14/17 AT 09:26 (NRC#1199628). THE INVESTIGATION DISCOVERED VERTICAL AND LATERAL STABILITY WAS REMOVED FROM LINE AM-53 WHEN 14' OF 1936 VINTAGE DRESSER COUPLER LINE WAS REMOVED IN PREPARATION FOR A WELD CAP. PULLOUT OCCURRED OF AN UNDETECTED 10X16" STYLE 40 DRESSER COUPLER (14' UPSTREAM, NEAR 193+69) FROM THE IN-SERVICE LINE. BOTH DRESSER COUPLERS IN THIS AREA (VINTAGE 1936 10X8" AND VINTAGE 1970 10X16") WERE NOT ANCHORED. SUPPLEMENTAL REPORT 3/22/18 SUMMARY OF CHANGES D.7.A WAS CHANGED FROM A PROJECTION OF $275,000 TO ACTUAL 95,786 H. THE NARRATIVE WAS UPDATED TO INCLUDE : VERTICAL AND LATERAL STABILITY WAS REMOVED FROM LINE AM-53 WHEN 14' OF 1936 VINTAGE DRESSER COUPLER LINE WAS REMOVED IN PREPARATION FOR A WELD CAP. PULLOUT OCCURRED OF AN UNDETECTED 10X16" STYLE 40 DRESSER COUPLER (14' UPSTREAM, NEAR 193+69) FROM THE IN-SERVICE LINE. BOTH DRESSER COUPLERS IN THIS AREA (VINTAGE 1936 10X8" AND VINTAGE 1970 10X16") WERE NOT ANCHORED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180009 | 17610 | 2018-01-11 14:29 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2018-01-02 00:01 | 2018 |  |  | 31.9626 | -91.8217 | 1200909 | 2018-01-02 01:00 |  | NATURAL GAS |  | 16280 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-01-02 00:57 | 2018-01-04 18:20 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-01-02 00:01 | 2018-01-02 00:01 | ONSHORE | LA | 71243 | Not Within a Municipality | FRANKLIN | MILEPOST | MP 0 IN YARD | STATION 834 - WINNSBORO STATION | 800-1 LINE; 834 TO 837 SEGMENT | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2017 |  | CARBON STEEL |  | OTHER | [8 empty] | ICE FORMED IN VALVE CONTROL CAUSING VALVE TO OPEN AND RELEASE NATURAL GAS | CLASS 1 LOCATION | NO |  | 633 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 46398 | 41791.1063829787 | 13650 | 14210.6029011786 | 2525 | 2628.70126926564 | 0 | 0 |  |  | 62573 | 51056.4225387885 | 58630.410553423 | [8 empty] | 737 |  | 936 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | VALVE OPERATED DUE TO ICE IN THE CONTROLLER | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [52 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | 16 DEGREES F, SEVERE COLD WEATHER; ICE FORMED IN THE CONTROLLER OF VALVE | YES |  |  |  | YES | EXTREME COLD FRONT FOR THIS PART OF THE COUNTRY, 16 DEGREES F | [301 empty] | WM. MARTIN MULLER | SPECIALIST - PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 2053253863 | 205 325 3592 |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713 369 9443 | jaime_hernandez@kindermorgan.com | ALL TIMES ARE CENTRAL STANDARD TIME; PIR = 633 FEET; KM TGP PIR WITH BUFFER = 673 FEET; 48-HOUR NRC UPDATE MADE EARLY DURING NORMAL BUSINESS HOURS, NRC # 1201018, 01/03/2018, 14:28 CST; GAS RELEASE REPORTED TO LA STATE POLICE 01/02/2018; REPORT NUMBER 18-00012; 01/02/18, STATION 834 IS ON LINE, OPERATING PERSONNEL IS ON SITE; WEATHER CONDITION IS UNUSUAL SEVERE COLD WEATHER; 15 DEGREES FAHRENHEIT; 01/02/2018, 00:01 HOUR, VALVE UNINTENTIONALLY BEGAN TO OPEN, RELEASING NATURAL GAS TO ATMOSPHERE; OPERATING PERSONNEL IMMEDIATELY HEARD THE SOUND OF VENTING NATURAL GAS AND INVESTIGATED SOURCE OF BLOWING GAS; OPERATING PERSONNEL THEN INITIATED A STATION SHUT DOWN; A SIDE VALVE UNINTENTIONALLY DID NOT CLOSE ALLOWING NATURAL GAS TO CONTINUE TO FEED OPEN VALVE; A RESIDENT HEARD THE SAME AND CALLED 911 (FARM HOUSES IN THE AREA); SHERIFF DEPARTMENT CALLED TGP GAS CONTROL; 00:57 HOUR, ANOTHER BLOCK VALVE WAS REMOTELY CLOSED BY EMPLOYEES THUS TERMINATING THE RELEASE OF NATURAL GAS TO ATMOSPHERE; INVESTIGATION AND REPAIR COMMENCED; MOISTURE CREATED ICE IN THE CONTROL BOX OF THE VALVE; SAID ICE CAUSED INCORRECT OPERATION OF THE CONTROLS THUS OPENING THE VALVE UNINTENTIONALLY; THE CONTROLS WERE CLEANED AND LUBRICATED AND THE CONTROL BOX WAS REINSTALLED; CONTROLS OF THE SIDE VALVE WERE FREED FROM ICE IN THE WORM GEAR HOUSING AND THE ACTUATOR WAS LUBRICATED AND RETURNED TO SERVICE MODE; 01/04/2018, 18:20 HOURS, STATION 834 RETURNED TO ON LINE STATUS;
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180010 | 30949 | 2018-01-12 16:47 | SUPPLEMENTAL FINAL | 31565 | GULFSTREAM MANAGEMENT & OPERATING SERVICES,LLC | 1905 INTERMODAL CIRCLE, SUITE 310 | PALMETTO | FL | 34221 | 2017-12-16 10:45 | 2017 |  |  | 30.3211 | -88.4803 | 1200029 | 2017-12-19 08:50 |  | NATURAL GAS |  | 4080 | 50636 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-12-16 10:45 | 2017-12-23 09:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-12-16 10:45 | 2017-12-16 11:00 | ONSHORE | MS | 39567 | PASCAGOULA | JACKSON | MILEPOST | 60-1 VALVE | GULFSTREAM LINE 60 | STATION 55 TO 60-2 VALVE | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | DRAIN LINES | [38 empty] | UNKNOWN |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 769 |  | NO | NO | NO |  | 0 | 0 | 140000 | 148908.85513153 | 12000 | 10990.3846153846 | 40902 | 43504.7856613561 | 1000 | 1063.63467951093 | 6800 | 7232.71582067432 | ENVIRONMENTAL PERMITS |  | 200702 | 103525.412873714 | 211700.375908456 | [8 empty] | 960 |  | 2180 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | AUTOMATIC | 137280 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  |  | YES | [7 empty] | YES |  |  |  | NO | [11 empty] | YES | YES | [335 empty] | SHANE FRASIER | PIPELINE SAFETY ENGINEER | shane.frasier@williams.com | 801-584-6844 |  |  |  |  | LARRY LEGENDRE | PIPELINE SAFETY MANAGER | 7132152733 | larry.d.legendre@williams.com | 12/16/2017 WILLIAMS RECEIVED A CALL FROM CHEVRON'S REFINERY IN PASCAGOULA, MS THAT ONE OF OUR VALVES AT METER STATION 55 APPEARS TO HAVE A GAS LEAK. WILLIAMS LOCAL OPERATIONS DEPLOYED PERSONNEL TO INVESTIGATE AND MADE INTERNAL NOTIFICATIONS. PERSONNEL ON SIGHT CONFIRMED THE RUPTURE TO BE A VALVE BODY BLEED LINE THAT IS COMPROMISED (ABOUT A 3/4" DIAMETER LINE). OPERATIONS PROCEEDED TO BLOW DOWN THE ROUGHLY 26 MILE SECTION OF 36" PIPE IN ORDER TO REPAIR THE PROBLEM. BLOW DOWN OCCURRED NEAR THE COAST IN A REMOTE AREA. 12/19/2017 WILLIAMS ENVIRONMENTAL PERSONNEL COMPLETED THEIR ESTIMATIONS FOR THE GAS LOST UNINTENTIONALLY, THAT FIGURE EXCEEDED THE THRESHOLD FOR DOT REPORTABLE INCIDENT AND NOTIFICATION TO THE NRC WAS MADE BY WILLIAMS SOC. 12/23/2017 NEW BODY BLEED LINES WERE TESTED AND INSTALLED. FACILITY WAS RETURNED TO SERVICE. 1/12/2018 PHMSA REPORT SUBMITTED TO PORTAL. WE ARE STILL WAITING ON OVERALL COSTS ASSOCIATED WITH THIS INCIDENT AND WILL FILE SUPPLEMENTAL REPORT ASAP. COSTS UPDATED.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20180011 | 30460 | 2018-01-12 17:52 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2017-12-14 16:00 | 2017 |  |  | 28.4503 | -90.8968 | 1199697 | 2017-12-14 17:14 |  | NATURAL GAS |  | 53.5 | 735 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-12-14 16:28 | 2017-12-20 09:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-12-18 16:00 | 2017-12-18 13:30 | OFFSHORE | [28 empty] | 125 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SHIP SHOAL | 232 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 |  | 0.438 | 42000 | AP5L | SEAMLESS |  | KAISER STEEL | ASPHALT | [28 empty] | 1983 | 1983 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 200 |  | NO | NO | NO |  | 0 | 0 | 2205 | 2345.3144683216 | 160 | 146.538461538462 | 50000 | 53181.7339755465 | 67847 | 72164.4221007781 | 16421 | 17465.945072249 | PLIDCO REPAIR CLAMP |  | 136633 | 66783.0070895204 | 145303.954078434 | [8 empty] | 738 |  | 1440 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | AUTOMATIC | 33053 | NO | [5 empty] | YES | UPSTREAM END OF PIPELINE IS SUB-SEA WITH NO PIGGING FACILITIES. | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | YES | YES | YES | NO | NO | OTHER | THIRD PARTY HELICOPTER SPOTTED BUBBLES AND REPORTED IT |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | INSPECTED BY DIVERS, PINHOLE LEAK. |  |  | YES |  |  |  | YES |  | YES | INSPECTED BY DIVERS. | YES | [5 empty] | YES | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | EDGAR RODRIGUEZ | REGULATORY COMPLIANCE SPECIALIST SR. | edgar.x.rodriguez@williams.com | 7132152846 |  |  |  |  | LARRY LEGENDRE | MANAGER PIPELINE SAFETY | 713-215-2733 | larry.d.legendre@williams.com | ON 12/14/17/2017 A THIRD PARTY HELICOPTER SPOTTED THE BUBBLES AND REPORTED THEM TO WGP PIPELINE CONTROL. PIPELINE CONTROL NOTIFIED WGP OPERATIONS. OPERATIONS FLEW OUT TO VERIFY COORDINATES. THE BUBBLES WERE IN THE VICINITY OF A WGP 16" PIPELINE. THE WGP SECURITY OPERATIONS CENTER WAS NOTIFIED OF THE POTENTIAL LEAK. DUE TO INCLEMENT WEATHER PERSONNEL HAD TO TRAVEL BY BOAT TO GET TO THE ISOLATION POINTS. WE MADE THE DECISION TO SHUT IN PRODUCTION TO THE LINE ON 12/14/17. THE 16" SECTION OF PIPELINE WAS ISOLATED ON 12/16/17. THEY THEN STARTED REDUCING THE PRESSURE IN THE SECTION OF 16". THE DIVE BOAT WAS DISPATCHED AND DIVERS CONFIRMED THE LEAK WAS THE WGP 16" PIPELINE. THE SOC WAS NOTIFIED OF A CONFIRMED LEAK AND THEY NOTIFIED THE NRC. ON 12/15/2017 WGP OPERATIONS ACQUIRED A 16" PLIDCO CLAMPS THE FIRST WAS INSTALLED ON 12/20/17. 6/6/2018 AS OF THIS DATE, THERE HAS BEEN NO CHANGE TO THE OPERATIONAL STATUS OF THIS PIPELINE. IT REMAINS ISOLATED WITH NO PRESSURE. WE ARE WORKING WITH OUR PRODUCER PARTNERS AS WELL AS THE OTHER REGULATORY AGENCIES FOR APPROVAL TO ABANDON THE LINE. THE FINAL ABANDONMENT WILL TAKE PLACE IN 2020. AT THE REQUEST OF BRIAN PIERZINA, WE HAVE UPDATED THE "FACILITY RESTART" DATE TO 12/20/17 AS THAT WAS THE POINT IN WHICH ACTIVITIES ASSOCIATED WITH THE RELEASE EVENT WERE ESSENTIALLY CONCLUDED. THIS REPORT WILL BE NOW MARKED AS "FINAL".
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20180012 | 30461 | 2018-01-12 18:18 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2017-12-14 16:00 | 2017 |  |  | 28.4497 | -90.8964 | 1199697 | 2017-12-14 17:14 |  | NATURAL GAS |  | 53.5 | 735 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-12-14 16:28 | 2017-12-21 09:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-12-18 16:00 | 2017-12-18 13:30 | OFFSHORE | [28 empty] | 125 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SHIP SHOAL | 232 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 |  | 0.438 | 42000 | AP5L | SEAMLESS |  | KAISER STEEL | ASPHALT | [28 empty] | 1983 | 1983 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 200 |  | NO | NO | NO |  | 0 | 0 | 2205 | 2345.3144683216 | 160 | 146.538461538462 | 50000 | 53181.7339755465 | 67847 | 72164.4221007781 | 16421 | 17465.945072249 | PLIDCO REPAIR CLAMP |  | 136633 | 66783.0070895204 | 145303.954078434 | [8 empty] | 738 |  | 1440 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | AUTOMATIC | 33053 | NO | [5 empty] | YES | UPSTREAM END OF PIPELINE IS SUBSEA WITH NO PIGGING FACILITIES | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | YES | YES | YES | NO | NO | OTHER | THIRD PARTY HELICOPTER SPOTTED BUBBLES AND REPORTED IT |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | INSPECTED BY DIVERS - PINHOLE LEAK |  |  | YES |  |  |  | YES |  | YES | INSPECTED BY DIVERS. | YES | [5 empty] | YES | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | EDGAR RODRIGUEZ | REGULATORY COMPLIANCE SR | edgar.x.rodriguez@williams.com | 713-215-2846 |  |  |  |  | LARRY LEGENDRE | MANAGER PIPELINE SAFETY | 713-215-2733 | larry.d.legendre@williams.com | ON 12/14/17/2017 A THIRD PARTY HELICOPTER SPOTTED THE BUBBLES AND REPORTED THEM TO WGP PIPELINE CONTROL. PIPELINE CONTROL NOTIFIED WGP OPERATIONS. OPERATIONS FLEW OUT TO VERIFY COORDINATES. THE BUBBLES WERE IN THE VICINITY OF A WGP 16" PIPELINE. THE WGP SECURITY OPERATIONS CENTER WAS NOTIFIED OF THE POTENTIAL LEAK. DUE TO INCLEMENT WEATHER PERSONNEL HAD TO TRAVEL BY BOAT TO GET TO THE ISOLATION POINTS. WE MADE THE DECISION TO SHUT IN PRODUCTION TO THE LINE ON 12/14/17. THE 16" SECTION OF PIPELINE WAS ISOLATED ON 12/16/17. THEY THEN STARTED REDUCING THE PRESSURE IN THE SECTION OF 16". THE DIVE BOAT WAS DISPATCHED AND DIVERS CONFIRMED THE LEAK WAS THE WGP 16" PIPELINE. THE SOC WAS NOTIFIED OF A CONFIRMED LEAK AND THEY NOTIFIED THE NRC. ON 12/18/2017 WGP OPERATIONS ACQUIRED THE SECOND 16" PLIDCO CLAMP THAT WAS INSTALLED AND TORQUED.AS OF 12/21/17. 6/6/2018 AS OF THIS DATE, THERE HAS BEEN NO CHANGE TO THE OPERATIONAL STATUS OF THIS PIPELINE. IT REMAINS ISOLATED WITH NO PRESSURE. WE ARE WORKING WITH OUR PRODUCER PARTNERS AS WELL AS THE OTHER REGULATORY AGENCIES FOR APPROVAL TO ABANDON THE LINE. THE FINAL ABANDONMENT WILL TAKE PLACE IN 2020. AT THE REQUEST OF BRIAN PIERZINA, WE HAVE UPDATED THE "FACILITY RESTART" DATE TO 12/21/17 AS THAT WAS THE POINT IN WHICH ACTIVITIES ASSOCIATED WITH THE RELEASE EVENT WERE ESSENTIALLY CONCLUDED. THIS REPORT WILL BE NOW MARKED AS "FINAL".
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180013 | 17593 | 2018-01-16 09:43 | SUPPLEMENTAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2017-12-19 17:20 | 2017 |  |  | 33.4396 | -87.3044 | 1200105 | 2017-12-19 18:16 |  | NATURAL GAS |  | 15150 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | HOWEVER UNIT UNAVILABLE UNTIL REPAIR COMPLETED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-12-19 17:20 | 2017-12-19 17:50 | ONSHORE | AL | 35006 | Not Within a Municipality | TUSCALOOSA | MILEPOST | MP 286.138 | NORTH MAIN LINE | MCCONNELLS TO TARRANT | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1991 |  | CARBON STEEL |  | LEAK |  |  | OTHER | DIAPHRAGM OF ACUATOR LEAK | [5 empty] | CLASS 1 LOCATION | NO |  | 454 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 43178 | 39545.2355769231 | 1000 | 1063.63467951093 | 250 | 265.908669877733 | 0 | 0 |  |  | 44428 | 41608.6368259612 | 40874.7789263117 | [8 empty] | 206 |  | 245 | OTHER | 192.505(B) |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAKING DIAPHRAGM OF VALVE ACTUATOR CAUSED EVENT | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | YES | [34 empty] | YES | ACTUATOR DIAPHRAGM SPLIT (AGE, NORMAL WEAR) | [161 empty] | WM MARTIN MULLER | SPECIALIST - PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205 325 3863 | 2053253592 |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | ALL TIMES ARE CST; PIR OF PIPELINE IS 454 FEET; PIR WITH KM BUFFER IS 494 FEET; NRC 48-HOUR UPDATE REPORT NUMBER 1200280; DIAPHRAGM OF ACTUATOR ON CONTROL VALVE OF FUEL GAS SYSTEM SPLIT RESULTING IN LOSS OF VALVE CONTROL; SAID VALVE OPENED RELEASING NATURAL GAS THROUGH SYSTEM PIPING TO ATMOSPHERE; EMPLOYEE ARRIVED ON SITE AND ISOLATED SYSTEM TERMINATING NATURAL GAS RELEASE; INVESTIGATION AND REPAIR COMMENCED; UNIT WAS AVAILABLE FOR NORMAL SERVICE 12/19/2017 AT 20:30 HOURS;
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180014 | 30164 | 2018-01-16 14:28 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 4720 PIEDMONT ROW DR. | CHARLOTTE | NC | 28210 | 2017-12-19 09:13 | 2017 |  |  | 35.1142 | -78.9216 | 1200087 | 2017-12-19 16:32 |  | NATURAL GAS |  | 9970.92 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-12-21 07:00 | 2017-12-21 15:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2017-12-19 09:13 | 2017-12-19 09:30 | ONSHORE | NC | 28311 | FAYETTEVILLE | CUMBERLAND | SURVEY STATION NO. | 65474 | LINE 5 | LINE 5 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 0.75 |  | 0.13 |  | STEEL PIPE | SEAMLESS |  | UNKNOWN | COAL TAR | [28 empty] | 2001 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | VEHICLE HIT FACILITY. | [5 empty] | CLASS 3 LOCATION | NO |  | 100 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 29912 | 27395.3653846154 | 178634 | 190001.317339755 | 22765 | 24213.6434790663 | 0 | 0 |  |  | 231311 | 126732.338700943 | 241610.326203437 | [8 empty] | 580 |  | 718 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ABOVE GROUND FACILITY WAS HIT BY A CAR. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [260 empty] | CHRISTOPHER RANSOME | PIPELINE SAFETY AND COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | MANAGER- PIPELINE SAFETY | 704-731-4618 | farris.berry@duke-energy.com | A DRIVER TRAVELING EAST OF SHAW MILL ROAD EXPERIENCED A MEDICAL CONDITION. THE VEHICLE RAN OFF THE SIDE OF THE ROAD STRIKING A REGULATOR STATION CAUSING DAMAGE TO BOTH THE VEHICLE AND REGULATOR STATION. THE INCIDENT RESULTED IN A FIRE AND A RELEASE OF GAS. THE DRIVER OF THE VEHICLE WAS HOSPITALIZED BECAUSE OF A PRE-EXISTING MEDICAL CONDITION AND NOT DUE TO A RELEASE OF GAS.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180015 | 32186 | 2018-01-16 16:02 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2017-12-17 14:00 | 2017 |  |  | 40.0681 | -75.128 | 1200163 | 2017-12-20 13:56 |  | NATURAL GAS |  | 1522 | 490 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-12-20 16:30 | 2017-12-21 17:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-12-19 19:00 | 2017-12-19 20:30 | ONSHORE | PA | 19027 | ELKINS PARK | MONTGOMERY | SURVEY STATION NO. | 18.59 | LINE 1-B | EAGL-LAMB | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 40 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | FLANGE ASSEMBLY | [38 empty] | 1949 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | YES | METHOD2 | 237 |  | NO | NO | NO |  | 0 | 0 | 1470 | 1563.54297888107 | 4566 | 4181.84134615385 | 90000 | 95727.1211559837 | 0 | 0 | 0 | 0 |  |  | 96036 | 48994.4868380739 | 101472.505481019 | [8 empty] | 593 |  | 718 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 37488 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | LOCAL DISTRIBUTION OPERATOR |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS TOO SMALL TO BE IDENTIFIED BY CONTROL ROOM PERSONNEL. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | GASKET | [7 empty] | YES | [172 empty] | DWAYNE TESCHENDORF | ENGINEER SPECIALIST | dwayne.teschendorf@enbridge.com | 713-627-5573 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | PECO BECAME AWARE OF A NATURAL GAS PIPELINE LEAK ON DECEMBER 17, 2017 IN MONTGOMERY COUNTY, PENNSYLVANIA WHICH PECO HAD REASON TO BELIEVE WAS ASSOCIATED WITH THEIR FACILITIES DUE TO THE CONCENTRATION OF NATURAL GAS IN THAT VICINITY. AFTER PECO EXCAVATED POINTS OVER THEIR PIPELINE FOR TWO DAYS IT BECAME LESS EVIDENT THAT THE LEAK WAS ASSOCIATED WITH A PECO FACILITY. LATE IN THE DAY ON DECEMBER 19, 2017 PECO ADVISED ENBRIDGE THAT NATURAL GAS LEAK NOW APPEARED TO BE IN THE VICINITY OF THE TEXAS EASTERN PIPELINE. THE ENBRIDGE TEXAS EASTERN TRANSMISSION, LP 12-INCH LINE 1-B NATURAL GAS TRANSMISSION PIPELINE IN MONTGOMERY COUNTY, PENNSYLVANIA WAS DISCOVERED TO HAVE A LEAK ON DECEMBER 20, 2017. THE PIPELINE WAS SHUTDOWN THE SAME DAY. UPON EXCAVATION THE ORIGIN OF THE LEAK WAS DETERMINED TO BE AT A FLANGE. THE FLANGE BOLTS WERE APPARENTLY NOT EQUALLY TIGHTENED. THE FLANGE AND ASSOCIATED PIPING WAS REPLACED WITH PIPE AND THE LINE 1-B WAS RETURNED TO SERVICE ON DECEMBER 21, 2017.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180016 | 17581 | 2018-01-18 17:11 | SUPPLEMENTAL FINAL | 22655 | WBI ENERGY TRANSMISSION, INC. | 1250 WEST CENTURY AVENUE | BISMARCK | ND | 58503 | 2016-07-31 14:51 | 2016 |  |  | 48.2278 | -103.5756 | 1154962 | 2016-07-31 17:15 |  | NATURAL GAS |  | 3880 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELEASE WAS THROUGH A RELIEF VALVE CAUSED BY POWER OUTAGE AT STATION. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2016-07-31 10:19 | 2016-07-31 10:30 | ONSHORE | ND | 58801 | WILLISTON | WILLIAMS | SURVEY STATION NO. | 419+56 | WILLISTON COMPRESSOR STATION | WILLISTON COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2008 |  | CARBON STEEL |  | OTHER | [8 empty] | A RELIEF VALVE OPENED AS DESIGNED WHEN COMPRESSOR UNITS WENT DOWN ON POWER OUTAGE. | CLASS 1 LOCATION | NO |  | 243 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 9972 | 10240.7870619946 | 0 | 0 | 1620 | 1754.28706148623 | 0 | 0 |  |  | 11592 | 11422.3530000885 | 11995.0741234808 | [8 empty] | 700 |  | 700 | 192.619(A)(2) |  |  |  | PRESSURE EXCEEDED MAOP, BUT DID NOT EXCEED THE APPLICABLE ALLOWANCE IN 192.201 | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT'S ROOT CAUSE WAS A POWER OUTAGE; THEREFORE ACTIONS OF THE CONTROLLERS COULD NOT HAVE PREVENTED THIS EVENT FROM HAPPENING. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | OTHER | POWER OUTAGE CAUSED COMPRESSOR UNITS TO GO DOWN. BACKUP GENERATOR FAILED START. | [9 empty] | YES | [173 empty] | KENT KAHL | DOT COMPLIANCE SUPERVISOR | kent.kahl@wbienergy.com | 406-359-7222 | 406-359-7244 |  |  |  | KENT KAHL | DOT COMPLIANCE SUPERVISOR | 406-359-7222 | kent.kahl@wbienergy.com | ON JULY 31, 2016 WBI ENERGY TRANSMISSION EXPERIENCED A POWER OUTAGE AT THE CHARBONNEAU COMPRESSOR STATION LOCATED IN A RURAL LOCATION APPROXIMATELY 5.5 MILES NORTHEAST OF CARTWRIGHT, ND. THE BACKUP GENERATOR FAILED TO START AND CAUSED ALL FOUR COMPRESSOR UNITS TO GO DOWN. THE COMPRESSORS BEING DOWN CAUSED PRESSURE TO BUILD UP ON THE PIPELINE BETWEEN THE CHARBONNEAU COMPRESSOR STATION AND THE WILLISTON COMPRESSOR STATION. THE LINE PRESSURE ULTIMATELY REACHED THE 700 PSI MAOP OF THE PIPELINE AND CAUSED THE RELIEF VALVE AT THE WILLISTON COMPRESSOR STATION TO OPEN AS DESIGNED AND VENT NATURAL GAS TO ATMOSPHERE. THE WILLISTON COMPRESSOR STATION IS LOCATED IN A RURAL LOCATION APPROXIMATELY 4 MILES NORTHEAST OF WILLISTON, ND. THE AMOUNT OF NATURAL GAS VENTED TO ATMOSPHERE WAS 3,880 MSCF. SINCE THE RELEASE OCCURRED, WBI ENERGY TRANSMISSION HAS HAD SEVERAL DISCUSSIONS WITH HANS SHIEH, PHMSA CENTRAL REGION, ABOUT THE REPORTING OF THIS RELEASE OF NATURAL GAS THROUGH A RELIEF VALVE AS AN INCIDENT. A LETTER WAS SENT TO MR. SHIEH ON AUGUST 30, 2016 STATING THE REASONING WHY WBI ENERGY TRANSMISSION BELIEVED THIS EVENT DID NOT MEET THE INCIDENT DEFINITION AS DEFINED IN 49CFR191.3. WBI ENERGY TRANSMISSION DOES NOT AGREE WITH PHMSA THAT THE RELEASE OF NATURAL GAS THROUGH AN APPURTENANCE DESIGNED TO RELEASE GAS SHOULD BE REPORTED AS AN INCIDENT, BUT HAVE DECIDED AT THIS TIME TO SUBMIT THE INCIDENT REPORT AND DECIDE AT A LATER DATE WHETHER OR NOT WBI ENERGY TRANSMISSION WILL FOLLOW UP WITH A FORMAL REQUEST FOR AN INTERPRETATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180017 | 30235 | 2018-01-19 09:27 | SUPPLEMENTAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2017-12-24 14:30 | 2017 |  |  | 32.664 | -92.4422 | 1200488 | 2017-12-24 15:24 |  | NATURAL GAS |  | 129 | 6376 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-12-24 16:30 | 2018-01-05 09:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-12-24 14:30 | 2017-12-24 14:50 | ONSHORE | LA | 71234 | DOWNSVILLE | LINCOLN | MILEPOST | 25+0125 | GUTHRIE-LISBON 20" | GUL 20" | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 39 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 20 |  | 0.25 | 45000 | API 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | YOUNGSTOWN | COAL TAR | [9 empty] | PIPE GIRTH WELD | [18 empty] | 1947 | 1947 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 393 |  | NO | NO | NO |  | 0 | 0 | 19946 | 21215.257317525 | 404 | 370.009615384615 | 136689 | 145387.16070767 | 8846 | 9408.91237495369 | 0 | 0 |  |  | 165885 | 81177.450804429 | 176381.340015533 | [8 empty] | 740 |  | 810 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 20370 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1947 | YES | YES | YES |  |  |  | 2017 |  |  |  | YES | [190 empty] | YES | YES | [6 empty] | 2017 | [55 empty] | YES | 1982 | 1115 | NO | [13 empty] | NO | [63 empty] | SHANNON MATTINGLY | PA OQ AND EVENT SUPPORT PROGRAM LEADER | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | DARRAL WARD | MANAGER PIPELINE SAFETY | 2706886356 | darral.ward@bwpmlp.com | A LANDOWNER CONTACTED TEXAS GAS CONTROL ROOM TO REPORT A SUSPECTED LEAK. OPERATIONS PERSONNEL VERIFIED THE LEAK AND ISOLATED THE SECTION OF PIPE CONTAINING THE LEAK UNTIL COMPLETE INVESTIGATION COULD BE PERFORMED. INVESTIGATION CONFIRMED LEAK AND THE PIPE JOINT CONTAINING THE LEAK WAS REPLACED. THE ROOT CAUSE OF THE EVENT IS CORROSION INTERACTING WITH A WELD DEFECT IN THE CIRCUMFERENTIAL WELD. THIS IS WHY THE ILI TOOL DID NOT DETECT THIS DEFECT IN 2017. WITHOUT THE CORROSION, THE CIRCUMFERENTIAL WELD DEFECT WOULD HAVE REMAINED STABLE, THEREFORE, THE ROOT CAUSE FOR THIS DEFECT IS CORROSION. 3-5-18 UPDATE PER PHMSA REQUEST. *LANDOWNER NOTIFICATION OCCURRED ON 12-24-2017 AT 14:30 *CONFIRMED DISCOVERY OCCURRED ON 12-24-2017 AT 14:50 *NRC CALL WAS MADE ON 12-24-2017 AT 15:24 *WILL UPDATE COSTS WHEN THEY BECOME AVAILABLE. 4-25-18 UPDATE WITH FINAL COSTS AND SUBMIT FINAL REPORT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180018 | 17579 | 2018-01-19 10:05 | ORIGINAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2018-01-04 09:45 | 2018 |  |  | 30.0869 | -92.0297 | 1201063 | 2018-01-04 10:55 |  | NATURAL GAS |  | 8100 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE PILOT ON THE RELIEF VALVE OPENED DUE TO SENSING LINE FREEZING | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-01-04 09:45 | 2018-01-04 09:45 | ONSHORE | LA | 70555 | YOUNGSVILLE | LAFAYETTE | MILEPOST | 40.1 | YOUNGSVILLE CS | EUNICE-THIBODAUX 20" LINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ABOVEGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1963 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE ACTIVATED DUE TO FROZEN PILOT | CLASS 1 LOCATION | NO |  | 224 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 22616 | 20370.4397163121 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 22616 | 21118.9598108747 | 20370.4397163121 | [8 empty] | 1010 |  | 1052 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | YES |  |  |  | YES | SUB-FREEZING TEMPERATURES FOR EXTENDED PERIOD OF TIME | [301 empty] | SHANNON MATTINGLY | PA OQ AND EVENT SUPPORT PROGRAM LEADER | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | JEFFREY B. MCMAINE | MANAGER CODES AND STANDARDS | 2706886361 | jeff.mcmaine@bwpmlp.com | SENSING LINE FOR PILOT OPERATED RELIEF VALVE; IT WAS FROZEN DUE TO EXTREMELY LONG PERIOD OF SUB-FREEZING TEMPERATURES. LOCAL TECHNICIANS WERE ONSITE WHEN RELIEF VALVE OPENED AND IMMEDIATELY RESPONDED TO CLOSE VALVE. THERE WAS NO COST ASSOCIATED WITH EMERGENCY RESPONSE BECAUSE EMPLOYEES WERE ALREADY ONSITE AT TIME OF INCIDENT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180019 | 17590 | 2018-01-26 14:36 | SUPPLEMENTAL FINAL | 31712 | GUARDIAN PIPELINE, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2017-12-31 20:47 | 2017 |  |  | 41.4503 | -88.1835 | 1200873 | 2017-12-31 23:50 |  | NATURAL GAS |  | 26600 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | ONLY IMPACTED SINGLE COMPRESSOR UNIT | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-12-31 20:46 | 2017-12-31 21:47 | ONSHORE | IL | 60410 | CHANNAHON | WILL | MILEPOST | 0 | JOLIET COMPRESSOR STATION | 237 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2002 |  | CARBON STEEL |  | OTHER | [8 empty] | VALVE CONTROL | CLASS 1 LOCATION | YES | METHOD2 | 786 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 100000 | 91586.5384615385 | 0 | 0 | 300 | 319.090403853279 | 0 | 0 |  |  | 100300 | 95098.3939920768 | 91905.6288653917 | [8 empty] | 625 |  | 999 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER RECOGNIZED THE ISSUE AND RESPONDED IN A TIMELY AND APPROPRIATE MANNER. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | YES | [34 empty] | YES | LOOSE FITTING LED TO ICE BLOCKAGE IN CONTROL LINE | [161 empty] | DUANE FOURNIER | REGULATORY COMPLIANCE COORDINATOR | duane.fournier@oneok.com | 515-491-3551 |  |  |  |  | DUANE FOURNIER | REGULATORY COMPLIANCE COORDINATOR | 515-491-3551 | duane.fournier@oneok.com | AT APPROXIMATELY 20:46 ON DECEMBER 31, 2017, THE GUARDIAN PIPELINE GAS CONTROLLER ON DUTY IDENTIFIED A POSSIBLE ISSUE.. THE ONEOK FIELD REPRESENTATIVE WAS CONTACTED AND ARRIVED AT THE JOLIET STATION AT APPROXIMATELY 21:47 AT WHICH TIME GAS WAS FOUND BLOWING FROM THE BLOW DOWN ON THE UNIT #1 COMPRESSOR. GAS CONTROL WAS CONTACTED AND THE COMPRESSOR UNIT WAS SHUT DOWN. THE FIELD REPRESENTATIVE LOCATED A FROST BALL ON ONE OF THE SUPPLY FITTINGS, THAWED THE SUPPLY LINE, RETIGHTENED THE FITTING, AND THE VALVE CLOSED. UNIT 1 WAS THEN RETURNED TO NORMAL SERVICE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180020 | 17586 | 2018-01-29 11:43 | ORIGINAL FINAL | 13063 | NATIONAL FUEL GAS SUPPLY CORP | 6363 MAIN STREET | WILLIAMSVILLE | NY | 14221-5887 | 2018-01-01 03:08 | 2018 |  |  | 41.8995 | -77.9158 | 1200878 | 2018-01-01 04:02 |  |  |  | 0 | 714 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-01-01 03:08 | 2018-01-01 20:10 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-01-01 03:08 | 2018-01-01 03:08 | ONSHORE | PA | 16923 | Not Within a Municipality | POTTER | MILEPOST | ALP1 | ELLISBURG COMPRESSOR STATION | N/A | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | ELECTRICAL CONTROL RELAY | 2017 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | ELECTRICAL CONTROL RELAY | OTHER | [8 empty] | EMERGENCY SHUTDOWN | CLASS 1 LOCATION | NO |  | 400 |  | NO | NO | NO |  | 0 | 0 | 2200 | 2290.35358114234 | 0 | 0 | 111 | 115.558748866727 | 16802 | 17492.0549410698 | 0 | 0 |  |  | 19113 | 9133.69202175885 | 19897.9672710789 | [8 empty] | 1038 |  | 1084 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ELECTRICAL EQUIPMENT FAILURE UNRELATED TO CONTROL ROOM OPERATIONS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | FAILURE OF AN ELECTRICAL COMPONENT (RELAY) DUE TO MANUFACTURING DEFECT. | [10 empty] | YES | [174 empty] | JOHN SEAGER | INTEGRITY ENGINEER | seagerj@natfuel.com | 7168577899 | 7168577469 |  |  |  | BRIAN KEMPSKI | OPERATIONS SUPERINTENDENT | 7168272131 | kempskib@natfuel.com | ON JANUARY 1, 2018 AT 3:08 AM EST ELLISBURG COMPRESSOR STATION EXPERIENCED AN EMERGENCY SHUT DOWN DUE TO A FAULTY ELECTRICAL RELAY IN THE STATION CONTROL PANEL. NO PIPELINES OR STRUCTURES WERE DAMAGED. ELLISBURG COMPRESSOR STATION IS LOCATED IN POTTER COUNTY AT 188 ROSE LAKE ROAD, GENESEE, PA 16923. THE EMERGENCY SHUT DOWN OF THE STATION AFFECTED NATURAL GAS TRANSMISSION THROUGH-PUT. PRIMARY FIRM TRANSPORTATION SERVICE AND LEASE TRANSPORTATION SERVICE WAS REDUCED BY 79% TO 21% THROUGH THE LINE X SEGMENT DOWNSTREAM OF THE ELLISBURG COMPRESSOR STATION. AS A RESULT OF THE REDUCTION IN NATURAL GAS THROUGH-PUT, NATIONAL FUEL IS REPORTING THIS EVENT AS AN INCIDENT. STATION PERSONNEL WERE IMMEDIATELY MOBILIZED AND THE FAULTY RELAY WAS IDENTIFIED AND REPLACED. THE COMPRESSOR STATION AND TRANSMISSION CAPACITY WERE RESTORED TO FULL SERVICE AT 8:10 PM EST ON JANUARY 1, 2018.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180021 | 17611 | 2018-01-31 16:49 | SUPPLEMENTAL FINAL | 993 | CROSSROADS PIPELINE COMPANY | 700 LOUISIANA STREET | HOUSTON | TX | 77002 | 2018-01-06 14:25 | 2018 |  |  | 41.5072 | -87.4498 | 1201223 | 2018-01-06 17:51 |  | NATURAL GAS |  | 14603 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | AFFECTED PIPELINE SEGMENT WAS ISOLATED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-01-06 14:26 | 2018-01-06 15:08 | ONSHORE | IN | 46375 | SCHERERVILLE | LAKE | MILEPOST | BDV-0011 | SCHERERVILLE COMPRESSOR STATION | 6-IN BLOW-OFF VALVE/BDV-0011 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1958 |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENDED RELEASE OF NATURAL GAS THROUGH THE 6-INCH BLOWOFF VALVE | CLASS 3 LOCATION | NO |  | 177 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 36800 | 33146.0992907801 | 6600 | 6871.06074342702 | 0 | 0 | 0 | 0 | NO ADDITIONAL COSTS WERE NOTED OTHER THAN LOSS OF MATERIAL INTO ATMOSPHERE |  | 43400 | 37518.0643806168 | 40017.1600342072 | [8 empty] | 250 |  | 720 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO MANIPULATION OF CONTROLS OR ISSUANCE OF ANY COMMANDS THAT MAY HAVE CONTRIBUTED TO THIS UNINTENDED RELEASE | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | 6-INCH BLOW-OFF VALVE WAS INADVERTENTLY ACTIVATED DUE TO POTENTIAL PRESENCE OF A FOREIGN OBJECT. | [22 empty] | YES | SUSPECTED FOREIGN OBJECT (FROST) AS NOTED FROM COMPLETED INCIDENT INVESTIGATION | [161 empty] | GEORGE HAMATY | ENGINEER | george_hamaty@transcanada.com | (304) 553-8306 |  |  |  |  | LEE ROMACK | USRC MANAGER | (832) 584-3178 | lee_romack@transcanada.com | ON JANUARY 6TH, 2018, AN UNINTENDED RELEASE OF NATURAL GAS (MATERIAL) WAS REPORTED TO THE NATIONAL RESPONSE CENTER @ 18:51 EASTERN STANDARD TIME (EST). THIS EVENT TOOK PLACE AT SCHERERVILLE COMPRESSOR STATION (CS) IN LAKE COUNTY, NEAR THE TOWN OF SCHERERVILLE, INDIANA. THIS FACILITY IS OPERATED AND MAINTAINED BY CROSSROADS PIPELINE COMPANY, LLC. THIS EVENT DID NOT TRIGGER THE ESD SYSTEM OF THE CS AND THE UNINTENDED RELEASE WAS NOTED FROM A 6-INCH SUCTION BLOW-OFF VALVE (BDV-0011) THAT VENTED INTO ATMOSPHERE FOR ABOUT 145 MINUTES. THE COMPANY OPERATIONS PERSONNEL WHO RESPONDED TO THE SITE WERE THERE IN AROUND 20MINUTES. BASED ON THE PRELIMINARY DATA WHERE AT AN OPERATING PRESSURE OF 250 PSIG AND A 6-IN DIAMETER OUTLET RELEASING FOR MORE THAN 60 MINUTES, CROSSES THE 3,000 MCF. MATERIAL LOST CALCULATIONS WAS UP TO 6,400 MCF. THERE WAS NO FIRE, NO FATALITIES, NO INJURIES OR EVACUATIONS. THE EMERGENCY RESPONDERS WERE ON SITE DUE TO THE NOISE CREATED BY THE NOZZLE EFFECT FROM THE BLOW-OFF VALVE OUTLET SUB. THE AREA WAS MADE SAFE AND THE SECTION OF THIS PIPE WAS MADE ISOLATING IT. FURTHER INVESTIGATIONS WILL TAKE PLACE TO IDENTIFY THE REASON BEHIND THIS UNINTENDED RELEASE OF MATERIAL INTO ATMOSPHERE. THE INITIAL NRC REPORT NO. IS 1201223 RECEIVED AT 18:51 EST AND THE 48-HR UPDATE NRC REPORT WAS COMPLETED ON JANUARY 8TH, 2018 @ 16:23 WITH REPORT NO. 1201330 WITH A REVISED GAS LOST CALCULATION THAT INCREASED UP TO 14,600 MCF. FACILITY PERSONNEL WITH SUPPORTING RELIABILITY ENGINEER, CONDUCTED FIELD TESTING OF THE ESD SYSTEM, SUCTION BLOW-OFF VALVE POST-INCIDENT INVESTIGATION. THE ATTEMPTS TO REPLICATE THE EVENT IN VARIOUS CASE-SCENARIOS FAILED TO RECREATE THE EVENT OR CHAIN OF EVENTS THAT LED TO THIS UNINTENDED RELEASE OF MATERIAL. ALL TESTS CONCLUDED IN SUCCESSFUL RESPONSES AND NO FAILURE INDICATIONS WERE RECORDED TO ANY OF THE ESD SYSTEM COMPONENTS. PROBABLE CAUSE INDICATED THAT A POTENTIAL RESIDUE OF MOISTURE MAY HAVE FROZEN-OFF LEADING TO THE INITIATION OF THE UNINTENDED RELEASE THROUGH THE BLOW-OFF VALVE. THE OUTSIDE TEMPERATURE AT THE TIME OF THE INCIDENT WAS 6 DEGREES F. WITH MODERATE WINDS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180022 | 31923 | 2018-02-08 10:26 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2018-01-09 03:55 | 2018 |  |  | 34.4463 | -119.6222 | 1201382 | 2018-01-09 06:08 |  | NATURAL GAS |  | 12820 | 9910 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-01-09 03:55 |  | YES |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2018-01-09 03:55 | 2018-01-09 05:00 | ONSHORE | CA | 93108 | MONTECITO | SANTA BARBARA | MILEPOST | 12.6 | 1005 | NA | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 102 |  | YES | [6 empty] | YES | UNCASED | SAN YSIDRO CREEK | UNKNOWN | BELOW WATER, PIPE IN BORED/DRILLED CROSSING | [11 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 22 |  | 0.438 | 48000 | API 5XL | DSAW |  | NA | COAL TAR | [28 empty] | 1965 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | FULL SEPARATION DUE TO MUDSLIDE-RELATED IMPACT | CLASS 3 LOCATION | YES | METHOD1 | 469 |  | NO | YES | NO |  | 2511110 | 2614240.80961015 | 59460 | 61902.0108794198 | 76920 | 69282.5531914894 | 1380745 | 1437451.93427017 | 0 | 0 | 2870099 | 2987973.41949229 | POSSIBLE OVERHEADS AND FLEET ALLOCATIONS |  | 6898334 | 3331635.5486674 | 7170850.72744353 | [8 empty] | 943 |  | 955 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | AUTOMATIC | 50899 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NATURAL DISASTER AT AREA OF INCIDENT - MUDSLIDE/FLOODING | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [52 empty] | HEAVY RAINS/FLOODS |  | MUDSLIDE |  |  |  | NO | [306 empty] | ALI MATIN | PIPELINE SAFETY AND COMPLIANCE ADVISOR | amatin@semprautilities.com | 9099190463 |  |  |  |  | TROY BAUER | PIPELINE SAFETY AND COMPLIANCE MANAGER | 9093357915 | tbauer@semprautilities.com | SOCALGAS OBSERVED A PRESSURE DROP IN THE TRANSMISSION PIPELINE IN SANTA BARBARA COUNTY. AUTOMATED SAFETY EQUIPMENT DESIGNED TO STOP THE FLOW OF GAS SHUT OFF THE NATURAL GAS FLOW TO THE SECTION OF THE DAMAGED PIPELINE. UPON A PRELIMINARY SITE VISIT, SOCALGAS DISCOVERED A SECTION OF LINE 1005 DAMAGED, LIKELY DUE TO THE HEAVY RAIN WEATHER AND RESULTING MUD, DEBRIS FLOW, AND/OR FLOODING. AS SOON AS SAFETY PERMITTED, SOCALGAS CREWS AND CONTRACTORS CUT AND CAPPED THE LINE ON EITHER SIDE OF THE DAMAGED SECTION AND PURGED ALL REMAINING NATURAL GAS. SOCALGAS HAS RECEIVED SOME INFORMATION SUGGESTING THAT ONE OR MORE PEOPLE MAY HAVE BEEN INJURED CONSEQUENTIAL TO THE MUD/DEBRIS FLOW DAMAGE SUSTAINED BY LINE 1005. THE ISOLATION AND FOLLOWING CUT AND CAP PROCEDURE DID NOT YIELD ANY SERVICE INTERRUPTIONS. SOCALGAS IS CONTINUING TO ASSESS THE TRANSMISSION PIPELINE SYSTEM IN THE MONTECITO AREA FOR ANY ADDITIONAL DAMAGES. THIS EVENT WAS REPORTED TO THE DOT AND TO THE CPUC DUE TO THE POTENTIAL RELEASE OF GAS AND THE DAMAGE COST EXCEEDING $50,000. THE TOTAL COST IN RESPONSE TO THIS EVENT IS PENDING AND WILL BE PROVIDED ONCE AVAILABLE. THE 48-HOUR NOTIFICATION WAS COMPLETED PER NRC #1201510. FOR ANY FURTHER QUESTIONS, PLEASE CONTACT IK SONG AT (818) 279-5388. UPDATE (4/30/2018): THE PRELIMINARY COST INFORMATION IN PART D HAS BEEN UPDATED AS A PART OF THIS SUPPLEMENTAL REPORT. THE COST IS NOT FINALIZED AND WILL BE UPDATED ACCORDINGLY. PLEASE CONTACT IK SONG AT (818) 279-5388 FOR ANY FURTHER QUESTIONS. UPDATE 4/8/2019: UPDATED YTD TOTAL COST INFORMATION (FINALIZED). NUMBER OF PEOPLE EVACUATED DUE TO INCIDENT IS UNKNOWN AS THE ENTIRE AREA WAS UNDER MANDATORY AND VOLUNTARY EVACUATION PROTOCOLS. FOR ANY FURTHER QUESTIONS, PLEASE CONTACT ALI MATIN AT (909) 919-0463.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180023 | 30964 | 2018-02-08 13:02 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2018-01-22 17:37 | 2018 |  |  | 34.3556 | -89.9904 | 1202589 | 2018-01-22 18:52 |  | NATURAL GAS |  | 4030 | 7799 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-01-22 18:21 | 2018-01-30 23:05 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-01-22 17:37 | 2018-01-22 18:05 | ONSHORE | MS | 38606 | BATESVILLE | PANOLA | MILEPOST | 63-1+6.63 | 100-1 | 63-1+6.63 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 77 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 |  | 0.281 | 45000 | SEAMLESS, CARBON STEEL | SEAMLESS |  | NATIONAL TUBE | COAL TAR | [28 empty] | 1944 | 1944 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 2 LOCATION | NO |  | 435 |  | NO | NO | NO |  | 0 | 0 | 26126 | 27198.9898458749 | 13500 | 12159.5744680851 | 137061 | 142690.069174977 | 7200 | 7495.70262919311 | 66719 | 69459.1366273799 | METALLURGICAL REPORT, KM INTEGRITY GROUP AND KM METALLURGICAL GROUP EXPENSES. |  | 250606 | 125914.245716711 | 259003.47274551 | [8 empty] | 690 |  | 750 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 49738 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM WAS NOT THE CAUSE OR CONTRIBUTING FACTOR TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES | [7 empty] | YES | TENSILE OVERLOAD | [16 empty] | YES | [59 empty] | YES | YES |  |  | YES |  |  |  | 2011 | [31 empty] | 2011 | [23 empty] | YES | 1967 | 1041 | NO | [13 empty] | NO | [63 empty] | JORGE LOPEZ | SENIOR PIPELINE ENGINEER COMPLIANCE CODES AND STD | jorge_lopez@kindermorgan.com | 701-609-6218 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR ENGINEERING COMPLIANCE CODES AND STD | 713-369-9443 | jaime_hernandez@kindermorgan.com | AT 5:37 PM A LOCAL RESIDENT CONTACTED, BY PHONE, A TGP LINE PATROLLER TO REPORT A SUSPECTED LEAK. THE LEAK WAS CONFIRMED ONSITE AND COMPANY EMERGENCY RESPONSE PROCEDURES WERE IMPLEMENTED AT 6:05 P.M. THE VALVE SECTION 63-1BL TO 64-1 WAS ISOLATED BY 6:21 P.M., BLOWN DOWN, AND THE LEAK SITE WAS SECURED. A SECTION OF THE PIPE INCLUDING THE LEAK LOCATION WAS CUT OUT AND SHIPPED BY TGP PERSONNEL TO ANDERSON AND ASSOCIATES IN HOUSTON, TEXAS FOR METALLURGICAL EVALUATION. THE SECTION OF PIPELINE REMOVED WAS REPLACED AND THE PIPELINE SEGMENT WAS PLACED BACK INTO SERVICE ON JANUARY 30, 2018 AT 11:05 P.M CORRECTIVE ACTION: PRIOR TO RETURN TO SERVICE, PIPE WITH CIRCUMFERENTIAL CRACKING AND THE REMAINING SAG WRINKLE BENDS IN THE VICINITY WHERE REMOVED AND REPLACED WITH COMMENSURATE PIPING FOR THE LOCATION. POST COMPLETION OF STARTUP OPERATIONS CONDUCTED A GAS LEAK SURVEY OVER THE ENTIRE VALVE SECTION. NO PUBLIC AND NON-OPERATOR PRIVATE PROPERTY DAMAGE WERE INCURRED WITH THIS INCIDENT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180024 | 32937 | 2018-02-08 17:00 | SUPPLEMENTAL FINAL | 180 | SPIRE ALABAMA INC. | 605 RICHARD ARRINGTON JR BLVD N | BIRMINGHAM | AL | 35203 | 2018-01-06 15:06 | 2018 |  |  | 33.6571 | -86.6657 | 1201299 | 2018-01-08 09:40 |  | NATURAL GAS |  | 1090.725 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | SHUTDOWN NOT REQUIRED FOR PIPELINE TO CONTINUE TO OPERATE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-01-06 15:06 | 2018-01-06 15:06 | ONSHORE | AL | 35215 | BIRMINGHAM | JEFFERSON | MILEPOST | UNKNOWN | EAST BIRMINGHAM FEEDER | 1041 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 |  |  |  | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1959 | 1959 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | NO |  | 195 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 13531 | 12187.4964539007 | 26508 | 27596.678513146 | 36661 | 38166.6602901179 | 0 | 0 |  |  | 76700 | 42822.4387661847 | 77950.8352571645 | [8 empty] | 415 |  | 550 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL |  | NO |  | YES | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE VOLUME OF RELEASED GAS WAS NOT SIGNIFICANT ENOUGH TO BE IDENTIFIED BY SCADA. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [64 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | [10 empty] | NO |  |  | YES | PRIVATE EASEMENT | [7 empty] | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO | [7 empty] | PREVIOUS DAMAGE | [121 empty] | NO | [62 empty] | NO | NO |  |  | NO | [13 empty] | NO | [63 empty] | LAURA KLECKLEY | MANAGER- PIPELINE SAFETY- INTEGRITY MANAGEMENT | laura.kleckley@spireenergy.com | 205-326-2680 |  |  |  |  | CRAIG HOEFERLIN | VICE PRESIDENT - OPERATION SERVICES | 314-349-2972 | craig.hoeferlin@spireenergy.com | ON JANUARY 6, 2018 AT 3:06 PM CT SPIRE CREWS RESPONDED TO A LEAK ON A 12" 500 PSIG MAOP TRANSMISSION PIPELINE AND DISCOVERED A 3" DIAGONAL CRACK IN THE BODY OF THE PIPE. SPIRE CREWS INSTALLED A STOPPER FITTING AND UTILIZED A CRITICAL VALVE TO ISOLATE AND REPLACE THE SECTION OF DAMAGED PIPE. THE REPAIR ON THE PIPELINE WAS COMPLETED ON JANUARY 10, 2018 AT 2:11 AM CT. THE DAMAGED SECTION OF PIPE WAS SENT TO AN INDEPENDENT TESTING LABORATORY AND THE EVALUATION CONFIRMED THAT THE LEAK WAS CAUSED BY PIPE FAILURE DUE TO PREVIOUS EXTERNAL MECHANICAL DAMAGE. IT IS UNKNOWN WHEN THIS DAMAGE OCCURRED .SPIRE DETERMINED THIS WAS A REPORTABLE INCIDENT ON JANUARY 8, 2018 AT APPROXIMATELY 9:40 AM CT BASED ON REPAIR COSTS EXCEEDING THE $50,000 THRESHOLD. NOTE: IN PART E, QUESTION 5, SPIRE WAS REQUIRED TO INPUT AN ANSWER FOR 5A, 5B AND 5C CONCERNING VALVES USED TO INITIALLY ISOLATE THE PIPELINE. WE DID NOT UTILIZE VALVES TO INITIALLY ISOLATE THE LINE UPON DISCOVERY OF THE LEAK. DURING THE REPAIR PROCESS, WE UTILIZED A CRITICAL VALVE AND A STOPPER FITTING TO ISOLATE AND REPAIR THE SECTION OF DAMAGED PIPE ONLY. NOTE: THIS REPORT WAS DUE TO PHMSA ON FEBRUARY 6, 2018 BUT SPIRE WAS UNABLE TO SUBMIT THIS REPORT ON THAT DATE DUE TO THE PHMSA PORTAL BEING DOWN. THE PHMSA PORTAL WAS BACK UP AT 10:46 AM ET ON FEBRUARY 8, 2018.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180025 | 30884 | 2018-02-09 09:00 | SUPPLEMENTAL FINAL | 39210 | BOARDWALK STORAGE COMPANY, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2018-01-20 12:59 | 2018 |  |  | 30.3107 | -91.3076 | 1202423 | 2018-01-20 13:34 |  | NATURAL GAS |  | 104 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-01-20 13:00 | 2018-01-25 12:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2018-01-20 12:59 | 2018-01-20 13:05 | ONSHORE | LA | 70427 | PLAQUEMINE | IBERVILLE | MILEPOST | 804-0+00 | CHOCTAW BSC COMPRESSOR STATION | BSC | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | OTHER | COMPRESSOR STATION YARD |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2008 |  | CARBON STEEL |  | OTHER | [8 empty] | NATURAL GAS COMPRESSOR MECHANICAL FAILURE AND ENERGY RELEASE | CLASS 1 LOCATION | NO |  | 628 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 290 | 261.205673758865 | 1056806 | 1100208.82121487 | 200 | 208.213961922031 | 0 | 0 |  |  | 1057296 | 505391.259448871 | 1100678.24085055 | [8 empty] | 765 |  | 1440 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | YES | 2 | 0 | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  | YES | [31 empty] | YES | LOSS OF STATION COMMUNICATION NETWORK | [161 empty] | SHANNON MATTINGLY | PA OQ AND EVENT SUPPORT PROGRAM LEADER | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | DARRAL WARD | MANAGER PIPELINE SAFETY | 2706886356 | darral.ward@bwpmlp.com | BOARDWALK STORAGE COMPANY'S CHOCTAW COMPRESSOR NO. 1 EXPERIENCED A FAILURE. SCADA INDICATED A FUSIBLE LOOP FIRE DETECTION SHUTDOWN AND ESD. THE ROOT CAUSE WAS DETERMINED TO BE DEFECTIVE PLC COMMUNICATIONS. THE COMMUNICATION NETWORK MISTAKENLY SIGNALED FOR THE LUBE OIL PUMPS AND AIR COMPRESSORS TO SHUTDOWN. IT IS ALSO BELIEVED THE SUCTION VALVE WAS COMMANDED TO CLOSE BUT THIS CANNOT BE VERIFIED. THE COMMAND TO SHUTDOWN THE MOTOR WAS NEVER RECEIVED BY THE MOTOR SWITCHGEAR. THE RESULT WAS THE LOSS OF LUBE OIL AND THE MOTOR CONTINUED TO RUN. 8-31-18 UPDATED COSTS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180026 | 30614 | 2018-02-09 12:14 | SUPPLEMENTAL FINAL | 3 | ACADIAN GAS PIPELINE SYSTEM | 1100 LOUISIANA ST. | HOUSTON | TX | 77002 | 2018-01-14 12:54 | 2018 |  |  | 30.185 | -91.0097 | 1201916 | 2018-01-14 13:44 |  | NATURAL GAS |  | 17000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-01-14 12:54 |  | YES |  |  |  | YES |  |  |  |  | YES | [6 empty] | 0 | 2018-01-14 12:54 | 2018-01-14 13:30 | ONSHORE | LA | 70734 | GEISMAR | ASCENSION | SURVEY STATION NO. | 2+00 | KOCH-GEISMAR 16" | 307-0203 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.25 | 52000 | API-5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | LONESTAR LINE PIPE | COAL TAR | [28 empty] | 1965 | 1965 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 96 | 16 |  | CLASS 1 LOCATION | NO |  | 345 |  | NO | NO | NO |  | 50000 | 52053.4904805077 | 0 | 0 | 47000 | 42333.3333333333 | 500000 | 520534.904805077 | 220000 | 229035.358114234 | 0 | 0 |  |  | 817000 | 411855.344011283 | 843957.086733152 | [8 empty] | 692 |  | 975 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | MANUAL | 2255 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER ON DUTY ACTED IN ACCORDANCE WITH THE ROLE AND RESPONSIBILITIES REQUIRED FOR HIS JOB AND DID NOT CONTRIBUTE TO THIS INCIDENT. | [12 empty] | YES | 1 | 0 | YES | 1 | 0 | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING | [5 empty] | YES | THE EXACT ENVIRONMENT THAT CONTRIBUTED TO THE OBSERVED CORROSION IS UNKNOWN. |  | YES |  |  | YES | [5 empty] | NO | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | NATHAN L. GRAY JR. | SENIOR PIPELINE COMPLIANCE SPECIALIST | ngray@eprod.com | 985-493-4629 |  |  |  |  | NATHAN L. GRAY JR. | SENIOR PIPELINE COMPLIANCE SPECIALIST | 985-493-4629 | ngray@eprod.com | AT 12:54 PIPELINE CONTROL CENTER RECEIVED AN ALARM ON THE KOCH-GEISMAR 16" PIPELINE NEAR THE MISSISSIPPI RIVER ROAD, HIGHWAY 75, IN GEISMAR, LOUISIANA. PIPELINE CONTROL CENTER DISPATCHED OPERATIONS TO SHUT DOWN ALL RELATED PIPELINES IN THE IMMEDIATE AREA UNTIL FIELD VERIFICATIONS COULD BE DETERMINED AS TO THE CAUSE OF THE LOW PRESSURE. OPERATIONS PERSONNEL ARRIVED AT APPROXIMATELY 13:30 AND FOUND A RUPTURED PIPELINE WITH FIRE AND EMERGENCY OFFICIALS ON SITE. AT 13:32 IT WAS DETERMINED THE RUPTURE EXCEEDED REPORTING REQUIREMENTS AND THE NRC WAS NOTIFIED AT 13:44. THE FIRE SELF-EXTINGUISHED AT 15:42 AND THE SITE WAS SECURED BY COMPANY PERSONNEL. THE FRACTURE SURFACE COINCIDED WITH AN AREA OF CORROSION PRESENT ALONG THE BOTTOM OF THE PIPE. METALLOGRAPHY CONFIRMED THE PRESENCE OF INTERNAL CORROSION AND IDENTIFIED AN ISOLATED AREA OF ENVIRONMENTAL CRACKING PRESENT AT THE BASE OF THE INTERNAL CORROSION. THE EXACT ENVIRONMENT THAT CONTRIBUTED TO THE OBSERVED CORROSION AND CRACKING IS UNKNOWN. THE KOCH-GEISMAR 16" PIPELINE REMAINS OUT OF SERVICE PURGED OF PRODUCT AND CAPPED UNDERGROUND AT THE SITE OF THE INCIDENT. THE CHICO D 20" NORTH PIPELINE NEAR THE KOCH-GEISMAR 16" PIPELINE RUPTURE SITE HAS BEEN MODIFIED REPLACING A BELOW GROUND VALVE WITH AN ABOVE GROUND VALVE AND RETURNED TO SERVICE. 48 HR. NRC NUMBER 1202025 A SUPPLEMENTAL/FINAL REPORT ON JULY 12, 2018 REFLECTS A CHANGE TO PART E 5(A) CHANGING ORIGINAL VALVE CLOSED TO REMOTELY OPERATED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180027 | 17609 | 2018-02-13 15:14 | ORIGINAL FINAL | 31286 | ONEOK GAS TRANSPORTATION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2018-01-18 11:30 | 2018 |  |  | 35.2769 | -97.6283 | 1202570 | 2018-01-22 16:50 |  | NATURAL GAS |  | 1089 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | USED PLUGGING AND BYPASS TO ISOLATE AFFECTED SEGMENT | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-01-18 11:30 | 2018-01-18 11:45 | ONSHORE | OK | 73065 | NEWCASTLE | MCCLAIN | MILEPOST | MP 21.50 | A-1100 | F JUNCTION | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 24 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PULSATION BOTTLE OR DRIP/DRIP COLLECTION DEVICE | [38 empty] | 1970 |  | CARBON STEEL |  | LEAK |  |  | OTHER | INTERNAL CORROSION | [5 empty] | CLASS 2 LOCATION | NO |  | 442 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 3000 | 2702.12765957447 | 78000 | 81203.445149592 | 10000 | 10410.6980961015 | 0 | 0 |  |  | 91000 | 44854.7275965613 | 94316.270905268 | [8 empty] | 667 |  | 810 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 86 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | OTHER | OPERATOR NOTIFIED BY LOCAL DISTRIBUTION COMPANY EMPLOYEE |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS UNDETECTABLE BY SCADA SYSTEM. THE CONTROLLER RESPONDED AS EXPECTED ONCE THE LEAK WAS CONFIRMED. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | GENERAL CORROSION | [5 empty] | YES | INTERNAL CORROSION | YES | [5 empty] | YES |  |  |  | NO | NO | YES | YES | [313 empty] | KAREN PEREZ | REGULATORY COMPLIANCE COORDINATOR | karen.perez@oneok.com | 918-595-1703 |  |  |  |  | WESLEY DUNBAR | VP NATURAL GAS PIPELINE OPERATIONS | 918-588-7424 | wesley.dunbar@oneok.com | AT 11:30 CST ON 01/18/2018 ONEOK GAS TRANSPORTATION (OGT) PIPELINE OPERATOR RECEIVED A CALL FROM LOCAL DISTRIBUTION COMPANY EMPLOYEE. HE STATED THAT OGT HAD GAS POSSIBLY EMERGING FROM THE GROUND WEST OF PIG BARREL ON A-1100 WEST 16, AT F-JUNCTION, NEAR NEWCASTLE, OK. OGT PIPELINE OPERATOR CONTACTED PIPELINE CONTROL AND OPERATIONS PERSONNEL WERE IMMEDIATELY DISPATCHED TO LOCATION. LEAK WAS VERIFIED AND OGT NOTIFIED OKLAHOMA CORPORATION COMMISSION. NO RESIDENCES, STRUCTURES OR PUBLIC SPACES WERE IMPACTED BY THE NATURAL GAS. THE PIPELINE PRESSURE WAS LOWERED FROM 667 PSIG TO 532 PSIG AND CONTINUED TO FEED CUSTOMERS. OGT OPERATIONS PERSONNEL STARTED EXCAVATING FOR THE REPAIR ON 01/18/2018. THE SITE WAS EXCAVATED AND A PIPELINE DRIP (LEAK LOCATION) WAS REMOVED AND A NEW SECTION OF PIPE WAS INSTALLED. THE PIPELINE WAS RETURNED TO REGULAR SERVICE ON 01/20/2018.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180028 | 17612 | 2018-02-15 13:39 | ORIGINAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2018-01-22 01:00 | 2018 |  |  | 34.3745 | -92.7661 | 1202539 | 2018-01-22 11:37 |  | NATURAL GAS |  | 4047 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | ISOLATED THE FAILED OPEN REGULATOR AND REPAIRED. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-01-22 01:00 | 2018-01-22 01:45 | ONSHORE | AR | 72104 | PERLA | HOT SPRING | MILEPOST | PERLA | PERLA | PERLA | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ABOVEGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | BARTON CONTROLLER BOURDEN TUBE BROKE IN TWO PIECES CAUSING 1 4" REGULATOR TO FAIL CLOSE AND ONE 4 " TO FAIL OPEN CAUSING RELIEF VALVE TO BLOW. | CLASS 1 LOCATION | NO |  | 121 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 11600 | 10448.2269503546 | 0 | 0 | 450 | 468.481414324569 | 0 | 0 |  |  | 12050 | 11047.1966311521 | 10916.7083646792 | [8 empty] | 803 |  | 850 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EQUIPMENT FAILURE | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | YES | [19 empty] | YES | [177 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | DURING THE EARLY MORNING OF 1/22/18, A BOURDON TUBE BROKE IN A BARTON CONTROLLER CAUSING A 4 INCH REGULATOR TO FAIL CLOSE AND ANOTHER 4 INCH TO FAIL OPEN. THIS CAUSED A RELIEF VALVE TO RELIEVE. SYSTEM CONTROL NOTIFIED THE LOCAL OPERATIONS GROUP OF THE ISSUE. TWO O&M TECHNICIANS WERE DISPATCHED AND ARRIVED ON SITE AT 01:45. THE O&M TECHNICIANS INSTALLED GAUGES AND DISCOVERED THE PROBLEM. THEY ISOLATED THE FAILED OPEN REGULATOR (WHICH HAD THE FAILED CONTROLLER) AND THE FAILED SHUT REGULATOR CAME BACK INTO SERVICE. THE FAILED CONTROLLER WAS REPAIRED. PLANS HAVE BEEN MADE ARE TO REPLACE THE ENTIRE CONTROLLER WITH A BECKER PILOT CONTROLLER. GAS LOSS WAS CALCULATED TO BE 4,047 MCF. THE NRC WAS NOTIFIED ON 1/22/18 AT 11:37 (NRC#1202539). A FOLLOW UP CALL WAS PROVIDED TO THE NRC ON 1/24/18 AT 07:37 (NRC#1202699).
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180029 | 30892 | 2018-03-01 08:04 | SUPPLEMENTAL FINAL | 32163 | ROCKIES EXPRESS PIPELINE LLC | 370 VAN GORDON ST | LAKEWOOD | CO | 80228 | 2018-01-31 02:41 | 2018 |  |  | 39.83 | -81.3188 | 1203240 | 2018-01-31 03:51 |  | NATURAL GAS |  | 23500 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-01-31 03:15 | 2018-02-28 16:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2018-01-31 02:41 | 2018-01-31 03:00 | ONSHORE | OH | 43788 | 2.5 MILES NE OF SUMMERFIELD | NOBLE | MILEPOST | APPROX 209+05 | ROCKIES EXPRESS PIPELINE | SENECA LATERAL | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 72 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 24 |  | 0.344 | 70000 | API 5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | STUPP | EPOXY | [9 empty] | PIPE GIRTH WELD | [18 empty] | 2014 | 2013 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 24 | 24 |  | CLASS 1 LOCATION | NO |  | 634 |  | NO | NO | NO |  | 150000 | 156160.471441523 | 0 | 0 | 85367 | 76890.8439716312 | 3500000 | 3643744.33363554 | 65000 | 67669.53762466 | 345000 | 359169.084315503 | GEOTECH, METALLURGICAL, X-RAY REVIEW, MONITORING AND MODELING |  | 4145367 | 2019902.99268704 | 4303634.27098886 | [8 empty] | 1297 |  | 1444 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 74097 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO, THE CONTROLLER CONFIRMED THE RUPTURE (LOSS OF PRESSURE) BEFORE OPERATOR PERSONNEL ARRIVED ON SITE | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [52 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | LANDSLIDE |  |  |  |  | NO | [306 empty] | AMY LAGA | COMPLIANCE COORDINATOR | amy.o.laga@tallgrassenergylp.com | 303-763-3445 |  |  |  |  | JENNIFER ECKELS | COMPLIANCE MANAGER | 303-763-3486 | jennifer.eckels@tallgrassenergylp.com | THE SENECA LATERAL, A PORTION OF THE ROCKIES EXPRESS PIPELINE, OWNED AND OPERATED BY TALLGRASS ENERGY (TALLGRASS), EXPERIENCED AN IN-SERVICE RUPTURE ON JANUARY 31, 2018 NEAR THE CITY OF SUMMERFIELD, OH AT 2:41 AM EASTERN LOCAL TIME. THE RUPTURE OCCURRED ALONG THE GIRTH WELD SEAM OF WELD ID BML-079 (STA.209+05.9). THE RUPTURED GIRTH WELD WAS A MAIN LINE WELD BETWEEN TWO 24-INCH OUTER DIAMETER (OD), 0.344-INCH WALL THICKNESS (WT), API 5L PSL 2 X70 GRADE PIPE. THE RUPTURE OCCURRED BETWEEN ROAD 513 AND ROAD 379 IN A FORESTED PORTION OF THE RIGHT OF WAY (ROW). THE MAXIMUM ALLOWABLE OPERATING PRESSURE (MAOP) OF THE LINE AT THIS LOCATION IS 1444 PSIG AND WAS OPERATING AT 1297 PSIG AT THE TIME OF RUPTURE. THE RUPTURE LOCATION IS APPROXIMATELY 4 MILES FROM THE MARK WEST PROCESSING PLANT AND 10 MILES FROM THE SENECA COMPRESSOR STATION. THE ENTIRE ROUTE IS CLASS 1 NON-HCA. THE LINE WAS NOT FLOWING ANY GAS AT THE TIME OF FAILURE. FIRE RESULTED FROM THE LINE FAILURE, THERE WERE NO INJURIES, AND THE ONLY KNOWN PROPERTY DAMAGE WAS TO SURROUNDING TREES. TALLGRASS CONDUCTED A ROOT CAUSE ANALYSIS (RCA) WITH THE GOALS OF IDENTIFYING CAUSAL FACTORS ASSOCIATED WITH THE RUPTURE EVENT AND DEVELOPING POTENTIAL PROACTIVE ACTION PLANS FOR ELIMINATING SIMILAR THREATS. THE RCA TEAM FOCUSED ON CAUSAL FACTORS ASSOCIATED WITH THE RUPTURE EVENT: ENVIRONMENTAL, MATERIALS, CONSTRUCTION/INSTALLATION AND INTEGRITY MANAGEMENT. SUBSEQUENT TO THE RCA DISCUSSION, AND WITH AGREEMENT FROM ALL PARTIES INVOLVED, IT WAS DEEMED THAT THE GIRTH WELD RUPTURE WAS AN OVERLOAD FAILURE CAUSED BY AXIAL STRESS DUE TO MOVEMENT OF THE PIPE THAT EXCEEDED THE CROSS-SECTIONAL TENSILE STRENGTH OF THE NET SECTION WELD ZONE SURROUNDING THE CRACK INITIATION LOCATION. THIS DETERMINATION IS SUPPORTED BY METALLURGICAL ANALYSIS, STRAIN CAPACITY EVALUATION AND GEOTECHNICAL FINDINGS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180030 | 30421 | 2018-03-02 16:01 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 4720 PIEDMONT ROW DR. | CHARLOTTE | NC | 28210 | 2018-02-03 10:25 | 2018 |  |  | 34.4829 | -82.631 | 1203747 | 2018-02-06 15:55 |  | NATURAL GAS |  | 0 | 19.905 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-02-05 03:00 | 2018-02-25 15:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-02-03 10:25 | 2018-02-03 10:45 | ONSHORE | SC | 29624 | ANDERSON | ANDERSON | MILEPOST | 1.43 | LINE 347 | LINE 347 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 4 |  | 0.237 |  | GRADE B PIPE | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1952 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | VERY SMALL FISH EGG BUBBLES | [5 empty] | CLASS 3 LOCATION | NO |  | 123 |  | NO | NO | NO |  | 0 | 0 | 57 | 59.3409791477788 | 0 | 0 | 211500 | 220186.264732548 | 0 | 0 | 0 | 0 |  |  | 211557 | 101098.544605621 | 220245.605711695 | [8 empty] | 600 |  | 720 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 5000 | NO | [5 empty] | YES | TOO SMALL. | YES |  |  |  |  | YES | 4 INCH TOO SMALL. | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT RESULTED FROM MINOR LEAK FROM THE PIPE. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [146 empty] | CHRISTOPHER RANSOME | PIPELINE SAFETY AND COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | MANAGER- PIPELINE SAFETY | 704-731-4618 | farris.berry@duke-energy.com | DURING A NORMAL RECOAT PROJECT, A BUBBLING ON THE PIPE WRAPPING WAS DISCOVERED. WHAT APPEARED TO BE A "POSSIBLE" LEAK WAS NOT MEASURABLE DUE TO ITS SMALL SIZE. A SECTION OF THE PIPING WAS CUT OUT AND SENT FOR ANALYSIS. PIPE WAS TESTED DURING ANALYSIS. TWO SMALL LEAKS WERE FOUND ON THE SEAM. THE CAUSE IS UNKNOWN.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180031 | 30307 | 2018-03-07 17:38 | SUPPLEMENTAL FINAL | 22435 | WEST TEXAS GAS INC | 211 NORTH COLORADO | MIDLAND | TX | 79701 | 2018-02-09 10:55 | 2018 |  |  | 28.6681 | -100.4526 | 1203954 | 2018-02-09 11:37 |  | NATURAL GAS |  | 50 | 187 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-02-09 11:15 | 2018-02-09 19:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-02-09 11:00 | 2018-02-09 11:05 | ONSHORE | TX | 78852 | EAGLE PASS | MAVERICK | MILEPOST | 44.75 | 6K-16 EL INDIO PIPELINE | EAGLE PASS CLASS 3 /HCA | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 72 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6.625 |  | 0.188 | 42000 | API5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1975 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | YES | METHOD1 | 163 |  | NO | NO | NO |  | 0 | 0 | 800 | 832.855847688123 | 225 | 202.659574468085 | 25000 | 26026.7452402538 | 5000 | 5205.34904805077 | 14000 | 14574.9773345422 | CNG DURING PERMANENT REPAIR OUTAGE |  | 45025 | 21619.063771918 | 46842.587045003 | [8 empty] | 450 |  | 1015 | 192.619(A)(4) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 23033 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | YES | YES | STATE HIGHWAY | [9 empty] | CONTRACTOR | AUGER | ROAD WORK | YES | 1852258633 | TEXAS 811 | UTILITY OWNER | YES | YES | YES | 8 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO MAINTAIN THE MARKS | [263 empty] | RAY REED | DIRECTOR OF IM | rreed@westtexasgas.com | (806)358-1321 | (806)354-0797 |  |  |  | BART BEAN | OPERATIONS MANAGER | (432)682-4349 | bbean@westtexasgas.com | DURING TXDOT MAINTENANCE ACTIVITIES TO REPLACE/UPGRADE GUARD RAILS ON FM 1021 WITHIN THE CITY LIMITS OF EAGLE PASS, TX A SUB CONTRACTOR AUGURED INTO THE TOP OF WTG'S 6K-16 EL INDIO PIPELINE. PIPELINE SEGMENT WAS IMMEDIATELY ISOLATED AND DE-PRESSURED. TWO DELIVERIES TO TEXAS STATE GAS WERE IMPACTED AND SUSTAINED OUTAGES FOR APPROXIMATELY EIGHT HOURS.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180032 | 30612 | 2018-03-15 14:40 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2018-02-22 16:57 | 2018 |  |  | 41.8139 | -77.2791 | 1205015 | 2018-02-22 19:35 |  | NATURAL GAS |  | 11720 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-02-22 16:35 | 2018-02-22 21:50 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-02-22 16:25 | 2018-02-22 18:00 | ONSHORE | PA | 16901 | Not Within a Municipality | TIOGA | MILEPOST | 0 | TGP STATION 315 (WELLSBORO CS) | LINE 300-1; VALVE SEGMENT 313 - 315 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1969 |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENTIONAL GAS RELEASE FOLLOWING STATION ESD EVENT CAUSED BY STORM WEATHER AND LOSS OF STATION POWER; ISSUE WITH CONTROL SYSTEM OF VALVE AS-2 DID NOT ALLOW CLOSE CYCLE OF VALVE ALLOWING CONTINUED VENTING OF NATURAL GAS; ALSO THERE WAS AN ISSUE WITH EMERGENCY GENERATOR AND UPS. | CLASS 1 LOCATION | NO |  | 850 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 32933 | 29663.0567375887 | 5700 | 5934.09791477788 | 1000 | 1041.06980961015 | 8690 | 9046.89664551224 | INVESTIGATION AND TESTING COSTS |  | 48323 | 38107.5881423755 | 45685.1211074889 | [8 empty] | 804 |  | 1170 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LOCAL STATION SYSTEM NOT FUNCTIONING DUE TO LOS OF POWER; GAS CONTROL RECOGNIZED LOSS OF COMMUNICATION AND ENGINES COMING OFF-LINE; GAS CONTROL NOTIFIED TECHNICIANS TO RESPOND; | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES |  |  | YES |  |  |  | YES | UNINTENTIONAL GAS RELEASE FOLLOWING STATION ESD EVENT CAUSED BY STORM WEATHER AND LOSS OF STATION POWER; ISSUE WITH CONTROL SYSTEM OF VALVE AS-2 DID NOT ALLOW CLOSE CYCLE OF VALVE ALLOWING CONTINUED VENTING OF NATURAL GAS; ALSO THERE WAS AN ISSUE WITH EMERGENCY GENERATOR AND UPS / BPS. | [11 empty] | YES | [10 empty] | YES | PLEASE SEE PART H NARRATIVE | [161 empty] | WILLIAM MARTIN MULLER | SPECIALIST - PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205 325 3863 | 205 325 3592 |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713 369 9443 | jaime_hernandez@kindermorgan.com | 02/22/2018; STORM WEATHER CAUSED A LOSS OF COMMERCIAL ELECTRICAL POWER AND COMMUNICATIONS AT TGP STATION 315 AT 16:25 EST OR LATER. WITH LOSS OF COMMERCIAL POWER, THE STATION ESD SYSTEM FUNCTIONED AS DESIGNED. 16:35 EST, GAS CONTROL NOTIFIED OPERATORS AT MANNED STATION 313 OF STATION 315 COMPRESSOR UNITS FALLING OFF-LINE. TECHNICIANS WERE IMMEDIATELY DISPATCHED AND ARRIVED AT STATION 315 AT 18:00 EST AND FOUND NATURAL GAS VENTING TO ATMOSPHERE FROM THE STATION BLOW DOWN. TECHNICIANS FOUND VALVE AS-2 HAD NOT CLOSED. TECHNICIANS CLOSED VALVE AS-2 AT 18:10 EST THEREBY TERMINATING THE UNINTENTIONAL NATURAL GAS VENTING. THE STATION UPS AND BPS SYSTEMS, WHICH HAD SHUT OFF AS UPS DEPLETED, WERE TESTED AND RESET. THE CONTROLS OF VALVE AS-2 WERE TESTED, FLUID LEVELS CHECKED AND THE VALVE WAS GREASED. STATION 315 WAS RETURNED TO SERVICE ON 02/22/2018 AT APPROXIMATELY 21:50 PM, EST. THERE WAS NO CUSTOMER IMPACT. INVESTIGATION AND MODIFICATIONS CONTINUED. 03/23/ 2018, DEBRIS WAS CLEANED FROM FILTERS OF VALVE CONTROLLERS IN THE YARD. UPS WAS RETIRED AND BPS PROVIDED ANOTHER ELECTRICAL SOURCE. 05/18/2018, STATION ESD SYSTEM TESTED PROPERLY. TESTING OF THE EMERGENCY GENERATOR WAS COMPLETED ON 06/27/2018; AN ISSUE WAS FOUND WITH THE AIR / FUEL CONTROLLER THUS UNIT WAS NOT PROVIDING FULL STATION LOAD, NOT SUPPORTING UPS AND BPS. REPAIR OF AIR / FUEL CONTROLLER HAS BEEN COMPLETED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180033 | 30642 | 2018-03-21 22:07 | SUPPLEMENTAL FINAL | 19610 | TRANSWESTERN PIPELINE COMPANY LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2018-02-16 12:18 | 2018 |  |  | 35.6195 | -108.5529 | 1204895 | 2018-02-21 17:02 |  | NATURAL GAS |  | 1047 | 23398 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-02-16 16:21 | 2018-03-01 12:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-02-16 12:18 | 2018-02-16 12:52 | ONSHORE | NM | 87301 | GALLUP | MCKINLEY | MILEPOST | MP 89 | NMBM154B | SAN JUAN 36" LOOP | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 96 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 36 |  | 0.43 | 70000 | API 5L | SPIRAL WELDED |  | CORINTH PIPEWORKS | EPOXY | [9 empty] | PIPE GIRTH WELD | [18 empty] | 2005 | 2004 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 861 |  | NO | NO | NO |  | 0 | 0 | 51826 | 53954.4839528558 | 2319 | 2088.74468085106 | 85000 | 88490.9338168631 | 1000 | 1041.06980961015 | 40000 | 41642.7923844062 | METALLURGICAL LAB ANALYSIS |  | 180145 | 87144.7209325953 | 187218.024644586 | [8 empty] | 874 |  | 1202 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 48176 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK RATE WAS NON-DETECTABLE BY THE SCADA SYSTEM. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | YES | [7 empty] | YES | CRACK IN A GIRTH WELD. | [12 empty] | YES | [63 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | NATHAN HLAVATY | DIRECTOR - REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | (713)857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - REGULATORY COMPLIANCE | (713)857-5479 | nathan.hlavaty@energytransfer.com | 2/16/18 12:18 GAS CONTROL RECEIVED NOTIFICATION FROM A LANDOWNER OF A POSSIBLE LEAK. 14:40 MCKINLEY COUNTY SHERIFF DEPARTMENT AND LANDOWNER WERE NOTIFIED OF BLOWDOWN. 16:21 THE AFFECTED LINE SEGMENT WAS ISOLATED AND BLOWN DOWN BETWEEN VALVE SECTIONS. 2/21/18 EXCAVATION OPERATIONS CONFIRMED LEAK SOURCE; CRACK IN GIRTH WELD. NRC TELEPHONIC NOTIFICATION MADE AT 17:02 NRC#1204895. PHMSA AID NOTIFIED. 2/23/18 48-HOUR UPDATE NRC NOTIFICATION MADE AT 11:24 NRC#1205058. PHMSA AID UPDATED. 3/1/18 REPAIRS COMPLETED, THE LINE WAS RETURNED TO SERVICE AT 12:00. 7/11/18 THIS SUPPLEMENTAL/FINAL REPORT UPDATES PART G APPARENT CAUSE. THE RESULTS OF THE METALLURGICAL ANALYSIS INDICATED THAT THE LEAK INITIATED AT A BOTTOM SIDE CRACK IN A GIRTH WELD. PART D - 7.D COST FOR THE METALLURGICAL ANALYSIS WAS ALSO UPDATED. 7/16/18 THIS SUPPLEMENTAL/FINAL REPORT UPDATES THE PART A #4 - TO 2/16/18 AT 12:18.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180034 | 30644 | 2018-03-23 16:31 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2018-02-26 01:18 | 2018 |  |  | 42.9404 | -76.1176 | 1205235 | 2018-02-26 08:59 |  | NATURAL GAS |  | 13126 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | ONLY UNIT 1A SHUTDOWN; OTHER CS 241 UNITS REMAINED ON LINE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-02-25 23:30 | 2018-02-26 07:15 | ONSHORE | NY | 13084 | Not Within a Municipality | ONONDAGA | MILEPOST | 0 | TGP STATION 241 LAFAYETTE | LINE 200-1, VALVE SECTION 237 TO 245 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 1998 |  | CARBON STEEL |  | OTHER | [8 empty] | A LOOSE WIRE INTERFERED WITH SOFTWARE LOGIC WHICH LED TO UNINTENTIONAL SHUTDOWN OF UNIT 1A AND UNINTENTIONAL OPENING OF THE UNIT VENT VALVE THUS ALLOWING AN UNINTENTIONAL RELEASE OF NATURAL GAS TO ATMOSPHERE. | CLASS 1 LOCATION | NO |  | 593 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 36884 | 33221.7588652482 | 1700 | 1769.81867633726 | 100 | 104.106980961015 | 4050 | 4216.33272892112 | THREE PERSONS (DIAGNOSE, TROUBLE SHOOT, REMEDIATE, SOFTWARE AND SYSTEM TESTING) |  | 42734 | 37238.0952120694 | 39312.0172514676 | [8 empty] | 735 |  | 821 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A LOOSE WIRE INTERFERED WITH SOFTWARE LOGIC WHICH LED TO UNINTENTIONAL SHUTDOWN OF UNIT 1A AND UNINTENTIONAL OPENING OF THE UNIT VENT VALVE THUS ALLOWING AN UNINTENTIONAL RELEASE OF NATURAL GAS TO ATMOSPHERE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | A WIRING ISSUE CONCERNING THE UNIT'S BYPASS VALVE OPERATOR CAUSED LOSS OF "CLOSE" SIGNAL FROM A LOCAL PLC WHICH CAUSED VENT VALVE TO OPEN WHILE SUCTION AND DISCHARGE VALVES ALSO REMAINED OPEN ALLOWING UNINTENTIONAL RELEASE OF NATURAL GAS; | [18 empty] | YES |  |  |  | YES | SEE "OTHER" ABOVE AND NARRATIVE | [161 empty] | WILLIAM MARTIN MULLER | SPECIALIST - PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205 410 4383 | 205 325 3592 |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713 369 9443 | jaime_hernandez@kindermorgan.com | ON 02/26/2018; TECHNICIANS ARRIVED AT UNMANNED COMPRESSOR STATION 241 FOR ROUTINE TASKS AT WHICH TIME THEY HEARD GAS VENTING TO ATMOSPHERE THROUGH THE STATION'S BLOWDOWN SILENCER. THE TECHNICIANS ASSESSED THE ATMOSPHERE SAFETY OF A-BUILDING BY EVALUATING THE STATUS OF ITS GAS MONITORING SYSTEM WHICH WAS DETERMINED TO BE SAFE. THEY PROCEEDED TO ENTER A-BUILDING AND ASSESSED THE HMI NEAREST TO THE BUILDING ENTRANCE AND OBSERVED NORMAL RUN STATUS FOR UNIT 1A. CONTINUING THEIR INVESTIGATION TO FIND THE SOURCE OF THE VENTING GAS, THE TECHNICIAN THEN APPROACHED UNIT 1A AND OBSERVED VISUALLY AND AUDIBLY THAT IT WAS NOT RUNNING, EVEN THOUGH THE HMI HAD INDICATED IT WAS. FOLLOWING THE NOISE OF THE VENTING GAS, A 1 1/2-INCH VENT VALVE ON UNIT 1A WAS FOUND TO BE IN THE OPEN POSITION AS OPPOSED TO ITS NORMAL CLOSED POSITION. THE TECHNICIAN CLOSED THE VALVE MANUALLY TERMINATING THE RELEASE OF NATURAL GAS AT 07:20. OUR INCIDENT INVESTIGATION FOUND A LOSS OF "CLOSE" SIGNAL FROM A LOCAL PLC TO THIS VALVE CAUSED THE VENT VALVE TO OPEN AS DESIGNED. WE ALSO DETERMINED THAT A WIRING ISSUE CONCERNING THE UNIT'S BYPASS VALVE OPERATOR CAUSED AN ISSUE WITH THE PLC PROGRAM AND A SOFTWARE LOCK-UP OF THE PLC PROCESSOR ( MAJOR FAULT OF PLC PROCESSOR ) RESULTING IN DE-ENERGIZED OUTPUTS CAUSING VENT VALVE TO OPEN WHILE SUCTION AND DISCHARGE VALVES ALSO REMAINED OPEN. WE ALSO DETERMINED THAT AN ALARM TO INDICATE A LOSS OF LOCAL COMMUNICATION WAS NOT ENABLED WITHIN THE PCL LOGIC THEREFORE GAS CONTROL DID NOT RECEIVE NOTICE OF LOSS OF LOCAL COMMUNICATION. POST INVESTIGATION WIRING REPAIR WAS COMPLETED 02/26/2018 AND UNIT 1A WAS RETURNED TO SERVICE ON 02/26/2018. IN ADDITION CHANGES TO PLC LOGIC AND STATION ALARM WERE COMMISSIONED BY 02/27/2018. TGP ALSO DETERMINED THAT THE UNINTENTIONAL RELEASE OF GAS STARTED ON 02/25/2018, AT 23:30 HOURS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180035 | 30176 | 2018-03-29 11:52 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2018-03-01 19:31 | 2018 |  |  | 27.7484 | -97.8569 | 1205581 | 2018-03-01 20:28 |  | NATURAL GAS |  | 24118 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE ESD HAPPENED BEFORE THE INCIDENT. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-03-01 20:03 | 2018-03-01 20:03 | ONSHORE | TX | 78330 | AGUA DULCE | NUECES | MILEPOST | VALVE A2-D1 | COMPRESSORE STATION # 1 | GAS SUPPY TUBING TO VALVE A2-D1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | TUBING | [38 empty] | 1999 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL | OTHER | [8 empty] | THE SUPPLY GAS TUBING TO THE STATION DISCHARGE VALVE'S ACTUATOR CAME DISLODGED DURING AN ESD EVENT WHICH KEPT THE VALVE FROM GOING FULLY CLOSED. | CLASS 1 LOCATION | NO |  | 481 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 65118 | 58652.3829787234 | 608 | 632.970444242974 | 0 | 0 | 0 | 0 |  |  | 65726 | 61098.138788475 | 59285.3534229664 | [8 empty] | 845 |  | 860 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | OTHER | LOCAL OPERATING PERSONNEL INCLUDING CONTRACTORS. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A MANNED FACILITY AND THE GAS CONTROL OR SCADA WAS NOT RESPONSIBLE FOR THE EVENTS THAT OCCURRED AT THE COMPRESSOR STATION. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | DEFECTIVE OR LOOSE TUBING OR FITTING | MATERIAL/WELD/EQUIP FAILURE | DEFECTIVE OR LOOSE TUBING/FITTING | [166 empty] | DEFECTIVE OR LOOSE TUBING OR FITTING | [20 empty] | YES | [177 empty] | KRITI BHAYANI | PIPELINE ENGINEER - COMPLIANCE-CODES AND STANDARDS | kriti_bhayani@kindermorgan.com | 3616886492 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR - COMPLIANCE - CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | ON 3/1/18 AT APPROXIMATELY 7:31 PM A COMPRESSOR ON UNIT 2 IN THE COMPRESSOR BUILDING HAD AN ISSUE WHEREBY THE COMPRESSOR ROD PACKING BEGAN LEAKING CAUSING THE GAS DETECTOR TO SENSE 40% LEL WHICH INITIATED A STATION HAZARD ATMOSPHERE ALARM AND CAUSED EMERGENCY SHUT DOWN (ESD). AT 8:00PM AN ERL CALL WAS SENT OUT. AT 8:03 LOCAL OPERATING PERSONNEL IDENTIFIED THAT THE STATION ESD VALVE WAS STILL VENTING GAS BEYOND THE TYPICAL STATION BLOW DOWN TIME. UPON FURTHER INVESTIGATION PERSONNEL FOUND THAT STATION DISCHARGE VALVE (A2-D1) DID NOT FULLY CLOSED AS REQUIRED WITH AN ESD EVENT. PERSONNEL IDENTIFIED THAT THE SUPPLY GAS TUBING TO THE STATION DISCHARGE VALVE'S ACTUATOR CAME DISLODGED DURING THE INITIATION OF THE ESD PROCESS WHICH PREVENT THE FULL CLOSURE OF THIS VALVE. PERSONNEL ISOLATED THE SUPPLY GAS AND THEN RECONNECTED IT TO THE ACTUATOR. ONCE RECONNECTED THE GAS SUPPLY WAS OPENED AGAIN AND THE STATION DISCHARGE VALVE CLOSED AS REQUIRED. THIS STOPPED THE VENTING OF NATURAL GAS FROM THE STATION'S ESD VALVE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180036 | 30148 | 2018-04-04 10:18 | ORIGINAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2018-03-27 18:40 | 2018 |  |  | 34.4343 | -92.9037 | 1207823 | 2018-03-27 20:09 |  | NATURAL GAS |  | 4600 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELIEF VALVE WAS ISOLATED AND REPAIRED. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-03-27 18:43 | 2018-03-27 19:05 | ONSHORE | AR | 72104 | MAGNET COVE | HOT SPRING | MILEPOST | BM-28 | BM-28 | LAKE CATHERINE POWER PLANT | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | TUBING | [38 empty] | UNKNOWN |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | NO |  | 219 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 12528 | 11284.085106383 | 500 | 520.534904805077 | 500 | 520.534904805077 | 0 | 0 |  |  | 13528 | 12176.6019174013 | 12325.1549159931 | [8 empty] | 153 |  | 175 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | DEFECTIVE OR LOOSE TUBING OR FITTING | MATERIAL/WELD/EQUIP FAILURE | DEFECTIVE OR LOOSE TUBING/FITTING | [166 empty] | DEFECTIVE OR LOOSE TUBING OR FITTING | [20 empty] | YES | [177 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | ON MARCH 27TH, 2018 AT 18:43 ENABLE GAS TRANSMISSION SYSTEM CONTROL RECEIVED A CALL FROM THE LAKE CATHERINE POWER PLANT THAT A RELIEF VALVE WAS VENTING. AT 18:45 AN ENABLE O&M TECH WAS DISPATCHED TO THE SCENE. THE O&M TECH REPORTED THAT THE PILOT CONTROLLED RELIEF VALVE BELONGED TO ENABLE (BM-28) AND IT WAS VENTING WHEN HE ARRIVED. BROKEN PILOT STAINLESS STEEL TUBING WAS DETERMINED TO BE THE CAUSE FOR THE VENTING. THE CAUSE OF THE TUBING TO BREAK IS DUE TO VIBRATION. THE O&M TECH REPLACED THE TUBING AND FITTINGS AND THE RELIEF VALVE WAS PLACED BACK IN SERVICE. THE GAS RELEASE IS ESTIMATED TO BE 4.6 MMCF. THE NRC WAS NOTIFIED AT 20:09, (NRC #1207823). A 48 HOUR FOLLOW UP (NRC #1207860) WAS PROVIDED ON MARCH 28TH AT 11:01 CST.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180038 | 30811 | 2018-04-04 21:34 | SUPPLEMENTAL FINAL | 18112 | SAN DIEGO GAS & ELECTRIC CO | 8326 CENTURY PARK COURT | SAN DIEGO | CA | 92123 | 2018-03-07 10:43 | 2018 |  |  | 32.7718 | -117.162 | 1206139 | 2018-03-07 11:57 |  | NATURAL GAS |  | 1324 | 619 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-03-07 18:15 | 2018-03-09 02:50 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-03-07 10:43 | 2018-03-07 10:50 | ONSHORE | CA | 92108 | SAN DIEGO | SAN DIEGO | SURVEY STATION NO. | 111+88.00 | SUPPLY LINE 49-11 | L-49-11 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 264 |  | YES |  |  |  |  | YES | UNCASED | [16 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.25 | 52000 | PIPE,STEEL,20", .250 WALL API 5L-X-52 | OTHER | UNKNOWN | UNKNOWN | OTHER | WRAPPED- UNKNOWN TYPE | [27 empty] | 1958 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 0.3 | 0.8 | [7 empty] | CLASS 3 LOCATION | YES | METHOD2 | 276 |  | NO | NO | NO |  | 0 | 0 | 3714 | 3866.53327289211 | 7944 | 7155.23404255319 | 265000 | 275883.499546691 | 135000 | 140544.424297371 | 0 | 0 |  |  | 411658 | 200344.402084579 | 427449.691159507 | [8 empty] | 320 |  | 400 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | YES | NO | NOT MANDATED |  |  | MANUAL | MANUAL | 13000 | NO |  | YES | YES |  |  |  |  | YES |  | YES | YES |  |  |  | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO | YES | STATE HIGHWAY | [9 empty] | CONTRACTOR | DIRECTIONAL DRILLING | ROAD WORK | YES | 180650610 | DIGALERT | CONTRACT LOCATOR | YES | YES | YES | 40 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | EXCAVATION PRACTICES NOT SUFFICIENT (OTHER) | [263 empty] | BRYON WALSH | PIPELINE SAFETY AND COMPLIANCE ADVISOR | bwalsh@semprautilities.com | 619-992-1473 |  |  |  |  | KHOA LE | SR PIPELINE SAFETY AND COMPLINACE ADVISOR | 626-893-4536 | kle2@semprautilities.com | ON MARCH 7, 2018 AT APPROXIMATELY 10:43 AM, A THIRD-PARTY SUBCONTRACTOR STRUCK A 20-INCH GAS STEEL TRANSMISSION LINE WHILE PERFORMING DIRECTIONAL BORING. THIS RESULTED IN AN ESCAPE OF GAS. CREWS RESPONDED AND WERE ABLE TO CONTROL THE GAS THROUGH CLOSING VALVES AT NEARBY REGULATOR STATIONS. THERE WERE NO INJURIES THAT RESULTED FROM THIS INCIDENT. INVESTIGATION REVEALED THAT PRIOR TO THE INCIDENT, THE THIRD-PARTY SUBCONTRACTOR HAD A USA TICKET WHICH EXPIRED ON MARCH 5, 2018. THE LINE HAD BEEN PROPERLY MARKED BY AN SDG&E CONTRACTOR. AT THE TIME OF THE INCIDENT, THE THIRD-PARTY SUBCONTRACTOR DID NOT HAVE A VALID USA TICKET FOR THE EXCAVATION ACTIVITIES PERFORMED. IN ADDITION, THE THIRD-PARTY SUBCONTRACTOR FAILED TO REQUEST A STAND-BY FROM D SDG&E WHICH IS REQUIRED WHEN EXCAVATING NEAR HIGH PRESSURE GAS FACILITIES. THIS INCIDENT WAS REPORTED TO DOT AND CPUC DUE TO ESTIMATED DAMAGE AMOUNT EXCEEDING $50,000. FOR ANY FURTHER QUESTIONS, CONTACT KHOA LE AT (626) 893-4536.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180039 | 30308 | 2018-04-09 09:34 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2018-03-10 19:11 | 2018 |  |  | 40.098 | -75.6813 | 1206477 | 2018-03-10 22:07 |  | NATURAL GAS |  | 12672 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RESPONDING OPERATION PERSONNEL, WERE ABLE TO MANUALLY CLOSE THE ESD VALVE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-03-10 19:11 | 2018-03-10 19:42 | ONSHORE | PA | 19425 | EAGLE | CHESTER | MILEPOST | FIRE VALVES | EAGLE COMPRESSOR STATION | FIRE VALVES T-5, T-3, L-7216 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | MAINLINE | BALL |  | CAMERON |  |  |  | 1983 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | UNINTENDED RELEASE OF NATURAL GAS THROUGH TWO 6-INCH BLOW OFF VALVES, DUE TO FIRE VALVES DID NOT FULLY CLOSED. | CLASS 3 LOCATION | YES | METHOD2 | 506 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 30032 | 27050.0992907801 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 30032 | 28044.0661938534 | 27050.0992907801 | [8 empty] | 830 |  | 1200 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE MALFUNCTION OF THE ESD SYSTEM WAS NOT DUE TO ANY INVOLVEMENTS BY GAS CONTROL PERSONNEL OR MANIPULATION OF ANY CONTROL.. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | A COUPLING FAILURE LED TO A COOLANT SPILL TRIGGERED THE GAS DETECTION. | [161 empty] | KAMRAN ROSTAMI ASRABADI | COMPLIANCE SPECIALIST | kamran_rostami@transcanada.com | 3043572351 |  |  |  |  | GEORGE HAMATY | MANAGER | 3043573728 | george_hamaty@transcanada.com | ON MARCH 10TH, 2018, AN UNINTENDED RELEASE OF NATURAL GAS (MATERIAL) EVENT INTO ATMOSPHERE WAS REPORTED TO THE NATIONAL RESPONSE CENTER (NRC). THIS EVENT TOOK PLACE AT EAGLE COMPRESSOR STATION (CS) FACILITY IN CHESTER COUNTY, PENNSYLVANIA. THIS CS IS CLASSIFIED AS TRANSMISSION WHERE IT IS OPERATED AND MAINTAINED BY COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA). AT 19:25 E.S.T., EAGLE CS HAD ANEMERGENCY SHUTDOWN (ESD) WHICH WAS SUBJECT TO THE FAILURE OF ALL THE STATION FIRE VALVES TO CLOSE. ALL TIMES WERE RECORDED IN EASTERN STANDARD TIME. THE CAUSE OF THE CS ESD WAS THE RESULT OF A COOLING SYSTEM ISSUE ON UNIT 2 AT THE STATION. AT APPROXIMATELY AT 18:52 UNIT 2 HAD A HYDRAULIC PUMP COUPLING FAIL WHICH CAUSED THE ENGINE TO BEGIN TO OVERHEAT. AT APPROXIMATELY AT 19:11 THE UNIT HAD SHUT DOWN ON A HIGH COOLING WATER OUTLET TEMPERATURE WHEN ENGINE OUTLET TEMPERATURE REACHED 200 DEGREES F. THE TEMPERATURE ON THE UNIT CONTINUED TO INCREASE TO A MAXIMUM RECORDED TEMP OF 216 DEGREES F ON THE WATER OUTLET TRANSMITTER AND THE COOLANT EXPANDED AND OVERFLOWED FROM THE COOLING SYSTEM EXPANSION TANK ON TO THE COMPRESSOR BUILDING FLOOR INTO THE BASEMENT OF THE COMPRESSOR BUILDING NEAR UNIT 2. THE WATER/ALCOHOL COOLANT WHICH OVERFLOWED INTO THE BASEMENT WAS DETECTED AS A POTENTIAL FLAMMABLE GAS LEAK BY THE BASEMENT GAS DETECTION SYSTEM RIGHT BELOW UNIT NO. 2 AND THE GAS DETECTION SHUTDOWN ALL UNITS AT THE STATION. ONCE THE GAS DETECTION REACHED A LEVEL OF GREATER THAN 50% LOWER EXPLOSIVE LEVEL, THE GAS DETECTION INITIATED AN ESD OF THE STATION TO EVACUATE THE GAS FROM THE DETECTED RELEASE OF MATERIAL IN THE COMPRESSOR BUILDING. THERE WAS A REPORTABLE RELEASE OF MATERIAL FROM THE STATION AS A RESULT OF BLOWDOWN VALVES C54-66, AND C54-61 OPENING AND THE CORRESPONDING EMERGENCY VALVES FAILURE TO CLOSE IN ORDER TO ISOLATE STATION FROM THE PIPELINE. APPROXIMATELY 19:42., OPERATIONS PERSONNEL ARRIVED ON SITE, WHERE THE UNINTENDED RELEASE OF MATERIAL WAS ISOLATED AND THE AREA WAS SECURED SAFELY. A 48-HR UPDATE NOTICE WAS CALLED-IN TO THE NRC, WHERE THE UPDATE REPORT NO. WAS 1206574. IN ORDER TO PREVENT ANY FUTURE EVENTS FROM SIMILAR RECURRENCE, THE IDENTIFIED KEY RECOMMENDED CHANGES TO EAGLE CS FACILITY WERE: 1. UNIT COOLING SYSTEM HIGH TEMP ALARM/SHUTDOWN SETPOINTS LOWER TO AVOID ANOTHER UPSET OR BOIL-OVER CONDITION. THE OVERFLOWS FROM EXPANSION TANKS WERE PLUMBED TO 55 GALLON DRUMS OUTSIDE OF THE COMPRESSOR BUILDING. 2. DURING THE NEXT ANNUAL ESD SYSTEM TEST, THE ESD PNEUMATIC SYSTEM WILL BE PURGED WITH CLEAN DRY AIR. KEY COMPONENTS OF ESD PNEUMATIC PANEL TO BE INSPECTED, CHECKED FOR CONTAMINATION AND CLEANED THEN TESTED BEFORE RETURNING THEM INTO SERVICE. SIMILARLY, THE INDIVIDUAL EMERGENCY BLOWDOWN, ESD VERSA VALVES WILL BE CLEANED, INSPECTED, OR FULL FUNCTIONALITY BEFORE RETURNING THEM BACK INTO SERVICE. 3. THE ESD SYSTEM SOLENOID VALVE OPERATION DID NOT OPERATE AS DESIGNED WHICH WAS MOST LIKELY DUE TO MOISTURE/ICE IN THE VALVE. ADDITIONAL INSPECTIONS ARE RECOMMENDED TO BE IMPLEMENTED TO THE PNEUMATIC SYSTEM IN ORDER TO ENSURE FREE LINES OF MOISTURE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180040 | 30218 | 2018-04-16 13:46 | SUPPLEMENTAL FINAL | 2714 | DOMINION ENERGY TRANSMISSION, INC. | 925 WHITE OAKS BOULEVARD | BRIDGEPORT | WV | 26330 | 2018-03-18 05:37 | 2018 |  |  | 40.6319 | -79.4436 | 1207068 | 2018-03-18 08:54 |  | NATURAL GAS |  | 20200 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | UNINTENTIONAL RELEASE OF GAS FROM RELIEF VALVE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-03-18 05:27 | 2018-03-18 06:37 | ONSHORE | PA | 15686 | SPRING CHURCH | ARMSTRONG | MILEPOST | GA-26 | MCILWAIN JUNCTION | LN-26 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENTIONAL RELEASE OF GAS FROM RELIEF VALVE. | CLASS 1 LOCATION | NO |  | 464 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 43896 | 39537.5319148936 | 0 | 0 | 500 | 520.534904805077 | 0 | 0 |  |  | 44396 | 41229.2938665021 | 40058.0668196987 | [8 empty] | 678 |  | 945 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL |  | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | RELIEF VALVE NEARING END OF EXPECTED SERVICE LIFE AND SCHEDULED FOR REPLACEMENT. | [161 empty] | DANIEL STAHL | PIPELINE INTEGRITY ENGINEER | daniel.s.stahl@dominionenergy.com | 6818423365 |  |  |  |  | JONELL CARVER | MANAGER PIPELINE INTEGRITY | 6818423633 | jonell.l.carver@dominionenergy.com | GAS CONTROL RECEIVED INITIAL NOTIFICATION OF THIS INCIDENT ON 3/18/18 AT 5:27 AM AND RELAYED THE INFORMATION TO THE ON-DUTY OPERATIONS SUPERVISOR. THE ON-DUTY OPERATIONS SUPERVISOR DISPATCHED OPERATIONS PERSONNEL TO MCILWAIN JUNCTION TO INVESTIGATE. OPERATIONS PERSONNEL ARRIVED AT MCILWAIN JUNCTION ON 3/18/18 AT 6:37 AM AND CONFIRMED THE UNINTENTIONAL RELEASE OF GAS FROM A RELIEF VALVE ON LN-26. THE MAXIMUM ALLOWABLE OPERATING PRESSURE OF LN-26 IS 945 PSIG. THE OPERATING PRESSURE OF LN-26 AT THE TIME OF THE INCIDENT WAS 678 PSIG. THE PURPOSE OF THE RELIEF VALVE IS TO PROTECT LN-26 FROM THE MAXIMUM ALLOWABLE OPERATING PRESSURE OF LN-19. THE MAXIMUM ALLOWABLE OPERATING PRESSURE OF LN-19 IS 1000 PSIG. THE OPERATING PRESSURE OF LN-19 AT THE TIME OF THE INCIDENT WAS 677 PSIG. THE OPERATIONS PERSONNEL ISOLATED THE RELIEF VALVE BY CLOSING THE ISOLATION VALVE AT THE INLET OF THE RELIEF VALVE. THE OPERATIONS PERSONNEL VISUALLY INSPECTED, OPERATED, AND VERIFIED THE SET POINT OF THE RELIEF VALVE AND DETERMINED THAT THE RELIEF VALVE WAS FUNCTIONING PROPERLY. THE OPERATIONS PERSONNEL PLACED THE RELIEF VALVE BACK INTO SERVICE AND OPENED THE ISOLATION VALVE ON 3/18/18 AT 8:10 AM. IT WAS DETERMINED ON 3/18/18 AT 7:59 AM THAT THE INCIDENT LIKELY INVOLVED AN UNINTENTIONAL ESTIMATED GAS LOSS OF THREE MILLION CUBIC FEET OR MORE WHICH WOULD CLASSIFY IT AS REPORTABLE. INITIAL TELEPHONIC NOTIFICATION WAS MADE TO THE NATIONAL RESPONSE CENTER ON 3/18/18 AT 8:54 AM. THE NATIONAL RESPONSE CENTER ASSIGNED INCIDENT REPORT #1207068 TO THE INITIAL NOTIFICATION OF THE INCIDENT. ADDITIONAL TELEPHONIC NOTIFICATION WAS MADE TO THE NATIONAL RESPONSE CENTER ON 3/19/18 AT 3:42 PM TO CONFIRM THE INITIAL TELEPHONIC NOTIFICATION AND REVISE THE ESTIMATE OF THE VOLUME OF GAS UNINTENTIONALLY RELEASED BY THE RELIEF VALVE. THE NATIONAL RESPONSE CENTER ASSIGNED INCIDENT REPORT #1207203 FOR THE ADDITIONAL NOTIFICATION OF THE INCIDENT.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20180041 | 30226 | 2018-04-16 13:53 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2017-05-19 15:17 | 2017 |  |  | 37.3685 | -82.7441 | 1207960 | 2018-03-29 09:59 |  |  |  | 1486 | 46 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-05-20 13:55 | 2017-06-01 11:31 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-05-19 15:17 | 2017-05-19 17:57 | ONSHORE | KY | 41636 | BUCKINGHAM | FLOYD | SURVEY STATION NO. | 75+400 | PM-3 | PM3-20 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10 |  | 0.188 | 24000 | UNKNOWN | OTHER | UNKNOWN | UNKNOWN | NONE | [28 empty] | 1954 | 1954 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 2 LOCATION | NO |  | 157 |  | NO | NO | NO |  | 0 | 0 | 136 | 144.654316413486 | 4413 | 4041.71394230769 | 425465 | 452539.328918118 | 0 | 0 | 0 | 0 |  |  | 430014 | 211984.12156657 | 456725.697176839 | [8 empty] | 75 |  | 180 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 2300 | NO | [5 empty] | YES | NON-PIGGABLE GATHERING LINE - MECHANICALLY COUPLED PIPE | YES |  |  |  |  | YES | MECHANICALLY COUPLED PIPE | TYPE B GATHERING | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK DISCOVERED WAS NOT DUE TO ANY INVOLVEMENTS BY GAS CONTROL PERSONNEL | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | YES |  | NO | YES | YES |  |  |  | 2017 |  |  |  | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | CODY BOWERS | REGULATORY COMPLIANCE SPECIALIST | cody_bowers@transcanada.com | (304) 357-2814 |  |  |  |  | LEE ROMACK | MANAGER - REGULATORY COMPLIANCE | (832) 320-5315 | lee_romack@transcanada.com | ON MAY 19TH, 2017, LINE PM-3 WAS SUBJECT TO AN UNINTENTIONAL RELEASE OF NATURAL GAS (MATERIAL) INTO ATMOSPHERE RESULTING IN THE TOTAL COST EXCEEDING $50,000. LINE PM-3 IS A JURISDICTIONAL GATHERING TYPE B LINE THAT IS OPERATED AND MAINTAINED BY COLUMBIA GAS TRANSMISSION, LLC (TRANSCANADA) AND IS LOCATED IN FLOYD COUNTY, NEAR THE TOWN OF BUCKINGHAM, KENTUCKY. TRANSCANADA RECEIVED A NOTIFICATION FROM THE PUBLIC REGARDING A POTENTIAL GAS RELEASE OF MATERIAL IN CLOSE PROXIMITY TO LINE PM-3 AT 15:17 EST AND OPERATIONS PERSONNEL WERE DISPATCHED TO INVESTIGATE THE REPORTED MATERIAL RELEASE. UPON DISCUSSION AND INVESTIGATION BETWEEN THE LOCAL DISTRIBUTION COMPANY AND TRANSCANADA, THE LEAK WAS CONFIRMED AT 17:57 TO BE TRANSCANADA'S. IT WAS DETERMINED THAT GALVANIC CORROSION WAS THE PROBABLE CAUSE OF THE PINHOLE LEAK ON LINE PM-3 AND HAS SINCE BEEN REPAIRED AND RETURNED TO SERVICE ON JUNE 1ST, 2017. AFTER RECEIVING THE FINAL PROJECT COST WORK-ORDERS, THE REPAIR AMOUNT FOR THIS EVENT WAS FOUND TO HAVE EXCEEDED $50,000 IN REPAIR COSTS. AFTER IDENTIFYING THIS FACT, THIS EVENT WAS PROMPTLY CALLED INTO THE NATIONAL RESPONSE CENTER (NRC). A 48-HR UPDATE NOTICE WAS CALLED-IN TO THE NRC ON MARCH 31, 2018, REPORT NO. WAS 1208132.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180042 | 31038 | 2018-04-16 14:24 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | ONE ENERGY PLAZA | DETROIT | MI | 48226 | 2018-03-15 00:04 | 2018 |  |  | 42.5419 | -83.5606 | 1206906 | 2018-03-15 19:22 |  | NATURAL GAS |  | 7500 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | VALVE FAILED OPEN THROUGH ESD VENT, CLOSED VALVE. PIPELINE WAS NOT SHUT DOWN. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-03-15 00:04 | 2018-03-15 01:13 | ONSHORE | MI | 48381 | MILFORD | OAKLAND | MILEPOST | 1008 | MILFORD COMPRESSOR STATION | MILFORD COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENTIONAL RELEASE OF GAS THROUGH COMPRESSOR ESD VENT. UPSTREAM PIPELINE VALVE 1008 FAILED OPEN CAUSING RELEASE OF APPROXIMATELY 7.5 MMCF. | CLASS 3 LOCATION | NO |  | 660 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 22500 | 20265.9574468085 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 22500 | 21010.6382978723 | 20265.9574468085 | [8 empty] | 680 |  | 880 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | YES | [28 empty] | YES | [167 empty] | JOHN NEWTON | CODES AND STANDARDS SUPERVISOR | john.newton@dteenergy.com | 616-405-0719 |  |  |  |  | JOHN NEWTON | CODES AND STANDARDS SUPERVISOR | 616-405-0719 | john.newton@dteenergy.com | ON MARCH 15, 2018, AN ESD OCCURRED AT MILFORD COMPRESSOR STATION RESULTING IN A RELEASE OF NATURAL GAS AT VENT VALVE 1008. VENT VALVE 1008 WAS LOCKED CLOSED TO PREVENT RECURRENCE DURING INVESTIGATION. MILFORD COMPRESSOR STATION HAS ADEQUATE PROTECTION IN THE EVENT OF AN ESD. ON MARCH 23, 2018, IT WAS DETERMINED THAT THE SOLENOID CASING THAT CONTROLS THE VALVE HAD AN ACCUMULATION OF WATER. THE SEAL PROTECTING THE SOLENOID WAS NOT FULLY SEALED. WATER WAS REMOVED AND THE SEAL WAS FIXED. ADDITIONAL INVESTIGATION IS IN PROGRESS TO REVIEW ELECTRONICS OF THE SYSTEM. UPON FURTHER INVESTIGATION, IT WAS FOUND THAT AN EXCESS OF CURRENT TO THE CONTROL MODULE CAUSED THE SOLENOID CONTROLLING VALVE 1008 TO FAIL. THE CONTROL MODULE WAS REPLACED AND UPGRADED. DTE CONTROL MAINTENANCE TESTED ALL THE REMAINING CONTROL MODULES FOR VENT VALVES AT MILORD. IT WAS FOUND THAT ALL THE CURRENT READINGS WERE WITHIN THE OUTPUT LIMITS OF THE MODULES BEFORE PUTTING THE STATION BACK INTO SERVICE. RESULTS OF TESTING AND REPLACEMENT OF MODULES HAS BEEN SUPPLIED TO THE MICHIGAN PUBLIC SERVICE COMMISSION. DTE GAS BELIEVES THAT WITH THESE ACTIONS, WE DO NOT EXPECT A REPEAT OCCURRENCE. MILFORD COMPRESSOR STATION WAS PUT BACK INTO SERVICE ON APRIL 12, 2018.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180043 | 30255 | 2018-04-20 09:34 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2018-03-20 00:01 | 2018 |  |  | 32.9712 | -102.7493 | 1207240 | 2018-03-20 04:39 |  | NATURAL GAS |  | 3900 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELIEF VALVE LEAKING GAS ONLY. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-03-20 00:01 | 2018-03-20 04:00 | ONSHORE | TX | 79714 | Not Within a Municipality | YOAKUM | MILEPOST | MP 38.63 | PLAINS COMPRESSOR STATION | M840B FLOREY TO PLAINS | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | THE RELIEF VALVE FAILED AND VENTED GAS. THE ROOT CAUSE WAS THE PILOT SEAT WAS HARDENED AND THEN DEFORMED. ALSO, THE PILOT SPRING WOULD NOT HOLD A STEADY SET PRESSURE. THERE WAS ALSO CORROSION IN THE MAIN VALVE BODY, PISTON, SEAT AND DEBRIS IN THE PILOT. THE RELIEF VALVE VENTED DUE TO THE PILOT REGULATOR NOT HOLDING SETPOINT, AND THE RELIEF VALVE WOULD NOT RESEAT PROPERLY DUE TO THE INTERNAL CORROSION IN THE MAIN BODY. | CLASS 1 LOCATION | NO |  | 585 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 104000 | 93673.7588652482 | 100 | 104.106980961015 | 2000 | 2082.13961922031 | 0 | 0 |  |  | 106100 | 98119.3841211054 | 95860.0054654296 | [8 empty] | 653 |  | 800 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE GAS CONTROLLERS WERE NOT A CONTRIBUTING FACTOR TO THE RELIEF VALVE VENTING. | [12 empty] | YES | 4 | 0 | YES | 1 | 0 | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [22 empty] | YES | [168 empty] | JOHN A GORMLEY | SR. CORROSION SPECIALIST | john.gormley@nngco.com | 402-398-7494 |  |  |  |  | THOMAS CORRELL | VP PIPELINE SAFETY AND RISK | 402-398-7715 | thomas.correll@nngco.com | ON MARCH 20, 2018, THE RELIEF VALVE ON THE 30 INCH DIAMETER M840B IN THE PLAINS STATION YARD FAILED AND VENTED GAS TO THE ATMOSPHERE. A RELEASE OF 39 MILLION CUBIC FEET WAS REPORTED TO THE NATIONAL RESPONSE CENTER. THE LAST INSPECTION WAS PERFORMED ON MARCH 19, 2018. ROOT CAUSE: INTERNAL CORROSION IN MAIN VALVE BODY, PISTON AND SEAT, PILOT SEAT WAS HARD AND CRUSHED AND PILOT SPRING WOULD NOT HOLD A STEADY SET PRESSURE. THESE ISSUE CAUSED RELIEF VALVE TX-193 ' 2000 END OF 30-INCH-DIAMETER METER HEAD TO FAIL.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180044 | 31459 | 2018-04-20 15:16 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2018-03-23 02:27 | 2018 |  |  | 40.8222 | -73.959 | 1207487 | 2018-03-23 03:52 |  |  |  | 0 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | SHUTDOWN NOT REQ., PRESSURE REDUCED TO NORMAL USING EXISTING TRANSMISSION SYSEM. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-03-23 02:27 | 2018-03-23 02:27 | ONSHORE | NY | 10031 | NEW YORK CITY | NEW YORK | MILEPOST | ROV 62190 | CON EDISON | M1 - UPSTREAM OF ROV 62190 | NO | OPERATOR-CONTROLLED PROPERTY | TRANSITION AREA | SOIL/AIR INTERFACE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 |  | 0.5 | 52000 | API 5L / GRADE X52/X60 | OTHER | 30" SEGMENT SAW, 26" SEGMENT DSAW | MITTAL/ARCELOR MITTAL | OTHER | PRITECH AND RAVEN 405 EPOXY | [27 empty] | 2013 | 2013 | CARBON STEEL |  | OTHER | [8 empty] | PRESSURE EXCEEDED SEGMENT MAOP | CLASS 4 LOCATION | YES | METHOD1 | 387 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | [8 empty] | 478 |  | 350 | 192.619(A)(1) |  |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 | NO |  |  |  |  | AUTOMATIC | REMOTELY CONTROLLED | 87 | NO | YES | YES | YES |  |  |  |  | YES |  |  |  |  | YES | NO LAUNCHERS AVAILABLE | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES |  |  | YES |  | YES |  |  | NO |  |  | NO |  |  | INCORRECT OPERATION | PIPELINE OR EQUIPMENT OVERPRESSURED | INCORRECT OPERATION | PIPELINE/EQUIPMENT OVERPRESSURED | [204 empty] | PIPELINE OR EQUIPMENT OVERPRESSURED |  |  |  | YES | YES |  |  |  | NON-ROUTINE OPERATING CONDITIONS (ABNORMAL OPERATIONS OR EMERGENCIES) | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | VICTOR DADARIO | DEPARTMENT MANAGER | dadariov@coned.com | 718 7942873 |  |  |  |  | ANTHONY LETO | CHIEF ENGINEER | 718 8391759 | letoa@coned.com | ON MARCH 23, 2018, A MAIN VALVE INSPECTION WAS PERFORMED THAT INCLUDED A FULL REMOTE CLOSURE INSPECTION OF REMOTELY OPERATED VALVE (ROV) 62190, LOCATED IMMEDIATELY DOWNSTREAM OF THE TRANSCO (PIPELINE) 134TH STREET CITY GATE STATION IN MANHATTAN. THIS INSPECTION WAS PERFORMED BY CON EDISON GAS OPERATIONS PRESSURE CONTROL PERSONNEL WITH ASSISTANCE FROM INTERSTATE TRANSMISSION PIPELINE COMPANY PERSONNEL, WHO WERE ALSO ON SITE. PRIOR TO THE INSPECTION, THE CITY GATE STATION WAS FLOWING AT 13,000 DEKATHERMS PER HOUR AT AN OUTLET PRESSURE OF 287 PSIG INTO CON EDISON'S TRANSMISSION SYSTEM. AT 01:51, ALL PERSONNEL WERE ON SITE AND READY TO BEGIN THE INSPECTION ACTIVITIES, AT WHICH TIME CON EDISON'S GAS CONTROL GROUP BEGAN COORDINATING THE SHUTDOWN OF THE CITY GATE STATION WITH THE PIPELINE'S GAS CONTROL GROUP. AT 02:05, CON EDISON'S GAS CONTROL GROUP CONFIRMED WITH PIPELINE ON-SITE PERSONNEL THAT THE CITY GATE STATION WAS FULLY SHUTDOWN, WHICH HAD BEEN ACCOMPLISHED BY CLOSURE OF THE STATION METER RUNS MANUAL OUTLET VALVES. AT 02:08, AFTER BEING NOTIFIED THAT THE GATE STATION WAS FULLY SHUTDOWN, CON EDISON PRESSURE CONTROL PERSONNEL BEGAN PERFORMING THE MANUAL OPERATION PORTION OF THE ROV INSPECTION, WHICH WAS COMPLETED AT 02:09. CON EDISON PRESSURE CONTROL PERSONNEL THEN BEGAN PERFORMING THE REMOTE OPERATION PORTION OF THE ROV INSPECTION. AT 02:10, THE STATION OUTLET PRESSURE FELL BELOW 250 PSIG. AT 02:17, THE REMOTE OPERATION PORTION OF THE INSPECTION WAS COMPLETED, THEREBY CONCLUDING ALL TASKS ASSOCIATED WITH THE PLANNED ROV INSPECTION. AT 02:21, AN ON-SITE PIPELINE TECHNICIAN REQUESTED THAT CON EDISON GAS CONTROL CLOSE ROV 62190 DUE TO ACTIVATION OF THE STATION'S UNDER-PRESSURE PROTECTION, EQUIPMENT DESIGNED TO MAINTAIN A MINIMUM PRESSURE IN THE DOWNSTREAM PIPING, WHICH HAD ENGAGED WHEN THE STATION OUTLET PRESSURE FELL BELOW 250 PSIG. THE PIPELINE TECHNICIAN'S PLAN WAS TO INCREMENTALLY OPEN THE METER RUN #1 ISOLATION VALVE TO RAISE THE DOWNSTREAM PRESSURE ABOVE 250 PSIG, WHICH WOULD CAUSE THE UNDER-PRESSURE PROTECTION TO DISENGAGE AND THE REGULATOR RUNS TO CLOSE AUTOMATICALLY. CON EDISON GAS CONTROL WOULD THEN BE NOTIFIED TO RE-OPEN ROV 62190. AT 02:22, CON EDISON GAS CONTROL CLOSED ROV 62190. AT 02:23, CON EDISON GAS CONTROL NOTIFIED THE PIPELINE TECHNICIAN THAT THE ROV WAS CLOSING. THE PIPELINE TECHNICIAN RESPONDED INDICATING THAT, ONCE THE ROV WAS CLOSED, HE WOULD PROCEED TO OPEN THE MANUAL ISOLATION VALVE A SMALL AMOUNT TO INCREASE THE DOWNSTREAM PRESSURE. AT 02:26, CON EDISON GAS CONTROL RECEIVED A "HIGH-HIGH" PRESSURE ALARM AT THE GATE STATION, AND AT 02:27, THE PIPELINE TECHNICIAN NOTIFIED CON EDISON GAS CONTROL THAT ROV 62190 COULD BE RE-OPENED. AT 02:28, CON EDISON GAS CONTROL BEGAN SLOWLY OPENING ROV 62190 IN 10% INCREMENTS, WHICH CLEARED THE "HIGH-HIGH" PRESSURE ALARM AT 02:29. CON EDISON GAS CONTROL DETERMINED POST INCIDENT THAT THE MAXIMUM ALLOWABLE OPERATING PRESSURE (MAOP) OF THE CON EDISON OWNED SEGMENT OF TRANSMISSION PIPELINE IMMEDIATELY UPSTREAM OF THE ROV HAD BEEN EXCEEDED FOR APPROXIMATELY 2 MINUTES, DURING WHICH THE PRESSURE PEAKED AT 478 PSIG AT 02:28. INTERNAL NOTIFICATIONS WERE MADE AT 03:22, AND CON EDISON NOTIFIED THE NEW YORK PUBLIC SERVICE COMMISSION AND THE NATIONAL RESPONSE CENTER AT 03:52. TO PREVENT FUTURE RE-OCCURRENCE OF A SIMILAR EVENT, INTERNAL COMPANY OPERATING SPECIFICATIONS ARE BEING REVISED TO REQUIRE GAS ENGINEERING OVERSIGHT IN THE FORM OF WRITTEN WORK PROCEDURES FOR ROV'S LOCATED ON THE OUTLET OF CITY GATES AS WELL AS THE ELIMINATION OF FULL OPERATION TESTING TO BETTER ALIGN WITH REGULATORY REQUIREMENTS.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180046 | 30767 | 2018-04-28 21:01 | SUPPLEMENTAL FINAL | 4900 | KINDER MORGAN TEJAS PIPELINE | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2018-03-30 05:00 | 2018 |  |  | 26.4773 | -98.7207 | 1208067 | 2018-03-30 09:19 |  | NATURAL GAS |  | 3920 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-03-30 08:30 | 2018-04-23 11:12 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-03-30 08:25 | 2018-03-30 08:00 | ONSHORE | TX | 78582 | Not Within a Municipality | STARR | SURVEY STATION NO. | 0+22.5 | RIO GRANDE CS COMPRESSOR UNIT NO. 80 | CALPINE EXPANSION LATERAL | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2017 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE LEAKED PRIOR TO ACHIEVING ESTABLISHED SET POINT. | CLASS 1 LOCATION | NO |  | 378 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 11030 | 9934.82269503546 | 2600 | 2706.7815049864 | 1500 | 1561.60471441523 | 0 | 0 |  |  | 15130 | 12259.1837005888 | 14203.2089144371 | [8 empty] | 940 |  | 1170 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WERE NO SCADA INDICATIONS ASSOCIATED WITH THE EVENT THAT WOULD CAUSE THE GAS CONTROLLER TO SUSPECT AN ABNORMAL OPERATION AT THE STATION. GAS CONTROLLER ACTIONS DID NOT CAUSE OR CONTRIBUTE TO THE EVENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [16 empty] | YES | [174 empty] | STEPHEN R. DINES | ENGINEER - CODES AND STANDARDS | stephen_dines@kindermorgan.com | 719 329-5633 |  |  |  |  | JAIME A. HERNANDEZ | DIRECTOR OF ENGINEERING CODES AND STANDARDS | 713 369-9443 | jaime_hernandez@kindermorgan.com | ON MARCH 30, 2018 AT 8:00 AM, A TEJAS PIPELINE COMPANY (TEJAS) EMPLOYEE ARRIVED AT THE RIO GRANDE CS OFFICE IN STARR COUNTY, TEXAS AND HEARD THE SOUND OF AIR OR GAS VENTING. THE EMPLOYEE ACCESSED THE STATION DATA TO SAFELY IDENTIFY THE CAUSE OF THE SOUND. HE OBSERVED NO PRESSURES EXCEEDING MAOP. HE THEN APPROACHED THE COMPRESSOR BUILDING AND AT 8:25 AM CONFIRMED THAT THE SOUND WAS NATURAL GAS VENTING FROM THE RELIEF VALVE (RV) ON DISCHARGE PIPING DOWNSTREAM OF COMPRESSOR NO. 80. HE SHUT NO. 80 DOWN AND ISOLATED THE RV BY 8:30 AM STOPPING THE RELEASE OF NATURAL GAS. THE REPORTED CAPACITY OF THE RV (FARRIS ENGINEERING SERIES 2600 PRESSURE RELIEF VALVE TYPE 26KC1-4-920) WAS 39,333 SCFM WITH A SET PRESSURE OF 1,100 PSIG. THE NRC WAS NOTIFIED OF THE RELEASE ON MAY 30, 2018 AT 09:19 AM. THE TOTAL VOLUME OF THE RELEASE REPORTED WAS ESTIMATED TO BE 24,000 MCF. AT 9:43 AM, THE RRC OF TEXAS WAS ALSO NOTIFIED OF THE INCIDENT. ON APRIL 1, 2018 AT 5:52 AM, A REVISED RELEASE VOLUME (17,414 MCF) WAS REPORTED WITH THE 48-HOUR UPDATE TO THE NRC (NRC NO. 1208193). THE VOLUME WAS BASED ON THE MAXIMUM CAPACITY, ORIFICE DIAMETER OF 3 INCHES AT 940 PSIG FOR 325 MINUTES, ASSUMING THE RELEASE BEGAN AT 3:24 AM, BASED ON AVAILABLE DATA AT THE STATION. THIS TIME WAS SELECTED AS THE EARLIEST POSSIBLE MOMENT THE INCIDENT BEGAN AND WAS BASED ON AN OBSERVED PRESSURE DROP RECORDED ON DISCHARGE PIPING FOR NO. 80 THE MORNING OF THE EVENT. IT WOULD BE DETERMINED LATER IN THE INVESTIGATION THAT THIS OBSERVED PRESSURE DROP WAS CAUSED BY A STOP COMMAND ISSUED BY GAS CONTROL ON COMPRESSOR UNIT NO. 79; DETERMINED TO BE UNRELATED TO THE EVENT. ON APRIL 2, 2018, THE RV WAS INSPECTED BY TEJAS AND THEY WERE UNABLE TO LOCATE ANY SIGNS OF PHYSICAL DAMAGE TO THE UNIT BUT THEY DID NOTICE THE UNIT CONTINUED TO LEAK GAS. ON APRIL 11, 2018, TEJAS DECIDED TO SEND THE RV TO THE SUPPLIER FOR FURTHER INSPECTION AND REPAIR. THE VENDOR REPORTED THAT THE DISC HOLDER AND SOFT RETAINER SCREW WERE FOUND TO BE DAMAGED. AT THAT TIME, THE UNIT WAS REPAIRED WITH NEW PARTS AND ADJUSTED TO REESTABLISH THE REQUIRED SET POINT AND TESTED BY THE VENDOR. THE RV UNIT WAS REINSTALLED APRIL 16TH 2018. HOWEVER, NO.80 WAS NOT PLACED BACK INTO SERVICE UNTIL APRIL 23, 2018 AS THE UNIT WAS NOT NEEDED UNTIL THAT TIME. ON APRIL 11, 2018, TEJAS RE-ESTIMATED THE RELEASE VOLUME USING THE ACTUAL RV SPECIFICATIONS USING THE MAXIMUM CAPACITY FOR A TOTAL DURATION OF 325 MINUTES WITH THE RELEASE BEGINNING AT 3:24 AM AND ESTIMATED THE VOLUME TO BE 13,591 MCF. THIS WAS THE VALUE REPORTED WITH THE INITIAL 30-DAY INCIDENT REPORT TO PHMSA AND THE TRRC. ON MAY 3, 2018, THE RELEASE VOLUME WAS RE-ESTIMATED USING HOURLY GAS VOLUME MEASUREMENT DATA TO ESTABLISH AN HOURLY VOLUME LOSS THROUGH THE STATION DURING THE EVENT. THE TOTAL RELEASE VOLUME WAS 3,920 MCF. THE ESTIMATED DURATION OF THE EVENT USING THIS DATA REVEALED THE EVENT TRIGGERED A REPORTING REQUIREMENT BETWEEN 5:00 AM AND 6:00 AM AND LASTING UNTIL THE UNIT WAS ISOLATED AT 8:30 AM THAT MORNING. THEREFORE, TEJAS CHANGED THE RESPONSE TO PART A Q4 FROM 3:24 AM TO 5:00 AM WITH THIS REPORT. TEJAS BELIEVES THE HOURLY GAS LOSS REMAINS THE BEST ESTIMATE OF ACTUAL RELEASE VOLUME SINCE THE RV COULD NOT OPEN TO FULL CAPACITY DUE TO THE INTERNAL DAMAGE TO THE DISC PLATE AND SEAL THAT WOULD NOT ALLOW IT TO PROPERLY RESEAT. THIS EXPLAINS WHY THE RV WAS FOUND TO BE VENTING AT A PRESSURE BELOW THE ESTABLISHED SET POINT. THE RELEASE VOLUME IS ALSO UPDATED TO REFLECT 3,920 MCF DISCUSSED ABOVE. ON MAY 4, 2018, THE DAMAGED RV COMPONENTS WERE SENT TO AN-TECH LAB IN HOUSTON, TEXAS. ON JUNE 29, 2018, THE RESULTS OF THEIR METALLURGICAL INVESTIGATION SHOWED THE IMMEDIATE CAUSE WAS DUE A FRACTURED DISC LOCKING SCREW WHICH PREVENTED THE DISC FROM SEALING PROPERLY AGAINST THE ASSOCIATED O-RING. THE FRACTURE MORPHOLOGY IN THE DISC LOCKING SCREW WAS TORSIONAL OVERLOAD INDICATING THE LOCKING SCREW WAS OVER TORQUED DURING ASSEMBLY; REPRESENTING THE ROOT CAUSE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180047 | 31242 | 2018-05-01 09:17 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2018-04-03 15:21 | 2018 |  |  | 39.57 | -82.273 | 1208401 | 2018-04-03 19:37 |  | NATURAL GAS |  | 8204 | 11.8 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-04-03 17:30 | 2018-11-07 14:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-04-03 15:21 | 2018-04-03 16:30 | ONSHORE | OH | 43766 | Not Within a Municipality | HOCKING | SURVEY STATION NO. | 20+74 | LINE H-109 | LINE H-109 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | OTHER | A SPAN OVER A CREEK |  |  | YES | [6 empty] | YES | UNCASED | MONDAY CREEK | UNKNOWN | SHORELINE/BANK/MARSH CROSSING | [11 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 |  | 0.156 | 42000 | X42 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | EXTRUDED POLYEHYLENE | [28 empty] | 1981 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 6 | 1 |  | CLASS 1 LOCATION | NO |  | 113 |  | NO | NO | NO |  | 0 | 0 | 29 | 30.1910244786945 | 20510 | 18473.5460992908 | 1320000 | 1374212.1486854 | 0 | 0 | 40000 | 41642.7923844062 | OTHER COSTS INCLUDE METALLURGICAL ANALYSIS |  | 1380539 | 669081.000421589 | 1434358.67819358 | [8 empty] | 100 |  | 125 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 7844 | NO | YES | [6 empty] | YES |  | YES |  |  |  |  | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [52 empty] | HEAVY RAINS/FLOODS |  | OTHER |  |  | ABOVEGROUND CROSSING SUBMERSED IN FLOODED CREEK AND FAILED. | YES |  |  |  | YES | SUBMERGED SPAN WAS SUBJECT TO IMPACT BY FOREIGN OBJECTS FLOATING DOWNSTREAM. | [301 empty] | KAMRAN ROSTAMI ASRABADI | COMPLIANCE SPECIALIST | kamran_rostami@transcanada.com | (304)357-2351 |  |  |  |  | GEORGE HAMATY | US RC EAST MANAGER | (304)357-3728 | george_hamaty@ transcanada.com | ON APRIL 3, 2018, AT 15:21 EASTERN STANDARD TIME (EST) COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA) MONITORING CENTER RECEIVED A CALL FROM THE HOCKING COUNTY FIRE DEPARTMENT REGARDING A POTENTIAL NATURAL GAS RELEASE FROM COLUMBIA FACILITY IN NEW STRAITSVILLE, OH. COLUMBIA OPERATIONS PERSONNEL WERE ON SITE AT 16:30 EST AND CONFIRMED THAT THE UNINTENDED GAS RELEASE TO BE FROM LINE H-109. THE INVOLVED SECTION OF LINE H-109 IN THIS EVENT CROSSED-OVER A CREEK (SPAN) AND THE ENTIRE AREA WAS SUBJECT TO HEAVY RAIN DOWNPOURS AND FLOODED. CONSEQUENTLY, THE SPAN SEGMENT OF LINE H-109 WAS COMPLETELY SUBMERGED UNDER WATER. LINE H-109, IS CLASSIFIED AS TRANSMISSION , OPERATED AND MAINTAINED BY COLUMBIA. AT 17:30 EST, THE LEAK WAS ISOLATED AND THE PIPELINE WAS REMOVED FROM SERVICE. BY APRIL 6TH, 2018,THE AREA DEEMED SAFE WHERE THE FLOODED REGION WAS ACCESSIBLE AFTER THE WATER RECEDED. COLUMBIA OPERATIONS PERSONNEL COULD ACCESS AND SURVEY THE FAILURE SITE, IT WAS CONFIRMED THAT LINE H-109 HAD SEPARATED AT THE FAILURE LOCATION. THE INVOLVED SEGMENTS OF LINE H-109 WERE SENT TO A METALLURGICAL FAILURE ANALYSIS LABORATORY TO ESTABLISH THE ROOT CAUSE BEHIND THIS PIPELINE FAILURE. THE 48-HR UPDATE NRC WAS COMPLETED ON APRIL 5, 2018 WITH REPORT NO.1208575. THE METALLURGICAL FAILURE ANALYSIS REPORT OF LINE H-109 IDENTIFIED THAT THERE WAS NO EVIDENCE OF SIGNIFICANT CORROSION ON THE CRACK FACES AND THE MORPHOLOGY OF THE FRACTURE SURFACE IS CONSISTENT WITH LOW CYCLE FATIGUE, INDICATING THAT THE PIPE FAILED UNDER HIGH CYCLIC LOADING OVER A RELATIVELY SHORT PERIOD OF TIME. THE CONSTRUCTION OF THE REPLACEMENT SECTION FOR LINE H-109 WAS COMPLETED BY USING HORIZONTAL DIRECTIONAL DRILLING METHOD FOR INSTALLING PIPE UNDER THE CREEK TO PROTECT THE PIPE FROM SIMILAR WEATHER-RELATED EVENTS. LINE H-109 WAS RETURNED TO SERVICE ON NOVEMBER 7, 2018.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180048 | 31270 | 2018-05-01 10:13 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2018-03-30 21:45 | 2018 |  |  | 31.9525 | -101.4843 | 1208130 | 2018-03-31 00:57 |  | NATURAL GAS |  | 13200 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | COMPRESSOR UNIT WAS BYPASSED. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-03-30 23:07 | 2018-03-30 23:07 | ONSHORE | TX | 79721-2551 | GARDEN CITY | GLASSCOCK | SURVEY STATION NO. | 742+42 | GARDEN CITY COMPRESSOR STATION | UNIT 637 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2017 |  | CARBON STEEL |  | OTHER | [8 empty] | NATURAL GAS RELEASED FROM A VENT VALVE ON A COMPRESSOR STATION, WHEN A SUCTION VALVE FAILED TO FULLY CLOSE WHILE RESTARTING THE UNIT. | CLASS 1 LOCATION | NO |  | 805 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 36500 | 32875.8865248227 | 3500 | 3643.74433363554 | 200 | 208.213961922031 | 0 | 0 |  |  | 40200 | 35852.0748485219 | 36727.8448203803 | [8 empty] | 962 |  | 1051 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER NOR CONTROL ROOM WERE A CONTRIBUTING FACTORS. | [12 empty] | YES | 1 | 0 | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | OTHER | SUCTION VALVE FAILED TO FULLY CLOSE WHILE RESTARTING THE UNIT | [20 empty] | YES | THE HARD STOPS IN THE ACTUATOR WERE OUT OF ADJUSTMENT. | [161 empty] | AMIT SHAMGAR | SENIOR PIPELINE COMPLIANCE SPECIALIST | ashamgar@eprod.com | 713381-6741 |  |  |  |  | NHAN TRUONG | MANAGER COMPLIANCE | 713-381-2493 | nvtruong@eprod.com | AT 2124 ON 3/30/2018, CONTROLLER TRIED TO REMOTE START A COMPRESSOR UNIT WITH NO RESPONSE. CONTROLLER TRIED TO START THE UNIT A SECOND TIME WITH NO RESPONSE AND DISPATCHED A TECHNICIAN. WHEN THE TECHNICIAN ARRIVED AT 2307, THE TECHNICIAN DISCOVERED THAT THE SUCTION VALVE TO THE UNIT WAS NOT FULLY CLOSED AND THAT NATURAL GAS WAS RELEASING FROM THE VENT VALVE ON THE UNIT. THE TECHNICIAN CLOSED THE VALVE AND THE RELEASE STOPPED. AT 0030 ON 03/31/2018, IT WAS ESTIMATED THAT 52.7 MMCF OF GAS WAS RELEASED AND THE NRC/TRRC WAS NOTIFIED. THE RELEASE ESTIMATE WAS REVISED TO 13.2 MMCF AFTER THE VALVE WAS FOUND TO BE PARTIALLY OPEN. TIME OF THE INCIDENT (PART A, #4) IS ESTIMATED BASED ON TOTAL RELEASE VOLUME. INSPECTION OF THE VALVE IDENTIFIED THE HARD STOPS WERE OUT OF ADJUSTMENT CAUSING THE VALVE TO NOT FULLY CLOSE. THE VALVE WAS REPAIRED AND TESTED PRIOR TO BEING RETURNED TO SERVICE. THE TRRC WAS NOTIFIED ON 3/31/2018 AT 0057 AND A 48 HOUR COURTESY UPDATE ON 04/01/2018 AT 1913. 48-HOUR NRC# 1208229 SUPPLEMENTAL NOTIFICATION WAS MADE 04/01/2018 AT 1905. 12/04/2018 UPDATE - ADDED MORE SIGNIFICANT FIGURES TO LAT/LONG TO PROVIDE MORE ACCURATE LOCATION OF INCIDENT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180049 | 30998 | 2018-05-02 11:49 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2018-04-05 10:05 | 2018 |  |  | 29.5763 | -95.8685 | 1208559 | 2018-04-05 13:13 |  | NATURAL GAS |  | 0 | 398 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | FACILITY NOT YET COMMISSIONED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-04-05 10:05 | 2018-04-05 10:05 | ONSHORE | TX | 77471 | ROSENBERG | FORT BEND | MILEPOST | 126 | BRAZOS COMPRESSOR STATION | INDEX 129 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | BLOWDOWN STACKS | 2018 |  | CARBON STEEL |  | OTHER | [8 empty] | DURING ESD TEST, BLOW DOWN STACKS FAILED. | CLASS 1 LOCATION | NO |  | 193 |  | NO | NO | NO |  | 0 | 0 | 1091 | 1135.80716228468 | 0 | 0 | 563250 | 586382.570262919 | 0 | 0 | 0 | 0 |  |  | 564341 | 269686.437987308 | 587518.377425204 | [8 empty] | 757 |  | 780 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | THRUST FORCES ON THE BLOW DOWN STACKS DURING A BLOW-DOWN EVENT WERE NOT ADEQUATELY CONSIDERED DURING DESIGN OF THE BLOW DOWN STACKS. | [147 empty] | SHANNON MATTINGLY | PA OQ AND EVENT SUPPORT PROGRAM LEADER | shannon.mattingly@bwpmlp.com | 2706886357 | 2706886948 |  |  |  | DARRAL WARD | MANAGER PIPELINE SAFETY | 2706886356 | darral.ward@bwpmlp.com | PRIOR TO COMMISSIONING A NEW FACILITY, GULF SOUTH PIPELINE EMPLOYEES WERE CONDUCTING AN ESD TEST TO DETERMINE STATION BLOW DOWN TIME. DURING THE BLOW DOWN, THE STACK SUPPORTS FAILED CAUSING THE BLOW DOWN STACKS TO FAIL. THRUST FORCES ON THE BLOW DOWN STACKS DURING A BLOW-DOWN EVENT WERE NOT ADEQUATELY CONSIDERED DURING DESIGN OF THE BLOW DOWN STACKS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180050 | 31241 | 2018-05-04 15:40 | SUPPLEMENTAL FINAL | 6660 | GREAT LAKES GAS TRANSMISSION CO | 700 LOUISIANA STREET | HOUSTON | TX | 77002 | 2018-02-12 14:30 | 2018 |  |  | 48.9909 | -97.0596 | 1208953 | 2018-04-10 12:25 |  | NATURAL GAS |  | 1 | 909 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-02-12 14:30 | 2018-09-28 16:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-02-12 14:30 | 2018-02-12 14:30 | ONSHORE | MN | 56775 | Not Within a Municipality | KITTSON | MILEPOST | MP 0.7 | ST. VINCENT COMPRESSOR STATION | VALVE SECTION 1-0 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 40 |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 24 |  | 0.5 | 60000 | API 5L | SEAMLESS |  | LADISH COMPANY | EPOXY | [28 empty] | 1998 | 1997 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 835 |  | NO | NO | NO |  | 0 | 0 | 2174 | 2263.28576609247 | 120 | 108.085106382979 | 740000 | 770391.659111514 | 0 | 0 | 0 | 0 |  |  | 742294 | 354781.064353183 | 772763.029983989 | [8 empty] | 860 |  | 974 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PINHOLE LEAK COULD NOT HAVE BEEN DETECTED BY THE CONTROL ROOM. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROST HEAVE |  | NO | [306 empty] | CHRIS MASON | COMPLIANCE SPECIALIST | chris_mason@transcanada.com | 8323205980 |  |  |  |  | HOWARD LEE ROMACK | DIRECTOR US REGULATORY COMPLIANCE | 8323205315 | lee_romack@transcanada.com | THE INCIDENT INVOLVED A MINOR LEAK ORIGINALLY DISCOVERED ON 2/12/18 (THEN ISOLATED AND BLOWN DOWN THE SAME DAY) AT THE GLGT ST. VINCENT COMPRESSOR STATION IN MINNESOTA. THE LEAK LOCATION WAS EXCAVATED ON 4/10/18 AND VISUALLY DETERMINED TO BE ORIGINATING FROM A BURIED 24 INCH ELL FITTING. AN UNDERGROUND 24" ELL DEVELOPED A PIN HOLE LEAK. THE 24" ELL CONNECTED TO A 1" WELD-O-LET, THEN TO 1" PIPING LEADING TO AN ABOVE GROUND PRESSURE TRANSMITTER, USED FOR FLOW MEASUREMENT PURPOSES. THE 24" ELL WAS CUT OUT AN REPLACED. THE CUT OUT SECTION WAS SENT TO METALLURGICAL ANALYSIS COMPANY FOR IMMEDIATE CAUSE DETERMINATION. THE METALLURGICAL ANALYSIS SUMMARY CONCLUDED THERE WERE TWO LEAK LOCATIONS PRESENT IN THE ELBOW SECTION; ONE IN THE ELBOW AND ONE IN THE ATTACHED PIPING. THE LEAK IN THE PIPING WAS LOCATED AT A THROUGH-WALL CRACK AT THE TOE OF THE WELD BETWEEN THE PIPING AND WELD-O-LET. THE CRACK WAS MOST LIKELY CAUSED BY OVERLOAD, ALTHOUGH THIS CAUSE COULD NOT BE DEFINITIVELY DETERMINED BECAUSE OF EROSION DAMAGE TO THE FRACTURE SURFACES. THE CAUSE OF THE LEAK IN THE ELBOW WAS EROSION FROM THE GAS ESCAPING FROM THE CRACK IN THE PIPING. TRANSCANADA SME EVALUATION CONCLUDED, THE LIKELY SOURCE OF THE OVERLOAD REFERENCED IN THE METALLURGICAL REPORT WAS THE 1" RISER BEING PULLED UPWARD BY THE SOIL AROUND IT NEAR THE GROUND SURFACE IN A PROCESS CALLED "FROST JACKING" DURING THE COLD MONTHS. THE REPEATED CYCLES OF FREEZING AND THAWING MAY HAVE INDUCED STRESSES ON THE ELBOW-PIPE JOINT, THEREBY, CAUSING THE CRACK. REGARDING THE EXISTENCE OF SIMILAR DESIGNS IN THE SYSTEM, IT HAS BEEN CONFIRMED ST. VINCENT WAS THE ONLY STATION THAT HAD THE ELBOW FLOW METER OUTSIDE A UNIT BUILDING. THE OTHER GLGT STATIONS HAVE THE ELBOW FLOW METERS INSIDE THE BUILDINGS AND NOT SUBJECTED TO SIMILAR CONDITIONS. TRANSCANADA WILL CONTINUE TO EVALUATE PIPING ARRANGEMENTS WHERE FROST-SUSCEPTIBLE SOIL CONDITIONS MAY EXIST WITHIN THE GLGT SYSTEM UNDER THE THREAT MANAGEMENT PROGRAM.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180051 | 31564 | 2018-05-11 09:19 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2018-04-12 13:00 | 2018 |  |  | 34.5957 | -82.4071 | 1209263 | 2018-04-13 14:02 |  | NATURAL GAS |  | 6610 | 32488 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-04-12 14:00 | 2018-07-12 14:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-04-12 13:00 | 2018-04-12 13:00 | ONSHORE | SC | 29669 | PELZER | GREENVILLE | MILEPOST | 1177.29 | MAINLINE D | ML-D MLV 135D10 TO 135D20 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 50 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION | [19 empty] | OTHER BUTT WELD | [18 empty] | 1967 |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 2 LOCATION | NO |  | 809 |  | NO | NO | NO |  | 0 | 0 | 87300 | 90885.3943789665 | 17755 | 15992.0921985816 | 615000 | 640257.932910245 | 20000 | 20821.3961922031 | 0 | 0 | VALVE WAS ALREADY SCHEDULED TO BE REPLACED UNDER A CURRENT ONGOING PROJECT. |  | 740055 | 361751.378177719 | 767956.815679996 | [8 empty] | 661 |  | 780 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | REMOTELY CONTROLLED | 78448 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | YES | [7 empty] | YES | CAUSE IS LIKELY HYDROGEN-INDUCED TOE CRACKING OR COLD CRACKING | [12 empty] | YES | [63 empty] | YES | YES |  |  | YES |  |  |  | 2014 | [31 empty] | 2014 | [23 empty] | NO |  |  | Yes, but the point of the Accident was not identified as a dig site |  | 2016 | [11 empty] | NO | [63 empty] | TIM HUGGINS | ENGINEER PRINCIPAL | timothy.n.huggins@williams.com | 7132152889 | 7132152790 |  |  |  | CLINT RATKE | MANAGER PIPELINE SAFETY | 9185736724 | clint.ratke@williams.com | PLEASE REFERENCE THE ORIGINAL REPORT NO. 20180051-30306 DATED AND FILED ON 05/11/2018 FOR THE INITIAL INCIDENT REPORT INFORMATION AND DETAILED TIME LINE OF EVENTS FOR THIS INCIDENT. A BRIEF SUMMARY IS DESCRIBED BELOW. ON 04/12/2018 AT APPROXIMATELY 1:00 PM (13:00), A LEAK WAS DISCOVERED NEAR MLV 135D10 AND EVENTUALLY DETERMINED TO BE ON THE ON THE DOWNSTREAM SIDE OF THE VALVE. OPERATIONS PERSONNEL MOBILIZED TO THE SITE AND BEGAN TO ISOLATE THE VALVE SEGMENTS AT 2:00 PM (14:00), AND THEN THE BLOW DOWN FROM MLV 135D10 TO MLV 135D20 WAS COMPLETED ON 04/13/2018 AT 12:00 PM (12:00). PIPELINE SAFETY REVIEWED THE EVENT AND DETERMINED THE NRC SHOULD BE CONTACTED SINCE THE REPAIR COST WILL EXCEED $50,000. THE NRC WAS INITIALLY CONTACTED AT 2:02 PM (14:02), UNDER NRC# 1209263. ON 04/20/2018 AT 12:37 PM (12:37), THE NRC WAS CONTACTED TO UPDATE THE INCIDENT, UNDER NRC# 1209842. PHMSA REQUESTED CORRECTIONS TO THE ORIGINAL REPORT AND PREVIOUS ILI DATA FOR REVIEW ON 05/18/2018, AND ON 05/21/2018 PHMSA REQUESTED THAT ALL COSTS ASSOCIATED WITH THE VALVE REPLACEMENT MUST BE REPORTED. THIS FINAL INCIDENT REPORT UPDATES THE COMPLETED VALVE REPLACEMENT WORK, INCLUDES THE ASSOCIATED COSTS, REQUESTED CORRECTIONS, INCLUDES THE PREVIOUS 2014 ILI DATA SUMMARY AS DESCRIBE BELOW, AND INCLUDES A SUMMARY OF THE FINDINGS FROM THE METALLURGY LABORATORY ANALYSIS OF THE CRACKED WELD JOINT BETWEEN THE PREVIOUS 36-INCH MAINLINE BLOCK VALVE (MLV 135D10) AND THE REDUCER (42 IN. X 36 IN.). THE EXISTING 36-INCH MAINLINE BLOCK VALVE AND REDUCER WERE ALREADY SCHEDULED FOR REPLACEMENT WITH A NEW 42-INCH VALVE AND PIPE WHEN THE GAS LEAK INCIDENT OCCURRED. THE EXISTING 42-INCH PIPELINE SEGMENT WAS KEPT OUT OF SERVICE UNTIL THE NEW VALVE AND PIPE COULD BE SCHEDULED FOR REPLACEMENT AS PLANNED. THE VALVE REPLACEMENT WORK BEGAN ON 06/05/2018. THE NEW 42-INCH VALVE AND PIPE WERE INSTALLED AND THE EXISTING 42-INCH PIPELINE SEGMENT WAS PLACED BACK INTO SERVICE ON 07/12/2018 AT APPROXIMATELY 2:30 PM EST (14:30). THE EXISTING 36-INCH VALVE AND REDUCER WERE CUT-OUT AND THEN SENT TO HERRERA, STAFFORD & ASSOCIATES (HSA) FOR ANALYSIS ON OR ABOUT 07/24/2018. WILLIAMS PROVIDED PHMSA AN EMAIL UPDATE STATUS ON 07/27/2018. ON 11/08/2018, HAS ISSUED THE FINAL METALLURGICAL EVALUATION FOR THE CRACKED GIRTH WELD SECTION BETWEEN THE EXISTING MLV 135D10 VALVE AND REDUCER. THE METALLURGICAL EXAMINATION DETERMINED THE CRACK-LIKE INDICATION WAS A TOE CRACK OBSERVED ON THE REDUCER SIDE OF THE GIRTH WELD. ELEVATED HARDNESSES, MARTENSITE, AND SECONDARY INTERGRANULAR CRACKS INDICATE THE CRACK WAS LIKELY THE RESULT OF HYDROGEN ASSISTED CRACKING IN THE HEAT AFFECTED ZONE OF THE WELD (ALSO KNOWN AS HYDROGEN-INDUCED TOE CRACKING OR COLD CRACKING). THE CRACK MEASURED 16-INCHES ON THE OD SURFACES AND WAS THROUGH WALL FOR 6.75 INCHES. THE RECENT ILI (MFL) TOOL RUN WAS PERFORMED ON 10/30/2014 FROM OUR COMPRESSOR STATION 130 TO COMPRESSOR STATION 140, AND INCLUDED THE MLV 135D10 VALVE SITE LOCATION. THE PREVIOUS ILI DATA WAS REVIEWED 500-FEET UPSTREAM AND DOWNSTREAM FOR THIS LOCATION, AND INDICATED 10% TO 20% WALL LOSS WITH A PBURST THAT VARIED FROM 1.99 TO 2.40. THESE FEATURES WOULD NOT HAVE BEEN CLASSIFIED AS ANOMALIES FOR INVESTIGATION. THE INITIAL ILI (MFL) BASELINE ASSESSMENT WAS PERFORMED ON 12/17/2007. ALL THE INFORMATION WAS GATHERED AND VERIFIED WITH CORRECTIONS, AND A FINAL INCIDENT REPORT WAS SUBMITTED ON 12/14/2018. PHMSA RETURNED COMMENTS AND CORRECTIONS TO THE FINAL REPORT ON 01/04/2019. A REVISED FINAL INCIDENT REPORT WAS SUBMITTED ON 01/29/2019 WITH THE CORRECTIONS MADE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180052 | 30316 | 2018-05-14 12:09 | ORIGINAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2018-04-18 11:42 | 2018 |  |  | 38.821 | -79.8357 | 1209636 | 2018-04-18 12:42 |  | NATURAL GAS |  | 4000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THIS WAS A PARTIAL ESD. GAS REMAINED IN SERVICE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-04-18 11:42 | 2018-04-18 11:42 | ONSHORE | WV | 26253 | BEVERLY | RANDOLPH COUNTY | MILEPOST | COMP. STATION | FILES CREEK COMPRESSOR STATION | FILES CREEK COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | COMPRESSOR STATION EMERGENCY SHUTDOWN WAS PARTIALLY ACTIVATED. | CLASS 3 LOCATION | NO |  | 831 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 10500 | 9457.44680851064 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 10500 | 9804.96453900709 | 9457.44680851064 | [8 empty] | 750 |  | 1000 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | OPERATOR WAS PRESENT AT THE TIME OF THE RELEASE. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL ROOM WAS NOT A SUSPECTED CAUSE AND LATER WAS DETERMINE NOT PART OF THE CAUSE OF THE RELEASE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | THE ELECTRICAL SYSTEM CONTROLLING THE FOUR ESD FIRE VALVES INVOLVED IN THE EVENT WAS EVALUATED AND DETERMINED TO BE OVERLOADED, THUS CAUSING THE FUSE TO FAIL. TO RESOLVE THE ISSUE, THE CURRENT LOAD WAS SPLIT ONTO AN ADDED CIRCUIT, THUS REDUCING THE CURRENT LOAD ON THE ESD SYSTEM. | [5 empty] | YES | [172 empty] | CHRIS LEGG | US REGULATORY COMPLIANCE SPECIALIST | chris_legg@transcanada.com | 304-545-4350 |  |  |  |  | LEE ROMACK | MANAGER - US REGULATORY COMPLIANCE | 832-320-5315 | lee_romack@transcanada.com | ON APRIL 18, 2018, AN UNINTENDED RELEASE OF NATURAL GAS (MATERIAL) EVENT INTO ATMOSPHERE WAS REPORTED TO THE NATIONAL RESPONSE CENTER (NRC). THIS EVENT TOOK PLACE AT FILES CREEK COMPRESSOR STATION (CS) IN RANDOLPH COUNTY, WEST VIRGINIA. THIS CS IS OPERATED AND MAINTAINED BY COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA). AT 11:42 AM EST, A 15-AMP ELECTRICAL FUSE FAILED CAUSING (4) FIRE VALVES TO OPEN ON THE EMERGENCY SHUTDOWN (ESD) SYSTEM. THE FIRE VALVES (3-8" & 1-4") BLEW FOR 3 1/2 MINUTES RELEASING 4000 MCF OF GAS TO THE ATMOSPHERE THROUGH THE ASSOCIATED BLOW-OFF PIPING BEFORE BEING ISOLATED AND SHUT IN BY ON-SITE EMPLOYEES. THE PRELIMINARY MATERIAL LOSS CALCULATIONS WAS DETERMINED TO BE GREATER THAN 3,000 MCF, HENCE, THE EVENT WAS REPORTED TO NRC AS AN INCIDENT. A 48-HR UPDATE NOTICE WAS CALLED-IN TO THE NRC WHERE THE UPDATE REPORT NO. WAS 1209832. THE ELECTRICAL SYSTEM CONTROLLING THESE VALVES WAS EVALUATED AND DETERMINED TO BE OVERLOADED, THUS CAUSING THE FUSE TO FAIL. TO RESOLVE THE ISSUE, THE CURRENT LOAD WAS SPLIT INTO TWO CIRCUITS, THUS REDUCING THE CURRENT LOAD
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180053 | 30685 | 2018-05-15 08:49 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2018-04-06 16:00 | 2018 |  |  | 41.2596 | -77.2292 | 1209456 | 2018-04-16 12:11 |  | NATURAL GAS |  | 1000 | 2467 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-04-06 17:30 | 2018-06-22 19:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-04-06 16:00 | 2018-04-06 16:00 | ONSHORE | PA | 17740 | JERSEY SHORE | LYCOMING | MILEPOST | 157.63 | STATION 520 | COMPRESSOR STATION VALVE YARD 520S2 VALVE | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | MAINLINE | BALL |  | GROVE |  |  |  | 1965 | 1965 | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 2 LOCATION | NO |  | 574 |  | NO | NO | NO |  | 0 | 0 | 6500 | 6766.953762466 | 2700 | 2431.91489361702 | 400000 | 416427.923844062 | 5000 | 5205.34904805077 | 0 | 0 |  |  | 414200 | 199168.28475531 | 430832.141548195 | [8 empty] | 940 |  | 1200 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) | [11 empty] | YES | INVESTIGATION SHOWED A POSSIBLE LEAK IN THE AREA OF AN UNDERGROUND VALVE IN STATION VALVE YARD AREA (520S2) | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | OTHER | BODY BLEED LEAK AND BODY FLANGE LEAK. | [18 empty] | YES | AGE OF THE VALVE | [161 empty] | TIM HUGGINS | PRINCIPAL ENGINEER | timothy.n.huggins@williams.com | 713-215-2889 | 713-215-2790 |  |  |  | CLINT RATKE | MANAGER PIPELINE SAFETY | 918-573-6724 | clint.ratke@williams.com | FOUND GAS LEAKING FROM STATION YARD BY PICKING UP ON GAS MONITORS. PROBED HOLES AROUND THE AREA TO PINPOINT THE LEAK. FOUND STRONGER LEVELS OF GAS AND HAND DUG TO EXPOSE SOME PIPING AND VALVE WHERE THEN AN ICE BALL WAS FOUND WHERE THE LEAK WAS COMING FROM. PERFORMED ISOLATION AND BLOWDOWN OF THE STATION TO MAKE IT SAFE AND SCHEDULED CONTRACTOR TO COME IN TO BEGIN HYDROVAC AREA TO FIND THE LEAK. PERFORMED BLOWDOWN OF LEIDY A LINE FROM MLV 520LA1 TO 520LA10 TO REMOVE PRESSURE IN THE LINE TO INVESTIGATE LEAK AROUND 520S2 VALVE AND 24-INCH STATION HEADER PIPING. TIME LINE BELOW; 4/6/2018 16:30 IDENTIFIED A SMALL GAS LEAK NEAR VALVE 520S2. HAND-EXCAVATED GROUND AND IDENTIFIED ICE NEAR THE VALVE SITE AND LEAK INDICATIONS TOWARD LEIDY LINE A. OPERATIONS DECIDED TO BLOW-DOWN THE STATION YARD PIPING. BEGAN TO ASSEMBLE PERSONNEL AND EQUIPMENT. 18:00 TO 20:00 BLOWDOWN STATION YARD PIPING. STARTED LEAK INVESTIGATION. 4/11/2018 10:00 COMPLETED BLOWDOWN OF 2.5 MILES OF 24" LEIDY LINE. GAS VOLUME WAS DRAWN BY METER STATIONS AND BLOWDOWN AT LOWER PRESSURE. CONTINUE LEAK INVESTIGATION. 4/12/2018 15:00 DECIDED TO REPLACE THE VALVE AND LOCATED SURPLUS VALVE. THE EXISTING 24" BOLTED BODY VALVE WAS LEAKING AT THE BODY FLANGE AND THREADED DRAIN PLUG AT BOTTOM OF THE VALVE. THE EXISTING VALVE WAS INSTALLED IN 1965. OPERATIONS BEGAN TO ASSEMBLE PERSONNEL, MATERIAL, AND EQUIPMENT FOR THE VALVE REPLACEMENT. 4/16/2018 12:11 PIPELINE SAFETY WAS CONTACTED AND WILLIAMS - SECURITY OPERATIONS CENTER (SOC) CONTACTED THE NRC. ORIGINAL INCIDENT REPORT# 1209456. 4/18/2018 NEW 24" VALVE ASSEMBLY WAS TESTED AND PLAN TO INSTALL ON 4/20/2018 4/19/2018 14:01 PIPELINE SAFETY CONTACTED NRC FOR THE FOLLOW-UP. WILLIAMS IS WORKING ON THE VALVE REPLACEMENT. NEW INCIDENT REPORT# 1209745. 4/20/2018 VALVE REPLACED WITH NEW 24" BALL VALVE. EXISTING VALVE HAD BODY BLEED LEAK AND BODY FLANGE LEAK AT CONNECTIONS. CONTINUE TO INVESTIGATE PIPING AND HEADERS FOR CORROSION AND COATINGS WHILE COMPRESSOR STATION IS SHUT DOWN. 5/21/2018 13:30 LEIDY LINE A WAS RETURNED TO SERVICE FROM MLV 520LA0 - 520LA10. STATION 520 IS STILL OUT OF SERVICE, CONTINUE TO INVESTIGATE PIPING AND HEADERS FOR CORROSION AND COATINGS WHILE COMPRESSOR STATION IS SHUT DOWN. 6/22/2018 COMPLETED INVESTIGATION. 19:00 STATION 520 RETURNED TO SERVICE.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20180054 | 30510 | 2018-05-15 17:04 | SUPPLEMENTAL FINAL | 39352 | GENESIS OFFSHORE HOLDINGS, LLC | 919 MILAM STREET SUITE 2100 | HOUSTON | TX | 77002 | 2018-04-17 20:45 | 2018 |  |  | 28.4589 | -96.3866 | 1209604 | 2018-04-17 22:45 |  | NATURAL GAS |  | 12680 | 0 | 3458 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE PIPELINE WAS SHUT IN AND NOT FLOWING AT THE TIME OF THE INCIDENT. | [6 empty] | YES |  |  |  |  | NO | [6 empty] | 12 | 2018-04-17 22:14 | 2018-04-18 03:00 | OFFSHORE | [28 empty] | 12 | IN STATE WATERS | TX | MATAGORDA BAY | STATE TRACT 135 | CALHOUN |  |  |  | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 20 |  | 0.438 | 52000 | API 5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | OTHER | CONCRETE COATING | [27 empty] | 1988 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 4 | 10.5 | [7 empty] | CLASS 1 LOCATION | NO |  | 530 |  | NO | NO | NO |  | 5000000 | 5205349.04805077 | 0 | 0 | 34743 | 31293.3404255319 | 443478 | 461691.557026292 | 123370 | 128436.782411605 | 233415 | 243001.309610154 | COST OF CONDENSATE RELEASED. |  | 5835006 | 2804264.28524591 | 6069772.03752435 | [8 empty] | 450 |  | 1440 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | AUTOMATIC | 146741 | NO |  |  | YES | YES |  |  |  | YES |  | YES | YES |  |  |  | OFFSHORE GATHERING | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS CAUSED BY 3RD PARTY DAMAGE TO THE PIPELINE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES | YES | OTHER | [9 empty] | CONTRACTOR | VACUUM EQUIPMENT | WATERWAY IMPROVEMENTS | NO | [7 empty] | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | JORGE MORICE | PIPELINE COMPLIANCE SPECIALIST | jorge.morice@genlp.com | 225-263-0575 |  |  |  |  | JOHN JEWETT | DOT COMPLIANCE MANAGER | 713-860-2506 | john.jewett@genlp.com | A DREDGING SPUD BARGE OPERATED BY RLB CONTRACTING, INC. WAS PERFORMING UNDERWATER OPERATIONS IN THE MATAGORDA BAY, TX AREA NEAR PORT O'CONNOR ON THE NIGHT OF 4/17/2018. RECORDS SHOW THAT AT THIS POINT, GENESIS WAS NOT NOTIFIED OF THE OPERATION AND A ONECALL NOTIFICATION WAS NOT MADE BY THE CONTRACTOR PRIOR TO OPERATIONS. AT APPROXIMATELY 20:45, THE BARGE DROPPED A SPUD ON THE GENESIS OFFSHORE HOLDINGS, LLC PIPELINE NAMED TOMCAT, A 20" NATURAL GAS GATHERING PIPELINE. THE SPUD CAUSED A 2.5" BY 4" PUNCTURE HOLE ON THE PIPELINE RELEASING THE PRODUCT. THE NATURAL GAS AND CONDENSATE RELEASED IGNITED ABOVE THE WATER SURFACE. THE BARGE PERSONNEL QUICKLY CALLED 811 TO REPORT A HIT PIPELINE AT 20:58. A GENESIS OPERATOR RECEIVED THE 811 NOTICE AND CALLED THE GENESIS OFFSHORE SUPERINTENDENT TO REPORT THE INCIDENT. TGLO, TRRC, NRC, AND PHMSA WERE NOTIFIED. A GENESIS OPERATOR WAS DISPATCHED TO THE DOWNSTREAM VALVE AT MILSP PLANT TO BEGIN THE CONTROLLED BLOWDOWN OF THE PRODUCT HOWEVER BY THE TIME HE ARRIVED AT THE PLANT, THE PRESSURE WAS ALREADY AT APPROXIMATELY 150PSI AND DROPPING. RLB INITIALLY CONTRACTED HORIZON (OSRO) TO BEGIN EMERGENCY RESPONSE EFFORTS. GENESIS ALSO EXECUTED THE RESPONSE PLAN AND ACTIVATED APPROPRIATE RESPONSE CONTRACTORS. USCG ARRIVED AT THE SCENE AND ASSUMED INCIDENT COMMAND OF THE RESPONSE OPERATIONS. THE BARGE CREW WAS SAFELY EVACUATED FROM THE BARGE AND BOOM WAS DEPLOYED TO CONTAIN LIQUIDS. GAS FIRE EXTINGUISHED AT APPROXIMATELY 15:00 ON 4/18/2018. THE TEMPORARY REPAIR ON THE PIPELINE WAS COMPLETED AND THE WORK SPREAD DEPARTED EARLY APRIL 27TH. NOTE: PART D, QUESTION 7D IS THE SUM OF THE TOTAL PRODUCT LOST (NOT RECOVERED) AS REPORTED IN PART A QUESTIONS 12. THIS IS EQUAL TO 3,458 BARRELS OF CONDENSATE PRICED AT $67.50 PER BARREL ($233,415). NOTE: PART E, QUESTION 6: SCADA WAS FULLY FUNCTIONAL AT THE TIME OF THE INCIDENT HOWEVER THE CONTROL ROOM WAS UNABLE TO SEE A PRESSURE DROP BECAUSE THEY WERE SEEING THE PRESSURE DOWNSTREAM OF THE BLOCK VALVE AT THE MILSP PLANT. THE PIPELINE WAS SHUT IN AND NOT FLOWING AT THE TIME OF THE INCIDENT, AS REPORTED IN PART A, QUESTION 15. SUPPLEMENTAL REPORT (6/18/2018) - UPDATE TO PART D. RECEIVED ESTIMATE FROM RLB CONTRACTING FOR ESTIMATED NON-OPERATOR DAMAGES INCURRED (QUESTION 7A). IN ADDITION, UPDATED QUESTIONS 7B AND 7C TO REFLECT MORE ACCURATE ESTIMATES.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180055 | 30361 | 2018-05-21 15:53 | ORIGINAL FINAL | 19610 | TRANSWESTERN PIPELINE COMPANY LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2018-04-24 13:47 | 2018 |  |  | 32.0994 | -103.5116 | 1210226 | 2018-04-24 16:29 |  | NATURAL GAS |  | 13090 | 22939 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-04-24 17:35 | 2018-04-26 01:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-04-24 13:47 | 2018-04-24 15:35 | ONSHORE | NM | 88252 | JAL | LEA | SURVEY STATION NO. | 554+78 | 30" W. TEXAS LATERAL LOOP | NMBW221 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 46 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 |  | 0.375 | 60000 | API-5LX | DSAW |  | U. S. STEEL | COLD APPLIED TAPE | [28 empty] | 1969 | 1968 | CARBON STEEL |  | MECHANICAL PUNCTURE | 0.5 | 0.1 | [7 empty] | CLASS 1 LOCATION | NO |  | 663 |  | NO | NO | NO |  | 0 | 0 | 48400 | 50387.7787851315 | 27620 | 24877.5886524823 | 300028 | 312350.092837715 | 0 | 0 | 0 | 0 |  |  | 376048 | 192297.980346744 | 387615.460275329 | [8 empty] | 785 |  | 1051 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 96822 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LINE WAS STRUCK BY A THIRD PARTY CONTRACTOR. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES | YES | OTHER |  |  | YES | [6 empty] | CONTRACTOR | TRENCHER | NATURAL GAS | NO | [5 empty] | YES | 32 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | ON 4/24/18, A CALL WAS RECEIVED FROM A THIRD PARTY CONTRACTOR THAT HAD STRUCK AND DAMAGED THE TRANSWESTERN 30" WEST TEXAS LATERAL LOOP PIPELINE. THE LINE SEGMENT WAS ISOLATED AND BLOWN DOWN. ON 4/25, THE CONTRACTOR WAS MOBILIZED FOR REPAIRS. ON 4/26, THE PERMANENT PIPE REPLACEMENT REPAIRS WERE COMPLETED AND THE PIPELINE WAS RETURNED TO SERVICE. THE INITIAL NRC TELEPHONIC NOTIFICATION WAS MADE ON 4/24 - NRC#1210226, AND THE PHMSA AID WAS NOTIFIED. THE 48 HOUR NRC NOTIFICATION WAS MADE ON 4/26 - NRC #1210409, AND THE PHMSA AID WAS NOTIFIED THAT THE LINE WAS RETURNED TO SERVICE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180057 | 30997 | 2018-06-04 16:05 | SUPPLEMENTAL FINAL | 288 | ALGONQUIN GAS TRANSMISSION, L.L.C. (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2018-05-05 01:30 | 2018 |  |  | 41.6321 | -72.6727 | 1212079 | 2018-05-14 11:56 |  | NATURAL GAS |  | 5805 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELIEF VALVE RELEASED GAS BELOW SET POINT. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-05-05 01:30 | 2018-05-05 01:30 | ONSHORE | CT | 06416 | CROMWELL | MIDDLESEX | MILEPOST | CROMWELL CS | CROMWELL COMPRESSOR STATION | CROMWELL COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1985 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE RELEASE BELOW SETPOINT | CLASS 2 LOCATION | NO |  | 569 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 17415 | 15685.8510638298 | 1000 | 1041.06980961015 | 0 | 0 | 0 | 0 |  |  | 18415 | 16740.1125556992 | 16726.9208734399 | [8 empty] | 711 |  | 750 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL ROOM COULD NOT HAVE CONTRIBUTED TO THE EVENT OCCURRING AND FIELD PERSONNEL WERE ON SITE WHEN THE EVENT OCCURRED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | CONTROL PILOT DRIFTED OFF SET POINT | [161 empty] | DWAYNE TESCHENDORF | ENGINEER SPECIALIST | dwayne.teschendorf@enbridge.com | 713-627-5573 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | A RELIEF VALVE AT THE CROMWELL COMPRESSOR STATION ON THE ALGONQUIN GAS TRANSMISSION PIPELINE SYSTEM RELEASED NATURAL GAS TO ATMOSPHERE AT 1:30 AM ON MAY 5, 2018 WHILE PIPELINE SYSTEM WAS OPERATING BELOW THE RELIEF VALVE'S SET POINT. THE AMOUNT OF NATURAL GAS RELEASED EXCEEDED 5 MILLION CUBIC FEET BEFORE THE RELIEF VALVE WAS ISOLATED. THE APPARENT CAUSE OF THE INADVERTENT OPERATION OF THE RELIEF VALVE WAS ITS CONTROL PILOT DRIFTING OFF SET POINT.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180058 | 30537 | 2018-06-06 08:01 | SUPPLEMENTAL FINAL | 31565 | GULFSTREAM MANAGEMENT & OPERATING SERVICES,LLC | 1905 INTERMODAL CIRCLE, SUITE 310 | PALMETTO | FL | 34221 | 2018-05-26 21:35 | 2018 |  |  | 27.7492 | -81.8502 | 1213420 | 2018-05-27 19:07 |  | NATURAL GAS |  | 9229 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | CUSTOMER ON OUTAGE. REGULATORS CANNOT BE TUNED UNTIL CUSTOMER RESUMES FLOW | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-05-27 01:34 | 2018-05-27 02:27 | ONSHORE | FL | 33841 | FORT MEADE | POLK | MILEPOST | STATION 6+65 | STATION 415 | TIGER BAY M&R | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2001 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE ACTUATION | CLASS 1 LOCATION | NO |  | 338 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 26000 | 23418.4397163121 | 0 | 0 | 0 | 0 | 200 | 208.213961922031 | PARTS REPAIR FAILED REGULATOR BOOT |  | 26200 | 24374.5355135039 | 23626.6536782341 | [8 empty] | 490 |  | 1480 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | CUSTOMER NOTIFICATION |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS DUE TO RELIEF VALVE NOT RESEATING. CONTROLLERS RECEIVED HIGH PRESSURE ALARM THAT CLEARED WHEN RELIEVE VALVE ACTUATED. ONCE THE PRESSURE DROPPED THE RELIEF VALVE DID NOT RESEAT AND CONTINUED TO VENT GAS. THE FLOW RATE INDICATED IN SCADA WAS COMPARABLE TO CUSTOMERS NOMINATION FOR THE DAY SO THERE WERE NO FURTHER INDICATIONS. THE HIGH-PRESSURE ALARM WAS DUE TO THE TRIM RUN REGULATORS NOT LOCKING UP WHEN CUSTOMER SHUTDOWN FOR THE DAY. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES |  |  | YES | [25 empty] | YES | BOOTS FAILED DUE TO HIGH INSTANTANEOUS FLOW RATE CAUSED BY RELIEF VENTING | [161 empty] | EDGAR RODRIGUEZ | REGULATORY COMPLIANCE SPECIALST SR. | edgar.x.rodriguez@williams.com | 8326613182 |  |  |  |  | CLINT RATKE | MANAGER PIPELINE SAFETY | 918-573-6724 | clint.ratke@williams.com | 5/26/18 21:19 - TIGER BAY FLOW WENT TO 0 21:31 - TIGER BAY HIGH DISCHARGE PRESSURE ALARM WHICH APPEARED TO BE DUE TO METER SHUTTING IN AS IT DOES EACH NIGHT. 21:35 - THE RELIEF LIFTED DUE TO SLOW LOCKUP ON THE REGULATORS. TIGER BAY ALARM CLEARED AND NO ADDITIONAL ALARMS WERE RECEIVED, EVERYTHING APPEARED NORMAL. SCADA BEGAN TO SEE A FLOW RATE OF 43000M RATE WHICH APPEARED TO CONTINUE NOM OF 38,999M. THE FAILURE OF THE RELIEF TO RESEAT CAUSED THE REGULATOR/CONTROL VALVES TO OPEN IN ORDER TO MAINTAIN THE PRESSURE. 5/27/18 01:34 - MACCUNNINHAM WITH DUKE ENERGY TIGER BAY CONTROL ROOM CALLED WILLIAMS CONTROL CENTER NOTIFYING OF RELIEF VALVE RELEASING GAS INTO THE ATMOSPHERE 01:39 - WILLIAMS TECH WAS NOTIFIED OF THE INCIDENT AND WAS ON ROUTE TO METER STATION TO INVESTIGATE AND GATHER ADDITIONAL INFORMATION 02:27 - WILLIAMS TECH ARRIVED AT THE LOCATION AND CONFIRMED GAS VENTING TO ATMOSPHERE THROUGH RELIEF VALVE AND CLOSED DESIGNATED VALVES TO SHUT IN FLOW 02:52 - WILLIAMS TECH CONFIRMED SOC WAS GIVEN ALL RELATED INFORMATION AND WILL MAKE EXTERNAL NOTIFICATIONS AS NECESSARY. 05/29/18 REPAIRED FAILED REGULATOR BOOT AND RESEATED RELIEF VALVE
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180059 | 32778 | 2018-06-08 07:38 | SUPPLEMENTAL FINAL | 4070 | EAST TENNESSEE NATURAL GAS, LLC (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2018-05-21 16:15 | 2018 |  |  | 35.2454 | -85.7532 | 1212853 | 2018-05-21 16:50 |  | NATURAL GAS |  | 3 | 1681 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-05-21 17:41 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-05-21 16:15 | 2018-05-21 16:15 | ONSHORE | TN | 37387 | Not Within a Municipality | GRUNDY | MILEPOST | 35.56 | 3200-1 | TRCY-OOLT | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12.75 |  | 0.25 | 42000 | API-5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | AO SMITH | COAL TAR | [28 empty] | 1950 | 1950 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 247 |  | NO | NO | NO |  | 0 | 0 | 5043 | 5250.11504986401 | 9 | 8.1063829787234 | 251000 | 261308.522212149 | 0 | 0 | 0 | 0 |  |  | 256052 | 122365.852396752 | 266566.743644991 | [8 empty] | 500 |  | 787 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 59452 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLERS COULD NOT HAVE IDENTIFIED THE PIN HOLE LEAK. | [12 empty] | NO |  |  | YES | 1 | 0 | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION | [6 empty] | YES | INACTIVE |  |  | YES |  |  |  | YES | YES |  | YES | YES | YES |  |  |  | 2018 |  |  |  | YES | [190 empty] | YES | YES | [6 empty] | 2017 | [55 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DWAYNE TESCHENDORF | ENGINEER SPECIALIST | dwayne.teschendorf@enbridge.com | 713-627-5573 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | A NATURAL GAS PIN HOLE LEAK WAS DISCOVERED DURING A CORROSION ANOMALY INVESTIGATION ON THE EAST TENNESSEE NATURAL GAS 12-INCH LINE 3200-1 AT MILE POST 35.56 NEAR TRACY CITY, TENNESSEE AT 4:15 PM, MAY 21, 2018. THE CAUSE OF THE PIN HOLE WAS EXTERNAL CORROSION. THE PIPE REPLACEMENT WAS COMPLETED JULY 20, 2018.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180060 | 30724 | 2018-06-08 13:34 | SUPPLEMENTAL FINAL | 2620 | COLUMBIA GULF TRANSMISSION, LLC | 700 LOUISIANA ST. SUITE 700 | HOUSTON | TX | 77002 | 2018-05-18 01:52 | 2018 |  |  | 32.4155 | -91.4897 | 1212526 | 2018-05-18 03:11 |  | NATURAL GAS |  | 3805 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-05-18 02:24 | 2018-05-18 13:26 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-05-18 02:07 | 2018-05-18 02:20 | ONSHORE | LA | 71232 | DELHI | RICHLAND | MILEPOST | BLOWDOWN VLV | DELHI COMPRESSOR STATION | ML 100 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1991 |  | CARBON STEEL |  | OTHER | [8 empty] | MALFUNCTION OF A 4" RELIEF VALVE, RESULTING IN AN UNINTENTIONAL RELEASE OF NATURAL GAS TO ATMOSPHERE | CLASS 2 LOCATION | NO |  | 148 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 10350 | 9322.34042553191 | 0 | 0 | 500 | 520.534904805077 | 0 | 0 |  |  | 10850 | 9903.83287359426 | 9842.87533033699 | [8 empty] | 902 |  | 935 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE MALFUNCTION OF THE RELIEF VALVE ACTIVATION WAS NOT DUE TO ANY INVOLVEMENTS BY GAS CONTROL PERSONNEL | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | DEBRIS IN THE SENSING LINE CAUSED THE UNINTENTIONAL OPERATION OF RELIEF VALVE | [161 empty] | CODY BOWERS | COMPLIANCE SPECIALIST | cody_bowers@transcanada.com | (304) 357-2814 |  |  |  |  | GEORGE HAMATY | COMPLIANCE MANAGER | (304) 357-3728 | george_hamaty@transcanada.com | ON MAY 18TH, 2018, DELHI COMPRESSOR STATION (CS) WAS SUBJECT TO AN UNINTENTIONAL RELEASE OF NATURAL GAS (MATERIAL) RESULTING IN MATERIAL LOSS EXCEEDING 3,000 MCF. DELHI IS A TRANSMISSION CS THAT IS MAINTAINED BY COLUMBIA GULF TRANSMISSION, LLC (TRANSCANADA) AND IS LOCATED IN RICHLAND PARISH, NEAR THE TOWN OF DELHI, LOUISIANA. AT APPROXIMATELY 02:07 CST TRANSCANADA'S MONITORING CENTER RECEIVED A NOTIFICATION FROM THE PUBLIC OF A POTENTIAL RELEASE OF MATERIAL AT DELHI CS. ONCE OPERATIONS PERSONNEL ARRIVED ON-SITE AT APPROXIMATELY 02:20 CST, THE UNINTENDED RELEASE OF MATERIAL WAS IDENTIFIED AND ISOLATED AT APPROXIMATELY AT 02:24 CST. THE MATERIAL LOSS CALCULATIONS WERE DETERMINED TO BE GREATER THAN 3,000 MCF, HENCE, THE EVENT WAS REPORTED TO THE NATIONAL RESPONSE CENTER (NRC). THE INVESTIGATION DETERMINED THAT GREASE AND DEBRIS IN THE SUPPLY/SENSING LINE AND FILTER SCREENS OF THE PILOT RELIEF VALVE CAUSED THE UNINTENTIONAL OPERATION OF THE RELIEF VALVE. A 48-HR. UPDATE WAS CALLED-IN TO THE NRC WHERE THE UPDATE REPORT NO. WAS 1212599.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180061 | 31450 | 2018-06-11 09:14 | SUPPLEMENTAL FINAL | 39109 | SUSQUEHANNA GATHERING COMPANY I, LLC | ONE ENERGY PLAZA - WCB 2130 | DETROIT | MI | 48226 | 2018-05-18 03:03 | 2018 |  |  | 41.805 | -75.7386 | 1212527 | 2018-05-18 07:47 |  | NATURAL GAS |  | 3260 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-05-18 06:51 | 2018-05-19 12:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-05-18 06:03 | 2018-05-18 06:51 | ONSHORE | PA | 18834 | NEW MILFORD | SUSQUEHANNA | SURVEY STATION NO. | UNIT 10 | CDP 5 COMPRESSOR STATION | CDP 5 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 2018 |  | CARBON STEEL |  | OTHER | [8 empty] | MALFUNCTION OF A MECHANICAL RELIEF VALVE | CLASS 1 LOCATION | NO |  | 628 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 3782 | 3406.48226950355 | 3000 | 3123.20942883046 | 300 | 312.320942883046 | 0 | 0 |  |  | 7082 | 5108.65393971739 | 6842.01264121705 | [8 empty] | 1410 |  | 1440 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE FAILURE WAS NOT A RESULT OF CONTROLLER ACTIONS. FAILURE WAS A RESULT OF MECHANICAL FAILURE OF A RELIEF DEVICE BELOW ITS SET POINT WHICH DID NOT RESET. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [13 empty] | YES |  |  | YES | [11 empty] | YES | SPRING FAILURE | [161 empty] | PATRICK J. RAICHEL | SENIOR CODES AND COMPLIANCE ENGINEER | patrick.raichel@dteenergy.com | 304-322-4004 |  |  |  |  | PATRICK J. RAICHEL | SENIOR CODES AND COMPLIANCE ENGINEER | 304-322-4004 | patrick.raichel@dteenergy.com | CDP 5, A MULTI-UNIT COMPRESSOR STATION IN GATHERING SERVICE, SUFFERED AN UNINTENTIONAL RELEASE OF NATURAL GAS ON THE MORNING OF MAY 18TH, 2018. THIS RELEASE WAS A RESULT OF A FAILURE OF A MECHANICAL RELIEF VALVE BETWEEN THE 2ND STAGE COMPRESSION AND THE COOLER ON UNIT #10. THE RELIEF VALVE FAILED SAFE AT A PRESSURE BELOW THE MAOP AND CONTINUED TO VENT GAS UNTIL THE UNIT WAS TAKEN OFF-LINE AND THE FLOW OF GAS WAS SECURED. THE EVENT BEGAN AT 03:03 HOURS AND LASTED UNTIL 06:51 HOURS. A LOCAL LAND OWNER REPORTED A NOISE COMPLAINT TO ANOTHER OPERATOR IN THE SHARED PIPELINE CORRIDOR, WHO IN TURN NOTIFIED DTE GAS CONTROL AT 06:03 HOURS. THE ON-CALL TECHNICIAN WAS DISPATCHED TO INVESTIGATE. UPON ARRIVAL, HE FOUND GAS BLOWING FROM A RELIEF VALVE ON UNIT #10, A SKID-MOUNTED RECIPROCATING COMPRESSOR. THE BLOWING GAS WAS SECURED BY SECURING THE INLET AND OUTLET VALVES ON THE UNIT. FOLLOW UP INVESTIGATIONS DETERMINED THAT THE RELIEF VALVE OPERATED BELOW IT'S SET POINT AND FAILED TO RESET. THE INCIDENT AND INVESTIGATION HAVE ALSO BEEN REPORTED TO THE PA PUBLIC UTILITIES COMMISSION. SECOND (48 HOUR) NRC REPORT NUMBER IS 1212719.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180062 | 30498 | 2018-06-14 08:45 | ORIGINAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2018-05-24 04:15 | 2018 |  |  | 35.6919 | -100.2275 | 1213124 | 2018-05-24 12:28 |  | NATURAL GAS |  | 13500 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-05-24 04:49 | 2018-05-24 06:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-05-24 04:15 | 2018-05-24 04:45 | ONSHORE | TX | 79011 | BRISCOE | HEMPHILL | MILEPOST | AD-23 | AD-23 | ONEOK METER STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1978 |  | CARBON STEEL |  | LEAK |  |  | OTHER | RELIEF VALVE MALFUNCTION | [5 empty] | CLASS 1 LOCATION | NO |  | 175 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 39107 | 35224.0354609929 | 500 | 520.534904805077 | 500 | 520.534904805077 | 0 | 0 |  |  | 40107 | 36996.2354871412 | 36265.1052706031 | [8 empty] | 971 |  | 1000 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE GAS RELEASE WAS DUE TO RELIEF VALVE MALFUNCTION. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [13 empty] | YES | [177 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | ON MAY 24, 2018 AT 04:15 AN ENABLE O&M TECH WAS NOTIFIED BY PERSONNEL AT THE WOODALL PLANT THAT A RELIEF VALVE WAS GOING OFF ON LINE AD-23 IN HEMPHILL COUNTY, TEXAS. THE O&M TECHNICIAN ARRIVED AT THE METER STATION LOCATION AT 04:49 AND BACKED OFF THE RELIEF VALVE, LOCKED IT OUT, AND RESET IT. THE EVENT WAS COMPLETE AT 06:15. APPROXIMATELY 13.5 MMCF OF NATURAL GAS WAS RELEASED. NO INJURIES, NO DAMAGE TO COMPANY PROPERTY. NRC WAS NOTIFIED ON 5/24 (#1213124) AND A 48 HR. FOLLOW UP ON 5/25 (#1213192). UPON INVESTIGATION THE O&M TECHNICIAN DETERMINED THE SETPOINT (971 [PSIG) OF THE RELIEF VALVE HAD SHIFTED CAUSING THE RELEASE. THE RELIEF WAS RESET TO THE PROPER SETPOINT (999 PSIG) AND THE RELIEF WAS PLACED BACK INTO SERVICE. PRIOR TO THE INCIDENT, THE RELIEF VALVE WAS LAST INSPECTED IN JULY 2017.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180063 | 30514 | 2018-06-19 16:18 | ORIGINAL FINAL | 4900 | KINDER MORGAN TEJAS PIPELINE | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2018-05-28 10:02 | 2018 |  |  | 29.0423 | -96.084 | 1213476 | 2018-05-28 13:16 |  | NATURAL GAS |  | 13911 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-05-28 11:12 | 2018-05-29 09:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-05-28 10:30 | 2018-05-28 11:00 | ONSHORE | TX | 77456 | Not Within a Municipality | MATAGORDA COUNTY | MILEPOST | STATION 3B | COMPRESSOR STATION 3B | UNIT NO. 1 DISCHARGE PIPING | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | OTHER | COMPRESSOR STATION DISCHARGE PIPING. |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2012 |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENTIONAL RELEASE OF NATURAL GAS THROUGH A RELIEF VALVE LOCATED ON UNIT NO. 1 COMPRESSOR DISCHARGE PIPING. | CLASS 1 LOCATION | NO |  | 214 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 34769 | 31316.7588652482 | 1200 | 1249.28377153218 | 120 | 124.928377153218 | 0 | 0 | NA |  | 36089 | 33098.3055475182 | 32690.9710139336 | [8 empty] | 894 |  | 960 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLERS ACTIONS DID NOT CAUSE THE RELIEF VALVE TO ACTUATE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | A DEFECTIVE O-RING IN THE PILOT VALVE HOUSING CAUSED THE RELIEF VALVE TO OPEN | [161 empty] | STEPHEN R. DINES | ENGINEER - CODES AND STANDARDS | stephen_dines@kindermorgan.com | (719) 329-5633 |  |  |  |  | JAIME A. HERNANDEZ | DIRECTOR OF ENGINEERING CODES AND STANDARDS | 713 369-9443 | jaime_hernandez@kindermorgan.com | ON 5/28/18 TEJAS GAS PIPELINE (TEJAS) GAS CONTROL RECEIVED A CALL FROM A LOCAL NEARBY RESIDENT AT APPROXIMATELY 10:30 AM LOCAL TIME WITH A REPORT OF GAS VENTING AT THE 3B COMPRESSOR STATION IN MATAGORDA COUNTY, TEXAS. AT APPROXIMATELY 10:35 AM LOCAL TIME, GAS CONTROL DISPATCHED TEJAS OPERATIONS PERSONNEL TO INVESTIGATE THE REPORT OF VENTING GAS. AT 11:12 AM LOCAL TIME, OPERATIONS PERSONNEL CONFIRMED, ISOLATED, AND STOPPED THE RELEASE OF NATURAL GAS. THEY DETERMINED THE GAS ORIGINATED FROM THE RELIEVE VALVE (PSV 2020) ON COMPRESSOR UNIT NO. 1. A TOTAL OF 13,911 MSCF OF NATURAL WAS RELEASED AND REPORTED TO THE NRC AND THE TEXAS RAILROAD COMMISSION. A COURTESY NOTIFICATION TO THE PHMSA ACCIDENT INVESTIGATION GROUP WAS ALSO PROVIDED. A REVISED NRC REPORT WAS SUBMITTED TO CORRECT THE COMPANY NAME AND LOCATION INFORMATION (NRC NO. 1213482) ON THE SAME DAY OF THE EVENT AND A 48-HOUR UPDATE WAS ALSO PROVIDED (NRC NO. 1213568) THE FOLLOWING DAY. PSV 2020 IS LOCATED ON 10' DIAMETER STATION DISCHARGE PIPING BETWEEN THE COMPRESSOR ENGINE AND THE COOLING FANS. UPON INVESTIGATION, IT WAS DETERMINED THE RELEASE OF GAS WAS CAUSED BY THE PSV 2020 ACTUATING BELOW ITS ESTABLISHED SET-POINT. THE PRESSURES OBSERVED DURING THE EVENT DID NOT EXCEED THE ESTABLISHED MAOP OF THE STATION OR DOWNSTREAM FACILITIES. A REVIEW OF OPERATION AND MAINTENANCE RECORDS FOR PSV 2020 SHOWED IT WAS LAST TESTED ON 3/26/18 AND REPORTED TO BE WORKING PROPERLY WITH NO PROBLEMS NOTED. THE EVENT WAS CLASSIFIED AS AN ABNORMAL OPERATION AND THE IMMEDIATE CAUSE OF THE RELEASE WAS IDENTIFIED AS DEFECTIVE EQUIPMENT: A DEFECTIVE O-RING IN THE PILOT VALVE HOUSING CAUSED THE PILOT VALVE TO OPEN THE RELIEF VALVE PRIOR TO THE ESTABLISHED SET POINT. THE ROOT CAUSE OF THE O-RING FAILURE WAS DETERMINED TO BE EXCESSIVE WEAR AND TEAR. THE EXISTING PILOT UNIT WAS REMOVED AND REPLACED WITH A NEW PILOT AND PSV 2020 WAS PLACED BACK INTO SERVICE ON 5/29/18.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180064 | 30720 | 2018-06-20 10:05 | SUPPLEMENTAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2018-05-28 12:57 | 2018 |  |  | 35.3099 | -93.5601 | 1213484 | 2018-05-28 14:40 |  | NATURAL GAS |  | 21700 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-05-28 13:51 | 2018-05-30 16:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 1 | 2018-05-28 13:03 | 2018-05-28 13:51 | ONSHORE | AR | 72865 | SUBIACO | LOGAN | MILEPOST | BT-14 | BT-14 | BT-14 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 |  | 0.25 | 46000 | UNKNOWN | SEAMLESS |  | NATIONAL TUBE | COAL TAR | [28 empty] | 1954 | 1954 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 28 | 0.5 |  | CLASS 1 LOCATION | NO |  | 249 |  | NO | NO | NO |  | 12000 | 12492.8377153218 | 0 | 0 | 62861 | 56619.4822695035 | 59000 | 61423.1187669991 | 5000 | 5205.34904805077 | 0 | 0 |  |  | 138861 | 95018.7551787624 | 135740.787799875 | [8 empty] | 756 |  | 901 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 86247 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS CAUSED BY A RUPTURE DUE TO MECHANICAL DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [64 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | [10 empty] | YES |  |  |  |  | YES | [6 empty] | OCCUPANT | BACKHOE/TRACKHOE | UNKNOWN/OTHER | NO | [5 empty] | YES | 51 | DATA NOT COLLECTED | [121 empty] | YES | YES |  |  | YES |  |  | YES | 2018 | [31 empty] | 2018 | [17 empty] | COMBINATION TOOL | 2018 |  |  |  | NO | YES | 1986 | 1701 | NO | [13 empty] | NO | [63 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | ON 5/28/18 AT 13:03 ENABLE GAS TRANSMISSION NOTICED HIGH DIFFERENTIAL READINGS AT LINE J TO BT-14 TAKE OFF AND FLOW INCREASE TO APPROXIMATELY 80 MILLION. FALLING UPSTREAM AND DOWNSTREAM PRESSURE READINGS INDICATED A POTENTIAL GAS RELEASE. AT 13:12 A O&M TECHNICIAN WAS DISPATCHED TO INVESTIGATE. ENABLE GAS TRANSMISSION SYSTEM CONTROL RECEIVED A CALL FROM THE LOGAN COUNTY SHERIFF'S OFFICE AT 13:20 WITH A REPORT OF GAS BLOWING. AROUND 13:51 IT WAS CONFIRMED THAT BT-14 HAD FAILED AND THE UPSTREAM VALVE WAS CLOSED. THE DOWNSTREAM VALVE WAS CLOSED AT 14:09 AND THE SEGMENT WAS ISOLATED. ONE HOUSE WAS EVACUATED AS A PRECAUTION BY THE LOGAN COUNTY SHERIFF'S OFFICE AND 11 DOMESTIC METERS LOST SERVICE. UPON ARRIVAL TO THE INCIDENT SITE, FIRST RESPONDERS OBSERVED TREES PUSHED OVER IN THE RIGHT-OF-WAY AND THE DIRT BEHIND THE INCIDENT SITE, AND IN THE GENERAL AREA, LOOKED LIKE IT HAD BEEN REMOVED BY MECHANICAL EQUIPMENT. IN REVIEWING LOCATE TICKETS BACK TO 2015, A ONE CALL LOCATE REQUEST HAS NOT BEEN SUBMITTED IN THE INCIDENT AREA. THE NRC WAS NOTIFIED AT 14:38 (NRC#1213484) AND A 48 HOUR FOLLOW UP CALL WAS PROVIDED ON 5/30/2018 AT 07:13 (NRC#1213629). AN ILI RUN WAS PERFORMED ON BT-14 IN APRIL 2018. THE ILI REPORT DID CALL OUT DENTS AND GEOMETRIC MAGNETIC ANOMALIES (GMA) IN THE AREA OF THE INCIDENT, BUT THE INCIDENT OCCURRED BEFORE THE PRELIMINARY ILI RESULTS WERE RECEIVED FROM THE VENDOR. ANALYSIS OF THE FINAL ILI REPORT SHOWED NO OTHER SECTIONS IN THE AREA OF THE INCIDENT SITE CONTAINING GMA'S. THE LINE WAS REPAIRED AND PLACED BACK INTO SERVICE ON 5/30/2018. INITIAL INSPECTION OF THE FAILED SECTION INDICATE MECHANICAL DAMAGE AND EXCAVATION ACTIVITIES HAVE OCCURRED NEAR THE PIPELINE. CURRENTLY, THE INCIDENT IS UNDER INVESTIGATION AND THE FAILED SECTION OF PIPE HAS BEEN SENT FOR METALLURGICAL ANALYSIS. WHEN THE INVESTIGATION TEAM RECEIVES THE RESULTS OF THE METALLURGICAL ANALYSIS, AND DETERMINE FINAL COSTS, A SUPPLEMENTAL REPORT WILL BE SUBMITTED. SUPPLEMENTAL REPORT ??/??/???? PART A 15B CHANGED RESTART TIME FROM 0800 TO 1630 PART C 3A. NOMINAL PIPE CHANGED FROM 12.75 TO 12.00 6. TYPE OF INCIDENT LONGITUDINAL CHANGED TO CIRCUMFERENTIAL .5 INCHES WIDE AND 28 INCHES LONG INSERTED. PART E 8. "INCIDENT WAS INITIATED BY A RUPTURE" TO "THE INCIDENT WAS CAUSED BY A RUPTURE DUE TO MECHANICAL DAMAGE.." PART G 3. CHANGED FROM "EXCAVATION DAMAGE BY THIRD PARTY" TO "PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY. 16A. CHANGED OUTAGE HOURS FROM 30 TO 51. PART H UPDATED FINAL REPORT RECEIVED FROM METALLURGIST STATING THE FOLLOWING: THE RESULTS OF THE METALLURGICAL FAILURE EXAMINATION INDICATED THAT THE STEEL PIPELINE FAILED DUE TO THE PRESENCE OF MECHANICAL DAMAGE ON THE OD SURFACE OF THE PIPE. THE MECHANICAL DAMAGE WAS IN THE FORM OF A SERIES OF DENTS AND A GOUGE THAT WAS APPROXIMATELY 28 INCHES LONG AND 0.5 INCHES WIDE LOCATED IN THE 12:00 POSITION. THE EDGE OF THE GOUGE EXHIBITED SCORE MARKS THAT CAUSED CRACK INITIATION. AFTER THE CRACK INITIATED, THE CRACK BEGAN TO PROPAGATE BY FATIGUE FROM THE OD TO THE ID UNTIL THE CRACK REACHED SUFFICIENT DEPTH TO PROPAGATE THE LENGTH OF THE PIPE IN A FAST BRITTLE FRACTURE MODE. FROM A METALLURGICAL AND CORROSION VIEWPOINT, THE PIPE WAS IN GOOD CONDITION AND WOULD NOT HAVE FAILED HAD IT NOT BEEN MECHANICALLY DAMAGED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180065 | 30517 | 2018-06-20 10:46 | ORIGINAL FINAL | 31286 | ONEOK GAS TRANSPORTATION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2018-06-01 13:30 | 2018 |  |  | 35.7552 | -97.7548 | 1213924 | 2018-06-01 13:50 |  | NATURAL GAS |  | 15348 | 2965 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-06-01 13:20 | 2018-06-02 16:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-06-01 12:10 | 2018-06-01 12:30 | ONSHORE | OK | 73750 | Not Within a Municipality | KINGFISHER | MILEPOST | MP 6.08 | F-190 | SIMMONS JUNCTION | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12.75 |  | 0.219 | 42000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | JONES & LAUGHLIN | COAL TAR | [28 empty] | 1960 | 1960 | CARBON STEEL |  | MECHANICAL PUNCTURE | 2 | 4 | [7 empty] | CLASS 1 LOCATION | NO |  | 255 |  | NO | NO | NO |  | 0 | 0 | 6369 | 6630.57361740707 | 32978 | 29703.5886524823 | 40000 | 41642.7923844062 | 200 | 208.213961922031 | 0 | 0 |  |  | 79547 | 53049.3835803493 | 78185.1686162175 | [8 empty] | 749 |  | 840 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 64000 | NO |  |  |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELEASE WAS CAUSED BY THIRD PARTY LINE STRIKE DURING EXCAVATION WHICH RESULTED IN DAMAGE TO THE PIPELINE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | UNKNOWN/OTHER | YES | 18051713312414 |  | UTILITY OWNER | YES | YES | YES | 30 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO MAINTAIN CLEARANCE | [263 empty] | KAREN PEREZ | REGULATORY COMPLIANCE COORDINATOR | karen.perez@oneok.com | 918-595-1703 |  |  |  |  | WESLEY DUNBAR | VP NATURAL GAS PIPELINE OPERATIONS | 918-588-7424 | wesley.dunbar@oneok.com | 06/01/2018 AT APPROXIMATELY 12:08 PM 3RD PARTY CONTRACTOR STRUCK F-190 WHILE EXCAVATING FOR NEW PIPELINE CONSTRUCTION. F-190 WAS CLEARLY MARKED WITH FLAGS AND PAINT AS WELL; COMMUNICATIONS HAD BEEN MADE WITH THE CONTRACTOR BY COMPANY PERSONNEL. A ONEOK PIPELINE OPERATOR HAD COMMUNICATED WITH THE CONTRACTOR EXPRESSING THE LOCATION OF F-190 AND VERIFYING WHERE THE WORK WAS TO TAKE PLACE, AFTER COMMUNICATIONS THE PIPELINE OPERATOR WAS ON LOCATION SEVERAL DAYS BEFORE THE INCIDENT INSPECTING WHILE THE CONTRACTOR CROSSED F-190 IN A SEPARATE LOCATION. ONCE WORK WAS COMPLETED COMMUNICATIONS WERE ONCE AGAIN MADE CONCERNING ANY FURTHER WORK, THE CONTRACTOR EXPRESSED THEY WOULD NOT BE NEAR ANY ONEOK PIPELINES MOVING FORWARD. SPEAKING TO THE CONTRACTOR AFTER THE INCIDENT ON 6-1-18 THEY ADMITTED THEY MOVED PART OF THEIR EXCAVATION AND KNEW THE PIPELINE'S LOCATION AND FAILED TO CONTACT ONEOK. 06/01/2018 ONEOK ISOLATED THE 13 MILE SECTION OF F-190 BETWEEN OKARCHE TAKE OFF AND SIMMONS JCT, BLEW THE PIPELINE DOWN TO 0 PSI, CHECKED THE ATMOSPHERE AT THE INCIDENT LOCATION AND ONCE DEEMED SAFE EXCAVATION BEGAN. 06/01/2018 TELEPHONIC NOTIFICATIONS WERE MADE TO NRC (PHMSA) AND OKLAHOMA CORPORATION COMMISSION. 06/02/2018 ONEOK RESUMED EXCAVATION; ONCE EXCAVATED AND BELL HOLE MADE SAFE REPAIRS BEGAN, 4' OF 12" PIPE WAS REMOVED AND REPLACED WITH LIKE KIND, X-RAYED, PURGED AND RETURNED TO NORMAL OPERATION AROUND 4:30 PM. 06/03/2018 NRC# 1214058 (48) HOUR REVISED INCIDENT REPORT FILED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180066 | 31130 | 2018-06-25 17:21 | SUPPLEMENTAL FINAL | 32231 | MONUMENT PIPELINE, LP | 601 TRAVIS STREET SUITE 1900 | HOUSTON | TX | 77002 | 2018-05-26 21:00 | 2018 |  |  | 29.5832 | -95.3484 | 1213372 | 2018-05-27 00:52 |  | NATURAL GAS |  | 20017.851 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-05-26 21:18 | 2018-05-30 16:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-05-26 21:15 | 2018-05-26 23:13 | ONSHORE | TX | 77581 | PEARLAND | BRAZORIA | MILEPOST | 80642.72 FT | MONUMENT | P-16 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 79 |  | YES |  |  |  |  | YES | UNCASED | [16 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.281 | 46000 | API 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1951 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 16 | 48 |  | CLASS 3 LOCATION | NO |  | 313 |  | NO | NO | NO |  | 200000 | 208213.961922031 | 0 | 0 | 60000 | 54042.5531914894 | 175000 | 182187.216681777 | 0 | 0 | 12500 | 13013.3726201269 | COST OF FAILURE ANALYSIS |  | 447500 | 241206.292638388 | 457457.104415424 | [8 empty] | 813 |  | 808 | 192.619(A)(2) |  |  |  | PRESSURE EXCEEDED MAOP, BUT DID NOT EXCEED THE APPLICABLE ALLOWANCE IN 192.201 | NO |  |  |  |  | MANUAL | MANUAL | 44786 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [5 empty] | YES | INVESTIGATION IDENTIFIED THAT CONTROLLER POST-RUPTURE RESPONSE TIME CONTRIBUTED TO THE DURATION OF THE INCIDENT. | YES | 1 | 0 | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  |  |  | YES | [6 empty] | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO | [5 empty] | NO |  | DATA NOT COLLECTED | [266 empty] | DAVID BUSBY | SR. PGD OPERATIONS SPECIALIST | david.busby@nexteraenergy.com | 713-951-5318 |  |  |  |  | WILLIAM MEYER | DIRECTOR REGULATORY AFFAIRS ASSET INTEGRITY | 713-951-5331 | william.meyer@nexteraenergy.com | DURING A SEVERE THUNDERSTORM, MONUMENT'S PRIMARY DELIVERY CUSTOMER LOST POWER TO THEIR FACILITY AND SHUT IN THE METER. DURING THE RESULTING PRESSURE BUILD-UP, THE PIPELINE RUPTURED. THE PIPELINE RUPTURE OCCURRED AT A RECENT EXCAVATION LOCATION WHERE A STORM WATER LINE, SEWER LINE, AND NEW DRIVEWAY WERE INSTALLED. UPON DISCOVERY, THE RUPTURED PIPELINE SECTION WAS ISOLATED BETWEEN TWO MAINLINE VALVES AND THE PRESSURE BLED DOWN TO 0 PSI. THE PIPELINE REPAIR WAS COMPLETED AND THE PIPELINE RETURNED TO SERVICE ON 5/30/2018. FINAL REPORT FINAL DETERMINATION BASED ON COMPLETION OF METALLURGICAL ANALYSIS WAS MECHANICAL DAMAGE CONSISTENT WITH THIRD PARTY EXCAVATION EQUIPMENT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180067 | 31416 | 2018-06-27 11:41 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2018-06-07 04:16 | 2018 |  |  | 39.8067 | -80.7594 | 1214458 | 2018-06-07 06:12 |  | NATURAL GAS |  | 165000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-06-07 05:20 | 2018-07-15 14:18 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 0 | 2018-06-07 04:37 | 2018-06-07 06:00 | ONSHORE | WV | 26041 | MOUNDSVILLE | MARSHALL | MILEPOST | MP 21.3 | LEACH XPRESS | MAINLINE VALVE LEX-500 TO MAINLINE VALVE LEX-600 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 36 |  | 0.515 | 70000 | API 5L X70M | DSAW |  | DURABOND | EPOXY | [28 empty] | 2017 | 2015 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 113 | 36 |  | CLASS 1 LOCATION | NO |  | 1056 |  | NO | NO | NO |  | 600000 | 624641.885766092 | 0 | 0 | 437250 | 393835.106382979 | 13422000 | 13973238.9845875 | 0 | 0 | 5925384 | 6168738.39274705 | BACK TO SERVICE SITES |  | 20384634 | 9940732.94466028 | 21160454.3694836 | [8 empty] | 1280 |  | 1440 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | AUTOMATIC | 71280 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL ROOM PERSONNEL WERE NOT PERFORMING ANY CHANGES TO THE PIPELINE SYSTEM THAT MAY HAVE IDENTIFIED AS A CONTRIBUTING FACTOR THAT MAY HAVE POTENTIALLY LED TO THE PIPELINE FAILURE | [12 empty] | YES | 1 | 0 | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [52 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | SUBSIDENCE |  |  |  |  | NO | [306 empty] | KAMRAN ROSTAMI ASRABADI | COMPLIANCE SPECIALIST | kamran_rostami@transcanada.com | 304-357-2351 |  |  |  |  | GEORGE HAMATY | MANAGER US REGULATORY COMPLIANCE EAST | 304-357-3728 | george_hamaty@transcanada.com | ON JUNE 7TH, 2018, AN UNINTENDED RELEASE EVENT OF NATURAL GAS (MATERIAL) INTO THE ATMOSPHERE WAS REPORTED TO THE NATIONAL RESPONSE CENTER (NRC). THIS EVENT TOOK PLACE ON THE LEACH EXPRESS (LEX) PIPELINE THAT IS OPERATED AND MAINTAINED BY COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA). LEX PIPELINE IS A 36 INCH DIAMETER NATURAL GAS PIPELINE AND IS CLASSIFIED AS TRANSMISSION, WITH A MAXIMUM ALLOWABLE OPERATING PRESSURE OF 1,440 PSIG. LEX IS A UNIDIRECTIONAL FLOW PIPELINE THAT STARTS NEAR MAJORSVILLE , WEST VIRGINIA AND TERMINATES AT THE TIE-IN WITH R-SYSTEM REGULATOR STATION (OHIO). AT 04:16 EASTERN STANDARD TIME (EST), THE COLUMBIA GAS CONTROL PERSONNEL NOTED A LOW PRESSURE SCADA ALARM AND COLUMBIA OPERATIONS PERSONNEL WERE DISPATCHED TO INVESTIGATE THE EVENT. AT 04:37 EST, THE COLUMBIA MONITORING CENTER RECEIVED A CALL FROM THE MARSHALL COUNTY 911 REGARDING A PIPELINE FAILURE IN MARSHALL COUNTY, WV NEAR WV STATE ROUTE 21/1 (NIXON RIDGE ROAD). THE FAILURE WAS WITHIN VALVE SECTION (VS) MAINLINE VALVE LEX-500 TO MAINLINE VALVE LEX-600 (ISOLATED SEGMENT). THE MATERIAL IGNITED. LIMITED DAMAGE OCCURRED TO VEGETATION AND TREES WITHIN THE AREA OF THE PIPELINE FAILURE SITE. NO STRUCTURES WERE IDENTIFIED NEAR THE FAILURE SITE. NO FATALITIES OR INJURIES WERE REPORTED AS A RESULT OF THIS PIPELINE FAILURE. THE FAILED PIPELINE SECTION WAS ISOLATED AT APPROXIMATELY 05:20 EST. THE FAILED SECTIONS OF THE PIPELINE WERE SENT TO A METALLURGICAL LABORATORY TO DETERMINE THE PROBABLE CAUSE BEHIND THE FAILURE OF THE PIPELINE. THE 48-HR UPDATETO THE NRC WAS COMPLETED ON JUNE 8TH, 2018 WITH REPORT NO. 1214673. THE LABORATORY REPORT IDENTIFIED THE INCIDENT WAS CAUSED BY A SINGLE, OVERLOAD EVENT. OVERLOADING OF THE PIPELINE RESULTED FROM WHAT WAS LIKELY A SERIES OF LATERAL DISPLACEMENTS WITH ACCOMPANYING BENDING.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180068 | 30587 | 2018-07-03 11:50 | ORIGINAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2018-06-11 09:35 | 2018 |  |  | 31.4509 | -104.1989 | 1214945 | 2018-06-11 12:17 |  | NATURAL GAS |  | 23567 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | IMMEDIATE ACTION INCLUDED CLOSURE OF A MANUAL 2-INCH BYPASS VALVE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-06-11 09:35 | 2018-06-11 11:27 | ONSHORE | TX | 79855 | Not Within a Municipality | CULBERSON | MILEPOST | 0065-MP65 | GRESHAM COMPRESSOR STATION | 01600 LINE FROM WAHA TO EHRENBERG | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | ESD BREAK GLASS SWITCH. | UNKNOWN |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | COPPER WIRE AND STEEL CONDUIT | OTHER | [8 empty] | STATION EMERGENCY SHUTDOWN (ESD) SYSTEM | CLASS 1 LOCATION | NO |  | 671 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 49571 | 44649.0567375887 | 0 | 0 | 70 | 72.8748866727108 | 0 | 0 | NOT APPLICABLE |  | 49641 | 46323.155987646 | 44721.9316242614 | [8 empty] | 908 |  | 1050 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLERS ACTIONS DID NOT CAUSE THE UNINTENTIONAL EMERGENCY SHUTDOWN (ESD). | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | WIRE WITH ELECTRICAL SHORT TRIGGERING ACTIVATION OF THE ESD SYSTEM. | [22 empty] | YES | WORN/WEATHERED COPPER WIRE INSULATION ON ESD BREAK GLASS SWITCH. | [161 empty] | STEPHEN R. DINES | ENGINEER - CODES AND STANDARDS | stephen_dines@kindermorgan.com | 719 329-5633 |  |  |  |  | JAIME A. HERNANDEZ | DIRECTOR ENGINEERING - CODES AND STANDARDS | 713 369-9443 | jaime_hernandez@kindermorgan.com | GRESHAM STATION EXPERIENCED AN UNSCHEDULED EMERGENCY SHUT-DOWN (ESD) ON JUNE 11, 2018 AT APPROXIMATELY 9:35 AM LOCAL TIME. OPERATIONS PERSONNEL WERE DISPATCHED BY GAS CONTROL TO THE SITE AND CONFIRMED DISCOVERY AT 11:27 AM LOCAL TIME. THE STATION ESD EQUIPMENT FUNCTIONED AS INTENDED WITH A TOTAL OF 23,576 MSCF GAS VENTED TO ATMOSPHERE THROUGH A 4' BLOCK VENT VALVE DURING THE EVENT. THE GAS LOSS DURING THIS EVENT WAS CONFIRMED TO BE A REPORTABLE EVENT TO THE NRC - REPORT NO. 1214945 AND TO THE TECQ. A 48-HOUR UPDATE TO THE NRC - REPORT NO. 1215067 THE FOLLOWING DAY INCLUDING THE LATITUDE AND LONGITUDE FOR THE RELEASE LOCATION AND MAJOR CROSS STREETS. THE NORMAL ESD VOLUME FOR THE STATION SHOULD ONLY BE 135 MSCF. UPON INVESTIGATION, IT WAS DETERMINED THAT A MANUAL 2' BYPASS/LOADING VALVE LOCATED AT THE STATION DISCHARGE GAS BLOCK VALVE (VO-9113) WAS LEFT IN THE OPEN POSITION. DURING NORMAL OPERATION, THE POSITION OF THIS VALVE SHOULD BE CLOSED. HOWEVER, WITH THE 2-INCH VALVE IN THE OPEN POSITION, PIPELINE GAS WAS FREE TO BYPASS THE STATION ISOLATION VALVE VO-9113 AND ENTER THE ESD VENT PIPING CONTRIBUTING TO A REPORTABLE GAS RELEASE ABOVE THE NORMAL ESD VOLUME. TO DETERMINE THE ROOT CAUSE OF THE ESD ACTIVATION AND RELEASE OF NATURAL GAS, OPERATIONS COMPLETED AN INSPECTION OF THE ESD SYSTEM INCLUDING THE ALL OF THE ESD BREAK GLASS STATIONS, THE ESD PULL SWITCHES, THE FIRE DETECTION SYSTEM, THE GAS DETECTION SYSTEM, THE LOW SUCTION PRESSURE SWITCH, AND THE LOW INSTRUMENT AIR PRESSURE SWITCH. THE INSPECTION DETERMINED THAT THE IMMEDIATE CAUSE WAS AN ELECTRICAL SHORT IN THE ESD BREAK GLASS STAND NO. 3 WIRE THAT TRIGGERED THE ACTIVATION OF THE ESD SYSTEM. THE ROOT CAUSE OF THE ESD WAS THE SEEPAGE OF RAINWATER INTO AN OPEN ELECTRICAL CONDUIT CONTACTING AN EXPOSED ELECTRICAL WIRE RESULTING IN AN ELECTRICAL SHORTAGE TO THE CASING; TRIGGERING THE STATION ESD SYSTEM. CORRECTIVE ACTION INCLUDED REPLACING THE EXPOSED WIRE AND CONDUIT TO ELIMINATE THE SHORT ON THE NO. 3 ESD BREAK GLASS SWITCH STATION. IN ADDITION OPERATIONS WILL REPLACE EXPOSED WIRES ON THE ESD SYSTEM AND SEAL OPEN CONDUITS TO PREVENT WATER FROM ENTERING THE ELECTRICAL CONDUITS TO PREVENT ELECTRICAL SHORTING OF THE ESD WIRING AND AVOID INADVERTENT ACTIVATION OF THE ESD SYSTEM.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180069 | 30689 | 2018-07-03 13:55 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2018-06-18 03:24 | 2018 |  |  | 44.2693 | -93.3212 | 1215599 | 2018-06-18 07:00 |  | NATURAL GAS |  | 4670 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | EQUIPMENT WAS A BLOW DOWN VALVE TO A COMPRESSOR STATION THAT WAS NOT INOPERATION | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-06-18 03:24 | 2018-06-18 04:09 | ONSHORE | MN | 55021 | Not Within a Municipality | RICE | SURVEY STATION NO. | COMPRESSOR ST | FARIBAULT | 4594 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | BLOW DOWN VALVE OPENED | CLASS 1 LOCATION | NO |  | 654 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 12000 | 10808.5106382979 | 1400 | 1457.49773345422 | 0 | 0 | 0 | 0 | COSTS FOR NEW PILOT AND 12 HOURS OF WORK |  | 13400 | 11874.7036772696 | 12266.0083717521 | [8 empty] | 930 |  | 1000 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER NOT INVOLVED IN INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | SEAL FAILURE | [21 empty] | YES | BELIEVED SEAL MALFUNCTIONED. | [161 empty] | KENTON ANDERSON | INTERNAL CORROSION SPECIALIST | ken.anderson@nngco.com | 402-398-7617 |  |  |  |  | KENTON ANDERSON | INTERNAL CORROSION SPECIALIST | 402-398-7617 | ken.anderson@nngco.com | THE FARIBAULT D SUCTION BLOW DOWN VALVE OPENED VENTING GAS. THE VALVE HAD BEEN CLOSED. THE DETAILS ARE THE D LINE SUCTION PRESSURE WAS 930-PSIG, THE D SUCTION BLOW DOWN VALVE IS A 6-INCH GOV-121 NORDSTRUM PLUG VALVE, THE VALVE OPENED AT 0324, THE VALVE WAS CLOSED AT 0409, THE PRESSURE AFTER CLOSING WAS 861-PSIG.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180070 | 30592 | 2018-07-03 14:55 | ORIGINAL FINAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2018-06-05 12:17 | 2018 |  |  | 39.8422 | -97.2799 | 1214288 | 2018-06-05 12:47 |  | NATURAL GAS |  | 252 | 30491 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-06-05 15:00 | 2018-06-10 11:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-06-05 12:17 | 2018-06-05 17:00 | ONSHORE | KS | 66944 | HADDAM | WASHINGTON | MILEPOST | STN: 19567+00 | AMARILLO LINE #3 | CS 105 TO CS 106 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 54 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 36 |  | 0.344 | 52000 | API-5LX | FLASH WELDED |  | AO SMITH | ASPHALT | [28 empty] | 1958 | 1958 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 662 |  | NO | NO | NO |  | 0 | 0 | 85070 | 88563.8087035358 | 703 | 633.198581560284 | 79718 | 82992.0030825023 | 1000 | 1041.06980961015 | 0 | 0 |  |  | 166491 | 79882.9886584836 | 173230.080177209 | [8 empty] | 650 |  | 712 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | AUTOMATIC | 97574 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM PERSONNEL WERE NOT INVOLVED IN THE INITIAL IDENTIFICATION OF THE LEAK NOR WOULD THEY HAVE SEEN ANY CHANGES IN PRESSURES OR OTHER INDICATORS BASED ON THE ESTIMATED SIZE OF THE LEAK. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | YES | [14 empty] | YES | PIPE MANUFACTURE DEFECT | [6 empty] | YES | [63 empty] | YES | YES | [6 empty] | 2015 | [55 empty] | YES | 1981 | 1018 | NO | [13 empty] | NO | [63 empty] | SHELLEY BROMAN | PIPELINE ENGINEER | shelley_broman@kindermorgan.com | 303-570-7819 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR- COMPLIANCE- CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | ON JUNE 5, 2018 AT 12:17PM, A KINDER MORGAN TECH EMPLOYEE WORKING IN THE AREA NOTICED THE SMELL OF GAS AND A 10FT DIAMETER CIRCLE OF DEAD VEGETATION CENTERED DIRECTLY ON TOP OF AMARILLO LINE #3. THAT DAY, THE LINE WAS ISOLATED, BLOWN DOWN, AND SECURED AND AN EMERGENCY ONE CALL WAS PLACED. ON JUNE 6, 2018 THE LINE WAS MARKED FOR EXCAVATION. EXCAVATION COMMENCED ON JUNE 7, 2018. THE LEAK WAS LOCATED AND EXCAVATION WAS COMPLETED ON JUNE 8, 2018. THE LEAK WAS DETERMINED TO BE THE RESULT OF A WELD SEAM PENETRATOR DEFECT PRESENT FROM THE ORIGINAL MANUFACTURE OF THE PIPE. ON JUNE 9, 2018 THE LEAK WAS REPAIRED BY INSTALLING A PIPE LINE WELD ON SLEEVE AND THE PIPE WAS RECOATED. ON JUNE 10, 2018 THE LINE WAS BACKFILLED AND REGRADED AND AT 11:00AM, THE LINE WAS PLACED BACK INTO NORMAL SERVICE. ALL TIMES ABOVE ARE IN CENTRAL TIME.
2021-02-26 10:37 | NO | NO | UNGS (Underground Natural Gas Storage) | 20180072 | 30602 | 2018-07-06 17:45 | ORIGINAL | 31287 | WILD GOOSE STORAGE LLC | 2780, WEST LIBERTY ROAD | GRIDLEY | CA | 95948 | 2018-06-08 15:22 | 2018 |  |  | 39.3245 | -121.8831 | 1214718 | 2018-06-08 16:35 |  | NATURAL GAS |  | 5 | 90 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-06-08 15:23 | 2018-06-09 14:28 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-06-08 15:22 | 2018-06-08 15:22 | ONSHORE | CA | 95948 | GRIDLEY | BUTTE | MILEPOST | NON-APPLICABL | WILD GOOSE UNDERGROUND GAS STORAGE FACILITY | STORAGE WELLS PAD | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | OTHER | GAS STORAGE WELL |  |  | NO | [22 empty] | INTRASTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | OTHER | [37 empty] | SUB-SURFACE SAFETY VALVE AND PACKER | 2007 |  | CARBON STEEL |  | OTHER | [8 empty] | TEMPORARY LOSS OF WELL CONTROL DURING TUBING AND PACKER INSTALLATION WORKOVER DUE TO FAILURE OF SUB-SURFACE SAFETY VALVE PACKER TO EQUALIZE PRESSURE. | CLASS 1 LOCATION | NO |  | 775 |  | NO | NO | NO |  | 0 | 0 | 281 | 292.540616500453 | 16 | 14.4113475177305 | 10000 | 10410.6980961015 | 0 | 0 | 0 | 0 |  |  | 10297 | 4928.00989199883 | 10717.6500601197 | [8 empty] | 1100 |  | 1885 | OTHER | CALIFORNIA DEP. OF CONSERVATION - DOGGR PROJECT APPROVAL |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INDIVIDUAL STORAGE WELL INVOLVED IN THE INCIDENT WAS INTENTIONALLY DISCONNECTED FROM THE SCADA SYSTEM AND RELEASED TO CONTRACTORS FOR A TUBING AND PACKER INSTALLATION WORKOVER (MAINTENANCE WORK). | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | FAILURE OF THE SUB-SURFACE SAFETY VALVE PACKER TO EQUALIZE PRESSURE UPON RELEASE. | [15 empty] | YES | FAILURE TO EQUALIZE PRESSURE. | [161 empty] | MATHIEU FOURNIER | VICE PRESIDENT ENGINEERING AND OPERATIONS | mathieu.fournier@rockpointgs.com | 403-513-8657 |  |  |  |  | MATHIEU FOURNIER | VICE PRESIDENT ENGINEERING AND OPERATIONS | 403-513-8657 | mathieu.fournier@rockpointgs.com | THIS INCIDENT OCCURRED ON STORAGE WELL 24HZ DURING A TUBING AND PACKER INSTALLATION WORKOVER WITH A SERVICE RIG, AFTER ATTEMPTING TO UNSEAT AND PULL THE SUB-SURFACE SAFETY VALVE (SSSV) PACKER FROM THE WELL. 0730 HRS. SERVICES ARRIVE ON LOCATION. THE CONSULTANT SUPERVISORS CONDUCT THE SAFETY MEETING, JOB PROCEDURE AND JSA'S WITH ALL PERSONNEL. 0800 HRS. REPLACE TUBING HANGER HOLD DOWN SCREWS WITH NEW. PREPARE TO KILL TUBING. CLOSE ANNULAR PREVENTER. PRESSURE UP ON TUBING AND OPEN TIW VALVE. 1130 HRS. PUMP DOWN TUBING WITH 25 BBL OF WEIGHTED HEC POLYMER PILL AND 30 BBL OF 8.7 #/FT. BRINE. TP - VACUUM. SICP - 1100 PSI. EQUALIZE BOP STACK WITH CASING PRESSURE. RETRACT HOLD DOWN SCREWS. 1200 HRS. WITH SSSV MANUFACTURING COMPANY REPRESENTATIVE PRESENT, ATTEMPT TO RELEASE THE SSSV PACKER. MANUFACTURER PROCEDURE IS TO PICK UP ON PACKER, THIS OPENS THE EQUALIZING PORTS AND PULLING 10,000 # ( +/- 28,000 # ) IN EXCESS OF THE TUBING WEIGHT, THE SSSV PACKER SHOULD RELEASE. FOLLOWING ATTEMPTS AT PULLING TO 100,000 # TOTAL TENSION WITHOUT THE PACKER RELEASING, CALCULATIONS WERE MADE BY THE CONSULTANT SUPERVISORS TO CONFIRM THAT PULLING WEIGHT COULD BE INCREASED. THE SUPERVISORS HAD A TAILGATE VERBAL SAFETY MEETING WITH ALL PERSONNEL ON SITE DIRECTING THE DRILLER TO INCREASE PULL UP TO 110,000 #. WHILE PULLING TOWARDS 110,000 #, THE SSSV PACKER APPEARED TO RELEASE AT 105,000 #. THE TUBING JUMPED UP APPROXIMATELY 10 FT, WEDGING THE TUBING HANGER INTO THE BOTTOM ELEMENT OF THE ANNULAR BAG. 1430 HRS. PUMP DOWN CASING WITH 25 BBL OF BRINE AND RIG PUMP BEGAN TO PRESSURE UP. PUMP AN ADDITIONAL 10 BBL WHILE OPENING TIW VALVE TO CHECK FOR FLOW. FLUID COMING FROM TUBING. THIS LED THE SUPERVISORS ON LOCATION TO BELIEVE THAT TUBING ABOVE THE SSSV MAY HAVE PARTED. THE SUPERVISORS THEN BLED THE CASING PRESSURE TO 0 PSI TO HELP ASSESS THE SITUATION AND PRESSURE DID NOT INCREASE. THIS WAS ANOTHER INDICATION THAT THE TUBING MAY HAVE PARTED AND THE SSSV PACKER FAILED TO RELEASE AND EQUALIZE. THE SUPERVISORS AND PERSONNEL ON SITE THEN HAD ANOTHER VERBAL TAILGATE SAFETY MEETING, INSTRUCTING THE BOP OPERATOR TO BE READY TO SHUT IN IF REQUIRED. AFTER DISCUSSIONS BETWEEN SUPERVISORS ON SITE, THE HEAD SUPERVISOR MADE THE DECISION TO OPEN THE ANNULAR BAG OF THE BOP AND GET A WEIGHT MEASUREMENT ON THE TUBING. WHEN THE ANNULAR BAG OPENED, THE TUBING STRING IMMEDIATELY BEGAN TO EJECT OUT OF THE HOLE. 16 JOINTS OF TUBING ABOVE THE SSSV SYSTEM WITH 1/4" CONTROL LINE WERE EJECTED FROM THE WELL IN AN ESTIMATED 5 TO 7 SECONDS BEFORE THE BOP'S ANNULAR BAG AND PIPE RAMS CLOSED ON TUBING AND REGAINED CONTROL OF THE WELL. NOTIFICATIONS OF THE INCIDENT WERE MADE TO THE CONTROL ROOM OPERATORS, COMPANY MANAGEMENT AND REGULATORY AUTHORITIES. EJECTED TUBING WAS CUT ABOVE THE PUP JOINT COLLAR SO THAT THE WELL COULD BE SECURED FOR THE NIGHT WITH A TIW SAFETY VALVE. WELL WAS SECURE WITH RAMS AND ANNULAR CLOSED AND TIW VALVE ON THE TUBING.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180073 | 31115 | 2018-07-12 16:25 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2018-06-15 07:37 | 2018 |  |  | 38.1321 | -97.4949 | 1215328 | 2018-06-15 07:57 |  | NATURAL GAS |  | 38450 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-06-15 09:15 | 2018-06-19 21:10 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 0 | 2018-06-15 07:37 | 2018-06-15 07:40 | ONSHORE | KS | 67062 | Not Within a Municipality | HARVEY | SURVEY STATION NO. | 180 / 1084135 | LINE R | HUGOTON LINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 72 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 26 |  | 0.312 | 52000 | A. O. SMITH NO. 64-400-500 | FLASH WELDED |  | A.O. SMITH | COAL TAR | [28 empty] | 1948 | 1947 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 840 | 26 |  | CLASS 1 LOCATION | NO |  | 538 |  | NO | NO | NO |  | 80000 | 83285.5847688123 | 0 | 0 | 94401 | 85027.8510638298 | 435510 | 453396.312783318 | 15612 | 16253.1818676337 | 0 | 0 |  |  | 625523 | 341964.025701665 | 637962.930483594 | [8 empty] | 837 |  | 899 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | MANUAL | 132000 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 1 | 0 | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED |  | YES | [15 empty] | STRESS CORROSION CRACKING | [5 empty] | YES | [63 empty] | YES | [6 empty] | YES | [50 empty] | COMBINATION TOOL | 2012 |  |  |  |  | NO |  |  | Yes, but the point of the Accident was not identified as a dig site |  | 2009 | [11 empty] | NO | [63 empty] | JOHN ERIC GLAHN | PIPELINE COMPLIANCE ENGINEER | john.glahn@sscgp.com | 270-852-4414 | 270-852-5016 |  |  |  | SHAWN PATTERSON | VP AND CHIEF OPERATIONS OFFICER | 270-852-4670 | shawn.patterson@sscgp.com | ON JUNE 15, 2018, AT 7:37 AM LOCAL TIME SOUTHERN STAR CENTRAL GAS PIPELINE, INC. (SSCGP) INCURRED A RUPTURE AND SUBSEQUENT FIRE ON ITS 26 INCH LINE R PIPELINE SEGMENT LOCATED IN HARVEY COUNTY, KANSAS WITHIN A CLASS 1, NON-HCA AREA. THE INITIAL RUPTURE AND FIRE WAS WITNESSED BY A SSCGP EMPLOYEE ON HIS WAY TO WORK AND HE IMMEDIATELY PROCEEDED TO THE RUPTURE SITE ARRIVING AT 7:40 AM LOCAL TIME. THE EMPLOYEE NOTIFIED HEADQUARTERS ON HIS WAY TO THE SITE. SSCGP SCADA CONTROLLER IMMEDIATELY NOTICED A PRESSURE DROP ON LINE R AND SSCGP CALLED A SIGNIFICANT EVENT. LOCAL EMERGENCY RESPONDERS WERE ON SITE BY 8:12 AM. SSCGP CALLED NRC AT 7:57 AM. A SEPARATE CALL WAS MADE TO PHMSA AT 8:08 AM. MAINLINE REMOTE CONTROLLED VALVES WERE CLOSED AT 7:39 AM AND VALVES AT HESSTON STATION WERE MANUALLY CLOSED AT 7:42 AM. PARTRIDGE RCV WAS CLOSED AT 9:12 AM AND A 20" GATE VALVE WAS MANUALLY CLOSED AT 9:15 AM, THE RUPTURE SITE WAS ISOLATED. THERE WERE NO INJURIES, FATALITIES, OR DAMAGE TO STRUCTURES, AND THE LINE SEGMENT WAS SAFETY ISOLATED, GAS FLOW STOPPED AND FIRE EXTINGUISHED BY 10:21 AM. PHMSA INVESTIGATORS EXAMINED THE SITE BEFORE ANYTHING WAS DISTURBED. AFTER BEING GIVEN PERMISSION, THE DAMAGED SECTION OF PIPE WAS SHIPPED TO G2MT LABORATORIES IN HOUSTON, TEXAS FOR METALLURGICAL EXAMINATION. SSCGP THEN MADE ARRANGEMENTS TO REPAIR THE DAMAGE AND PLACED THE AFFECTED SECTION OF LINE R BACK IN SERVICE ON 6/19/2018 AT 9:10 PM LOCAL TIME UNDER A VOLUNTARY 20% PRESSURE REDUCTION. 189 FEET OF 26", 0.406" WALL, X70 PIPE WAS INSTALLED TO MAKE THE PERMANENT REPAIR. THE REPLACEMENT PIPE WAS STRENGTH TESTED ON SITE. G2MT SUBMITTED THE RESULTS OF THE METALLURGICAL FAILURE EXAMINATION TO SSCGP ON 9/18/2018. KEIFNER AND ASSOCIATES PERFORMED THE ROOT CAUSE FAILURE ANALYSIS (RCFA) AND SUBMITTED THE DRAFT RESULTS TO SSCGP ON 10/23/2018. THE RCFA DETERMINED THE CAUSE OF THE RUPTURE WAS NEAR-NEUTRAL PH STRESS CORROSION CRACKING. PART G HAS BEEN REVISED TO REFLECT THE FINDINGS OF THE RCFA.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180074 | 30753 | 2018-07-13 15:48 | SUPPLEMENTAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2018-06-16 10:00 | 2018 |  |  | 29.244 | -95.8793 | 1215478 | 2018-06-16 14:11 |  | NATURAL GAS |  | 4000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-06-16 10:00 | 2018-06-16 20:50 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-06-16 10:00 | 2018-06-16 10:45 | ONSHORE | TX | 77420 | NEW GULF | WHARTON | MILEPOST | 14.5354 | 4362 TX GULF SULPHUR 8 INCH | 4362 TX GULF SULPHUR 8 INCH | YES | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 31 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 |  | 0.223 | 35000 | API 5L | OTHER | PIPE BODY | UNKNOWN | COLD APPLIED TAPE | [28 empty] | 1966 | 1966 | CARBON STEEL |  | MECHANICAL PUNCTURE | 3 | 5 | [7 empty] | CLASS 1 LOCATION | NO |  | 194 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 13000 | 11709.219858156 | 13000 | 13533.907524932 | 0 | 0 | 0 | 0 |  |  | 26000 | 18351.9005763349 | 25243.127383088 | [8 empty] | 660 |  | 720 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 42240 | NO | [5 empty] | YES | MODIFICATIONS NECESSARY TO ACCOMMODATE. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY STRIKE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [7 empty] | FARMER | GRADER/SCRAPER | AGRICULTURE | NO | [5 empty] | YES | 9 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | ALEJANDRO ALCALA | REGULATORY COMPLIANCE ENGINEER | alex.alcala@energytransfer.com | 713-289-5529 |  |  |  |  | ALEJANDRO ALCALA | REGULATORY COMPLIANCE ENGINEER | 713-289-5529 | alex.alcala@energytransfer.com | 6/16/18 AT APPROXIMATELY 10:00AM, A THIRD PARTY CONTRACTOR OPERATING FARMING EQUIPMENT STRUCK THE TEXAS GULF SULPHUR 8 INCH GAS TRANSMISSION LINE. THE THIRD PARTY CONTRACTOR DID NOT MAKE A ONE-CALL NOTIFICATION. GAS CONTROL NOTICED A PRESSURE DROP AND PROCEEDED TO SHUT DOWN THE LINE. NRC TELEPHONIC NOTIFICATION MADE AT 14:11 NRC # 1215478. DURING INVESTIGATION, THE LANDOWNER CONTACTED A PIPELINE TECHNICIAN. AT APPROXIMATELY 8:50PM, THE PIPELINE WAS REPLACED AND REPAIRED WITH 8.5 FEET OF PRE-TESTED EMERGENCY PIPE AND PUT BACK INTO SERVICE. 6/18/18 48-HOUR UPDATE NRC NOTIFICATION MADE AT 13:50. ON 5/21/18, AREA OPERATIONS SUPERVISOR AND LANDOWNER SPOKE ABOUT A DITCH THE LANDOWNER WANTED TO INSTALL. AREA OPERATIONS SUPERVISOR TOLD THE LANDOWNER TO CONTACT HIM WHEN HE WAS READY TO INSTALL THE DITCH AND THE COMPANY WOULD INSTALL FOR HIM. 8/3/18 AS A PRUDENT OPERATOR, ETC DID IT'S BEST WITHIN THEIR CAPABILITIES. NOT ONLY DID ETC MEET WITH THE LANDOWNER NUMEROUS TIMES, BUT OFFERED TO DO ANY DITCHING OR INSTALLATION OF THE CULVERT FOR THE LANDOWNER; TO ENSURE NO INCIDENTS OR DAMAGE TO THE PIPELINE AND TO ENSURE SAFETY OF THE PEOPLE. THIS LINE HAS BEEN LOCATED NUMEROUS TIMES AND THE PROBLEM WAS THAT THE THIRD PARTY CONTRACTOR DID NOT CALL 8-1-1. ETC PIPELINE MAKERS ARE VISIBLE THROUGHOUT THE ROW AND SPECIFICALLY IN THIS AREA. ETC WILL CONTINUE TO PRACTICE SAFE PIPELINE PROCEDURES AND SPREAD PUBLIC AWARENESS AS WE ALREADY DO, TO PREVENT REOCCURRENCES.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180075 | 30666 | 2018-07-19 14:08 | ORIGINAL FINAL | 3 | ACADIAN GAS PIPELINE SYSTEM | 1100 LOUISIANA ST. | HOUSTON | TX | 77002 | 2018-06-25 10:51 | 2018 |  |  | 29.9604 | -91.0566 | 1216382 | 2018-06-25 12:02 |  | NATURAL GAS |  | 15000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-06-25 13:21 | 2018-06-27 14:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-06-25 11:00 | 2018-06-25 11:00 | ONSHORE | LA | 70390 | NAPOLEONVILLE | ASSUMPTION | MILEPOST | MP 34 | HOUMA TO WHITE CASTLE | 307-0300 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 8 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 7 |  | 0.185 | 52000 | API 5L | OTHER | UNKNOWN | UNKNOWN | COAL TAR | [28 empty] | 1940 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 4 | 6 | [7 empty] | CLASS 1 LOCATION | NO |  | 106 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 42000 | 37829.7872340426 | 35000 | 36437.4433363554 | 0 | 0 | 0 | 0 |  |  | 77000 | 55945.6061161372 | 74267.2305703979 | [8 empty] | 330 |  | 366 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 29115 | NO | YES | YES |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NOTIFICATION FROM THIRD PARTY INDICATING THEY WERE THE CAUSE OF THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | YES | [6 empty] | FARMER | FARM EQUIPMENT | AGRICULTURE | NO | [5 empty] | YES | 48 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | NATHAN L. GRAY JR. | SENIOR PIPELINE COMPLIANCE SPECIALIST | ngray@eprod.com | 985-493-4629 |  |  |  |  | NATHAN L. GRAY JR. | SENIOR PIPELINE COMPLIANCE SPECIALIST | 985-493-4629 | ngray@eprod.com | AT 10:51 AN ENTERPRISE PIPELINE TECHNICIAN (PT) WAS NOTIFIED BY A FARMER THAT THEY STRUCK AND RUPTURED AN ENTERPRISE PIPELINE WHILE SUBSOILING. THE PT NOTIFIED PIPELINE CONTROL CENTER AND CONFIRMED PRESSURE LOSS ON THE PIPELINE USING SCADA DATA. OPERATIONS PERSONNEL PROCEEDED TO ISOLATE THE PIPELINE SEGMENT. AT 11:58 HOURS IT WAS DETERMINED THE RUPTURE MET INCIDENT REPORTING CRITERIA AND THE NRC WAS NOTIFIED AT 12:02 HOURS. ALTERNATE GAS SUPPLIES WERE USED TO PROVIDE SERVICE TO LOCAL CUSTOMERS DOWNSTREAM OF THE RUPTURE. THE PIPELINE RUPTURE WAS SECURED AT 13:21 HOURS. THE PIPELINE WAS REPAIRED AND RETURNED TO SERVICE ON JUNE 27TH AT 14:00 HOURS. LADNR WAS NOTIFIED AT 12:03 HOURS ON JUNE 25, 2018. 48 HR. NRC NUMBER 1216494 ENTERPRISE PARTICIPATES IN THE CGA DIRT REPORTING PROGRAM AND WILL FILE A REPORT DIRECTLY TO CGA.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180076 | 30672 | 2018-07-20 11:31 | ORIGINAL FINAL | 18152 | SEA ROBIN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2018-06-22 15:35 | 2018 |  |  | 28.2141 | -91.7034 | 1216143 | 2018-06-22 16:01 |  | NATURAL GAS |  | 300 | 1836 | 0.1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-06-22 17:48 | 2018-06-25 10:06 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-06-22 15:35 | 2018-06-23 16:17 | OFFSHORE | [28 empty] | 260 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EUGENE ISLAND | 330 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12.75 |  | 0.438 | 52000 | UNKNOWN | OTHER | UNKNOWN | UNKNOWN | OTHER | MASTIC AND CONCRETE | [27 empty] | 1973 | 1973 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 318 |  | NO | NO | NO |  | 0 | 0 | 5502 | 5727.96609247507 | 898 | 808.836879432624 | 182292 | 189778.697733454 | 90506 | 94223.0641885766 | 0 | 0 |  |  | 279198 | 133832.148128144 | 290538.564893938 | [8 empty] | 930 |  | 1306 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 30729 | NO | YES |  | YES |  |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | PRODUCER PLATFORM PERSONNEL |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS TOO SMALL FOR SCADA TO DETECT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | LEAK AT THE 6 O'CLOCK POSITION. | YES | [7 empty] | YES | LOW FLOW CONDITIONS |  |  |  |  | YES | 6 O'CLOCK POSITION. | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | (713)857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | (713)857-5479 | nathan.hlavaty@energytransfer.com | 6/22/18 RECEIVED NOTIFICATION OF A POSSIBLE LEAK. NRC TELEPHONIC NOTIFICATION MADE AT 16:01 NRC#1216143. PHMSA AID NOTIFIED 17:11 6/23/18 DIVE SUPPORT VESSEL ON LOCATION. CONFIRMED SEA ROBIN PIPELINE AS THE SOURCE OF THE LEAK. PHMSA AID UPDATED. 6/24/18 48-HOUR UPDATE NRC NOTIFICATION MADE AT 08:30 NRC#1216256. PHMSA AID UPDATED. 6/25/18 REPAIR COMPLETED. LINE WAS RETURNED TO SERVICE
2021-02-26 10:37 | YES | NO | UNGS (Underground Natural Gas Storage) | 20180077 | 31443 | 2018-07-20 17:08 | SUPPLEMENTAL FINAL | 32416 | ARCADIA GAS STORAGE, LLC | 508 MINDEN ST. SUITE A | RUSTON | LA | 71270 | 2018-06-23 12:40 | 2018 |  |  | 32.529 | -92.9093 | 1216207 | 2018-06-23 13:28 |  | NATURAL GAS |  | 30000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | ONLY THE ALREADY SHUT IN GH-1 CAVERN WELL | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-06-23 12:40 | 2018-06-23 12:40 | ONSHORE | LA | 71001 | ARCADIA | BIENVILLE | SURVEY STATION NO. | CW GH-1 | ARCADIA GAS STORAGE LLC | CAVERN WELL GH-1 | NO | OPERATOR-CONTROLLED PROPERTY | BELOWGROUND STORAGE OR ABOVEGROUND STORAGE VESSEL, INCLUDING ATTACHED APPURTENANCE |  |  |  |  | NO | [22 empty] | INTRASTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | UNDERGROUND GAS STORAGE OR CAVERN | [38 empty] | 2013 |  | CARBON STEEL |  | OTHER | [8 empty] | CAVERN WELL GH-1 CASING COLLAPSE OF THE 8 5/8" HANGING STRING | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 120300 | 108355.319148936 | 4324914 | 4502537.39456029 | 250000 | 260267.452402538 | 0 | 0 |  |  | 4695214 | 2298589.97952329 | 4871160.16611176 | [8 empty] | 2300 |  | 3150 | OTHER | LAC 43 CHAPTER 3 SUBPART 29-M |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | WELL WAS ISOLATED FOR CONTRACTOR WORKOVER AT TIME; OPERATOR WITNESSED INCIDENT |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CAVERN WAS NOT BEING OPERATED AND WAS ISOLATED FROM THE CONTROL ROOM AT THE TIME OF THE INCIDENT DUE TO A WORK-OVER THAT WAS BEING PERFORMED BY OUTSIDE CONTRACTORS AND UNDER LOCAL CONTROLS AT THE TIME | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | SALT DOME STORAGE CAVERN CASING COLLAPSE WHILE CONTRACTOR WAS PERFORMING DOWN-HOLE SNUBBING WORK-OVER. | [147 empty] | RJ SHEFFIE | SAFETY SUPERVISOR | rj.sheffie@cardinalgs.com | (318)254-8951 |  |  |  |  | BOBBY RAINES | SR. VP OF ENGINEERING AND OPERATIONS | (713)3502506 | bobby.raines@cardinalgs.com | AN AGS CONTRACTOR WAS CONDUCTING A DOWN-HOLE SNUBBING WORKOVER IN THE CAVERN WELL GH-1 (SN 973567) TO RUN ADDITIONAL 8 5/8 INCH CASING IN THE 20 INCH PRODUCTION CASING UNDER 2300 PSI WELL PRESSURE. AT 12:40 PM, AN INITIAL BURST OCCURRED AND NATURAL GAS PROCEEDED TO EXIT THE 8 5/8 INCH CASING AND EVENTUALLY THE 20 INCH CASING. THE RIG OPERATORS EXITED THE SNUBBING WORK FLOOR, REACHED GROUND LEVEL SAFELY, AND THE SNUBBING BLOW-OUT PREVENTER (BOP) OPERATOR AND ONSITE SUPERVISOR CLOSED THE BLIND SHEAR RAM SECURING BOTH THE 8 5/8 INCH AND 20 INCH CASING AT 12:48 PM. ALL AGS PERSONNEL AND CONTRACTORS WERE ACCOUNTED FOR AND NO INJURIES WERE REPORTED. NATURAL GAS MONITORING WAS CONDUCTED TO ENSURE THAT THE GAS RELEASE WAS DISPERSED PRIOR TO RETURNING BACK TO THE SITE. THE WELL IS NOW SECURE AND WORK-OVER OPERATIONS HAVE RESUMED TO CONTINUE SNUBBING IN 8 5/8" CASING TO DE-WATER THE CAVERN WELL FOR NATURAL GAS STORAGE OPERATIONS. THE WELL WAS PLACED BACK IN SERVICE ON 08/04/2018. A ROOT CAUSE ANALYSIS HAS NOT BEEN PERFORMED.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180078 | 33253 | 2018-07-26 17:49 | SUPPLEMENTAL FINAL | 12642 | SPIRE GULF INC. | 2828 DAUPHIN STREET | MOBILE | AL | 36606 | 2018-06-26 13:39 | 2018 |  |  | 30.7718 | -88.0617 | 1216517 | 2018-06-26 16:33 |  | NATURAL GAS |  | 103 | 1108 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-06-26 22:00 | 2018-06-29 23:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 3 | 2018-06-26 13:39 | 2018-06-26 14:09 | ONSHORE | AL | 36611 | CHICKASAW | MOBILE | SURVEY STATION NO. | 767+06 | PHILLIPS | 759+12 TO 801+18 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | YES |  |  | YES | CASED | [18 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10 |  | 0.25 | 42000 | X-42 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | U.S. STEEL | COAL TAR | [28 empty] | 1975 | 1975 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 185 |  | NO | NO | NO |  | 0 | 0 | 3381 | 3519.85702629193 | 316 | 284.624113475177 | 240365 | 250236.744786945 | 53509 | 55706.6044424297 | 0 | 0 |  |  | 297571 | 142346.860167521 | 309747.830369142 | [8 empty] | 650 |  | 720 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 50712 | NO |  |  | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CAUSE OF LEAK WAS DUE TO OUTSIDE FORCE. THERE WAS NO NEED TO CONSIDER CONTROLLER ACTIONS OR CONTROL ROOM ISSUES. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | [103 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [261 empty] | LAURA KLECKLEY | MANAGER TIM CORROSION CONTROL PUBLIC AWARENESS | laura.kleckley@spireenergy.com | 2053262680 |  |  |  |  | CRAIG HOEFERLIN | VICE PRESIDENT OPERATIONS SERVICES | 3143492972 | craig.hoeferlin@spireenergy.com | AT THE STATED LOCATION, A DOWNED POWER LINE CAME IN CONTACT WITH THE VENT OF A 10" ENCASED STEEL PIPELINE CAUSING AN ELECTRICAL ARC INSIDE THE CASING AND A PINHOLE LEAK IN THE STEEL PIPELINE. THE LEAK RESULTED IN AN ABOVE-GROUND BRUSH FIRE THAT CAUSED NO ADDITIONAL DAMAGES. VALVES WERE CLOSED TO SHUT DOWN THE AFFECTED SECTION OF PIPELINE AND STOP THE RELEASE OF NATURAL GAS ON JUNE 26, 2018 AT 22:00. FINAL REPAIRS WERE COMPLETED ON DECEMBER 19, 2018. AN ADDITIONAL INVESTIGATION OF THE PIPE SEGMENT WAS PERFORMED AND IT CONFIRMED THAT A HIGH-VOLTAGE ELECTRICAL ARC INSIDE THE CASING WAS THE CAUSE OF THE LEAK. AT APPROXIMATELY 16:30 ON JUNE 26, 2018 , THE OPERATOR DETERMINED THAT THIS EVENT WOULD BE A REPORTABLE INCIDENT DUE TO ESTIMATING THE DAMAGE AND REPAIR COSTS TO EXCEED $50,000.
2021-02-26 10:37 | NO | NO | GG (Gas Gathering) | 20180079 | 31631 | 2018-07-26 20:49 | SUPPLEMENTAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2018-06-29 15:15 | 2018 |  |  | 28.4618 | -90.9087 | 1217170 | 2018-07-03 06:46 |  | NATURAL GAS |  | 48 | 895.5 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-12-14 16:00 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-06-29 15:15 | 2018-06-29 16:30 | OFFSHORE | [28 empty] | 125 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SHIP SHOAL | 233 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 |  | 0.438 | 42000 | AP5L | SEAMLESS |  | KAISER STEEL | ASPHALT | [28 empty] | 1983 | 1983 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 200 |  | NO | NO | NO |  | 0 | 0 | 1236 | 1286.76228467815 | 74 | 66.6524822695036 | 0 | 0 | 7200 | 7495.70262919311 | 50000 | 52053.4904805077 | COSTS UNKNOWN AT THIS TIME. PIPELINE ABANDONMENT TO TAKE PLACE POST REPORT. |  | 58510 | 27994.410449044 | 60902.6078766485 | [8 empty] | 606 |  | 1440 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | AUTOMATIC | 33053 | NO | [5 empty] | YES | UPSTREAM END OF PIPELINE IS SUB-SEA WITH NO PIGGING FACILITIES | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | YES | YES | YES | NO | NO | OTHER | THIRD PARTY HELICOPTER SPOTTED BUBBLES AND REPORTED IT |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  |  | YES |  |  |  | YES |  | YES | PREVIOUS LINE HISTORY | YES | [5 empty] | YES | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | STEPHANIE ROSS | PIPELINE SAFETY ENGINEER | stephanie.ross@williams.com | 713-215-4163 |  |  |  |  | CLINT RATKE | MANAGER PIPELINE SAFETY | 918-573-6724 | clint.ratke@williams.com | ON 06/29/2018 A THIRD PARTY HELICOPTER SPOTTED THE BUBBLES AND REPORTED THEM TO WGP PIPELINE CONTROL. PIPELINE CONTROL NOTIFIED WGP OPERATIONS. OPERATIONS FLEW OUT TO VERIFY COORDINATES. THE BUBBLES WERE IN THE VICINITY OF A WGP 16" PIPELINE. THE WGP SECURITY OPERATIONS CENTER WAS NOTIFIED OF THE POTENTIAL LEAK. AT 16:30 ON 6/29/18 WILLIAMS OPERATOR ARRIVED AND REPORTED THAT THERE WAS 606PSI ON THE PREVIOUSLY ISOLATED SECTION OF PIPELINE. DUE TO A LEAKING ISOLATION VALVE AND A BLEED VALVE THAT HAD BEEN CLOSED, THE PRESSURE ON THE LINE WAS CAUSED DUE TO THERMAL EXPANSION. HE THE STARTED BLOWING DOWN THE LINE DUE TO THE FINDINGS AND LEAK LOCATION. ON 6/30/2018 AT 16:30 THE BUBBLES STOPPED. AT 17:20 ON 6/30/2018 THE LINE WAS AT ZERO AND NOTIFICATIONS WERE MADE. THE LINE REMAINS OUT OF SERVICE AT THIS TIME. AWAITING ABANDONMENT PLAN. 12/25/18 LINE REMAINS OUT OF SERVICE. ABANDONMENT EXPECTED 2019/2020. 2/11/2019 PLEASE EXPLAIN HOW 606 PSI WAS ON THE PREVIOUSLY ISOLATED SECTION OF PIPE? THERE WAS A LEAKING ISOLATION VALVE AND A BLEED VALVE HAD BEEN CLOSED. DUE TO THE THERMAL EXPANSION, THIS CAUSED THE PRESSURE ON THIS ISOLATED SEGMENT OF PIPE. IS THE ENTIRE LINE BEING ABANDONED OR ARE THERE OTHER SECTIONS THAT MAY BE SUSCEPTIBLE? THE ENTIRE LINE IS PLANNED FOR ABANDONMENT. IS THE ENTIRE SECTION THAT WILL BE ABANDONED ISOLATED? YES, AND VENTED. WILL THERE BE ANY CHANGES TO THE INTERNAL CORROSION CONTROL PROGRAM? OPERATIONS HAS CHANGED THE TYPE OF CORROSION INHIBITOR USED PER REQUEST BY THE PIPELINE INTEGRITY GROUP. THEY ARE NOT SURE IF IT WOULD HAVE HELPED THIS SECTION, DUE IT TO NOT BEING PIGGABLE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180081 | 31025 | 2018-08-08 10:12 | SUPPLEMENTAL FINAL | 4900 | KINDER MORGAN TEJAS PIPELINE | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2018-07-10 17:29 | 2018 |  |  | 26.3548 | -98.4127 | 1217937 | 2018-07-10 18:24 |  | NATURAL GAS |  | 6270 | 1132 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-07-10 18:31 | 2018-07-31 19:10 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-07-10 17:29 | 2018-07-10 17:41 | ONSHORE | TX | 78574 | Not Within a Municipality | HIDALGO | MILEPOST | 120259.26 | STARR 8" | 423300 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 12 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8.625 |  | 0.25 | 35000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1977 | 1977 | CARBON STEEL |  | MECHANICAL PUNCTURE | 2.3 | 2.3 | [7 empty] | CLASS 1 LOCATION | NO |  | 216 |  | NO | NO | NO |  | 0 | 0 | 3170 | 3300.19129646419 | 17556 | 15812.8510638298 | 37700 | 39248.3318223028 | 4000 | 4164.27923844062 | 0 | 0 |  |  | 62426 | 37836.3095940793 | 62525.6534210374 | [8 empty] | 764 |  | 1318 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 60509 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | CONTROLLER |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | YES | [6 empty] | FARMER | FARM EQUIPMENT | AGRICULTURE | NO | [5 empty] | NO |  | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | SHELLEY BROMAN | PIPELINE ENGINEER | shelley_broman@kindermorgan.com | 713-420-4417 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | ON JULY 10, 2018 AT 17:29, KINDER MORGAN TEJAS PIPELINE (TEJAS) GAS CONTROL NOTICED A PRESSURE DROP ON THE STARR 8" LINE AND NOTIFIED FIELD PERSONNEL. AT 17:41, A LINE PATROLLER VISUALLY CONFIRMED THAT THERE WAS A GAS RELEASE. THE RELEASE RESULTED FROM A 3RD PARTY LINE STRIKE. A FARMER USING FARMING EQUIPMENT IN HIS FIELD PUNCTURED THE LINE CAUSING 6,270MCF OF GAS TO BE RELEASED UNINTENTIONALLY. THERE WERE NO INJURIES. THE FARMER DID NOT PLACE A ONE-CALL BEFORE STARTING HIS WORK. IN RESPONSE TO THIS EVENT, TEJAS ISOLATED THE PIPELINE AT 18:31 ON JULY 10. THE PIPELINE WAS THEN BLOWN DOWN. ON JULY 11, EXCAVATION OF THE LINE BEGAN. ON JULY 26, THE PUNCTURED SEGMENT OF THE PIPE WAS CUTOUT AND NEW PIPE WAS INSTALLED. ON JULY 27, THE LINE WAS RECOATED. ON JULY 31, THE LINE WAS PURGED, PACKED, AND RETURNED TO SERVICE. IN ORDER TO PREVENT A REOCCURRENCE, THE NEW PIPELINE WAS INSTALLED WITH A DEPTH OF COVER OF 36 INCHES.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180082 | 30778 | 2018-08-09 11:07 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2018-07-16 20:51 | 2018 |  |  | 42.0349 | -72.6335 | 1218573 | 2018-07-16 22:47 |  | NATURAL GAS |  | 8610 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-07-16 20:51 | 2018-07-16 22:35 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-07-16 20:51 | 2018-07-16 20:51 | ONSHORE | MA | 01001 | AGAWAM | HAMPDEN | MILEPOST | 261 | AGAWAM COMPRESSOR STATION NO. 261 | LINE 200 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | ESD SYSTEM | 1956 |  | CARBON STEEL |  | OTHER | [8 empty] | COMPRESSOR STATION EMERGENCY SHUTDOWN SYSTEM ACTIVATION/BLOWDOWN | CLASS 3 LOCATION | YES | METHOD2 | 613 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 24194 | 21791.7588652482 | 0 | 0 | 470 | 489.302810516772 | 0 | 0 |  |  | 24664 | 22817.1088113441 | 22281.061675765 | [8 empty] | 522 |  | 878 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | NO | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE EVENT WAS TRIGGERED COMPLETELY AT THE FIELD LOCATION WITH ABSOLUTELY NO CONTROLLER INVOLVEMENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | BLOCK VALVE IN ESD SYSTEM FAILED TO CLOSE | [161 empty] | KENNETH PETERS | SENIOR PIPELINE ENGINEER | ken_peters@kindermorgan.com | 2053257554 | 2053253787 |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | ON JULY 16, 2018 AT 8:51 PM EDT, AN EMERGENCY SHUTDOWN (ESD) WAS INADVERTENTLY ACTIVATED RESULTING IN THE BLOWDOWN OF THE TGP AGAWAM COMPRESSOR STATION NO. 261. VALVE BS-1, WHICH IS ONE OF THE STATION ESD ISOLATION VALVES, DID NOT CLOSE RESULTING IN AN EXTENDED VENTING PERIOD OF 33 MINUTES. AN ESTIMATED 8,610 MCF OF NATURAL GAS WAS RELEASED TO THE ATMOSPHERE. THE ESD ACTIVATED WHEN THE SYSTEM WAS RETURNED TO NORMAL MODE, HAVING PREVIOUSLY BEEN IN BYPASS MODE TO ALLOW FOR WELDING ACTIVITIES IN ONE OF THE COMPRESSOR BUILDINGS. INVESTIGATION REVEALED THAT POWER GAS TO THE OPERATOR FOR VALVE BS-1 WAS BLOCKED DUE TO A CLOSED VALVE IN THE OPERATOR'S GAS SUPPLY LINE, RESULTING IN THE ISOLATION VALVE FAILING TO CLOSE AND THE PROLONGED GAS RELEASE. A 48-HOUR UPDATE WAS PROVIDED TO THE NRC ON JULY 18, 2018 AT 3:07 PM EDT, NRC REPORT NO. 1218764, PROVIDING THE VOLUME OF GAS RELEASED WHICH WAS UNKNOWN AT THE TIME OF THE ORIGINAL NOTIFICATION ON JULY 16.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180084 | 31320 | 2018-08-20 10:03 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2018-07-02 23:43 | 2018 |  |  | 34.8476 | -82.0096 | 1218827 | 2018-07-19 09:39 |  | NATURAL GAS |  | 0.325 | 96.03 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-07-03 01:45 | 2018-09-06 21:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-07-02 23:43 | 2018-07-02 22:30 | ONSHORE | SC | 29369 | MOORE | SPARTANBURG | MILEPOST | 1205.89 | STATION 140 MAIN UNIT #14 | DISCHARGE HEADER | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | OTHER | MAIN UNIT #14 DISCHARGE HEADER |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | WELD/FUSION | [19 empty] | OTHER | CRACK ON 4"X24" WELDOLET ON MU #14 D.H. | [17 empty] | 1970 |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 468 |  | NO | NO | NO |  | 0 | 0 | 286 | 297.745965548504 | 1 | 0.900709219858156 | 164000 | 170735.448776065 | 1000 | 1041.06980961015 | 0 | 0 |  |  | 165287 | 78987.5617299907 | 172075.165260444 | [8 empty] | 720 |  | 800 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES |  |  |  |  | YES | MECHANICAL VIBRATION | [16 empty] | YES | [63 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | TIM HUGGINS | PRINCIPAL ENGINEER | timothy.n.huggins@williams.com | 713-215-2889 |  |  |  |  | CLINT RATKE | MANAGER PIPELINE SAFETY | 918-573-6724 | clint.ratke@williams.com | PLEASE REFERENCE THE ORIGINAL REPORT NO. 20180084-30821 FOR THE INITIAL INCIDENT REPORT INFORMATION. A BRIEF SUMMARY IS NOTED BELOW. ON JULY 2, 2018 AT APPROXIMATELY 10:00 PM (22:00), OPERATION TECHNICIAN WAS CALLED OUT TO STATION 140 ON REPORT OF MAIN UNITS (MUS) 14 AND 15 FALLING OFFLINE. UPON ARRIVAL AT APPROXIMATELY 10:30 PM (22:30), TECHNICIAN REVIEWED ALARM LOGS IN CONTROL ROOM, AND INSPECTED MUS 14 AND 15, AND IDENTIFIED A CRACK ON THE MU 14 DISCHARGE HEADER AT THE 4' BLOWDOWN PIPING CONNECTION. IDENTIFIED AT APPROXIMATELY 11:43 PM (23:43). OPERATION TECHNICIAN CONTACTED OPERATIONS MANAGER TO NOTIFY OF LEAK, CONTACTED PIPELINE CONTROL, AND CONTACTED ADDITIONAL TECHNICIANS TO COME HELP ISOLATE AND BLOWDOWN MU 14 PIPING. UPON ARRIVAL OF BACKUP SUPPORT, PROCEEDED TO ISOLATE MU 14 AND PERFORM REMOTE ESD OF MU 14 PIPING. (APPROXIMATELY 1:45AM (01:45) ON JULY 3) REPAIR OPTIONS WERE DETERMINED TO EXCEED $50,000 ON JULY 19, 2018 AND SECURITY OPERATIONS CENTER (SOC) WAS INSTRUCTED TO CONTACT THE NRC FOR A DOT REPORTABLE INCIDENT. THE FIRST INITIAL NRC REPORT# 1218827 ON JULY 19 WAS IN ERROR (REPORTED INCIDENT AS 'FIXED'). PHMSA REQUESTED TO CORRECT THE REPORT TO INCIDENT AS 'PIPELINE' UNDER NRC REPORT# 1218832. A 48-HOUR UPDATE WAS SUBMITTED UNDER NRC REPORT# 1219242 ON JULY 23, 2018. ON AUGUST 21, 2018, PHMSA REQUESTED CORRECTIONS TO THE INITIAL INCIDENT REPORT AND ARE REFLECTED ON THIS FINAL INCIDENT REPORT. A STATION OUTAGE WAS REQUIRED TO REPAIR THE DISCHARGE HEADER AND SAFELY INSTALL THE NEW REPLACEMENT TEE. THE REPAIR WAS COMPLETED, AND MU 14 WAS RETURNED TO SERVICE ON SEPTEMBER 6, 2018 AT APPROXIMATELY 9:00 PM EST (21:00). THE FINAL INFORMATION WAS GATHERED AND VERIFIED, AND THIS FINAL INCIDENT REPORT WAS SUBMITTED ON DECEMBER 13, 2018
2021-02-26 10:37 | YES | YES | GT (Gas Transmission) | 20180085 | 32215 | 2018-08-29 17:47 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2018-08-01 12:30 | 2018 |  |  | 31.8772 | -101.8162 | 1220198 | 2018-08-01 13:29 |  | NATURAL GAS |  | 1119 | 0 | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES | 1 | 0 | 0 | 3 | 0 | 4 |  | YES |  | 2018-08-01 12:16 | 2018-08-10 15:20 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 0 | 2018-08-01 12:30 | 2018-08-01 12:20 | ONSHORE | TX | 79706 | Not Within a Municipality | MIDLAND COUNTY | MILEPOST | MP 3+0889 | LINE 3130 | TEX-HARVEY - AKA: JAMESON POOL | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 26 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 |  | 0.25 | 35000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1953 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 90 | 30 |  | CLASS 1 LOCATION | NO |  | 257 |  | NO | NO | NO |  | 500 | 520.534904805077 | 0 | 0 | 3286 | 2959.7304964539 | 68000 | 70792.7470534905 | 5000 | 5205.34904805077 | 18000 | 18739.2565729828 | FIELD INVESTIGATION: LABOR, SURVEYING, SAMPLING/ANALYSIS, AND TRAVEL EXPENSES. |  | 94786 | 46794.3709504918 | 98217.618075783 | [8 empty] | 765 |  | 855 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 23813 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER'S ACTIONS HAD NO ROLE IN THE CAUSES(S) OR SEVERITY OF THE ACCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [103 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [261 empty] | STEPHEN R. DINES | ENGINEER - CODES AND STANDARDS | stephen_dines@kindermorgan.com | 719 329-5633 |  |  |  |  | JAIME A. HERNANDEZ | DIRECTOR OF ENGINEERING CODES AND STANDARDS | 713 369-9443 | jaime_hernandez@kindermorgan.com | ON AUGUST 1, 2018 AT APPROXIMATELY 11:14 AM CT, EPNG GAS CONTROL RECEIVED A REPORT OF A FIRE NEAR FM 1379 (I.E., FARM TO MARKET ROAD NO. 1379), WHICH WAS LATER IDENTIFIED TO BE IN THE VICINITY OF ITS L3130 NATURAL GAS PIPELINE IN MIDLAND COUNTY, TEXAS. SHORTLY BEFORE 11:51 AM CT, EPNG OPERATIONS CONFIRMED THE PRESENCE OF FLAMES ON THE EPNG RIGHT-OF-WAY (ROW) AND BY 12:16 PM CT HAD ISOLATED THE L3130 VALVE SECTION AND MONITORED PRESSURES ON THE ISOLATED SEGMENT AND CONFIRMED THAT THE PIPELINE WAS HOLDING PRESSURE. AN EPNG OPERATIONS SUPERVISOR WENT TO THE SITE OF THE RUPTURE AT 12:20 PM CT AND VISUALLY CONFIRMED THAT IT WAS THE NAVITAS MIDSTREAM PARTNERS' LINE THAT HAD RUPTURED. EPNG WAS GETTING READY TO BLOW DOWN ITS LINE WHEN THE RUPTURE OF THE EPNG LINE OCCURRED. AT 12:33 PM CT, EPNG'S RTU DATA LOG AT JAMESON CHECK METER ON L3130 SHOWED A "HIGH-HIGH" ALARM. DURING THE INVESTIGATION IT WAS DETERMINED THAT THE RUPTURE OCCURRED AT APPROXIMATELY 12:30 PM CT. AT APPROXIMATELY 12:44 PM CT, EPNG GAS CONTROL RECEIVED A CALL FROM THE EPNG OPERATIONS AT THE SITE STATING THAT ITS LINE HAD BEEN COMPROMISED. THREE NAVITAS EMPLOYEES, A NAVITAS CONTRACTOR EMPLOYED BY QIS AND THE EPNG OPERATIONS SUPERVISOR WERE ADMITTED TO THE HOSPITAL. ONE NAVITAS EMPLOYEE LATER DIED FROM HIS INJURIES. TWO FIREFIGHTERS WERE TREATED AND RELEASED AT THE HOSPITAL THE SAME DAY, AS WAS ONE OF THE NAVITAS EMPLOYEES. EPNG NOTIFIED THE NRC (NO. 1220198) AT 13:29 PM CT OF THE INCIDENT INVOLVING EPNG'S L3130 WITH AN UNKNOWN QUANTITY OF GAS RELEASED AND POSSIBLY CAUSED BY A FIRE ON A THIRD PARTY PIPELINE WITHIN THE ROW. THE NRC LOGGED THE REPORT AT 13:46 PM CT. EPNG PROVIDED A 48-HOUR NOTICE TO THE NRC (NO. 1220423) ON AUGUST 3, 2018 AT 11:51 CT TO UPDATE INFORMATION ON THE LOCATION OF THE INCIDENT, ESTIMATED VOLUME OF UNINTENTIONAL NATURAL GAS RELEASED, AND A REPORT RECEIVED FROM THE OPERATOR OF THE THIRD PARTY PIPELINE THAT ONE OF ITS EMPLOYEE'S INJURIES WERE FATAL. EPNG ISSUED ANOTHER REVISED NOTICE NRC (NO. 1220429) TO CORRECT THE TOTAL VOLUME OF UNINTENTIONAL NATURAL GAS RELEASED. THE CORRECT RELEASE VOLUME WAS 1,060 MSCF AT THE TIME OF THE 48 HOUR NOTICE. THE INVESTIGATION UTILIZED THE METALLURGICAL DATA COLLECTED FROM THE EVENT AND THE DNV SYSTEMATIC CAUSE ANALYSIS TECHNIQUE (SCAT) ROOT CAUSE ANALYSIS TOOL PER KINDER MORGAN/EPNG PROCEDURES TO DETERMINE BASIC CAUSE, ROOT CAUSE AND CONTRIBUTING FACTORS. BASED ON THE INVESTIGATION REPORT, WHICH WAS PROVIDED TO PHMSA, THE BASIC/ROOT CAUSES WERE DETERMINED TO BE "12.1 INADEQUATE PREVENTATIVE MAINTENANCE" - PER THE METALLURGY FINDINGS, THE NAVITAS LINE WAS LEAKING EVEN PRIOR TO THE RUPTURE. NAVITAS HAD NOT IDENTIFIED THE LEAK, THE SELECTIVE ERW SEAM CORROSION, NOR CONDUCTED REPAIRS/MAINTENANCE AND . "14.4 INADEQUATE MONITORING OF COMPLIANCE" - AFTER THE NAVITAS LINE RUPTURED, NAVITAS PERSONNEL DID NOT BELIEVE THAT THE NAVITAS LINE WAS BURNING AND ARGUED WITH REPRESENTATIVES FROM KINDER MORGAN/EPNG, WHO TRIED TO TELL NAVITAS PERSONNEL ON THE SCENE THAT IT WAS THE NAVITAS LINE OBSERVED TO BE ON FIRE. THE INVESTIGATION ALSO DETERMINED THAT THE INITIAL RUPTURE LOCATION WAS AT THE NAVITAS H-LOOP (NPS 6) LINE AND IT CONTINUED TO BURN FOLLOWING THE INCIDENT UNTIL THE EVENING OF AUGUST 3, 2018. DURING THIS TIME, NAVITAS REPORTED THAT THE SOURCE OF THE FUEL FOR THE FIRE COULD NOT BE CONFIRMED. NAVITAS THOUGHT THE CAUSE MAY HAVE BEEN A LEAKING TAP VALVE, AND SO THEY WERE VERIFYING THAT THEIR VALVES WERE NOT LEAKING; ALSO NAVITAS LOOKED FOR POSSIBLE ADDITIONAL TAPS (INTERCONNECTS) THAT WERE NOT ON THEIR MAPS AND MAY HAVE BEEN FUELING THE FIRE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180086 | 31505 | 2018-08-29 18:22 | SUPPLEMENTAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2018-07-30 15:15 | 2018 |  |  | 30.0586 | -90.8717 | 1219961 | 2018-07-30 15:53 |  | NATURAL GAS |  | 0 | 36 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE LEAKING HEADER WAS BYPASSED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-07-30 15:15 | 2018-07-30 15:20 | ONSHORE | LA | 70086 | ST. JAMES | ST. JAMES | MILEPOST | 66.22 | SCHRIEVER | 62-30 VALVE SITE | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 36 |  | 0.5 |  | TBD | OTHER | WILL UPDATE WITH SUPPLEMENTAL | TBD | OTHER | OPERATIONS TO VERIFY | [27 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | TBD | [5 empty] | CLASS 1 LOCATION | NO |  | 783 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 50000 | 52053.4904805077 | 0 | 0 | 0 | 0 | COSTS CURRENTLY UNKNOWN BUT EXPECTED TO EXCEED $50K |  | 50000 | 23893.9256572983 | 52053.4904805077 | [8 empty] | 760 |  | 995 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 96 | NO | YES |  |  |  |  | YES | HEADER DESIGN WITH NO FLANGES TO INSPECT | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [146 empty] | STEPHANIE ROSS | PIPEINE SAFETY ENGINEER | stephanie.ross@williams.com | 713-215-4163 |  |  |  |  | CINT RATKE | MANAGER PIPELINE SAFETY | 918-573-6724 | clint.ratke@williams.com | ON MONDAY JULY 30, A LEAK WAS DISCOVERED AT THE 62-30 VALVE SITE, BY A CONTRACTOR WORKING FOR WILLIAMS AT 15:15. HE IMMEDIATELY NOTIFIED MANAGER OF OPERATIONS WHICH INTERN NOTIFIED OPERATIONS AT STATION 63 TO INVESTIGATE. AFTER INVESTIGATION, IT WAS DEEMED A NATURAL GAS LEAK ON THE 36 INCH HEADER SYSTEM UNDER GROUND. THE FLOW WAS REDIRECTED FROM A LINE TO B LINE AND HEADER SYSTEM WAS ISOLATED, LOTO AND BLOWN DOWN. AFTER HEADER WAS BLOWN DOWN, IT WAS CONFIRMED THAT LEAK NO LONGER PRESENT. INVESTIGATION IS ONGOING. THE REPAIR COSTS ARE UNKNOWN AT THIS TIME BUT EXPECT TO EXCEED $50K. OPERATIONS IS WORKING TO DETERMINE IF WE REPAIR IN THE NEAR FUTURE OR DELAY UNTIL PROJECTS SLATED IN 2019 AND 2021 TO BRING THIS SITE ABOVE GROUND. INITIAL NRC REPORT #1219961 ON 7/30/2018 AT 15:53. FOLLOWUP NRC REPORT #1220196 ON 8/1/2018 AT 14:22. A SUPPLEMENTAL/FINAL REPORT WILL BE SUBMITTED WHEN ADDITIONAL COST AND PIPE INFORMATION IS KNOWN AND/OR THE REPAIR IS COMPLETED. 1/17/2019: HEADER SYSTEM IS STILL ISOLATED UNDERGROUND. CAUSE STILL UNKNOWN UNTIL REPLACEMENT (TO BE COMPLETED IN 2019).
2021-02-26 10:37 | YES | NO | UNGS (Underground Natural Gas Storage) | 20180087 | 31099 | 2018-09-04 09:20 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2018-08-02 15:17 | 2018 |  |  | 38.3555 | -98.1677 | 1220341 | 2018-08-02 15:51 |  | NATURAL GAS |  | 17020 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-08-03 16:34 | 2018-08-03 17:04 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-08-02 15:17 | 2018-08-02 15:17 | ONSHORE | KS | 67554 | Not Within a Municipality | RICE | MILEPOST | WELL 35-08 | WELL 35-08 | PULLIAM | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1975 |  | CARBON STEEL |  | LEAK |  |  | OTHER | 1-INCH VALVE KNOCKED OFF | [5 empty] | CLASS 1 LOCATION | NO |  | 45 |  | NO | NO | NO |  | 5000 | 5205.34904805077 | 0 | 0 | 50039 | 45070.5886524823 | 600 | 624.641885766092 | 60000 | 62464.1885766092 | 0 | 0 |  |  | 115639 | 78075.5562306969 | 113364.768162908 | [8 empty] | 950 |  | 1440 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION IN STORAGE FIELD | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 2 | 0 | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OPERATOR'S CONTRACTOR | [260 empty] | JOHN A. GORMLEY | SR. CORROSION SPECIALIST - PIPELINE SAFETY | john.gormley@nngco.com | 4023987494 |  |  |  |  | THOMAS CORRELL | VP PIPELINE SAFETY AND RISK | 4023987715 | thomas.correll@nngco.com | ON AUGUST 2, 2018 AT APPROXIMATELY 15:17 A CONTRACTOR WORKING FOR NORTHERN NATURAL GAS COMPANY MOVED A FORK LIFT STYLE PIECE OF EQUIPMENT TOO CLOSE TO WELL 35-08 AND BROKE OFF A 1-INCH VALVE AND NIPPLE ATTACHED TO THE CASING BELOW THE MASTER VALVE. THE ESCAPING GAS BLEW HORIZONTALLY ABOUT 1-FOOT ABOVE THE GROUND IN A NORTHERLY DIRECTION. A WELL CONTROL SPECIALIST WAS CALLED IN AND THEY WERE ABLE TO PUMP WATER INTO A 2-INCH VALVE ON THE OPPOSITE SIDE OF THE WELL TO ESSENTIALLY "KILL" IT. THE VALVE AND NIPPLE WAS REPLACED IMMEDIATELY AFTER THE KILL.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180088 | 31836 | 2018-09-04 14:40 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2018-08-06 14:42 | 2018 |  |  | 36.8512 | -99.7584 | 1220709 | 2018-08-06 15:26 |  | NATURAL GAS |  | 81600 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-08-06 15:58 | 2018-08-10 10:50 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-08-06 14:42 | 2018-08-06 15:32 | ONSHORE | OK | 73834 | Not Within a Municipality | HARPER | SURVEY STATION NO. | 100 / 4949+42 | LINE N | OKLAHOMA HUGOTON 26" | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 26 |  | 0.25 | 56000 | NON-STANDARD | FLASH WELDED |  | A.O. SMITH | COAL TAR | [28 empty] | 1943 | 1943 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 480 | 26 |  | CLASS 1 LOCATION | NO |  | 496 |  | NO | NO | NO |  | 5000 | 5205.34904805077 | 0 | 0 | 198288 | 178599.829787234 | 233000 | 242569.265639166 | 5000 | 5205.34904805077 | 0 | 0 |  |  | 441288 | 301287.031885959 | 431579.793522502 | [8 empty] | 750 |  | 765 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 58000 | YES | [7 empty] | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 1 | 0 | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED |  | YES | [15 empty] | STRESS CORROSION CRACKING | [5 empty] | YES | [63 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | JOHN ERIC GLAHN | PIPELINE COMPLIANCE ENGINEER | john.glahn@sscgp.com | 270-852-4414 | 270-852-5016 |  |  |  | SHAWN PATTERSON | VP AND CHIEF OPERATIONS OFFICER | 270-852-4670 | shawn.patterson@sscgp.com | AT 2:42 PM LOCAL TIME ON 8/6/2018 SOUTHERN STAR CENTRAL GAS PIPELINE (SSCGP) RECEIVED A CALL FROM HARPER COUNTY, OKLAHOMA, EMERGENCY RESPONDERS ABOUT THE SOUND OF A GAS LEAK. SSCGP SCADA CONTROLLER IMMEDIATELY NOTICED THE PRESSURE DROPPING ON LINE N. SSCGP CALLED A SIGNIFICANT EVENT AND DISPATCHED THE FIELD CREWS TO THE LOCATION. SSCGP CALLED THE NRC AT 3:26 PM. A SEPARATE CALL WAS MADE TO PHMSA AT 3:43 PM AND A FOLLOW UP CALL WAS MADE AT 4:07 PM. THE FIELD CREW ARRIVED AT THE BUFFALO ML GATE WEST OF THE RUPTURE SITE AND HAD IT CLOSED BY 3:32 PM. THEY PROCEEDED TO THE DOBY ML GATE APPROXIMATELY 11 MILES TO THE EAST OF THE BUFFALO MLG AND HAD IT CLOSED BY 3:51 PM. THE FIELD CREW THEN PROCEEDED TO THE RUPTURE SITE, ARRIVED AT 3:58 PM AND CONFIRMED THAT THE RUPTURE WAS EFFECTIVELY ISOLATED. LOCAL EMERGENCY RESPONDERS ARRIVED ON SITE AT APPROXIMATELY 3:30 PM AND HAD THE AREA SECURED BY 3:58 PM. PHMSA INVESTIGATORS EXAMINED THE SITE BEFORE ANYTHING WAS DISTURBED. AFTER BEING GIVEN PERMISSION, THE DAMAGED SECTION OF PIPE WAS SHIPPED TO G2MT LABORATORIES IN HOUSTON, TEXAS FOR METALLURGICAL EXAMINATION. SSCGP THEN MADE ARRANGEMENTS TO REPAIR THE DAMAGE AND PLACED THE AFFECTED SECTION OF LINE N BACK IN SERVICE ON 8/10/2018 AT 10:50 AM LOCAL TIME UNDER A VOLUNTARY 20% PRESSURE REDUCTION. 112 FEET OF 26" 0.375" WALL X70 PIPE WAS INSTALLED TO MAKE THE PERMANENT REPAIR. THE AFFECTED SECTION OF LINE N WILL CONTINUE TO BE OPERATED AT A 20% PRESSURE REDUCTION PENDING THE RESULTS OF FURTHER INVESTIGATION. THE INITIAL INCIDENT REPORT INDICATED HYDROGEN STRESS CRACKING AS THE CAUSE BASED ON INITIAL ANALYSIS BY G2MT. KEIFNER AND ASSOCIATES PERFORMED AN ADDITIONAL METALLURGICAL EXAMINATION AND SUBMITTED THE DRAFT RESULTS TO SSCGP ON 2/26/2019. THE KEIFNER METALLURGICAL REPORT FINDS THE CAUSE OF THE RUPTURE WAS HIGH PH STRESS CORROSION CRACKING. PART G HAS BEEN REVISED TO REFLECT THE FINDINGS OF THE KEIFNER METALLURGICAL EXAMINATION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180089 | 30907 | 2018-09-05 18:14 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2017-07-08 11:15 | 2017 |  |  | 35.6653 | -119.8504 | 1183501 | 2017-07-08 17:30 |  | NATURAL GAS |  | 2000 | 2800 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2017-07-08 23:00 | 2017-07-09 04:40 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2017-07-08 11:16 | 2017-07-08 12:45 | ONSHORE | CA | 93249-0000 | LOST HILLS | KERN | MILEPOST | 30.04 | LINE 85 NORTH | 1586+35 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 8 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 26 |  | 0.25 | 30000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | ASPHALT | [28 empty] | 1931 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 0.2 | 0.2 | [7 empty] | CLASS 1 LOCATION | NO |  | 359 |  | NO | NO | NO |  | 0 | 0 | 16800 | 17869.0626157836 | 12000 | 10990.3846153846 | 262515 | 279220.057891812 | 200 | 212.726935902186 | 0 | 0 |  |  | 291515 | 147863.623599909 | 308292.232058882 | [8 empty] | 384 |  | 400 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL |  | NO | YES | YES | YES |  |  |  |  | YES | YES | [5 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT CALLED IN IMMEDIATELY BY DAMAGING PARTY. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | YES | [6 empty] | FARMER | FARM EQUIPMENT | AGRICULTURE | NO | [5 empty] | NO |  | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | ALEXANDER HUGHES | PIPELINE SAFETY AND COMPLIANCE ADVISOR | ahughes@semprautilities.com | 949 697 2539 |  |  |  |  | ALEXANDER HUGHES | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 949 697 2539 | ahughes@semprautilities.com | THIS INCIDENT WAS ORIGINALLY REPORTED ON FORM F7100.1 - 20170069-16615; THIS IS THE SAME INCIDENT, NOW BEING ENTERED CORRECTLY ON A FORM F7100.2. ON 7/8/17, A 3RD PARTY CONTRACTOR WAS DISCING THE LOCATION OF THE SOCALGAS PIPELINE FOR AGRICULTURE WORK. THE DISC IMPLEMENT STRUCK A 1 INCH FITTING ON TOP OF THE GAS MAIN. THE TOP OF THE FITTING WAS SHEARED OFF, CAUSING THE RELEASE OF GAS. SOCALGAS CREWS RESPONDED, ISOLATED THE SECTION OF MAIN, AND CONTROLLED THE GAS BY 23:00 OF THE INCIDENT DATE. PERMANENT REPAIRS WERE COMPLETED AND THE SECTION RE-ENERGIZED BY 04:40 ON 07/09/17. INVESTIGATION OF THE INCIDENT SHOWED THERE WAS NO VALID USA TICKET. THIS INCIDENT WAS REPORTED TO THE DOT AND CPUC DUE TO DAMAGE COSTS EXCEEDING $50,000. FOR ANY FURTHER QUESTIONS, PLEASE DON'T HESITATE TO CONTACT ALEXANDER HUGHES AT (949)697 2539.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180090 | 30946 | 2018-09-06 20:23 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2018-08-11 09:03 | 2018 |  |  | 30.4351 | -92.8763 | 1221207 | 2018-08-11 09:11 |  | NATURAL GAS |  | 3788 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-08-11 08:30 | 2018-08-11 16:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-08-11 08:28 | 2018-08-11 08:28 | ONSHORE | LA | 70648 | Not Within a Municipality | JEFFERSON DAVIS | MILEPOST | MP 0; 0+00 | STATION 823 - KINDER COMPRESSOR STATION (YARD) | LINE 801; STATION 823-1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1955 |  | CARBON STEEL |  | LEAK |  |  | OTHER | VALVE 823-AD1 OFF SET LIMITS | [5 empty] | CLASS 1 LOCATION | NO |  | 633 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 10830 | 9754.68085106383 | 2000 | 2082.13961922031 | 3000 | 3123.20942883046 | 0 | 0 |  |  | 15830 | 12502.5131331057 | 14960.0298991146 | [8 empty] | 801 |  | 936 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | HEAD END UNLOADER VALVE STEM LEAK AND YARD VALVE DID NOT FULLY CLOSE DURING THE ESD PROCESS | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | APPURTENANCE FAILURE | [21 empty] | YES | HEAD END UNLOADER; VALVE 823-AD1; PLEASE SEE NARRATIVE | [161 empty] | WM. MARTIN MULLER | SPECIALIST - PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205-325-3863 | 205-325-3508 |  |  |  | JAIME HERNANDEZ | DIRECTOR ENGINEERING CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | IN THE TGP STATION 823 A-1 COMPRESSOR BUILDING, A GAS DETECTOR UNIT PROVIDE ALARM AT 20% LFL. THE ON DUTY OPERATOR SAFELY ENTERED THE BULDING TO STOP UNIT #4A BUT THE GAS DETECTOR UNIT SENSED 40% LFL AND INITIATED A COMPLETE STATION ESD. THE UNIT #4A, #2 CYLINDER HEAD END UNLOADER VALVE STEM HAD A PACKING LEAK OF APPROXIMATELY 5 MCF. DURING THE STATION ESD PROCESS WHICH STOPPED THE UNIT, THE PIPING SYSTEM DID NOT FULLY ISOLATE AS VALVE 823-AD1 DID NOT COMPLETELY CLOSE. OPERATION STAFF DETERMINED IT WAS SAFE TO CLOSE VALVE 823-AD1 THEREFORE TERMINATING THE RELEASE OF NATURAL GAS TO ATMOSPHERE. NOTIFICATIONS WERE MADE TO THE NRC AND TO THE LOUISIANA STATE POLICE AS REQUIRED. INVESTIGATION FOUND THE CYLINDER HEAD END UNLOADER POCKET PISTON SET SCREW HAD BACKED OUT ALLOWING A NUT TO LOOSEN; PULSATION CAUSED THE POCKET PISTON TO DISENGAGE; THE MISSING PISTON ALLOWED THE VALVE STEM TO OVER TRAVEL ALLOWING GAS TO VENT AROUND THE GLAND AND OUT TO ATMOSHPERE THROUGH AN UNLOADER WEEP HOLE. VALVE 823-AD1, SLIGHTLY OFF CLOSE LIMITS, ALLOWED ADDITIONAL VENTING OF NATURAL GAS BEFORE OPERATION STAFF SAFELY CLOSED THE VALVE. THE VALVE SET LIMITS HAVE BEEN RESET AND THE VALVE ASSEMBLY INPSECTED. THE HEAD END UNLOADER HAS BEEN REPAIRED. INSPECTION OF OTHER HEAD END UNLOADER COMPONENTS FOUND TWO OTHER UNITS WITH LOOSE SET SCREWS; THESE UNITS HAVE ALSO BEEN REPAIRED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180091 | 32088 | 2018-09-07 16:05 | SUPPLEMENTAL FINAL | 31439 | HARDEE POWER PARTNERS LTD | 6695 COUNTY RD 663 N | BOWLING GREEN | FL | 33834 | 2018-08-07 12:00 | 2018 |  |  | 27.6388 | -81.9583 | NRC NOTIFICATION NOT REQUIRED |  |  |  |  | 0 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-08-07 12:00 | 2018-08-14 15:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2018-08-07 12:00 | 2018-08-07 12:00 | ONSHORE | FL | 33834 | Not Within a Municipality | HARDEE | MILEPOST | 320 | HPP/GULFSTREAM STATION 320 | 320 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | INSTRUMENTATION | [38 empty] | 2003 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | INSTRUMENT TRANSDUCER | LEAK |  |  | OTHER | TRANSDUCER NORM BLEED IGNITED | [5 empty] | CLASS 1 LOCATION | NO |  | 259 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 3000 | 3123.20942883046 | 0 | 0 | 0 | 0 | THE INVESTIGATION COST IS NOT INCLUDED (INVESTIGATION EST AT 11K) |  | 3000 | 1433.6355394379 | 3123.20942883046 | [8 empty] | 465 |  | 974 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE TRANSDUCER FAILURE IN THE FIELD. THE FAILURE OCCURRED DURING A TIME WHEN THE YARD WAS NOT BEING DISPATCHED. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [146 empty] | MICHAEL MCMULLEN | ENGINEER | mmcmullen@invenergyllc.com | 863-375-3266 | 863-375-2092 |  |  |  | ALEC GEORGE | VICE PRESIDENT | 312-582-1415 | ageorge@invenergyllc.com | ON 8/7/2018 AT APPROXIMATELY 12:00 NOON, HARDEE POWER PARTNERS (HPP) DISCOVERED AN ELECTRONIC INSTRUMENT TRANSDUCER ON FIRE (INCIDENT) IN THE HPP PORTION OF GAS YARD 320 ON REGULATING RUN #2. THE AREA WAS SECURED AND THE SMALL FIRE EXTINGUISHED WHEN THE GAS SUPPLY TO THE INSTRUMENT TREE WAS ISOLATED. THE GAS YARD SERVES TO BACK UP HPP'S MAIN GAS SUPPLIER AND WAS NOT DISPATCHED AT THE TIME OF INCIDENT; HOWEVER, BECAUSE OF THE FAILED TRANSDUCER, THE STATION WAS FLOWING GAS FOR CONSUMPTION IN THE POWER PLANT. IT WAS THIS FLOW INDICATION THAT WAS NOTICED BY THE HPP CONTROL ROOM OPERATOR SHORTLY BEFORE NOON THAT BEGAN THE INVESTIGATION THAT LED TO THE DISCOVERY OF THE TRANSDUCER FAILURE. DUE TO THE TRANSDUCER FAILURE, THE HPP FLOW COMPUTER AT 320 WAS NOT ABLE TO CONTROL THE FLOW VALVE; AS A RESULT, THE LOCAL BECKER PNEUMATIC PILOT REGULATOR WAS CONTROLLING THE FLOW VALVE, BY DESIGN, IN PRESSURE CONTROL AND ENSURED THAT FROM THE TIME OF FAILURE UNTIL THE TIME THAT THE SYSTEM WAS ISOLATED BY HPP, THE DISCHARGE PRESSURE OF THE REGULATING STATION WAS CONTROLLED TO THE BECKER PILOT REGULATOR SETPOINT. FOLLOWING THE INCIDENT, THE STATION WAS VERIFIED CLEARED FOR SERVICE ON RUN#1 AND MADE AVAILABLE 08/14/18 FOR RUN 1 OPERATION. THE CAUSE OF THE INCIDENT (IGNITION OF THE TRANSDUCER NORMAL BLEED OFF) HAS BEEN INVESTIGATED BY HPP, HOWEVER NO IGNITION SOURCE PATH, NO DEFICIENCIES IN ISOLATION NOR DEFICIENCIES IN GROUNDING WERE DISCOVERED TO EXPLAIN THE IGNITION PATH. HPP IS SELF REPORTING THIS INCIDENT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180092 | 30926 | 2018-09-11 12:00 | ORIGINAL FINAL | 18152 | SEA ROBIN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2018-08-20 19:00 | 2018 |  |  | 28.2141 | -91.7034 | 1222188 | 2018-08-20 19:46 |  | NATURAL GAS |  | 300 | 1906 | 0.1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-08-20 19:00 | 2018-08-25 01:39 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-08-20 19:00 | 2018-08-22 13:00 | OFFSHORE | [28 empty] | 260 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EUGENE ISLAND | 330 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12.75 |  | 0.438 | 52000 | UNKNOWN | OTHER | UNKNOWN | UNKNOWN | OTHER | MASTIC AND CONCRETE | [27 empty] | 1973 | 1973 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 318 |  | NO | NO | NO |  | 0 | 0 | 5508 | 5734.21251133273 | 867 | 780.914893617021 | 209454 | 218056.235902085 | 90000 | 93696.2828649139 | 0 | 0 |  |  | 305829 | 146544.397055098 | 318267.646171949 | [8 empty] | 920 |  | 1306 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 30729 | NO | YES |  | YES |  |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | PRODUCER PLATFORM PERSONNEL |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS TOO SMALL FOR SCADA TO DETECT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | LEAK AT THE 6 O'CLOCK POSITION. | YES | [7 empty] | YES | LOW FLOW CONDITIONS |  |  |  |  | YES | 6 O'CLOCK POSITION | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | (713)857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | (713)857-5479 | nathan.hlavaty@energytransfer.com | 8/20/18 RECEIVED NOTIFICATION OF A POSSIBLE LEAK. NRC TELEPHONIC NOTIFICATION MADE AT 19:46 NRC#1222188. PHMSA AID NOTIFIED 20:59 8/21/18 PHMSA AID UPDATED 18:53, VESSEL MOBILIZING, NO VISIBLE SHEEN. 8/22/18 48-HOUR UPDATE NRC NOTIFICATION MADE AT 14:58 NRC# 1222374. DIVE SUPPORT VESSEL ON LOCATION. CONFIRMED SEA ROBIN PIPELINE AS THE SOURCE OF THE LEAK. 8/23/18 PHMSA AID UPDATED AT 07:27 8/24/18 NRC UPDATE MADE AT 09:38 NRC# 1222547. 8/25/18 PHMSA AID UPDATED 09:28, THE REPAIRS ARE COMPLETED, LINE HAS BEEN RETURNED TO SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180093 | 32861 | 2018-09-12 11:38 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | PG&E - GAS OPERATIONS, REGULATORY COMPLIANCE 6111 BOLLINGER CANYON RD., | SAN RAMON | CA | 94583 | 2018-08-13 18:43 | 2018 |  |  | 38.4145 | -122.8446 | 1221447 | 2018-08-13 20:30 |  | NATURAL GAS |  | 50 | 1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-08-13 18:43 | 2018-08-14 23:59 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-08-13 18:43 | 2018-08-13 18:43 | ONSHORE | CA | 95472 | SEBASTAPOL | SONOMA | MILEPOST | 9.7 | DFM 1302-02 | PFL # 614 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 30 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | TAP FITTING(STOPPLE, THREAD-O-RING, WELD-O-LET, ETC.) | [20 empty] | BRANCH WELD AT SERVICE TEE & DFM | [17 empty] | 1964 |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | NO |  | 56 |  | NO | NO | NO |  | 0 | 0 | 3 | 3.12320942883046 | 150 | 135.106382978723 | 135558 | 141125.341251133 | 37544 | 39085.9249320036 | 0 | 0 |  |  | 173255 | 82863.2309401183 | 180349.495775544 | [8 empty] | 130 |  | 150 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 8 | NO | [5 empty] | YES | THE LINE IS NOT PIGGABLE DUE TO OPERATING CONDITIONS AND THAT THE MAOP OF THE LINE IS 150 PSIG | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CLOSEST SCADA ASSET TO DRM 13-02 MP 9.7 IS RKS_PT0101 IN SEBASTOPOL. NO INVESTIGATION WAS REQUIRED AS GAS CONTROL DID NOT RECEIVE ALARMS DUE TO THIS GRADE 1 LEAK. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES | [7 empty] | YES | POROSITY AND SOLIDIFICATION CRACKING CREATED DURING THE BRAZE WELDING PROCESS | [12 empty] | YES | [63 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | ENZA BARBATO | REGULATORY COMPLIANCE | e1bo@pge.com | 925-357-7889 |  |  |  |  | SUSIE RICHMOND | REGULATORY COMPLIANCE MANAGER | 925-786-0267 | gsr8@gpe.com | ON MONDAY, AUGUST 13, 2018, AT 1843 HOURS, PG&E WAS NOTIFIED OF A GRADE ONE TRANSMISSION LEAK AT 1311 GRAVENSTEIN HWY N IN SEBASTOPOL, CA. PG&E'S CONTRACTOR WAS ON SITE WHILE HAND DIGGING AND EXPOSING THE LEAK APPROXIMATELY AT 1843 HOURS. PG&E CREWS ARRIVED ON-SITE AND REMAINED ON SCENE OVERNIGHT UNTIL THE REPAIRS WERE COMPLETED. ON AUGUST 14, 2018, THE LEAKING SERVICE TEE WAS CUTOUT ALONG WITH THE SECTION OF 6" PIPE IT WAS WELDED TO. THE LEAK WAS LOCATED ALONG LINE DFM 1302-02 AT MILE POINT 9.7. THERE WAS NO CUSTOMER IMPACT. THERE WERE NO OF INJURIES OR NO FATALITIES. THERE WAS NO MEDIA, POLICE, FIRE DEPARTMENT REPORTED. THIS INCIDENT WAS REPORTED TO THE DOT AND CPUC DUE TO THE >$50,000 CRITERIA.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180094 | 31814 | 2018-09-17 12:42 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2018-09-06 05:30 | 2018 |  |  | 40.2205 | -96.7408 | 1223813 | 2018-09-06 13:05 |  | NATURAL GAS |  | 3685 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | PRESSURE REDUCED BETWEEN TWO CROSS-OVER VALVES | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-09-06 05:30 | 2018-09-06 06:00 | ONSHORE | NE | 68310 | Not Within a Municipality | GAGE COUNT | SURVEY STATION NO. | BEATRICE | BEATRICE STATION | 179M590D | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | 1-INCH NIPPLE BROKE FROM A CROSS-OVER LO | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | 1-INCH NIPPLE TO A CROSS-OVER VALVE WITH REGULATOR BROKE. THE CROSS-OVER VALVE IS BETWEEN TWO PIPELINES. THE REGULATOR REMAINED FUNCTIONAL. | CLASS 1 LOCATION | NO |  | 607 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 8055 | 7255.21276595745 | 300 | 312.320942883046 | 2500 | 2602.67452402538 | 0 | 0 |  |  | 10855 | 8859.868347447 | 10170.2082328659 | [8 empty] | 800 |  | 860 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL |  | NO |  |  | YES |  |  |  |  | YES |  |  |  |  | YES | CROSS-0VER SECTION | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | 1-INCH NIPPLE BROKE BETWEEN CROSS-OVER VALVES WITH REGULATOR ON CROSS-OVER. | YES | [177 empty] | KEN ANDERSON | SENIOR INTERNAL CORROSION ENGINEER | ken.anderson@nngco.com | 402-398-7617 |  |  |  |  | KEN ANDERSON | SENIOR INTERNAL CORROSION ENGINEER | 402-398-7617 | ken.anderson @nngco.com | ON SEPTEMBER 6, 2018 AT 0657 - OPERATIONS AT BEATRICE REPORTED BLOWING GAS AT THE BEATRICE STATION. OPERATIONS DISCOVERED A BROKEN VALVE NIPPLE ON THE 1-INCH DIAMETER M590 C TO D DISCHARGE LINE. THE LINE CONNECTS THE 24-INCH DIAMETER MANIFOLD TO THE 590C MAINLINE. THE SEGMENT WAS ISOLATED AND NIPPLE, VALVE AND PLUG WERE INSTALLED AT 0930 ON SEPTEMBER 6, 2018. FISHER VALVE STATED THE NOISE AND VIBRATION EXCEEDED THE RECOMMENDED LEVELS ON THE CONTROL VALVE AT THE CROSS-OVER. FISHER VALVE WILL MAKE RECOMMENDATIONS TO RECTIFY THE PROBLEM.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180095 | 31003 | 2018-09-25 15:47 | SUPPLEMENTAL FINAL | 39750 | GREYLOCK MIDSTREAM, LLC | 500 CORPORATE LANDING | CHARLESTON | WV | 25311 | 2018-08-29 10:00 | 2018 |  |  | 39.8439 | -80.095 | 1223209 | 2018-08-30 16:15 |  | NATURAL GAS |  | 3646 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | GAS VENTING THROUGH STUCK DUMP VALVE, DUMP VALVE WAS CLOSED & VENTING STOPPED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-08-29 10:00 | 2018-08-29 10:00 | ONSHORE | PA | 15370 | WAYNESBURG | GREENE | SURVEY STATION NO. | MS 642822 | VERES TCO M&R STATION | GC-1001-S2 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | OTHER | FILTER SEPARATOR DUMP VALVE |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | DRAIN LINES | [38 empty] | 2015 |  | CARBON STEEL |  | OTHER | [8 empty] | DUMP VALVE ON AUXILIARY PIPING ON FILTER SEPARATOR GOT STUCK IN OPEN POSITION AND VENTED GAS TO TANK | CLASS 1 LOCATION | NO |  | 285 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 6672 | 6009.53191489362 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6672 | 6230.35460992908 | 6009.53191489362 | [8 empty] | 830 |  | 1480 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | DUMP VALVE | [15 empty] | YES | APPEARS DEBRIS GOT STUCK IN DUMP VALVE AND HELD IT IN OPEN POSITION | [161 empty] | KYLE P FLANAGAN | MIDSTREAM COMPLIANCE ENGINEER | kflanagan@greylockenergy.com | 3049419006 |  |  |  |  | RYAN DEADERICK | SR. VP OF PRODUCTION AND MIDSTREAM | 304-925-6100 | rdeaderick@greylockenergy.com | AT AROUND 10AM ON 8/29/2018 GREYLOCK EMPLOYEES ARRIVED ONSITE AND FOUND THAT GAS WAS VENTING TO THE FLUID TANK FROM THE FILTER SEPARATOR. UPON INVESTIGATION ONE OF THE DUMP VALVES ON THE FILTER SEPARATOR WAS FOUND TO BE STUCK IN THE OPEN POSITION. A MANUAL VALVE WAS SHUT TO STOP TO THE FLOW OF GAS TO THE TANK AND TO ISOLATE THE DUMP VALVE. THE DUMP VALVE ADJUSTMENT SCREW WAS ADJUSTED AND THE VALVE STARTED OPENING AND CLOSING PROPERLY. A VENT LINE UPSTREAM OF THE DUMP VALVES WAS OPENED TO TRY AND BLOW AND DEBRIS OUT OF THE LINE THAT MAY HAS CAUSED TO DUMP VALVE TO GET STUCK IN THE OPEN POSITION. THE VALVE WAS THEN TURNED BACK INLINE. AT THE TIME OF THE INCIDENT GREYLOCK WAS UNAWARE OF HOW MUCH GAS VENTED OR FOR HOW LONG IT HAD BEEN VENTING AND COULD NOT CONFIRM AN INCIDENT HAD OCCURRED UNTIL FURTHER INVESTIGATION. ON 8/30/2018 AT AROUND 3:50PM FACILITIES RECEIVED AN EMAIL FROM THE MARKETING GROUP SHOWING THAT GREYLOCK HAD VENTED APPROXIMATELY 3646 MSCF OF GAS CONFIRMING AN INCIDENT HAD OCCURRED. AT THAT TIME A TELEPHONIC NOTICE WAS MADE TO PHMSA AT APPROXIMATELY 4:15PM. IN ORDER TO PREVENT REOCCURRENCE GREYLOCK OPENED UP THE FILTER SEPARATOR AND CLEANED THE FILTER OF BLACK/DARK GREY SEDIMENT THAT HAD COLLECTED IN THE FILTER SEPARATOR. GREYLOCK ALSO REPLACED THE OLD FILTERS AND INSTALLED NEW CLEAN FILTERS AND BLEW OUT DUMP LINES. GREYLOCK HAS ALSO SCHEDULED A TRAINING WITH THE MANUFACTURER AND IS WORKING ON A MAINTENANCE PROCEDURE FOR THE FILTER SEPARATORS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180096 | 31134 | 2018-09-26 19:14 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2018-08-27 14:59 | 2018 |  |  | 38.875 | -78.859 | 1222867 | 2018-08-27 17:07 |  | NATURAL GAS |  | 2200 | 3300 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-08-27 15:48 | 2018-08-28 15:02 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 5 | 2018-08-27 14:59 | 2018-08-27 14:59 | ONSHORE | WV | 26812 | MATHIAS | HARDY | MILEPOST | UNKNOWN | PIPELINE WV2VA | UNKNOWN AT THIS TIME | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | TAP FITTING(STOPPLE, THREAD-O-RING, WELD-O-LET, ETC.) | [38 empty] | 2017 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 2 LOCATION | NO |  | 578 |  | NO | NO | NO |  | 0 | 0 | 8811 | 9172.86609247507 | 5874 | 5290.76595744681 | 110000 | 114517.679057117 | 0 | 0 | 0 | 0 | THE COST OF THE TD WILLIAMSON STOPPLE MACHINE IS UNKNOWN. |  | 124685 | 62262.4013303499 | 128981.311107039 | [8 empty] | 840 |  | 870 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 31680 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A CONTRACTOR AND COMPANY EMPLOYEES WERE ONSITE WORKING WITH THE FAILED FITTING AND CONTROL ROOM WAS NOT A FACTOR IN THE CAUSE OF THE INCIDENT. | [12 empty] | NO |  |  | YES | 1 | 0 | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [8 empty] | YES | [16 empty] | YES | [172 empty] | CHRIS LEGG | US REGULATORY COMPLIANCE SPECIALIST | chris_legg@transcanada.com | 304-545-4350 |  |  |  |  | GEORGE HAMATY | MANAGER US REGULATORY COMPLIANCE - EAST | 304-357-3728 | george_hamaty@transcanada.com | THE INCIDENT OCCURRED ON PIPELINE WV2VA (24") JUST OUTSIDE THE LOST RIVER COMPRESSOR STATION. THIS LOCATION IS IN HARDY COUNTY, MATHIAS, WV, GPS COORDINATES 38.875, -78.859. AS PART OF THE TRANSCANADA WB EXPRESS PROJECT, AN INSTALLATION OF A STOPPLE FITTING WAS BEING COMPLETED BY THE CONTRACTOR (TD WILLIAMSON). THE ORIGINAL FITTING WAS INSTALLED IN 2017 . DURING THIS OPERATION, THE TD WILLIAMSON TECHNICIAN REMOVE THE COMPLETION PLUG AND INSTALL THE STOPPLE/BYPASS. THE 24" BLIND FLANGE WAS REMOVED AND THE FITTING SNIFFED FOR GAS. HE THEN INSTALLED A DEVICE /ADAPTER ONTO THE COMPLETION PLUG. THE STOPPLE VALVE ( SANDWICH VALVE) WAS INSTALLED. THE TAPPING MACHINE WAS THEN INSTALLED. THE TDW TECHNICIAN BEGAN TO HOOK UP HYDRAULIC UNIT TO THE TAPPING MACHINE TO PULL THE 24" COMPLETION PLUG. HE BEGAN THE PROCESS OF REMOVING THE PLUG HE INFORMED THE TRANSCANADA AND BICON EMPLOYEES (PRIMARY CONTRACTOR) THAT HE NEEDED TO RESET THE MACHINE AND TO DO SO HE NEEDED TO BLOW DOWN THE GAS PRESSURE OFF THE MACHINE. HE THEN OPENED THE BLOW OFF VALVE AND BEGAN BLOWING DOWN, THE GAS BLEW THOUGH THE BLOWDOWN VALVE FOR A FEW SECONDS WITHOUT ANY SIGN OF DIMINISHING, THEN THE TOP BLEW OFF THE MACHINE AND ALLOWED FULL LINE PRESSURE TO ESCAPE TO THE OPEN ATMOSPHERE. THE EXHAUSTING GAS BLEW SEVERAL MACHINE PARTS OUT THE TOP OF THE MACHINE. NO INJURIES OCCURRED AND THE PIPELINE WAS ISOLATED BY MANUALLY CLOSING MAINLINE VALVES. THE AREA AT THE STOPPLE WAS CLEARED AS THE GAS WAS RELEASED. NO STRUCTURES (APPROX. 250')OR ROADS (APPROX. 175') WERE IN THE IMMEDIATE AREA. THE LOCAL FIRE DEPARTMENT RESPONDED, HELPING DIRECT VEHICLE TRAFFIC AND FIVE RESIDENCE WERE EVACUATED. THE INITIAL PIPELINE PRESSURE WAS 840 PSIG AND IS NOW BLOWN DOWN AND ISOLATED. THE MAOP IS 870 PSIG. A ROOT-CAUSE INVESTIGATING WAS JOINTLY CONDUCTED BY TRANSCANADA AND TD WILLIAMSON. IT WAS DETERMINED THE TD WILLIAMSON TECHNICIAN DID NOT PROPERLY FOLLOW THE PROCEDURE WHILE ATTEMPTING TO REMOVE THE COMPLETION PLUG. DURING THE INITIAL PLUG REMOVAL PROCESS, THE TECHNICIAN BECAME CONCERNED THAT THE RETRIEVAL WAS NOT GOING AS EXPECTED. THE TECHNICIAN ATTEMPTED TO RE-SET THE COMPLETION PLUG, IMPLEMENTED A STOP WORK, AND CONTACTED A TDW SME FOR GUIDANCE. WHILE THE TECHNICIAN RECEIVED GUIDANCE, HE DID NOT EFFECTIVELY COMMUNICATE THE FULL DEPTH AND BREADTH OF THE SITUATION. IT WAS LATER DETERMINED THAT WHILE ATTEMPTING TO REMOVE THE COMPLETION PLUG, THE PLUG HAD NOT BEEN FULLY REMOVED FROM ITS GROOVES AND HAD ONLY BEEN PARTIALLY RESET (WINGS NOT FULLY ENGAGED). AFTER RECEIVING GUIDANCE, THE TECHNICIAN DECIDED THE BEST COURSE OF ACTION WAS TO BLOW DOWN THE TAPPING MACHINE, REMOVE IT, AND INVESTIGATE THE PLUG EXTRACTION ASSEMBLY. AT THIS TIME, THE PRESSURE IN THE TAPPING MACHINE WAS EQUALIZED WITH PIPELINE PRESSURE AT 800-PSI. THE BLOWDOWN PROCEDURE CREATED A DIFFERENTIAL PRESSURE ACROSS THE COMPLETION PLUG. AS THE COMPLETION PLUG WINGS WERE NOT FULLY ENGAGED INTO THE PLUG FITTING GROOVES, THE DIFFERENTIAL PRESSURE ACTING ACROSS THE PARTIALLY SET COMPLETION PLUG, CAUSED IT TO BE RELEASED FROM ITS POSITION. THE COMPLETION PLUG THEN IMPACTED THE BORING BAR AND FORCED IT THROUGH THE TOP OF THE TAPPING MACHINE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180097 | 32356 | 2018-10-01 20:42 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2018-09-02 22:04 | 2018 |  |  | 44.201 | -85.2074 | 1223491 | 2018-09-03 05:36 |  | NATURAL GAS |  | 3200 | 74.6 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-09-02 23:13 | 2019-02-27 11:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2018-09-02 22:04 | 2018-09-02 22:47 | ONSHORE | MI | 49657 | MCBAIN | MISSAUKEE | MILEPOST | MCBAIN DEHY | MCBAIN-LAKE CITY DEHYDRATION UNIT | LATERAL 80W | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ABOVEGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | DEHYDRATOR/DRIER/TREATER/SCRUBBER | [38 empty] | 1982 |  | CARBON STEEL |  | OTHER | [8 empty] | THE UNIT'S KIMRAY CONTROLLER CAUSED THE FUEL TRAIN REGULATOR TO CONTINUE TO FEED FUEL TO THE BURNER, CAUSING THE DIETHYLENE GLYCOL TO BOIL OVER AND IGNITE. | CLASS 1 LOCATION | NO |  | 156 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 9396 | 8463.06382978723 | 2673007 | 2782786.88857661 | 6470 | 6735.7216681777 | 0 | 0 |  |  | 2688873 | 1289238.527322 | 2797985.67407457 | [8 empty] | 668 |  | 800 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) | [11 empty] | YES | THE HIGH-HIGH TEMPERATURE ALARM LIMIT OF 300° F WAS NOT RECOGNIZED IN GAS CONTROL PRIOR TO THE MCBAIN FIRE BECAUSE THE TELEMETRY DATA RECEIVED NEVER EXCEEDED THE 300 DEGREE ALARM LIMIT THRESHOLD DUE TO THE SCALING OF THE TRANSDUCER(0-300) IN THE FIELD. | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | EQUIPMENT FAILURE AT A KIMRAY CONTROLLER CAUSING THE FUEL TRAIN REGULATOR TO CONTINUE TO FEED THE FUEL TO THE BURNER, LEADING THE DIETHYLENE GLYCOL TO BOIL OVER AND IGNITE. | [15 empty] | YES | EQUIPMENT FAILURE A KIMRAY CONTROLLER | [161 empty] | CARMELLA KING | SENIOR ENGINEERINGTECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  |  |  |  | JASON PIONK | SENIOR ENGINEERING LEAD | 989-791-5749 | jason.pionk@cmsenergy.com | ON SEPTEMBER 2, 2018 AT APPROXIMATELY 22:04 CONSUMERS ENERGY GAS CONTROLLER DISPATCHED AN INSTRUMENT MECHANIC TO THE MCBAIN CITY GATE BECAUSE OF ERRATIC READINGS ON THE TRANSMITTERS AT THIS LOCATION. THE MCBAIN CITY GATE IS LOCATED IN MCBAIN, MICHIGAN (MISSAUKEE COUNTY). THE MECHANIC ARRIVED AT THE MCBAIN CITY GATE AT APPROXIMATELY 22:47 AND OBSERVED A FIRE AT/NEAR THE DEHYDRATION UNIT BUILDING. THE MECHANIC NOTIFIED THE FIELD LEADER AND REQUESTED ADDITIONAL SUPPORT TO ISOLATE THE PIPELINE SEGMENT SUPPLYING THE UNIT. ADDITIONAL RESOURCES ARRIVED AT THE 80-W VALVE SITE AT APPROXIMATELY 23:13 AND THE MECHANICS SIMULTANEOUSLY CLOSED THE VALVES AT 80-W AND MCBAIN CITY GATE TO ISOLATE THE GAS FLOW TO THE DEHYDRATION UNIT. THE FIRE CONTINUED AS THE AS THE PIPELINE DEPRESSURIZED AND THEN WAS EXTINGUISHED. THERE WERE NO FATALITIES OR INJURIES AS A RESULT OF THE INCIDENT. THE MCBAIN FIRE DEPARTMENT WAS ON SCENE AND PRELIMINARY INVESTIGATION DETERMINED A LIGHTNING STRIKE TO BE THE CAUSE. CONSUMERS ENERGY ALSO RECEIVED A REPORT FROM STRIKENET© CONFIRMING THE PRESENCE OF 22 CLOUD-TO-GROUND LIGHTNING STRIKES WERE DETECTED WITHIN 2 MILES OF THE PROPERTY ON SEPTEMBER 2, 2018. NEW VALVES WERE INSTALLED ON THE WELL LINES (R-178 AND R-179) AND A TEMPORARY HOSE TO THE 2" BLOWDOWN FOR THE LINE THAT SUPPLIES THE MCBAIN CITY GATE WAS INSTALLED. THE LINE WAS RE-PRESSURIZED ON SEPTEMBER 3, 2018 AT APPROXIMATELY 04:44. THE INCIDENT RESPONSE AND TEMPORARY REPAIRS WERE COMPLETED WITH NO CUSTOMER IMPACT AND/OR LOSS OF SERVICE. THE INLET AND OUTLET VALVES TO THE DEHYDRATION UNIT WERE BLIND FLANGED AND THE SYSTEM WAS BYPASSED TO SUPPLY THE LAKE CITY AND MCBAIN CITY GATES. AN ACTION PLAN WILL BE DEVELOPED TO PREPARE FOR WINTER OPERATIONS. AN INTERNAL TEAM WAS ASSEMBLED TO COMPLETE A ROOT CAUSE INVESTIGATION AND IDENTIFY COUNTERMEASURES TO MINIMIZE FUTURE OCCURRENCES. A ROOT CAUSE INVESTIGATION CONCLUDED THE ORIGIN OF THE FIRE WAS AT OR NEAR THE DEHYDRATION UNIT AND MAY HAVE BEEN THE RESULT OF AN EQUIPMENT FAILURE AT A KIMRAY CONTROLLER CAUSING THE FUEL TRAIN REGULATOR TO CONTINUE TO FEED THE FUEL TO THE BURNER, LEADING THE DIETHYLENE GLYCOL TO BOIL OVER AND IGNITE. HOWEVER, DUE TO THE LACK OF PHYSICAL EVIDENCE THE EXACT CAUSE REMAINS UNDETERMINED. THE DEHYDRATION UNIT WAS IN-SERVICE WHILE THE RIVERSIDE STORAGE FIELD WAS SHUT IN. LEAVING THE UNIT IN SERVICE ALLOWS CONSUMERS ENERGY TO CONTINUE TO PROVIDE REQUIRED QUALITY OF GAS TO THE CITY GATES. SEVERAL FACTORS THAT MAY HAVE CAUSED OR CONTRIBUTED TO THE SEVERITY OF THE INCIDENT HAVE BEEN OUTLINED IN THE ROOT CAUSE REPORT AND ACTION ITEMS TO PREVENT RE-OCCURRENCE HAVE BEEN IMPLEMENTED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180098 | 31101 | 2018-10-04 19:05 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2018-09-06 15:03 | 2018 |  |  | 37.9175 | -83.9849 | 1223832 | 2018-09-06 15:43 |  | NATURAL GAS |  | 7533 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-09-06 15:05 | 2018-09-06 23:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-09-06 14:56 | 2018-09-06 14:56 | ONSHORE | KY | 40312 | Not Within a Municipality | POWELL | MILEPOST | 12+76 | COMPRESSOR STATION 106, CLAY CITY STATION | LINE 100-3 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2005 |  | CARBON STEEL |  | LEAK |  |  | OTHER | RELIEF VALVE DID NOT RESEAT | [5 empty] | CLASS 2 LOCATION | NO |  | 454 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 21545 | 19405.780141844 | 17000 | 17698.1867633726 | 700 | 728.748866727108 | 2000 | 2082.13961922031 | INVESTIGATION COST |  | 41245 | 29533.0601368715 | 39914.855391164 | [8 empty] | 808 |  | 750 | 192.619(C) |  |  |  | PRESSURE EXCEEDED MAOP, BUT DID NOT EXCEED THE APPLICABLE ALLOWANCE IN 192.201 | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LOOSE WIRE IN PANEL CAUSED INADVERTENT SIGNAL TO ESD OF BUILDING C CLOSING TWO VALVES CAUSING RV BD3 TO LIFT TWICE; SECOND TIME VALVE DID NOT SEAT; ON SITE EMPLOYEES HEARD RELEASE; | [12 empty] | YES | 2 | 0 | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [14 empty] | YES | [13 empty] | YES | RELIEF VALVE SEAT DAMAGED DURING ACTIVATION | [161 empty] | WILLIAM MARTIN MULLER | SPECIALIST-PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205 325 3863 | 205 325 3504 |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713 369 9443 | jaime_hernandez@kindermorgan.com | APPROXIMATELY 14:55 (EASTERN), OPERATIONS STAFF WERE WORKING IN A ESD RELAY PANEL. AN INADVERTENT ESD SIGNAL WAS SENT TO BUILDING "C" RESULTING IN CLOSURE OF TWO VALVES. COMPRESSOR UNITS IN BUILDING "B" AND "D" WERE ON LINE. OVERPRESSURING BEGAN TO OCCUR IN A DISCHARGE HEADER; RELIEF VALVE 106-BD5 LIFTED THEN RESEATED. RELIEF VALVE 106-BD3 ALSO LIFTED AND RESEATED. HOWEVER RELIEF VALVE 106-BD3 LIFTED AGAIN BUT DID NOT RESEAT DUE TO DAMAGE CAUSED BY THE PASSING OF HIGH PRESSURE GAS. STATION EMPLOYEES OBSERVED THE EVENT AND ISOLATED THE GAS FLOW AS QUICKLY AS POSSIBLE. THE FOLLOWING INVESTIGATION FOUND A LOOSE WIRE, A DIODE JUMPER, HAD BECOME DISLODGED FROM THE RELAY IN THE PANEL CAUSING THE INADVERTENT ESD SIGNAL. RELIEF VALVE 106-BD3 WAS REPAIRED AS WELL AS THE LOOSE WIRE. APPROPRIATE CHECKS AND INSPECTIONS WERE MADE AND COMPRESSOR STATION RETURNED TO SERVICE. THE WORK AT THE RELAY PANEL INVOLVED BUILDING "A". WITH POST-EVENT INVESTIGATION AND FOLLOW-UP, THE RESPECTIVE WIRING HAS BEEN REVISED TO SEPARATE BUILDING "A" FROM IMPACTING OTHER BUILDINGS. ALSO, POST-EVENT INVESTIGATION FOUND FINAL GAS LOST VOLUME LESS THAN ORIGINALLY CALCULATED AND REPORTED TO NRC.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180099 | 32816 | 2018-10-09 09:29 | SUPPLEMENTAL FINAL | 4070 | EAST TENNESSEE NATURAL GAS, LLC (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2018-09-11 19:50 | 2018 |  |  | 35.2856 | -86.0973 | 1224407 | 2018-09-12 12:02 |  | NATURAL GAS |  | 6739 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE NATURAL GAS RELEASE WAS ISOLATED TO ONE COMPRESSOR. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-09-11 19:50 | 2018-09-11 22:40 | ONSHORE | TN | 37398 | WINCHESTER | FRANKLIN | MILEPOST | 109.14 | 3200 | ESTILL SPRINGS | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1990 |  | CARBON STEEL |  | LEAK |  |  | OTHER | COMPRESSOR UNIT CASE VENTING | [5 empty] | CLASS 1 LOCATION | NO |  | 43 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 20217 | 18209.6382978723 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 20217 | 18878.7588652482 | 18209.6382978723 | [8 empty] | 576 |  | 973 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER IMMEDIATELY NOTIFIED FIELD PERSONNEL OF THE "CALL ATTENDANT" ALARM. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [30 empty] | YES | FAULTY CELLS IN THE BATTERY | [161 empty] | DWAYNE TESCHENDORF | ENGINEER SPECIALIST | dwayne.teschendorf@enbridge.com | 713-627-5573 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: AT 7:50 PM CENTRAL TIME SEPTEMBER 11, 2018, GAS CONTROL PERSONNEL ADVISED FIELD OPERATION PERSONNEL A "CALL ATTENDANT" ALARM HAD BEEN RECEIVED FOR THE ESTILL COMPRESSOR STATION NEAR WINCHESTER, TENNESSEE. THE STATION OPERATOR ARRIVED ON SITE TO FIND SUCTION AND DISCHARGE BLOCK VALVES OPEN FOR A COMPRESSOR UNIT AND THE UNIT CASE VENT VALVE OPEN WHICH WAS VENTING GAS THROUGH THE STATION BLOWDOWN SILENCER. THE OPERATOR MANUALLY CLOSED THE UNIT SUCTION AND DISCHARGE VALVES, ALLOWING THE CASE TO COMPLETELY BLOW DOWN, CLEARING THE ALARM AND RETURNING THE UNIT TO NORMAL OPERATING STATUS. THE ROOT CAUSE OF THE EVENT IS UNDER INVESTIGATION. SUPPLEMENTAL/FINAL REPORT: 48 HR NRC REPORT 1224528 THE CAUSE WAS LOOSE WIRING AND FAULTY RELAYS. TWO UNIT VALVE CONTROL RELAYS WERE INSPECTED AND REPLACED. IN ADDITION, LOOSE WIRE CONNECTIONS WERE TIGHTENED. THE UNIT VALVES WERE THEN OPERATED THROUGH SEVERAL AUTOMATIC AND MANUAL CYCLES WITH NO ISSUES. SUPPLEMENTAL/FINAL REPORT 10/14/19: THE CAUSE WAS FAULTY CELLS IN THE BATTERY WHICH RESULTED IN A DROP IN VOLTAGE WHICH PREVENTED VALVES FROM OPENING.
2021-02-26 10:37 | YES | NO | GG (Gas Gathering) | 20180100 | 33486 | 2018-10-10 15:04 | SUPPLEMENTAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2018-09-10 05:21 | 2018 | EASTERN | NO | 40.622 | -80.3111 | 1224150 | 2018-09-10 07:04 | 1224314 | NATURAL GAS |  | 40000 | 3900 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | POST-CONSTRUCTION COMMISSIONING | [5 empty] | NO |  |  | YES | 2018-09-10 05:21 | OTHER | OPERATOR ISOLATED LINE AND GAS WAS ALLOWED TO BURN OUT | 40000 | NO | VALVE CLOSURE |  | 2018-09-10 05:24 | VALVE CLOSURE |  | 2018-09-10 06:06 | 49 | 2018-09-10 05:21 | 2018-09-10 05:24 | ONSHORE | PA | 15001-0000 | ALIQUIPPA | BEAVER | SURVEY STATION NO. | 1115+09 | REVOLUTION 24" | 20150150 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 64 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 24 |  | 0.495 | 70000 | API5L/PSL2 | LONGITUDINAL ERW - HIGH FREQUENCY |  | EVRAZ | EPOXY |  | YES | [7 empty] | PIPE GIRTH WELD |  | NO | [16 empty] | 2018 | 2017 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 75.4 | 1 |  | CLASS 3 LOCATION | NO |  | 690 |  | YES | YES |  |  | 99192 | 103265.79655485 | 15975 | 16631.0902085222 | 163844 | 147575.80141844 | 6704700 | 6980060.7524932 | 5000 | 5205.34904805077 | 22435 | 23356.4011786038 | REIMBURSEMENT TO EMERGENCY RESPONDERS | 4.0961 | 7011146 | 3425177.03310036 | 7276095.19090167 | 0 | 0 | 38 | 1 | NO |  |  |  | 813 | 20000 | 1440 | 192.619(A)(2) |  | 2018-02-16 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 59980 | YES | [7 empty] | NO | [6 empty] | TYPE A GATHERING | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 3 | 0 | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [52 empty] | HEAVY RAINS/FLOODS |  | MUDSLIDE |  |  |  | YES |  | YES |  | YES | THERE WERE THREE DAYS OF HEAVY RAIN ASSOCIATED WITH TROPICAL STORM GORDON JUST PRIOR TO THIS EVENT. THIS RAIN IN CONJUNCTION WITH THE OTHER RAIN IN THE PREVIOUS TWO & 1/2 MONTHS TOTAL TO BE OVER 14 INCHES OF RAIN IN THE LOCAL AREA. | [261 empty] | YES | [39 empty] | CHRIS KRESTA | MANAGER - REGULATORY COMPLIANCE | chris.kresta@energytransfer.com | 7139897077 | 7139891188 |  |  |  | DANNY NICHOLS | SENIOR DIRECTOR OF REGULATORY COMPLIANCE | 7139897232 | danny.nichols@energytransfer.com | ON SEPTEMBER 10, 2018 AT 05:17 AM (EASTERN), ENERGY TRANSFER OPERATIONS WAS NOTIFIED BY AN OFF DUTY EMPLOYEE OF A POSSIBLE LAND SLIDE AND PIPELINE RUPTURE AND FIRE NEAR THE REVOLUTION 24IN. PIPELINE RIGHT OF WAY. GAS CONTROL WAS NOTIFIED AND VERIFIED A PRESSURE LOSS ON THE REVOLUTION 24IN. PIPELINE. THIS PIPELINE IS AN INTRASTATE GAS GATHERING PIPELINE LOCATED IN A CLASS THREE AREA NEAR CENTER TOWNSHIP, PA. IN BEAVER COUNTY. AT 05:26 AM (EASTERN), PENNSYLVANIA 911 OPERATOR (DAVID) NOTIFIED ENERGY TRANSFER GAS CONTROL OF A PIPELINE RUPTURE AND FIRE IN THE GENERAL AREA OF IVY LANE IN CENTER TOWNSHIP. THE PENNSYLVANIA PUC WAS NOTIFIED AT 05:47 AM (EASTERN) AND NRC WAS NOTIFIED AT 07:07 AM (EASTERN) UNDER INCIDENT# 1224150, WITH THE 48 HOUR FOLLOW UP NOTIFICATION TO THE NRC MADE ON SEPTEMBER 11TH AT 04:31 PM (EASTERN), INCIDENT # 1224314. AT 05:24 AM (EASTERN), THE ETC OPERATIONS MANAGER DIRECTED ETC PIPELINE TECHNICIANS TO CLOSE THE MAIN LINE VALVES AT FREEDOM CRIDER ROAD, BROADHEAD ROAD, AND NEWMAN ROAD TO BEGIN TO ISOLATE THE PIPELINE SEGMENT. THE ISOLATION VALVE AT THE REVOLUTION CRYOGENIC PLANT WAS CLOSED AT 6:36 AM (EASTERN) TO COMPLETE THE LINE ISOLATION. THE LINE SEGMENT DEPRESSURIZED AT THE RUPTURE LOCATION. THERE WERE NO INJURIES, HOSPITALIZATIONS, OR FATALITIES. FORTY-NINE NEARBY RESIDENTS WERE EVACUATED. THE INVESTIGATION TO DETERMINE THE CAUSE OF THE FAILURE IS ONGOING, BUT PRELIMINARY RESULTS INDICATE THAT A LAND SLIDE OCCURRED NEAR THE RUPTURE SITE AS A RESULT OF MULTIPLE DAYS OF HEAVY RAIN PRECEDING THE EVENT. THE FAILED SECTION HAS BEEN SENT TO A THIRD PARTY LABORATORY FOR METALLURGICAL TESTING. ** UPDATE 3/29/2019 ** ~THE TIMES IN THE NARRATIVE ABOVE AND THROUGHOUT THE DOCUMENT HAVE BEEN CHANGED TO REFLECT THE LOCAL TIME OF THE INCIDENT AS EASTERN TIME ZONE. ~THE LINE HAS NOT BEEN PLACED IN SERVICE. ~ THE CAUSE OF THE INCIDENT WAS CHANGED FROM G8 / UNDER INVESTIGATION TO G2 / NATURAL FORCE DAMAGE. THERE WERE THREE DAYS OF HEAVY RAIN ASSOCIATED WITH TROPICAL STORM GORDON JUST PRIOR TO THE MUDSLIDE THAT CAUSED THIS EVENT. THIS RAIN IN CONJUNCTION WITH THE OTHER RAIN IN THE PREVIOUS TWO & 1/2 MONTHS TOTAL TO BE OVER 14 INCHES OF RAIN IN THE LOCAL AREA. ** UPDATE 8/19/2019** ENERGY TRANSFER CONTINUES TO WORK WITH THE PENNSYLVANIA DEPARTMENT OF ENVIRONMENTAL PROTECTION ON APPROVAL OF STABILIZATION AND E&S PLANS. ENERGY TRANSFER HAS ALSO WORKED CLOSELY WITH THE PENNSYLVANIA PUBLIC UTILITY COMMISSION IN PROVIDING ESSENTIAL DATA THE COMMISSION HAS REQUESTED. NO DATE FOR COMPLETION AT THIS TIME. ** UPDATE 2/20/2020** THE TIMES INCLUDED IN THE NARRATIVE WERE CLARIFIED TO BE EASTERN TIME ZONE. REFERENCE TO CENTRAL TIME ZONE WAS REMOVED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180101 | 32516 | 2018-10-11 11:52 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2018-09-19 08:15 | 2018 |  |  | 40.9001 | -96.1787 | 1225056 | 2018-09-19 09:29 |  | NATURAL GAS |  | 3869 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE RELIEF WAS RESET IMMEDIATELY. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-09-19 08:15 | 2018-09-19 08:15 | ONSHORE | NE | 68403 | Not Within a Municipality | CASS | MILEPOST | 15.31 | OMAHA 3RD LINE | NEB49301 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ABOVEGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2018 |  | CARBON STEEL |  | OTHER | [8 empty] | THE RELIEF VALVE OPENED BELOW ITS SETPOINT. THE NEW PIPELINE WAS BEING PURGED AND PRESSURED PRIOR TO BEING PLACED IN-SERVICE. | CLASS 1 LOCATION | NO |  | 312 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 10911 | 9827.63829787234 | 10 | 10.4106980961015 | 10 | 10.4106980961015 | 0 | 0 |  |  | 10931 | 10198.3164355111 | 9848.45969406454 | [8 empty] | 750 |  | 800 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 2 | NO |  | YES | [5 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATOR EMPLOYEES ON SITE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [13 empty] | YES | [177 empty] | JOHN A GORMLEY | SR CORROSION SPECIALIST - PIPELINE SAFETY | john.gormley@nngco.com | 4023987494 |  |  |  |  | THOMAS CORRELL | VP PIPELINE SAFETY AND RISK | 4023987715 | thomas.correll@nngco.com | ON SEPTEMBER 19, 2018, OPERATIONS PERSONNEL WERE MAKING PLANED PRESSURE ADJUSTMENTS TO THE OMAHA 3RD BRANCH LINE TO RAISE PRESSURE FROM 725 TO 775 PSIG. THE MAOP IS 800 PSIG. WHEN PRESSURE REACHED 750 PSIG, THE RELIEF VALVE BEGAN TO VENT. OPERATIONS PERSONNEL ISOLATED THE RELIEF VALVE AND THE VENTING STOPPED. VENTING OCCURRED FOR APPROXIMATELY 5 MINUTES. APPROXIMATELY 3,869 MCF OF GAS WAS RELEASED. THE CAUSE OF THE RELIEF VALVE TO VENT BELOW SET POINT WAS VIBRATION CREATED BY THE V250 CONTROL VALVE AND THE FACILITY PIPING. THE ENERGY TRANSFERRED IN THE FORM OF VIBRATION OVER TIME LOOSENED THE LOCKING NUT ON THE PILOT SET POINT ADJUSTMENT STEM. THIS ALLOWED THE STEM TO BACK OUT, CHANGING (LOWERING) THE SET POINT. CONTRIBUTING CAUSES MAY HAVE BEEN THE INCREASED CONTROL VALVE NOISE LEVEL DUE TO A CHANGE IN OPERATING PRESSURES (INCREASED PRESSURE DROP DURING CONSTRUCTION ACTIVITIES) AND/OR INSUFFICIENT TORQUE ON THE LOCK NUT WHEN PREVIOUSLY TESTED. ADDITIONAL IMPACT TO THE RELIEF VALVE ASSEMBLY WAS DUE TO THE IMPROPER DESIGN OF THE VENT PIPING AND SUPPORT STRUCTURE, WHICH ENHANCED THE SIDE THRUST WHEN THE RELIEF VALVE OPENED.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180102 | 31292 | 2018-10-11 12:02 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2018-09-22 01:30 | 2018 |  |  | 42.6865 | -89.641 | 1225389 | 2018-09-22 11:05 |  | NATURAL GAS |  | 3489 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-09-22 01:30 | 2018-09-22 04:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-09-22 01:30 | 2018-09-22 04:30 | ONSHORE | WI | 53818 | Not Within a Municipality | GREEN | SURVEY STATION NO. | WI-001 | BELLEVILLE COMPRESSOR STATION | WI-001 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | INSTRUMENTATION | [38 empty] | 1996 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | ALUMINUM | OTHER | [8 empty] | A PLC ON UNIT #4 AT THE STATION FAILED RESULTING IN A GAS RELEASE. | CLASS 1 LOCATION | NO |  | 427 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 8897 | 8013.60992907801 | 100 | 104.106980961015 | 500 | 520.534904805077 | 0 | 0 |  |  | 9497 | 8594.80039393959 | 8638.25181484411 | [8 empty] | 910 |  | 960 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLERS DETECTED THE SHUT DOWN IMMEDIATELY AND NOTIFIED FIELD OPERATIONS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  | YES | [31 empty] | YES | AGE OF EQUIPMENT AND LONG USE | [161 empty] | JOHN A. GORMLEY | SR CORROSION SPECIALIST - PIPELINE SAFETY | john.gormley@nngco.com | 4023987494 | 4025485267 |  |  |  | THOMAS CORRELL | VP PIPELINE SAFETY AND RISK | 4023987715 | thomas.correll@nngco.com | ON 9/22/2018, AT APPROXIMATELY 1:30AM, A PLC FAILED ON UNIT #4 AT THE BELLEVILLE COMPRESSOR STATION RESULTING IN A GAS RELEASE. THE FACILITY WAS SECURED AT ~4:30AM. THE ESTIMATED GAS LOSS WAS 3,489 MCF. THE INITIAL CALCULATION HAD AN ERROR AND IT WAS THOUGHT TO BE UNDER THE REPORTING LIMIT. UPON FURTHER REVIEW WHEN IT WAS REALIZED THAT THE REPORTING THRESHOLD WAS EXCEEDED, AN URGENT OCC CALL WAS INITIATED AT 10:55AM WITH MEMBERS FROM THE PLATTEVILLE TEAM, FACILITY PLANNING, AND PIPELINE SAFETY DEPARTMENTS. UPDATE: ON 12/07/2018 THE NRC REPORT NUMBER WAS CORRECTED TO SHOW THE ORIGINAL IN PLACE OF THE 48-HOUR UPDATE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180103 | 31159 | 2018-10-12 13:26 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2018-09-17 09:00 | 2018 |  |  | 38.8467 | -79.3763 | 1224829 | 2018-09-17 09:56 |  | NATURAL GAS |  | 4551 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | SENECA COMPRESSOR STATION EMERGENCY SHUTDOWN (ESD) ACTIVATED. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-09-17 09:00 | 2018-09-17 09:00 | ONSHORE | WV | 26884 | SENECA ROCKS | PENDLETON | MILEPOST | SENECA CS | SENECA COMPRESSOR STATION | NA | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | OTHER | GAS UNINTENTIONALLY RELEASED THROUGH ESD |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | BLOWOFF VALVE ON ESD SYSTEM MALFUNCTIONED AND REMAINED OPENED BEYOND THE DESIGNED PERIOD. (> 5 MINUTES) | CLASS 1 LOCATION | NO |  | 750 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 12151 | 10944.5177304965 | 0 | 0 | 0 | 0 | 0 | 0 | NA |  | 12151 | 11346.6784869976 | 10944.5177304965 | [8 empty] | 720 |  | 800 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CAUSE OF THE UNINTENDED GAS RELEASE WAS KNOWN AND A CONTROL ROOM INVESTIGATION WAS NOT NECESSARY. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | BLOWOFF VALVE ON THE ESD SYSTEM MALFUNCTIONED AND DID NOT CLOSE. | [161 empty] | CHRIS LEGG | US REGULATORY COMPLIANCE SPECIALIST | chris_legg@transcanada.com | 304-545-4350 | 304-722-8530 |  |  |  | GEORGE HAMATY | MANAGER US REGULATORY COMPLIANCE EAST | 304-357-3728 | george_hamaty@transcanada.com | ON 09/17/2018 AT 9:00 AM EST, THE EMERGENCY SHUTDOWN SYSTEM WAS ACCIDENTLY TRIGGERED AT SENECA COMPRESSOR STATION (CS) SENECA CS IS LOCATED AT SENECA ROCKS, PENDLETON COUNTY, WEST VIRGINIA. THE ESD ACTIVATED AS DESIGN WHEN A FIRE-EYE DETECTION DEVICE DETECTED A FLASH OF LIGHT FROM NEARBY CONSTRUCTION PROJECT AND TRIGGERED THE ESD SYSTEM. NORMALLY, THE GAS RELEASED FROM THE ESD SYSTEM WOULD NOT EXCEED 3000 MCF BUT ONE OF THE 8" BLOW-OFF VALVES DID NOT CLOSE PROPERLY AND CONTINUED TO BLOW GAS TO THE ATMOSPHERE FOR AN EXTENDED PERIOD OF TIME, RELEASING AN ESTIMATED 4551 MCF.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180104 | 31224 | 2018-10-25 12:25 | SUPPLEMENTAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2018-09-26 08:21 | 2018 |  |  | 39.4783 | -79.0417 | 1225754 | 2018-09-26 11:37 |  |  |  | 54.83 | 5.4 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-09-28 15:50 | 2018-09-28 21:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-09-26 08:16 | 2018-09-26 09:28 | ONSHORE | WV | 26750 | PEIDMONT | MINERAL | SURVEY STATION NO. | 14464 | PIPELINE 8012 | 8012-015 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | OTHER | ABOVEGROUND PIPELINE |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 |  | 0.277 | 24000 | BARE STEEL, SCREW JOINT AND COULPED PIPE | OTHER | OTHER | UNKNOWN | NONE | [28 empty] | 1906 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | HEAVY RAINS IN THE AREA INITIATED LAND MOVEMENT CAUSING LINE 8012 TO BECOME BUCKLED WHICH BEGAN LEAKING AT THE BUCKLED AREAS(2). | CLASS 3 LOCATION | NO |  | 112 |  | NO | NO | NO |  | 0 | 0 | 14 | 14.5749773345422 | 146 | 131.503546099291 | 64151 | 66785.669356301 | 0 | 0 | 0 | 0 |  |  | 64311 | 30799.4104934104 | 66931.7478797348 | [8 empty] | 65 |  | 70 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 1453 | NO | YES | YES | YES | YES |  |  |  | YES |  | YES |  |  |  |  | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS INCIDENT WAS CAUSED BY LAND MOVEMENT DAMAGING THE PIPELINE. THIS LOW PRESSURE SYSTEM IS NOT CONTROLLED BY SCADA AND NO INVOLVEMENT BY GAS CONTROL HAD TAKEN PLACE RELATIVE TO THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [52 empty] | HEAVY RAINS/FLOODS |  | MUDSLIDE |  |  |  | NO | [306 empty] | WILLIAM YOUSE | COMPLIANCE SPECIALIST | william_youse@transcanada.com | 304-357-3596 | 304-357-3522 |  |  |  | GEORGE HAMATY | MANAGER US REGULATORY COMPLIANCE EAST | (304) 357-3728 | george_hamaty@transcanada.com | THIS INCIDENT WAS THE RESULT OF LAND MOVEMENT (SLIP) OCCURRING ALONG THE RIGHT-OF-WAY, DUE TO SEVERAL DAYS OF HEAVY RAINS. THE ABOVE GROUND PIPELINE NUMBER 8012 SUFFERED BUCKLING DUE TO THE FORCE OF THE LAND MOVEMENT. FRACTURES RESULTED IN THESE BUCKLED AREAS WHICH WAS THE CAUSE OF THE GAS RELEASE. NO RUPTURE OR DISCONTINUITY OF THE PIPE OCCURRED. COLUMBIA GAS TRANSMISSION, LLC. (OPID 2616) (COLUMBIA) OWNS AND OPERATES PIPELINE 8012 WHICH IS AN 8.625-INCH, 0.277 WALL BARE STEEL LINE WITH A MAOP OF 70 PSIG. THE LOCAL COLUMBIA OPERATIONS PERSONNEL MADE THE SITE SAFE FOR THE PUBLIC. THE LEAK IS APPROXIMATELY 30 FEET FROM A RAILWAY. THE RAILROAD OPERATOR WAS CONTACTED BY COLUMBIA. THIS PIPELINE IS A SINGLE-FEED PIPELINE TO THE TOWN OF WESTERNPORT, MARYLAND. THE TOWN IS SERVED BY COLUMBIA GAS OF MARYLAND AND HAS 800-1200 GAS CUSTOMERS AT THE TIME OF THE INCIDENT. COLUMBIA GAS OF MARYLAND GAVE COLUMBIA GAS TRANSMISSION, LLC THE APPROVAL TO REDUCE THE PRESSURE TO 25 PSIG UNTIL THE REPAIRS COULD BE MADE. AN INITIAL REPORT WAS FILED WITH THE NATIONAL REPORTING CENTER (NRC) (NRC 1225754) ON SEPTEMBER 26, 2018 AND A 48-HOUR UPDATE WAS ALSO PROVIDED (NRC 1225907).
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180106 | 31537 | 2018-10-26 13:55 | SUPPLEMENTAL FINAL | 39167 | SABAL TRAIL TRANSMISSION, LLC (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2018-09-29 14:00 | 2018 |  |  | 30.0715 | -82.8852 | 1226291 | 2018-10-02 12:50 |  | NATURAL GAS |  | 26404 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | PIPELINE FLOW WAS BYPASSING COMPRESSOR WHERE EVENT OCCURRED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-09-30 09:48 | 2018-09-30 10:20 | ONSHORE | FL | 32071 | O'BRIEN | SUWANNEE | MILEPOST | 299.14 | HILDRETH COMPRESSOR STATION | HILD-DUNN | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2016 |  | CARBON STEEL |  | OTHER | [8 empty] | VALVE FAILED OPEN DUE TO BLOWN FUSE | CLASS 1 LOCATION | NO |  | 53 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 79212 | 71346.9787234043 | 1 | 1.04106980961015 | 0 | 0 | 0 | 0 |  |  | 79213 | 73969.1303607827 | 71348.0197932139 | [8 empty] | 256 |  | 1456 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [52 empty] | LIGHTNING |  |  | SECONDARY IMPACT SUCH AS RESULTING NEARBY FIRES |  |  | NO | [306 empty] | MAYRA SALINAS | ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: AT 2:00 PM ON SEPTEMBER 29, 2018, AN APPARENT LIGHTNING STRIKE AT OR NEAR THE ENBRIDGE SABAL TRAIL HILDRETH COMPRESSOR STATION IN O'BRIEN, FLORIDA CAUSED A FUSE ON A SAFETY DEVICE CIRCUIT INSIDE THE COMPRESSOR BUILDING TO BLOW. THIS CAUSED A 2-INCH FUEL GAS VALVE TO FAIL IN THE OPEN POSITION VENTING NATURAL GAS OUTSIDE THE COMPRESSOR BUILDING TO THE ATMOSPHERE. AT 9:48 AM ON SEPTEMBER 30, 2018 AN ENBRIDGE EMPLOYEE WAS ADVISED BY A NEARBY LANDOWNER ABOUT A NOISE COMING FROM THE COMPRESSOR STATION. ANOTHER ENBRIDGE EMPLOYEE WAS DISPATCHED TO THE COMPRESSOR STATION AND ISOLATED THE GAS RELEASE AT 10:20 AM ON SEPTEMBER 30, 2018. THE EVENT RESULTED IN A NATURAL GAS RELEASE OF 26.4 MILLION CUBIC FEET. SUPPLEMENTAL REPORT: 48 HR NRC REPORT 1226485 THE TIME LAG BETWEEN THE FIELD OPERATING PERSONNEL IDENTIFYING THE GAS RELEASE AT THE SABAL TRAIL HILDRETH COMPRESSOR STATION AND THE INITIAL REPORT TO THE NATIONAL RESPONSE CENTER (NRC) HAS IDENTIFIED THE NEED TO ADDITIONAL TRAINING AND AWARENESS OF THE REQUIREMENT TO IMMEDIATELY REPORT SUCH EVENTS TO INTERNAL PERSONNEL RESPONSIBLE FOR NRC NOTIFICATIONS. THE TRAINING WILL BE DEVELOPED AND IMPLEMENTED SYSTEM-WIDE IN 2019.
2021-02-26 10:37 | YES | YES | GT (Gas Transmission) | 20180107 | 31486 | 2018-10-26 16:06 | SUPPLEMENTAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2018-09-28 07:45 | 2018 |  |  | 27.7061 | -97.8653 | 1225979 | 2018-09-28 13:13 |  | NATURAL GAS |  | 0.1 | 0 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 |  | NO | THE INCIDENT DID NOT AFFECT THE OPERATIONS OF THE STATION. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-09-28 07:45 | 2018-09-28 07:45 | ONSHORE | TX | 78380 | ROBSTOWN | NUECES | SURVEY STATION NO. | ROBSTOWN CS | ROBSTOWN COMPRESSOR STATION | ROBSTOWN COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | INSTRUMENTATION | [38 empty] | 2007 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | ALUMINUM/STAINLESS STEEL/MONEL | OTHER | [8 empty] | PRESSURE GAUGE RUPTURE ON DISCHARGE FILTER OF COMPRESSOR | CLASS 1 LOCATION | NO |  | 425 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1561.60471441523 | 0 | 0 | 0 | 0 |  |  | 1500 | 716.817769718949 | 1561.60471441523 | [8 empty] | 1140 |  | 1170 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS INCIDENT OCCURRED DUE TO RUPTURING OF A PRESSURE GAUGE AND THE CONTROLLERS ACTIONS WERE NOT A FACTOR IN THIS INCIDENT. | [12 empty] | YES | 1 | 0 | NO |  |  | EQUIPMENT FAILURE | DEFECTIVE OR LOOSE TUBING OR FITTING | MATERIAL/WELD/EQUIP FAILURE | DEFECTIVE OR LOOSE TUBING/FITTING | [166 empty] | DEFECTIVE OR LOOSE TUBING OR FITTING | [25 empty] | YES | [172 empty] | ALEX ALCALA | REGULATORY COMPLIANCE ENGINEER | alex.alcala@energytransfer.com | 713-989-2021 |  |  |  |  | CHRISTOPHER KRESTA | MANAGER-INTRASTATE REGULATORY COMPLIANCE | 713-989-7077 | chris.kresta@energytransfer.com | ON 9-28-18, A PIPELINE OPERATOR HEARD A LEAK FROM A DIFFERENTIAL PRESSURE GAUGE AT APPROXIMATELY 7:15 AM, HE THEN PROCEEDED TO ISOLATE THE PIECE OF EQUIPMENT BY CLOSING THE SUPPLY VALVES. THE PIPELINE OPERATOR THEN NOTIFIED AN I&E TECHNICIAN WHO THEN ARRIVED ON SITE TO TROUBLESHOOT THE DIFFERENTIAL PRESSURE GAUGE. AT APPROXIMATELY 7:45 AM, THE I&E TECHNICIAN OPENED THE SUPPLY SENSING NEEDLE VALVES TO THE DIFFERENTIAL PRESSURE GAUGE ABOUT ONE TURN TO LISTEN FOR LEAKING GAS. AS HE WAS CLOSING THE NEEDLE VALVES, THE GAUGE COVER RUPTURED STRIKING THE EMPLOYEE IN THE ARM. THE RESULTING INJURY WAS A LACERATION ON THE EMPLOYEES LEFT ARM JUST BELOW THE ELBOW. THE EMPLOYEE WAS RUSHED INTO THE EMERGENCY ROOM AND ADMITTED OVERNIGHT. HE RECEIVED STITCHES TO THE LACERATION BUT DID NOT HAVE ANY BROKEN BONES OR ADDITIONAL SIGNIFICANT INJURIES. THE ROOT CAUSE HAS BEEN IDENTIFIED AS IMPROPER INSTALLATION OF THE TUBING TO THE HI PORT ON THE BACK OF THE DIFFERENTIAL PRESSURE GAUGE. THE DIFFERENTIAL PRESSURE GAUGE AND THE HOUSING ASSEMBLY CAME DIRECTLY FROM THE MANUFACTURER ALREADY MOUNTED ON THE DISCHARGE FILTER VESSEL. ETC DID NOT ASSEMBLE THE COMPONENTS. THIS SYSTEM IS UNDER THE JURISDICTION OF THE TX RRC AS INTRASTATE. THIS INCIDENT WAS TELEPHONICALLY REPORTED TO THE TX RRC ON SEPTEMBER 28, 2018 A 48 HR. NRC UPDATE WAS MADE ON OCTOBER 1, 2018 AT 08:50 HRS. INCIDENT REPORT # 1226171
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180108 | 31768 | 2018-11-07 10:54 | SUPPLEMENTAL | 12350 | CENTERPOINT ENERGY RESOURCES CORP., DBA CENTERPOINT ENERGY MINNESOTA GAS | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2018-09-20 20:16 | 2018 |  |  | 44.3352 | -93.2888 | 1225289 | 2018-09-21 09:46 |  | NATURAL GAS |  | 10367 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-09-20 21:40 | 2018-11-14 09:58 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2018-09-20 20:16 | 2018-09-20 22:05 | ONSHORE | MN | 55021 | FARIBAULT | RICE | MILEPOST | TOWN BORDER S | FARIBAULT TBS | 563-001 | NO | PIPELINE RIGHT-OF-WAY | BELOWGROUND STORAGE OR ABOVEGROUND STORAGE VESSEL, INCLUDING ATTACHED APPURTENANCE |  |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | FILTER/STRAINER/SEPARATOR | [38 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | FIRE AT TOWN BORDER STATION. | CLASS 2 LOCATION | NO |  | 117 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 29050 | 26165.6028368794 | 10327 | 10751.1279238441 | 73847 | 76879.882230281 | 0 | 0 |  |  | 113224 | 67352.0145234682 | 113796.612991005 | [8 empty] | 708 |  | 800 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO ALARMS OR ALERTS WERE RAISED IN SCADA AT THE TIME OF THE INCIDENT. SCADA COMMUNICATIONS WITH THE SITE WERE INSTANTANEOUSLY INTERRUPTED AT THE TIME THE INCIDENT OCCURRED. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [52 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | A STORM ' THUNDER, LIGHTNING, TORNADO, HIGH WINDS AND STATIC ELECTRICITY - CAME THROUGH THE FARIBAULT AREA. A CENTERPOINT ENERGY REGULATOR WAS DAMAGED DURING THE STORM CAUSING A FIRE. | YES |  |  | YES | [303 empty] | STEVE OLINGER | OPERATIONS SPECIALIST II | steve.olinger@centerpointenergy.com | 612.321.5453 |  |  |  |  | DEAN HEADLEE | PIPELINE SAFETY AND COMPLIANCE MANGER | 612.321.5366 | dean.headlee@centerpointenergy.com | SEPTEMBER 2018, A STORM ' THUNDER, LIGHTNING, TORNADO, HIGH WINDS AND STATIC ELECTRICITY - CAME THROUGH THE FARIBAULT AREA. A CENTERPOINT ENERGY REGULATOR WAS DAMAGED DURING THE STORM CAUSING A FIRE. THE STRAINER/ FILTER WAS DAMAGED BY THE FIRE. PRIOR TO CENTERPOINT ENERGY EMPLOYEES ARRIVING ON SCENE, NORTHERN NATURAL GAS HAD SHUT OFF THE FEED TO THE REGULATOR SYSTEM. CENTERPOINT ENERGY LOST COMMUNICATIONS WITH THE RTU UNIT DUE TO THE INCIDENT. NO ALARMS OR ALERTS WERE RAISED IN SCADA, HOWEVER, SCADA COMMUNICATIONS WITH THE SITE WERE INSTANTANEOUSLY INTERRUPTED AT THE TIME OF THE INCIDENT. AN INSULATOR, WHICH WAS CHECKED THE YEAR PRIOR, SEPARATING THE BUSINESS FROM CENTERPOINT ENERGY'S DISTRIBUTION, WAS SHORTED. THE INSULATOR WAS REPLACED AND IS FUNCTIONING PROPERLY. THE REGULATOR STATION IS ALSO FUNCTIONING PROPERLY. THE ROOT CAUSE FOR THE INCIDENT IS UNKNOWN.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180109 | 32128 | 2018-11-08 09:37 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2018-09-20 09:04 | 2018 |  |  | 40.4419 | -74.3147 | 1228268 | 2018-10-23 11:11 |  | NATURAL GAS |  | 0 | 185.58 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-09-20 09:04 | 2018-09-21 15:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-09-20 09:04 | 2018-09-20 10:00 | ONSHORE | NJ | 08859 | OLD BRIDGE | MIDDLESEX | SURVEY STATION NO. | 99+29 | STATION 207 | COMPRESSOR BLOWDOWN UNIT 3 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2017 |  | CARBON STEEL |  | OTHER | [8 empty] | CLOSED DRAIN VALVE | CLASS 2 LOCATION | NO |  | 100000 |  | NO | NO | NO |  | 0 | 0 | 540 | 562.177697189483 | 0 | 0 | 200000 | 208213.961922031 | 4000 | 4164.27923844062 | 27000 | 28108.8848594742 | CARBON REPLACEMENT FOR DEODERIZER |  | 231540 | 110647.990933817 | 241049.303717135 | [8 empty] | 714 |  | 1000 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS DUE TO A OPEN 4" VALVE | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [204 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE |  |  |  |  | YES |  |  |  | OTHER MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | ROBERT T. FORD JR | OPERATIONS SUPERVISOR | robert.t.ford@williams.com | [5 empty] | MARK CLARKE | SENIOR ENGINEER | 7132153051 | mark.clarke@williams.com | AT APPROXIMATELY 8:04 AM CST ON 09/20/2018, UNIT #3 @ COMPRESSOR STA 207 WAS SCHEDULED FOR AN AUTOMATIC BLOW DOWN DUE TO AN UPCOMING PROJECT TO REMOVE THE INLET STRAINER. WHEN UNIT #3'S BLOWDOWN VALVE OPENED, GAS ENTERED THE CHARCOAL FILLED DEODORIZER AND WOULD NORMALLY FLOW UP AND OUT OF THE TOP OF THE STACK ABOVE THE BUILDING ROOFLINE TO ATMOSPHERE. DUE TO A 4" DRAIN LINE AT THE BOTTOM OF THE DEODORIZER VESSEL IN THE OPEN POSITION, THE VENTING GAS AND CHARCOAL WERE ABLE TO ENTER INTO THE DRAIN SYSTEM OF COMPRESSOR BUILDINGS 1&2. THIS IN TURN ACTIVATED BOTH BUILDINGS EMERGENCY SHUT DOWN (ESD) SYSTEMS AS DESIGNED AT 20% LEL (ESD) AND 40% LEL (ESD 2). THE STATION WAS SHUT DOWN IN A SAFE STATE AND THE BUILDING'S FANS EVACUATED THE GAS. WILLIAMS' PERSONNEL RESPONDED TO THE SITE AND INITIATED THE STATIONS EMERGENCY ACTION PLAN WITH THE LOCAL EMERGENCY RESPONDERS.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180110 | 31170 | 2018-11-08 12:44 | SUPPLEMENTAL FINAL | 5304 | FLORIDA GAS TRANSMISSION CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2018-10-11 02:00 | 2018 |  |  | 30.7791 | -85.5583 | 1227167 | 2018-10-11 07:22 |  |  |  | 0 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-10-11 02:00 | 2018-10-11 09:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-10-11 02:00 | 2018-10-11 03:00 | ONSHORE | FL | 32428 | CHIPLEY | WASHINGTON | MILEPOST | MP 12.5 | FGT CHIPLEY M&R | CHIPLEY LATERAL | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | METER | [38 empty] | 2010 |  | CARBON STEEL |  | OTHER | [8 empty] | METER RUN VALVE. | CLASS 3 LOCATION | NO |  | 27 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146000 | 151996.192203082 | 0 | 0 |  |  | 146000 | 69770.262919311 | 151996.192203082 | [8 empty] | 101 |  | 120 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | FAILURE OF FIELD EQUIPMENT. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [52 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | HURRICANE MICHAEL | YES | YES | [305 empty] | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | DUE TO SCHEDULED MAINTENANCE, ONE OF THE METER RUNS WERE OUT OF SERVICE, AND WITH POWER OUTAGE DURING THE HURRICANE, SERVICE WAS INTERRUPTED. FGT PLANS TO REVISE THE STATION DESIGN FOR THIS STATION, ALTER PROCEDURES FOR STORM PREPARATION AND REVIEW PROCEDURES AND PROCESSES WITH THOSE RESPONSIBLE FOR STATION MAINTENANCE TO PREVENT REOCCURRENCE. 10/11/18 MEASUREMENT TECHNICIAN RECEIVED NOTIFICATION FROM PUBLIC AT 02:00 THAT THE CITY OF CHIPLEY, FL WAS WITHOUT GAS. NRC TELEPHONIC NOTIFICATION MADE AT 07:22 NRC#1227167. PHMSA AID NOTIFIED. 10/11/18 FGT OPENED THE VALVE AND PRESSURED UP TO THE CUSTOMERS MAIN GATE STATION AT 09:00. 10/12/18 48-HOUR UPDATE NRC NOTIFICATION MADE AT 19:40 NRC#1227325. 10/15/18 CITY OF CHIPLEY WAS RETURNED TO FULL SERVICE, RELIGHT COMPLETE AT 07:45. SUPPLEMENTAL REPORT SUBMITTED 11/13/18, IS TO CORRECT THE LATITUDE/LONGITUDE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180111 | 31155 | 2018-11-08 14:01 | ORIGINAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2018-10-26 18:40 | 2018 |  |  | 35.5326 | -99.3737 | 1228821 | 2018-10-29 09:10 |  | NATURAL GAS |  | 4512 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELIEF VALVE WAS ISOLATED FROM PIPELINE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-10-26 18:47 | 2018-10-26 19:10 | ONSHORE | OK | 73650 | HAMMON | ROGER MILLS | MILEPOST | LINE 2 | LINE 2 | CARPENTER STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2018 |  | CARBON STEEL |  | OTHER | [8 empty] | PILOT VALVE FAILURE ON RELIEF VALVE. | CLASS 1 LOCATION | NO |  | 350 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 13800 | 12429.7872340426 | 1000 | 1041.06980961015 | 1000 | 1041.06980961015 | 0 | 0 |  |  | 15800 | 13842.281848987 | 14511.9268532629 | [8 empty] | 875 |  | 1000 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE SYSTEM WAS WELL WITHIN NORMAL PARAMETERS, AND NO CONTROL CHANGES HAD BEEN MADE WHICH WOULD HAVE CAUSED THIS YARD, OR LINE 2 SOUTH TO EXCEED MAOP. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | PILOT FAILURE | [161 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | ON 10/26/18 ENABLE GAS TRANSMISSION SYSTEM CONTROL RECEIVED A CALL FROM THE GENERAL PUBLIC OF A BLOWING RELIEF VALVE IN ROGER MILLS COUNTY, OKLAHOMA. AN EMPLOYEE WAS DISPATCHED AND WHEN THEY ARRIVED TO THE SITE COULD SEE A RELIEF VALVE BLOWING. THE TECHNICIAN INSTALLED A PRESSURE GAUGE AND VERIFIED PRESSURE TO BE BELOW MAOP. THE VALVE WAS SHUT IN STOPPING THE VENTING GAS. PRESSURE WAS RECHECKED TO ASSURE THERE WERE NO PRESSURE PROBLEMS. THE VALVE WAS ISOLATED UNTIL REPAIRS COULD BE COMPLETED. DURING REPAIR, THE VALVE WAS ACTIVATING AROUND 700 PSIG AND THE CONTRACTOR REBUILT THE PILOT ON THE VALVE. THE VALVE WAS RE-TESTED AND PLACED INTO SERVICE. ORIGINALLY, THE GAS LOSS WAS CALCULATED TO BE NEAR 800 MCF. ON 10/29/18 IT WAS DETERMINED THE ORIGINAL CALCULATION USED INCORRECT RELIEF VALVE SIZING AND WAS RECALCULATED FOR A GAS LOSS OF 4512 MCF. THE NRC WAS NOTIFIED ON 10/29/18 09:10 (NRC#1228821). THE 48 HOUR FOLLOW UP WAS PROVIDED ON 10/31/18 07:20 (NRC# 1229004).
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180112 | 31168 | 2018-11-13 09:06 | ORIGINAL FINAL | 26330 | ENABLE OKLAHOMA INTRASTATE TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2018-10-20 09:30 | 2018 |  |  | 35.2688 | -97.9439 | 1228020 | 2018-10-20 12:45 |  | NATURAL GAS |  | 4200 | 845 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-10-20 13:00 | 2018-10-21 20:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-10-20 09:40 | 2018-10-20 10:00 | ONSHORE | OK | 73059 | MINCO | GRADY | MILEPOST | L-107 | L-107 | 267+90 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.219 | 60000 | API-5LX | LONGITUDINAL ERW - HIGH FREQUENCY |  | US STEEL | COAL TAR | [28 empty] | 1972 | 1972 | CARBON STEEL |  | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 1 LOCATION | NO |  | 343 |  | NO | NO | NO |  | 0 | 0 | 2422 | 2521.47107887579 | 12038 | 10842.7375886525 | 35000 | 36437.4433363554 | 2500 | 2602.67452402538 | 0 | 0 |  |  | 51960 | 30319.0243942482 | 52404.326527909 | [8 empty] | 750 |  | 960 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL |  | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS RELATED TO 3RD PARTY DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | YES |  |  |  |  | YES | [6 empty] | CONTRACTOR | TRENCHER | NATURAL GAS | YES | 18101614292635 |  | UTILITY OWNER | YES | YES | YES | 31 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | EXCAVATION PRACTICES NOT SUFFICIENT (OTHER) | [263 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MGR. | casey.roberts@enablemidstream.com | 405 558 4647 |  |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MGR. | 405 558 4647 | casey.roberts@enablemidstream.com | ON OCTOBER 20TH A CONTRACTOR (BENNETT CONSTRUCTION) WORKING FOR CARDINAL MIDSTREAM STRUCK ENABLE OKLAHOMA INTRASTATE TRANSMISSION LINE 107 CAUSING SMALL LEAK SIGNIFICANT ENOUGH TO REROUTE GAS AND BLOW DOWN AND REPLACE PIPE. THIS SECTION OF L-107 HAD BEEN PREVIOUSLY MARKED BY ENABLE WHO MADE POSITIVE CONTACT WITH BENNET ON 10/18/18 REQUESTING NOTIFICATION BEFORE DIGGING. IT WAS ALSO DISCUSSED ON 10/18/18 THAT ENABLE PERSONNEL WOULD MEET WITH BENNETT ON MONDAY, 10/22/2018, WHILE THEY CROSSED LINE 107. BENNETT WORKED ON SATURDAY 10/20/18 WITHOUT ENABLE OR CARDINAL KNOWLEDGE (AND WITHOUT ENABLE PERSONNEL PRESENT), AND DID NOT RESPECT THE 24" TOLERANCE ZONE. ENABLE DID NOT RECEIVE CALL FOR WORK THAT WAS PERFORMED ON 10/20/18. L-107 WAS COMPLETELY PUT BACK INTO SERVICE AND RELEASED TO SYSTEM CONTROL TO RESUME NORMAL OPERATIONS AT APPROXIMATELY 8:00 PM 10/21/2018. A NOTIFICATION WAS PROVIDED TO THE NRC (#1228020) ON 10/20/18 AT 12:45 AND A 48 HR. FOLLOW UP (# 1228152) WAS PROVIDED ON 10/22/18 AT 11:28. AFTER REVIEW OF THE NRC ARCHIVE, #1228184 WAS ADDED TO THIS INCIDENT AS WELL.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180113 | 32471 | 2018-11-15 13:59 | SUPPLEMENTAL FINAL | 2731 | CHEVRON PIPE LINE CO | 1400 SMITH STREET | HOUSTON | TX | 77002 | 2018-10-17 19:47 | 2018 |  |  | 38.0316 | -121.9352 | 1227786 | 2018-10-17 19:53 |  | NATURAL GAS |  | 7.1 | 1400 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-10-17 19:48 | 2018-10-26 21:10 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 4000 | 2018-10-17 19:47 | 2018-10-17 19:26 | ONSHORE | CA | 94565 | BAY POINT | CONTRA COSTA | MILEPOST | MILEPOST 29.2 | NORTHERN CALIFORNIA NATURAL GAS PIPELINE | CAL0007 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | OTHER | VALVE SITE LOCATION |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | TUBING | [38 empty] | 2003 |  | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 216 |  | NO | NO | NO |  | 0 | 0 | 2851 | 2968.09002719855 | 14 | 12.6099290780142 | 327442 | 340889.980598368 | 100000 | 104106.980961015 | 0 | 0 |  |  | 430307 | 205640.852343169 | 447977.66151566 | [8 empty] | 430 |  | 686 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | REMOTELY CONTROLLED | 69234 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, BUT THE INVESTIGATION OF THE CONTROL ROOM AND/OR CONTROLLER ACTIONS HAS NOT YET BEEN COMPLETED BY THE OPERATOR (SUPPLEMENTAL REPORT REQUIRED) | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | [103 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [261 empty] | GARRETT S. PARKER | DOT SPECIALIST | parkerg@chevron.com | 7133726847 | 7133725968 |  |  |  | GARRETT S. PARKER | DOT SPECIALIST | 7133726847 | parkerg@chevron.com | 10/17/2018 17:48- FIRE DEPARTMENT DISPATCHED TO FIRE ON RIGHT OF WAY(ROW) DUE TO DOWNED POWERLINE 18:30- FIRE DEPARTMENT NOTIFIED CONTROL CENTER OF FIRE ON ROW 18:37- CONTROL CENTER NOTIFIED FIELD TEAM MEMBER ABOUT FIRE ON ROW MILEPOST 29.2 18:39- FIELD TEAM MEMBER NOTIFIED TEAM LEADER OF FIRE 19:26- FIELD TEAM MEMBER ARRIVES ON SITE AND ESTABLISHES UNIFIED COMMAND WITH FIRE DEPARTMENT 19:31- UPDATE TO TEAM LEADER OF CURRENT SITUATION 19:47- FIELD TEAM MEMBER NOTIFIES CONTROL HE HEARS HISSING FROM PIPELINE 19:48- CONTROL CENTER BLOCKED IN PIPELINE(SHUTDOWN) 20:20- TEAM LEADER ON SITE 20:34- FIRE DEPARTMENT ESTABLISHES HOT ZONE WITH NO ENTRY 21:26- COMMAND POST SET UP 22:08- LAW ENFORCEMENT BEGINS EVACUATIONS OF HOMES 10/18/2018 15:04- FIRE CONFIRMED OUT AND EVACUATION IS LIFTED 10/19/2018 NITROGEN PURGE OF PIPELINE LOS MEDANOS TO AVON WORK CONTINUES TO FIX VALVE. 10/25/2018 FIRST DAY OF RESTART OF PIPELINE 10/26/2018 APPROXIMATELY 21:10 LINE IS FULLY OPERATIONAL AND RUNNING IT WAS CONFIRMED THE SOURCE OF THE FAILURE ON THE PIPELINE WAS ARCING FROM THE VALVE BOX INTO THE PIPELINE CAUSED BY A DOWNED POWERLINE ACROSS THE VALVE BOX.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180114 | 33102 | 2018-11-15 18:17 | SUPPLEMENTAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2018-10-18 10:15 | 2018 |  |  | 30.1749 | -91.514 | 1227837 | 2018-10-18 11:21 |  | NATURAL GAS |  | 474 | 969 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | IM ANOMALY REPAIR PROJECT, LINE WAS NOT RETURNED TO SERVICE BEFORE LEAK | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-10-18 10:15 | 2018-10-18 10:15 | ONSHORE | LA | 70582 | Not Within a Municipality | ST. MARTIN | MILEPOST | 17 - 02+08 | SOUTH SECTION 28 LINE | MILEPOST 17 - JAKE'S BAYOU | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | UNDER JAKE'S BAYOU | 336 |  | YES | [6 empty] | YES | UNCASED | JAKE'S BAYOU | 10 | BELOW WATER, PIPE BURIED BELOW BOTTOM (NOT IN BORED/DRILLED CROSSING) | [11 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.344 | 52000 | API-5L | FLASH WELDED |  | A O SMITH | COAL TAR | [28 empty] | 1958 | 1957 | CARBON STEEL |  | MECHANICAL PUNCTURE | 3.3 | 2 | [7 empty] | CLASS 1 LOCATION | NO |  | 458 |  | NO | NO | NO |  | 0 | 0 | 2772 | 2885.84551223935 | 1356 | 1221.36170212766 | 2000000 | 2082139.61922031 | 1200 | 1249.28377153218 | 250000 | 260267.452402538 | COST OF SPECIMEN RETRIEVAL |  | 2255328 | 1078391.02916739 | 2347763.56260875 | [8 empty] | 26 |  | 1100 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 151880 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK FROM 2ND PARTY EXCAVATION DAMAGE OCCURRED AT 26 PSIG WHILE OPERATOR WAS RE-PRESSURIZING THE PIPELINE FOR RETURN TO SERVICE WHILE ANOMALY PROJECT WAS TEMPORARILY HALTED; | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [10 empty] | NO | YES | OTHER |  |  | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 180517556 |  | CONTRACT LOCATOR | YES | YES |  |  | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO MAINTAIN CLEARANCE | [263 empty] | WM. MARTIN MULLER | SPECIALIST-PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205-325-3863 | 205-325-3592 |  |  |  | JAIME HERNANDEZ | DIRECTOR ENGINEERING CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | BECAUSE OF PIPELINE DEPTH AND DEVELOPING SITE CONDITIONS, A PREVIOUSLY PLANNED ANOMALY REPAIR PROJECT HAD BEEN HALTED WITH THE DECISION TO RETURN THE PIPELINE TO SERVICE UNTIL NECESSARY PROJECT DETAILS AND ADDITIONAL PLANS WERE ESTABLISHED TO PROPERLY CONTINUE THE ANOMALY REPAIR PROJECT. OCTOBER 18, 2018, OPERATIONS HAD BEGUN FLOWING NATURAL GAS INTO THE VACATED VALVE SECTION. TWENTY MINUTES INTO THE RE-PRESSURE PROCESS, SNG OPERATIONS AND SNG ANOMALY REPAIR CONTRACT EMPLOYEES NOTICED BUBBLES APPEARING IN JAKE'S BAYOU. VALVES WERE IMMEDIATELY CLOSED; RELEASE OF NATURAL GAS WAS AN EIGHT MINUTE DURATION. PRESSURE OF THE NATURAL GAS IN THE VALVE SECTION WAS 26 PSIG. WITH THE VALVE SECTION AT ZERO PRESSURE, OCTOBER 31, 2018, THE SNG CONTRACTOR SUCCESSFULLY RECOVERED THE PIPE CONTAINING EXCAVATION DAMAGE. FOLLOWING THE NECESSARY PERMITTING PROCESS AND THE BEGINNING OF LOW WATER SEASON IN THE BAYOU, THIRD QUARTER 2019, SNG'S CONTRACTOR BEGAN THE PIPELINE REPAIR PROCESS IN JAKE'S BAYOU. DECEMBER 04, 2019, SNG RETURNED THE REPAIRED PORTION OF THE SOUTH SECTION 28 LINE TO SERVICE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180115 | 31187 | 2018-11-16 09:35 | ORIGINAL FINAL | 26330 | ENABLE OKLAHOMA INTRASTATE TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2018-10-22 08:25 | 2018 |  |  | 35.3243 | -97.6122 | 1228144 | 2018-10-22 10:37 |  | NATURAL GAS |  | 5100 | 16 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-10-22 09:30 | 2018-11-01 07:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-10-22 08:30 | 2018-10-22 09:15 | ONSHORE | OK | 73173 | OKLAHOMA CITY | CLEVELAND | MILEPOST | 78+08 | LINE 106B | LINE 106B | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | IN OR SPANNING AN OPEN DITCH |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 |  | 0.203 | 42000 | API-5LX | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | LONE STAR STEEL | COAL TAR | [28 empty] | 1960 | 1960 | CARBON STEEL |  | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 1 LOCATION | NO |  | 215 |  | NO | NO | NO |  | 1000 | 1041.06980961015 | 250 | 260.267452402538 | 14618 | 13166.5673758865 | 90000 | 93696.2828649139 | 2500 | 2602.67452402538 | 0 | 0 |  |  | 108368 | 58451.4888580253 | 110766.862026838 | [8 empty] | 400 |  | 668 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | AUTOMATIC | 28500 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | 3RD PARTY DAMAGE DETERMINED AS CAUSE OF INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  | YES | PRIVATE BUSINESS | YES | [6 empty] | OCCUPANT | GRADER/SCRAPER | WATERWAY IMPROVEMENTS | NO | [5 empty] | NO |  | DATA NOT COLLECTED | [266 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | LINE 106B WAS STRUCK ON 10/22/18 BY A DOZER PERFORMING WATER REMEDIATION ACTIVITIES IN CLEVELAND COUNTY, OKLAHOMA. THE DAMAGE OCCURRED IN THE MIDDLE OF A SAND/DIRT PIT RIGHT NEXT TO A LARGE POND THAT WAS FLOODED WITH UP TO 24" OF WATER. THE BULLDOZER WAS OWNED AND OPERATED BY BUTLER BROS. SAND WHO ALSO OWNED THE LAND. BUTLER BROS. WAS TRYING TO DRAIN THE AREA BY LEAVING TRACK RUTS IN THE WET MUD, ALLOWING A PATH FOR THE WATER TO DRAIN TO NEARBY RUN OFF AREAS. AS THE DOZER WAS CROSSING A BERM NEAR AN EXPOSED SECTION OF L-106B (WHICH WAS ALL UNDERWATER, BUT IDENTIFIED WITH PIPELINE MARKERS). THE SATURATED BERM COLLAPSED UNDER THE WEIGHT OF THE DOZER. THE DOZER SLID DOWN THE EDGE OF THE BERM EMBANKMENT INTO THE EXPOSED SECTION OF LINE CREATING DAMAGE TO THE PIPE AND CAUSING IT TO LEAK GAS. ENABLE GAS CONTROL WAS NOTIFIED IMMEDIATELY AND INITIATED SHUT-IN FOR THAT SECTION OF L-106B. ENABLE O&M REPRESENTATIVES ARRIVED SHORTLY THEREAFTER TO CONTINUE TO ASSESS THE SITUATION AND CLOSE THE UPSTREAM VALVE. THE AREA WAS DRAINED AND THE PIPE WAS EVALUATED. IT WAS CONFIRMED THE DAMAGED PIPE WAS LOCATED IN AN OPEN SPAN THAT AT THE TIME OF THE INCIDENT WAS ALL UNDERWATER. THE OPEN SPAN WAS NEAR A ROAD AND WAS IDENTIFIED WITH SIGNAGE AT THE BEGINNING AND END OF THE EXPOSURE. DURING REPLACEMENT, A DECISION WAS MADE TO INCREASE THE DEPTH OF THE PIPELINE ELIMINATING THE EXPOSURE AND REDUCING THE CHANCE FOR LINE STRIKES IN THE FUTURE. THE LINE WAS RETURNED TO SERVICE ON 11/1/2018. A CALL WAS PLACED TO THE NRC ON 10/22/18 AT 10:37 (NRC#1228144) AND A 48 HOUR FOLLOW UP WAS PROVIDED ON 10/24/18 AT 09:30 (NRC #1228370).
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180116 | 31831 | 2018-11-16 10:37 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2018-10-19 10:50 | 2018 |  |  | 28.6597 | -96.9984 | 1227933 | 2018-10-19 10:56 |  | NATURAL GAS |  | 201.4 | 10579.1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-10-19 10:20 | 2018-11-03 19:05 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-10-18 17:39 | 2018-10-18 22:22 | ONSHORE | TX | 77905 | Not Within a Municipality | VICTORIA | SURVEY STATION NO. | 470+14.5 | LINE 100-2 | 5-2 (MLV) TO 9-2S | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 42 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 |  | 0.25 | 52000 | X52 | DSAW |  | REPUBLIC | COAL TAR | [28 empty] | 1949 | 1949 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 454 |  | NO | NO | NO |  | 20000 | 20821.3961922031 | 32689 | 34031.5310063463 | 627 | 564.744680851064 | 300000 | 312320.942883046 | 10000 | 10410.6980961015 | 0 | 0 |  |  | 363316 | 173906.776508298 | 378149.312858548 | [8 empty] | 719 |  | 750 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 69168 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL ROOM WAS NOT THE CAUSE OR CONTRIBUTING FACTOR TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING | [6 empty] | YES | ELECTROCHEMICAL |  |  |  | YES |  |  | YES | YES | 1956 | YES | YES | YES |  |  |  | 2017 |  |  |  | YES | [190 empty] | YES | YES |  |  | YES |  |  |  | 2011 | [31 empty] | 2011 | [23 empty] | YES | 1991 | 1042 | NO | [13 empty] | NO | [63 empty] | KRISTIN VAN DER LAAN | COMPLIANCE CODES AND STDS MANAGER - ENGINEERING | kristin_vanderlaan@kindermorgan.com | 303-914-7753 |  |  |  |  | JAIME HERNANDEZ | COMPLIANCE CODES AND STDS DIRECTOR - ENGINEERING | 713-369-9443 | jaime_hernandez@kindermorgan.com | OCTOBER 18, 2018 17:39 - TENNESSEE GAS PIPELINE COMPANY (TGP) OPERATIONS PERSONNEL NOTIFIED BY THE LANDOWNER OF A POSSIBLE LEAK, PERSONNEL DEPLOYED TO THE LOCATION. 22:22 - SUSPECTED SITE FOUND BASED ON LANDOWNER DESCRIPTION. NO VISIBLE EVIDENCE OF A LEAK. AREA MONITORED OVERNIGHT. OCTOBER 19, 2018 10:00 - SMALL LEAK CONFIRMED ON LINE 100-2 USING GAS DETECTION EQUIPMENT. 10:27 - INITIATED INTERNAL EMERGENCY RESPONSE LINE (ERL) CALL NOTIFICATIONS PER COMPANY PROCEDURES TO DISCUSS THE INCIDENT. 10:45 - ERL CALL BEGAN. 10:50 - EVENT DETERMINED REPORTABLE TO NRC BASED ON REPAIR COSTS ESTIMATED OVER $50,000 DUE TO LOCATION AND WEATHER CONDITIONS. CALL TO NRC MADE FOLLOWED BY COURTESY CALL TO PHMSA ACCIDENT INVESTIGATION TEAM. 14:58 - COMPLETED LINE 100-2 BLOWN DOWN BETWEEN MLV 8-2 TO 9-2 16:40 - ONE-CALL TICKET (1879296796) ISSUED. OCTOBER 23, 2018 - ONE-CALL TICKET CLEARED. BECAUSE ACCESS TO LEAK SITE WAS VERY MUDDY AND THERE WAS STANDING WATER THROUGHOUT THE ROAD, IT WAS NECESSARY TO LAY MATS TO OBTAIN ACCESS. THIS TOOK APPROXIMATELY ONE WEEK TO LAY ALL OF THE MATS TO ACCESS THE SITE. DURING THIS TIME, THE LINE REMAINED BLOWN DOWN. OCTOBER 31, 2018 - MATTING COMPLETED AND PIPELINE EXPOSED IN PREPARATION FOR INSPECTION. NOVEMBER 1, 2018 - NDE PERFORMED AND IT APPEARS THAT THE LEAK WAS THE RESULT OF EXTERNAL METAL LOSS. DETERMINATION MADE TO REPLACE THE PIPE JOINT. NOVEMBER 2, 2018 - PIPE REPLACEMENT COMPLETED. NOVEMBER 3, 2018 - BELL HOLE BACKFILLED. LINE BACK IN SERVICE AT 7:05PM. POST-INCIDENT: BACTERIAL ANALYSIS PERFORMED. RESULTS WERE INCONCLUSIVE. MARCH 14, 2019 - METALLURGICAL TESTING REPORT COMPLETED AND CONCLUDED THAT THE CAUSE OF THE PINHOLE LEAK WAS ELECTROCHEMICAL EXTERNAL CORROSION AND THAT THE CHARACTERISTICS COMMONLY ASSOCIATED WITH MICROBIOLOGICALLY INDUCED CORROSION (MIC) WERE NOT PRESENT. ADDITIONAL NOTES: 48-HOUR NRC REPORT #1228045
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180117 | 32673 | 2018-11-16 16:15 | SUPPLEMENTAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2018-10-18 10:50 | 2018 |  |  | 27.5289 | -97.9619 | 1227857 | 2018-10-18 13:26 |  | NATURAL GAS |  | 213570 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-10-18 11:35 | 2018-11-12 09:00 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 0 | 2018-10-18 11:10 | 2018-10-18 11:08 | ONSHORE | TX | 78364 | KINGSVILLE | KLEBERG | MILEPOST | 498+54 | 3045 AQUA DULCE TO LOMA BLANCA | 3045 AQUA DULCE TO LOMA BLANCA | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 96 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.25 | 52000 | API 5L | OTHER | LONGITUDINAL ERW - DC | YOUNGSTOWN SHEET AND TUBE | COAL TAR | [28 empty] | 1964 | 1964 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 16 | 21.5 |  | CLASS 1 LOCATION | NO |  | 425 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 728273 | 655962.205673759 | 250000 | 260267.452402538 | 0 | 0 | 0 | 0 |  |  | 978273 | 799535.432068997 | 916229.658076297 | [8 empty] | 1140 |  | 1170 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 41554 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) | [5 empty] | YES | [7 empty] | YES | 2 | 0 | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  |  |  |  | YES | [6 empty] | YES |  |  | YES | YES | 1965 | YES | YES | YES | YES |  |  | 2018 | 2018 |  |  | YES | [190 empty] | YES | [6 empty] | YES | [50 empty] | COMBINATION TOOL | 2013 |  |  |  |  | NO |  |  | NO | [13 empty] | NO | [63 empty] | ALEJANDRO ALCALA | REGULATORY COMPLIANCE ENGINEER | alejandro.alcala@energytransfer.com | 713-989-2021 |  |  |  |  | DANNY NICHOLS | SR. DIRECTOR OF REGULATORY COMPLIANCE | 713-989-7232 | danny.nichols@energytransfer.com | ON 10-18-18 AT APPROXIMATELY 10:50AM, ENERGY TRANSFER EXPERIENCED A RELEASE OF NATURAL GAS ON THE 3045 AQUA DULCE TO LOMA BLANCA SYSTEM IN KINGSVILLE, TX. ENERGY TRANSFER PERSONNEL ARRIVED ON SITE AT APPROXIMATELY 11:08 AM AND IDENTIFIED AT 11:10 AM THAT THE PIPELINE BELONGED TO ENERGY TRANSFER. COMPANY PERSONNEL IMMEDIATELY PROCEEDED TO SHUT IN PIPELINE BY SHUTTING IN THE UPSTREAM MAINLINE VALVE AND DOWNSTREAM MAINLINE VALVE AT 11:35AM AND 12:07PM RESPECTIVELY. THE AFFECTED PIPE SEGMENT WAS CUT OUT AND SENT TO A LABORATORY FOR TESTING AND REPLACED WITH PRE-TESTED PIPE. ENERGY TRANSFER RAN MULTIPLE ILI INSPECTION TOOLS TO VERIFY PIPELINE INTEGRITY. THE PIPELINE WILL BE BROUGHT BACK TO NORMAL SERVICE FOLLOWING SUCCESSFUL ILI INSPECTION. THE CAUSE OF THIS RELEASE IS CURRENTLY UNDER INVESTIGATION. 48HR FOLLOW UP NRC # 1227958. THIS FACILITY IS UNDER THE JURISDICTION OF THE TEXAS RAILROAD COMMISSION. UPDATE MADE ON 3/29/2019 THE CAUSE OF THIS RELEASE HAS BEEN IDENTIFIED AS EXTERNAL MICROBIOLOGICALLY INDUCED CORROSION. THE PIPELINE WAS BROUGHT BACK TO SERVICE WITH NO PRESSURE RESTRICTIONS ON 3-21-19 FOLLOWING A SUCCESSFUL ILI ASSESSMENT. UPDATE MADE ON 9/6/2019 WE RECEIVED A FINAL ROOT CAUSE ANALYSIS FROM A 3RD PARTY CONTRACTOR. THEIR ANALYSIS ATTRIBUTED THE CAUSE OF THE FAILURE TO EXTERNAL CORROSION WHICH LED TO A DUCTILE OVERLOAD. IN AN EFFORT TO PREVENT REOCCURRENCE , ENERGY TRANSFER WILL BE CONDUCTING ADDITIONAL VERIFICATION DIGS ON THIS SYSTEM AND A CLOSE INTERVAL SURVEY WILL BE CONDUCTED IN CONJUNCTION WITH THE NEXT SCHEDULED IN LINE INSPECTION.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180118 | 31504 | 2018-11-17 12:58 | SUPPLEMENTAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2018-10-18 17:35 | 2018 |  |  | 30.6569 | -92.0267 | 1228019 | 2018-10-20 12:10 |  | NATURAL GAS |  | 1.724 | 1995 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-10-18 17:43 | 2018-10-19 18:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-10-18 17:35 | 2018-10-18 17:35 | ONSHORE | LA | 70589 | WASHINGTON | ST. LANDRY | MILEPOST | VALVE 2 | COMPRESSOR STATION 54 | N/A | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 42 |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | UNKNOWN |  | CARBON STEEL |  | LEAK |  |  | OTHER | LEAKING FROM STUDS AND FLANGE | [5 empty] | CLASS 1 LOCATION | NO |  | 75 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 260267.452402538 | 0 | 0 | 0 | 0 |  |  | 250000 | 119469.628286491 | 260267.452402538 | [8 empty] | 700 |  | 780 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE VALVE WAS LEAKING FROM THE FLANGE AND STUDS. THEREFORE, IT DID NOT CONSTITUTE AN INVESTIGATION INTO THE SCADA SYSTEM. THE SCADA DID NOT AND WOULD NOT PLAY A ROLE IN THE LEAK. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [30 empty] | YES | BODY FLANGE NEEDED TO BE TORQUED. CONTINUED IN SUMMARY DUE TO FONT COUNT LIMITS. | [161 empty] | STEPHANIE ROSS | PIPEINE SAFETY ENGINEER | stephanie.ross@williams.com | 713-215-4163 |  |  |  |  | CINT RATKE | MANAGER PIPELINE SAFETY | 918-573-6724 | clint.ratke@williams.com | ON OCTOBER 18, 2018, AT STATION 54, THE SUSPECTED LEAK WAS DISCOVERED BY AN EMPLOYEE WALKING THROUGH THE STATION YARD AND SAW BUBBLES AROUND THE VALVE. UPON FURTHER INVESTIGATION, AT 5:35 PM THE LEAK WAS CONFIRMED TO BE GAS. THE STATION WAS ISOLATED AND BLOWN DOWN. HAND DIGGING WAS INITIATED AT 6:30PM. HYDROVAC TRUCK SHOWED UP AROUND 7P AND EXPOSED THE VALVES. ON 10/19/18, THE YARD WAS PURGED AND PACKED TO 300PSI AND THE LEAK POINTS WERE VERIFIED AT 6:00AM. VALVE WAS MONITORED AND RETURNED TO SERVICE AT 6PM. THE VALVE CONTINUED TO BE MONITORED AND THE MANUFACTURER WAS CONTACTED FOR REPAIR RECOMMENDATIONS. THE LEAK WAS ON A GROVE BALL VALVE WITH A FLANGED BODY. THE RECOMMENDED REPAIR METHOD WAS TO TORQUE THE FLANGED BODY. ON 10/30/18, THE VALVE BODY BOLTS WERE RE-TORQUED TO MANUFACTURERS TORQUE SPECIFICATIONS AND THE LEAK WAS STOPPED. RETURNED TO SERVICE AT 3PM. CONTINUED FROM G6 ITEM 6: BODY FLANGE NEEDED TO BE TORQUED. THE VALVE'S FLANGED BODY IS OVER 40 YEARS OLD AND IS BELIEVED TO HAVE LOST SOME TORQUE OVER THE YEARS DUE TO AGE ALONG WITH EXPANSION AND CONTRACTION WITH TEMPERATURE AND TIME. UPDATE 1/17/2019 - LEAK WAS REPORTED TO THE NRC ON 10/20/2018 WHEN THE COST OF THE REPAIR WAS DISCOVERED TO BE EXPECTED TO EXCEED $50K.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180119 | 31236 | 2018-11-19 08:18 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2018-10-26 12:30 | 2018 |  |  | 30.5236 | -92.862 | 1228623 | 2018-10-26 13:30 |  | NATURAL GAS |  | 35600 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELIEF VALVE WAS ISOLATED WHICH DID NOT REQUIRE PIPELINE SHUTDOWN | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-10-26 13:00 | 2018-10-26 14:10 | ONSHORE | LA | 70648 | KINDER | ALLEN | MILEPOST | 82 | LINE 18 | GILL-OPEL | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | RELIEF VALVE | 1982 |  | CARBON STEEL |  | OTHER | [8 empty] | GAS RELEASE FROM RELIEF VALVE | CLASS 1 LOCATION | NO |  | 633 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 115700 | 104212.056737589 | 1500 | 1561.60471441523 | 0 | 0 | 0 | 0 |  |  | 117200 | 108758.188928111 | 105773.661452004 | [8 empty] | 840 |  | 936 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 45426 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURES THAT WOULD HAVE BEEN WITNESSED BY SCADA WOULD NOT HAVE BEEN OUTSIDE ACCEPTABLE LIMITS THEREFOR NO ALARMS WOULD HAVE BEEN RECEIVED BY THE CONTROLLERS | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | SENSING LINE FROM PIPELINE TO RELIEF VALVE BLOCKED WITH FOREIGN MATERIAL | [161 empty] | DWAYNE TESCHENDORF | ENGINEER SPECIALIST | dwayne.teschendorf@enbridge.com | 713-627-5573 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | A LANDOWNER NOTIFIED ENBRIDGE THAT THE SOUND OF A NATURAL GAS RELEASE WAS COMING FROM THE VICINITY OF THE TEXAS EASTERN TRANSMISSION, LP NATURAL GAS PIPELINE APPROXIMATELY 2.5 MILES NORTHWEST OF KINDER, LOUISIANA IN A REMOTE AREA. ENBRIDGE PERSONNEL WERE IMMEDIATELY DISPATCHED TO THE SITE AND CLOSED THE BLOCK VALVE BELOW THE RELIEF VALVE WHICH WAS THE SOURCE OF THE GAS RELEASE. BECAUSE THE BLOCK VALVE IMMEDIATELY BELOW THE RELIEF VALVE WAS CLOSED WHICH COMPLETELY ISOLATED THE SOURCE OF NATURAL GAS RELEASE, IT WAS NOT NECESSARY TO CLOSE THE MAINLINE BLOCK VALVES UPSTREAM AND DOWNSTREAM OF THE RELIEF VALVE. THE PRESSURE SENSING LINE BETWEEN THE RELIEF VALVE PILOT AND MAINLINE WAS DETERMINED TO BE BLOCKED BY FOREIGN MATERIAL. THE SENSING LINE WAS CLEARED OF FOREIGN MATERIAL AND THE RELIEF VALVE RETURNED TO SERVICE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180120 | 31218 | 2018-11-21 14:22 | ORIGINAL FINAL | 12408 | DTE GAS COMPANY | ONE ENERGY PLAZA | DETROIT | MI | 48226 | 2018-10-22 08:21 | 2018 |  |  | 44.7719 | -84.8496 | 1228336 | 2018-10-23 18:29 |  | NATURAL GAS |  | 8650 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | COMPRESSOR STATION WAS NOT IN SERVICE AT THE TIME | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-10-22 08:22 | 2018-10-22 08:21 | ONSHORE | MI | 49733 | Not Within a Municipality | KALKASKA | MILEPOST | GOOSE CREEK | GOOSE CREEK COMPRESSOR STATION | BOILER FUEL LINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | INSTRUMENTATION | [38 empty] | 1996 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | ELECTRICAL FUSE | OTHER | [8 empty] | RELEASE FROM COMPRESSOR STATION EMERGENCY SHUTDOWN RELIEF DEVICE | CLASS 1 LOCATION | NO |  | 447 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 24740 | 22283.5460992908 | 0 | 0 | 500 | 520.534904805077 | 0 | 0 |  |  | 25240 | 23341.3033227668 | 22804.0810040959 | [8 empty] | 852 |  | 1050 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | YES | [5 empty] | YES |  |  | YES | [13 empty] | YES | [173 empty] | JOHN D LUEDERS | PRINCIPAL COMPLIANCE ENGINEER | john.lueders@dteenergy.com | 6166322646 | 6166322687 |  |  |  | JOHN D LUEDERS | PRINCIPAL COMPLIANCE ENGINEER | 6166322646 | john.lueders@dteenergy.com | FAILURE OF ELECTRICAL FUSE CAUSED SIGNAL FROM CONTROL PANEL TO INITIATE STATION ESD. AT THE TIME OF THE EVENT A FUEL SOURCE FROM OUTSIDE THE COMPRESSOR BLOCK VALVES WAS SUPPLYING AN AUXILIARY HEATING BOILER, AND THE FUEL SYSTEM FED BACK INTO THE STATION BLOW-DOWN SYSTEM.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180121 | 32256 | 2018-11-22 11:56 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2018-10-23 00:40 | 2018 |  |  | 29.011 | -96.053 | 1228924 | 2018-10-30 10:56 |  | NATURAL GAS |  | 9660 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELEASE WAS STOPPED BY CLOSING THE VALVE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-10-23 02:15 | 2018-10-23 02:20 | ONSHORE | TX | 77456 | MARKHAM | MATAGORDA | MILEPOST | STATION 24 | STATION 24 | NA | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1981 |  | CARBON STEEL |  | OTHER | [8 empty] | VALVE OPENED AS DESIGNED. NO ISSUES WITH VALVE. | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | [8 empty] | 945 |  | 1050 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM OPERATORS DISCOVERED AND RESPONDED TO THE RELEASE IN A SAFE, TIMELY, AND ACCEPTABLE MANNER. THE RELEASE WAS NOT ASSOCIATED WITH ANY ACTION THAT THE OPERATORS FAILED TO DO OR DID INCORRECTLY. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | EBD VALVE ACTUATOR MOVED NORMALLY CLOSED VALVE TO OPEN POSITION WITHOUT THE STATION EBD SYSTEM BEING ACTIVATED. | [19 empty] | YES | [165 empty] | STEPHANIE ROSS | PIPEINE SAFETY ENGINEER | stephanie.ross@williams.com | 713-215-4163 |  |  |  |  | CINT RATKE | MANAGER PIPELINE SAFETY | 918-573-6724 | clint.ratke@williams.com | OPERATORS AT MARKHAM GAS PROCESSING PLANT 0.6 MILES NORTH OF STATION 24 NOTICED AN INLET PRESSURE DROP. GOING OUTSIDE OF CONTROL ROOM THEY HEARD AND SAW GAS VENTING FROM BLOW DOWN SILENCER AT STATION 24. OPERATOR WENT TO STATION 24, VERIFIED THE EBD VALVE THAT HAD OPENED, AND OPERATED THE GAS-POWERED ACTUATOR TO CLOSE THE VALVE. THE VALVE WAS CLOSED COMPLETELY AND RELEASE STOPPED. THE CAUSE OF THE RELEASE WAS DUE TO A EIM VALVE ACTUATOR THAT MOVED AN EBD VALVE OPEN WITHOUT RECEIVING ANY SIGNAL TO DO SO. WHILE WE KNOW THE ACTUATOR WAS THE CAUSE WE DO NOT YET KNOW WHY THE ACTUATOR OPERATED. WE HAVE COMPLETED A TEMPORARY MOC, ISOLATED THE VALVE, AND REMOVED THE EIM GAS-POWERED ACTUATOR OFF OF THE VALVE. WE ARE STILL TRYING TO ARRANGE FOR A QUALIFIED SHOP TO INSPECT THE ACTUATOR TO DETERMINE THE ISSUE THAT CAUSE IT TO MOVE THE VALVE. WE INTEND TO HAVE A WILLIAMS REPRESENTATIVE PRESENT DURING THE INVESTIGATION TO VERIFY THE FINDINGS. 1/17/2019 - INITIAL GAS LOSS CALCULATIONS WERE ESTIMATED AT 1MMCF ON 10/23. UPON EXPORT OF DATA FROM THE CONTROL SYSTEM AT STATION 24 AND FURTHER ANALYSIS COMPLETED ON 10/26, IT WAS DETERMINED THE RELEASE VOLUME EXCEEDED 3 MMCF. PIPELINE SAFETY NOTIFIED THE NRC UPON RECEIPT OF THE CORRECTED CALCULATION. 6/10/2019 THE INSPECTION REPORT BY THE THIRD PARTY VENDOR- CI ACTUATION- DID NOT REVEAL ANY CAUSE OR ADDITIONAL INFORMATION. WILLIAM'S TECHS HAD PULLED AND INSPECTED THE SPOOL PIECE JUST AFTER THE EVENT. NOTHING WAS FOUND AT THAT TIME THAT WOULD INDICATE A FAILURE. BECAUSE THE SPOOL WAS PREVIOUSLY INSPECTED BY WILLIAMS PERSONNEL CI ACTUATION WAS NOT ABLE OR WILLING TO DETERMINE CAUSE OF FAILURE. NOTE FROM THIRD PARTY VENDOR: "ON FRIDAY DECEMBER 13TH, 2018 AT WILLIAMS PARTNERS FACILITY IN MARKHAM TEXAS, I DISASSEMBLED CUSTOMERS GAS OPERATED EMERGENCY BLOWDOWN EIM 1/4 TURN ACTUATOR FOR INSPECTION OF ITS COMPONENTS TO DETERMINE THE CAUSE OF ACTUATOR REPORTEDLY TRAVELING OPEN WITHOUT PROCESS CONDITIONS DICTATING THAT IT DO SO. UPON COMPLETING DISASSEMBLY OF THE SUBJECT ACTUATOR, SEVERAL WILLIAMS EMPLOYEES AND MYSELF VISUALLY INSPECTED ALL ACTUATOR COMPONENTS FOR ANY INDICATION OF EXCESSIVELY WORN, DEFECTIVE, OR FAILED PARTS. NONE WERE FOUND. I WAS AT THIS TIME INFORMED BY WILLIAMS EMPLOYEES THAT FOLLOWING ACTUATORS UNDESIRABLE OPERATION, BUT PRIOR TO MY DISASSEMBLY AND INSPECTION, MULTIPLE O-RINGS ON THE ACTUATOR MOUNTED TRAVEL CONTROL VALVE WERE REMOVED AND REPLACED WITH NEW TO PREVENT A RE-OCCURRENCE OF THE ABOVE NOTED UNDESIRED OPERATION. DUE TO FUNCTION CRITICAL PARTS (CONTROL VALVE O-RINGS) BEING REPLACED WITH NEW FOLLOWING THE SUBJECT INCIDENT, BUT PRIOR TO MY INSPECTION, I AM UNABLE TO PROVIDE AN EVIDENCE BACKED CAUSE OF THE AFOREMENTIONED UNDESIRED FUNCTION." EIM GAS-POWERED ACTUATORS THAT ARE ON THE EBD SYSTEM ARE OBSOLETE AND HARD TO OBTAIN REPAIR PARTS. PARTS ARE EXPECTED BY CI ACTUATION THIS WEEK (WEEK OF 6/10) AND WILL BE INSTALLED IMMEDIATELY ONCE RECEIVED. RETURN TO SERVICE EXPECTED WITHIN THE NEXT TWO WEEKS.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180122 | 32000 | 2018-11-26 16:39 | SUPPLEMENTAL FINAL | 39730 | MELISSA RENEWABLES | PO BOX 51710 | MIDLAND | TX | 79710 | 2018-10-30 17:15 | 2018 |  |  | 33.2773 | -96.5336 | 1229251 | 2018-11-02 12:02 |  | NATURAL GAS |  | 49.251 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-10-30 17:30 | 2018-11-02 18:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-10-30 17:15 | 2018-10-30 17:30 | ONSHORE | TX | 75454 | MELISSA | COLLIN | SURVEY STATION NO. | PIPELINE BORE | MELISSA RENEWABLES LLC. PIPELINE | MELISSA RENEWABLES LLC PIPELINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 204 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 4 |  | 0.337 | 64380 | API 5L X-52 .337 | LONGITUDINAL ERW - HIGH FREQUENCY |  | NEXTEEL CO., LTD. | EPOXY | [28 empty] | 2017 | 2017 | CARBON STEEL |  | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | NO |  | 119 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 1034 | 931.333333333333 | 70294 | 73180.9611967362 | 3500 | 3643.74433363554 | 0 | 0 | ALL REPAIRS WERE COMPLETED AND ARE INCLUDED IN 7B AND 7C. TOTAL IS $73,793.74. |  | 74828 | 36230.122554649 | 77756.038863705 | [8 empty] | 350 |  | 1480 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 24816 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | MELISSA RENEWABLES LLC. DOESN'T HAVE A "CONTROL ROOM" ENVIRONMENT. THE MELISSA RENEWABLES LLC. PLANT RECEIVED A LOW SALES PRESSURE ALARM FROM THE PLANT MONITORING ALARM PANEL. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | YES | YES | OTHER |  |  | YES | [6 empty] | UTILITY | BACKHOE/TRACKHOE | BUILDING CONSTRUCTION | YES | 1878535138 | TEXAS 811 | CONTRACT LOCATOR | YES | YES | NO |  | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | EXCAVATION PRACTICES NOT SUFFICIENT (OTHER) | [263 empty] | ALLAN DALE MILLER | PIPELINE AND SAFETY MANAGER | amiller@morrowenergy.com | 903-262-8089 |  |  |  |  | ALLAN DALE MILLER | PIPELINE AND SAFETY MANAGER | 903-262-8089 | amiller@morrowenergy.com | UTILITY COMPANY WAS EXCAVATING TO INSTALL A NEW SUBDIVISION'S SEWER CONNECTION. THE PIPELINE OPERATOR'S PIPELINE HAD BEEN PREVIOUSLY MARKED BY PIPELINE OPERATOR'S 3RD. PARTY LOCATING SERVICE FOR THIS EXCAVATION PROCESS. THE PIPELINE WAS 17 FEET DEEP IN SOLID ROCK AS IT WAS PART OF A SECTION OF PIPELINE THAT WAS DIRECTIONAL BORED IN. THE UTILITY COMPANY WAS AWARE OF THE PIPELINE LOCATION, BUT DID NOT CALL THE PIPELINE OPERATOR WHEN EXCAVATION STARTED. UTILITY COMPANY EQUIPMENT OPERATOR STATED TO THE PIPELINE OPERATOR'S PLANT MANAGER " WE KNEW THE PIPELINE WAS THERE. WE THOUGHT WHEN WE GOT THROUGH THE DIRT AND HIT SOLID ROCK THAT WE WERE OK". THE UTILITY COMPANY EQUIPMENT OPERATOR STRUCK PIPELINE OPERATOR'S PIPELINE AT APPROXIMATELY 17 FEET IN DEPTH, AND PUNCTURED THE PIPELINE WITH ONE 2" TOOTH ON UTILITY COMPANY'S TRACKHOE. PIPELINE OPERATOR'S PIPELINE HAD APPROXIMATELY 350 PSIG. ON THE PIPELINE.UTILITY COMPANY'S EQUIPMENT OPERATOR DID SHUT DOWN HIS EQUIPMENT AND NOTIFY TEXAS 811 OF THE PIPELINE STRIKE WITHIN A FEW MINUTES OF THE INCIDENT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180124 | 31245 | 2018-11-30 08:28 | ORIGINAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2018-11-05 19:49 | 2018 |  |  | 38.7114 | -94.22 | 1229534 | 2018-11-05 21:55 |  | NATURAL GAS |  | 69 | 964 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-11-07 12:00 | 2018-11-07 22:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-11-05 21:00 | 2018-11-05 21:00 | ONSHORE | MO | 64080 | Not Within a Municipality | CASS | SURVEY STATION NO. | 135/2913+75 | LINE XT | SEDALIA 12" LINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | PIG LAUNCHER AND VALVE FACILITY | 1930 |  | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 204 |  | NO | NO | NO |  | 8000 | 8328.55847688123 | 2500 | 2602.67452402538 | 185 | 166.631205673759 | 642000 | 668366.817769719 | 5000 | 5205.34904805077 | 0 | 0 |  |  | 657685 | 314377.876530588 | 684670.03102435 | [8 empty] | 516 |  | 535 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 37000 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS INCIDENT WAS CAUSED BY A MOTOR VEHICLE ACCIDENT AND THE GAS LOSS WAS MINOR SO THERE WAS NO NOTICEABLE PRESSURE LOSS OR ASSOCIATED ALARMS. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [260 empty] | JOHN ERIC GLAHN | PIPELINE COMPLIANCE ENGINEER | john.glahn@sscgp.com | 270-852-4414 | 270-852-5016 |  |  |  | SHAWN PATTERSON | VP AND CHIEF OPERATIONS OFFICER | 270-852-4670 | shawn.patterson@sscgp.com | ON 11/5/2018, AT 7:49 PM LOCAL TIME, SOUTHERN STAR CENTRAL GAS PIPELINE (SSCGP) WAS CONTACTED BY CASS COUNTY, MO, EMERGENCY RESPONDERS REPORTING A MOTOR VEHICLE ACCIDENT THAT IMPACTED FACILITIES POSSIBLY BELONGING TO SSCGP. IT WAS A SINGLE CAR ACCIDENT AND THE SINGLE OCCUPANT WAS NOT INJURED. THERE WERE NO OTHER INJURIES RELATED TO THIS ACCIDENT. THERE WERE NO CUSTOMERS IMPACTED OR NOTICEABLE PRESSURE LOSS IN THIS AREA. THERE WAS DAMAGE TO ABOVE GROUND FACILITIES INCLUDING THE FENCING, PIG LAUNCHER, VARIOUS ABOVE GROUND PIPING, BLOW-OFF VALVES AND DAMAGE TO LINE XT MAINLINE GATE VALVE MAKING IT INOPERABLE AND LEAKING. LINE XT IS LISTED ON THE INCIDENT REPORT BUT THE FOLLOWING LINES WERE ALL IMPACTED AT THIS JUNCTION SETTING: XM, XMA, XT, XT-022. THE FACILITY IS LOCATED ALONG A STRAIGHT SECTION OF ROAD AND IS A FENCED ENCLOSURE THAT HAD BEEN SECURED BY LOCAL EMERGENCY RESPONDERS. THE ROAD WAS CLOSED IN BOTH DIRECTIONS AS A PRECAUTION. SSCGP PERSONNEL ARRIVED ON SITE AT 9:00 PM AND CONFIRMED THAT IT WAS A SSCGP FACILITY. IT WAS DETERMINED THAT THE NRC SHOULD BE NOTIFIED AND THE CALL WAS PLACED AT 9:55 PM ON 11/5/2018 WITH A FOLLOW-UP CALL ON 11/7/2018 AT 4:42 PM. ALL REPAIRS THAT AFFECTED OPERATION OF THE TRANSMISSION LINE WERE COMPLETED ON 11/7/2018. REPAIRS TO ABOVE GROUND FACILITIES (PIG LAUNCHER, PIPING, PAINTING, FENCING) AND SURFACE RESTORATION ARE ONGOING AND WILL BE COMPLETED AS WEATHER PERMITS.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180125 | 31252 | 2018-11-30 13:45 | ORIGINAL FINAL | 26330 | ENABLE OKLAHOMA INTRASTATE TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2018-11-07 06:45 | 2018 |  |  | 36.2826 | -95.6616 | 1229736 | 2018-11-07 10:46 |  | NATURAL GAS |  | 4714 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-11-07 08:30 | 2018-11-08 12:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-11-07 06:45 | 2018-11-07 07:45 | ONSHORE | OK | 74019 | CLAREMORE | ROGERS | MILEPOST | CLAREMORE CS | CLAREMORE COMPRESSOR STATION | CLAREMORE COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | INTERNAL PARTS INSIDE THE PILOT WERE WORN DUE TO VIBRATION OVER TIME. | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 13511 | 12169.4822695035 | 1500 | 1561.60471441523 | 500 | 520.534904805077 | 0 | 0 |  |  | 15511 | 13572.4118726276 | 14251.6218887239 | [8 empty] | 499 |  | 1014 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELEASE WAS DUE TO EQUIPMENT FAILURE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [13 empty] | YES | [177 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | AT 06:45 ON 11/7/2018 THE ENABLE OKLAHOMA INTRASTATE TRANSMISSION (EOIT) SYSTEM CONTROL RECEIVED A CALL ABOUT AN ODOR OF GAS AT THE CLAREMORE COMPRESSOR STATION IN CLAREMORE, OKLAHOMA. WHEN THE EOIT O&M TECHNICIAN ARRIVED AT THE STATION, HE PERFORMED A COMPLETE INSPECTION AND FOUND A INTERSTAGE RELIEF VALVE DISCHARGING. THE RELIEF VALVE WAS CLOSED AND THE UNIT WAS SHUTDOWN WHILE REPAIRS WERE PERFORMED. IT WAS DETERMINED THE RELIEF VALVE VENTED PREMATURELY DUE TO A BREAKDOWN OF MATERIALS IN THE PILOT VALVE. IT IS ASSUMED THIS BREAKDOWN IS DUE TO VIBRATION. THE RELIEF WAS REBUILT AND THE UNIT WAS RESTARTED ON 11/8/2018. WHEN IT WAS SAFE TO DO SO, THE AMOUNT AND DURATION OF GAS LOSS WAS CALCULATED TO BE 4.7 MMCF. THESE TOTALS WERE CONFIRMED AT 10:30 AND A CALL WAS PLACED TO NRC AT 10:46 (NRC#1229736). A FOLLOW UP CALL WAS PLACED WITH THE NRC ON 11/8/18 AT 11:12 (NRC#1229852).
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180126 | 31294 | 2018-12-07 16:49 | ORIGINAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2018-11-08 10:25 | 2018 |  |  | 30.1763 | -92.6684 | 1229862 | 2018-11-08 12:05 |  | NATURAL GAS |  | 1 | 312 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-11-08 10:51 | 2018-11-17 14:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-11-08 10:25 | 2018-11-08 10:45 | ONSHORE | LA | 70546 | Not Within a Municipality | JEFFERSON DAVIS | SURVEY STATION NO. | 10+18 | ANR LATERAL 703 SOUTH JENNINGS | ROUTE ID: 8001703 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION |  | 12 |  | 0.25 | 42000 | API 5LX | LONGITUDINAL ERW - LOW FREQUENCY |  | LONESTAR | COAL TAR | [9 empty] | PIPE GIRTH WELD | [18 empty] | 1956 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 328 |  | NO | NO | NO |  | 12000 | 12492.8377153218 | 12000 | 12492.8377153218 | 1 | 0.900709219858156 | 138000 | 143667.633726201 | 0 | 0 | 0 | 0 |  |  | 162001 | 77417.2529357931 | 168654.209866065 | [8 empty] | 796 |  | 1050 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 7387 | NO | [5 empty] | YES | PIPELINE WAS INSTALLED PRIOR TO DESIGN REQUIREMENTS FOR INTERNAL INSPECTION TOOLS | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE MINIMAL AMOUNT OF GAS LOSS WAS NOT DETECTABLE DUE TO THE SMALL SIZE OF THE LEAK. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [8 empty] | YES | CONSTRUCTION-RELATED | [13 empty] | YES | [62 empty] | NO | [63 empty] | YES | 1982 | 1638 | NO | [13 empty] | NO | [63 empty] | ROGER STREET | COMPLIANCE SPECIALIST | roger_street@transcanada.com | 615-465-5123 |  |  |  |  | ROGER STREET | COMPLIANCE SPECIALIST | 615-465-5123 | roger_street@transcanada.com | ON 8 NOVEMBER 2018 AT 10:25 CT, A CONTRACT EMPLOYEE, WHILE CONDUCTING A CLOSE INTERVAL SURVEY, OBSERVED BUBBLING FROM THE GROUND ABOVE THE ANR LATERAL 703 SOUTH JENNINGS LINE. UPON DISCOVERY OF THE CONDITION, THE EMPLOYEE CONTACTED THE AREA OFFICE, WHO DISPATCHED A QUALIFIED TECHNICIAN TO SHUT IN VALVES TO THE 703 LATERAL AND INVESTIGATE THE SOURCE OF THE LEAK. THE INITIAL FIELD INVESTIGATION DETERMINED THAT THE SOURCE OF THE BUBBLING WAS DUE TO LEAK ON THE PIPELINE. AT 12:05 CT, AN INCIDENT WAS REPORTED INTO THE NATIONAL RESPONSE CENTER (REPORT #1229862). A COURTESY CALL WAS ALSO PLACED THE PHMSA ACCIDENT INVESTIGATION DIVISION (AID) TO INFORM THE DIVISION OF THE INCIDENT. FOLLOWING THE DISCOVERY OF THE LEAK, ACTIONS INCLUDED THE REDUCTION OF PIPELINE PRESSURE FROM DISCOVERY PRESSURE OF 976PSIG TO 100PSIG, COMPLETED . ON 12 NOVEMBER 2018, REPAIR CREWS ARRIVED AT THE SITE TO REPAIR THE PIPELINE. ON NOVEMBER 13 PRIOR TO EXCAVATION, PIPELINE PRESSURE WAS REDUCED TO 20PSIG. ON 15 NOVEMBER THE PIPELINE WAS EXPOSED, THE COATING WAS EXAMINED, AND A DEFECT WAS FOUND ON THE GIRTH WELD. IT WAS DETERMINED TO REPAIR THE LEAK BY PLACING A TYPE-B PRESSURE CONTAIN SLEEVE ACROSS THE DEFECT. ON 16 NOVEMBER, THE TYPE-B SLEEVE WAS WELDED ONTO THE PIPELINE AND THE REPAIR WAS COMPLETED. THE DEFECT WAS LIMITED TO A SINGLE PIN HOLE LOCATED AT THE 06:00 POSITION ON THE WELD WITH NO ANOMALIES OBSERVED NEAR THE GIRTH WELD. THE PIPELINE WAS PURGED, LOADED, AND RETURNED TO SERVICE AT 14:00 ON NOVEMBER 17, 2018.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180127 | 31545 | 2018-12-13 10:04 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2018-11-28 04:35 | 2018 |  |  | 35.0336 | -88.8904 | 1231460 | 2018-11-28 07:00 |  | NATURAL GAS |  | 7501 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | EVENT ONLY INVOLVED UNIT 1B | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-11-28 06:00 | 2018-11-28 06:00 | ONSHORE | TN | 38052 | Not Within a Municipality | HARDEMAN COUNTY | MILEPOST | MLV 71-1 | STATION 71 (MIDDLETON) (STA 71-1) | LINE 100-1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2015 |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENTIONAL VENTING THROUGH UNIT 1B VENT VALVE (IN PROPER OPEN POSITION) BECAUSE OF ICE IN CONTROL SYSTEM OF UNIT 1B DISCHARGE VALVE. | CLASS 1 LOCATION | NO |  | 567 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 31580 | 28444.3971631206 | 1800 | 1873.92565729828 | 1000 | 1041.06980961015 | 0 | 0 |  |  | 34380 | 30827.6579455558 | 31359.392630029 | [8 empty] | 650 |  | 750 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INVESTIGATION FOUND ICE IN THE CONTROL SYSTEM OF UNIT 1B DISCHARGE VALVE | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | NO | [306 empty] | WILLIAM MARTIN MULLER | SPECIALIST-PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205 325 3863 | 205 325 3592 |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713 369 9443 | jaime_hernandez@kindermorgan.com | AT APPROXIMATELY 06:00 HOURS, 11/28/2018, A TGP EMPLOYEE ARRIVED AT STATION 71 AND DISCOVERED NATURAL GAS BLOWING FROM THE 2-INCH UNIT VENT VALVE ON COMPRESSOR UNIT 1B. THE EMPLOYEE IMMEDIATELY CONTACTED THE STATION SUPERVISOR FOR EVENT NOTIFICATION. THE STATION SUPERVISOR IMMEDIATELY DISPATCHED ADDITIONAL EMPLOYEES TO ASSIST. THE STATION E&C TECHNICIAN ARRIVED AT STATION 71 AT 6:20 HOURS AND CONFIRMED NATURAL GAS BLOWING FROM THE 2-INCH UNIT VENT VALVE AND DISCOVERED THE UNIT DISCHARGE VALVE WAS OPEN. AT 6:25 HOURS, THE MANUAL LOCKING VALVE BENEATH THE 2-INCH UNIT VENT VALVE WAS CLOSED THEREBY TERMINATING THE NATURAL GAS RELEASE. THE 2-INCH UNIT VENT VALVE WAS ALSO CLOSED. THE UNIT HAD PREVIOUSLY BEEN BLOWN DOWN FROM AN EARLIER EMERGENCY SHUTDOWN (ESD) TEST AND WAS LEFT WITH THE 2-INCH VENT VALVE IN THE NORMAL OPEN POSITION. AS PART OF POST INCIDENT INVESTIGATION, PRESSURE TRENDING INFORMATION WAS ANALYZED AND IT WAS DETERMINED THE DISCHARGE VALVE OPENED AT 3:25 HOURS AND REPORTABLE VOLUME WAS MET AT 04:35 HOURS. INVESTIGATION ALSO IDENTIFIED ICE HAD FORMED IN THE CONTROL SYSTEM OF THE UNIT 1B DISCHARGE VALVE, IMPAIRING ITS OPERATION, ALLOWING THE DISCHARGE VALVE TO OPEN PREMATURELY THEREFORE ALLOWING NATURAL GAS TO VENT THROUGH THE OPEN 2-INCH UNIT VENT VALVE TO ATMOSPHERE. POST EVENT REPAIRS INCLUDED THE CONTROL SYSTEM OF THE UNIT DISCHARGE VALVE WAS BLOWN CLEAN, FREE OF MOISTURE, AND THE CONTROL SYSTEM FILTER WAS REPLACED. PRIOR TO RETURN TO SERVICE, THE 2-INCH UNIT VENT VALVE WAS CONFIRMED RETURNED TO THE OPEN POSITION, ALSO THE MANUAL LOCKING VALVE BENEATH THE 2-INCH UNIT VENT VALVE WAS CONFIRMED RETURNED TO THE OPEN POSITION. THE UNIT SUCTION AND THE UNIT DISCHARGE VALVES WERE CONFIRMED PROPERLY CLOSED. COMPRESSOR UNIT 1B WAS CONFIRMED SAFE AND READY TO RETURN TO SERVICE AS NEEDED ON 11/28/2018. SINCE 11/28/2018, OPERATIONS HAS REVISED THE WINTERIZATION PLAN FOR STATION 71 TO INCLUDE INSPECTION OF VALVE CONTROL SYSTEMS TO DISCOVER CONDENSATE ISSUES AND ELIMINATE THE ISSUES BEFORE FREEZING CONDITIONS BEGIN. PLEASE NOTE THE FOLLOWING REQUESTED INFORMATION: THE ORIGINAL NRC REPORT NUMBER IS 1231460. THE UPDATED INFORMATION NRC REPORT NUMBER IS 1231506. THE REQUIRED PHMSA 48-HOUR NRC REPORT NUMBER IS 1231637.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180128 | 31323 | 2018-12-13 14:34 | ORIGINAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2018-11-27 09:45 | 2018 |  |  | 42.0421 | -93.271 | 1231388 | 2018-11-27 10:43 |  | NATURAL GAS |  | 7000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-11-27 13:56 | 2018-11-29 10:18 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-11-27 09:49 | 2018-11-27 11:00 | ONSHORE | IA | 50056 | Not Within a Municipality | STORY | MILEPOST | 20.5 | MARSHALLTOWN 10-INCH | IAB66101 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 44 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10.75 |  | 0.219 | 42000 | 5LX | LONGITUDINAL ERW - LOW FREQUENCY |  | REPUBLIC | COLD APPLIED TAPE | [28 empty] | 1950 | 1950 | CARBON STEEL |  | MECHANICAL PUNCTURE | 3 | 1 | [7 empty] | CLASS 1 LOCATION | NO |  | 166 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 32410 | 29191.9858156028 | 90000 | 93696.2828649139 | 10000 | 10410.6980961015 | 0 | 0 |  |  | 132410 | 78052.5085249985 | 133298.966776618 | [8 empty] | 425 |  | 500 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 39000 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE THIRD PARTY CONTACTED NORTHERN BEFORE THE CONTROLLERS COULD REACT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [7 empty] | CONTRACTOR | TRENCHER | DRAINAGE | NO | [5 empty] | NO |  | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | JOHN A GORMLEY | SR CORROSION SPECIALIST | john.gormley@nngco.com | 4023987494 |  |  |  |  | THOMAS G CORRELL | VP PIPELINE SAFETY AND RISK | 4023987715 | thomas.correll@nngco.com | ON NOVEMBER 27, 2018, MUMM BACKHOE AND EXCAVATING, LLC, WAS INSTALLING DRAIN TILE IN FARMLAND LOCATED NEAR COLO, IOWA. COMPANY OWNER GREG MUMM ("MUMM") AND EMPLOYEE TIM ABEL ("ABEL") WERE HIRED BY LAND OWNER DAVE EGGER ("EGGER") TO INSTALL DRAIN TILE IN HIS FARM FIELD DUE TO DRAINAGE ISSUES ENCOUNTERED EARLIER IN THE YEAR. ABEL WAS OPERATING THE TILING MACHINE ON THE SOUTHEAST 1/4 SECTION, (S34, T48N, R21W) IN STORY COUNTY, IOWA, AND MUMM WAS ROUTING DRAIN TILE WITH HIS VEHICLE AND DRAIN TILE TRAILER. AT APPROXIMATELY 0945, ABEL WAS USING THE TILING MACHINE TO INSTALL DRAIN TILE IN THE NORTHWEST CORNER OF THE PROPERTY IN AN EASTERLY DIRECTION AND MADE CONTACT WITH AND DAMAGED NORTHERN NATURAL GAS ("NORTHERN") 10-INCH-DIAMETER IAB66101 BRANCH LINE CAUSING A RUPTURE AND GAS LEAK. NORTHERN ISOLATED AND BLEW DOWN BRANCH LINE IAB66101 AND COMPLETED REPAIRS TO RESTORE SERVICE NOVEMBER 29, 2018. THE INCIDENT RESULTED IN A GAS RELEASE OF APPROXIMATELY 7.0 MCF AND AN EMERGENCY WHICH WAS REPORTED TO THE NATIONAL RESPONSE CENTER (NOTIFICATION #1231388 AND 1231571). THE ROOT CAUSE WAS FAILURE BY MUMM TO MAKE A ONE CALL NOTIFICATION PRIOR TO PERFORMING TRENCHING ACTIVITIES. HAD MUMM PROPERLY SUBMITTED A ONE CALL, THIS WOULD HAVE NOTIFIED NORTHERN TO PERFORM A LINE LOCATE, WHICH COULD HAVE PREVENTED THE LINE STRIKE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180129 | 32591 | 2018-12-13 18:45 | SUPPLEMENTAL FINAL | 12874 | DOMINION ENERGY QUESTAR PIPELINE, LLC | 333 SOUTH STATE STREET P.O. BOX 45360 | SALT LAKE CITY | UT | 84145-0360 | 2018-11-17 18:26 | 2018 |  |  | 41.4259 | -111.1775 | 1230701 | 2018-11-17 20:53 |  | NATURAL GAS |  | 48855 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-11-17 19:47 | 2019-01-10 12:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-11-17 18:26 | 2018-11-17 20:12 | ONSHORE | UT | 84086 | Not Within a Municipality | RICH COUNTY | SURVEY STATION NO. | 1933+30.07 | ML048 | ML048/TL112 JUNCTION TO ML048/JL057 JUNCTION | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 43 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.312 | 42000 | API 5L X42 | LONGITUDINAL ERW - HIGH FREQUENCY |  | US STEEL NATIONAL DUQUESNE | COLD APPLIED TAPE | [28 empty] | 1980 | 1977 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 432 | 62.8 |  | CLASS 1 LOCATION | NO |  | 418 |  | NO | NO | NO |  | 20000 | 20821.3961922031 | 0 | 0 | 118923 | 107115.042553192 | 462080 | 481057.53762466 | 21997 | 22900.4126019946 | 0 | 0 | ESTIMATED MISCELLANEOUS OTHER COSTS. |  | 623000 | 351938.595639873 | 631894.388972049 | [8 empty] | 780 |  | 918 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 89232 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS CLEAR THAT CONTROLLER/CONTROL ROOM ISSUES WERE NOT THE CAUSE OR A CONTRIBUTING FACTOR | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  |  |  |  | YES |  | YES | KIEFNER ANALYSIS CONCLUDED THAT FAILURE OCCURRED DUE TO CORROSION CAUSED BY DISBONDED COATING AND CP SHIELDING |  |  |  | YES |  |  | YES | YES | 1980 | YES | YES | YES |  |  |  | 2018 |  |  |  | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | CALEB BENTLEY | ENGINEER II - PIPELINE COMPLIANCE | caleb.a.bentley@dominionenergy.com | 8013245117 |  |  |  |  | RON JORGENSEN | VP WESTERN PIPELINE OPERATIONS | 8013245145 | ron.jorgensen@dominionenergy.com | ON 11/17/2018 AT 18:26 LOCAL TIME, DOMINION ENERGY QUESTAR PIPELINE'S (DEQP) MAIN LINE 048 (ML048) RUPTURED IN RICH COUNTY, UT. OPERATORS WERE DISPATCHED AND SHUTDOWN THE ML048 TRANSMISSION PIPELINE VIA MANUAL BLOCK VALVES AT 19:47. AT 20:12, A DEQP OPERATOR ARRIVED ON-SITE OF THE INCIDENT AND DISCOVERED A RUPTURE OF THE 20" ML048 PIPELINE WHICH HAD RESULTED IN AN UNINTENDED NATURAL GAS LOSS OF APPROXIMATELY 48.9 MMSCF. ONCE IT WAS CONFIRMED AT 20:48 THAT THE INCIDENT WAS REPORTABLE, INCLUDING CONFIRMATION OF EXACT FAILURE LOCATION, DEQP NOTIFIED THE NATIONAL RESPONSE CENTER VIA TELEPHONIC REPORT ON 11/17/2018 AT 20:53. A 48-HOUR CONFIRMATION OF THE INCIDENT WAS REPORTED TO THE NRC ON 11/19/2018 AT 17:56. AN INCIDENT INVESTIGATION TEAM WAS DEPLOYED AND PROGRESSED AN INVESTIGATION OF THE FAILURE AND REPAIR OF THE PIPELINE. CAUSE OF THE FAILURE WAS EXTERNAL CORROSION AS A RESULT OF DISBONDED COATING AND CP SHIELDING AS DETERMINED BY A KIEFNER & ASSOCIATES METALLURGICAL ANALYSIS. NOTES ON PARTICULAR QUESTIONS PART A: Q 6-7. SECOND NRC NOTIFICATION NUMBER 1230856 ON 11/19/2018 AT 17:56 LOCAL TIME Q 15B. COMPANY REPAIRED THE PIPELINE SEGMENT DIRECTLY AFFECTED BY THE FAILURE AND PLACED THE SEGMENT BACK IN-SERVICE SUBJECT TO SEVERAL COMMITMENTS: 1) MAINTAIN A PIPELINE PRESSURE AT 80% OF OPERATING PRESSURE AT TIME OF FAILURE, 2) CONTRACT WITH INDEPENDENT PARTY AND COMPLETE A PIPE FAILURE ANALYSIS, 3) COMPLETE INLINE INSPECTION OF MAIN LINE 048 FROM YELLOW CREEK SITE TO THE MAIN LINE 048-MAIN LINE 060 JUNCTION, AND 4) PERFORM NECESSARY REMEDIATION. THE PIPE FAILURE ANALYSIS HAS BEEN COMPLETED BY KIEFNER AND ASSOCIATES. INLINE INSPECTION IS IN PROGRESS AT THE TIME/DATE OF THIS SUPPLEMENTAL REPORT, AND THE PIPELINE REMAINS UNDER THE OPERATING RESTRICTION COMMITMENT (80% OF OPERATING PRESSURE AT TIME OF FAILURE). Q 19A. TIME ENTERED REFERS TO TIME OPERATOR BECAME AWARE OF INCIDENT BUT HAD NOT CONFIRMED
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180130 | 32377 | 2018-12-14 08:54 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2018-11-16 02:16 | 2018 |  |  | 37.5559 | -81.3697 | 1230533 | 2018-11-16 02:32 |  | NATURAL GAS |  | 3920 | 3.64 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-11-16 02:45 | 2019-06-10 09:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2018-11-16 02:16 | 2018-11-16 01:45 | ONSHORE | WV | 25826 | CORRINE | WYOMING | SURVEY STATION NO. | RS-807629 | LINE KA TO KA-14 | LINE KA-14 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | FLANGE ASSEMBLY | [38 empty] | 1999 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 49 |  | NO | NO | NO |  | 0 | 0 | 11 | 11.4517679057117 | 11564 | 10415.8014184397 | 525715 | 547306.014959202 | 2200 | 2290.35358114234 | 0 | 0 | TEMPORARY REPAIRS, EQUIPMENT WILL BE REMOVED WHEN PERMANENT REPAIRS ARE COMPLETE |  | 539490 | 263083.026210057 | 560023.62172669 | [8 empty] | 560 |  | 1000 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER WAS NOTIFIED OPERATING PERSONNEL ABOUT THE PRESSURE ALARM AND MADE OPERATIONS AWARE THERE WAS A CALL ALREADY FROM WYOMING 911. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | GASKET | [17 empty] | YES | AGE AND CONDITIONS OF SOFT GOODS | [161 empty] | MARK NEWMAN | COMPLIANCE SPECIALIST US REGULATORY COMPLIANCE | mark_newman@transcanada.com | 304-722-8475 | 304-722-8420 |  |  |  | GEORGE HAMATY | MANAGER EAST US REGULATORY COMPLIANCE | 304-357-3728 | george_hamaty@transcanada.com | ALL TIMES RECORDED WERE IN EASTERN STANDARD TIME ON 11/15/18 AT 23:54, TRANSCANADA'S GAS CONTROL (GC) CENTER (COLUMBIA GAS TRANSMISSION OPID 2616) WAS NOTIFIED BY WEST VIRGINIA WYOMING COUNTY 911 OF A GAS RELEASE AND FIRE AT CAIRO HOLLOW IN THE TOWN OF BUD, WV. COMPANY PERSONNEL WAS DISPATCHED BY LOCAL OPERATIONS AT THAT TIME. AT 00:36 ON 11/16/18, GC RECEIVED A LOW-PRESSURE ALARM OF 0 AT MEASURING STATION (MS) 804927 CORRINE DELIVERY POINT (DP) AT THE END OF LINE KA-14. COMPANY PERSONNEL ARRIVED ONSITE AT 01:45 ON 11/16/2018 AND CONFIRMED A FIRE AT CORRINE REGULATOR STATION (RS) 807629 LOCATED AT PIPELINES KA TO KA-14. COMPANY PERSONNEL CLOSED THE VALVE TO PIPELINE KA-14 AT 02:45 ON 11/16/2018 ISOLATING RS-807629 AND PIPELINE KA-14. COMPANY PERSONNEL CONTACTED MOUNTAINEER GAS COMPANY (LOCAL DISTRIBUTION OPERATOR) TO ISOLATE THE FEED AT MS-804927 CORRINE DP TO PREVENT BACKFEED INTO PIPELINE KA-14. PRELIMINARY INVESTIGATION IDENTIFIED A FAILED 2" ANSI-600 FLANGED CONNECTION THAT WAS MISSING PART OF THE GARLOCK GASKET. THE MISSING GASKET ALIGNS WITH HEAT MAPS OF THE FACILITY TO INDICATE THE FIRE DAMAGE IS SOURCED FROM THIS FLANGE. IGNITION SOURCE FOR THE LEAK AT THE INLET FLANGE TO THE REGULATION COULD BE THE IN-DIRECT FIRED HEATER ONSITE. TEMPORARY SERVICE WILL BE RESTORED USING A 2" SKID MOUNTED REGULATION SKID AND 2" CONNECTION TO AND FROM BELOW GROUND PIPING TO PIPELINE KA-14. PERMANENT INSTALLATION OF FACILITY WILL COMMENCE IN 2019 WITH EXPECTED IN SERVICE OF MARCH 29, 2019. THE INITIAL NRC REPORT NO. 1230533 REPORTED ON NOVEMBER 16, 2016 @ 02:32 AND THE 48-HR UPDATE NRC REPORT NO. 1230594 WAS REPORTED ON NOVEMBER 16, 2018 @ 14:23. AN APPARENT GASKET FAILURE OCCURRED IN TOP WORKS OF THE PRESSURE REGULATOR AT CORRINE REGULATOR STATION (RS) 807629. REPAIRS WERE COMPLETED ON JUNE 10, 2019.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180131 | 31342 | 2018-12-18 11:02 | ORIGINAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2018-12-10 03:10 | 2018 |  |  | 39.9268 | -101.9388 | 1232489 | 2018-12-10 05:17 |  | NATURAL GAS |  | 25100 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-12-10 03:10 | 2018-12-10 15:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-12-10 04:21 | 2018-12-10 05:02 | ONSHORE | KS | 67756 | Not Within a Municipality | CHEYENNE | SURVEY STATION NO. | 160 / 4594+62 | LINE W | ST FRANCIS COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1980 |  | CARBON STEEL |  | OTHER | [8 empty] | DURING ESD OF THE ST FRANCIS COMPRESSOR STATION, THE STATION ISOLATION VALVE LITERALLY FROZE WHILE PARTIALLY OPEN ALLOWING MAINLINE GAS TO VENT DURING THE STATION BLOW-DOWN. | CLASS 1 LOCATION | NO |  | 128 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 100380 | 90413.1914893617 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 100380 | 93735.4609929078 | 90413.1914893617 | [8 empty] | 621 |  | 960 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE AUTOMATIC ESD WAS CAUSED BY GAS DETECTION AT THE STATION AND THE UNINTENTIONAL GAS RELEASE FROM THE FROZEN ISOLATION VALVE, THE CONTROLLER WAS NOT AT FAULT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | FROZEN ISOLATION VALVE | [161 empty] | JOHN ERIC GLAHN | PIPELINE COMPLIANCE ENGINEER | john.glahn@sscgp.com | 270-852-4414 | 270-852-5016 |  |  |  | SHAWN PATTERSON | VP AND CHIEF OPERATIONS OFFICER | 270-852-4670 | shawn.patterson@sscgp.com | ON 12/10/2018 AT 3:10 AM LOCAL TIME, SOUTHERN STAR CENTRAL GAS PIPELINE (SSCGP) RECEIVED A HIGH LEVEL GAS DETECTION ALARM WHICH TRIGGERED AN AUTOMATIC EMERGENCY SHUTDOWN (ESD) OF THE ST. FRANCIS COMPRESSOR STATION IN CHEYENNE COUNTY, KANSAS. OPERATIONS PERSONNEL WERE DISPATCHED TO THE STATION ARRIVING AT 5:02 AM. AS PART OF THE ESD, THE STATION IS AUTOMATICALLY ISOLATED AND BLOWN DOWN. THE SCADA OPERATOR RECEIVED ALARMS THAT SSCGP LINE W WAS EXPERIENCING A RAPID DROP IN PRESSURE UPSTREAM OF THE STATION. THE UPSTREAM STATION ISOLATION VALVE FAILED TO FULLY CLOSE DURING THE ESD CAUSING MAINLINE GAS TO ESCAPE ALSO. ALL GAS WAS RELEASED THROUGH THE STATION BLOW-OFF VALVES. THE PERSONNEL ON SITE WARMED THE FROZEN ISOLATION VALVE AND HAD IT FULLY CLOSED BY 5:40 AM. A SMALL FITTING INSIDE OF THE STATION WAS LEAKING WHICH PROPERLY CAUSED THE ORIGINAL ESD. THIS FITTING WAS REPAIRED AND THE STATION WAS BROUGHT BACK ON-LINE AT 3:30 PM ON 12/10/2018.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180132 | 31694 | 2018-12-18 18:02 | SUPPLEMENTAL FINAL | 2564 | COLORADO INTERSTATE GAS CO | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2018-11-20 15:13 | 2018 |  |  | 39.6983 | -104.7007 | 1230933 | 2018-11-20 16:33 |  | NATURAL GAS |  | 5962 | 3045 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-11-20 16:14 | 2018-11-21 19:42 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-11-20 15:13 | 2018-11-20 15:43 | ONSHORE | CO | 80018 | AURORA | ARAPAHOE | MILEPOST | MP 105+4872 | 9A PIPELINE | PUEBLO/WATKINS MAINLINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 44 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.25 | 60000 | API 5L X-60 | DSAW |  | KAISER STEEL | COAL TAR | [28 empty] | 1966 | 1966 | CARBON STEEL |  | MECHANICAL PUNCTURE | 3 | 3.3 | [7 empty] | CLASS 3 LOCATION | NO |  | 395 |  | NO | NO | NO |  | 0 | 0 | 12116 | 12613.6018132366 | 23722 | 21366.6241134752 | 28414 | 29580.9575702629 | 0 | 0 | 0 | 0 |  |  | 64252 | 41520.1655467895 | 63561.1834969747 | [8 empty] | 500 |  | 820 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | REMOTELY CONTROLLED | 38260 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS CAUSED BY A THIRD-PARTY LINE STRIKE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | NO |  |  | YES | PRIVATE BUSINESS | YES | [6 empty] | CONTRACTOR | GRADER/SCRAPER | SITE DEVELOPMENT | YES | 830500140 |  | UTILITY OWNER | YES | YES | NO |  | OTHER |  |  |  | INEDEQUATE HEI CONSTRUCTION INSTRUCTION/PROCEDURE. INEDEQUATE HEI CONSTRUCTION COMMUNICATION/HARDWARE/SOFTWARE/PROCESS. INEDEQUATE VERTICAL COMMUNICATION BETWEEN HEI CONSTRUCTION SUPERVISOR AND OPERATOR. | [262 empty] | KRITI BHAYANI | PIPELINE ENGINEER - CODES AND STANDARDS | kriti_bhayani@kindermorgan.com | 7134206633 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR - CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan,com | ON NOVEMBER 20, 2018 AT 3:13 PM MST COLORADO INTRASTATE GAS COMPANY (CIG) GAS CONTROL RECEIVED A CALL FROM A THIRD-PARTY CONTRACTOR INDICATING THAT WHILE GRADING THEY THE THIRD-PARTY CONTRACTOR HAD HIT AND PUNCTURED A NATURAL GAS PIPELINE. CIG PERSONNEL ARRIVED AT THE LOCATION OF THE LINE STRIKE AT 3:43 PM MST AND CONFIRMED THAT IT WAS ON THE CIG PIPELINE. THE THIRD-PARTY CONTRACTOR STRUCK THE CIG 9A PIPELINE WHILE GRADING THE AREA FOR A NEW HOUSING DEVELOPMENT. THERE WAS AN OPEN ONE CALL TICKET AND CIG DAMAGE PREVENTION PERSONNEL HAD MARKED THE LINE. THE CONTRACTOR HAD PREVIOUSLY AGREED ORALLY AND IN WRITING TO CIG'S REQUEST THAT A CIG REPRESENTATIVE BE ONSITE FOR ANY WORK WITHIN 25 FEET OF OUR PIPELINE ASSETS. FURTHER, THE CONTRACTOR TOLD CIG A FEW DAYS BEFORE THE INCIDENT THAT NO WORK WOULD BE PERFORMED WITHIN 25 FEET OF THE PIPELINE ON THE DAY OF THE LINE STRIKE. DESPITE THE PIPELINE MARKINGS AND THE PRIOR AGREEMENTS, THE THIRD-PARTY CONTRACTOR PROCEEDED WITH GRADING OVER THE PIPELINE WITHOUT NOTIFYING CIG. POST CONFIRMATION BY CIG FIELD PERSONNEL THAT OUR PIPELINE HAD BEEN STRUCK, THEY PROCEEDED TO ISOLATE THE PIPELINE BETWEEN MLV 11 AND 11.9. CIG THEN IMPLEMENTED A BLOW DOWN PROCESS FOR THIS SEGMENT. ONCE THE LEAK SITE WAS DECLARED SAFE AND FREE OF GAS VAPORS CIG PROCEEDED TO MAKE REPAIRS. THE REPAIRS CONSISTED OF REPLACING SIXTY FEET OF PRETESTED TWENTY INCH PIPE. THE REPAIRS WERE COMPLETED ON NOVEMBER 21, 2018. UPON COMPLETING THE REPAIRS CIG IMPLEMENTED A PURGE AND PACK PROCESS FOR THIS SEGMENT. ONCE THE PURGE PROCESS WAS CONFIRMED TO BE COMPLETED THE SEGMENT PRESSURE WAS ALLOWED TO EQUALIZE. THE SEGMENT WAS THEN RETURNED TO GAS CONTROL FOR NORMAL OPERATIONS AND WAS BACK IN SERVICE AT 7:42 PM MST ON NOVEMBER 21, 2018.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20180133 | 31532 | 2018-12-19 09:14 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2018-11-23 16:24 | 2018 |  |  | 40.438 | -78.5911 | 1231182 | 2018-11-24 16:15 |  | NATURAL GAS |  | 23240 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | GAS WAS ABLE TO BYPASS THE COMPRESSOR STATION. NOT REQUIRING PIPELINE SHUTDOWN. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-11-23 16:24 | 2018-11-23 16:51 | ONSHORE | PA | 15938 | LILLY | CAMBRIA | MILEPOST | 54.76 | LINE 19 | ARMAGH-LILLY | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | MAINLINE | GATE |  | 30" X 24" NORDSTRUM PLUG VALVE |  |  |  | 1961 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | COMPRESSOR STATION EMERGENCY SHUTDOWN. | CLASS 1 LOCATION | NO |  | 671 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 100164 | 90218.6382978723 | 100 | 104.106980961015 | 0 | 0 | 0 | 0 |  |  | 100264 | 93581.5467165628 | 90322.7452788334 | [8 empty] | 618 |  | 1050 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL ROOM PERSONNEL COULD NOT HAVE CAUSED THE MALFUNCTION OF THE VALVE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [30 empty] | YES | EXTERNAL FREEZING IN THE SHAFER OPERATOR CONTROL PILOT | [161 empty] | MAYRA SALINAS | ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: ON FRIDAY, NOVEMBER 23, AT 4:24 PM EST LILLY STATION HAD A STATION EMERGENCY SHUT DOWN (ESD). THE ESD WAS CAUSED BY A COMMERCIAL POWER DISRUPTION. THE EMERGENCY GENERATOR STARTED THOUGH A CIRCUIT BREAKER TRIPPED CAUSING A LOSS OF ELECTRICAL POWER WHICH RESULTED IN FULL STATION ESD ACTIVATION. WHEN THE ESD OCCURRED, GAS VENTED THROUGH THE THREE STATION ESD BLOW DOWN VALVES BECAUSE 30"X 24" (VALVE 19-149) FAILED TO CLOSE AUTOMATICALLY. OPERATOR PERSONNEL MANUALLY CLOSED VALVE 19-149 AT 5:01 PM EST. TOTAL GAS LOSS THROUGH THE THREE ESD BLOW DOWN VALVES WAS CALCULATED TO BE 23.24 MMSCF. WHEN THE ESD SYSTEM ACTIVATED, THE CONTROL PILOT ASSEMBLY IN THE SHAFER ACTUATOR FOR VALVE 19-149 FROZE DUE TO THE PRESENCE OF WATER (EXTERNAL TO THE CONTROL) AND COLD AMBIENT TEMPERATURES WHICH CAUSED THE VALVE TO REMAIN OPEN. SUPPLEMENTAL REPORT: 48 HR NRC REPORT 1231234 PRIOR TO THE NOVEMBER 23, 2018 INCIDENT AT TETLP'S LILLY COMPRESSOR STATION, TETLP HAD CALCULATED THE ESTIMATED GAS LOSS FOR A NORMAL ESD EVENT AT LILLY STATION TO BE 1.23 MMSCF. BASED ON THIS CALCULATION, AN ESD OPERATING AS ANTICIPATED WOULD NOT BE REPORTABLE, SINCE THE GAS RELEASE WOULD BE WELL UNDER THE 3 MMSCF THRESHOLD FOR REPORTING. HOWEVER, ONE OF THE ESD ISOLATION VALVES UNEXPECTEDLY DID NOT CLOSE PROPERLY, SO THE ACTUAL GAS LOSS WAS GREATER THAN THE ESTIMATED 1.23 MMSCF, AND GREATER THAN THE 3 MMSCF REPORTING THRESHOLD. ON NOV. 24, THE ESTIMATED GAS LOSS WAS CALCULATED TO BE MORE THAN 3 MMSCF, AND THEN WAS REPORTED TO NRC. THIS EVENT HAS IDENTIFIED THE NEED FOR ADDITIONAL TRAINING AND AWARENESS OF THE REQUIREMENT TO IMMEDIATELY REPORT SUCH EVENTS TO INTERNAL PERSONNEL RESPONSIBLE FOR NRC NOTIFICATIONS. THE TRAINING WILL BE DEVELOPED AND IMPLEMENTED SYSTEM-WIDE IN 2019.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20180134 | 31360 | 2018-12-20 08:37 | ORIGINAL FINAL | 13063 | NATIONAL FUEL GAS SUPPLY CORP | 6363 MAIN STREET | WILLIAMSVILLE | NY | 14221-5887 | 2018-11-22 21:23 | 2018 |  |  | 42.6763 | -78.9443 | 1231490 | 2018-11-28 11:29 |  | NATURAL GAS |  | 5300 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELIEF VALVE REPAIR DID NOT REQUIRE SHUTDOWN OF THE PIPELINE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-11-22 21:47 | 2018-11-22 21:59 | ONSHORE | NY | 14006 | TOWN OF EVANS | ERIE | MILEPOST | RELIEF VALVE | LINE RM32/FERRIER RD. STATION | STATION EVE 47 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | RELIEF VALVE CONTROLS | 2001 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL | OTHER | [8 empty] | RELIEF VALVE RELEASE | CLASS 2 LOCATION | NO |  | 74 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 16000 | 14411.3475177305 | 200 | 208.213961922031 | 2100 | 2186.24660018132 | 0 | 0 |  |  | 18300 | 16040.0189253894 | 16805.8080798339 | [8 empty] | 317 |  | 320 | OTHER | SYSTEM MAXIMUM OPERATING PRESSURE |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE FACILITY IS CONNECTED TO A PIPELINE THAT WAS MONITORED AND CONTROLLED THROUGH SCADA BY THE CONTROLLERS WITHIN PARAMETERS. THE CAUSE OF THE INCIDENT WAS NOT DUE TO CONTROLLER ACTION NOR WAS THE INCIDENT NEGATIVELY AFFECTED BY CONTROLLER ACTION OR LACK OF ACTION. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES |  |  |  |  | YES | RELIEF VALVE PILOT GAS CONTROL FLOW RESTRICTOR. | [22 empty] | YES | COMPONENT FAILURE | [161 empty] | JOHN SEAGER | PIPELINE INTEGRITY ENGINEER | seagerj@natfuel.com | 716-857-7899 | 716-857-7508 |  |  |  | WILLIAM SNYDER | OPERATIONS SUPERINTENDENT | 716-827-2327 | snyderw@natfuel.com | NATIONAL FUEL GAS SUPPLY CORPORATION HAS REPORTED A NATURAL GAS INCIDENT AS A RESULT OF AN UNINTENTIONAL RELEASE OF NATURAL GAS ESTIMATED AT GREATER THAN THREE (3) MILLION CUBIC FEET, THAT OCCURRED AT 7700 FERRIER RD. IN THE TOWN OF EVANS, ERIE COUNTY, NY. NATIONAL FUEL CONFIRMED DISCOVERY OF THE INCIDENT ON WEDNESDAY NOVEMBER 28, 2018 AFTER COMPLETING A COMPREHENSIVE FLOW ANALYSIS OF GAS LOST DURING A RELIEF VALVE RELEASE THAT OCCURRED FROM APPROXIMATELY 9:23 PM TO 11:33 PM ON THURSDAY NOVEMBER 22ND, 2018. THE PROBABLE CAUSE OF THE INCIDENT WAS EQUIPMENT FAILURE OF A RESTRICTOR VALVE FOR A RELIEF VALVE CONTROL THAT CAUSED THE DEVICE TO FAIL IN AN OPEN POSITION. THERE WERE NO INJURIES OR PROPERTY DAMAGE. THE UPDATED NRC REPORT NUMBER 1231680.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190001 | 31882 | 2019-01-07 18:29 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2018-12-08 20:50 | 2018 |  |  | 42.2057 | -83.9686 | 1232438 | 2018-12-09 11:02 |  | NATURAL GAS |  | 5264 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-12-08 21:40 | 2018-12-09 14:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-12-08 20:50 | 2018-12-08 21:30 | ONSHORE | MI | 48158 | MANCHESTER | WASHTENAW | MILEPOST | ENGINE 3-1 | FREEDOM COMPRESSOR STATION | ENGINE 3-1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2016 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL TUBING - PILOT LINE | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 390 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 16358 | 14733.8014184397 | 1200 | 1249.28377153218 | 400 | 416.427923844062 | 645 | 671.490027198549 | LABORATORY EXAMINATION |  | 18603 | 16348.0382076392 | 17071.0031410145 | [8 empty] | 659 |  | 800 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | APPROPRIATE NOTIFICATIONS/RESPONSE WERE COMPLETED ACCORDING TO PROCEDURE - IMMEDIATE NOTIFICATION TO GAS CONTROL WHEN THE FAILURE WAS IDENTIFIED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | THE PILOT TUBE FOR A PILOT OPERATED PRESSURE RELIEF VALVE ON A HIGH PRESSURE COMPRESSOR DISCHARGE LINE CRACKED. AFTER THE PILOT TUBE CRACKED AND LEAKED DOWN CONTROL PRESSURE TO THE RELIEF VALVE WAS LOST AND THE RELIEF VALVE WENT INTO AN OPEN CONDITION, RELEASING GAS TO THE ATMOSPHERE. | YES |  |  |  |  | YES | [6 empty] | YES | [165 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  |  |  |  | JASON PIONK | GAS COMPLIANCE LEAD | 989-791-5749 | jason.pionk@cmsenergy.com | ON DECEMBER 8, 2018 AT APPROXIMATELY 20:50 HOURS CONSUMERS ENERGY GAS CONTROL RECEIVED A NOTIFICATION OF A POSSIBLE GAS RELEASE FROM A CONTRACTOR WORKING ONSITE AT CONSUMERS ENERGY FREEDOM COMPRESSOR STATION. FREEDOM COMPRESSOR STATION IS LOCATED IN MANCHESTER, MICHIGAN (WASHTENAW COUNTY) A STATION MECHANIC ARRIVED ONSITE AT APPROXIMATELY 21:30 HOURS AND IDENTIFIED A RELEASE AT RELIEF VALVE #171 (UNIT 3-1). THE MECHANIC CLOSED VALVE 171 TO ISOLATE THE GAS FROM ENGINE 3-1 WHICH STOPPED GAS FROM BLOWING. UPON FURTHER INVESTIGATION A CRACK (LEAK) ON THE RELIEF VALVE PILOT LINE WAS DISCOVERED. THE PILOT LINE LEAK CAUSED PRESSURE TO BLEED OFF WHICH ALLOWED THE RELIEF VALVE TO OPEN AND RELEASE GAS TO THE ATMOSPHERE. NEW PILOT LINE TUBING WAS INSTALLED AND A RELIEF VALVE INSPECTION PERFORMED TO VERIFY NO CHANGE IN SET PRESSURE OCCURRED AS A RESULT OF THE FAILURE. ADDITIONAL VALVE INSPECTIONS AND LEAK TESTS WERE PERFORMED ON THREE ADDITIONAL RELIEF VALVES LOCATED IN PLANT 3 AS A PRECAUTIONARY MEASURE. NO ADDITIONAL LEAKS WERE DISCOVERED. THE FAILED EQUIPMENT WAS SENT TO CONSUMERS ENERGY'S LABORATORY SERVICES FOR FURTHER ANALYSIS. A SUMMARY OF THE FINDINGS ARE DETAILED BELOW: THE LONGER LEG OF THE TUB FRACTURED IN HIGH CYCLE FATIGUE INITIATING AT MULTIPLE LOCATIONS ON THE TUB OD UNDER THE FERRULE, APPROXIMATELY 3/8" FROM THE END OF THE TUBE. THE FATIGUE CRACK HAD PROPAGATED APPROXIMATELY 300 DEGREES AROUND THE TUBE PRIOR TO THE TUBE BEING TAKEN OUT OF SERVICE. THE FRACTURE SURFACE EXHIBITED A TRANSITION AFTER APPROXIMATELY 150 DEGREES OF PROPAGATION INDICATING THE STATE OF STRESS CHANGED OR THE PROPAGATION RATE INCREASED. THE FERRULE AT THIS LOCATION WAS NOT SQUARE WITH THE TUBE ABOVE IT, INDICATING A SIDE LOAD MAY HAVE BEEN APPLIED AT SOME POINT. THERE WAS NO APPARENT DEFECTS AT THE CRACK ORIGIN LOCATION. THE TUBE, FERRULE AND NUT FROM THE FAILURE LOCATION WERE ALL MADE OF TYPE 316 STAINLESS STEEL. ALTHOUGH NO RELATED TO THE FAILURE, THE ID OF THE TUBING HAD AN INTER-GRANULAR TEXTURE CONSISTENT WITH HAVING BEEN IN CONTACT WITH A CORROSIVE MEDIA. THE CAUSE OF THIS IS NOT UNDERSTOOD, AND THIS CONDITION MAY HAVE BEEN PRESENT AS-RECEIVED FROM THE MANUFACTURER.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190002 | 31989 | 2019-01-09 17:33 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2018-12-10 19:00 | 2018 |  |  | 32.9133 | -97.5859 | 1232643 | 2018-12-11 12:01 |  | NATURAL GAS |  | 25 | 475 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-12-11 06:30 | 2018-12-11 20:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-12-10 19:00 | 2018-12-10 20:40 | ONSHORE | TX | 76020 | RENO | PARKER | SURVEY STATION NO. | 916+16 | LINE CA | NORTH FORT WORTH TO SPRINGTOWN | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 |  | 0.25 | 35000 | API 5L | SEAMLESS |  | UNKNOWN | COAL TAR | [28 empty] | 1950 | 1950 | CARBON STEEL |  | MECHANICAL PUNCTURE | 0.1 | 0.1 | [7 empty] | CLASS 3 LOCATION | YES | METHOD2 | 191 |  | NO | NO | NO |  | 0 | 0 | 2463 | 2564.15494106981 | 130 | 117.09219858156 | 75000 | 78080.2357207616 | 11685 | 12164.9007252947 | 0 | 0 |  |  | 89278 | 42723.308488991 | 92926.3835857076 | [8 empty] | 356 |  | 470 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 26400 | NO | [5 empty] | YES | NO LAUNCHERS | YES |  |  |  |  | YES | NO LAUNCHERS | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | NO |  |  |  |  | YES | [6 empty] | UTILITY | BORING | TELECOMMUNICATIONS | YES | 1884483868 | TEXAS811 | CONTRACT LOCATOR | NO | NO | YES | 14 | LOCATING PRACTICES NOT SUFFICIENT |  | FACILITY WAS NOT LOCATED OR MARKED | [264 empty] | SCOTT MCCRACKEN | OPERATIONS MANAGER | benjamine.mccracken@atmosenergy.com | 817-207-2803 |  |  |  |  | MARLO SUTTON | VICE PRESIDENT TECHNICAL SERVICES | 214-206-2033 | marlo.sutton@atmosenergy.com | ADDITIONAL NRC REPORT # 1232875 ON DECEMBER 10, 2018 AT 19:00, A THIRD PARTY CONTRACTOR HIT ATMOS ENERGY'S LINE CA, PUNCTURING THE LINE AND CAUSING A LEAK. THE LINE SEGMENT WAS ISOLATED AT 06:30 ON DECEMBER 11, 2018, AND A CONTROLLED GAS RELEASE WAS PERFORMED UNTIL LINE PRESSURE WAS ELIMINATED. AT THAT POINT, A TEN FOOT PIPE SEGMENT WAS REMOVED BY ATMOS ENERGY, AND APPROPRIATE REPAIRS WERE MADE. CNG RESOURCES WERE UTILIZED TO HOLD UP A SMALL RESIDENTIAL AREA AND SEVEN FARM TAP CUSTOMERS ON THE SEGMENT WERE OUT OF SERVICE DURING THE SHUTDOWN. SERVICE WAS RESTORED AT 20:30 ON DECEMBER 11, 2018. AFTER INVESTIGATION OF THE INCIDENT, IT WAS DETERMINED THAT CONTRACT LOCATOR DID NOT APPROPRIATELY MARK THE LINE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190003 | 31462 | 2019-01-10 10:16 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2018-12-12 09:50 | 2018 |  |  | 35.8487 | -87.4505 | 1232747 | 2018-12-12 11:20 |  | NATURAL GAS |  | 4529 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE UNIT WAS ALREADY SHUTDOWN. RELEASED GAS WAS THROUGH AN OPEN VENT VALVE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-12-12 10:09 | 2018-12-12 10:09 | ONSHORE | TN | 37137 | NUNNELY | HICKMAN | MILEPOST | VENT VALVE 1B | COMPRESSOR STATION 860 - BUILDING B | UNIT 1B VENT VALVE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2016 |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENTIONAL VENTING THROUGH UNIT 1B VENT VALVE (IN PROPER OPEN POSITION) BECAUSE OF OPEN LOAD VALVE. | CLASS 3 LOCATION | NO |  | 42 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 19784 | 17819.6312056738 | 350 | 364.374433363554 | 0 | 0 | 0 | 0 |  |  | 20134 | 18641.6782833836 | 18184.0056390373 | [8 empty] | 799 |  | 936 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE STATION WAS OPERATING WITHIN NORMAL RANGE PRIOR TO FALLING OFFLINE. THE CONTROLLERS DID NOT MAKE ANY SETPOINT OR OTHER HP CHANGES THAT WOULD PROMPT AN INVESTIGATION INTO THEIR ACTIONS. WHEN THE STATION FELL OFFLINE CONTROLLERS IMMEDIATELY CONTACTED THE FIELD. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | A SOLENOID OPERATED VALVE ACTUATOR IN THE BUILDING B SOLENOID OPERATED CONTROLS FAILED, ALLOWING THE SUPPLY PRESSURE TO OPEN THE LOAD VALVE. | [22 empty] | YES | SOLENOID OPERATED VALVE ACTUATOR FAILURE | [161 empty] | KRISTIN VAN DER LAAN | MANAGER-ENGINEERING-COMPLIANCE CODES AND STANDARDS | kristin_vanderlaan@kindermorgan.com | 303-914-7753 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR-ENGINEERING-COMPLIANCE CODES AND STANDARD | 713-369-9443 | jaime_hernandez@kindermorgan.com | TUESDAY, DECEMBER 11 (DETERMINED WEDNESDAY, DECEMBER 12, THROUGH TRENDING): A SOLENOID OPERATED VALVE ACTUATOR IN THE TENNESSEE GAS PIPELINE COMPANY (TGP) STATION 860 BUILDING B FAILED, ALLOWING THE SUPPLY PRESSURE TO OPEN THE LOAD VALVE TO BUILDING B'S COMPRESSOR UNIT 1B (UNIT 1B) UNIT 1B WAS NOT RUNNING AND WAS IN A NORMAL AVAILABLE-DEPRESSURIZE STATE AT THE TIME OF THE ACTUATOR FAILURE, NO ONE HAD BEEN IN BUILDING B ON DECEMBER 11 OR 12 PRIOR TO THE EVENT, THEREFORE THE ACTUATOR FAILURE WAS NOT DISCOVERED UNTIL DECEMBER 12. WEDNESDAY, DECEMBER 12: MORNING OF DECEMBER 12 - TECHNICIAN WAS CALIBRATING PRESSURE TRANSMITTERS IN THE STATION 860 YARD. FOLLOWING COMPANY PROCESS AND PROCEDURES, HE BYPASSED THE PRESSURE TRANSMITTERS PRIOR TO PERFORMING CALIBRATION. THE CONTROL LOGIC FOR THE STATION 860 CONTROLS QUERIED EACH TRANSMITTER FOR PRESSURES. WHEN THE COMPUTER DID NOT RECEIVE PRESSURE INFORMATION FROM THE THREE DISABLED PRESSURE TRANSMITTERS, IT ISSUED A DEFAULT PRESSURE OF 1000PSIG IN ORDER TO INITIATE A STATION SHUTDOWN DUE TO HIGH-PRESSURE CONDITION. 08:29A - STATION 860 SHUT DOWN. ALL UNITS IN BOTH BUILDINGS A AND B SHUTDOWN. 10:09A - LOCAL FIELD OPERATIONS DISCOVERED THE UNIT 1B VENT VALVE OPEN AND RELEASING GAS TO ATMOSPHERE. THE VALVE WAS IMMEDIATELY SHUT IN AND MANAGEMENT WAS NOTIFIED. 10:58A - GAS LOSS CALCULATIONS FINALIZED RESULTING IN AN ESTIMATED 4,529 MCF TOTAL UNINTENTIONAL RELEASE OF GAS. POST EVENT REPAIRS/ACTIONS: THE BUILDING B LOAD VALVE WAS PLACED IN MANUAL MODE, AND THE VENT VALVE WAS PLACED BACK IN OPERATION AND CLOSED. A NEW VALVE ACTUATOR HAS BEEN ORDERED AND REPAIRS ARE SCHEDULED FOR COMPLETION BEFORE THE END OF JANUARY 2019. BUILDING A WAS PLACED BACK IN OPERATION. POST EVENT EVALUATION - GAS RELEASE: WHEN THE UNIT 1B PLC RECEIVES THE SHUTDOWN COMMAND, IT SHUTS THE UNIT DOWN AND OPENS THE 2-INCH VENT VALVE, RELEASING THE GAS FROM UNIT 1B. IN THIS INSTANCE, THERE SHOULD NOT HAVE BEEN ANY GAS TO RELEASE BECAUSE OF THE AVAILABLE-DEPRESSURIZE STATE OF THE UNIT BUT BECAUSE THE ACTUATOR FAILURE CAUSED THE LOAD VALVE TO OPEN, THE LOAD VALVE FED GAS TO THE VENT VALVE. NOTE THAT BUILDING A CONTROL PROGRAMMING VARIES FROM BUILDING B CONTROL PROGRAMMING IN THAT BUILDING A SHUTS DOWN THE UNITS WITHOUT VENTING GAS. POST EVENT EVALUATION - STATION 860 SHUT DOWN: THE EMPLOYEE WAS FOLLOWING ESTABLISHED PROCESS AND PROCEDURE FOR CALIBRATING THE STATION TRANSMITTERS. THE SITE-SPECIFIC PROCEDURES FOR CALIBRATING THE STATION PRESSURE TRANSMITTERS DID NOT ADDRESS CONTROL SYSTEM SETTINGS WHEN BYPASSING THE PRESSURE TRANSMITTERS. THE SITE-SPECIFIC JOB PROCEDURE HAS BEEN UPDATED TO REFLECT THE ADDITIONAL CALIBRATION REQUIREMENTS PRIOR TO ACTUAL TESTING OF PRESSURE TRANSMITTERS. ADDITIONAL NOTES: 48-HOUR UPDATE NRC 1232934 PART A4 ESTIMATED BASED ON 100 MINUTES RELEASE = 4529 MCF. 3000MCF MET IN APPROX. 1 HOUR 21 MIN.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190004 | 32646 | 2019-01-11 15:44 | SUPPLEMENTAL FINAL | 288 | ALGONQUIN GAS TRANSMISSION, L.L.C. (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2018-12-13 09:38 | 2018 |  |  | 41.6432 | -72.8743 | 1232901 | 2018-12-13 14:36 |  | NATURAL GAS |  | 9.975 | 100 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-01-09 13:30 | 2019-01-10 15:09 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-12-13 09:38 | 2018-12-13 10:30 | ONSHORE | CT | 06489 | SOUTHINGTON | HARTFORD | MILEPOST | 4.229 | LINE M-2 | MSYS-EOLN | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 74 |  | YES |  |  |  |  | YES | UNCASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | 1" THREADED NIPPLE | UNKNOWN |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | YES | METHOD2 | 63 |  | NO | NO | NO |  | 0 | 0 | 302 | 314.403082502266 | 31 | 27.9219858156028 | 198467 | 206618.001903898 | 0 | 0 | 0 | 0 |  |  | 198800 | 95016.3821700542 | 206960.326972216 | [8 empty] | 165 |  | 189.5 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 43571 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | NOTIFICATION FROM PUBLIC |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURES THAT WOULD HAVE BEEN WITNESSED BY SCADA WOULD NOT HAVE BEEN OUTSIDE ACCEPTABLE LIMITS THEREFORE NO ALARMS WOULD HAVE BEEN RECEIVED BY THE CONTROLLERS | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | [204 empty] | EQUIPMENT NOT INSTALLED PROPERLY | [6 empty] | YES | INADEQUATE TORQUING OF NIPPLE | CONSTRUCTION | NO | [150 empty] | MAYRA SALINAS | SENIOR ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: 48 HR NRC REPORT 1233090 AT APPROXIMATELY 9:38 AM EST ON DECEMBER 13, 2018, A GAS UTILITY COMPANY NOTIFIED ENBRIDGE OF A POSSIBLE NATURAL GAS RELEASE DISCOVERED DURING A LEAK SURVEY IN CLOSE PROXIMITY TO ALGONQUIN GAS TRANSMISSION'S (AGT) NATURAL GAS PIPELINE AT SOUTHINGTON, CONNECTICUT. ENBRIDGE PERSONNEL WERE IMMEDIATELY DISPATCHED TO THE SITE AT ABOUT 10:30 AM EST. AGT'S INITIAL LEAK SURVEYS WAS INCONCLUSIVE BECAUSE OF THE LOW GAS LEVELS. AGT PERFORMED FURTHER TESTS WITH AN ETHANE GAS DETECTOR AND CONCLUSIVELY DETERMINED THE ORIGIN OF THE GAS RELEASE WAS FROM AGT'S PIPELINE FACILITIES AT ABOUT 2:00 PM EST. AGT PROACTIVELY MADE THE NRC CALL AT 2:36 PM EST AFTER DETERMINING THE COST OF EXCAVATION ACTIVITIES TO REPAIR THE LEAK WOULD EXCEED THE $50,000. AGT MADE EMERGENCY ONE CALL TICKETS AND REQUESTS FROM THE CITY OF SOUTHINGTON WERE PUT IN FOR EXCAVATION ACTIVITIES. AGT MOBILIZED CONTRACTORS TO BEGIN EXCAVATION ACTIVITIES AT THE SITE ON DECEMBER 14 AT ABOUT 8:00 AM. AGT UPON EXCAVATION, ENBRIDGE DETERMINED THAT THE APPARENT CAUSE OF THE LEAK WAS FROM A 1INCH THREADED NIPPLE. THE PIPE WAS REPLACED ON JANUARY 9-10, 2019. THE CAUSE OF THE RELEASE IS UNDER INVESTIGATION. SUPPLEMENTAL REPORT: THE APPARENT CAUSE IS THE 1 INCH THREADED NIPPLE WAS NOT PROPERLY TORQUED INTO THE THREAD-O-LET, RESULTING IN THE NATURAL GAS LEAK.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190005 | 34310 | 2019-01-15 16:40 | SUPPLEMENTAL FINAL | 4070 | EAST TENNESSEE NATURAL GAS, LLC (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2018-12-15 14:09 | 2018 | CENTRAL | NO | 36.3705 | -85.9609 | 1233110 | 2018-12-15 15:50 | 1233260 | NATURAL GAS |  | 46436 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2018-12-15 14:19 | 2018-12-29 19:00 |  | YES | OPERATOR | 2018-12-15 14:21 | NO | [5 empty] | VALVE CLOSURE |  | 2018-12-15 14:19 | VALVE CLOSURE |  | 2018-12-15 14:47 | 12 | 2018-12-15 14:09 | 2018-12-15 17:00 | ONSHORE | TN | 37145 | PLEASANT SHADE | SMITH | MILEPOST | MP 49.147 | DIXON SPRINGS - GAINESBORO | 3100-1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 22 | NO | 0.281 | 42000 | API 5L | OTHER | ERW - RESISTANCE WELDED USING A DC WELDING CURRENT | YOUNGSTOWN | COAL TAR |  | UNKNOWN | [26 empty] | 1949 | 1949 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 805 | 42 |  | CLASS 2 LOCATION | NO |  | 422 |  | NO | NO |  |  | 100000 | 104106.980961015 | 0 | 0 | 187601 | 168973.95035461 | 2865200 | 2982873.21849501 | 0 | 0 | 0 | 0 |  | 4.04 | 3152801 | 1592188.33408349 | 3255954.14981064 | 0 | 0 | 0 | 1 | NO |  |  |  | 756 | 193080 | 773 | 192.619(A)(1) |  | 1999-08-15 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | REMOTELY CONTROLLED | REMOTELY CONTROLLED | 123922 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE DID NOT EXCEED MAOP PRIOR TO THE FAILURE, AND THUS CONTROLLER ERROR WAS NOT THE CAUSE OF THE FAILURE. WHEN THE PRESSURE LOSS WAS OBSERVED, THE CONTROLLER PROMPTLY NOTIFIED APPROPRIATE COMPANY PERSONNEL TO RESPOND TO THE FAILURE. | [12 empty] | YES | 6 | 0 | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED |  | YES | [15 empty] | OTHER | THE MOST LIKELY MECHANISM FOR THE REDUCTION IN TOUGHNESS WAS HYDROGEN EMBRITTLEMENT OF THE ERW SEAM HEAT AFFECTED ZONE (HAZ.) | [11 empty] | YES | THE MOST LIKELY MECHANISM FOR THE REDUCTION IN TOUGHNESS WAS HYDROGEN EMBRITTLEMENT OF THE ERW SEAM HEAT AFFECTED ZONE (HAZ.) | UNKNOWN | [54 empty] | YES | YES | [6 empty] | 2018 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2012 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [45 empty] | YES | 2013 | 1025 | NO | [13 empty] | NO | [63 empty] | MAYRA SALINAS | ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: AT APPROXIMATELY 2:09 P.M. CST ON DECEMBER 15, 2018, ETNG'S 22-INCH DIAMETER LINE 3100-1 TRANSPORTING NATURAL GAS FROM DIXON SPRINGS COMPRESSOR STATION TO GAINESBORO COMPRESSOR STATION IN TENNESSEE FAILED AT MP 49.147. THE FAILED PIPE IS 22 INCH DIAMETER BY 9/32 INCH WALL THICKNESS, X-42. THE FAILURE RESULTED IN A RUPTURE WITHOUT FIRE. THERE WERE NO INJURIES OR FATALITIES. APPROXIMATELY 12 RESIDENTS EVACUATED UNTIL LOCAL EMERGENCY RESPONDERS OPENED ACCESS TO THE AREA. THE COMPRESSOR UNITS AT THE DIXON SPRINGS COMPRESSOR STATION WERE SHUTDOWN REMOTELY BY THE CONTROL ROOM AT 2:19 PM CST. THE ESD AT THE DIXON SPRING COMPRESSOR STATION WAS ACTIVATED AT 2:56 PM CST. THE MLV AT GAINESBORO COMPRESSOR STATION WAS CLOSED AT 2:47 PM CST FOLLOWED BY ESD ACTIVATION, COMPLETING INITIAL ISOLATION OF THE FAILURE SITE. ETNG PERSONNEL WERE ALSO DISPATCHED TO CLOSE THE MAINLINE BLOCK VALVES IMMEDIATELY DOWNSTREAM OF THE FAILURE SITE WHICH WAS CLOSED AT APPROXIMATELY 4:30 PM CST. ETNG PERSONNEL ARRIVED AT THE FAILURE SITE AT APPROXIMATELY 5:00 PM CST. THE NRC WAS NOTIFIED AT 3:50 PM CST, AS SOON AS LOCATION INFORMATION FOR THE FAILURE SITE WAS AVAILABLE. THE LINE WAS REPLACED, TESTED, AND SUBSEQUENTLY PUT IN-SERVICE ON DECEMBER 29, 2018. A 3RD PARTY METALLURGICAL INVESTIGATION IS ONGOING. THE ROOT CAUSE IS PENDING. SUPPLEMENTAL REPORT 09/27/2020 THE FAILURE HAS BEEN DETERMINED TO BE DUE TO A RELATIVELY SMALL 0.09' DEEP X 0.44' LONG HYDROGEN INDUCED CRACK IN THE ERW SEAM HEAT AFFECTED ZONE AT A LOCATION WHERE HYDROGEN EMBRITTLEMENT HAD REDUCED THE MATERIAL TOUGHNESS TO A LEVEL SUCH THAT THE PIPE COULD NOT WITHSTAND RUPTURE AT MOP.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190006 | 31535 | 2019-01-23 14:43 | ORIGINAL FINAL | 15259 | UGI PENN NATURAL GAS | 1 UGI DRIVE | DENVER | PA | 17517 | 2018-12-23 08:06 | 2018 |  |  | 41.4739 | -75.5452 | 1233820 | 2018-12-23 17:12 |  | NATURAL GAS |  | 9200 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-12-23 08:56 | 2018-12-23 11:49 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-12-23 08:06 | 2018-12-23 08:42 | ONSHORE | PA | 18434 | JESSUP | LACKAWANNA | MILEPOST | LEC METER | UGI METER AT LACKAWANNA ENERGY CENTER | UNIONDALE 16 PEI - MARSHWOOD | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | RELIEF VALVE | 2017 |  | CARBON STEEL |  | OTHER | [8 empty] | THE FACILITY INVOLVED WAS UGI'S OVER PRESSURE PROTECTION DEVICE WHICH WAS A 10"X12" RELIEF VALVE. THE RELIEF VALVE VENTED EXCESS GAS BUT DID NOT RE-SEAT ITSELF. | CLASS 3 LOCATION | YES | METHOD2 | 352 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 36000 | 32425.5319148936 | 3700 | 3851.95829555757 | 2000 | 2082.13961922031 | 0 | 0 |  |  | 41700 | 36340.9288015278 | 38359.6298296715 | [8 empty] | 684 |  | 720 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE ACTIONS OF THE CONTROLLER(S) DID NOT LEAD TO THIS INCIDENT NOR COULD HAVE PREVENTED THIS INCIDENT FROM OCCURRING. CONTROLLERS TOOK PROPER ACTIONS IN REACTING TO THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [13 empty] | YES | [177 empty] | JOHN D. TOUMEH | SENIOR ENGINEER | jtoumeh@ugi.com | 717 675 4606 |  |  |  |  | HANS G. BELL | CHIEF OPERATIONS OFFFICIER | 610 796 3450 | hbell@ugi.com | UGI UTILITIES, INC. (UGI) PROVIDES NATURAL GAS SERVICE TO A LARGE END USE CUSTOMER, THE LACKAWANNA ENERGY CENTER IN JESSUP, PA. UGI OPERATES MEASUREMENT AND REGULATION FACILITIES WHICH ARE LOCATED ON CUSTOMER'S PREMISES. WHILE THE CUSTOMER WAS PERFORMING TESTING OF ITS UTILIZATION EQUIPMENT, THE CUSTOMER'S EMERGENCY SHUTDOWN SYSTEM ACTIVATED, WHICH TRIGGERED THE ABRUPT CLOSURE OF A CUSTOMER OWNED VALVE LOCATED JUST DOWNSTREAM FROM THE UGI REGULATION FACILITIES. THE ABRUPT SHUTDOWN CAUSED A PRESSURE SPIKE AND THE UGI OVER-PRESSURE PROTECTION RELIEF VALVE OPENED TO RELIEVE EXCESS NATURAL GAS. WHEN PRESSURE WAS REDUCED, THE RELIEF DEVICE FAILED TO RE-SEAT AND CONTINUED TO VENT NATURAL GAS UNTIL THE REGULATOR STATION WAS ISOLATED THROUGH AN UPSTREAM STATION VALVE. ONCE ISOLATED, THE RELIEF WAS INSPECTED AND DAMAGE TO THE INTERNAL WEARING PARTS WAS REPAIRED. UGI HAS WORKED WITH THE CUSTOMER TO IMPROVE EMERGENCY SHUT-DOWN PROTOCOLS TO MINIMIZE THE POTENTIAL OF OVER-PRESSURE PROTECTION ACTIVATION. ADDITIONALLY, UGI IS IMPLEMENTING FACILITY MODIFICATIONS TO IMPROVE OVER-PRESSURE PROTECTION SYSTEM PERFORMANCE. AFTER THE SITUATION WAS MADE SAFE AND IMMEDIATE HAZARDS WERE MITIGATED, UGI PROCEEDED TO CALCULATE THE AMOUNT OF GAS RELEASED. ONCE UGI DETERMINED THAT THE GAS RELEASED EXCEEDED 3,000 MCF, A CALL WAS MADE TO THE NRC.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190007 | 31556 | 2019-01-25 09:30 | SUPPLEMENTAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2018-12-27 08:00 | 2018 |  |  | 34.004 | -93.8662 | 1234021 | 2018-12-27 11:51 |  | NATURAL GAS |  | 200 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | STOPPLES WERE INSTALLED WITH NEW PIPE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-12-27 08:00 | 2018-12-27 09:15 | ONSHORE | AR | 71852 | NASHVILLE | HOWARD | MILEPOST | ROAD CROSSING | AM-165 | AM-165 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | YES |  |  |  |  | YES | CASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 4 |  | 0.125 | 35000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | OTHER | MILL WRAP | [27 empty] | 1963 | 1963 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 2 LOCATION | NO |  | 62 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 834 | 751.191489361702 | 167000 | 173858.658204896 | 3000 | 3123.20942883046 | 0 | 0 |  |  | 170834 | 82018.1415610553 | 177733.059123088 | [8 empty] | 120 |  | 500 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 53741 | NO |  | YES | [5 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [52 empty] | LIGHTNING |  |  | DIRECT HIT |  |  | NO | [306 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 | 405 246 9273 |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | ON 12-27-2018, A NATURAL GAS LEAK WAS REPORTED ON ENABLE GAS TRANSMISSION LINE AM-165. THE LEAK WAS REPORTED TO BE COMING FROM A CASING VENT ON MOUNT PLEASANT DRIVE NEAR NASHVILLE, AR IN HOWARD COUNTY. THE PIPELINE WAS EXCAVATED ON BOTH SIDES OF THE ROAD AND NO SOLUTIONS FOR REPAIR WERE FOUND AS THE LEAK APPEARED TO BE INSIDE THE CASING. PLANS WERE INITIATED TO COMPLETE A BORE ACROSS THE ROAD AND TIE IN WITH STOPPLE FITTINGS. THE ROAD WAS CLOSED AND MANNED DURING THE REPAIR EFFORTS. THE BORE AND TIE-IN WERE COMPLETED ON 12-29-2018. UPON COMPLETION OF THE CONSTRUCTION, PIPING WAS REMOVED FROM THE CASING AND EXAMINED TO DETERMINE A CAUSE OF THE LEAK. THE CASING AND PIPE HISTORY WERE EVALUATED AND DID NOT HAVE A HISTORY OF BEING SHORTED AND THE PIPELINE HAD MET THE ESTABLISHED -.850 V POLARIZED POTENTIAL CRITERIA. UPON EXAMINATION OF THE PIPE, THERE WAS EVIDENCE OF LIGHTNING DAMAGE. THIS WAS IDENTIFIED BY METAL PUDDLING AND SPLATTER AT THE SITE OF THE LEAK. THE SURROUNDING PIPELINE SYSTEM WAS EVALUATED FOR ANY ADDITIONAL EFFECTS OF THE LIGHTNING AND NO OTHER DAMAGE WAS FOUND. AN INITIAL CALL WAS PLACED TO THE NRC ON 12/27 (#1234021) AND A 48 HOUR FOLLOW UP WAS PROVIDED ON 12/29 (#1234159). DURING THE 48 HOUR FOLLOW UP 3.1 MMCF WAS PROVIDED AS THE ESTIMATED VOLUME OF COMMODITY RELEASED. THIS ESTIMATE WAS CALCULATED USING A 1/2" HOLE AT 120 PSIG FOR 96 HOURS (EXPECTED TIME FOR COMPLETION). AFTER COMPLETION OF THE NEW BORE THE OLD CARRIER PIPE AND CASING WERE REMOVED AND IT WAS DISCOVERED THAT THE SIZE OF THE HOLE TO BE 1/8". THE LENGTH OF THE TIME OF GAS LOSS WAS SHORTER THAN INITIALLIY CALCULATED (56 HOURS INSTEAD OF 96). WHEN REPLACING 1/2" WITH AN 1/8", AND 96 HOURS WITH 56 THE GAS LOSS WAS LOWERED FROM 3.1 MMCF TO 200 MCF 1/28/2019 SUPPLEMENTAL REPORT PART E. 1 CHANGED ESTIMATED PRESSURE AT THE POINT AND TIME OF THE INCIDENT FROM 400 PSIG TO 120 PSIG. PART H ADDITIONAL DETAIL AROUND GAS LOSS CALCULATION FOR INCIDENT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190008 | 31567 | 2019-01-29 15:05 | ORIGINAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2019-01-10 14:30 | 2019 |  |  | 38.8486 | -79.3761 | 1234982 | 2019-01-10 14:40 |  | NATURAL GAS |  | 14230 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-01-10 13:05 | 2019-01-10 18:18 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-10 12:59 | 2019-01-10 12:59 | ONSHORE | WV | 26884 | SENECA ROCKS | PENDLETON | MILEPOST | 00+00 | SENECA ROCKS COMPRESSOR STATION | COMPRESSOR STATION EMERGENCY SHUTDOWN SYSTEM (ESD) | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | EMERGENCY SHUT SYSTEM (ESD) VALVE DID NOT CLOSE AS DESIGNED ALLOWING AN EXCESSIVE VOLUME OF GAS TO BE RELEASED OUT THE BLOW-OFF PIPE TO THE ATMOSPHERE. | CLASS 1 LOCATION | NO |  | 891 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 48382 | 48382 | 0 | 0 | 0 | 0 | 0 | 0 | N/A |  | 48382 | 50159.8162729659 | 48382 | [8 empty] | 862 |  | 1000 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATIONAL PERSONNEL AT THE COMPRESSOR STATION WERE PRESENT WHEN THE STATION'S EMERGENCY SHUTDOWN SYSTEM ACTIVATED THUS THE CONTROL ROOM WAS NOT INVOLVED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | STATION ESD VALVE DID NOT PROPERLY CLOSE AFTER UNINTENTIONAL ESD ACTIVIATION | [161 empty] | CHRIS LEGG | US REGULATORY SPECIALIST | chris_legg@transcanada.com | 304-545-4350 |  |  |  |  | GEORGE HAMATY | MANAGER TC-EAST | 304-357-3728 | george_hamaty@transcanada.com | ON JANUARY 10, 2019, AT 12:59 PM WHILE SETTING UP THE VALVE INDICATION, AN ELECTRICAL SHORT OCCURRED THAT CAUSED A RAPID DEGRADATION OF AN ELECTRICAL FUSE THAT WAS LINKED TO THE ESD SYSTEM. THIS NEW VALVE (NUMBER C7-273) WAS INSTALLED AS PART OF 2018-2019 WBX PROJECT. THE BLOWN FUSE CAUSED THE STATION TO ACTIVATE THE EMERGENCY SHUTDOWN SYSTEM (ESD). AFTER A PROLONGED BLOW DOWN, IT WAS DISCOVERED THAT VALVE 3029(STATION FIRE VALVE) DID NOT OPERATE/CLOSE. A PRELIMINARY INVESTIGATION INDICATED THE VALVE DID NOT CLOSE DUE TO ICE BUILDUP IN THE ACTIVATION SWITCH. BECAUSE VALVE 3029 DID NOT CLOSE DURING THE ESD, AN EXCESSIVE AMOUNT OF GAS WAS EVACUATED. GAS LOSS WAS APPROXIMATELY 14,230 MCF. NO FIRE OR EXPLOSIONS, DEATHS, INJURIES OR EVACUATIONS OCCURRED AS A RESULT OF THE RELEASE. GAS WAS RELEASE THROUGH DESIGNED ESD BLOW-OFF STACKS/PIPES TO THE ATMOSPHERE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190009 | 31641 | 2019-01-29 16:58 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2019-01-20 04:10 | 2019 |  |  | 38.4018 | -81.4172 | 1235614 | 2019-01-20 04:17 |  | NATURAL GAS |  | 5129 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE RELIEF VALVE WAS ISOLATED BUT THE STATION CONTINUED TO OPERATE/RUN. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-20 03:19 | 2019-01-20 03:19 | ONSHORE | WV | 25071 | ELKVIEW | KANAWHA | MILEPOST | 00+00 | COCO COMPRESSOR STATION | STATION GAS SUCTION/WITHDRAW HEADER PIPING | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENTIONAL ACTIVATION OF A RELIEF VALVE | CLASS 1 LOCATION | NO |  | 891 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 17439 | 17439 | 0 | 0 | 0 | 0 | 0 | 0 | N/A |  | 17439 | 18079.8031496063 | 17439 | [8 empty] | 781 |  | 1000 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE ACTIVATION OF A RELIEF VALVE RESULTING IN A GAS RELEASE DID NOT INVOLVE CONTROL ROOM. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | ICE IN THE PILOT SENSING DEVICE | [161 empty] | CHRIS LEGG | US REGULATORY COMPLIANCE SPECIALIST | chris_legg@transcanada.com | 304-545-4350 |  |  |  |  | GEORGE HAMATY | MANAGER - US REGULATORY COMPLIANCE - EAST | 304-357-3728 | george_hamaty@transcanada.com | ON 01/20/2019, AN 8" RELIEF VALVE AT COCO COMPRESSOR STATION UNINTENTIONALLY ACTIVATED AND RELEASED A REPORTABLE QUANTITY (5,129 MCF) OF NATURAL GAS TO THE ATMOSPHERE. THE RELIEF VALVE IS LOCATED ON THE 36" SUCTION HEADER OF THE STATION AND ACTS AS A TERTIARY OVERPRESSURE-PRESSURE PROTECTION (OPP) DEVICE. THE FIRST AND SECOND OPP DEVICES DID NOT ACTIVATE. THE CAUSE OF THE RELEASE WAS INVESTIGATED. ICE BUILD-UP IN THE PRESSURE SENSING LINES (PILOT)CREATED A DIFFERENTIAL IN PRESSURE CAUSING THE RELIEF VALVE TO OPEN. NO FIRE, EXPLOSION, DEATHS, INJURIES OR EVACUATIONS OCCURRED AS A RESULT OF THE RELEASE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190010 | 31640 | 2019-01-30 15:21 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2019-01-21 03:40 | 2019 |  |  | 38.4771 | -81.7106 | 1235670 | 2019-01-21 05:43 |  | NATURAL GAS |  | 5406 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE EMERGENCY SHUTDOWN VALVE WAS ISOLATED BUT THE STATION CONTINUED TO RUN | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-21 03:43 | 2019-01-21 04:45 | ONSHORE | WV | 25159 | CHARLESTON | KANAWHA | MILEPOST | 00+00 | LANHAM COMPRESSOR STATION | CABOT EMERGENCY SHUTDOWN SYSTEM (ESD) VALVE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | OTHER | ESD VALVE (#C9-149) |  |  | NO | [22 empty] | INTERSTATE | ABOVEGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | OTHER | [37 empty] | EMERGENCY SHUTDOWN SYSTEM VALVE | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | MECHANICAL/EQUIPMENT FAILURE OF AN EMERGENCY SHUTDOWN SYSTEM (ESD) VALVE | CLASS 1 LOCATION | NO |  | 857 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 18380 | 18380 | 0 | 0 | 0 | 0 | 0 | 0 | N/A |  | 18380 | 19055.3805774278 | 18380 | [8 empty] | 742 |  | 920 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CAUSE OF THE ESD VALVE FAILURE DID NOT INVOLVE THE CONTROL ROOM. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | ICE BUILD-UP IN THE VALVE ACTUATOR/TRIGGER DEVICE | [161 empty] | CHRIS LEGG | US REGULATORY COMPLIANCE SPECIALIST | chris_legg@transcanada.com | 304-545-4350 |  |  |  |  | GEORGE HAMATY | MANAGER - US REGULATORY COMPLIANCE - EAST | 304-357-3728 | george_hamaty@transcanada.com | ON 01/21/2019 AT 3:40 AM EST, AT LANHAM COMPRESSOR STATION, LOCATED IN CHARLESTON, WV, KANAWHA COUNTY, AN EMERGENCY SHUTDOWN SYSTEM (ESD) VALVE (C9-149) MALFUNCTIONED AND OPENED RELEASING NATURAL GAS TO THE ATMOSPHERE. THE OPERATING PRESSURE OF THE PIPING AT THE TIME OF THE RELEASE WAS 742 PSIG (920 MAOP). THE GAS WAS RELEASED THROUGH A 4" ESD BLOWOFF STACK IN A DESIGNED/SAFE LOCATION. THE PUBLIC HEARD THE GAS RELEASE AND NOTIFIED THE MONITORING CENTER, PART OF THE CONTROL ROOM AT 3:43 AM. OPERATIONS PERSONNEL WERE CALLED TO THE SCENE, ARRIVING AT 4:45 AM AND MANUALLY ISOLATED THE VALVE AT APPROX. 5:00 AM, AS THE REST OF THE STATION CONTINUED TO RUN. THE GAS VOLUME THAT WAS RELEASED WAS CALCULATED AT 5,406 MCF. NO DEATHS, INJURIES, FIRE, EXPLOSION OR EVACUATIONS RESULTED FROM THE RELEASE. THE PRELIMINARY INVESTIGATION OF THE FAILURE DETERMINED ICE HAD ACCUMULATED IN THE VALVE CONTROLLER/TRIGGER DEVICE CAUSING THE VALVE TO ACTUATE.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190011 | 32162 | 2019-01-31 16:22 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2019-01-03 18:13 | 2019 |  |  | 35.3966 | -110.3354 | 1234503 | 2019-01-03 20:04 |  | NATURAL GAS |  | 7663 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-01-03 18:13 | 2019-01-04 07:22 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-03 18:13 | 2019-01-03 19:06 | ONSHORE | AZ | 86047 | Not Within a Municipality | NAVAJO | MILEPOST | VALVE: 20 1/2 | DILKON COMPRESSOR STATION | DILKON COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | INSTRUMENTATION | [38 empty] | UNKNOWN |  | CARBON STEEL |  | LEAK |  |  | OTHER | LOW POWER GAS PRESSURE | [5 empty] | CLASS 1 LOCATION | NO |  | 619 |  | NO | NO | NO |  | 0 | 0 | 0 | 0 | 21529 | 21529 | 4600 | 4693.60227474676 | 50 | 51.0174160298561 | 0 | 0 |  |  | 26179 | 24497.9974970696 | 26273.6196907766 | [8 empty] | 556 |  | 894 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER(S) ACTIONS DID NOT CAUSE OR CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | LOW POWER GAS PRESSURE TO POWER THE VALVE ACTUATOR. | [147 empty] | JORGE LOPEZ | ENGINEER COMPLIANCE CODES AND STANDARDS | jorge_lopez@kindermorga.com | 7016096218 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | ON JANUARY 3, 2019, A FIRE EYE ALARM AT DILKON COMPRESSOR STATION RESULTED IN A STATION ESD. A NORMAL ESD OPERATION AT THIS FACILITY WOULD NOT HAVE MET THE DOT/PHMSA REPORTABLE RELEASE VOLUME OF 3,000 MCF. AT THE TIME OF THE ESD NO UNITS AT THE STATION WERE RUNNING AND THE STATION VALVES WERE OPEN. DURING THE ESD OPERATION GAS VENTED THROUGH A 4" BRANCH CONNECTION THROUGH A VENT VALVE. AS PART OF OUR INVESTIGATION IT WAS DETERMINED THAT THE ACTUATOR ON THE STATION DISCHARGE VALVE DID NOT CLOSE COMPLETELY DUE TO LOW POWER GAS PRESSURE. THE INCOMPLETE VALVE CLOSURE IS WHAT CAUSED THE GAS TO VENT FOR A LONGER PERIOD OF TIME AND EVENTUALLY SURPASSED THE REPORTABLE QUANTITY OF 3,000 MCF. AT 18:13 KM TECHNICIAN WAS DISPATCHED TO THE SITE BY GAS CONTROL AND ARRIVED AT 19:06 WHERE HE VISUALLY DISCOVERED THE GAS VENTING AND CONFIRMED A FALSE FIRE ALARM. THE EMPLOYEE THEN PROCEEDED TO MANUALLY CLOSE THE DISCHARGE VALVE AT 19:20. AN ERL CALL WAS HELD AT 19:50 WHERE THE GAS LOSS WAS ESTIMATED TO EXCEED THE REPORTING THRESHOLD. CODES AND COMPLIANCE REPORTED THIS EVENT PRIOR TO THE 1 HOUR DEADLINE FROM CONFIRMED DISCOVERY. TOTAL GAS LOSS VOLUME WAS UNKNOWN AT THE TIME INCIDENT WAS INITIALLY REPORTED TO NRC, OPERATIONS CALCULATED THE GAS LOSS AT 10,404 MCF FOR THE 48HR NRC UPDATE. AS PART OF OUR INVESTIGATION AFTER FURTHER REVIEW BY KINDER MORGAN MEASUREMENT SME'S THE TOTAL GAS LOSS WAS CALCULATED AT 7,663 MCF. THE POWER GAS FOR THIS ACTUATOR COMES FROM A BURIED PRESSURE BOTTLE FED BY THE SUCTION SIDE OF THE PLANT DOWNSTREAM OF THE STATION SUCTION VALVE. NORMALLY THIS BURIED BOTTLE HAS PLENTY OF PRESSURE TO CLOSE ALL REQUIRED VALVES, BUT IN THE EVENING HOURS OF JANUARY 3RD THE MAINLINE HAD LOWER THAN NORMAL OPERATING PRESSURE. WHEN THE STATION EXPERIENCED AN ESD THE PRESSURE IN THE BOTTLE WAS NOT SUFFICIENT TO CLOSE THE STATION DISCHARGE VALVE. ON JANUARY 4TH EMPLOYEES RETURNED THE STATION TO SERVICE AT 07:22, INCLUDING RESTORING PRESSURE TO THE UNDERGROUND ESD STORAGE BOTTLE BY 07:45, CLEARED THE ESD ALARMS, AND TESTED THE VALVE ACTUATOR WHICH WORKED AS DESIGNED AND HAD APPROPRIATED GAS PRESSURE TO OPERATE.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190012 | 32865 | 2019-02-05 15:27 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | ONE ENERGY PLAZA | DETROIT | MI | 48226 | 2018-12-30 00:22 | 2018 |  |  | 42.7645 | -83.903 | 1234214 | 2018-12-30 09:59 |  | NATURAL GAS |  | 14700 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | BLOCK VALVE FOR RELIEF SHUT-OFF | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-12-30 00:22 | 2018-12-30 01:15 | ONSHORE | MI | 48855 | DEERFIELD TOWNSHIP | LIVINGSTON COUNTY | MILEPOST | MLV 9 | C PIPELINE | 8,000 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | SUSPECTED MECHANICAL FAILURE OF THE PILOT CONTROL FOR THE RELIEF VALVE | CLASS 1 LOCATION | NO |  | 645 |  | NO | NO | NO |  | 110 | 114.517679057117 | 0 | 0 | 47775 | 43031.3829787234 | 15000 | 15616.0471441523 | 200 | 208.213961922031 | 0 | 0 |  |  | 63085 | 51928.908688747 | 58970.1617638549 | [8 empty] | 722 |  | 844 | OTHER | 192.611(A)(1)(I) |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL |  | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE FACILITY BEING MONITORED WOULD NOT HAVE PROVIDED AN INDICATION THAT SOMETHING WAS WRONG. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | BREAK DOWN OF THE DIAPHRAGM GASKET | [161 empty] | FRENAE SMITH | MANAGER CODES AND STANDARDS | frenae.smith@dteenergy.com | 313-389-7762 |  |  |  |  | FRENAE SMITH | MANAGER CODES AND STANDARDS | 313-389-7762 | frenae.smith@dteenergy.com | DTE GAS DISPATCH RECEIVED A CALL FROM A CUSTOMER AT 00:22 OF AN ODOR IN AIR NEAR MAIN LINE VALVE 9 AT E. COHOCTAH RD. AND LUTZ RD. GAS DISPATCH CONTACTED GAS CONTROL AND THEY CONTACTED OPERATIONS. OPERATIONS SENT AN EMPLOYEE TO MLV 9 TO INVESTIGATE AND THE EMPLOYEE DISCOVERED THE RELIEF VALVE NORTH OF MLV 9 ON THE C LINE RELIEVING GAS TO ATMOSPHERE. THE TECHNICIAN CLOSED THE BLOCK VALVE UNDER THE RELIEF VALVE TO STOP THE BLOWING GAS. THE TECHNICIAN DID NOT OBSERVE ANY APPARENT PHYSICAL DAMAGE TO THE RELIEF. THE C LINE (MAOP 844) WAS MADE "COMMON" WITH THE A & B LINES (MAOP 811) AND THE ALARM POINT FOR THE C LINE WAS LOWERED TO 811 THUS PROTECTING THE C LINE UNTIL PERMANENT REPAIRS CAN BE MADE. THE CAUSE OF FAILURE (RELIEF VALVE) WAS DUE MATERIAL FAILURE. A NEW VALVE WAS INSTALLED ON 5/29/2019 AND THE C-LINE WAS RETURNED TO SERVICE WITH AN ALARM POINT AT 844 MAOP.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190013 | 32616 | 2019-02-07 15:06 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2019-01-08 14:34 | 2019 |  |  | 30.459 | -93.1459 | 1234847 | 2019-01-08 15:20 |  | NATURAL GAS |  | 112.8 | 41 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THIS STATION WAS CURRENTLY NOT RUNNING. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-08 14:34 | 2019-01-08 14:34 | ONSHORE | LA | 70657 | RAGLEY | BEAUREGARD PARISH | MILEPOST | 64.4 | GILLIS COMPRESSOR STATION | GILL-OPEL | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 96 |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | WELD/FUSION |  | 2 |  | 0.218 | 35000 | ASTM A106 | SEAMLESS |  | VALLOUREC | EPOXY | [9 empty] | PIPE GIRTH WELD | [18 empty] | 2017 | 2016 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 42 |  | NO | NO | NO |  | 0 | 0 | 130 | 132.645281677626 | 358 | 358 | 250000 | 255087.08014928 | 0 | 0 | 0 | 0 |  |  | 250488 | 117523.743268652 | 255577.725430958 | [8 empty] | 855 |  | 936 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE VOLUME OF THE LEAK WAS MINIMAL TO BE DETERMINED BY CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [52 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | BASED ON THE METALLURGICAL TESTING, ASSESSMENT OF THE SITE AND REVIEW OF THE RADIOGRAPHIC REPORT IT WAS DETERMINED THAT THE TWO PIPES SETTLED IN DIFFERENT DIRECTIONS CAUSING A STRESS CONCENTRATION AT THIS POINT. | NO | [306 empty] | MAYRA SALINAS | ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: 48 HR NRC REPORT 1234963 AT APPROXIMATELY 2:34 PM CST ON JANUARY 8, 2019, AN ENBRIDGE EMPLOYEE DISCOVERED A NATURAL GAS RELEASE BELOW GROUND AT THE GILLIS COMPRESSOR STATION ON THE TEXAS EASTERN TRANSMISSION (TETLP) SYSTEM IN BEAUREGARD PARISH, LA. THE LEAK WAS LOCATED NEAR THE INLET OF A FILTER SEPARATOR. THE FILTER SEPARATOR WAS ISOLATED AND BLOWN DOWN ON JANUARY 8, 2019, AND IT REMAINED ISOLATED UNTIL REPAIR WAS COMPLETE. THE APPARENT CAUSE IS UNDER INVESTIGATION. THE 2 INCH PIPE WAS REPLACED AND ADDITIONAL PIPE SUPPORTS WERE INSTALLED. SUPPLEMENTAL REPORT (08/26/2019) TETLP PERFORMED METALLURGICAL TESTING OF THE PIPE AND THE RESULTS DID NOT IDENTIFY ANY ROOT CAUSE. IN ADDITION, THE RADIOGRAPH FILM WAS REVIEWED BY AN ASNT LEVEL III. THE RADIOGRAPH WAS FREE OF DEFECTS AND MET API 1104. BASED ON THE METALLURGICAL TESTING PERFORMED, ASSESSMENT OF THE SITE AND REVIEW OF THE RADIOGRAPHIC REPORT IT WAS DETERMINED THAT THE CAUSE OF THE LEAK WAS THE TWO PIPES SETTLING IN DIFFERENT DIRECTIONS CAUSING A STRESS CONCENTRATION AT THIS POINT.
2021-02-26 10:37 | YES | NO | GT (Gas Transmission) | 20190014 | 31704 | 2019-02-13 14:31 | SUPPLEMENTAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 499 W. SHERIDAN STE 1500 | OKLAHOMA CITY | OK | 73102 | 2019-01-18 13:45 | 2019 |  |  | 33.4618 | -94.3726 | 1235534 | 2019-01-18 15:50 |  | NATURAL GAS |  | 5 | 10 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-01-18 14:20 | 2019-01-22 23:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-18 13:45 | 2019-01-18 13:45 | ONSHORE | TX | 75570 | NEW BOSTON | BOWIE | MILEPOST | CM-22 | CM-22 | CM-22 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | YES |  |  | YES | CASED | YES | CASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 4 |  | 0.237 | 24000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1953 | 1953 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 44 |  | NO | NO | NO |  | 1000 | 1020.34832059712 | 40 | 40.8139328238848 | 20 | 20 | 170000 | 173459.214501511 | 10000 | 10203.4832059712 | 0 | 0 |  |  | 181060 | 84813.860907781 | 184743.859960903 | [8 empty] | 220 |  | 250 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 1165 | NO |  | YES | [5 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [8 empty] | YES | PINHOLE LEAK IN WELD | [13 empty] | YES | [62 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | ON 1/18/2019 ENABLE MIDSTREAM O&M TECHNICIANS WERE IN THE NEW BOSTON, TEXAS AREA PERFORMING MAINTENANCE AND NOTICED A SLIGHT GAS ODOR WHILE TRAVELING DOWN TEXAS STATE HIGHWAY 82. DUE TO CM-22 (4') BEING IN THE AREA, THE TECHNICIANS PERFORMED AN INSPECTION OF THE AREA USING GAS DETECTION EQUIPMENT. IT WAS CONFIRMED THAT CM-22 WAS LEAKING WITHIN A CASED RAILROAD CROSSING PARALLEL TO US HWY 82 NEAR NEW BOSTON TEXAS. THE TEAM CLOSED THE HWY TEMPORARILY WHILE THE LINE WAS ISOLATED AND BLOWN DOWN. THE ROAD WAS CLOSED AT 2:20 PM AND REOPENED AT 4:30 PM. A NEW BORE WAS PERFORMED AND THE FINAL TIE-INS WERE COMPLETED 1/22/2019. WHEN THE CARRIER PIPE WAS REMOVED THE PIPE WAS THOROUGHLY CLEANED AND INSPECTED, AND NO CORROSION WAS OBSERVED ON THE PIPE. DUE TO THIS, IT IS ASSUMED THERE IS A SMALL PINHOLE LEAK IN A WELD SOMEWHERE ON THE PIPE. THE PIPE WILL HAVE END CAPS WELDED ON AND PRESSURED UP TO DETERMINE WHERE THE LEAK IS COMING FROM. AN INITIAL CALL WAS PLACE TO THE NRC ON 1/18/2019 @ 16:50 (NRC# 1235534) AND A 48 HOUR FOLLOW UP WAS PLACED ON 1/20/2019 @ 08:26 (NRC# 1235618). A SUPPLEMENTAL REPORT WILL BE PROVIDED WHEN TESTING AND FINAL CONSTRUCTION COSTS ARE COMPLETED. 2/26/2019 SUPPLEMENTAL D.7.B CHANGED FROM $85,000 TO $170,000 D.7.C CHANGED FROM $500 TO $10,000 NARRATIVE - A THOROUGH REVIEW OF THE PIPE WAS PERFORMED AND CORROSION DEFECTS WERE NOT FOUND. THERE IS HIGH CONFIDENCE THAT THE LEAK IS DUE TO A PINHOLE IN A WELD AND WE WILL NOT BE MOVING FORWARD WITH WELDING THE PIPE BACK TOGETHER AND HYDROTESTING.
2021-02-26 10:37 | NO | NO | GT (Gas Transmission) | 20190015 | 32062 | 2019-02-15 10:42 | SUPPLEMENTAL FINAL | 2564 | COLORADO INTERSTATE GAS CO | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2019-01-18 03:55 | 2019 |  |  | 40.1173 | -104.6089 | 1235460 | 2019-01-18 02:04 |  | NATURAL GAS |  | 3282 | 96.1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-01-18 04:17 | 2019-01-18 15:06 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-17 23:55 | 2019-01-18 01:18 | ONSHORE | CO | 80642 | Not Within a Municipality | WELD | MILEPOST | MP 63 +563 | L0250A HIGH PLAINS MAIN LINE | STA 250-A HUDSON | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | WELD/FUSION | [19 empty] | OTHER BUTT WELD | [18 empty] | 2013 |  | CARBON STEEL |  | LEAK |  |  | OTHER | WELD FAILURE. | [5 empty] | CLASS 1 LOCATION | NO |  | 717 |  | NO | NO | NO |  | 0 | 0 | 337 | 343.85738404123 | 11516 | 11516 | 5000 | 5101.74160298561 | 500 | 510.17416029856 | 700 | 714.243824417985 | METALLURGICAL LABORATORY ANALYTICAL COST. |  | 18053 | 15000.8738956391 | 18186.0169717434 | [8 empty] | 817 |  | 1200 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | NOTIFICATION FROM A 3RD-PARTY OIL AND GAS OPERATOR WORKING NEAR THE LOCATION. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO CONTROLLER ACTIONS OR CONTROL ROOM ISSUES WERE DETERMINED TO BE A CAUSE OR CONTRIBUTING FACTOR TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES |  |  |  | YES | MECHANICAL VIBRATION | [23 empty] | YES | HIGH-CYCLE, LOW STRESS, UNIDIRECTIONAL BENDING FATIGUE. | [55 empty] | NO | [63 empty] | YES |  |  | NO | [13 empty] | NO | [63 empty] | STEPHEN R. DINES | ENGINEER - CODES AND STANDARDS | stephen_dines@kindermorgan.com | (719) 329-5633 |  |  |  |  | JAIME A. HERNANDEZ | DIRECTOR ENGINEERING - CODES AND STANDARDS | 713 369-9443 | jaime_hernandez@kindermorgan.com | ON JANUARY 17, 2019 AT APPROXIMATELY 11:55 PM LOCAL TIME, COLORADO INTERSTATE GAS (CIG) GAS CONTROL RECEIVED A TELEPHONE CALL FROM A THIRD-PARTY OIL AND GAS OPERATOR REPORTING A SOUND OF GAS RELEASING FROM OUR PIPELINE FACILITY AT THE L250A PIG LAUNCHER AND PIG RECEIVING FACILITY IN WELD COUNTY, COLORADO. UPON RECEIVING THE THIRD-PARTY REPORT, GAS CONTROL CALLED THE CIG AREA SUPERVISOR AND DISPATCHED HIM TO THE LOCATION. HE ARRIVED ON SITE AT 1:18 AM LOCAL TIME ON JANUARY 18, 2019 AND VERIFIED THAT THE GAS LEAK WAS IN FACT ON THE CIG L250 PIPELINE PIG TRAP FACILITY. AT 1:50 AM LOCAL TIME ON JANUARY 18, 2019, CIG INITIATED AN INTERNAL EMERGENCY-RESPONSE-LINE (ERL) TELEPHONE CALL TO DISCUSS THE AVAILABLE INFORMATION REGARDING THE GAS LEAK TO DETERMINE WHETHER DISCOVERY OF A REPORTABLE EVENT OCCURRED. SINCE THE 250A SEGMENT IMPACTED BY THE LEAK COULD NOT BE IMMEDIATELY ISOLATED UNTIL ALTERNATIVE GAS SUPPLIES FOR CIG'S CUSTOMERS SERVED FROM THAT SEGMENT COULD BE ARRANGED, CIG DECIDED TO ASSUME THE RELEASE VOLUMES WOULD EXCEED THE REPORTABLE THRESHOLD AND DECIDED TO NOTIFY THE NATIONAL RESPONSE CENTER (NRC) OF THE EVENT PRIOR TO ESTABLISHING THE ACTUAL VOLUMES RELEASED. IT WAS NOT UNTIL THE AFFECTED SEGMENT CONTAINING THE LEAK COULD BE ISOLATED AT 4:17 AM ON JANUARY 18, 2019, THAT CIG WAS ABLE TO ESTIMATE THE ACTUAL RELEASE VOLUME. DURING THE INITIAL INVESTIGATION, CIG CALCULATED THE TOTAL RELEASE VOLUME (3,282 MCF) AND DETERMINED IT HAD MET THE REPORTING REQUIREMENT FOR THE EVENT AT 3:55 AM ON JANUARY 18, 2019. THE NRC WAS NOTIFIED AT 2:04 AM LOCAL TIME ON JANUARY 18, 2019 (NRC NO. 1235460) OF THE GAS RELEASE WITH AN ESTIMATE TO BE GREATER THAN 3,000 MCF AND RESULTING IN A REPORTABLE EVENT. THE NRC LOGGED RECEIPT OF THE REPORT AT 2:09 AM LOCAL TIME. A COURTESY NOTIFICATION TO THE PHMSA INCIDENT INVESTIGATION TEAM WAS PROVIDED AT 2:38 AM LOCAL TIME THAT DAY. AT 3:06 PM LOCAL TIME ON JANUARY 18, 2019, ALL REPAIRS TO THE FACILITIES WERE COMPLETE AND RETURNED TO SERVICE. AT 3:54 PM LOCAL TIME ON JANUARY 18, 2019, A 48-HOUR UPDATE REPORT WAS CALLED INTO THE NRC (REPORT NO. 1235523) PROVIDING THE TOTAL VOLUME OF THE RELEASE (3,282 MCF) WITH CONFIRMATION THAT THERE WERE NO CUSTOMER IMPACTS DUE TO THE INCIDENT. THE NRC LOGGED THE RECEIPT OF THE REPORT AT 14:02 LOCAL TIME. THE 1' BLOW-OFF VALVE ASSEMBLY THAT FAILED WAS SENT FOR A COMPLETE METALLURGICAL ANALYSIS TO DETERMINE THE ROOT CAUSE OF THE FAILURE. FROM THE METALLURGICAL ANALYSIS, IT WAS DETERMINED THE ROOT CAUSE OF THE BUTT WELD FAILURE WAS CAUSED BY HIGH-CYCLE, LOW NOMINAL STRESS, UNIDIRECTIONAL-BENDING FATIGUE. OPERATIONS FIELD PERSONNEL OBSERVED THAT THE 1' BLOW-OFF VALVE ASSEMBLY WAS FOUND APPROXIMATELY 25 FEET FROM THE WELDED COUPLING LOCATED ON THE 250A PIPELINE FOLLOWING THE EVENT. THE THREADED NIPPLE END OF THE ASSEMBLY WAS LOCATED APPROXIMATELY 6-12 INCHES FROM THE REST OF THE VENT VALVE ASSEMBLY. THE VALVE WAS FOUND IN THE CLOSED POSITION. BASED ON THESE OBSERVATIONS, IT WAS CONCLUDED THAT THE WELDED END FAILED FIRST AND THE THREADED NIPPLE SEPARATED FROM THE VENT VALVE AFTER THE ENTIRE 1' BLOW-OFF VALVE ASSEMBLY WAS EJECTED AND IMPACTED WITH THE GROUND. THE METALLURGICAL ANALYSIS DID NOT IDENTIFY ANY MATERIAL COMPOSITION DEFICIENCIES OF THE ASSEMBLY. IN ADDITION NO EVIDENCE OF EXCESSIVE TORQUE WAS IDENTIFIED. CIG CONCLUDED THE ROOT CAUSE OF THE THREADED-END OF THE NIPPLE BLOW-OFF VALVE ASSEMBLY FAILURE RESULTED FROM THE ASSEMBLY IMPACTING THE GROUND SURFACE. THE ROOT CAUSE OF THE WELD FAILURE IS ASSOCIATED WITH A VIBRATION CAUSED FROM AN 8-INCH FLOW CONTROL VALVE AT THE REGULATOR STATION AT GATE 6. CIG FINALIZED A VIBRATION STUDY ON APRIL 24, 2019. RESULTS OF THE STUDY IDENTIFIED FACILITY MODIFICATIONS WILL BE NECESSARY TO HELP REDUCE VIBRATION AND UNTIL THESE CHANGES CAN BE COMPLETED, CIG WILL IMPLEMENT OPERATING CHANGES AS NEEDED TO HELP LOWER VIBRATION LEVELS.